## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:March-2023
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2023-03-01 |  | 2023-03-01 |  | 2022-03-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 12921 | 2023-03-13 | 11708 | 2023-02-27 | 13662 | 2022-03-31 | 15648 | 2023-04-19
|  |  | 19:00 |  | 19:00 |  | 19:30 |  | 21:00
2 | Minimum Generation (MW) | 6507 | 2023-03-20 | 6484 | 2023-02-04 | 6823 | 2022-03-05 | - | -
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 12921 | 2023-03-13 | 11708 | 2023-02-27 | 13662 | 2022-03-31 | 15648 | 2023-04-19
|  |  | 19:00 |  | 19:00 |  | 19:30 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 11515 | 2023-03-14 | 10493 | 2023-02-27 | 12116 | 2022-03-27 | 13415 | 2023-04-19
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 13046 | 2023-03-31 | 11795 | 2023-02-28 | 13662 | 2022-03-31 | 16096 | 2023-04-19
|  |  | 21:00 |  | 19:00 |  | 12:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 11615.6452 |  | 10536.9643 |  | 12057.9032
7 | Average Generation (MW) at Day Peak | 10322.4194 |  | 9326.8214 |  | 10564
8 | Maximum Power Import from India, BIPTC (MW) | 920 | 2023-03-02 | 919 | 2023-02-28 | 938 | 2022-03-29 | 956 | 27/3/2019
|  |  | 23:00 |  | 17:30 |  | 10:30 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 170 | 2023-03-13 | 152 | 2023-02-23 | 182 | 2022-03-23 | 194 | 12/06/19
|  |  | 14:00 |  | 18:00 |  | 18:30 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 236 | 2023-03-05 | 470 | 2023-02-14 | - | - | 4395 | 04/10/2022
|  |  | 19:00 |  | 19:00 |  | - |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 12052 | 2023-03-05 | 10328 | 2023-02-14 | - | - | 13200 | 04/10/2022
|  | - | 19:00 |  | 19:00 | - | - |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 40 | 2023-03-03 | 0 | 2023-02-18 | - | -
|  |  | 19:00 |  | 19:30
13 | Generation During Min. Load Shed (MW) at Evening Peak | 10693 | 2023-03-03 | 10586 | 2023-02-18 | - | -
|  |  | 19:00 |  | 19:30
14 | Maximum Load Shed (MW) at Day Peak | 356 | 2023-03-06 | 986 | 2023-02-12 | - | -
|  |  | 12:00 |  | 12:00
15 | Generation During Max. Load Shed (MW) at Day Peak | 10869 | 2023-03-06 | 8780 | 2023-02-12 | - | -
|  |  | 12:00 |  | 12:00
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2023-03-08 | 0 | 2023-02-17 | - | -
|  |  | 12:00 |  | 12:00
17 | Generation During Min. Load Shed (MW) at Day Peak | 9421 | 2023-03-08 | 8927 | 2023-02-17 | - | -
|  |  | 12:00 |  | 12:00
18 | Nos. of Days Load Shed at Evening Peak | 18 |  | 23 |  | -
19 | Nos. of Days Load Shed at Day Peak | 12 |  | 25 |  | -
20 | Gross Generation of BPDB (MKWH) | 1561.2501 |  | 1366.7592 |  | 1551.2856 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 46.9674 |  | 45.9327 |  | 80.4189
22 | Net Generation of BPDB (MKWH) | 1514.2827 |  | 1320.8266 |  | 1470.8667
23 | Net Generation of IPP (MKWH) | 4695.4667 |  | 3589.391 |  | 4916.0698
24 | Net Generation of REB (MKWH) | 121.5861 |  | 113.7895 |  | 144.2163
24 | Net Generation of Rental Power Plant (MKWH) | 299.4051 |  | 225.4883 |  | 498.1914
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 6630.7407 |  | 5249.4954 |  | 7029.3442 |  | 7842.9924 | April'22
26 | Energy Generation by Gas (MKWH) | 4237.6738 |  | 3202.315 |  | 3806.7453 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 214.1302 |  | 17.6361 |  | 475.2564 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1443.6516 |  | 1039.0523 |  | 2203.7804 |  | 2365.7466 | April'22
29 | Energy Generation by Hydro (MKWH) | 17.7881 |  | 22.8708 |  | 43.3314 |  | 104.66 | Sep-22
30 | Energy Generation by Solar (MKWH) | 146.7623 |  | 36.208 |  | 40.5844 |  | 40.58 | March-22
31 | Energy Generation by Coal (MKWH) | 617.702 |  | 977.3458 |  | 540.0652 |  | 950.96 | Sep'22
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 535.4411 |  | 629.869 |  | 644.0891 |  | 776.67 | August-22
33 | Monthly Load Factor (%) | 84.1419 |  | 76.3661 |  | 84.4682 |  | 92.62 | August-22

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:March-2023
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 12921 | 2023-03-13 | 19:00
Generation Period
| Dhaka | MW | 4484.55
| Chattogram | MW | 1384.7
| Cumilla | MW | 1030
| Mymensingh | MW | 815
| Sylhet | MW | 412
a) | Total supply in East zone | MW | 8126.25
| Khulna | MW | 1221
| Barisal | MW | 302.34
| Rajshahi | MW | 1076.6
| Rangpur | MW | 629
b) | Total supply in West zone | MW | 3228.94
c) | Total supply in both zone ( a+b) | MW | 11355.19
Ref: | 27.21.0000.603.16.087.20.649 | Date: 20/04/2023
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:November 2022
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 500 | 2023-03-15 | 7:00
| b) Ishurdi end | MW | 402 | 2023-03-24 | 6:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 1000 | 2023-03-20 | 15:00
| b) Ishurdi end | MW | 278 | 2023-03-12 | 21:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 6.49
| b) Ishurdi end | MKWH | 125.2
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 111.17
| b) Ishurdi end | MKWH | 6.29
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 240 | 2023-03-17 | 20:00
| b)Serajganj end | MW | 420 | 2023-03-24 | 6:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 380 | 2023-03-22 | 16:00
| b)Sirajganj end | MW | 244 | 2023-03-17 | 20:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 6.4
| b)Sirajganj end | MKWH | 91.5
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 88.5
| b)Sirajganj end | MKWH | 6.4
30 | Transmission loss of EWI /NO-2 | % | 2.941
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/3 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: March2023
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Joydebpur | Joydebpur 132/33kV Grid Sub-Station GT-4 HT | 2023-03-22 21:49 | 2023-03-22 22:05 | 0:16 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Savar | 132/33kV transformer T-3 LT | 2023-03-11 11:12 | 2023-03-11 11:17 | 0:05 | T | Due to 33kV L-32 and L-37 Feeder fault (over current trip). | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformerT-1 HT | 2023-03-22 06:51 | 2023-03-22 09:17 | 2:26 | T | Due to Over load | 0 | 0 | No interruption
| 132/33 kV transformerT-2 HT | 2023-03-22 07:55 | 2023-03-22 09:42 | 1:47 | T |  | 40 | 71.3333 | Power interruption
| 132/33 transformerT-2 HT | 2023-03-22 09:46 | 2023-03-22 10:00 | 0:14 | T |  | 40 | 9.3333 | Power interruption
Kishoreganj | 132/33 kV transformerTr-1 (404T) LT | 2023-03-04 18:57 | 2023-03-04 19:05 | 0:08 | T | Due to Over Load | 39 | 5.2 | Power interruption
| 132/33 kV transformerTr-2 (414T) HT | 2023-03-04 18:57 | 2023-03-04 20:06 | 1:09 | T | Tripped showing Differential relay | 0 | 0 | No interruption
| 132/33 kV transformerTr-2 (414T) LT | 2023-03-04 18:57 | 2023-03-04 20:10 | 1:13 | T | Due to Inter-trip relay | 39 | 47.45 | Power interruption
Mirpur | 132/33 kV TransformerT1 HT | 2023-03-06 08:48 | 2023-03-06 15:42 | 6:54 | E/O | Main Bus DS hotspot maintenance | 0 | 0 | No interruption
Mirpur | 132/33 kV TransformerT1 LT | 2023-03-06 08:48 | 2023-03-06 15:42 | 6:54 | E/O | Main Bus DS hotspot maintenance | 0 | 0 | No interruption
Agargaon | 230/132kV Transformer-1 (405T1) HT | 2023-03-11 08:59 | 2023-03-12 20:53 | 35:54 | E/O | Oil Leakage | 0 | 0 | No interruption
Agargaon | 230/132kV Transformer-1 (405T1) LT | 2023-03-11 08:45 | 2023-03-12 21:11 | 36:26 | E/O | Oil Leakage | 0 | 0 | No interruption
Kodda | 132/33 kV Transformer Tr-2 (416T) LT | 2023-03-15 06:36 | 2023-03-15 10:11 | 3:35 | E/O | Due to Red hot maintenance | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer XFR, T-2 HT | 2023-03-27 09:14 | 2023-03-27 11:31 | 2:17 | E/O | Due to Red hot maintenance at 33 kV | 90 | 205.5 | Power interruption
|  |  | Total : | 7:18 |  | Unserved Energy: |  | 133.3167
Dhaka (South) Grid Circle :
Hasnabad | 230/132 kV Transformer AUTO TR-1 HT | 2023-03-01 09:10 | 2023-03-03 09:55 | 48:45 | E/O | Oil Centrifuge | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer AUTO TR-1 LT | 2023-03-01 09:10 | 2023-03-03 09:55 | 48:45 | E/O | Oil Centrifuge | 0 | 0 | No interruption
Siddhirganj | 132/33 kV transformerT-1 HT | 2023-03-31 01:32 | 2023-03-31 02:25 | 0:53 | E/O | Cyclone & Lightning | 10 | 8.8333 | Power interruption
| 132/33 kV transformerT-1 LT | 2023-03-31 01:32 | 2023-03-31 05:00 | 3:28 | E/O | Cyclone & Lightning | 10 | 34.6667 | Power interruption
| 132/33 kV T-2 transformer HT | 2023-03-31 01:32 | 2023-03-31 02:25 | 0:53 | E/O | Cyclone & Linghtning | 10 | 8.8333 | Power interruption
| 132/33 kV transformerT-2 LT | 2023-03-31 01:32 | 2023-03-31 05:00 | 3:28 | E/O | Cyclone & Lightning | 0 | 0 | Power interruption
| 230/132 kV transformer MTR 1 HT | 2023-03-31 01:40 | 2023-03-31 14:06 | 12:26 | T | Due to 132 kV feeder Fault | 25 | 310.8333 | Power interruption
| 230/132 kV transformer MTR 2 HT | 2023-03-31 01:40 | 2023-03-31 03:45 | 2:05 | T | 132 kv side Fault | 25 | 52.0833 | Power interruption
Sonargaon | 132/33 kV transformerTr-2 LT | 2023-03-24 14:31 | 2023-03-24 17:01 | 2:30 | E/O | Due to Narsindi fedder CB pole insulators blast. | 0 | 0 | No interruption
| 132/33 kV transformerTr-2 LT | 2023-03-31 01:34 | 2023-03-31 03:20 | 1:46 | E/O | Langalband feeder isolator jumper wires problem. | 0 | 0 | No interruption
Maniknagar | 132/33Transformer GT-1 HT | 2023-03-31 09:52 | 2023-03-31 14:02 | 4:10 | E/O | Due to 33 kV breaker maintenance | 0 | 0 | No interruption
Rampura | 230/132 Auto Transformer - 03 HT | 2023-03-10 06:48 | 2023-03-10 09:17 | 2:29 | E/O | Due to Auxiliary Tx-3 oil refil | 0 | 0 | No interruption
Rampura | 230/132kV Auto Transformer - 03 LT | 2023-03-10 06:48 | 2023-03-10 09:17 | 2:29 | E/O | Due to Auxiliary Tx-3 oil refil | 0 | 0 | No interruption
Keranigonj | 230/132/33kV transformer TR-1 LT | 2023-03-18 08:55 | 2023-03-18 09:30 | 0:35 | E/O | Due to 33 KV Bus section 02 pole insulator blast of all three phases. | 28 | 16.3333 | Power interruption
Keranigonj | 230/132/33kV transformer TR-2 LT | 2023-03-18 08:55 | 2023-03-18 09:30 | 0:35 | E/O | Due to 33 KV Bus section 02 pole insulator blast of all three phases | 0 | 0 | No interruption
Munshiganj | 132/33 kV Transformer-1 LT | 2023-03-17 03:50 | 2023-03-17 04:05 | 0:15 | T | Kalvaishakhi | 17 | 4.25 | Power interruption
| 132/33 kV Transformer-2 HT | 2023-03-17 03:50 | 2023-03-17 04:05 | 0:15 | T | Kalvaishakhi | 17 | 4.25 | Power interruption
| 132/33 kV Transformer-2 LT | 2023-03-17 03:50 | 2023-03-17 04:05 | 0:15 | T | Kalvaishakhi | 17 | 4.25 | Power interruption
| Auxiliary Transformer-1 LT | 2023-03-17 03:50 | 2023-03-17 04:05 | 0:15 | T | Kalvaishakhi | 0 | 0 | No interruption
| 132/33 kV Transformer-1 LT | 2023-03-28 12:01 | 2023-03-28 13:01 | 1:00 | E/O | Emergency Maintenance Work at 33 kV side | 25 | 25 | Power interruption
Shyampur | Auto TR-1 HT | 2023-03-31 01:41 | 2023-03-31 02:21 | 0:40 | T | Due to stromy weather | 0 | 0 | No interruption
| Auto TR-2 HT | 2023-03-31 01:41 | 2023-03-31 02:39 | 0:58 | T | Due to stromy weather. | 0 | 0 | No interruption
Bhulta | 132/33 kV transformer GT1 HT | 2023-03-19 10:44 | 2023-03-19 14:58 | 4:14 | T | Undefine | 0 | 0 | No interruption
|  |  | Total : | 38:17 |  | Unserved Energy: |  | 440.0833
Chattogram Grid Circle :
Modern Steel | 132/11 kV transformerT-1(407T) HT | 2023-03-28 07:23 | 2023-03-28 09:11 | 1:48 | T | Did not get any reason. | 0 | 0 | No interruption
Coxsbazar | 132/33 kV transformer405T-T1 HT | 2023-03-14 09:13 | 2023-03-14 09:29 | 0:16 | T | 24- Over Flux | 38 | 10.1333 | Power interruption
| 132/33 kV transformer415T-T2 LT | 2023-03-27 08:33 | 2023-03-27 08:46 | 0:13 | T | Tripped showing MCGG relays | 10 | 2.1667 | Power interruption
| 132/33 kV transformer T3 HT | 2023-03-06 11:42 | 2023-03-06 11:45 | 0:03 | T | G2G project testing by system protection. | 22 | 1.1 | Power interruption
|  |  | Total : | 0:32 |  | Unserved Energy: |  | 13.4
Cumilla Grid Circle :
Chandpur | 132/33kV transformer 402T HT | 2023-03-15 12:18 | 2023-03-15 12:52 | 0:34 | E/O | Due to Post Insulator Broken & Flashing with 33KV Chandpur-3 Feeder | 12 | 6.8 | Power interruption
Chandpur | 132/33kV transformer 402T LT | 2023-03-15 12:18 | 2023-03-15 12:52 | 0:34 | E/O |  | 12 | 6.8 | Power interruption
Chandpur | 132/33 kV Transformer422T HT | 2023-03-23 06:50 | 2023-03-23 09:34 | 2:44 | S/O | Under Bus section -3(Tr-05) Feeder 33 kv motlob,Hajigonj 2,Kachua Riser, loop and breaker maintenance work. | 15 | 41 | Power interruption
Chandpur | 132/33 kV Transformer422T LT | 2023-03-23 06:50 | 2023-03-23 09:34 | 2:44 | S/O | Under Bus section -3(Tr-05) Feeder 33 kv motlob,Hajigonj 2,Kachua Riser, loop and breaker maintenance work. | 15 | 41 | Power interruption
Cumilla(N) | 230/132kV transformer T-05 LT | 2023-03-15 11:36 | 2023-03-15 12:49 | 1:13 | T | Tripped showing 33KV Borodhusia Feeder Fault | 0 | 0 | No interruption
Cumilla(S) | 132/33kV transformerTR-1 LT | 2023-03-10 07:40 | 2023-03-10 08:08 | 0:28 | T | Tripped showing Kasba feeder fault | 24 | 11.2 | Power interruption
Cumilla(S) | 132/33kV transformerTR-2 LT | 2023-03-10 07:40 | 2023-03-10 08:08 | 0:28 | T | Tripped showing Kasba feeder fault | 24 | 11.2 | Power interruption
Brahmanbaria | 132/33kV transformer401T LT | 2023-03-15 16:57 | 2023-03-15 17:14 | 0:17 | T | Tripped showing PBS Nabinagar 33KV feeder fault | 52 | 14.7333 | Power interruption
Brahmanbaria | 132/33kV transformer401T LT | 2023-03-31 05:28 | 2023-03-31 06:11 | 0:43 | T | Tripped showing LA,CT,CB blast of T3 Transformer ,BPDB | 30 | 21.5 | Power interruption
Brahmanbaria | 132/33kV transformer402T LT | 2023-03-15 16:57 | 2023-03-15 17:14 | 0:17 | T | Tripped showing33KV Nabinagar PBS feeder fault | 52 | 14.7333 | Power interruption
Brahmanbaria | 132/33kV transformer402T LT | 2023-03-31 05:28 | 2023-03-31 06:11 | 0:43 | T | Tripped showingLA,CT,CB blast of T3 Transformer ,BPDB | 30 | 21.5 | Power interruption
Shahjibazar | 132/33kV transformerTR-02 HT | 2023-03-05 11:09 | 2023-03-05 11:15 | 0:06 | T | Tripped showing 33KV feeder fault | 0 | 0 | No interruption
Shahjibazar | 132/33kV transformerTR-02 LT | 2023-03-05 11:09 | 2023-03-05 11:25 | 0:16 | T | Tripped showing 33KV feeder fault(O/C,E/F) | 8 | 2.1333 | Power interruption
Shahjibazar | 132/33kV transformerTR-02 LT | 2023-03-31 01:03 | 2023-03-31 02:10 | 1:07 | T | Tripped showing 33KV feeder fault(O/C,E/F) | 0 | 0 | No interruption
Shahjibazar | 132/33kV transformerTR-06 LT | 2023-03-23 13:58 | 2023-03-23 14:36 | 0:38 | T | Due to Jamuna feeder falut | 14 | 8.8667 | Power interruption
Shahjibazar | 132/33 kV TransformerTR-02 HT | 2023-03-15 06:31 | 2023-03-15 07:46 | 1:15 | S/O | HT side R phase clamp red hot maintenance. | 0 | 0 | No interruption
Shahjibazar | 132/33 kV TransformerTR-02 LT | 2023-03-15 06:29 | 2023-03-15 08:34 | 2:05 | S/O | HT side R phase clamp red hot maintenance. | 0 | 0 | No interruption
Sreemongol | 132/33kV transformer T-2 HT | 2023-03-03 06:12 | 2023-03-03 06:18 | 0:06 | T | Dueue to 33 kv vunibir feeder fault. | 18 | 1.8 | Power interruption
Sreemongol | 132/33kv transformerT-2 HT | 2023-03-18 05:41 | 2023-03-18 05:50 | 0:09 | T | due to 33 kV Bahubal-1 feeder fault. | 7 | 1.05 | Power interruption
Sreemongol | 132/33kv transformer T-2 HT | 2023-03-31 02:05 | 2023-03-31 02:09 | 0:04 | T | Tripped showing 33KV feeder fault(O/C,E/F) | 0 | 0 | No interruption
Sreemongol | 132/33kv transformerT-2 LT | 2023-03-18 05:41 | 2023-03-18 05:50 | 0:09 | T | Due to33 kV Bahubal-1 Feeder's fault. | 7 | 1.05 | Power interruption
Sreemongol | 132/33kv transformer T-2 LT | 2023-03-31 02:05 | 2023-03-31 02:10 | 0:05 | T | Tripped showing 33KV feeder fault(O/C,E/F) | 0 | 0 | No interruption
Sreemongol | 132/33kv transformer T-3 HT | 2023-03-03 06:12 | 2023-03-03 06:18 | 0:06 | T | Due to 33KV vunobir fedder fault | 18 | 1.8 | Power interruption
Sreemongol | 132/33kv transformer T-3 HT | 2023-03-18 05:41 | 2023-03-18 05:50 | 0:09 | T | Due to33 kV Bahubal-1 feeder fault | 15 | 2.25 | Power interruption
Sreemongol | 132/33kv transformerT-3 LT | 2023-03-03 06:12 | 2023-03-03 06:20 | 0:08 | T | Tripped showing O/C,& E/F | 18 | 2.4 | Power interruption
Chhatak | 132/33kv transformerT-1 LT | 2023-03-19 19:39 | 2023-03-19 19:43 | 0:04 | T | Due to 33kv Sunamganj PDB feeder fault. | 0 | 0 | No interruption
Chhatak | 132/33kv transformerT1 LT | 2023-03-20 14:27 | 2023-03-20 14:32 | 0:05 | T | Due to 33 kV Sunamganj PDB feeder fault | 0 | 0 | No interruption
Sylhet | 132/33kv transformer T1 LT | 2023-03-21 03:26 | 2023-03-21 03:51 | 0:25 | T | Due to Fault of 33KV Badaghat feeder | 10 | 4.1667 | Power interruption
Kulaura | 132/33 kV TransformerTR-1 HT | 2023-03-26 00:03 | 2023-03-26 00:35 | 0:32 | S/O | Red hot maintenance of REB-1 | 20 | 10.6667 | Power interruption
Kulaura | 132/33 kV TransformerTR-1 LT | 2023-03-26 00:03 | 2023-03-26 00:37 | 0:34 | S/O | Red hot maintenance of REB-1 | 20 | 11.3333 | Power interruption
Sylhet | 132/33kv transformer T1 LT | 2023-03-22 07:07 | 2023-03-22 10:05 | 2:58 | T | Due to Badhghat Feeder Fault, Sylhet PBS-1 | 7 | 20.7667 | Power interruption
|  |  | Total : | 21:46 |  |  |  | 258.75
Khulna Grid Circle :
Barishal | 132/33kv transformer T-1 (405T) HT | 2023-03-04 13:57 | 2023-03-04 14:16 | 0:19 | T | Due to Nolcity (PBS) FEEDER FAULT | 31 | 9.8167 | Power interruption
Barishal | 132/33kv transformerT-1 (405T) LT | 2023-03-04 13:57 | 2023-03-04 14:15 | 0:18 | T | Due to Nolcity (PBS) feeder fault. | 31 | 9.3 | Power interruption
Barishal | 132/33kv transformerT-2 (415T) HT | 2023-03-13 12:47 | 2023-03-13 12:50 | 0:03 | T | Due to Chandmari(WZPDCL) 33 kv feeder fault. | 63 | 3.15 | Power interruption
Barishal | 132/33kv transformerT-2 (415T) LT | 2023-03-04 13:57 | 2023-03-04 14:14 | 0:17 | T | Due to Nolcity (PBS) feeder fault | 19 | 5.3833 | Power interruption
Barishal | 132/33kv transformeT-2 (415T) LT | 2023-03-13 12:47 | 2023-03-13 12:50 | 0:03 | T | Due to Candmari (WZPDCL) 33kv feeder fault. | 63 | 3.15 | Power interruption
Barishal | 132/33kv transformeT-4 LT | 2023-03-15 03:45 | 2023-03-15 08:12 | 4:27 | T | Tripped showing Over current | 25 | 111.25 | Power interruption
Barishal | 132/33kv transformeT-5 LT | 2023-03-15 03:45 | 2023-03-15 08:12 | 4:27 | T | Tripped showing Over current | 25 | 111.25 | Power interruption
Barishal | 132/33 kV TransformerT-2 (415T) HT | 2023-03-14 07:07 | 2023-03-14 08:31 | 1:24 | E/O | Due to Red hot.maint. | 0 | 0 | No interruption
Barishal | 132/33 kV TransformerT-2 (415T) LT | 2023-03-14 07:05 | 2023-03-14 08:32 | 1:27 | E/O | Due to Red hot.maint. | 0 | 0 | No interruption
Barishal | 230/132kV Transformer ATR-1 HT | 2023-03-22 08:38 | 2023-03-22 18:17 | 9:39 | E/O | Due to Oil Leakge | 0 | 0 | No interruption
Barishal | 230/132kV TransformerATR-1 HT | 2023-03-24 10:14 | 2023-03-24 20:38 | 10:24 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Barishal | 230/132kV Transformer ATR-1 LT | 2023-03-22 08:37 | 2023-03-22 18:13 | 9:36 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Barishal | 230/132kV Transformer ATR-1 LT | 2023-03-24 10:14 | 2023-03-24 20:36 | 10:22 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Barishal | 230/132kV Transformer ATR-2 HT | 2023-03-23 08:56 | 2023-03-23 16:40 | 7:44 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Barishal | 230/132kV Transformer ATR-2 LT | 2023-03-23 08:39 | 2023-03-23 16:39 | 8:00 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Barishal n | 230/132kV Transformer T-4 HT | 2023-03-13 06:13 | 2023-03-13 08:27 | 2:14 | E/O | Due to Red Hot Maintenance | 0 | 0 | No interruption
Barishal | 230/132kV Transformer T-4 LT | 2023-03-13 06:13 | 2023-03-13 08:30 | 2:17 | E/O | Due to Red Hot Maintenance | 0 | 0 | No interruption
Barishal | 230/132kV TransformerT-5 HT | 2023-03-13 08:31 | 2023-03-13 12:19 | 3:48 | E/O | Due to Red hot.maint. | 0 | 0 | No interruption
Barishal | 230/132kV TransformerT-5 LT | 2023-03-13 08:31 | 2023-03-13 12:23 | 3:52 | E/O | Due to Red hot.maint. | 0 | 0 | No interruption
Patuakhali | 132/33kv transforme425T (T-3) HT | 2023-03-21 16:24 | 2023-03-21 17:09 | 0:45 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Patuakhali | 132/33kv transforme425T (T-3) LT | 2023-03-21 16:24 | 2023-03-21 17:09 | 0:45 | T | No signal | 0 | 0 | No interruption
Faridpur | 132/33kv transformeTransformer-2 LT | 2023-03-19 13:51 | 2023-03-19 14:04 | 0:13 | T | Tripped showing Rajbari 33kv wz feeder fault | 72 | 15.6 | Power interruption
Faridpur | 132/33kv transformeT-3 HT | 2023-03-26 14:15 | 2023-03-26 22:35 | 8:20 | T | Tripped showing 33kv Feeder Fault | 4 | 33.3333 | Power interruption
Faridpuron | 132/33kVTransformer-2 HT | 2023-03-18 08:25 | 2023-03-18 14:24 | 5:59 | E/O | Due to Red hot.maint. | 0 | 0 | No interruption
Faridpur n | 132/33kV Transformer-2 LT | 2023-03-06 07:15 | 2023-03-06 10:20 | 3:05 | E/O | Due to Oil Leakge | 0 | 0 | No interruption
Faridpurion | 132/33kV Transformer-2 LT | 2023-03-18 08:25 | 2023-03-18 14:25 | 6:00 | E/O | Red Hot maintenance | 0 | 0 | No interruption
Gopalganj tation | 132/33kV TransformerT1 HT | 2023-03-15 16:28 | 2023-03-15 17:50 | 1:22 | E/O | Due to REB- 1 Red hot maintenance. | 10 | 13.6667 | Power interruption
Gopalganjtation | 132/33kV Transforme T1 LT | 2023-03-15 16:28 | 2023-03-15 17:51 | 1:23 | E/O | Due to REB- 1 Red hot maintenance. | 10 | 13.8333 | Power interruption
Gopalganj | 132/33kv transformeT1 LT | 2023-03-15 09:25 | 2023-03-15 11:25 | 2:00 | T | Due toAuxiliary Tr-1 trip by bird | 25 | 50 | Power interruption
Gopalganj | 132/33kv transformeT2 LT | 2023-03-15 09:25 | 2023-03-15 10:03 | 0:38 | T | Due to T-1 Auxi-1 trip by bird | 25 | 15.8333 | Power interruption
Madaripur | 132/33kv transformeT1-405T HT | 2023-03-15 11:42 | 2023-03-15 12:01 | 0:19 | T | Due to Auxiliary Transformer R phase Out | 16 | 5.0667 | Power interruption
Madaripur | 132/33kv transformeT2-415T LT | 2023-03-15 11:42 | 2023-03-15 11:59 | 0:17 | T | Due to Auxiliary Transformer-2 R phase Out | 16 | 4.5333 | Power interruption
Madaripur | 132/33kV Transformer T3-426T HT | 2023-03-18 11:40 | 2023-03-18 11:57 | 0:17 | E/O | Due to CT Oil Leakage Maintenance | 0 | 0 | No interruption
Madaripuron | 132/33kV Transformer T3-426T LT | 2023-03-18 11:40 | 2023-03-18 11:59 | 0:19 | E/O | Due to CT Oil Leakage Maintenance | 0 | 0 | No interruption
Khulna © | 132/33kv transformeTR-1 425T LT | 2023-03-13 19:06 | 2023-03-13 19:40 | 0:34 | E/O | 33 KV BUS SECTION 2 PT FUSE BURN OUT. | 33 | 18.7 | Power interruption
Khulna (C) | 132/33kv transformeTr-2 415 T HT | 2023-03-13 19:04 | 2023-03-13 19:50 | 0:46 | E/O | 33 KV BUS SECTION 2 PT FUSE BURN OUT. | 33 | 25.3 | Power interruption
Khulna (C) | 132/33kv transformeTr-2 415 T LT | 2023-03-13 19:04 | 2023-03-13 19:50 | 0:46 | E/O | 33 KV BUS SECTION 2 PT FUSE BURN OUT. | 33 | 25.3 | Power interruption
Khulna (C) | 132/33kv transformeTr-3 405T HT | 2023-03-13 19:06 | 2023-03-13 19:20 | 0:14 | E/O | 33 kv bus section 2 pt fuse out | 31 | 7.2333 | Power interruption
Khulna © | 132/33kv transformeTr-3 405T LT | 2023-03-13 19:06 | 2023-03-13 19:20 | 0:14 | E/O | 33 kv bus section 2 pt fuse out | 31 | 7.2333 | Power interruption
Narail | 132/33kv transformeTR1 (403-T) LT | 2023-03-25 19:47 | 2023-03-25 20:13 | 0:26 | T | None | 15 | 6.5 | Power interruption
Narail | 132/33kv transformeTR2 (413-T) LT | 2023-03-25 19:47 | 2023-03-25 20:15 | 0:28 | T | None | 15 | 7 | Power interruption
Bagerhat | 132/33kv transformeT-1 (403T) HT | 2023-03-29 21:22 | 2023-03-29 21:34 | 0:12 | T | Thunder strom | 0 | 0 | No interruption
Bagerhat | 132/33kv transformeTr-1 (403T) LT | 2023-03-29 21:22 | 2023-03-29 21:34 | 0:12 | T | Thunder strom. | 0 | 0 | No interruption
Bagerhat | 132/33kv transformeT-2 (413 T) HT | 2023-03-29 21:22 | 2023-03-29 21:34 | 0:12 | T | Thunder strom. | 0 | 0 | No interruption
Bagerhat | 132/33kv transformer-2 (413 T) LT | 2023-03-29 21:22 | 2023-03-29 21:34 | 0:12 | T | Thunder strom. | 0 | 0 | No interruption
Bagerhat | 132/33kv transformeT-3 ( 423 T) LT | 2023-03-25 09:05 | 2023-03-25 09:54 | 0:49 | E/O | Wrong operation of Live line BSCIC feeder DS by PBS SBA. | 27 | 22.05 | Power interruption
Gollamari | 132/33kV Transformer Tr-1 LT | 2023-03-29 18:36 | 2023-03-29 19:56 | 1:20 | S/O | Red Hot | 0 | 0 | No interruption
Satkhira Station | 132/33kV Transformer-1 (T-1) HT | 2023-03-09 07:20 | 2023-03-09 09:06 | 1:46 | S/O | Red hot maintenance work. | 0 | 0 | No interruption
Satkhiraon | 132/33kV Transformer-1 (T-1) LT | 2023-03-09 07:20 | 2023-03-09 09:09 | 1:49 | S/O | Red hot maintenance work | 0 | 0 | No interruption
|  |  | Total : | 117:28 |  |  |  | 524.4833
HVDC Grid Circle :
Bheramara(GK) | 132/33kV TransformerTR-3 HT | 2023-03-07 17:28 | 2023-03-09 10:41 | 41:13 | E/O | Due to Emergency Maintenance Work | 0 | 0 | No interruption
Bheramara(GK) | 132/33kV TransformerTR-3 LT | 2023-03-07 17:27 | 2023-03-09 10:43 | 41:16 | E/O | Due to Emergency Maintenance Work | 0 | 0 | No interruption
Jashore | 132/33kV TransformerT-1 HT | 2023-03-29 08:50 | 2023-03-29 10:48 | 1:58 | E/O | Due to Red maintenance | 0 | 0 | No interruption
Jashore | 132/33kV TransformerT-1 HT | 2023-03-31 07:07 | 2023-03-31 10:21 | 3:14 | E/O | Due to Red maintenance | 12 | 38.8 | Power interruption
Jashore | 132/33kV TransformerT-1 HT | 2023-03-31 14:55 | 2023-03-31 15:58 | 1:03 | E/O | Due to Red maintenance | 0 | 0 | No interruption
Jashore | 132/33kV TransformerT-1 LT | 2023-03-29 08:49 | 2023-03-29 10:50 | 2:01 | E/O | Due to Red maintenance | 22 | 44.3667 | Power interruption
Jashore | 132/33kV TransformerT-1 LT | 2023-03-31 07:06 | 2023-03-31 10:24 | 3:18 | E/O | Due to Red maintenance | 12 | 39.6 | Power interruption
Jashore | 132/33kV TransformerT-1 LT | 2023-03-31 14:54 | 2023-03-31 15:59 | 1:05 | E/O | Due to Red maintenance | 0 | 0 | No interruption
Jashore | 132/33kV TransformerT-2 HT | 2023-03-29 06:49 | 2023-03-29 08:31 | 1:42 | E/O | Due to Red maintenance | 12 | 20.4 | Power interruption
Jashore | 132/33kV TransformerT-2 HT | 2023-03-31 11:03 | 2023-03-31 13:16 | 2:13 | E/O | Due to Red maintenance | 0 | 0 | No interruption
Jashore | 132/33kV TransformerT-2 LT | 2023-03-29 06:48 | 2023-03-29 08:34 | 1:46 | E/O | Due to Red maintenance | 12 | 21.2 | Power interruption
Jashore | 132/33kV TransformerT-2 LT | 2023-03-31 11:02 | 2023-03-31 13:17 | 2:15 | E/O | Due to Red maintenance | 0 | 0 | No interruption
Kushtia | 132/33kV TransformerT-1 LT | 2023-03-31 08:26 | 2023-03-31 10:29 | 2:03 | E/O | Due to Red maintenance | 26 | 53.3 | Power interruption
Ishurdi | 132/33kV Transformer T-2 LT | 2023-03-16 18:30 | 2023-03-16 19:51 | 1:21 | E/O | Due to Redhot maint.work | 0 | 0 | No interruption
Shahjadpur | 132/33kV TransformerT-1(405T) HT | 2023-03-19 11:02 | 2023-03-19 13:22 | 2:20 | E/O | Due to 33 kV incoming Ds flashing. | 0 | 0 | No interruption
Shahjadpur | 132/33kV TransformerT-1(405T) LT | 2023-03-17 20:12 | 2023-03-17 21:12 | 1:00 | E/O | 33 kv Talgachi incoming DS foult. | 0 | 0 | No interruption
Pabna | 132/33kV transformer T-1 LT | 2023-03-01 15:21 | 2023-03-01 15:37 | 0:16 | E/O | Due to 33KV T-1 BKR Y-Phase Blast. | 17 | 4.5333 | Power interruption
| 132/33kV transformer T-3 LT | 2023-03-23 17:45 | 2023-03-23 18:15 | 0:30 | T | Tripped showing Over current | 10 | 5 | Power interruption
|  |  | Total : | 0:46 |  |  |  | 9.5333
Bogura Grid Circle:
Bog-Sherpur | 132/33kV Transformer-1 (404T) HT | 2023-03-22 07:36 | 2023-03-22 09:23 | 1:47 | E/O | Due to Red Hot Maintenance | 0 | 0 | No interruption
Bog-Sherpur | 132/33kV Transformer-1 (404T) LT | 2023-03-22 07:35 | 2023-03-22 09:24 | 1:49 | E/O | Due to Red Hot Maintenance | 0 | 0 | No interruption
Bogura | 132/33kV Transformer-1 HT | 2023-03-28 10:07 | 2023-03-28 12:30 | 2:23 | E/O | Due to Red Hot Maintenance | 0 | 0 | No interruption
Bogura | 132/33kV Transformer1 LT | 2023-03-28 10:07 | 2023-03-28 12:30 | 2:23 | E/O | Due to Red Hot Maintenance | 0 | 0 | No interruption
Bogura | 132/33kV Transformer-2 HT | 2023-03-31 11:18 | 2023-03-31 12:38 | 1:20 | E/O | Due to Red hot maint.of 33 kV Side | 32 | 42.6667 | Power interruption
Bogura | 132/33kV Transformer-2 LT | 2023-03-31 11:18 | 2023-03-31 12:38 | 1:20 | E/O | Due to Red hot maint.of 33 kV Side | 32 | 42.6667 | Power interruption
Sirajganj | 132/33kV TransformerT4-(445) HT | 2023-03-21 19:21 | 2023-03-21 21:25 | 2:04 | E/O | Due to Red hot maint.of 33 kV Side | 15 | 31 | Power interruption
Sirajganj | 132/33kV TransformerT4-(445) HT | 2023-03-23 17:15 | 2023-03-23 18:10 | 0:55 | E/O | Due to Red hot maint.of 33 kV Side | 20 | 18.3333 | Power interruption
Sirajganj | 132/33kV TransformerT4-(445) LT | 2023-03-21 19:20 | 2023-03-21 21:26 | 2:06 | E/O | Due to Red hot maint.of 33 kV Side | 15 | 31.5 | Power interruption
Panchagarh | 132/33kV Transformer 427T(A+B) LT | 2023-03-16 19:30 | 2023-03-17 11:32 | 16:02 | E/O | Due to Red hot maint.of 33 kV Side | 0 | 0 | No interruption
Amnura | 132/33kV TransformerT-1 (406T) LT | 2023-03-20 07:16 | 2023-03-20 09:25 | 2:09 | E/O | Due to Red hot maint.of 33 kV Side | 0 | 0 | No interruption
Natore | 132/33kV TransformerTR-4 (435 T) HT | 2023-03-09 07:26 | 2023-03-09 08:40 | 1:14 | E/O | Due to maint.work | 0 | 0 | No interruption
Niamatpur | 132/33kV Transformer 417T HT | 2023-03-21 09:16 | 2023-03-21 15:30 | 6:14 | E/O | Due to Oil Leakage.at 33 kV | 0 | 0 | No interruption
Niamatpur | 132/33kV Transformer 417T LT | 2023-03-21 09:16 | 2023-03-21 15:31 | 6:15 | E/O | Due to Oil Leakage.at 33 kV | 0 | 0 | No interruption
Joypurhat | 132/33 Transformer T-4 (437 T) HT | 2023-03-22 09:50 | 2023-03-22 13:14 | 3:24 | E/O | N/A | 0 | 0 | No interruption
Panchagarh | 132/33 Transformer T427T(A+B) LT | 2023-03-23 11:39 | 2023-03-24 12:07 | 24:28 | E/O | T3 33kV Under Ground Cable Fault For Y Phase. | 25 | 611.6667 | Power interruption
Purbasadipur | 132/33 TransformerT-1 (403T) HT | 2023-03-26 02:13 | 2023-03-26 03:40 | 1:27 | T | Due to 33 kv feeder falt | 25 | 36.25 | Power interruption
Purbasadipur | 132/33 Transformer T1(403T) LT | 2023-03-26 02:12 | 2023-03-26 13:06 | 10:54 | T | Due to 33 kv feeder falt | 25 | 272.5 | Power interruption
Purbasadipur | 132/33 kV Transformer T3 (423T) HT | 2023-03-26 02:13 | 2023-03-26 07:05 | 4:52 | T | Due to 33 kv feeder falt | 15 | 73 | Power interruption
Purbasadipur | 132/33TransformerT3 (423T) LT | 2023-03-26 02:13 | 2023-03-26 13:23 | 11:10 | T | Due to 33 kv feeder falt | 15 | 167.5 | Power interruption
Thakurgaon | 132/33Transformer422T LT | 2023-03-19 03:33 | 2023-03-19 03:52 | 0:19 | E/O | Due to Thunderstorm | 7 | 2.2167 | Power interruption
Thakurgaon | 132/33Transformer422T LT | 2023-03-19 03:56 | 2023-03-19 04:05 | 0:09 | T | Tripped while Boda 33 kV Feeder giving trial | 7 | 1.05 | Power interruption
Thakurgaon | 132/33Transformer 412T LT | 2023-03-19 03:33 | 2023-03-19 03:52 | 0:19 | E/O | Due to Thunderstorm | 7 | 2.2167 | Power interruption
Thakurgaon | 132/33Transformer 412T LT | 2023-03-19 03:56 | 2023-03-19 04:05 | 0:09 | T | Tripped while Boda 33 kV Feeder giving trial | 7 | 1.05 | Power interruption
Natore | 132/33TransformerTR-1 (405 T) LT | 2023-03-23 08:28 | 2023-03-23 08:43 | 0:15 | T | Singra feeder problem. | 0 | 0 | No interruption
Natore | 132/33TransformerTR-2 (415 T) LT | 2023-03-23 08:28 | 2023-03-23 08:43 | 0:15 | E/O | Singra CB problem. | 0 | 0 | No interruption
Niamatpur | 132/33Transformer 407T LT | 2023-03-16 14:36 | 2023-03-16 14:46 | 0:10 | T | 33 kV PBS Manda Feeder E/F. | 78 | 13 | Power interruption
Niamatpur | 132/33Transformer407T LT | 2023-03-19 07:50 | 2023-03-19 08:10 | 0:20 | E/O | Thundering. | 50 | 16.6667 | Power interruption
Niamatpur | 132/33Transformer417T LT | 2023-03-16 14:36 | 2023-03-16 14:46 | 0:10 | T | Tripped showing 33 Kv, PBS Manda Feeder E/F. | 78 | 13 | Power interruption
Niamatpur | 132/33Transformer 417T LT | 2023-03-19 07:50 | 2023-03-19 08:10 | 0:20 | E/O | Due to Thundaring | 50 | 16.6667 | Power interruption
Rajshahi | 132/33 Transformer T-3 (425T) LT | 2023-03-20 01:18 | 2023-03-20 19:30 | 18:12 | T | Due to 33 kv feeder falt | 33 | 600.6 | Power interruption
|  |  | Total : | 76:53 |  |  |  | 1827.3833
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 380:28 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month:March2023
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bhaluka | Mymensingh- Bhaluka 132 kV Ckt- 02 | 2023-03-19 07:36 | 2023-03-19 07:48 | 0:12 | T | NA | 76 | 15.2 | Power interruption
Kodda | Kodda Rajendrapur 132 kV Ckt-1 | 2023-03-25 18:05 | 2023-03-25 18:55 | 0:50 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Rajendrapur | Rajendrapur Kodda 132 kV Ckt-1 | 2023-03-25 18:05 | 2023-03-25 18:56 | 0:51 | T | Tripped showing Sudden trip Kodda-1 | 0 | 0 | No interruption
Tongi 230 | Tongi-Basundhara 132 kV Ckt-2 | 2023-03-26 08:59 | 2023-03-26 09:13 | 0:14 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Savar | Manikganj PS-Savar 132 kV Ckt-2 | 2023-03-31 00:58 | 2023-03-31 01:06 | 0:08 | T | None | 100 | 13.3333 | Power interruption
Savar | Kishoreganj Mymensingh Ckt-1 | 2023-03-19 07:37 | 2023-03-19 07:49 | 0:12 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Kishoreganj | Kishoreganj Mymensingh Ckt-2 | 2023-03-19 07:37 | 2023-03-19 07:49 | 0:12 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Tangail | Tangail RPCL-132 kV Ckt-1 | 2023-03-19 03:47 | 2023-03-19 03:58 | 0:11 | T | Tripped showing REL670 relay | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV Ckt-2 | 2023-03-02 07:50 | 2023-03-02 10:38 | 2:48 | E/O | Due to Red Hot maninteance Work | 0 | 0 | No interruption
|  |  | Total : | 2:50 |  | Unserved Energy: |  | 28.5333
Dhaka (South) Grid Circle :
Rampura | Rampura Bhulta 230 kV Ckt-01 | 2023-03-31 01:18 | 2023-03-31 02:16 | 0:58 | T | Storm | 0 | 0 | No interruption
Rampura | Rampura Basundhara 132 kV -01 | 2023-03-16 10:51 | 2023-03-16 11:02 | 0:11 | T | Unknow | 0 | 0 | No interruption
Rampura | Basundhara-Rampura 132 kV Ckt-01 | 2023-03-31 01:17 | 2023-03-31 01:56 | 0:39 | T | Storm | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj-132 kV Ckt-1 | 2023-03-31 01:42 | 2023-03-31 04:10 | 2:28 | T | Heavy Rain and strom | 7 | 17.2667 | Power interruption
Haripur | Haripur-Siddhirganj-132 kV Ckt-2 | 2023-03-31 01:42 | 2023-03-31 02:08 | 0:26 | T | Heavy rain and strom | 7 | 3.0333 | Power interruption
Madanganj | Madanganj -Haripur 132 kv Ckt-1 | 2023-03-31 01:42 | 2023-03-31 02:12 | 0:30 | T | Heavy Rain and strom | 0 | 0 | No interruption
Madanganj | Madanganj -Bashundhara 132 kv Ckt | 2023-03-31 01:42 | 2023-03-31 02:30 | 0:48 | T | Heavy rain and strom | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Haripur 132 kV Ckt-1 | 2023-03-30 06:38 | 2023-03-30 07:00 | 0:22 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Haripur 132 kV Ckt-1 | 2023-03-31 01:32 | 2023-03-31 04:11 | 2:39 | T | Cyclone & Lighting | 10 | 26.5 | Power interruption
Siddhirganj | Siddhirganj-Haripur 132 kV Ckt-2 | 2023-03-31 01:32 | 2023-03-31 02:08 | 0:36 | T | Cyclone & Lightning | 20 | 12 | Power interruption
Siddhirganj | Siddhirganj-Ullon 132 kV Ckt-1 | 2023-03-10 08:35 | 2023-03-10 10:44 | 2:09 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj -Ullon 132 kV Ckt-1 | 2023-03-31 01:32 | 2023-03-31 03:59 | 2:27 | T | Cyclone & Lightning | 22 | 53.9 | Power interruption
Siddhirganj | Siddhirganj-100MW Dutch Bangla 132 kV Ckt | 2023-03-30 06:38 | 2023-03-30 07:22 | 0:44 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-120MW EGCB GT2 Bay | 2023-03-30 06:38 | 2023-03-30 07:30 | 0:52 | T | Tripped showing Master trip relay optd. | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-120MW EGCB GT2 bay | 2023-03-31 01:32 | 2023-03-31 03:26 | 1:54 | T | Cyclone & Lightning | 0 | 0 | No interruption
Siddhirganj | Siddhirganj -120MW EGCB GT1 | 2023-03-19 18:59 | 2023-03-19 19:52 | 0:53 | T | Tripped showing Master trip relay | 36 | 31.8 | Power interruption
Siddhirganj | Siddhirganj-120MW EGCB GT1 | 2023-03-20 01:37 | 2023-03-20 10:15 | 8:38 | T | Tripped showing Master trip relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-120MW EGCB GT1 | 2023-03-30 06:38 | 2023-03-30 07:30 | 0:52 | T | Tripped showing Master trip relay optd. | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-120MW EGCB GT1 | 2023-03-31 01:32 | 2023-03-31 03:25 | 1:53 | T | Cyclone & Lightning | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-210MW PDB L3 | 2023-03-30 06:38 | 2023-03-30 07:20 | 0:42 | E/O | Control panel DC fail, CB SF6 blocking | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV Ckt-2 | 2023-03-19 18:59 | 2023-03-19 22:07 | 3:08 | T | Tripped showing Dist. relay | 170 | 532.6667 | Power interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV Ckt-2 | 2023-03-20 01:37 | 2023-03-20 11:26 | 9:49 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Sonargaon | Sonargaon-OPSL(IEL-2) 132 kV Ckt | 2023-03-31 01:39 | 2023-03-31 02:42 | 1:03 | T | Thundering | 0 | 0 | No interruption
Narshingdi | Narshingdi-Brahmanbaria 132 kV Ckt-1 | 2023-03-19 08:47 | 2023-03-19 08:58 | 0:11 | T | Stormy weather. | 0 | 0 | No interruption
|  |  | Total : | 44:52 |  | Unserved Energy: |  | 677.1667
Chattogram Grid Circle :
Bakulia | Bakalia-Sikalbaha 132 Ckt-01 | 2023-03-22 15:31 | 2023-03-22 16:17 | 0:46 | T | Raining & thundering | 0 | 0 | No interruption
Khulshi | Khulshi-Bakalia132 kV Circuit-1 | 2023-03-02 11:40 | 2023-03-02 12:14 | 0:34 | T | Unknown | 0 | 0 | No interruption
Rampur | Rampur-Halishahar230 kV Ckt-2 | 2023-03-15 00:40 | 2023-03-15 01:25 | 0:45 | T | tripped at 00:40 B ph fault, Zone 1 trip, 67N IDMT Trip | 0 | 0 | No interruption
Baroaulia | Baroaulia - Hat 132 kV Ckt-1 | 2023-03-29 13:25 | 2023-03-29 13:56 | 0:31 | T | Due to high storm | 50 | 25.8333 | Power interruption
Baroirhat | Baroirhat-Hat 132 kV Ckt-2 | 2023-03-05 11:14 | 2023-03-05 11:32 | 0:18 | T | Distance Trip phase Y & B at zone -1. | 0 | 0 | No interruption
Baroirhat | Baroirhat-Hat 132 kV Ckt-2 | 2023-03-20 08:41 | 2023-03-20 17:52 | 9:11 | E/O | Due to Red Hot maintenance. | 0 | 0 | No interruption
Hathazari | Hathazari-AKSML-230 kV Ckt-02 | 2023-03-31 03:36 | 2023-03-31 04:42 | 1:06 | T | G.Trip,Zone-01,R-phase | 0 | 0 | No interruption
Rangamati | Rangamati-Chandraghona 132 kV Ckt-01 | 2023-03-26 06:25 | 2023-03-26 07:00 | 0:35 | E/O | All 132kV breakers tripped with no signals | 12 | 7 | Power interruption
Rangamati | Rangamati-Chandraghona 132 kV Ckt-01 | 2023-03-21 10:10 | 2023-03-21 10:17 | 0:07 | T | Thundering | 0 | 0 | No interruption
Coxsbazar | Coxsbazar-Doh132 kV Ckt-1 | 2023-03-15 03:50 | 2023-03-15 04:04 | 0:14 | T | Tripped showing Dist. relay | 25 | 5.8333 | Power interruption
Coxsbazar | Coxsbazar-Doh132 kV Ckt-2 | 2023-03-17 05:10 | 2023-03-17 05:33 | 0:23 | T | Distance Relay Phase A Trip Phase ABC Zone 1 (64.9KM) | 0 | 0 | No interruption
Dohazari | Dohazari-Cox's Bazar 132 kV ckt-1 | 2023-03-16 08:53 | 2023-03-16 13:39 | 4:46 | E/O | Due to Emergency work | 30 | 143 | Power interruption
Dohazari | Dohazari-Cox's Bazar 132 kV ckt-2 | 2023-03-23 09:08 | 2023-03-23 15:08 | 6:00 | E/O | Due to Emergency work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox's Bazar 132 kV Ckt-1 | 2023-03-15 03:50 | 2023-03-15 04:03 | 0:13 | T | Matarbari interruption of 25 MW for this trip | 25 | 5.4167 | Power interruption
|  |  | Total : | 25:29 |  | Unserved Energy: |  | 187.0833
Cumilla Grid Circle :
Chandpur | Chandpur-115MW CPGL Power Plant Incomer (L5) | 2023-03-30 21:01 | 2023-03-30 23:44 | 2:43 | T | Unknown | 116 | 315.1333 | Power interruption
Chowmuhani | Chowmuhani-Feni 132 Ckt-01 | 2023-03-21 17:18 | 2023-03-21 17:50 | 0:32 | T | None | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Feni 132 Ckt-01 | 2023-03-31 03:33 | 2023-03-31 04:00 | 0:27 | T | Tripped showing O/C & E/F | 15 | 6.75 | Power interruption
Chowmuhani | Chowmuhani-Feni 132 Ckt-02 | 2023-03-21 17:18 | 2023-03-21 17:51 | 0:33 | T | None | 0 | 0 | No interruption
Cumilla(N) | 230KV Cumilla(N)-Ashuganj Ckt-1 | 2023-03-16 05:19 | 2023-03-16 09:13 | 3:54 | T | Very Fog. | 0 | 0 | No interruption
Cumilla(N) | 230KV Cumilla(N)-Ashuganj Ckt-2 | 2023-03-16 04:48 | 2023-03-16 05:00 | 0:12 | T | None | 0 | 0 | No interruption
Cumilla(N) | 230KV Cumilla(N)-Ashuganj Ckt-2 | 2023-03-16 06:21 | 2023-03-16 07:33 | 1:12 | T | Very very Fog. | 0 | 0 | No interruption
Cumilla(N) | 230KV Cumilla(N)-BSRM Ckt-2 | 2023-03-16 01:56 | 2023-03-16 02:26 | 0:30 | T | None | 0 | 0 | No interruption
Daudkandi | Daudkandi -Sonargaon 132 kV Ckt-2 | 2023-03-15 10:22 | 2023-03-15 10:48 | 0:26 | T | Earth Fault | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV Ckt-2 | 2023-03-31 03:35 | 2023-03-31 04:04 | 0:29 | T | none | 0 | 0 | No interruption
Brahmanbaria | Brahmanbaria-Shahjibazar Circuit-1 | 2023-03-23 14:05 | 2023-03-23 15:27 | 1:22 | T | Tripped showing O/C & E/F | 0 | 0 | No interruption
Brahmanbaria | Brahmanbaria-Shahjibazar Circuit-2 | 2023-03-23 14:05 | 2023-03-23 15:30 | 1:25 | T | Tripped showing O/C & E/F | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-B.Baria 132 Ckt-01 | 2023-03-23 14:05 | 2023-03-23 14:12 | 0:07 | T |  | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-B.Baria 132 Ckt-02 | 2023-03-23 14:05 | 2023-03-23 14:12 | 0:07 | T |  | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Ashuganj Ckt-03 | 2023-03-23 14:03 | 2023-03-23 14:10 | 0:07 | T | Due to Stormy wrather | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-BPDB 60 MW 132 kV Ckt | 2023-03-23 14:03 | 2023-03-23 14:41 | 0:38 | T |  | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-SPCL 86 MW 132 kV Ckt | 2023-03-04 05:46 | 2023-03-04 05:57 | 0:11 | T | Tripped showing 33 kV feeder fault | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-SPCL 86 MW 132 kV Ckt | 2023-03-17 05:36 | 2023-03-17 05:55 | 0:19 | T | Tripped showing Pbs and pdb 33 kv feeder trip | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-SPCL 86 MW 132 kV Ckt | 2023-03-18 09:13 | 2023-03-18 09:27 | 0:14 | T | Tripped showing E/ F, O/C | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-SPCL 86 MW 132 kV Ckt | 2023-03-23 14:03 | 2023-03-23 14:08 | 0:05 | T |  | 0 | 0 | No interruption
Sreemongol | Sreemangal-Fenchugonj circuit-1 | 2023-03-23 11:37 | 2023-03-23 11:46 | 0:09 | T | thunder and heavy raining | 0 | 0 | No interruption
Sunamganj | Chhatak-Sunamgonj CKT-1 | 2023-03-27 08:30 | 2023-03-27 08:53 | 0:23 | T | Fault Occurred Opponent Part | 9 | 3.45 | Power interruption
Sylhet | Sylhet-90MW P/S | 2023-03-17 06:36 | 2023-03-17 07:12 | 0:36 | T | Due to Lighting | 0 | 0 | No interruption
Sylhet | Sylhet-Chhatak Ckt-2 | 2023-03-15 04:45 | 2023-03-15 05:15 | 0:30 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  |  | 17:11 |  | Unserved Energy: |  | 325.3333
Page: 3/3 | [8 empty] | OF-LDC-24
Khulna Grid Circle :
Gopalganj | Gopalganj-Gopalganj North Ckt-2 | 2023-03-26 19:07 | 2023-03-27 13:57 | 18:50 | E/O | Due to Y phase IVT Blast | 0 | 0 | No interruption
Khulna © | Khulna(C) Central-Noapara 132 kV Ckt-1 | 2023-03-21 16:14 | 2023-03-22 11:01 | 18:47 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Noapara | Noapara-khulna central 132 kV Ckt- 1 | 2023-03-21 16:14 | 2023-03-22 11:03 | 18:49 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
|  |  |  | 56:26 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Ishurdi | Ishurdi-132 kV Baghabari Line | 2023-03-29 07:14 | 2023-03-29 07:58 | 0:44 | T | Tripped showing E/ F, | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV Ckt-1 | 2023-03-01 13:19 | 2023-03-01 15:34 | 2:15 | T | Tripped showing E/ F, | 0 | 0 | No interruption
Jhenaidah | Jhenaidah-Jhenaidah New-2,132kV Circuit-2(L3) | 2023-03-25 18:45 | 2023-03-26 00:17 | 5:32 | T | Due to Thundering | 0 | 0 | No interruption
Jhenaidah (N) | Jhenaidah (New)-Jhenaidah (Old) Ckt-2 | 2023-03-25 18:45 | 2023-03-26 00:16 | 5:31 | T | Due to Bad Weather | 0 | 0 | No interruption
|  |  |  | 8:31 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Sirajganj | Sirajganj-Shahjadpur 132 kV Ckt | 2023-03-25 06:40 | 2023-03-25 07:15 | 0:35 | T | Power Swing, Zone-02, Phase A | 0 | 0 | No interruption
|  |  |  | 0:35 |  | Unserved Energy: |  | 0
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 155:54 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/14 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: March 2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Manikganj | 132/33 kV Transformer GT-3 (50/75 MVA) HT | 2023-03-05 10:45 | 2023-03-05 13:24 | 2:39 | S/O | Due to Maintenance.work | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformer GT-3 (50/75 MVA) HT | 2023-03-23 13:01 | 2023-03-23 17:20 | 4:19 | S/O | Due to SPMD-2 work | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformer GT-3 (50/75 MVA) LT | 2023-03-05 10:45 | 2023-03-05 13:24 | 2:39 | S/O | Due to Maintenance.work | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformer GT-3 (50/75 MVA) LT | 2023-03-23 13:01 | 2023-03-23 17:22 | 4:21 | S/O | Due to U/F scheme work by SPMD-2 | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformer GT-4 (50/75 MVA) HT | 2023-03-05 07:31 | 2023-03-05 09:31 | 2:00 | S/O | Due to junction point temp high. | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformer GT-4 (50/75 MVA) HT | 2023-03-23 17:26 | 2023-03-23 18:04 | 0:38 | S/O | Due to SPMD-2 work | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformer GT-4 (50/75 MVA) LT | 2023-03-05 07:31 | 2023-03-05 09:31 | 2:00 | S/O | Due to junction point temp high. | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformer GT-4 (50/75 MVA) LT | 2023-03-23 17:25 | 2023-03-23 18:05 | 0:40 | S/O | Due to SPMD-2 work | 0 | 0 | No interruption
Kodda | 132/33 kV TransformerTr-3 (426T) LT | 2023-03-02 13:01 | 2023-03-02 14:24 | 1:23 | S/O | Due to line DS work | 0 | 0 | No interruption
Kodda | 132/33 kV TransformerTr-5 (446T) HT | 2023-03-21 08:31 | 2023-03-21 17:50 | 9:19 | S/O | Due to PBS work | 100 | 931.6667 | Power interruption
Kodda | 132/33 kV TransformerTr-5 (446T) LT | 2023-03-21 08:31 | 2023-03-21 17:52 | 9:21 | S/O | Due to PBS work | 100 | 935 | Power interruption
New Tongi | 132/33 kV TransformerT1(403T) LT | 2023-03-18 10:30 | 2023-03-18 11:05 | 0:35 | S/O | Due to installation work | 0 | 0 | No interruption
New Tongi | 132/33 kV TransformerT2(413T) LT | 2023-03-18 11:07 | 2023-03-18 11:40 | 0:33 | S/O | Due to installation work | 0 | 0 | No interruption
Aminbazar 400/230/132 | 132 kv Bus 01 | 2023-03-21 12:24 | 2023-03-21 15:32 | 3:08 | S/O | Due to Development work | 0 | 0 | No interruption
Aminbazar | 230/132kv TransformerTr-01 HT | 2023-03-01 10:26 | 2023-03-01 17:40 | 7:14 | S/O | Due to Disk Insulator Cleaning work | 0 | 0 | No interruption
Aminbazar | 230/132kv Transformer Tr-01 LT | 2023-03-01 10:24 | 2023-03-01 17:42 | 7:18 | S/O | Due to Disk Insulator Cleaning work | 0 | 0 | No interruption
Aminbazar | 230/132kv TransformerTr-02 HT | 2023-03-02 08:59 | 2023-03-02 17:35 | 8:36 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Aminbazar | 230/132kv TransformerTr-02 LT | 2023-03-02 08:58 | 2023-03-02 17:36 | 8:38 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Aminbazar 400/230/132 | Bus-1 | 2023-03-31 13:20 | 2023-03-31 14:09 | 0:49 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Aminbazar 400/230/132 | Bus-2 | 2023-03-03 08:46 | 2023-03-03 11:42 | 2:56 | S/O | Due to 400/132 KV TR installation work | 0 | 0 | No interruption
Kallyanpur | 132 Main bus | 2023-03-04 07:36 | 2023-03-04 18:14 | 10:38 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Mirpur | 132 Main Bus | 2023-03-06 09:20 | 2023-03-06 15:37 | 6:17 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Savar | 132 kV Bus-A | 2023-03-18 10:50 | 2023-03-21 14:49 | 75:59 | S/O | Due to project work | 0 | 0 | No interruption
Savar | 132 kV Bus-B | 2023-03-04 09:59 | 2023-03-12 13:45 | 195:46 | S/O | Due to changing work | 0 | 0 | No interruption
Savar | 132/33 kV Auxiliary Transformer-2 HT | 2023-03-04 10:15 | 2023-03-12 13:56 | 195:41 | S/O | Due to maintenance work | 0 | 0 | No interruption
Savar | 132/ 33 kV Auxiliary Transformer-2 LT | 2023-03-04 09:30 | 2023-03-12 13:56 | 196:26 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kaliakoir | 400kV Bus 2 | 2023-03-23 18:05 | 2023-03-23 22:30 | 4:25 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kaliakoir | 400kV Bus 2 | 2023-03-26 23:21 | 2023-03-27 11:49 | 12:28 | S/O | Due to maintenance work | 0 | 0 | No interruption
Jamalpur | 132/33 kV TransformerT-1 LT | 2023-03-22 16:50 | 2023-03-22 16:55 | 0:05 | S/O | Due to parallel operation. | 20 | 1.6667 | Power interruption
Mymensingh | 132/33 kV Transformer-1 (404T) HT | 2023-03-29 08:20 | 2023-03-29 15:37 | 7:17 | S/O | ue to R phase high temperature | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-3 (424T) HT | 2023-03-09 07:15 | 2023-03-09 08:42 | 1:27 | S/O | Due to high temperature of T3 | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-3 (424T) LT | 2023-03-09 07:15 | 2023-03-09 08:42 | 1:27 | S/O | Due to high temperature | 30 | 43.5 | Power interruption
Sherpur | 132/33 kV Transformer- 03 HT | 2023-03-15 10:21 | 2023-03-15 12:27 | 2:06 | S/O | Due to Well temperature metre change | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer- 03 LT | 2023-03-15 10:21 | 2023-03-15 12:27 | 2:06 | S/O | Due to Oil temperature metre change | 0 | 0 | No interruption
Tangail | 132/33 kV TransformerTr-4 LT | 2023-03-02 06:50 | 2023-03-02 08:14 | 1:24 | S/O | Due to maintenance work | 10 | 14 | Power interruption
|  |  | Total : | 792:38 |  | Unserved Energy: |  | 1925.8333
Dhaka (South) Grid Circle :
Maniknagar | 132/33 kV Transformer GT-1 HT | 2023-03-29 14:09 | 2023-03-29 17:57 | 3:48 | S/O | Due to 33kv CB maintenance work, | 0 | 0 | No interruption
Haripur | 230/132 kV Transformer Auto TR-1 HT | 2023-03-05 07:43 | 2023-03-06 01:14 | 17:31 | S/O | Due to Bus conductor change | 0 | 0 | No interruption
Haripur | 230/132 kV Transformer Auto TR-1 LT | 2023-03-05 07:43 | 2023-03-06 01:14 | 17:31 | S/O | Due to Bus conductor change | 0 | 0 | No interruption
Haripur | 132kV Reserve Bus Sec-1 | 2023-03-05 07:54 | 2023-03-06 01:12 | 17:18 | S/O | Due to Bus conductor change | 0 | 0 | No interruption
Sonargaon | 132/33 kV TransformerTr-2 HT | 2023-03-15 15:24 | 2023-03-15 17:27 | 2:03 | S/O | Due to fuse maintenance work. | 20 | 41 | Power interruption
Sonargaon | 132/33 kV Transformer Tr-2 LT | 2023-03-15 15:23 | 2023-03-15 17:28 | 2:05 | S/O | Due to Auxiliary-02 R-ph fuse maintenance work. | 20 | 41.6667 | Power interruption
Keranigonj | 230/132 kV TransformerTR-1 HT | 2023-03-03 08:21 | 2023-03-03 11:38 | 3:17 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Keranigonj | 230/132 kV TransformerTR-1 HT | 2023-03-07 08:07 | 2023-03-07 13:10 | 5:03 | S/O | Due to Cooling fan repair and installation. | 0 | 0 | No interruption
Keranigonj | 230/132 kV TransformerTR-1 LT | 2023-03-03 08:22 | 2023-03-03 11:42 | 3:20 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Keranigonj | 230/132 kV TransformerTR-1 LT | 2023-03-07 08:07 | 2023-03-07 13:11 | 5:04 | S/O | Due to Cooling fan repair and installation. | 0 | 0 | No interruption
Keranigonj | 230/132 kV TransformerTR-2 LT | 2023-03-18 09:31 | 2023-03-18 16:57 | 7:26 | S/O | Due to PBS work | 0 | 0 | No interruption
Bhulta | 400/230 kV TransformerATR-01 HT | 2023-03-18 07:55 | 2023-03-18 16:11 | 8:16 | S/O | Due to Annual Maintenance Work. | 0 | 0 | No interruption
Bhulta | 400/230 kV TransformerATR-01 LT | 2023-03-18 07:55 | 2023-03-18 16:12 | 8:17 | S/O | Due to Annual Maintenance Work. | 0 | 0 | No interruption
Bhulta | 400/230 kV Transformer Aux Trafo-01 HT | 2023-03-18 07:48 | 2023-03-18 16:12 | 8:24 | S/O | Due to Annual Maintenance Work. | 0 | 0 | No interruption
Bhulta | 400/230 kV Transformer Aux Trafo-01 LT | 2023-03-18 07:47 | 2023-03-18 16:14 | 8:27 | S/O | Due to Annual Maintenance Work. | 0 | #REF! | No interruption
Narshingdi | 132/33 kV TransformerT-1 HT | 2023-03-18 15:02 | 2023-03-18 16:43 | 1:41 | S/O | Due to relay Maintenance | 0 | #REF! | No interruption
Narshingdi | 132/33 kV TransformerT-2 HT | 2023-03-19 12:22 | 2023-03-19 13:47 | 1:25 | S/O | Due to relay Maintenance | 0 | #REF! | No interruption
Narshingdi | 132/33 kV Transformer T-2 LT | 2023-03-19 12:21 | 2023-03-19 13:54 | 1:33 | S/O | Due to Maintenance work | 0 | #REF! | No interruption
|  |  | Total : | 122:29 |  | Unserved Energy: |  | #REF!
Chattogram Grid Circle :
Khulshi | 132/33 kV Transformer 425T(BSRM) HT | 2023-03-18 11:01 | 2023-03-18 12:01 | 1:00 | S/O | Due to Mainntenance Work | 0 | 0 | No interruption
Khulshi | 132/33 kV Transformer 425T(BSRM) HT | 2023-03-18 14:33 | 2023-03-18 15:15 | 0:42 | S/O | Due to Clean the tr. | 0 | 0 | No interruption
Khulshi | 132/33 kV Transformer 425T(BSRM) LT | 2023-03-18 14:33 | 2023-03-18 15:18 | 0:45 | S/O | Due to Clean the tr. | 0 | 0 | No interruption
Hathazari | 230/132 kV TransformerMT-02 HT | 2023-03-02 09:17 | 2023-03-02 17:29 | 8:12 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Hathazari | 230/132 kV TransformerMT-02 LT | 2023-03-02 09:17 | 2023-03-02 17:29 | 8:12 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Hathazari | 230/132 kV TransformerMT-03 HT | 2023-03-04 10:28 | 2023-03-04 17:54 | 7:26 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Hathazari | 230/132 kV TransformerMT-03 LT | 2023-03-04 10:28 | 2023-03-04 17:55 | 7:27 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Chandraghona | 132/33 kV TransformerTR-02(416T) HT | 2023-03-15 10:36 | 2023-03-15 13:38 | 3:02 | S/O | Due to Mainntenance Work | 0 | 0 | No interruption
Kalurghat | 132/33 kV Transformer TRFO-02(516T) HT | 2023-03-14 15:21 | 2023-03-14 17:26 | 2:05 | S/O | Due to Relay maintenance | 0 | 0 | No interruption
Madunaghat | T1 33kV BUS | 2023-03-28 11:37 | 2023-03-28 12:27 | 0:50 | S/O | Due to Maintenance By BPDB | 0 | 0 | No interruption
Madunaghat | 132/33 kV TransformerTR-2(517T) HT | 2023-03-28 11:37 | 2023-03-28 12:27 | 0:50 | S/O | Due to Maintenance By BPDB | 0 | 0 | No interruption
Madunaghat | 132/33 kV TransformerTR-2(517T) LT | 2023-03-28 11:35 | 2023-03-28 12:27 | 0:52 | S/O | Due to Maintenance By BPDB | 0 | 0 | No interruption
Madunaghat | T-2 33kV BUS | 2023-03-28 11:37 | 2023-03-28 12:27 | 0:50 | S/O | Due to Maintenance By BPDB | 0 | 0 | No interruption
TK chemical | 48/64MVA transformer T-2(415T) HT | 2023-03-13 11:15 | 2023-03-13 13:29 | 2:14 | S/O | Due to cable maint.work | 0 | 0 | No interruption
|  |  | Total : | 44:27 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Chandpur | 132/33 kV Transformer 402T HT | 2023-03-03 14:20 | 2023-03-03 16:37 | 2:17 | S/O | Due to Maintenance work | 16 | 36.5333 | Power interruption
Chandpur | 132/33 kV Transformer 402T LT | 2023-03-03 14:20 | 2023-03-03 16:38 | 2:18 | S/O | Due to Maintenance work | 16 | 36.8 | Power interruption
Chandpur | 132/33 kV Transformer412T HT | 2023-03-03 14:20 | 2023-03-03 16:37 | 2:17 | S/O | Due to Maintenance work | 16 | 36.5333 | Power interruption
Chandpur | 132/33 kV Transformer 422T HT | 2023-03-19 20:26 | 2023-03-19 22:30 | 2:04 | S/O | Due to Maintenance work bu 33 kV Bus | 5 | 10.3333 | Power interruption
Chandpur | 132/33 kV Transformer422T LT | 2023-03-19 20:26 | 2023-03-19 22:32 | 2:06 | S/O | Due to 33 KV Bus Maintenance | 5 | 10.5 | Power interruption
Chowmuhani | 132/33 kV TransformerTR1-415T HT | 2023-03-11 07:07 | 2023-03-11 15:11 | 8:04 | S/O | Due to 33 kv bus conductor change work. | 32 | 258.1333 | Power interruption
Chowmuhani | 132/33 kV TransformerTR1-415T HT | 2023-03-18 12:15 | 2023-03-18 17:15 | 5:00 | S/O | Due to 33 KV Bus conductor change. | 18 | 90 | Power interruption
Chowmuhani | 132/33 kV TransformerTR1-415T LT | 2023-03-11 07:07 | 2023-03-11 15:11 | 8:04 | S/O | Due to 33 kv bus conductor change work. | 32 | 258.1333 | Power interruption
Chowmuhani | 132/33 kV TransformerTR1-415T LT | 2023-03-18 12:15 | 2023-03-18 17:15 | 5:00 | S/O | Due to 33 kv bus conductor change work. | 18 | 90 | Power interruption
Chowmuhani | 132/33 kV TransformerTR2-425T HT | 2023-03-11 07:07 | 2023-03-11 15:11 | 8:04 | S/O | Due to 33 kv bus conductor change work. | 18 | 145.2 | Power interruption
Chowmuhani | 132/33 kV TransformerTR2-425T HT | 2023-03-14 07:15 | 2023-03-14 13:05 | 5:50 | S/O | Due to 33 kv bus conductor change work. | 20 | 116.6667 | Power interruption
Chowmuhani | 132/33 kV TransformerTR2-425T HT | 2023-03-18 07:16 | 2023-03-18 18:12 | 10:56 | S/O | Due to 33 kv bus conductor change work. | 30 | 328 | Power interruption
Chowmuhani | 132/33 kV TransformerTR2-425T LT | 2023-03-11 07:07 | 2023-03-11 15:11 | 8:04 | S/O | Due to 33 kv bus conductor change work. | 18 | 145.2 | Power interruption
Chowmuhani | 132/33 kV TransformerTR2-425T LT | 2023-03-14 07:15 | 2023-03-14 13:05 | 5:50 | S/O | Due to 33 kv bus conductor change work. | 20 | 116.6667 | Power interruption
Chowmuhani | 132/33 kV TransformerTR2-425T LT | 2023-03-18 07:15 | 2023-03-18 18:12 | 10:57 | S/O | Due to 33 kv bus conductor change work. | 30 | 328.5 | Power interruption
Chowmuhani | 132/33 kV TransformerTR3-435T HT | 2023-03-14 07:17 | 2023-03-14 16:30 | 9:13 | S/O | Due to 33 kv bus conductor change work. | 25 | 230.4167 | Power interruption
Chowmuhani | 132/33 kV TransformerTR3-435T HT | 2023-03-18 07:17 | 2023-03-18 12:15 | 4:58 | S/O | Due to 33 kv bus conductor change work. | 20 | 99.3333 | Power interruption
Chowmuhani | 132/33 kV TransformerTR3-435T LT | 2023-03-14 07:17 | 2023-03-14 16:30 | 9:13 | S/O | Due to 33 kv bus conductor change work. | 25 | 230.4167 | Power interruption
Chowmuhani | 132/33 kV TransformerTR3-435T LT | 2023-03-18 07:15 | 2023-03-18 12:16 | 5:01 | S/O | Due to 33 kv bus conductor change work. | 20 | 100.3333 | Power interruption
Cumilla(S) | 132/33 kV TransformerTR-3 LT | 2023-03-11 08:49 | 2023-03-11 12:51 | 4:02 | S/O | Due 33 Isolator Change . Work done By REB. | 4 | 16.1333 | Power interruption
Cumilla(S) | 132/33 kV TransformerTR-4 LT | 2023-03-04 09:24 | 2023-03-04 16:52 | 7:28 | S/O | Due to PBS-2 work | 0 | 0 | No interruption
Feni | 132/33 kV TransformerT-1(405T) HT | 2023-03-30 06:14 | 2023-03-30 08:26 | 2:12 | S/O | Due to 33 kV bus ds maintenance work | 20 | 44 | Power interruption
Fenchuganj | 230/132 kV TransformerAT-02 HT | 2023-03-20 09:24 | 2023-03-20 15:01 | 5:37 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Fenchuganj | 230/132 kV TransformerAT-02 LT | 2023-03-20 09:24 | 2023-03-20 15:02 | 5:38 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Sylhet | 132/33 kV TransformerT1 HT | 2023-03-22 08:20 | 2023-03-22 10:05 | 1:45 | S/O | Due to Bus section Maintenance | 7 | 12.25 | Power interruption
Sylhet | 132/33 kV TransformerT2 HT | 2023-03-11 07:30 | 2023-03-11 12:37 | 5:07 | S/O | Due to Ten delta test | 0 | 0 | No interruption
Sylhet | 132/33 kV TransformerT2 LT | 2023-03-11 07:30 | 2023-03-11 12:38 | 5:08 | S/O | Due to Ten delta test | 0 | 0 | No interruption
Sylhet | 132/33 kV TransformerT4 HT | 2023-03-11 08:35 | 2023-03-11 12:48 | 4:13 | S/O | Due to PDB work | 9 | 37.95 | Power interruption
Sylhet | 132/33 kV TransformerT4 LT | 2023-03-11 08:34 | 2023-03-11 12:49 | 4:15 | S/O | Due to PDB work | 9 | 38.25 | Power interruption
|  |  | Total : | 160:41 |  | Unserved Energy: |  | 2816.2833
Khulna Grid Circle :
Barishal | 132/33 kV TransformerT-1 (405T) HT | 2023-03-13 09:07 | 2023-03-13 16:31 | 7:24 | S/O | For transportation of old 50/75MVA transformer to Patuakhali Grid | 0 | 0 | No interruption
Barishal | 132/33 kV TransformerT-1 (405T) LT | 2023-03-13 09:06 | 2023-03-13 16:32 | 7:26 | S/O | For transportation of old 50/75MVA transformer to Patuakhali Grid | 0 | 0 | No interruption
Barishal | 132/33 kV TransformerT-1 (405T) LT | 2023-03-14 08:34 | 2023-03-14 18:03 | 9:29 | S/O | For transportation of old 50/75MVA transformer to Patuakhali Grid | 0 | 0 | No interruption
Barishal | 132/33 kV TransformerT-2 (415T) HT | 2023-03-11 11:49 | 2023-03-11 12:27 | 0:38 | S/O | Dueto Oil sample collections from OLTC for test. | 0 | 0 | No interruption
Barishal | 132/33 kV TransformerT-2 (415T) HT | 2023-03-14 08:35 | 2023-03-30 09:17 | 384:42 | S/O | For transportation of old 50/75MVA transformer to Patuakhali Grid | 0 | 0 | No interruption
Barishal | 132/33 kV TransformerT-2 (415T) HT | 2023-03-30 12:03 | 2023-03-30 13:30 | 1:27 | S/O | Due to High temperature remove at HT side | 0 | 0 | No interruption
Barishal | 132/33 kV TransformerT-2 (415T) LT | 2023-03-11 10:48 | 2023-03-11 12:28 | 1:40 | S/O | Due to Oil sample collections from OLTC for test. | 0 | 0 | No interruption
Barishal | 132/33 kV TransformerT-2 (415T) LT | 2023-03-30 12:02 | 2023-03-30 13:31 | 1:29 | S/O | Due to high temperature at HT side bushing | 0 | 0 | No interruption
Barishal | 230kV BUS | 2023-03-22 11:38 | 2023-03-22 16:01 | 4:23 | S/O | Due to Project Work | 0 | 0 | No interruption
Barishal | 230/132kV Transformer T-4 HT | 2023-03-19 17:08 | 2023-03-19 19:03 | 1:55 | S/O | S/D taken by Barishal pbs-2 | 0 | 0 | No interruption
Barishal | 230/132kV TransformerT-4 LT | 2023-03-19 17:06 | 2023-03-19 19:05 | 1:59 | S/O | Due to PBS work | 0 | 0 | No interruption
Bhandaria | 132/33kV Transformer-1 HT | 2023-03-01 07:27 | 2023-03-01 16:40 | 9:13 | S/O | Due to G2G project work. | 0 | 0 | No interruption
Bhandaria | 132/33kV Transformer-1 HT | 2023-03-02 05:57 | 2023-03-02 17:05 | 11:08 | S/O | Due to Project work | 0 | 0 | No interruption
Bhandaria | 132/33kV Transformer-1 HT | 2023-03-03 07:37 | 2023-03-03 18:15 | 10:38 | S/O | Due to G2G project work | 0 | 0 | No interruption
Bhandaria | 132/33kV Transformer-1 HT | 2023-03-05 07:30 | 2023-03-05 16:16 | 8:46 | S/O | Due to G2G project work | 0 | 0 | No interruption
Bhandaria | 132/33kV Transformer-1 HT | 2023-03-06 07:37 | 2023-03-06 17:45 | 10:08 | S/O | Due to G2G project work. | 0 | 0 | No interruption
Bhandariab-Station | 132/33kV Transformer-1 LT | 2023-03-01 07:26 | 2023-03-01 16:42 | 9:16 | S/O | Due to G2G project work. | 0 | 0 | No interruption
Bhandaria | 132/33kVTransformer-1 LT | 2023-03-02 05:56 | 2023-03-02 17:06 | 11:10 | S/O | Due to Project work | 0 | 0 | No interruption
Bhandaria | 132/33kVTransformer-1 LT | 2023-03-03 07:37 | 2023-03-04 17:09 | 33:32 | S/O | Due to G2G Project work | 0 | 0 | No interruption
Bhandaria | 132/33kVTransformer-1 LT | 2023-03-05 07:22 | 2023-03-05 16:17 | 8:55 | S/O | Due to Project work | 0 | 0 | No interruption
Bhandaria | 132/33kVTransformer-1 LT | 2023-03-06 07:36 | 2023-03-06 16:56 | 9:20 | S/O | Due to G2G Project work. | 0 | 0 | No interruption
Bhandaria | 132/33kVTransformer-2 HT | 2023-03-04 07:28 | 2023-03-04 17:08 | 9:40 | S/O | Due to G2G project work | 0 | 0 | No interruption
Bhandaria | 132/33kV Transformer-2 HT | 2023-03-06 06:40 | 2023-03-06 07:17 | 0:37 | S/O | Due to WZPDCL WORKS. | 13 | 8.0167 | Power interruption
Bhandaria | 132/33kVTransformer-2 HT | 2023-03-07 07:47 | 2023-03-07 13:15 | 5:28 | S/O | Due to G2G Project Work | 0 | 0 | No interruption
Bhandaria on | 132/33kVTransformer-2 HT | 2023-03-08 07:44 | 2023-03-08 17:19 | 9:35 | S/O | Due to G2G project work | 0 | 0 | No interruption
Bhandariaon | 132/33kV Transformer-2 HT | 2023-03-09 08:06 | 2023-03-09 17:12 | 9:06 | S/O | Due to G2G project work | 0 | 0 | No interruption
Bhandaria on | 132/33kV Transformer-2 HT | 2023-03-10 07:39 | 2023-03-10 16:40 | 9:01 | S/O | Due to G2G project work. | 0 | 0 | No interruption
Bhandaria | 132/33kV Transformer-2 LT | 2023-03-06 06:39 | 2023-03-06 07:18 | 0:39 | S/O | Due to WZPDCL WORKS. | 13 | 8.45 | Power interruption
Bhandarian | 132/33kV Transformer-2 LT | 2023-03-07 07:46 | 2023-03-07 13:16 | 5:30 | S/O | Due to G2G Project work. | 0 | 0 | No interruption
Bhandarian | 132/33kV Transformer-2 LT | 2023-03-08 07:43 | 2023-03-08 17:20 | 9:37 | S/O | Due to G2G Project work. | 0 | 0 | No interruption
Bhandaria | 132/33kVTransformer-2 LT | 2023-03-09 08:05 | 2023-03-09 17:13 | 9:08 | S/O | Due to G2G Project work. | 0 | 0 | No interruption
BhandariaStation | 132/33kVTransformer-2 LT | 2023-03-10 07:38 | 2023-03-10 16:40 | 9:02 | S/O | Due to G2G Project work. | 0 | 0 | No interruption
Faridpur | 132/33kV Transformer-2 HT | 2023-03-06 07:15 | 2023-03-06 10:18 | 3:03 | S/O | 33 kv CT oil leakage. | 0 | 0 | No interruption
Gopalganj n | 400/132 kV Transformer ATR-03 HT | 2023-03-18 11:49 | 2023-03-18 14:24 | 2:35 | S/O | Due to Project work. | 0 | 0 | No interruption
Gopalganj | 400/132 kV Transformer ATR-03 LT | 2023-03-18 11:48 | 2023-03-18 14:25 | 2:37 | S/O | Due to Project work. | 0 | 0 | No interruption
Madaripurtion | 132/33kV Transformer T2-415T HT | 2023-03-18 07:00 | 2023-03-18 11:21 | 4:21 | S/O | Due to maint.work | 0 | 0 | No interruption
Khulna © | 132/33kV Transformer TR-1 425T HT | 2023-03-14 10:08 | 2023-03-14 10:29 | 0:21 | S/O | Due to Relay Testing ( SPMD Khulna ) | 5 | 1.75 | Power interruption
Khulna (C) n | 132/33kV Transformer TR-1 425T LT | 2023-03-14 10:08 | 2023-03-14 10:29 | 0:21 | S/O | Due to Relay testing ( SPMD Khulna ) | 5 | 1.75 | Power interruption
Khulna (C) | 132/33kV Transformer Tr-2 415 T HT | 2023-03-14 10:34 | 2023-03-14 17:55 | 7:21 | S/O | Due to 33 KV Bus section-2 PT Change | 8 | 58.8 | Power interruption
Khulna © | 132/33kV Transformer Tr-2 415 T LT | 2023-03-14 10:34 | 2023-03-14 17:56 | 7:22 | S/O | Due to 33KV Bus section-2 PT Change | 8 | 58.9333 | Power interruption
Narail | 132/33kV Transformer TR2 (413-T) HT | 2023-03-06 12:36 | 2023-03-06 14:35 | 1:59 | S/O | Due to TR-02, 132 kv breaker contact resistance test. | 0 | 0 | No interruption
Narail | 132/33kV Transformer TR2 (413-T) LT | 2023-03-06 12:36 | 2023-03-06 14:35 | 1:59 | S/O | Due to TR-02, 132 kv breaker contact resistance test. | 0 | 0 | No interruption
Noapara | 132/33kV Transformer T-2 HT | 2023-03-06 07:24 | 2023-03-06 08:56 | 1:32 | S/O | Due to mmMaintenance work | 11 | 16.8667 | Power interruption
Noapara | 132/33kV Transformer T-2 LT | 2023-03-06 07:24 | 2023-03-06 08:58 | 1:34 | S/O | Due to Maintenance of High Temperature point 33 KV Side. | 11 | 17.2333 | Power interruption
Bagerhat | 132/33kV Transformer-3 ( 423 T) HT | 2023-03-31 05:45 | 2023-03-31 06:56 | 1:11 | S/O | Due to TR-03 S/D FOR HOT SPOT MAINTENANCE WORK. | 0 | 0 | No interruption
Bagerhat | 132/33kV Transformer-3 ( 423 T) LT | 2023-03-31 05:44 | 2023-03-31 06:57 | 1:13 | S/O | Due toTR-03 S/D FOR HOT SPOT MAINTENANCE WORK. | 0 | 0 | No interruption
Gollamari ion | 132/33kV Transformer Tr-1 HT | 2023-03-06 09:08 | 2023-03-20 14:14 | 341:06 | S/O | Due to Project Work | 0 | 0 | No interruption
Gollamari | 132/33kV Transformer Tr-1 LT | 2023-03-06 09:07 | 2023-03-20 15:37 | 342:30 | S/O | Due to Project Work | 0 | 0 | No interruption
Gollamari ion | 132/33kV Transformer Tr-1 LT | 2023-03-30 06:17 | 2023-03-30 09:10 | 2:53 | S/O | Due to 33Kv Bus DS maintainenc | 0 | 0 | No interruption
Gollamari tation | 132/33kV TransformerTr-2 HT | 2023-03-11 07:18 | 2023-03-11 17:34 | 10:16 | S/O | Due to 33 kv Bus DS Change. | 15 | 154 | Power interruption
GollamariStation | 132/33kV TransformerTr-2 LT | 2023-03-11 07:16 | 2023-03-11 17:36 | 10:20 | S/O | Due to G2G project work | 15 | 155 | Power interruption
Gollamari | 33 kV Bus | 2023-03-12 10:50 | 2023-03-12 15:10 | 4:20 | S/O | Due to G2G project work. | 3 | 13 | Power interruption
Satkhira ion | 132/33kV Transformer-2 (T-2) HT | 2023-03-15 06:28 | 2023-03-15 09:30 | 3:02 | S/O | Due to Underground cablemaint.work | 0 | 0 | No interruption
Satkhiraation | 132/33kV Transformer-2 (T-2) HT | 2023-03-28 18:59 | 2023-03-28 19:53 | 0:54 | S/O | Due to Underground cablemaint.work | 0 | 0 | No interruption
Satkhira | 132/33kV Transformer-2 (T-2) LT | 2023-03-15 06:28 | 2023-03-15 09:30 | 3:02 | S/O | Due to Underground cable termination kit 33kv side | 0 | 0 | No interruption
Satkhira | 132/33kV Transformer-2 (T-2) LT | 2023-03-28 18:58 | 2023-03-28 19:55 | 0:57 | S/O | Due to 33 KV Underground cable fault. | 0 | 0 | No interruption
|  |  | Total : | 1377:53 |  | Unserved Energy : |  | 493.8
HVDC Grid Circle
Pabna | 132/33kV TransformerT-1 LT | 2023-03-04 09:17 | 2023-03-04 11:45 | 2:28 | S/O | None | 5 | 12.3333 | Power interruption
Bheramara(GK) | 132/33kV TransformerTR-2 HT | 2023-03-11 09:18 | 2023-03-11 11:20 | 2:02 | S/O | Due to PBS maintenance.work | 5 | 10.1667 | Power interruption
Bheramara(GK) | 132/33kV TransformerTR-2 LT | 2023-03-11 09:17 | 2023-03-11 11:21 | 2:04 | S/O | Due to PBS maintenance.work | 5 | 10.3333 | Power interruption
Kushtia | 132/33kV TransformerT2 HT | 2023-03-18 07:05 | 2023-03-18 08:39 | 1:34 | S/O | Due to Maintenance work | 10 | 15.6667 | Power interruption
Kushtia | 132/33kV TransformerT2 LT | 2023-03-18 07:04 | 2023-03-18 08:41 | 1:37 | S/O | Due to Maintenance work | 10 | 16.1667 | Power interruption
|  |  | Total : | 9:45 |  | Unserved Energy : |  | 64.6667
Bogura Grid Circle:
Bogura | 132/33kV Transformer-2 HT | 2023-03-24 10:17 | 2023-03-24 11:02 | 0:45 | S/O | Due To change MC of 132 KV CB | 0 | 0 | No interruption
Bogura | 230KV Main bus- 1 | 2023-03-04 08:45 | 2023-03-04 16:13 | 7:28 | S/O | Due to PGCB work | 0 | 0 | No interruption
Joypurhat | 132/33kV Transformer T-3 (427 T) HT | 2023-03-10 07:54 | 2023-03-10 09:26 | 1:32 | S/O | Due to 33 KV Busbar Extension Work. | 10 | 15.3333 | Power interruption
Joypurhat | 132/33kV Transformer-3 (427 T) LT | 2023-03-10 07:51 | 2023-03-10 09:29 | 1:38 | S/O | Due to 33 KV Busbar Extension Work. | 10 | 16.3333 | Power interruption
Joypurhat | 132/33kV Transformer T-4 (437 T) HT | 2023-03-10 07:55 | 2023-03-10 09:28 | 1:33 | S/O | Due to 33 KV Busbar Extension Work. | 10 | 15.5 | Power interruption
Joypurhat | 132/33kV Transformer T-4 (437 T) LT | 2023-03-10 07:52 | 2023-03-10 09:30 | 1:38 | S/O | Due to 33 KV Busbar Extension Work. | 10 | 16.3333 | Power interruption
Mahasthangarh | 33KV Main bus T-1 | 2023-03-21 07:19 | 2023-03-21 10:51 | 3:32 | S/O | Due to 33 kv BUS & Feeder Maintenance work | 14 | 49.4667 | Power interruption
Mahasthangarh | 33KV Main bus T-2 | 2023-03-21 07:19 | 2023-03-21 10:50 | 3:31 | S/O | Due to 33 kv BUS & Feeder Maintenance work | 20 | 70.3333 | Power interruption
Sirajganj | 132/33kV TransformerT1-(415) HT | 2023-03-11 16:22 | 2023-03-11 16:39 | 0:17 | S/O | Due to T-01 xformer down oill tank transfer. | 0 | 0 | No interruption
Sirajganj | 132/33kV TransformerT1-(415) LT | 2023-03-11 16:22 | 2023-03-11 16:38 | 0:16 | S/O | Due to T-01 xformer down oill tank transfer. | 0 | 0 | No interruption
Purbasadipur | 132/33kV TransformerT-4 HT | 2023-03-12 06:15 | 2023-03-12 15:50 | 9:35 | S/O | None | 0 | 0 | No interruption
Purbasadipur | 132/33kV TransformerT-4 HT | 2023-03-15 08:15 | 2023-03-17 15:15 | 55:00 | S/O | Due to replacemnet work | 0 | 0 | No interruption
Purbasadipur | 132/33kV TransformerT-4 HT | 2023-03-17 16:05 | 2023-03-17 16:45 | 0:40 | S/O | as per manufacture instruction and observation of new transformer. | 0 | 0 | No interruption
Purbasadipur | 132/33kV TransformerT-4 LT | 2023-03-12 06:13 | 2023-03-12 15:55 | 9:42 | S/O | None | 0 | 0 | No interruption
Niamatpur | 132/33kV Transformer 426T HT | 2023-03-02 07:21 | 2023-03-02 17:30 | 10:09 | S/O | Due to New X-former installation. | 0 | 0 | No interruption
Niamatpur | 132/33kV Transformer 426T HT | 2023-03-03 07:26 | 2023-03-03 14:51 | 7:25 | S/O | Due to Project work. | 0 | 0 | No interruption
Niamatpur | 132/33kV Transformer 426T HT | 2023-03-10 07:21 | 2023-03-15 15:20 | 127:59 | S/O | Due to New Transformer T-3 installation work. | 0 | 0 | No interruption
Niamatpurion | 132/33kV Transformer 426T LT | 2023-03-02 07:21 | 2023-03-02 17:35 | 10:14 | S/O | Due to New Transformer T-3 installation work. | 0 | 0 | No interruption
Niamatpur | 132/33kV Transformer 426T LT | 2023-03-03 07:25 | 2023-03-03 14:55 | 7:30 | S/O | Due to Project work. | 0 | 0 | No interruption
Niamatpur | 132/33kV Transformer 426T LT | 2023-03-10 07:20 | 2023-03-15 16:07 | 128:47 | S/O | Due to New Transformer T-3 installation work. | 0 | 0 | No interruption
Niamatpur | 132/33kV Transformer 426T LT | 2023-03-15 16:17 | 2023-03-16 15:03 | 22:46 | S/O | Due to commissioning.work | 0 | 0 | No interruption
Rajshahi | 132/33kV Transformer T-1(405T) LT | 2023-03-15 07:04 | 2023-03-16 07:40 | 24:36 | S/O | Due to maint.work | 0 | 0 | No interruption
Rajshahi | 132/33kV Transformer T-2(415T) HT | 2023-03-23 07:09 | 2023-03-23 09:13 | 2:04 | S/O | Due to For maintenance work at T2 33 kv BUS. | 16 | 33.0667 | Power interruption
Rajshahi | 132/33kV Transformer T-2(415T) LT | 2023-03-23 07:08 | 2023-03-23 09:14 | 2:06 | S/O | Due to For maintenance work at T2 33 kv BUS. | 16 | 0 | No interruption
Rajshahi | 132/33kV Transformer T-3 (425T) HT | 2023-03-20 11:35 | 2023-03-20 19:25 | 7:50 | S/O | Due to For maintenance work at T3 33 kv BUS. | 0 | 0 | No interruption
Saidpur | 132/33kV TransformerTR-3 (424T) HT | 2023-03-23 07:40 | 2023-03-23 18:10 | 10:30 | S/O | Due to maint.work by NESCO. | 20 | 210 | Power interruption
Saidpur | 132/33kV TransformerTR-3 (424T) LT | 2023-03-23 07:32 | 2023-03-23 18:11 | 10:39 | S/O | Due to replacement work.at 33 kV | 0 | 0 | No interruption
Saidpur | 132/33kV TransformerTR-4 (414T) HT | 2023-03-11 11:54 | 2023-03-11 13:08 | 1:14 | S/O | Due to Transformer Body Temperature high. | 0 | 0 | No interruption
Saidpur | 132/33kV TransformerTR-4 (414T) LT | 2023-03-11 11:53 | 2023-03-11 13:09 | 1:16 | S/O | Due to Transformer Body Temperature high. | 0 | 0 | No interruption
|  |  | Total : | 472:12 |  | Unserved Energy : |  | 426.3667
Others :
No interruption
|  |  | Total : | 0:00 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 2980:05 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/12 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: March2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Joydebpur | Joydebpur- Kodda 132 kV ckt-1 | 2023-03-27 08:28 | 2023-03-27 17:19 | 8:51 | S/O | Joydebpur-Kodda ckt-1 Line Bypassing work | 0 | 0 | No interruption
Joydebpur | Joydebpur- Kodda 132 kV ckt-1 | 2023-03-31 09:50 | 2023-03-31 12:22 | 2:32 | S/O | Due to maint.work | 0 | 0 | No interruption
Joydebpur | Joydebpur- Kodda132 kV ckt-2 | 2023-03-28 11:41 | 2023-03-28 14:40 | 2:59 | S/O | Due to changing work | 0 | 0 | No interruption
Joydebpur | Joydebpur- Kodda 132 kV ckt-2 | 2023-03-31 12:28 | 2023-03-31 14:31 | 2:03 | S/O | Due to maint.work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-1-01 | 2023-03-16 10:54 | 2023-03-16 13:03 | 2:09 | S/O | Due to Insulator cleaning work | 0 | 0 | No interruption
Aminbazar | Amijbazar-Kallyanpur 132 kV Ckt-01 | 2023-03-15 14:06 | 2023-03-15 16:16 | 2:10 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Aminbazar | Amijbazar-Kallyanpur 132 kV Ckt-02 | 2023-03-15 09:06 | 2023-03-15 12:49 | 3:43 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 132 kV Ckt-01 | 2023-03-06 08:18 | 2023-03-06 16:32 | 8:14 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 132 kV -01 | 2023-03-22 09:03 | 2023-03-22 18:21 | 9:18 | S/O | Due to Dead line checking | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir-132 kV Ckt-01 | 2023-03-23 09:50 | 2023-03-23 17:33 | 7:43 | S/O | Due to Dead Line Checking | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir-132 kV Ckt-02 | 2023-03-28 10:06 | 2023-03-28 17:00 | 6:54 | S/O | Due to Dead line checking | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir-132 kV Ckt-02 | 2023-03-29 10:34 | 2023-03-29 16:19 | 5:45 | S/O | Due to Dead line Checking | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV Ckt-01 | 2023-03-21 08:30 | 2023-03-21 17:17 | 8:47 | S/O | Due to dead line checking | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV Ckt-02 | 2023-03-30 15:39 | 2023-03-30 22:08 | 6:29 | S/O | Due to 400 kV ATR Shifting under Meghnaghat line | 0 | 0 | No interruption
Aminbazar | Aminbazar-Agargaon 230 kV Ckt-02 | 2023-03-09 10:26 | 2023-03-09 13:06 | 2:40 | S/O | Due to Insulator cleaning work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Gopalganj 400 kV Ckt-1 | 2023-03-31 13:20 | 2023-03-31 14:10 | 0:50 | S/O | Due to 400 kV New ATR Shifting | 0 | 0 | No interruption
Kallyanpur | 132Kv Kallyanpur-Lalbag Ckt-01 | 2023-03-04 07:12 | 2023-03-04 18:30 | 11:18 | S/O | Due to LA Change Work. | 0 | 0 | No interruption
Kallyanpur | 132Kv Kallyanpur-Lalbag Ckt-02 | 2023-03-07 07:02 | 2023-03-07 17:34 | 10:32 | S/O | Due to LA Change Work. | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV Ckt-1 | 2023-03-03 07:29 | 2023-03-03 18:26 | 10:57 | S/O | Due to Line shifting work to ERS Tower | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV Ckt-2 | 2023-03-10 07:17 | 2023-03-10 16:36 | 9:19 | S/O | Due to Line Shifted od ERS Tower(ERS Tower Installation). | 0 | 0 | No interruption
Savar | 132kV Manikganj PS-Savar Ckt-1 | 2023-03-18 08:36 | 2023-03-18 08:58 | 0:22 | S/O | Due to SCADA testing | 0 | 0 | No interruption
Savar | 132kV Manikganj PS-Savar Ckt-1 | 2023-03-31 13:17 | 2023-03-31 21:23 | 8:06 | S/O | Due to Corrective maintenance work. | 0 | 0 | No interruption
Savar | 132kV Manikganj PS-Savar Ckt-2 | 2023-03-18 08:59 | 2023-03-18 09:23 | 0:24 | S/O | Due to SCADA testing | 6 | 2.4 | Power interruption
Savar | 132kV Manikganj PS-Savar Ckt-2 | 2023-03-31 19:09 | 2023-03-31 20:35 | 1:26 | S/O | Due to OPGW work | 104 | 149.0667 | Power interruption
Kabirpur | Kabirpur-Kadda 132 kV Ckt-1 | 2023-03-01 07:06 | 2023-03-01 17:55 | 10:49 | S/O | Due to Conductor Re-stringing work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kadda 132 kV Ckt-1 | 2023-03-02 06:56 | 2023-03-02 18:20 | 11:24 | S/O | Due to Conductor Re-stringing work | 0 | 0 | No interruption
Mymensingh | Mymensingh-RPCL Ckt-1 | 2023-03-03 09:42 | 2023-03-03 12:24 | 2:42 | S/O | Due to High temperature of CT | 0 | 0 | No interruption
|  |  | Total : | 158:26 |  | Unserved Energy: |  | 151.4667
Dhaka (South) Grid Circle :
Haripur | Haripur-HPL 230 kV Ckt-1 | 2023-03-12 09:02 | 2023-03-12 17:01 | 7:59 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Haripur | Haripur-Meghnaghat 230 kV Ckt-1 | 2023-03-09 09:38 | 2023-03-09 18:35 | 8:57 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Haripur | Haripur-Ullon 132 kV Ckt (Maniknagar-2) | 2023-03-31 05:21 | 2023-03-31 07:31 | 2:10 | S/O | Due to NLDC work | 7 | 15.1667 | Power interruption
Meghnaghat | Meghnaghat-Haripur 230 kV Ckt-01 | 2023-03-09 09:52 | 2023-03-09 18:41 | 8:49 | S/O | As per request of NLDC | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV Ckt- 2 | 2023-03-01 16:13 | 2023-03-07 08:15 | 136:02 | S/O | Due to Order of NLDC | 0 | 0 | No interruption
Sonargaon | Sonargaon-OPML(IEL-1) 132 kV Ckt | 2023-03-04 08:46 | 2023-03-04 16:01 | 7:15 | S/O | Due to Annual maintenance work. | 0 | 0 | No interruption
Hasnabad | Shyampur-Hasnabad 230 kV Ckt-1 | 2023-03-21 08:58 | 2023-03-22 00:07 | 15:09 | S/O | Due to Relay Replacement Work | 0 | 0 | No interruption
Shyampur | Shyampur-230 kV Hasnabad-1(D02) | 2023-03-21 09:00 | 2023-03-22 00:06 | 15:06 | S/O | Due to Maintenance work | 0 | 0 | No interruption
|  |  | Total : | 201:27 |  | Unserved Energy: |  | 15.1667
Chattogram Grid Circle :
Khulshi | Khulshi-Madunaghat 132 kV CKT-2 | 2023-03-18 08:55 | 2023-03-18 11:15 | 2:20 | S/O | Due to Maintenance | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 CKT-1(Rampur) | 2023-03-20 08:49 | 2023-03-20 15:20 | 6:31 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar CKT-2(Rampur) | 2023-03-07 08:36 | 2023-03-07 13:19 | 4:43 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Khulshi | Khulshi-MSML 132 kV Ckt Line | 2023-03-09 08:23 | 2023-03-09 12:47 | 4:24 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Rampur | Rampur 230 kV -Khulshi-2 | 2023-03-07 08:39 | 2023-03-07 13:21 | 4:42 | S/O | annual maintenance at khulshi grid | 0 | 0 | No interruption
Hathazari | Hathazari 230/132/33kV -Baroiarhat-01 | 2023-03-13 07:02 | 2023-03-13 15:24 | 8:22 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Hathazari | Hathazari 230/132/33kV -Baroiarhat-01 | 2023-03-21 08:52 | 2023-03-21 16:42 | 7:50 | S/O | Due to Maintenance | 0 | 0 | No interruption
Hathazari | Hathazari 230/132/33kV-Baroiarhat-02 | 2023-03-20 08:40 | 2023-03-20 17:50 | 9:10 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Hathazari | Hathazari-Madunaghat 132 kV Ckt-02 | 2023-03-03 08:14 | 2023-03-03 16:51 | 8:37 | S/O | Due to Maintenance | 0 | 0 | No interruption
Hathazari | Hathazari 230/132/33kV- Shikolbaha-01 | 2023-03-12 09:44 | 2023-03-12 17:10 | 7:26 | S/O | Due to Maintenance | 0 | 0 | No interruption
Hathazari | Hathazari 230/132/33kV- Shikolbaha-01 | 2023-03-13 09:31 | 2023-03-13 16:46 | 7:15 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Hathazari | Hathazari 230/132/33kV- Shikolbaha-01 | 2023-03-14 10:46 | 2023-03-14 16:50 | 6:04 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Khagrachori | Khagrachori -RANGAMATI 132 kV Ckt--2 | 2023-03-27 12:32 | 2023-03-27 15:34 | 3:02 | S/O | Due to Relay Testing | 0 | 0 | No interruption
Rangamati | Khagrachori -RANGAMATI 132 kV Ckt--2 | 2023-03-27 12:35 | 2023-03-27 15:32 | 2:57 | S/O | Due to Relay Testing | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-Sikalbaha 132 kV Ckt-1 | 2023-03-01 08:22 | 2023-03-01 13:26 | 5:04 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-Sikalbaha 132 kV Ckt-2 | 2023-03-02 07:38 | 2023-03-02 15:22 | 7:44 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Chandraghona | Chandraghona-Kaptai Ckt-02 | 2023-03-22 10:11 | 2023-03-22 15:38 | 5:27 | S/O | Due to maintenance work | 0 | 0 | No interruption
Coxsbazar | Doh-Cox 132 kV Ckt-1 | 2023-03-16 12:30 | 2023-03-16 13:40 | 1:10 | S/O | Due to maintenance work | 28 | 32.6667 | Power interruption
Dohazari | Dohazari-Sikalbaha 132 kV ckt-2 | 2023-03-18 08:34 | 2023-03-18 13:43 | 5:09 | S/O | Due to maintenance work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Hathazari-132 kV Ckt2 | 2023-03-03 08:12 | 2023-03-03 16:52 | 8:40 | S/O | Due to Deadline Checking | 0 | 0 | No interruption
Madunaghat | Madunaghat-Hathazari 132 kV Ckt-2 | 2023-03-04 09:23 | 2023-03-04 17:02 | 7:39 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Madunaghat | Madunaghat-Kulshi 132 kV Ckt-2 | 2023-03-05 08:22 | 2023-03-05 17:03 | 8:41 | S/O | Due to according to NLDC directions. | 0 | 0 | No interruption
Shikalbaha | Sikalbaha-Dohazari 132 kV Ckt-2 | 2023-03-18 08:35 | 2023-03-18 13:42 | 5:07 | S/O | Due to changing work | 0 | 0 | No interruption
|  |  | Total : | 138:04 |  | Unserved Energy: |  | 32.6667
Cumilla Grid Circle :
Chauddagram | Chauddagram-Cumilla South 132 kV Ckt-1 | 2023-03-22 10:51 | 2023-03-22 12:22 | 1:31 | S/O | Due to SPMD work | 0 | 0 | No interruption
Cumilla(N) | 132KV Cumilla(N)-Daudkandi Ckt-1 | 2023-03-02 08:43 | 2023-03-02 12:43 | 4:00 | S/O | Due to to remove wavetrap | 0 | 0 | No interruption
Cumilla(N) | 132KV Cumilla(N)-Daudkandi Ckt-1 | 2023-03-15 08:40 | 2023-03-15 13:14 | 4:34 | S/O | Due to Relay test | 0 | 0 | No interruption
Cumilla(N) | 132KV Cumilla(N)-Daudkandi Ckt-2 | 2023-03-02 12:45 | 2023-03-02 15:08 | 2:23 | S/O | Due to To remove wave trap. | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Cumilla North 132 kV Ckt-1 | 2023-03-23 11:08 | 2023-03-23 12:38 | 1:30 | S/O | Due to Teleprotation Test | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Cumilla North 132 kV Ckt-2 | 2023-03-23 12:39 | 2023-03-23 13:52 | 1:13 | S/O | Due to Teleprotation Test | 0 | 0 | No interruption
Daudkandi | Daudkandi -Cumilla(N) 132 kV Ckt-1 | 2023-03-02 08:45 | 2023-03-02 12:42 | 3:57 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Daudkandi | Daudkandi -Cumilla(N) 132 kV Ckt-1 | 2023-03-15 08:38 | 2023-03-15 13:13 | 4:35 | S/O | Due to SPMD Relay Test | 0 | 0 | No interruption
Ramganj | Ramgonj-Chowmuhani 132 kV Ckt-01 | 2023-03-18 07:13 | 2023-03-18 18:03 | 10:50 | S/O | Due to stringing work | 0 | 0 | No interruption
Ramganj | Ramgonj-Chowmuhani 132 kV Ckt-02 | 2023-03-18 07:28 | 2023-03-18 18:04 | 10:36 | S/O | Due to stringing work | 0 | 0 | No interruption
Bibiana | Bibi-Shahzi 230 kV Ckt-II | 2023-03-01 08:38 | 2023-03-01 15:52 | 7:14 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Brahmanbaria | Brahmanbaria-Narsingdi 132kV Ckt-1 | 2023-03-20 09:53 | 2023-03-20 13:51 | 3:58 | S/O | Due to SPMD Relay Test | 0 | 0 | No interruption
Brahmanbaria 1 | Brahmanbaria-Narsingdi 132kV Ckt-2 | 2023-03-20 14:11 | 2023-03-20 16:03 | 1:52 | S/O | Due to SPMD Relay Test | 0 | 0 | No interruption
Brahmanbaria | Brahmanbaria-Ashugonj 132 Circuit-1 | 2023-03-06 09:47 | 2023-03-06 15:35 | 5:48 | S/O | Due to SPMD Relay Test | 0 | 0 | No interruption
Brahmanbaria | Brahmanbaria-Ashugonj 132 Circuit-2 | 2023-03-06 15:38 | 2023-03-06 17:26 | 1:48 | S/O | Due to SPMD Relay Test | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-B.Baria 132 kV Ckt-01 | 2023-03-23 14:13 | 2023-03-23 15:45 | 1:32 | S/O | Due to SPMD Relay Test | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-B.Baria 132 kV Ckt-02 | 2023-03-23 14:13 | 2023-03-23 15:45 | 1:32 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Ashuganj 132 kV Ckt-03 | 2023-03-05 08:32 | 2023-03-05 15:48 | 7:16 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Ashuganj 132 kV Ckt-03 | 2023-03-06 08:13 | 2023-03-06 16:11 | 7:58 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Ashuganj 132 kV Ckt-03 | 2023-03-07 09:10 | 2023-03-07 16:31 | 7:21 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Chhatak | Chhatak-Sylhet 132 kV Ckt-01 | 2023-03-21 07:11 | 2023-03-22 11:05 | 27:54 | S/O | Due to replacement work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Fenchuganj P/S- 132 kV Ckt-1 | 2023-03-03 09:14 | 2023-03-03 19:33 | 10:19 | S/O | Due to P/S work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Fenchuganj P/S- 132 kV Ckt-1 | 2023-03-18 09:44 | 2023-03-18 16:02 | 6:18 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Fenchuganj P/S- 132 kV Ckt-1 | 2023-03-28 11:52 | 2023-03-28 16:59 | 5:07 | S/O | Due to SPMD relay testing | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Fenchuganj P/S- 132 kV Ckt-2 | 2023-03-03 09:14 | 2023-03-07 10:32 | 97:18 | S/O | Due to P/S work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Fenchuganj P/S- 132 kV Ckt-2 | 2023-03-29 12:48 | 2023-03-29 15:14 | 2:26 | S/O | Due to SPMD Relay Test | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Fenchuganj P/S- 132 kV Ckt-3 | 2023-03-03 09:14 | 2023-03-03 19:33 | 10:19 | S/O | Due to P/S work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Fenchuganj P/S- 132 kV Ckt-3 | 2023-03-29 09:52 | 2023-03-29 12:16 | 2:24 | S/O | Due to P/S work | 0 | 0 | No interruption
Sylhet | Sylhet-90MW 132 kV Ckt | 2023-03-03 09:12 | 2023-03-03 19:04 | 9:52 | S/O | Due to P/S work | 0 | 0 | No interruption
Sylhet | Sylhet-Chhatak 132 kV Ckt-1 | 2023-03-21 07:12 | 2023-03-22 11:09 | 27:57 | S/O | Due to Maintenance work | 0 | 0 | No interruption
|  |  | Total : | 291:22 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Bhandaria | Bhandaria-Barishal 132 kV Ckt (L4) | 2023-03-29 15:01 | 2023-03-29 15:34 | 0:33 | S/O | Due to Maintenance works | 0 | 0 | No interruption
Patuakhali | Barishal-Pautakhali 132kV Line | 2023-03-20 00:36 | 2023-03-20 00:44 | 0:08 | S/O | Due to Safety purpose | 5 | 0.66667 | Power interruption
Gopalganj | Gopalganj -Gallamari-132 kV Ckt-1 | 2023-03-13 10:08 | 2023-03-13 13:26 | 3:18 | S/O | Due to maintenance work | 0 | 0 | No interruption
Khulna | Khulna ©-Noapara 132 kV Ckt-1 | 2023-03-01 07:50 | 2023-03-01 12:06 | 4:16 | S/O | Du eto Contact resistance measurement | 0 | 0 | No interruption
Khulna (C) | Khulna ©-Noapara 132 kV Ckt-1 | 2023-03-23 11:07 | 2023-03-25 15:00 | 51:53 | S/O | Due to Maintenance works | 0 | 0 | No interruption
Khulna (C) | Khulna ©-Noapara 132 kV Ckt-2 | 2023-03-23 11:07 | 2023-03-25 15:01 | 51:54 | S/O | Due to Maintenance works | 0 | 0 | No interruption
Khulna (C) | Khulna(C)-Goalpara 132 kV Ckt-2 | 2023-03-01 12:15 | 2023-03-01 16:47 | 4:32 | S/O | Du eto Contact resistance measurement | 0 | 0 | No interruption
Khulna © | Khulna ©-KPCL 132 kV -2 | 2023-03-20 10:40 | 2023-03-20 17:36 | 6:56 | S/O | Due to Maintenance work by P/S | 0 | 0 | No interruption
Khulna (C) | Khulna ©-KPCL 132 kV -2 | 2023-03-21 08:22 | 2023-03-21 11:10 | 2:48 | S/O | Due to Maintenance work by P/S | 0 | 0 | No interruption
Khulna (C) | Khulna ©-KPCL 132 kV -2 | 2023-03-22 14:18 | 2023-03-22 17:20 | 3:02 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Khulna © | Khulna ©-KPCL 132 kV -2 | 2023-03-23 07:55 | 2023-03-23 18:12 | 10:17 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Khulna (C) | Khulna ©-KPCL 132 kV -2 | 2023-03-24 10:30 | 2023-03-24 16:17 | 5:47 | S/O | Due to ALDC work | 0 | 0 | No interruption
Noapara | Noapara-khulna central 132 kV Ckt - 1 | 2023-03-01 07:49 | 2023-03-01 11:56 | 4:07 | S/O | Due to ALDC work | 0 | 0 | No interruption
Bagerhat | Bagerhat- Bhandaria 132 kV Ckt | 2023-03-03 09:40 | 2023-03-03 14:29 | 4:49 | S/O | Due to Replacement work | 0 | 0 | No interruption
|  |  | Total : | 149:31 |  | Unserved Energy: |  | 0.66667
HVDC Grid Circle :
BIPTC | BIPTC - Baharampur-3 | 2023-03-30 10:04 | 2023-03-30 20:52 | 10:48 | S/O | Due to Maintenance work | 0 | 0 | No interruption
BIPTC | BIPTC - Baharampur-3 | 2023-03-31 10:23 | 2023-03-31 21:35 | 11:12 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Baghabari 132 kV Ckt | 2023-03-10 08:27 | 2023-03-10 12:27 | 4:00 | S/O | Due to Maintenance work | 0 | 0 | No interruption
|  |  | Total : | 26:00 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Bogura | Bogura-Naogaon 132 KV Line-1 | 2023-03-05 07:47 | 2023-03-05 19:53 | 12:06 | S/O | Du to Project Work | 0 | 0 | No interruption
Bogura | Bogura-Naogaon 132 KV Line-2 | 2023-03-25 06:54 | 2023-03-25 16:39 | 9:45 | S/O | Du to Project Work | 50 | 487.5 | Power interruption
Barapukuria | Barapukuria-Bogura 230 KV Ckt1 | 2023-03-06 08:25 | 2023-03-06 17:53 | 9:28 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Barapukuria | Barapukuria-Bogura 230 KV Ckt2 | 2023-03-04 08:56 | 2023-03-04 17:39 | 8:43 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Barapukuria | Barapukuria-Bogura 230 KV Ckt2 | 2023-03-05 08:26 | 2023-03-05 17:52 | 9:26 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Amnura | Amnura - Chapai Nawabganj 132 kV Ckt | 2023-03-30 07:37 | 2023-03-30 10:01 | 2:24 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Chapai | Chapai-Amnura 132 kV Ckt | 2023-03-30 07:35 | 2023-03-30 10:12 | 2:37 | S/O | Due to Maintenance work | 0 | 0 | No interruption
|  |  | Total : | 54:29 |  | Unserved Energy: |  | 487.5
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1019:19 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
12:37 | 16:50 | Chowmuhani-Feni 132 kV Ckt-2 Scheduled S/D Due to Annual Maintenance of SPMD Comilla.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:March 2023
| Area | Previous Month (February' 2023) |  |  |  | Current Month (March '2023)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 18 | 9 | 143 | 170 | 16 | 7 | 62 | 85
2 | Dhaka (South) Grid Circle. | 10 | 17 | 53 | 80 | 32 | 15 | 26 | 73
3 | Chattogram Grid Circle. | 2 | 5 | 104 | 111 | 14 | 4 | 37 | 55
4 | Cumilla Grid Circle. | 16 | 6 | 100 | 122 | 45 | 6 | 59 | 110
5 | Khulna Grid Circle. | 10 | 12 | 93 | 115 | 23 | 5 | 70 | 98
6 | HVDC Grid Circle | 6 | 8 | 48 | 62 | 21 | 1 | 8 | 30
7 | Bogura Grid Circle. | 2 | 21 | 27 | 50 | 20 |  | 36 | 56
8 | Others | Total number of E/O: 1; Total number of Total: 1; Total number of Total: 0
9 | Total | 64 | 79 | 568 | 711 | 171 | 38 | 298 | 507
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:March2023
| Area | Previous Month (October' 2022) |  |  |  | Current Month (November '2022)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 70.6 | 88.33 | 2392.08 | 2551.01 | 161.85 | 1882.33 | 402.67 | 2446.85
2 | Dhaka (South) Grid Circle. | 97.5 |  | 384.3333 | 481.8333 | 1156 | 121.4 | 122.83 | 1400.23
3 | Chattogram Grid Circle. | 0 | 0 | 620.9833 | 620.9833 | 64.48 | 466.5 | 175.67 | 706.65
4 | Cumilla Grid Circle. | 31.62 |  | 20.25 | 51.87 | 480 | 73.51 | 3111 | 3664.51
5 | Khulna Grid Circle. | 170.79 | 8.63 | 301.13 | 480.55 | 496.9 | 443.23 | 78.73 | 1018.86
6 | HVDC Grid Circle |  | 9.33 | 608.63 | 617.96 | 43.37 | 230 | 30 | 303.37
7 | Bogura Grid Circle. |  | 136.27 | 164 | 300.27 | 1227.38 | 676.8 | 208 | 2112.18
8 | Others | Energy unserved ( MWH ) due to Total: 0; Energy unserved ( MWH ) due to Total: 0
9 | Total | 370.51 | 242.56 | 4491.4067 | 5104.4767 | 3629.98 | 3893.77 | 4128.9 | 11652.65
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:March2023
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 8 | 2 | 10 | 3 | 3 | 7 | 2264.65
2 | Dhaka (South) | 5031.6 | 14 | 3 | 17 | 4 | 8 | 9 | 708.03
3 | Chattogram | 2042 | 6 | 0 | 6 | 3 | 3 | 3 | 480
4 | Khulna | 2434 | 27 | 6 | 33 | 14 | 21 | 12 | 1005.28
5 | HVDC | 5954.3 | 9 | 4 | 13 | 2 | 2 | 11 | 291.87
6 | Bogura | 3145.6 | 20 | 7 | 27 | 8 | 9 | 18 | 1748.77
7 | Cumilla | 2981 | 27 | 0 | 27 | 16 | 25 | 30 | 3148.55
8 | Others | - | - | - |  | - | - | - | 0
| Total | 30390.1 | [6 empty] | 9647.15
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.93%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.98%
4 | Khulna | 99.88%
5 | HVDC | 99.97% | [6 empty] | Executive Engineer
6 | Bogura | 99.88% | [6 empty] | Information Management Division
7 | Cumilla | 99.84% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:March2023
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 2 | 3 | 5 | 4 | 4 | 1 | - | 182.2
2 | Dhaka (South) | 990.29 |  | 7 | 1 | 8 | 1 | 3 | 5 | - | 692.33
3 | Chattogram | 917 | - | 4 | 2 | 6 | 2 | 4 | 2 | - | 219.75
4 | Khulna | 1238.4 | - | 0 | 1 | 1 | 1 | 1 | 0 |  | 0.67
5 | HVDC | 1325 | - | 0 | 0 | 0 | 0 | 0 | 0 | - | 0
6 | Bogura | 1803.3 | - | 2 | 1 | 3 | 0 | 0 | 3 | - | 1119.27
7 | Cumilla | 1648.16 | - | 3 | 1 | 4 | 2 | 2 | 2 | - | 516.13
8 | Others | - |  |  | - |  | - | - | - | - | -
| Total | 10176.6215 | [8 empty] | 2730.35
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.99%
4 | Khulna | 100%
5 | Bheramara (HVDC) | 100% | [7 empty] | Executive Engineer
6 | Bogura | 99.86% | [7 empty] | Information Management Division
7 | Cumilla | 99.98% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:March2023
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2023-03-01 | 8 | - | - | - | - | - | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/2 |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:March2023
| Total Nos.of | Total | Total | Remarks
Sub-station | Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
| Total Nos.of | Total | Total | Remarks
Sub-station | Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Amnura 132/33kV Grid Sub-Station | 1 | 2:09 | 15.05
Bagerhat 132/33kV Grid Sub-Station | 1 | 0:49 | 22.05
Barishal 132/33kV Grid Sub-Station | 5 | 1:00 | 30.8
Barishal 230/132kV Grid Sub-Station | 2 | 8:54 | 222.5
Baroaulia 132/33kV Grid Sub-Station | 1 | 0:31 | 25.8333
Bhaluka 132/33kV Grid Sub-Station | 1 | 0:12 | 15.2
Bhandaria 132/33kV Grid Sub-Station | 2 | 1:16 | 16.4667
Bheramara(GK) 132/33kV Grid Sub-Station | 2 | 4:06 | 20.5
Bogura 132/33kV Grid Sub-Station | 2 | 2:40 | 85.3333
Bogura 230/132kV Grid Sub-Station | 2 | 13:08 | 633.9333
Brahmanbaria 132/33kV Grid Sub-Station | 4 | 2:00 | 72.4667
Chandpur 132/33kV Grid Sub-Station | 12 | 21:05 | 556.1
Chhatak 132/33kV Grid Sub-Station | 2 | 8:28 | 8.4667
Chowmuhani 132/33kV Grid Sub-Station | 17 | 106:14 | 2574.75
Coxsbazar 132/33kV Grid Sub-Station | 8 | 211:19 | 518.4
Cumilla(S) 132/33kV Grid Sub-Station | 3 | 4:58 | 38.5333
Dohazari 132/33kV Grid Sub-Station | 2 | 4:59 | 148.4167
Faridpur 132/33kV Grid Sub-Station | 2 | 8:33 | 48.9333
Feni 132/33kV Grid Sub-Station | 4 | 3:21 | 63.3833
Gollamari 132/33kV Grid Sub-Station | 3 | 24:56 | 322
Gopalganj 132/33kV Grid Sub-Station | 4 | 5:23 | 93.3333
Haripur 230/132kV Grid Sub-Station | 3 | 5:04 | 35.4667
Jamalpur 132/33kV Grid Sub-Station | 3 | 2:06 | 82.3333
Jashore 132/33kV Grid Sub-Station | 5 | 12:01 | 164.3667
Joypurhat 132/33kV Grid Sub-Station | 4 | 6:21 | 63.5
Kabirpur 132/33kV Grid Sub-Station | 1 | 2:17 | 205.5
Keranigonj 230/132/33kV Grid Sub-Station | 1 | 0:35 | 16.3333
Khulna (C) 132/33kV Grid Sub-Station | 9 | 17:59 | 205
Kishoreganj 132/33kV Grid Sub-Station | 2 | 1:21 | 52.65
Kodda 132/33kV Grid Sub-Station | 2 | 18:40 | 1866.6667
Kulaura 132/33kV Grid Sub-Station | 2 | 1:06 | 22
Kushtia 132/33kV Grid Sub-Station | 3 | 5:14 | 85.1333
Madaripur 132/33kV Grid Sub-Station | 2 | 0:36 | 9.6
Mahasthangarh 132/33kV Grid Sub-Station | 2 | 7:03 | 119.8
Munshiganj 132/33kV Grid Sub-Station | 4 | 1:45 | 37.75
Mymensingh 132/33kV Grid Sub-Station | 1 | 1:27 | 43.5
Naogaon 132/33kV Grid Sub-Station | 1 | 12:08 | 485.3333
Narail 132/33kV Grid Sub-Station | 2 | 0:54 | 13.5
Niamatpur 132/33kV Grid Sub-Station | 4 | 1:00 | 59.3333
Noapara 132/33kV Grid Sub-Station | 2 | 3:06 | 34.1
Pabna 132/33kV Grid Sub-Station | 3 | 3:14 | 21.8667
Panchagarh 132/33kV Grid Sub-Station | 1 | 24:28 | 11.6667
Patuakhali 132/33kV Grid Sub-Station | 1 | 0:08 | 0.66667
Purbasadipur 132/33kV Grid Sub-Station | 4 | 28:23 | 549.25
Rajshahi 132/33kV Grid Sub-Station | 3 | 22:22 | 667.2667
Ramganj 132/33kV Grid Sub-Station | 1 | 10:36 | 190.8
Rangamati 132/33kV Grid Sub-Station | 2 | 1:10 | 14
Saidpur 132/33kV Grid Sub-Station | 1 | 10:30 | 210
Savar 132/33kV Grid Sub-Station | 4 | 2:20 | 167
Shahjadpur 132/33kV Grid Sub-Station | 1 | 0:35 | 33.8333
Shahjibazar 132/33kV Grid Sub-Station | 2 | 0:54 | 11
Siddhirganj 132/33kV Grid Sub-Station | 8 | 15:17 | 211.2
Siddhirganj 230/132kV Grid Sub-Station | 3 | 17:39 | 895.5833
Sirajganj 132/33kV Grid Sub-Station | 3 | 5:05 | 80.8333
Sonargaon 132/33kV Grid Sub-Station | 6 | 8:35 | 204.0833
Sreemongol 132/33kV Grid Sub-Station | 6 | 0:47 | 10.35
Sunamganj 132/33kV Grid Sub-Station | 1 | 0:23 | 3.45
Sylhet 132/33kV Grid Sub-Station | 5 | 13:36 | 113.3833
Tangail 132/33kV Grid Sub-Station | 1 | 1:24 | 14
Thakurgaon 132/33kV Grid Sub-Station | 4 | 0:56 | 6.5333
Grand Total | 193 | 705:06 | 12551.0833
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/3 |  |  | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:March '2023
Sl. No | Sub-station | Date and time | Load (MW)
1 | Aftabnagar 132/33kV Grid Sub-Station | 2023-03-04 18:30 | 32
2 | Agargaon 230/132kV Grid Sub-Station | 2023-03-26 15:00 | 87
3 | Banani 132/33kV Grid Sub-Station | 2023-03-15 09:00 | 44
4 | Bangabhaban 132/33kV Grid Sub-Station | 2023-03-12 11:00 | 21
5 | Bashundhara 132/33kV Grid Sub-Station | 2023-03-14 18:30 | 150
6 | BashundharaCement 132/33kV Sub-Station | 2023-03-04 11:00 | 6
7 | Bhulta 132/33kV Grid Sub-Station | 2023-03-14 10:00 | 261
8 | Cantonment 132/33kV GIS Grid Sub-Station | 2023-03-14 18:30 | 129
9 | Charsaidpur 132/33kV Sub-Station | 2023-03-24 07:00 | 51
10 | Dhaka University 132/33kV Grid Sub-Station | 2023-03-14 12:00 | 44
11 | Dhamrai 132/33kV Grid Sub-Station | 2023-03-13 15:00 | 112
12 | Dhanmondi 132/33kV Grid Sub-Station | 2023-03-12 13:00 | 133
13 | Fatullah 132/33kV Grid Sub-Station | 2023-03-30 10:00 | 69
14 | Ghorashal 132/33kV Sub-Station | 2023-03-11 12:00 | 148
15 | Gulshan 132/33kV Grid Sub-Station | 2023-03-28 12:00 | 116
16 | HaripurSBU 132/33kV Sub-Station | 2023-03-04 06:00 | 212
17 | Hasnabad 132/33kV Grid Substation | 2023-03-18 12:00 | 101
18 | Joydebpur 132/33kV Grid Sub-Station | 2023-03-18 18:30 | 150
19 | Kabirpur 132/33kV Grid Sub-Station | 2023-03-06 12:00 | 322
20 | Kallyanpur 132/33kV Grid Sub-Station | 2023-03-04 18:30 | 93
21 | Kamrangirchar 132/33kV Grid Sub-Station | 2023-03-23 13:00 | 71
22 | Kazla 132/33kV Grid Sub-Station | 2023-03-14 19:30 | 94
23 | Keranigonj 230/132/33kV Grid Sub-Station | 2023-03-15 12:00 | 74
24 | Kodda 132/33kV Grid Sub-Station | 2023-03-11 12:00 | 326
25 | Lalbag 132/33kV Grid Sub-Station | 2023-03-20 12:00 | 82
26 | Madanganj 132/33kV Grid Sub-Station | 2023-03-23 12:00 | 50
27 | Madartek 132/33kV Grid Sub-Station | 2023-03-14 21:00 | 75
28 | Manikganj 132/33kV Grid Sub-Station | 2023-03-15 18:30 | 104
29 | Maniknagar 132/33kV Grid Sub-Station | 2023-03-14 13:00 | 72
30 | Matuail 132/33kV Grid Sub-Station | 2023-03-16 16:00 | 69
31 | Millgate Tongi 132/33kV Grid Sub-Station | 2023-03-23 12:00 | 78
32 | Mirpur 132/33kV Grid Sub-Station | 2023-03-15 17:00 | 127
33 | Mogbazar 132/33kV Grid Sub-Station | 2023-03-30 14:00 | 123
34 | Motijheel 132/33kV Grid Sub-Station | 2023-03-14 13:00 | 35
35 | Munshiganj 132/33kV Grid Sub-Station | 2023-03-17 22:00 | 97
36 | Narinda 132/33kV Grid Sub-Station | 2023-03-15 13:00 | 70
37 | Narshingdi 132/33kV Grid Sub-Station | 2023-03-18 20:00 | 172
38 | Nawabganj 132/33kV Grid Sub-Station | 2023-03-30 18:30 | 42.4
39 | New Tongi 132/33kV Grid Sub-Station | 2023-03-13 12:00 | 79.8
40 | Postogola 132/33kV Grid Sub-Station | 2023-03-14 13:00 | 39
41 | Purbachal 132/33kV Grid Sub-Station | 2023-03-16 18:00 | 19
42 | Rahim Steel 132/33kV Sub-Station | 2023-03-11 12:00 | 60
43 | Rajendrapur 132/33kV Grid Sub-Station | 2023-03-18 19:00 | 130
44 | Satmasjid 132/33kV Grid Sub-Station | 2023-03-28 20:00 | 100
45 | Savar 132/33kV Grid Sub-Station | 2023-03-28 14:00 | 202
46 | Shitalakhya 132/33kV Grid Sub-Station | 2023-03-14 15:00 | 124
47 | Shyampur 132/33kV Grid Sub-Station | 2023-03-30 14:00 | 192
48 | Siddhirganj 132/33kV Grid Sub-Station | 2023-03-07 12:00 | 114
49 | Sonargaon 132/33kV Grid Sub-Station | 2023-03-06 17:00 | 125
50 | Srinagar 132/33kV Grid Sub-Station | 2023-03-06 20:00 | 41.19
51 | Tongi 230/132/33kV Grid Sub-Station | 2023-03-14 15:00 | 128
52 | Ullon 132/33kV Grid Sub-Station | 2023-03-29 20:00 | 47
53 | Uttara 132/33kV Grid Sub-Station | 2023-03-05 13:00 | 76
54 | UttaraNew 132/33kV Grid Sub-Station | 2023-03-15 09:00 | 28
56 | Zigatola 132/33kV Grid Sub-Station | 2023-03-14 13:00 | 72
57 | Agrabad 132/33kV Grid Sub-Station | 2023-03-14 15:00 | 68
58 | AKS 132/33kV Grid Sub-Station | 2023-03-04 19:00 | 22
59 | AKSML 230/33kV Grid Sub-Station | 2023-03-24 23:00 | 109
60 | Bakulia 132/33kV Grid Sub-Station | 2023-03-14 21:00 | 95
61 | Baroaulia 132/33kV Grid Sub-Station | 2023-03-30 12:00 | 82
62 | Baroirhat 132/33kV Grid Sub-Station | 2023-03-16 18:30 | 46
63 | BSRM 230/33kV Grid Sub-Station | 2023-03-18 19:00 | 115
64 | Chandraghona 132/33kV Grid Sub-Station | 2023-03-28 18:30 | 31
65 | Coxsbazar 132/33kV Grid Sub-Station | 2023-03-30 21:00 | 128
66 | Dohazari 132/33kV Grid Sub-Station | 2023-03-28 19:30 | 94
67 | GPH 230/33kV Grid Sub-Station | 2023-03-09 15:00 | 100
68 | Halishahar 132/33kV Grid Sub-Station | 2023-03-06 16:00 | 102
69 | Hathazari 230/132/33kV Grid Sub-Station | 2023-03-14 19:00 | 58
70 | Juldah 132/33kV Grid Sub-Station | 2023-03-09 15:00 | 35
71 | Kalurghat 132/33kV Grid Sub-Station | 2023-03-06 15:00 | 35
72 | Kaptai 132/33kV Sub-Station | 2023-03-26 15:00 | 12
73 | Khagrachori 132/33kV Grid Sub-Station | 2023-03-18 19:00 | 30
74 | Khulshi 132/33kV Grid Sub-Station | 2023-03-11 18:00 | 184
75 | KSRM 132/33kV Grid Sub-Station | 2023-03-26 19:00 | 50
76 | Madunaghat 132/33kV Grid Sub-Station | 2023-03-28 19:00 | 54
77 | Matarbari 132/33kV Sub-Station | 2023-03-11 12:00 | 60
78 | Mirsorai 230/33kV Grid Sub-Station | 2023-03-28 19:30 | 4
79 | Modern Steel 132/11kV Grid Sub-Station | 2023-03-01 | 0
80 | Rampur 230/132/33 kV GIS Grid Sub-Station | 2023-03-28 19:30 | 34
81 | Rangamati 132/33kV Grid Sub-Station | 2023-03-11 19:00 | 16
82 | Shahmirpur 132/33kV Grid Sub-Station | 2023-03-29 | 51
83 | Shikalbaha 132/33kV Sub-Station | 2023-03-11 12:00 | 72
84 | Sholosohor 132/33kV Grid Sub-Station | 2023-03-25 09:00 | 33
85 | SSM 132/33kV Grid Sub-Station | 2023-03-12 18:30 | 40
86 | TK chemical 132kV Grid Sub-Station | 2023-03-28 21:00 | 28.5
87 | Ashuganj 230/132/33kV Sub-Station | 2023-03-14 17:00 | 87.5
88 | Brahmanbaria 132/33kV Grid Sub-Station | 2023-03-30 21:00 | 160
89 | Chandpur 132/33kV Grid Sub-Station | 2023-03-18 18:00 | 64
90 | Chauddagram 132/33kV Grid Sub-Station | 2023-03-11 14:00 | 46
91 | Chowmuhani 132/33kV Grid Sub-Station | 2023-03-12 20:00 | 178
92 | Cumilla(N) 230/132/33kV Grid Sub-Station | 2023-03-05 23:00 | 162
93 | Cumilla(S) 132/33kV Grid Sub-Station | 2023-03-13 14:00 | 170
94 | Daudkandi 132/33kV Grid Sub-Station | 2023-03-16 19:30 | 125
95 | Feni 132/33kV Grid Sub-Station | 2023-03-12 18:30 | 120
96 | Kachua 132/33kV Grid Sub-Station | 2023-03-05 19:00 | 72
97 | PHP 132/33kV Sub-Station | 2023-03-25 16:00 | 11
98 | Ramganj 132/33kV Grid Sub-Station | 2023-03-21 22:00 | 122
99 | Bhaluka 132/33kV Grid Sub-Station | 2023-03-09 15:00 | 150
100 | Jamalpur 132/33kV Grid Sub-Station | 2023-03-15 19:00 | 168
101 | Kishoreganj 132/33kV Grid Sub-Station | 2023-03-05 18:30 | 146
101 | Mymensingh 132/33kV Grid Sub-Station | 2023-03-14 18:30 | 248
102 | Netrakona 132/33kV Grid Sub-Station | 2023-03-09 20:00 | 143
103 | Sherpur 132/33kV Grid Sub-Station | 2023-03-13 19:00 | 160
104 | Tangail 132/33kV Grid Sub-Station | 2023-03-05 07:00 | 238
105 | Beanibazar 132/33kV Grid Sub-Station | 2023-03-13 19:00 | 54
106 | Chhatak 132/33kV Grid Sub-Station | 2023-03-09 18:30 | 26
107 | Fenchuganj 230/132/33kV Grid Sub-Station | 2023-03-28 18:30 | 41
108 | Kulaura 132/33kV Grid Sub-Station | 2023-03-11 18:30 | 42
109 | Shahjibazar 132/33kV Grid Sub-Station | 2023-03-12 19:00 | 114
110 | Sreemongol 132/33kV Grid Sub-Station | 2023-03-13 18:30 | 55
111 | Sunamganj 132/33kV Grid Sub-Station | 2023-03-13 19:00 | 43
112 | Sylhet 132/33kV Grid Sub-Station | 2023-03-13 18:30 | 130
113 | Bagerhat 132/33kV Grid Sub-Station | 2023-03-05 19:00 | 91
114 | Benapole 132/33kV Grid Sub-Station | 2023-03-25 19:30 | 70
115 | Bheramara(GK) 132/33kV Grid Sub-Station | 2023-03-30 19:00 | 56
116 | Chuadanga 132/33kV Grid Sub-Station | 2023-03-30 19:30 | 103
117 | Faridpur 132/33kV Grid Sub-Station | 2023-03-28 19:30 | 130
118 | Goalpara 132/33kV Grid Sub-Station | 2023-03-30 19:30 | 36
119 | Gollamari 132/33kV Grid Sub-Station | 2023-03-16 22:00 | 58
120 | Gopalganj 132/33kV Grid Sub-Station | 2023-03-14 18:30 | 91.2
121 | Jashore 132/33kV Grid Sub-Station | 2023-03-30 21:00 | 138
122 | Jhenaidah 132/33kV Grid Sub-Station | 2023-03-30 19:00 | 122
123 | Khulna (C) 132/33kV Grid Sub-Station | 2023-03-30 19:00 | 111
124 | Kushtia 132/33kV Grid Sub-Station | 2023-03-07 18:30 | 122
125 | Madaripur 132/33kV Grid Sub-Station | 2023-03-23 21:00 | 84
126 | Magura 132/33kV Grid Sub-Station | 2023-03-14 19:00 | 58
127 | Mongla 132/33kV Grid Sub-Station | 2023-03-28 23:00 | 50
128 | Narail 132/33kV Grid Sub-Station | 2023-03-16 19:00 | 51
129 | Noapara 132/33kV Grid Sub-Station | 2023-03-29 19:00 | 54
130 | Rajbari 132/33kV Grid Sub-Station | 2023-03-28 19:00 | 58
131 | Satkhira 132/33kV Grid Sub-Station | 2023-03-29 19:30 | 130
132 | Shariatpur 132/33kV Grid Sub-Station | 2023-03-16 19:00 | 60
133 | Barguna 132/33kV Grid Sub-Station | 2023-03-25 19:30 | 16
134 | Barishal 132/33kV Grid Sub-Station | 2023-03-16 19:00 | 106
135 | Barishal 230/132kV Grid Sub-Station | 2023-03-30 19:00 | 98
136 | Bhandaria 132/33kV Grid Sub-Station | 2023-03-28 23:00 | 43
137 | Borhanuddin 230/33kV Grid Sub-Station | 2023-03-12 20:00 | 51
138 | Patuakhali 132/33kV Grid Sub-Station | 2023-03-25 19:00 | 87
139 | Payra 400/132/33kV Grid Sub-Station | 2023-03-30 21:00 | 14.36
140 | Amnura 132/33kV Grid Sub-Station | 2023-03-15 19:30 | 78
141 | Bhangura 132/33kV Grid Sub-Station | 2023-03-15 19:00 | 36
142 | Bog-Sherpur 132/33kV Grid Sub-Station | 2023-03-15 19:00 | 74
143 | Bogura 132/33kV Grid Sub-Station | 2023-03-27 21:00 | 152
144 | Chapai 132/33kV Grid Sub-Station | 2023-03-29 22:00 | 71
145 | Ishurdi 132/33kV Grid Sub-Station | 2023-03-15 19:00 | 65
146 | Joypurhat 132/33kV Grid Sub-Station | 2023-03-14 19:00 | 64
147 | Mahasthangarh 132/33kV Grid Sub-Station | 2023-03-06 20:00 | 72
148 | Naogaon 132/33kV Grid Sub-Station | 2023-03-14 20:00 | 136
149 | Natore 132/33kV Grid Sub-Station | 2023-03-28 20:00 | 150
150 | Niamatpur 132/33kV Grid Sub-Station | 2023-03-06 20:00 | 111
151 | Pabna 132/33kV Grid Sub-Station | 2023-03-26 03:00 | 105
152 | Rahanpur_I 400/132kV Grid Sub-Station | 2023-03-09 19:30 | 44
153 | Rajshahi 132/33kV Grid Sub-Station | 2023-03-30 21:00 | 146
154 | Rajshahi 230/132/33kV Grid Sub-Station | 2023-03-30 15:00 | 37
155 | Ruppur 132/11kV Grid Sub-Station | 2023-03-22 15:00 | 5.4
156 | Shahjadpur 132/33kV Grid Sub-Station | 2023-03-14 20:00 | 119
157 | Sirajganj 132/33kV Grid Sub-Station | 2023-03-14 12:00 | 118
158 | Barapukuria 230/132/33kV Grid Sub-Station | 2023-03-11 11:00 | 59
159 | Jaldhaka 132/33kV Grid Sub-Station | 2023-03-18 19:00 | 73
160 | Kurigram 132/33kV Grid Sub-Station | 2023-03-11 19:00 | 68
161 | Lalmonirhat 132/33kV Grid Sub-Station | 2023-03-13 19:00 | 48.62
162 | Mithapukur 132/33kV Grid Sub-Station | 2023-03-18 13:00 | 42
163 | Palashbari 132/33kV Grid Sub-Station | 2023-03-18 19:00 | 126
164 | Panchagarh 132/33kV Grid Sub-Station | 2023-03-06 19:00 | 58
165 | Purbasadipur 132/33kV Grid Sub-Station | 2023-03-12 18:00 | 115
166 | Rangpur 132/33kV Grid Sub-Station | 2023-03-29 18:00 | 143
167 | Saidpur 132/33kV Grid Sub-Station | 2023-03-15 18:30 | 116
168 | Thakurgaon 132/33kV Grid Sub-Station | 2023-03-13 19:00 | 93
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:March 2023
Area | MW | Date | Hour | Remarks
Dhaka | 4742 | 30.03.2023 | 14:00
Chattogram | 1338 | 28.03.2023 | 22:00
Cumilla | 1159.5 | 13.03.2023 | 19:00
Mymensingh | 1060 | 14.03.2023 | 20:00
Sylhet | 485 | 13.03.2023 | 19:00
Khulna | 1540.8 | 30.03.2023 | 19:30
Barishal | 363.4 | 30.03.2023 | 19:00
Rajshahi | 1435 | 14.03.2023 | 20:00
Rangpur | 909.62 | 13.03.2023 | 19:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [5 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: March '2023
SL. | 400 KV Substation | Rated | Maxm |  | Minm | Date and Time
No. |  | Voltage | Voltage | Date and Time | Voltage |  | Remarks
|  | kV | kV |  | kV
1 | Aminbazar 400/230/132kV Grid Sub-Station | 400 | 419 | 2023-03-31 02:00 | 384 | 2023-03-02 12:00
2 | Bhulta 400/230kV Grid Sub-Station | 400 | 404 | 2023-03-18 08:00 | 379 | 2023-03-27 09:00
3 | Bibiana 400/230kV Sub-Station | 400 | 412 | 2023-03-18 09:00 | 379 | 2023-03-01 16:00
4 | BIPTC | 400 | 408 | 2023-03-20 04:00 | 387 | 2023-03-31 12:00
5 | Gopalganj 400/132kV Grid Sub-Station | 400 | 423 | 2023-03-20 06:00 | 385 | 2023-03-06 15:00
6 | Kaliakoir 400/230/132kV Grid Sub-Station | 400 | 401 | 2023-03-25 18:00 | 377 | 2023-03-29 07:00
7 | Madunaghat_I 400/230kV Grid Sub-Station | 400 | 418 | 2023-03-02 19:30 | 375 | 2023-03-31 09:00
|  | Rated | Maxm |  | Minm | Date and Time
SL. | Substation | Voltage | Voltage | Date and Time | Voltage |  | Remarks
No. | 230 KV Substation | kV | kV |  | kV
1 | Agargaon 230/132kV Grid Sub-Station | 230 | 243 | 2023-03-31 02:00 | 221 | 2023-03-04 12:00
2 | AKSML 230/33kV Grid Sub-Station | 230 | 244 | 2023-03-03 08:00 | 203 | 2023-03-25 15:00
3 | Baghabari 230/132kV Grid Sub-Station | 230 | 238 | 2023-03-20 04:00 | 220 | 2023-03-11 09:00
4 | Barapukuria 230/132/33kV Grid Sub-Station | 230 | 232 | 2023-03-20 16:00 | 205 | 2023-03-02 07:00
5 | Barishal 230/132kV Grid Sub-Station | 230 | 242 | 2023-03-03 06:00 | 226 | 2023-03-28 15:00
6 | Bheramara 230/132kV Grid Sub-Station | 230 | 240 | 2023-03-20 05:00 | 221 | 2023-03-02 10:00
7 | Bogura 230/132kV Grid Sub-Station | 230 | 238 | 2023-03-20 05:00 | 214 | 2023-03-30 09:00
8 | BSRM 230/33kV Grid Sub-Station | 230 | 241 | 2023-03-03 08:00 | 221 | 2023-03-29 07:00
9 | Cumilla(N) 230/132/33kV Grid Sub-Station | 230 | 240 | 2023-03-31 02:00 | 225 | 2023-03-29 07:00
10 | Fenchuganj 230/132/33kV Grid Sub-Station | 230 | 247 | 2023-03-19 08:00 | 236 | 2023-03-01 12:00
11 | GPH 230/33kV Grid Sub-Station | 230 | 242 | 2023-03-02 19:00 | 218 | 2023-03-29 07:00
12 | Haripur 230/132kV Grid Sub-Station | 230 | 242 | 2023-03-31 02:00 | 223 | 2023-03-04 11:00
13 | Hasnabad 230/132kV Grid Sub-Station | 230 | 240 | 2023-03-29 17:00 | 220 | 2023-03-14 17:00
14 | Hathazari 230/132/33kV Grid Sub-Station | 230 | 242 | 2023-03-02 19:00 | 217 | 2023-03-31 09:00
15 | Ishurdi 230/132kV Grid Sub-Station | 230 | 242 | 2023-03-20 05:00 | 223 | 2023-03-14 07:00
16 | Jhenaidah 230/132kV Grid Sub-Station | 230 | 240 | 2023-03-20 01:00 | 217 | 2023-03-25 14:00
17 | Keranigonj 230/132/33kV Grid Sub-Station | 230 | 243 | 2023-03-31 02:00 | 221 | 2023-03-02 12:00
18 | Khulna(S) 230/132kV Grid Sub-Station | 230 | 246 | 2023-03-17 02:00 | 222 | 2023-03-22 18:30
19 | Maniknagar 230/132kV Grid Sub-Station | 230 | 237 | 2023-03-19 18:30 | 221 | 2023-03-02 12:00
20 | Meghnaghat 230/132kV Grid Sub-Station | 230 | 242 | 2023-03-08 19:00 | 230 | 2023-03-02 11:00 |  | 7345
21 | Mirsorai 230/33kV Grid Sub-Station | 230 | 240 | 2023-03-01 19:00 | 218 | 2023-03-31 10:00
22 | Rajshahi 230/132/33kV Grid Sub-Station | 230 | 240 | 2023-03-20 04:00 | 219 | 2023-03-14 07:00
23 | Rampura 230/132kV Grid Sub-Station | 230 | 242 | 2023-03-31 02:00 | 222 | 2023-03-06 12:00
24 | Shikalbaha 230/132kV Grid Sub-Station | 230 | 242 | 2023-03-01 18:30 | 217 | 2023-03-31 10:00
25 | Shyampur 230/132kV Grid Sub-Station | 230 | 241 | 2023-03-31 02:00 | 218 | 2023-03-10 12:00
26 | Siddhirganj 230/132kV Grid Sub-Station | 230 | 244 | 2023-03-31 01:00 | 225 | 2023-03-02 12:00
27 | Sirajgonj 230 kV Switching Station | 230 | 246 | 2023-03-22 05:00 | 213 | 2023-03-11 15:00
28 | Tongi 230/132/33kV Grid Sub-Station | 230 | 236 | 2023-03-31 01:00 | 200 | 2023-03-02 10:00
1 | Aftabnagar 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-31 02:00 | 126 | 2023-03-06 15:00
2 | Agrabad 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-18 08:00 | 124 | 2023-03-31 09:00
3 | AKS 132/33kV Grid Sub-Station | 132 | 138 | 2023-03-03 08:00 | 125 | 2023-03-15 12:00
4 | Amnura 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-20 07:00 | 119 | 2023-03-10 12:00
5 | Ashuganj 230/132/33kV Sub-Station | 132 | 142 | 2023-03-31 02:00 | 132 | 2023-03-02 15:00
6 | Bagerhat 132/33kV Grid Sub-Station | 132 | 142 | 2023-03-17 02:00 | 121 | 2023-03-22 18:30
7 | Bakulia 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-03 08:00 | 124 | 2023-03-31 23:00
8 | Banani 132/33kV Grid Sub-Station | 132 | 141 | 2023-03-31 02:00 | 126 | 2023-03-01 12:00
9 | Bangabhaban 132/33kV Grid Sub-Station | 132 | 141 | 2023-03-31 02:00 | 125 | 2023-03-01 13:00
10 | Barguna 132/33kV Grid Sub-Station | 132 | 137 | 2023-03-02 17:00 | 124 | 2023-03-22 18:30
11 | Barishal 132/33kV Grid Sub-Station | 132 | 137 | 2023-03-26 18:30 | 126 | 2023-03-28 14:00
12 | Baroaulia 132/33kV Grid Sub-Station | 132 | 142 | 2023-03-01 19:00 | 126 | 2023-03-31 11:00
13 | Baroirhat 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-08 18:00 | 125 | 2023-03-29 06:00
14 | Bashundhara 132/33kV Grid Sub-Station | 132 | 143 | 2023-03-31 01:00 | 120 | 2023-03-04 12:00
15 | BashundharaCement 132/33kV Sub-Station | 132 | 142 | 2023-03-31 02:00 | 128 | 2023-03-02 12:00
16 | Beanibazar 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-29 04:00 | 127 | 2023-03-26 15:00
17 | Benapole 132/33kV Grid Sub-Station | 132 | 139 | 2023-03-20 03:00 | 118 | 2023-03-25 14:00
18 | Bhaluka 132/33kV Grid Sub-Station | 132 | 136 | 2023-03-19 08:00 | 113 | 2023-03-01 12:00
19 | Bhandaria 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-19 18:00 | 125 | 2023-03-12 18:30
20 | Bhangura 132/33kV Grid Sub-Station | 132 | 144 | 2023-03-20 04:00 | 129 | 2023-03-02 10:00
21 | Bheramara(GK) 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-21 04:00 | 126 | 2023-03-12 18:30
22 | Bhulta 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-31 02:00 | 118 | 2023-03-02 12:00
23 | Bog-Sherpur 132/33kV Grid Sub-Station | 132 | 141 | 2023-03-20 05:00 | 120 | 2023-03-09 07:00
24 | Bogura 132/33kV Grid Sub-Station | 132 | 145 | 2023-03-08 22:00 | 121 | 2023-03-02 07:00
25 | Brahmanbaria 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-31 02:00 | 128 | 2023-03-02 12:00
26 | Cantonment 132/33kV GIS Grid Sub-Station | 132 | 141 | 2023-03-31 02:00 | 127 | 2023-03-02 12:00
27 | Chandpur 132/33kV Grid Sub-Station | 132 | 143 | 2023-03-07 18:30 | 123 | 2023-03-04 01:00
28 | Chandraghona 132/33kV Grid Sub-Station | 132 | 142 | 2023-03-03 08:00 | 127 | 2023-03-29 09:00
29 | Chapai 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-20 07:00 | 120 | 2023-03-12 07:00
30 | Charsaidpur 132/33kV Sub-Station | 132 | 141 | 2023-03-29 18:30 | 128 | 2023-03-04 12:00
31 | Chauddagram 132/33kV Grid Sub-Station | 132 | 142 | 2023-03-21 19:30 | 126 | 2023-03-24 11:00
32 | Chhatak 132/33kV Grid Sub-Station | 132 | 139 | 2023-03-29 06:00 | 126 | 2023-03-28 14:00
33 | Chowmuhani 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-21 18:30 | 118 | 2023-03-21 23:00
34 | Chuadanga 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-21 04:00 | 118 | 2023-03-04 18:30
35 | Coxsbazar 132/33kV Grid Sub-Station | 132 | 137 | 2023-03-16 02:00 | 113 | 2023-03-09 23:00
36 | Cumilla(S) 132/33kV Grid Sub-Station | 132 | 142 | 2023-03-21 19:00 | 120 | 2023-03-13 13:00
37 | Daudkandi 132/33kV Grid Sub-Station | 132 | 142 | 2023-03-31 02:00 | 127 | 2023-03-02 12:00
38 | Dhaka University 132/33kV Grid Sub-Station | 132 | 141 | 2023-03-31 01:00 | 126 | 2023-03-06 12:00
39 | Dhamrai 132/33kV Grid Sub-Station | 132 | 141 | 2023-03-31 02:00 | 126 | 2023-03-02 12:00
40 | Dhanmondi 132/33kV Grid Sub-Station | 132 | 144 | 2023-03-31 02:00 | 129.5 | 2023-03-02 12:00
41 | Dohazari 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-03 08:00 | 121 | 2023-03-26 23:00
42 | Faridpur 132/33kV Grid Sub-Station | 132 | 136 | 2023-03-19 18:00 | 125 | 2023-03-12 18:30
43 | Fatullah 132/33kV Grid Sub-Station | 132 | 142 | 2023-03-31 02:00 | 128 | 2023-03-04 12:00
44 | Feni 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-02 18:00 | 125 | 2023-03-24 11:00
45 | Ghorashal 132/33kV Sub-Station | 132 | 145 | 2023-03-31 01:00 | 129 | 2023-03-30 22:00
46 | Goalpara 132/33kV Grid Sub-Station | 132 | 141 | 2023-03-17 02:00 | 126 | 2023-03-22 18:30
47 | Gollamari 132/33kV Grid Sub-Station | 132 | 138 | 2023-03-15 21:00 | 124 | 2023-03-02 15:00
48 | Gopalganj 132/33kV Grid Sub-Station | 132 | 138 | 2023-03-15 16:00 | 124 | 2023-03-02 12:00
49 | Gulshan 132/33kV Grid Sub-Station | 132 | 139 | 2023-03-31 02:00 | 125 | 2023-03-06 12:00
50 | Halishahar 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-03 08:00 | 125 | 2023-03-28 07:00
51 | HaripurSBU 132/33kV Sub-Station | 132 | 145 | 2023-03-31 02:00 | 130 | 2023-03-11 17:00
52 | Hasnabad 132/33kV Grid Substation | 132 | 138 | 2023-03-02 11:00 | 128 | 2023-03-02 13:00
53 | Ishurdi 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-20 06:00 | 127 | 2023-03-12 18:30
54 | Jaldhaka 132/33kV Grid Sub-Station | 132 | 139 | 2023-03-20 06:00 | 113 | 2023-03-03 07:00
55 | Jamalpur 132/33kV Grid Sub-Station | 132 | 141 | 2023-03-17 19:30 | 113 | 2023-03-01 17:00
56 | Jashore 132/33kV Grid Sub-Station | 132 | 139 | 2023-03-17 02:00 | 121 | 2023-03-23 19:00
57 | Jhenaidah 132/33kV Grid Sub-Station | 132 | 142 | 2023-03-26 22:00 | 125 | 2023-03-06 18:30
58 | Joydebpur 132/33kV Grid Sub-Station | 132 | 146 | 2023-03-31 01:00 | 130 | 2023-03-06 15:00
59 | Joypurhat 132/33kV Grid Sub-Station | 132 | 137 | 2023-03-20 03:00 | 113 | 2023-03-01 11:00
60 | Juldah 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-10 18:30 | 125 | 2023-03-10 12:00
61 | Kabirpur 132/33kV Grid Sub-Station | 132 | 145 | 2023-03-31 01:00 | 118 | 2023-03-04 12:00
62 | Kachua 132/33kV Grid Sub-Station | 132 | 142 | 2023-03-19 19:30 | 122 | 2023-03-07 23:00
63 | Kallyanpur 132/33kV Grid Sub-Station | 132 | 142 | 2023-03-31 02:00 | 125 | 2023-03-01 13:00
64 | Kalurghat 132/33kV Grid Sub-Station | 132 | 141 | 2023-03-05 18:30 | 125 | 2023-03-31 10:00
65 | Kamrangirchar 132/33kV Grid Sub-Station | 132 | 138 | 2023-03-19 23:00 | 125 | 2023-03-06 12:00
66 | Kaptai 132/33kV Sub-Station | 132 | 140 | 2023-03-01 18:00 | 122 | 2023-03-04 07:00
67 | Kazla 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-31 03:00 | 126 | 2023-03-02 12:00
68 | Khagrachori 132/33kV Grid Sub-Station | 132 | 139 | 2023-03-02 19:00 | 127 | 2023-03-09 06:00
69 | Khulna (C) 132/33kV Grid Sub-Station | 132 | 141 | 2023-03-17 02:00 | 124 | 2023-03-22 18:30
70 | Khulshi 132/33kV Grid Sub-Station | 132 | 139 | 2023-03-01 19:00 | 125 | 2023-03-09 06:00
71 | Kishoreganj 132/33kV Grid Sub-Station | 132 | 138 | 2023-03-31 01:00 | 118 | 2023-03-14 21:00
| Kodda 132/33kV Grid Sub-Station | 132 | 145 | 2023-03-31 01:00 | 125 | 2023-03-30 09:00
SL. | KSRM 132/33kV Grid Sub-Station | 132 | 141 | 2023-03-27 17:00 | 126 | 2023-03-30 08:00
No. | Kulaura 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-29 04:00 | 132 | 2023-03-20 11:00
| Kurigram 132/33kV Grid Sub-Station | 132 | 137 | 2023-03-20 04:00 | 114 | 2023-03-14 07:00
72 | Kushtia 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-20 02:00 | 126 | 2023-03-02 12:00
73 | Lalbag 132/33kV Grid Sub-Station | 132 | 139 | 2023-03-26 18:30 | 125 | 2023-03-04 12:00
74 | Lalmonirhat 132/33kV Grid Sub-Station | 132 | 138 | 2023-03-19 04:00 | 113 | 2023-03-15 07:00
75 | Madanganj 132/33kV Grid Sub-Station | 132 | 142 | 2023-03-31 02:00 | 128 | 2023-03-02 12:00
76 | Madaripur 132/33kV Grid Sub-Station | 132 | 138 | 2023-03-26 18:30 | 127 | 2023-03-02 12:00
77 | Madartek 132/33kV Grid Sub-Station | 132 | 141 | 2023-03-31 02:00 | 125 | 2023-03-06 12:00
78 | Madunaghat 132/33kV Grid Sub-Station | 132 | 141 | 2023-03-05 18:30 | 125 | 2023-03-31 09:00
79 | Magura 132/33kV Grid Sub-Station | 132 | 141 | 2023-03-20 01:00 | 123 | 2023-03-06 18:30
80 | Mahasthangarh 132/33kV Grid Sub-Station | 132 | 139 | 2023-03-20 04:00 | 119 | 2023-03-01 07:00
81 | Manikganj 132/33kV Grid Sub-Station | 132 | 145 | 2023-03-31 01:00 | 118 | 2023-03-02 11:00
82 | Maniknagar 132/33kV Grid Sub-Station | 132 | 141 | 2023-03-31 02:00 | 124 | 2023-03-11 12:00
83 | Matarbari 132/33kV Sub-Station | 132 | 138 | 2023-03-09 01:00 | 113 | 2023-03-11 15:00
84 | Matuail 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-29 18:30 | 129 | 2023-03-02 12:00
85 | Millgate Tongi 132/33kV Grid Sub-Station | 132 | 144 | 2023-03-31 01:00 | 121 | 2023-03-04 12:00
86 | Mirpur 132/33kV Grid Sub-Station | 132 | 138 | 2023-03-19 18:30 | 124 | 2023-03-02 12:00
87 | Mithapukur 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-20 04:00 | 118 | 2023-03-02 07:00
88 | Modern Steel 132/11kV Grid Sub-Station | 132 | 139 | 2023-03-01 19:00 | 126 | 2023-03-09 06:00
89 | Mogbazar 132/33kV Grid Sub-Station | 132 | 142 | 2023-03-31 02:00 | 127 | 2023-03-06 13:00
90 | Mongla 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-17 03:00 | 122 | 2023-03-22 18:30
91 | Motijheel 132/33kV Grid Sub-Station | 132 | 141 | 2023-03-31 02:00 | 125 | 2023-03-01 13:00
92 | Munshiganj 132/33kV Grid Sub-Station | 132 | 139 | 2023-03-28 18:30 | 128 | 2023-03-01 15:00
93 | Mymensingh 132/33kV Grid Sub-Station | 132 | 139 | 2023-03-30 23:00 | 113 | 2023-03-02 21:00
94 | Naogaon 132/33kV Grid Sub-Station | 132 | 138 | 2023-03-20 04:00 | 114 | 2023-03-01 07:00
95 | Narail 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-20 05:00 | 121 | 2023-03-06 18:30
96 | Narshingdi 132/33kV Grid Sub-Station | 132 | 144 | 2023-03-31 02:00 | 121 | 2023-03-02 11:00
97 | Natore 132/33kV Grid Sub-Station | 132 | 139 | 2023-03-20 02:00 | 124 | 2023-03-02 07:00
98 | Nawabganj 132/33kV Grid Sub-Station | 132 | 138 | 2023-03-19 19:00 | 126 | 2023-03-02 12:00
99 | Netrakona 132/33kV Grid Sub-Station | 132 | 136 | 2023-03-19 08:00 | 113 | 2023-03-03 11:00
100 | New Tongi 132/33kV Grid Sub-Station | 132 | 143 | 2023-03-31 02:00 | 122 | 2023-03-04 12:00
101 | Niamatpur 132/33kV Grid Sub-Station | 132 | 136 | 2023-03-21 04:00 | 113 | 2023-03-01 10:00
102 | Noapara 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-17 02:00 | 121 | 2023-03-25 11:00
103 | Pabna 132/33kV Grid Sub-Station | 132 | 144 | 2023-03-21 05:00 | 124 | 2023-03-12 18:30
104 | Palashbari 132/33kV Grid Sub-Station | 132 | 138 | 2023-03-19 03:00 | 114 | 2023-03-01 07:00
105 | Panchagarh 132/33kV Grid Sub-Station | 132 | 139 | 2023-03-20 06:00 | 113 | 2023-03-03 08:00
106 | Patuakhali 132/33kV Grid Sub-Station | 132 | 137 | 2023-03-26 14:00 | 124 | 2023-03-18 22:00
107 | PHP 132/33kV Sub-Station | 132 | 140 | 2023-03-03 08:00 | 124 | 2023-03-16 14:00
108 | Postogola 132/33kV Grid Sub-Station | 132 | 142 | 2023-03-31 02:00 | 124 | 2023-03-17 20:00
109 | Purbachal 132/33kV Grid Sub-Station | 132 | 141 | 2023-03-31 01:00 | 124 | 2023-03-26 20:00
110 | Purbasadipur 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-20 03:00 | 113 | 2023-03-07 08:00
111 | Rahim Steel 132/33kV Sub-Station | 132 | 145 | 2023-03-31 02:00 | 130 | 2023-03-04 14:00
112 | Rajbari 132/33kV Grid Sub-Station | 132 | 137 | 2023-03-20 04:00 | 124 | 2023-03-12 18:30
113 | Rajendrapur 132/33kV Grid Sub-Station | 132 | 146 | 2023-03-31 02:00 | 125 | 2023-03-27 10:00
114 | Rajshahi 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-20 02:00 | 122 | 2023-03-12 07:00
115 | Ramganj 132/33kV Grid Sub-Station | 132 | 141 | 2023-03-21 19:00 | 119 | 2023-03-16 14:00
116 | Rangamati 132/33kV Grid Sub-Station | 132 | 141 | 2023-03-05 15:00 | 126 | 2023-03-29 07:00
117 | Rangpur 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-19 04:00 | 114 | 2023-03-15 07:00
118 | Ruppur 132/11kV Grid Sub-Station | 132 | 141 | 2023-03-21 05:00 | 127 | 2023-03-14 07:00
119 | Saidpur 132/33kV Grid Sub-Station | 132 | 139 | 2023-03-20 04:00 | 113 | 2023-03-14 07:00
120 | Satkhira 132/33kV Grid Sub-Station | 132 | 141 | 2023-03-17 02:00 | 122 | 2023-03-22 18:30
121 | Satmasjid 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-31 02:00 | 127 | 2023-03-02 12:00
122 | Savar 132/33kV Grid Sub-Station | 132 | 142 | 2023-03-31 02:00 | 123 | 2023-03-01 15:00
123 | Shahjadpur 132/33kV Grid Sub-Station | 132 | 145 | 2023-03-20 21:00 | 133 | 2023-03-09 08:00
124 | Shahjibazar 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-31 02:00 | 130 | 2023-03-02 15:00
125 | Shariatpur 132/33kV Grid Sub-Station | 132 | 138 | 2023-03-20 06:00 | 126 | 2023-03-02 12:00
126 | Sherpur 132/33kV Grid Sub-Station | 132 | 141 | 2023-03-30 22:00 | 113 | 2023-03-01 18:00
127 | Shikalbaha 132/33kV Sub-Station | 132 | 141 | 2023-03-05 18:30 | 121 | 2023-03-04 23:00
128 | Shitalakhya 132/33kV Grid Sub-Station | 132 | 142 | 2023-03-31 02:00 | 128 | 2023-03-02 12:00
129 | Sholosohor 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-03 08:00 | 125 | 2023-03-29 07:00
130 | Shyampur 132/33kV Grid Sub-Station | 132 | 137 | 2023-03-18 18:00 | 128 | 2023-03-04 12:00
131 | Siddhirganj 132/33kV Grid Sub-Station | 132 | 139 | 2023-03-08 18:00 | 129 | 2023-03-02 12:00
132 | Sirajganj 132/33kV Grid Sub-Station | 132 | 141 | 2023-03-20 04:00 | 124 | 2023-03-13 07:00
133 | Sonargaon 132/33kV Grid Sub-Station | 132 | 143 | 2023-03-31 02:00 | 127 | 2023-03-02 12:00
134 | Sreemongol 132/33kV Grid Sub-Station | 132 | 139 | 2023-03-31 02:00 | 130 | 2023-03-27 14:00
135 | Srinagar 132/33kV Grid Sub-Station | 132 | 141 | 2023-03-31 02:00 | 126 | 2023-03-02 12:00
136 | SSM 132/33kV Grid Sub-Station | 132 | 145 | 2023-03-21 13:00 | 129 | 2023-03-01 07:00
137 | Sunamganj 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-29 06:00 | 125 | 2023-03-26 18:30
138 | Sylhet 132/33kV Grid Sub-Station | 132 | 139 | 2023-03-29 04:00 | 129 | 2023-03-26 15:00
139 | Tangail 132/33kV Grid Sub-Station | 132 | 143 | 2023-03-31 01:00 | 123 | 2023-03-05 07:00
140 | Thakurgaon 132/33kV Grid Sub-Station | 132 | 140 | 2023-03-20 07:00 | 113 | 2023-03-06 08:09
141 | TK chemical 132kV Grid Sub-Station | 132 | 140 | 2023-03-02 19:00 | 124 | 2023-03-31 08:00
142 | Ullon 132/33kV Grid Sub-Station | 132 | 143 | 2023-03-26 03:00 | 126 | 2023-03-06 11:00
143 | Uttara 132/33kV Grid Sub-Station | 132 | 141 | 2023-03-31 02:00 | 121 | 2023-03-04 12:00
144 | UttaraNew 132/33kV Grid Sub-Station | 132 | 143 | 2023-03-31 01:00 | 123 | 2023-03-04 11:00
145 | Zigatola 132/33kV Grid Sub-Station | 132 | 138 | 2023-03-31 02:00 | 125 | 2023-03-06 13:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 |  |  |  |  | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month: March 2023
Name of the | Auto transformer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | MVA | Date and Time
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 127 | 179.6051 | 2023-03-26 19:00
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 148 | 156.8694 | 2023-03-28 14:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 185 | 192.72 | 2023-03-04 12:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 205 | 225.9425 | 2023-03-01 15:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 212 | 221.4498 | 2023-03-01 15:00
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 178 | 193.1554 | 2023-03-14 07:00
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 144 | 156 | 2023-03-14 07:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 162 | 167.869 | 2023-03-28 18:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 152 | 165.3149 | 2023-03-15 07:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 259 | 259.9327 | 2023-03-29 22:00
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 197 | 197.4285 | 2023-03-06 10:00
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 197 | 197.4285 | 2023-03-06 10:00
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | -536 | 539.6897 | 2023-03-04 18:00
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | -86 | 117.4564 | 2023-03-23 18:30
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 157 | 160.228 | 2023-03-30 03:00
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 157 | 160.228 | 2023-03-30 03:00
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 210 | 214.7673 | 2023-03-30 03:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-01 | 230/132 | 188 | 193.5459 | 2023-03-26 04:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-02 | 230/132 | 150 | 207.9327 | 2023-03-07 01:00
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 191 | 212.0024 | 2023-03-27 18:30
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 113 | 144.4611 | 2023-03-20 10:00
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 113 | 144.4611 | 2023-03-20 10:00
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 113 | 144.4611 | 2023-03-20 10:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 52 | 53.3667 | 2023-03-20 11:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 64 | 64.4981 | 2023-03-02
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 64 | 64.4981 | 2023-03-02
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 106 | 113.2961 | 2023-03-04 15:00
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 106 | 113.2961 | 2023-03-04 15:00
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 105 | 110.3676 | 2023-03-04 21:00
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 106 | 113.2961 | 2023-03-04 15:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 131 | 143.6732 | 2023-03-14 19:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 118 | 166.8772 | 2023-03-16 19:30
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 118 | 128.5496 | 2023-03-15 21:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | -228 | 241.6278 | 2023-03-23 19:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | -228 | 241.6278 | 2023-03-23 19:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 145 | 151.8223 | 2023-03-15 19:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 0 | 0 | 2023-03-01
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 145 | 151.8223 | 2023-03-15 19:00
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | -134 | 135.9596 | 2023-03-27 19:00
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | -134 | 135.9596 | 2023-03-27 19:00
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | -288 | 288.0156 | 2023-03-25
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 232 | 250.3198 | 2023-03-11 12:00
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 137 | 150.3762 | 2023-03-15 13:00
Rajshahi 230/132/33kV Grid Sub-Station | ATR-01 (704T) | 230/132 | -146 | 146.4138 | 2023-03-12 21:00
Rajshahi 230/132/33kV Grid Sub-Station | ATR-02 (714T) | 230/132 | -146 | 146.4138 | 2023-03-12 21:00
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 1 | 10.0499 | 2023-03-13 15:00
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 0 | 0 | 2023-03-01
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 01 | 230/132 | 197 | 201.4274 | 2023-03-14 13:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 | 230/132 | 159 | 242.4252 | 2023-03-20 19:30
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 | 230/132 | 197 | 201.4274 | 2023-03-14 13:00
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 217 | 230.5927 | 2023-03-04 20:00
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 217 | 230.5927 | 2023-03-04 20:00
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 132 | 146.2635 | 2023-03-06 18:00
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 120 | 130 | 2023-03-14 03:00
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 62 | 149.4657 | 2023-03-19 13:00
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 98 | 233.5551 | 2023-03-19 02:00
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 205 | 208.137 | 2023-03-16 11:00
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 205 | 208.137 | 2023-03-16 11:00
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 205 | 208.137 | 2023-03-16 11:00
Month: March 2023
Name of the | Transformer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | MVA | Date and Time
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 | 400/230 | 348 | 351.2947 | 2023-03-02 22:00
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 | 400/230 | 360 | 364.4846 | 2023-03-03 23:00
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | -281 | 313.4996 | 2023-03-07 10:00
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | -334 | 380.8477 | 2023-03-18 11:00
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | -191 | 191.1675 | 2023-03-31 02:00
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | -182 | 182 | 2023-03-31 02:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 34 | 389.4868 | 2023-03-07 16:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 137 | 192.3382 | 2023-03-08 06:00
Madunaghat_I 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 1 | 403.0012 | 2023-03-20 23:00
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | -237 | 246.0183 | 2023-03-12 18:30
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | -151 | 155.7081 | 2023-03-28 21:00
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | -237 | 246.0183 | 2023-03-12 18:30
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 266 | 329.8196 | 2023-03-17 16:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 311 | 326.6818 | 2023-03-23 07:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | 48 | 61.2209 | 2023-03-02 18:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | -48 | 61.2209 | 2023-03-02 18:00
Rahanpur_I 400/132kV Grid Sub-Station | AT-1 -Gen | 400/132 | 232 | 241.2053 | 2023-03-30 21:00

## QF-LDC-37
|  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:March-2023 | [6 empty] | (For Evening Peak) | [7 empty] | Month:March-2023 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2023-03-01 | 11822 | 11892 | 65 | 19:00 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | - | 2023-03-01 | 10772 | 10810 | 35 | 12:00 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | -
2023-03-02 | 11818 | 11865 | 43 | 19:00 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | - | 2023-03-02 | 10639 | 10807 | 155 | 12:00 | 60 | 0 | 10 | 0 | 0 | 85 | 0 | 0 | 0 | -
2023-03-03 | 10693 | 10693 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2023-03-03 | 9824 | 9947 | 113 | 12:00 | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | -
2023-03-04 | 11872 | 12065 | 178 | 19:00 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | - | 2023-03-04 | 10249 | 10366 | 125 | 12:00 | 35 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | -
2023-03-05 | 12052 | 12308 | 236 | 19:00 | 29 | 0 | 0 | 78 | 0 | 120 | 9 | 0 | 0 | - | 2023-03-05 | 10287 | 11271 | 161 | 12:00 | 0 | 0 | 0 | 51 | 0 | 110 | 0 | 0 | 0 | -
2023-03-06 | 12465 | 12521 | 52 | 19:30 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | - | 2023-03-06 | 10869 | 12255 | 356 | 12:00 | 0 | 98 | 0 | 60 | 31 | 130 | 37 | 0 | 0 | -
2023-03-07 | 11503 | 11568 | 60 | 19:00 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | - | 2023-03-07 | 11350 | 11388 | 35 | 12:00 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | -
2023-03-08 | 11020 | 11040 | 18 | 19:00 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | - | 2023-03-08 | 9421 | 9421 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-03-09 | 12096 | 12264 | 155 | 19:00 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | - | 2023-03-09 | 10842 | 10842 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-03-10 | 10945 | 10978 | 30 | 19:00 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | - | 2023-03-10 | 9948 | 9948 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-03-11 | 12172 | 12221 | 45 | 19:00 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | - | 2023-03-11 | 10238 | 10238 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-03-12 | 12748 | 12829 | 75 | 19:00 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | - | 2023-03-12 | 11332 | 11406 | 68 | 12:00 | 38 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | -
2023-03-13 | 12921 | 13046 | 115 | 19:00 | 10 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | - | 2023-03-13 | 11475 | 11509 | 31 | 12:00 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | -
2023-03-14 | 12920 | 12920 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-03-14 | 11515 | 11701 | 171 | 12:00 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | -
2023-03-15 | 12622 | 12665 | 40 | 19:00 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | - | 2023-03-15 | 10196 | 10428 | 214 | 9:00 | 40 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 39 | -
2023-03-16 | 12891 | 12926 | 32 | 19:00 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | - | 2023-03-16 | 11295 | 11306 | 10 | 12:00 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | -
2023-03-17 | 10220 | 10220 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-03-17 | 9637 | 9637 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-03-18 | 12345 | 12404 | 54 | 19:00 | 11 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | - | 2023-03-18 | 9999 | 9999 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-03-19 | 9675 | 9675 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-03-19 | 8684 | 8684 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-03-20 | 10324 | 10324 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-03-20 | 9336 | 9336 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-03-21 | 10376 | 10376 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-03-21 | 9259 | 9259 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-03-22 | 11259 | 11259 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-03-22 | 9758 | 9758 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-03-23 | 11742 | 11742 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-03-23 | 10194 | 10194 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-03-24 | 10892 | 10892 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-03-24 | 9543 | 9543 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-03-25 | 11194 | 11194 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-03-25 | 10555 | 10555 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-03-26 | 10776 | 10776 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-03-26 | 9974 | 9974 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-03-27 | 12072 | 12118 | 42 | 19:30 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | - | 2023-03-27 | 10788 | 10788 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-03-28 | 12575 | 12678 | 95 | 21:00 | 0 | 0 | 0 | 0 | 20 | 75 | 0 | 0 | 0 | - | 2023-03-28 | 11375 | 11375 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-03-29 | 11153 | 11153 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2023-03-29 | 10302 | 10302 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023-03-30 | 12128 | 12155 | 25 | 19:30 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 |  | 2023-03-30 | 11163 | 11163 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023-03-31 | 10794 | 10794 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2023-03-31 | 9176 | 9176 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Max. L/S | - | 236 | 2023-03-05 | 19:00 | [9 empty] | Max. L/S | - |  | 356 | 2023-03-06 | 12:00
| Min. L/S | - | 0 | 2023-03-03 | 19:00 | [9 empty] | Min. L/S | - |  | 0 | 2023-03-08 | 12:00
| No. of Days | - | 18 | - | [10 empty] | No. of Days | - | 12
| Average L/S |  | 43.871 | [11 empty] | Average L/S |  | 47.5484
|  | - | - | - | [11 empty] | - | -
| Generation During Max. Load Shed (MW) at Evening Peak |  |  | 12052 | [10 empty] | Generation During Max. Load Shed (MW) at Day Peak |  |  | 10869
| Generation During Min. Load Shed (MW) at Evening Peak |  |  | 10693 | [10 empty] | Generation During Min. Load Shed (MW) at Day Peak |  |  | 9421
[15 empty] | -81 | 74 | 12
[15 empty] | -125 | 34 | 13
[15 empty] | 0 | 186 | 14
[15 empty] | -43 | 232 | 15
[15 empty] | -35 | 11 | 16
[15 empty] | 0 | 0 | 17
[15 empty] | -59 | 0 | 18
[15 empty] | 0 | 0 | 19
[15 empty] | 0 | 0 | 20
[15 empty] | 0 | 0 | 21
[15 empty] | 0 | 0 | 22
[15 empty] | 0 | 0 | 23
[15 empty] | 0 | 0 | 24
[15 empty] | 0 | 0 | 25
[15 empty] | 0 | 0 | 26
[15 empty] | -46 | 0 | 27
[15 empty] | -103 | 0 | 28
[15 empty] | #REF! | #REF! | 29
[15 empty] | #REF! | #REF! | 30
[15 empty] | #REF! | #REF! | 31

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:March-2023
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 12921 | 2023-03-13 | 19:00
2 | Maximum Day Peak Genaration | MW | 11515 | 2023-03-14 | 12:00
3 | Maximum Evening Peak Demand | MW | 13046 | 2023-03-31 | 21:00
4 | Minimum Generation | MW | 6507 | 2023-03-20 | 6:00
5 | Average of the daily evening peak Genaration | MW | 11615.6452 | - | -
6 | Average of the daily day peak Genaration | MW | 10322.4194 | - | -
7 | Maximum load shed | MW | 236 | 2022-11-01 | 20:00
8 | Minimum load shed | MW | 0 | 2022-11-03 | 19:00
9 | Total nos. of load shed days | Day | 18 | - | -
10 | Average load shed ( Avg. of the 30 days in the month) | MW/Day | 43.871 | - | -
11 | Total Generation | MkWh | 7213.1492 | - | -
12 | Total Generation by BPDB | MkWh | 1561.2501 | % of total Gen. | 21.64%
13 | Total Generation by IPP | MkWh | 2436.9704 | '' | 33.79%
14 | A) Total Generation by Generation Companies | MkWh | 2258.4963 | '' | 31.31%
| B) Total Generation by REB | MkWh | 121.5861 | " | 1.686%
| C) Total Generation by RENTAL | MkWh | 299.4051 | " | 4.151%
| D) Total Imported from India (BIPTC) | MkWh | 446.9896 | " | 6.197%
| E) Total Imported from Tripura, India (A.C) | MkWh | 88.4515 | " | 1.226%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4237.6738 | % of total Gen. | 58.75%
| B) Oil | MkWh | 1657.7818 | '' | 22.98%
| C) Hydro | MkWh | 17.7881 | '' | 0.2466%
| D) Solar | MkWh | 146.7623 | '' | 2.035%
| E) Coal | MkWh | 617.702 | '' | 8.564%
| F) BIPTC (Import from India) | MkWh | 446.9896 | '' | 6.197%
| G) A.C (Import from Tripura, India) | MkWh | 88.4515 | '' | 1.226%
16 | Maximun of the daily total Generation . | MkWh | 270.0924 | 2023-03-28
17 | Monthly Load factor | % | 84.1419 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 26947.403 | - | -
| A) Gas | M.Taka | 4582.8494 | - | -
| B) Liquid fuel | M.Taka | 13978.227 | - | -
| C) Coal | M.Taka | 5796.1311 | - | -
| D) BIPTC (Import from India) | M.Taka | 1953.3445 | - | -
| E) Tripura(Import from India) | M.Taka | 636.8509 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1154.3072 | 2023-03-21
| A) Gas | M.Taka | 166.2702 | 2023-03-03
| B) Liquid fuel | M.Taka | 798.7999 | 2023-03-21
| C) Coal | M.Taka | 277.4667 | 2023-03-11
| D) BIPTC (Import from India) | M.Taka | 94.7734 | 2023-03-23
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 5.4204
| B) Excluding Hydro & Solar | Taka/kWhR | 5.5447
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 88.17 | 31/03/2023 | 06:00
b) | Actual | FT (MSL) | 76.02 | 31/03/2023 | 06:00
22 | Peak Genaration of March 2022 | MW | 13662 | 31/03/2022 | 19:30
23 | Peak Demand of March 2022 | MW | 13662 | 31/03/2022 | 19:30
24 | Maximum peak Generation recorded till date | MW | 15648 | 2023-04-19 | 21:00
25 | Maximum peak Demand recorded till date | MW | 16096 | 2023-04-19 | 21:00
26 | Maximum load shed recorded till date | MW | 7852 | 2022-10-04 | 15:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## FGMO
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220
6 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
7 | Meghnaghat CCPP(Summit) | IPP | 335 | √ | [14 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
8 | Ashuganj 450 MW CCPP(North) | APSCL | 360 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ |  |  |  | √ | √ | √
9 | Ashuganj 225 MW CCPP | APSCL | 221 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
10 | Bheramara 410 MW CCPP | NWPGCL | 410
11 | Haripur 412 MW CCPP | EGCB | 412
12 | Fenchugonj CCPP Phase-1 | BPDB | 97
13 | Chandpur 150 MW CCPP | BPDB | 163
14 | Siddhirganj 2x120 MW GTPP | EGCB | 210
15 | Shikalbaha 225 MW CCPP | BPDB | 225
16 | Shikalbaha Peaking GT | BPDB | 150
17 | Shahjibazar 330 MW CCPP | BPDB | 330
18 | Ashuganj 450 MW CCPP(South) | APSCL | 360
19 | Fenchugonj CCPP Phase-2 | BPDB | 104
20 | Bhola 225 MW CCPP | BPDB | 194
21 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
22 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
23 | Siddhirganj 335 MW CCPP | EGCB | 335
24 | Bibiyana-III 400 MW CCPP | BPDB | 400 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
25 | Sylhet 225 MW CCPP | BPDB | 231
26 | RPCL 210 MW CCPP | IPP | 210
27 | Khulna 225 MW CCPP | NWPGCL | 230
28 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
29 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
30 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
31 | Bibiyana South 400 MW CCPP | BPDB | 383
32 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
33 | Shajibazar 100 MW PP | BPDB | 100
34 | Payra 1320 MW Unit-1 | BCPCL | 622
35 | Kushiara 163 MW CCPP (KP) | IPP | 163
36 | Haripur 360MW CCPP(HPL) | IPP | 360
37 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450
38 | Ashuganj 420 MW CCPP(East) | APSCL | 400 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | [6 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
39 | Ashuganj 55 MW PP (Precision) | QRPP | 55 | [18 empty] | √
due to gas shortage