## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-05-18 | Thursday
|  | Date (day): | 2023-05-18 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11573.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13254 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-05-17 | 2023-05-18 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 392 | 401 | 380 | 380 | 32 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 342 | 313 | 340 | 340 | 20 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 8 | 8 | 8 | 92 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 52 | 320 | 320 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 5 | 79 | 17 | 85 |  | 17 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 5 | 15 | 0 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 20 | 4 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 15 | 19 | 19
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 103 | 0 | 0 |  | 210 | GT-1 Under maint & Gas Shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 7 | 18 | 16 | 17 | 83 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 50 | 24 | 50 | 52 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 0 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 150 | 100 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 35 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 40 | 42 | 48 | 48 |  | 32 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 22 | 33 | 20 | 20 |  | 13 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 50 | 16 | 48
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 32 | 195 | 45 | 195 | 105 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 40 | 40 | 60 |  | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 40 | 50 |  | 50 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 86 | 132 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 88 | 88 | 88 |  | 17 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 50 | 17 | 53 | 51 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 108 | 72 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 35 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 34 | 17 | 34 | 21 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5867 | 1998 | 2826 | 2959 | 3539 | 1089 | 1204
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 25 | 25 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 19 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 44 | 6 | 40 | 10 |  | Fuel shortage
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 25 | 25 | 25 | 50 | 205 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 71 | 151 | 145 | 150 | 75 |  | Gas shortage
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 87 | 17 | 87 | 18 |  | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 34 | 66 | 54 | 58 |  | 40 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 82 | 84 | 67 | 84 |  | 18 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 92 | 22 | 100 | 22 | 78 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 11 | 6 | 10 | 11 | 11 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 17 | 5 | 10
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 30 | 0 | 30 | 78 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 86 | 275 | 88 | 300
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 54 | 106 | 54 | 105 |  | 5 | Engine problem
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 17 | 99 |  | Fuel shortage
| Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 36 | 78 | 35 | 163 |  |  | On test.
| Chattogram area Total |  |  |  |  | 2605 | 2545 | 649 | 1100 | 740 | 1219 | 941 | 393
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 178 | 180 | 200 | 200 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 310 | 350 | 350 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 39 | 40 | 40 | 40
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 120 | 148 | 120 | 125 | 70 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 25 | 43 | 43 | 43 |  | 8 | Engine problem
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 16 | 150 | 20 | 150
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 37 | 36 | 35 | 35 |  | 17 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 17 | 17 | 17 | 183 |  | Fuel shortage
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 14 | 18 | 18 |  | 4 | Engine problem
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 6 | 5 | 7 |  | 4 | Engine problem
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 108 | 144 | 129 | 152
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 25 | 25 | 25 |  | 8 | Engine problem
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 0 | 52
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 0 | 18 | 21 | 21 |  | 4 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Contract Expired
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 70 | 114 | 114
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 26 | 95 | 26 | 113
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 35 | 35 | 35 |  | 19 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 54 | 108 | 54 | 115
| Cumilla Area Total |  |  |  |  | 3159 | 3096 | 947 | 1491 | 1252 | 1612 | 253 | 987
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 43 | 52 | 42 | 80 | 122 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 18 | 17 | 17 | 5 |  | Gas shortage
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 47 | 84 | 48 | 85 | 115 |  | Fuel shortage
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 47 | 88 | 47 | 88 | 27 |  | Fuel shortage
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 55 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 5 | 12 | 12 | 12 | 10 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 199 | 254 | 217.6 | 282 | 127 | 0
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 0 | 29 |  | 61 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 50 | 51 | 51
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 40 | 50 | 44 | 50
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 3 | 8 |  | 3 | Engine problem
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 63 | 61 | 61
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 72 | 77 | 84 | 84
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 207 | 207 | 210 | 210 |  | 21 | Machine problem
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 17 | 18
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 8 | 8 | 17 |  | Gas shortage
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 290 | 290 | 300 |  |  | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 367 | 367 | 400 | 400 |  |  | FGMO
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 378 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1604 | 1608 | 1621 | 1672 | 17 | 705
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 911 | 910 | 925 | 925
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 16 | 66 | 83 |  | 32 | Engine problem
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 20 | 43 |  | 11 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 60 | 70 |  | 39 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 24 | 40
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 17 | 17 | 88 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 50 | 85 | 105
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 105 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 181 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 318 | 370 | 330 | 330 |  |  | Coal Shortage.
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 2905 | 2901 | 1515 | 1363 | 1627 | 1613 | 744 | 82
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 0 | 16 | 94 |  | Fuel shortage
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 14 | 25 | 22 | 35 |  | 5 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 180 | 163 | 130 | 130
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 500 | 1020 | 1244 | 1244
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maintenance
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 150
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 153 | 152 | 150 | 150
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 847 | 1376 | 1563 | 1725 | 94 | 225
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 28 | 28 |  | 24 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 13 | 15 | 35 |  | 36 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 28 | 0 | 28 | 21 | 21
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 24 | 40 |  | 10 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 152 | 160 | 170 | 170 | 40 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 158 | 0 | 0 | 220 |  | Gas shortage
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 401 | 313 | 400 | 400
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 28 | 34 |  | 16 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 19 | 21 | 20 | 20
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 8 | 8 |  | 3 | Engine problem
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 30 | 52
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 82 | 80 | 80 |  | 24 | Enginr problem
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 35 | 50 | 63 |  | Fuel shortage
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 57 | 35 | 55 | 58 |  | Fuel shortage
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 748*1 | 748 | 748 | 397 | 400 | 0 | 0 |  |  | On test.
| Rajshahi Area Total |  |  |  |  | 2927 | 2905 | 1117 | 1412 | 942 | 1035 | 972 | 121
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 75 | 73 | 75 | 75 | 10 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 220 | 260 | 260 | 260
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 78 | 34 | 107 | 6 |  | Fuel shortage
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 109 | 115 | 115
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 35 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 166 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 500 | 520 | 652 | 557 | 56 | 85
| Total |  |  |  |  | 24143 | 23370 | 9376 | 11950 | 11573.6 | 13254 | 4293 | 3802
A. |  | 2023-05-17 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 11950 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 8469 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11950 | MW
3 | Day peak Generation : |  |  | 9376 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11369.48 | MW
4 | Evening peak Generation : |  |  | 11950 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 237.5124 | MKWHr | By Solar | 2.3298 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 117.7961 | MKWHr |  | By Oil: | 43.7531 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 49.5031 | MKWHr |  | By Hydro: | 0.304 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4293 | MW | Dhaka | 4429.18 | 4429.18 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3802 | MW | Chittagong | 1118.7 | 1118.7 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 8095 | MW | Khulna | 963.6 | 963.6 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 860.58 | MMCFD |  |  | Rajshahi | 1296.4 | 1296.4 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 132976150.036 | ii) Oil : | Taka | 596811067.22 | Comilla | 1052 | 1052 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 215656424.87 | Total | Taka | 945443642.126 | Mymensingh | 905 | 905 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 455 | 455 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 1664 | MW (E to W) at | 19:30 | hrs | Barisal | 361.6 | 361.6 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 432 | MW at | 23:00 | hrs | Rangpur | 788 | 788 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31.1° C |  |  | Total | 11369.48 | 11369.48 |  | 0
B. |  | 2023-05-18 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 31.1° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13254 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9400 | MW
4 | Reserve(Generation end) |  |  |  | 754 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 248.444 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 4959 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.8502 | MKWHr. | ii) HVDC Flow at Peak Time |  | 910 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.976 | MKWHr. | iii) Maximum HVDC Flow : |  | 911 | MW at | 3:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 73.79 |  | (b) Today: | 73.74 |  | (c) Rule Curve: |  | 78.96
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-05-17 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 146 | 341 |  | 0 | 450 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 9 | 16 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 15 | 23 | 27 | 25 | 32 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 |  | 12 | 55 | 79 | 10 | 0 | 6 | 11 | 26 | 0 | 0 | 0 | 340 | 0 | 202 | 197 | 0 | 42 | 0 | 0 | 43 | 0 | 37 | 0 | 0 | 4 | 0 | 18 | 130 | 85 | 0 | 18 | 0 | 43 | 28 | 53 | 50 | 0 | 0 | 56 | 72 | 0 | 204 | 18 | 0 | 10 | 290 | 16 | 8 | 0 | 47 | 254 | 40 | 47 | 40 | 17 | 0 | 12 | 17 | 80 | 400 | 28 | 88 | 17 | 0 | 87 | 17 | 54 | 52 | 8 | 12 | 400 | 17 | 0 | 17 | 17 | 0 | 35 | 0 | 22 | 17 | 0 | 17 | 0 |  | 816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 16 | 0 | 22 | 0 | 5 | 73 | 0 | 260 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 415 | 0 | 0 | 35 | 0 | 33 | 0 | 0 | 35 | 750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 203 | 436 | 0 | 0 |  | 5657 | 4030 | 9687 | 2990 | 816 | 1969 | 334 | 982 | 2095 | 0 | 151 | 220 | 130 | 0 | 0 | 73.8
2:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 202 | 336 |  | 0 | 450 | 0 | 9 | 17 | 0 | 0 | 0 | 0 | 9 | 16 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 15 | 23 | 27 | 25 | 32 | 8 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 151 | 0 | 0 |  | 12 | 55 | 84 | 10 | 0 | 6 | 11 | 20 | 0 | 0 | 0 | 310 | 0 | 179 | 197 | 0 | 42 | 0 | 0 | 34 | 0 | 37 | 0 | 0 | 4 | 0 | 18 | 130 | 85 | 0 | 18 | 0 | 43 | 28 | 53 | 47 | 0 | 0 | 57 | 72 | 0 | 204 | 18 | 0 | 10 | 285 | 16 | 8 | 0 | 47 | 140 | 28 | 47 | 40 | 17 | 0 | 12 | 17 | 18 | 366 | 28 | 88 | 17 | 0 | 87 | 0 | 54 | 52 | 9 | 12 | 400 | 17 | 0 | 17 | 17 | 0 | 35 | 0 | 18 | 17 | 0 | 17 | 0 |  | 853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 34 | 20 | 43 | 32 | 22 | 0 | 5 | 72 | 0 | 260 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 418 | 0 | 0 | 35 | 0 | 27 | 0 | 0 | 35 | 770 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 221 | 384 | 0 | 0 |  | 5433 | 4157 | 9590 | 2958 | 853 | 1954 | 208 | 947 | 2080 | 0 | 151 | 309 | 130 | 0 | 0 | 73.8
3:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 205 | 343 |  | 0 | 450 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 9 | 16 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 15 | 23 | 25 | 25 | 32 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 |  | 12 | 55 | 84 | 10 | 0 | 6 | 11 | 25 | 0 | 0 | 0 | 310 | 0 | 179 | 199 | 0 | 42 | 0 | 0 | 34 | 0 | 37 | 0 | 0 | 4 | 0 | 18 | 128 | 98 | 0 | 18 | 0 | 43 | 28 | 53 | 47 | 0 | 0 | 57 | 72 | 0 | 203 | 18 | 0 | 10 | 290 | 16 | 8 | 0 | 47 | 10 | 11 | 47 | 0 | 17 | 0 | 12 | 17 | 20 | 366 | 28 | 88 | 17 | 0 | 87 | 0 | 54 | 52 | 9 | 12 | 400 | 17 | 0 | 17 | 17 | 0 | 35 | 0 | 18 | 17 | 0 | 17 | 0 |  | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 11 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 21 | 34 | 40 | 52 | 32 | 22 | 0 | 5 | 74 | 0 | 260 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 417 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 202 | 407 | 0 | 0 |  | 5281 | 4164 | 9445 | 2971 | 911 | 1973 | 21 | 897 | 2036 | 0 | 151 | 357 | 128 | 0 | 0 | 73.8
4:00 | 0 | 0 | 119 | 180 | 0 | 0 | 0 | 248 | 352 |  | 0 | 450 | 0 | 9 | 17 | 0 | 0 | 0 | 0 | 9 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 23 | 25 | 25 | 32 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 |  | 12 | 24 | 34 | 10 | 0 | 6 | 11 | 26 | 0 | 0 | 0 | 310 | 0 | 180 | 199 | 0 | 42 | 0 | 0 | 34 | 0 | 37 | 0 | 0 | 4 | 0 | 18 | 124 | 99 | 0 | 18 | 0 | 43 | 28 | 53 | 47 | 0 | 0 | 57 | 72 | 0 | 203 | 18 | 0 | 10 | 285 | 16 | 8 | 0 | 15 | 0 | 0 | 46 | 0 | 17 | 0 | 12 | 17 | 20 | 367 | 28 | 51 | 17 | 0 | 87 | 0 | 54 | 52 | 9 | 12 | 386 | 17 | 0 | 17 | 17 | 0 | 35 | 0 | 18 | 17 | 0 | 17 | 0 |  | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 11 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 21 | 8 | 40 | 8 | 32 | 22 | 0 | 5 | 76 | 0 | 260 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 416 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 201 | 406 | 0 | 0 |  | 5059 | 3956 | 9015 | 2984 | 911 | 1977 | 0 | 704 | 1936 | 0 | 151 | 228 | 124 | 0 | 0 | 73.8
5:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 318 | 351 |  | 0 | 450 | 0 | 9 | 17 | 0 | 0 | 0 | 0 | 9 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 23 | 25 | 25 | 32 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 80 | 0 | 0 |  | 12 | 24 | 34 | 10 | 0 | 6 | 11 | 33 | 0 | 0 | 0 | 310 | 0 | 180 | 199 | 0 | 43 | 0 | 0 | 34 | 0 | 37 | 0 | 0 | 4 | 0 | 18 | 116 | 99 | 0 | 18 | 0 | 43 | 28 | 22 | 47 | 0 | 0 | 45 | 30 | 0 | 205 | 18 | 0 | 10 | 285 | 16 | 8 | 0 | 15 | 0 | 0 | 46 | 0 | 17 | 0 | 12 | 17 | 20 | 367 | 28 | 17 | 17 | 0 | 45 | 3 | 17 | 52 | 9 | 12 | 400 | 17 | 0 | 17 | 17 | 0 | 35 | 0 | 17 | 17 | 0 | 17 | 0 |  | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 11 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 21 | 8 | 40 | 8 | 32 | 22 | 0 | 5 | 76 | 0 | 260 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 153 | 402 | 0 | 0 |  | 4878 | 3710 | 8588 | 3009 | 910 | 1823 | 0 | 579 | 1843 | 0 | 80 | 228 | 116 | 0 | 0 | 73.79
6:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 322 | 302 |  | 0 | 450 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 9 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 23 | 25 | 25 | 32 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 61 | 0 | 0 |  | 12 | 24 | 33 | 10 | 0 | 6 | 11 | 33 | 0 | 0 | 0 | 325 | 0 | 191 | 189 | 0 | 42 | 0 | 0 | 34 | 0 | 37 | 0 | 0 | 4 | 0 | 20 | 110 | 99 | 0 | 18 | 0 | 43 | 28 | 22 | 47 | 0 | 0 | 45 | 30 | 0 | 206 | 18 | 0 | 10 | 290 | 16 | 8 | 0 | 15 | 0 | 0 | 46 | 0 | 17 | 0 | 12 | 17 | 20 | 375 | 28 | 17 | 17 | 0 | 45 | 17 | 17 | 17 | 9 | 12 | 360 | 17 | 5 | 17 | 17 | 0 | 35 | 2 | 18 | 17 | 0 | 17 | 0 |  | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 11 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 21 | 8 | 40 | 8 | 32 | 22 | 0 | 5 | 77 | 0 | 260 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 372 | 0 | 152 | 407 | 0 | 0 |  | 4784 | 3697 | 8481 | 3010 | 911 | 1807 | 0 | 558 | 1788 | 0 | 61 | 227 | 110 | 9 | 0 | 73.79
7:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 322 | 302 |  | 0 | 450 | 0 | 9 | 17 | 0 | 0 | 0 | 0 | 9 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 23 | 25 | 25 | 25 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 31 | 0 | 0 |  | 12 | 24 | 33 | 10 | 0 | 6 | 11 | 17 | 0 | 0 | 0 | 310 | 0 | 186 | 138 | 0 | 42 | 0 | 0 | 34 | 0 | 37 | 0 | 0 | 4 | 0 | 9 | 110 | 46 | 0 | 18 | 0 | 43 | 28 | 22 | 47 | 0 | 0 | 45 | 30 | 0 | 207 | 17 | 0 | 10 | 290 | 16 | 8 | 0 | 15 | 0 | 0 | 46 | 0 | 17 | 0 | 12 | 17 | 20 | 367 | 28 | 17 | 17 | 1 | 45 | 17 | 17 | 17 | 9 | 12 | 400 | 22 | 3 | 17 | 17 | 0 | 20 | 5 | 18 | 17 | 0 | 17 | 0 |  | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 10 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 28 | 8 | 40 | 8 | 32 | 16 | 0 | 0 | 77 | 0 | 260 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 430 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 35 | 520 | 0 | 0 | 0 | 0 | 14 | 0 | 25 | 0 | 372 | 0 | 152 | 403 | 14 | 0 |  | 4621 | 3851 | 8472 | 2946 | 911 | 1796 | 0 | 605 | 1784 | 0 | 56 | 227 | 110 | 37 | 0 | 73.79
8:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 322 | 302 |  | 0 | 450 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 9 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 23 | 25 | 25 | 30 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 31 | 0 | 0 |  | 12 | 24 | 33 | 10 | 0 | 6 | 11 | 7 | 0 | 0 | 0 | 305 | 0 | 179 | 138 | 0 | 42 | 0 | 0 | 34 | 0 | 37 | 0 | 0 | 4 | 0 | 21 | 126 | 46 | 0 | 19 | 0 | 43 | 28 | 22 | 47 | 0 | 0 | 45 | 30 | 0 | 207 | 17 | 0 | 10 | 285 | 16 | 0 | 0 | 15 | 0 | 0 | 46 | 0 | 17 | 8 | 12 | 17 | 20 | 367 | 28 | 17 | 17 | 3 | 45 | 17 | 17 | 17 | 9 | 12 | 400 | 17 | 0 | 17 | 17 | 0 | 17 | 6 | 18 | 17 | 0 | 17 | 0 |  | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 10 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 28 | 8 | 40 | 8 | 32 | 16 | 0 | 0 | 76 | 0 | 260 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 436 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 510 | 0 | 0 | 0 | 0 | 51 | 0 | 22 | 0 | 371 | 9 | 154 | 412 | 49 | 0 |  | 4619 | 3989 | 8608 | 2944 | 911 | 1787 | 0 | 651 | 1783 | 0 | 53 | 227 | 126 | 126 | 0 | 0
9:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 359 | 297 |  | 0 | 400 | 0 | 9 | 17 | 0 | 0 | 0 | 0 | 9 | 16 | 32 | 11 | 0 | 0 | 0 | 0 | 17 | 0 | 15 | 23 | 27 | 0 | 28 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 31 | 0 | 0 |  | 0 | 32 | 33 | 10 | 0 | 6 | 11 | 5 | 0 | 0 | 0 | 280 | 0 | 150 | 138 | 0 | 38 | 0 | 0 | 34 | 0 | 36 | 0 | 0 | 4 | 0 | 21 | 122 | 47 | 0 | 0 | 0 | 43 | 29 | 47 | 46 | 0 | 0 | 63 | 66 | 0 | 207 | 18 | 0 | 10 | 265 | 16 | 0 | 0 | 37 | 0 | 0 | 8 | 0 | 18 | 15 | 12 | 17 | 20 | 367 | 8 | 30 | 17 | 4 | 85 | 17 | 19 | 52 | 9 | 12 | 400 | 17 | 1 | 17 | 17 | 0 | 17 | 1 | 18 | 17 | 0 | 17 | 0 |  | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 10 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 15 | 0 | 32 | 21 | 0 | 0 | 75 | 0 | 260 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 308 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 65 | 0 | 69 | 0 | 372 | 15 | 152 | 402 | 94 | 0 |  | 4653 | 3816 | 8469 | 2899 | 911 | 1647 | 0 | 609 | 1761 | 0 | 100 | 225 | 122 | 195 | 0 | 0
10:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 329 | 272 |  | 0 | 330 | 0 | 8 | 7 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 76 | 0 | 0 |  | 0 | 40 | 52 | 10 | 0 | 6 | 11 | 2 | 0 | 0 | 0 | 280 | 0 | 152 | 68 | 0 | 38 | 0 | 0 | 5 | 0 | 37 | 0 | 0 | 4 | 0 | 12 | 136 | 46 | 0 | 0 | 0 | 43 | 29 | 5 | 5 | 0 | 0 | 40 | 0 | 0 | 200 | 18 | 0 | 9 | 210 | 16 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 24 | 16 | 12 | 17 | 10 | 317 | 0 | 2 | 24 | 4 | 85 | 17 | 51 | 38 | 15 | 12 | 340 | 17 | 5 | 17 | 17 | 0 | 0 | 30 | 19 | 0 | 0 | 17 | 0 |  | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 76 | 0 | 249 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 500 | 0 | 0 | 0 | 4 | 82 | 0 | 114 | 0 | 372 | 14 | 152 | 400 | 97 | 0 |  | 3988 | 3736 | 7724 | 2673 | 910 | 1221 | 0 | 446 | 1749 | 0 | 190 | 146 | 136 | 253 | 0 | 0
11:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 346 | 353 |  | 0 | 420 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 23 | 0 | 25 | 15 | 0 | 0 | 0 | 25 | 0 | 0 | 8 | 0 | 50 | 0 | 0 |  | 0 | 32 | 84 | 100 | 0 | 6 | 11 | 3 | 0 | 0 | 0 | 310 | 0 | 183 | 70 | 0 | 36 | 0 | 0 | 17 | 0 | 38 | 0 | 0 | 6 | 0 | 0 | 54 | 44 | 0 | 0 | 0 | 43 | 29 | 22 | 17 | 0 | 0 | 57 | 50 | 0 | 209 | 17 | 0 | 9 | 220 | 16 | 0 | 0 | 15 | 0 | 0 | 16 | 0 | 20 | 0 | 12 | 17 | 10 | 366 | 14 | 11 | 34 | 5 | 85 | 17 | 51 | 17 | 26 | 25 | 400 | 17 | 11 | 54 | 17 | 0 | 16 | 34 | 50 | 2 | 0 | 36 | 0 |  | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 76 | 0 | 220 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 500 | 0 | 0 | 0 | 3 | 98 | 0 | 183 | 0 | 368 | 17 | 155 | 393 | 97 | 0 |  | 4676 | 3844 | 8520 | 2891 | 911 | 1548 | 0 | 690 | 1712 | 25 | 233 | 190 | 54 | 266 | 0 | 0
12:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 392 | 342 |  | 0 | 450 | 0 | 8 | 5 | 5 | 0 | 0 | 0 | 7 | 24 | 48 | 4 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 23 | 17 | 25 | 22 | 0 | 0 | 0 | 25 | 0 | 0 | 8 | 0 | 71 | 0 | 0 |  | 5 | 34 | 82 | 92 | 0 | 6 | 11 | 2 | 0 | 0 | 0 | 310 | 0 | 178 | 120 | 0 | 39 | 0 | 0 | 25 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 108 | 43 | 0 | 0 | 2 | 43 | 30 | 50 | 40 | 0 | 0 | 63 | 72 | 0 | 207 | 17 | 0 | 9 | 290 | 16 | 0 | 0 | 32 | 0 | 0 | 47 | 0 | 86 | 19 | 25 | 17 | 16 | 367 | 47 | 50 | 34 | 5 | 86 | 17 | 54 | 0 | 26 | 25 | 400 | 17 | 55 | 54 | 17 | 0 | 17 | 35 | 54 | 17 | 0 | 36 | 0 |  | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 5 | 75 | 0 | 220 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 500 | 0 | 0 | 0 | 3 | 105 | 0 | 181 | 0 | 318 | 35 | 153 | 397 | 166 | 0 |  | 5397 | 3979 | 9376 | 2980 | 911 | 1834 | 0 | 937 | 1663 | 25 | 252 | 237 | 108 | 429 | 0 | 0
13:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 394 | 331 |  | 0 | 450 | 0 | 12 | 17 | 15 | 0 | 0 | 0 | 9 | 24 | 98 | 18 | 0 | 0 | 0 | 0 | 35 | 10 | 0 | 23 | 25 | 33 | 22 | 6 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 71 | 0 | 0 |  | 8 | 40 | 83 | 22 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 315 | 0 | 182 | 120 | 0 | 42 | 0 | 0 | 34 | 0 | 37 | 0 | 0 | 0 | 0 | 3 | 112 | 43 | 0 | 15 | 2 | 43 | 30 | 50 | 47 | 0 | 0 | 63 | 74 | 0 | 207 | 17 | 0 | 9 | 285 | 16 | 0 | 0 | 47 | 0 | 0 | 47 | 0 | 133 | 18 | 25 | 17 | 20 | 356 | 47 | 88 | 34 | 2 | 87 | 17 | 54 | 0 | 26 | 25 | 400 | 19 | 52 | 54 | 17 | 0 | 17 | 33 | 55 | 17 | 0 | 36 | 0 |  | 911 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 180 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 18 | 0 | 18 | 0 | 8 | 72 | 0 | 220 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 416 | 17 | 0 | 10 | 0 | 0 | 0 | 5 | 35 | 580 | 0 | 0 | 0 | 5 | 83 | 12 | 0 | 0 | 370 | 21 | 153 | 395 | 105 | 0 |  | 5578 | 4002 | 9580 | 3052 | 911 | 1844 | 0 | 1155 | 1790 | 25 | 71 | 294 | 112 | 326 | 0 | 0
14:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 397 | 326 |  | 0 | 450 | 0 | 11 | 17 | 0 | 0 | 0 | 0 | 9 | 24 | 98 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 19 | 23 | 27 | 33 | 30 | 8 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 71 | 0 | 0 |  | 12 | 48 | 77 | 22 | 12 | 6 | 8 | 2 | 0 | 0 | 0 | 335 | 0 | 198 | 128 | 0 | 41 | 0 | 0 | 34 | 0 | 37 | 6 | 0 | 0 | 0 | 3 | 114 | 33 | 0 | 15 | 2 | 43 | 29 | 50 | 50 | 0 | 0 | 61 | 74 | 0 | 207 | 17 | 0 | 9 | 285 | 16 | 2 | 0 | 47 | 0 | 0 | 47 | 0 | 48 | 14 | 25 | 17 | 20 | 397 | 47 | 88 | 34 | 0 | 86 | 17 | 54 | 0 | 28 | 25 | 395 | 33 | 47 | 54 | 17 | 0 | 17 | 29 | 59 | 17 | 0 | 36 | 0 |  | 909 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 16 | 179 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 25 | 0 | 18 | 0 | 8 | 72 | 0 | 220 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 390 | 17 | 0 | 35 | 34 | 5 | 0 | 5 | 35 | 840 | 0 | 0 | 0 | 3 | 67 | 35 | 0 | 0 | 372 | 22 | 153 | 393 | 95 | 0 |  | 5612 | 4333 | 9945 | 3153 | 909 | 1822 | 0 | 1221 | 2050 | 25 | 71 | 296 | 114 | 284 | 0 | 0
15:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 399 | 327 |  | 0 | 450 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 9 | 24 | 98 | 8 | 0 | 0 | 0 | 0 | 35 | 35 | 19 | 23 | 27 | 0 | 30 | 8 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 152 | 0 | 0 |  | 12 | 40 | 84 | 22 | 12 | 2 | 10 | 2 | 0 | 0 | 0 | 345 | 0 | 203 | 128 | 0 | 40 | 0 | 0 | 34 | 0 | 37 | 12 | 0 | 6 | 0 | 9 | 124 | 33 | 0 | 15 | 1 | 43 | 30 | 50 | 47 | 0 | 0 | 61 | 74 | 0 | 202 | 17 | 0 | 9 | 285 | 16 | 8 | 0 | 47 | 270 | 0 | 47 | 0 | 17 | 13 | 25 | 17 | 20 | 402 | 47 | 88 | 34 | 0 | 87 | 17 | 54 | 0 | 28 | 25 | 390 | 43 | 37 | 54 | 17 | 0 | 17 | 0 | 55 | 17 | 0 | 36 | 0 |  | 909 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 16 | 180 | 12 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 28 | 0 | 0 | 52 | 0 | 19 | 0 | 8 | 70 | 0 | 170 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 360 | 17 | 0 | 35 | 50 | 33 | 0 | 0 | 35 | 950 | 0 | 0 | 3 | 3 | 73 | 35 | 0 | 0 | 369 | 16 | 152 | 389 | 109 | 0 |  | 5911 | 4479 | 10390 | 3154 | 909 | 1797 | 270 | 1308 | 2100 | 25 | 152 | 299 | 124 | 252 | 0 | 73.77
16:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 403 | 328 |  | 0 | 450 | 10 | 9 | 17 | 0 | 0 | 0 | 0 | 9 | 32 | 98 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 20 | 23 | 27 | 25 | 33 | 8 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 150 | 0 | 0 |  | 12 | 32 | 67 | 22 | 12 | 12 | 5 | 2 | 0 | 0 | 0 | 350 | 0 | 205 | 128 | 0 | 37 | 0 | 0 | 34 | 0 | 37 | 36 | 0 | 6 | 0 | 9 | 128 | 33 | 0 | 15 | 1 | 43 | 30 | 50 | 47 | 0 | 0 | 61 | 74 | 0 | 200 | 17 | 0 | 9 | 285 | 16 | 8 | 0 | 47 | 300 | 40 | 47 | 40 | 17 | 7 | 25 | 17 | 20 | 404 | 47 | 88 | 51 | 0 | 88 | 17 | 66 | 17 | 28 | 25 | 385 | 53 | 14 | 54 | 17 | 0 | 17 | 13 | 54 | 17 | 0 | 36 | 0 |  | 910 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 16 | 180 | 13 | 16 | 0 | 0 | 0 | 0 | 6 | 44 | 28 | 25 | 0 | 52 | 0 | 19 | 0 | 8 | 70 | 0 | 170 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 328 | 17 | 0 | 35 | 50 | 33 | 0 | 3 | 35 | 980 | 0 | 0 | 17 | 2 | 27 | 35 | 0 | 0 | 375 | 6 | 153 | 407 | 55 | 0 |  | 6128 | 4492 | 10620 | 3174 | 910 | 1777 | 380 | 1473 | 2155 | 25 | 150 | 320 | 128 | 128 | 0 | 73.77
17:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 405 | 327 |  | 0 | 450 | 10 | 8 | 17 | 0 | 0 | 0 | 0 | 9 | 33 | 98 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 20 | 23 | 27 | 33 | 33 | 8 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 151 | 0 | 0 |  | 12 | 32 | 84 | 22 | 17 | 19 | 6 | 2 | 0 | 0 | 0 | 320 | 0 | 183 | 147 | 0 | 37 | 0 | 0 | 34 | 0 | 30 | 50 | 9 | 6 | 0 | 9 | 124 | 44 | 0 | 15 | 1 | 43 | 30 | 50 | 47 | 0 | 0 | 59 | 74 | 0 | 200 | 17 | 0 | 9 | 285 | 16 | 8 | 0 | 47 | 151 | 40 | 47 | 40 | 17 | 1 | 25 | 17 | 25 | 380 | 58 | 88 | 51 | 0 | 87 | 17 | 93 | 114 | 28 | 25 | 394 | 53 | 7 | 54 | 17 | 0 | 17 | 6 | 54 | 30 | 0 | 36 | 0 |  | 910 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 16 | 180 | 19 | 16 | 0 | 0 | 0 | 28 | 17 | 73 | 28 | 25 | 24 | 52 | 10 | 19 | 0 | 8 | 70 | 0 | 170 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 319 | 17 | 0 | 35 | 50 | 33 | 0 | 2 | 35 | 930 | 0 | 0 | 17 | 0 | 24 | 35 | 0 | 0 | 370 | 4 | 153 | 416 | 19 | 0 |  | 6089 | 4495 | 10584 | 3130 | 910 | 1792 | 231 | 1616 | 2109 | 25 | 151 | 432 | 124 | 64 | 0 | 73.77
18:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 402 | 273 |  | 0 | 450 | 10 | 9 | 20 | 0 | 0 | 0 | 0 | 10 | 33 | 115 | 0 | 0 | 0 | 0 | 35 | 55 | 0 | 20 | 23 | 20 | 33 | 33 | 50 | 0 | 0 | 25 | 0 | 0 | 1 | 0 | 115 | 0 | 0 |  | 12 | 56 | 84 | 22 | 30 | 0 | 6 | 4 | 0 | 0 | 0 | 290 | 0 | 180 | 147 | 0 | 37 | 0 | 0 | 34 | 0 | 30 | 52 | 14 | 6 | 25 | 9 | 122 | 44 | 0 | 15 | 0 | 43 | 30 | 50 | 50 | 0 | 0 | 62 | 77 | 0 | 201 | 17 | 0 | 9 | 285 | 16 | 11 | 0 | 57 | 0 | 0 | 56 | 0 | 40 | 0 | 25 | 17 | 37 | 319 | 58 | 88 | 75 | 0 | 121 | 17 | 94 | 114 | 28 | 25 | 400 | 53 | 1 | 54 | 17 | 0 | 17 | 0 | 54 | 34 | 0 | 36 | 0 |  | 910 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 8 | 180 | 17 | 16 | 0 | 0 | 0 | 28 | 28 | 74 | 28 | 8 | 40 | 52 | 29 | 19 | 0 | 8 | 70 | 0 | 225 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 258 | 17 | 0 | 35 | 15 | 33 | 0 | 1 | 35 | 800 | 0 | 0 | 35 | 0 | 5 | 35 | 0 | 0 | 375 | 1 | 153 | 404 | 5 | 0 |  | 5939 | 4288 | 10227 | 3067 | 910 | 1683 | 0 | 1745 | 2027 | 25 | 115 | 520 | 122 | 13 | 0 | 73.77
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 402 | 293 |  | 0 | 450 | 25 | 8 | 70 | 12 | 0 | 0 | 105 | 18 | 50 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 15 | 23 | 20 | 33 | 33 | 50 | 0 | 0 | 25 | 0 | 0 | 18 | 0 | 110 | 0 | 0 |  | 12 | 66 | 84 | 22 | 30 | 44 | 6 | 10 | 0 | 0 | 0 | 310 | 0 | 180 | 147 | 0 | 40 | 0 | 0 | 43 | 0 | 30 | 52 | 14 | 6 | 25 | 18 | 142 | 50 | 0 | 18 | 0 | 43 | 30 | 50 | 50 | 0 | 0 | 62 | 77 | 0 | 207 | 17 | 0 | 10 | 290 | 16 | 11 | 0 | 190 | 20 | 40 | 84 | 0 | 132 | 0 | 25 | 17 | 115 | 366 | 88 | 88 | 87 | 0 | 273 | 17 | 106 | 114 | 95 | 25 | 400 | 48 | 0 | 108 | 17 | 0 | 24 | 0 | 61 | 34 | 0 | 43 | 0 |  | 910 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 180 | 25 | 16 | 0 | 0 | 0 | 28 | 28 | 82 | 28 | 8 | 40 | 52 | 30 | 20 | 0 | 8 | 73 | 0 | 260 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 319 | 17 | 0 | 40 | 22 | 45 | 0 | 0 | 57 | 850 | 0 | 0 | 35 | 0 | 0 | 64 | 0 | 0 | 377 | 0 | 152 | 399 | 0 | 0 |  | 7146 | 4507 | 11653 | 3256 | 910 | 1809 | 60 | 2649 | 2111 | 25 | 110 | 581 | 142 | 0 | 0 | 73.76
19:30 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 401 | 313 |  | 0 | 450 | 52 | 8 | 79 | 15 | 0 | 0 | 103 | 18 | 50 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 15 | 22 | 20 | 33 | 33 | 50 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 151 | 0 | 0 |  | 12 | 66 | 84 | 22 | 30 | 44 | 6 | 17 | 0 | 0 | 0 | 310 | 0 | 180 | 148 | 0 | 40 | 0 | 0 | 43 | 0 | 36 | 52 | 14 | 6 | 25 | 18 | 144 | 52 | 0 | 18 | 0 | 43 | 30 | 50 | 50 | 0 | 0 | 63 | 77 | 0 | 207 | 17 | 0 | 9 | 290 | 16 | 11 | 0 | 195 | 0 | 0 | 84 | 0 | 132 | 0 | 25 | 17 | 150 | 367 | 88 | 88 | 87 | 0 | 275 | 17 | 106 | 70 | 95 | 25 | 378 | 50 | 0 | 108 | 17 | 0 | 35 | 0 | 108 | 34 | 0 | 78 | 0 |  | 910 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 25 | 16 | 0 | 0 | 0 | 0 | 13 | 82 | 28 | 0 | 40 | 52 | 30 | 21 | 0 | 8 | 73 | 0 | 260 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 313 | 17 | 0 | 50 | 50 | 78 | 0 | 0 | 57 | 1020 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0 | 370 | 0 | 152 | 400 | 0 | 0 |  | 7279 | 4671 | 11950 | 3217 | 910 | 1858 | 0 | 2791 | 2275 | 25 | 151 | 579 | 144 | 0 | 0 | 0
20:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 383 | 312 |  | 0 | 450 | 80 | 9 | 81 | 55 | 0 | 0 | 62 | 18 | 50 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 15 | 22 | 27 | 33 | 33 | 50 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 150 | 0 | 0 |  | 12 | 66 | 84 | 22 | 30 | 44 | 6 | 17 | 0 | 0 | 0 | 275 | 0 | 180 | 148 | 0 | 41 | 0 | 0 | 43 | 0 | 39 | 52 | 16 | 6 | 25 | 18 | 146 | 56 | 0 | 18 | 0 | 43 | 30 | 50 | 50 | 0 | 0 | 63 | 77 | 0 | 209 | 17 | 0 | 10 | 290 | 16 | 11 | 0 | 195 | 0 | 0 | 84 | 0 | 132 | 0 | 25 | 17 | 150 | 318 | 88 | 88 | 87 | 0 | 278 | 17 | 106 | 17 | 94 | 25 | 370 | 53 | 0 | 108 | 17 | 0 | 35 | 0 | 100 | 34 | 0 | 163 | 0 |  | 801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 40 | 52 | 30 | 22 | 0 | 8 | 73 | 0 | 260 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 253 | 17 | 0 | 50 | 15 | 86 | 0 | 0 | 57 | 900 | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 370 | 0 | 153 | 401 | 0 | 0 |  | 7248 | 4321 | 11569 | 3098 | 801 | 1827 | 0 | 2711 | 2157 | 25 | 150 | 654 | 146 | 0 | 0 | 73.76
21:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 315 | 353 |  | 0 | 450 | 130 | 8 | 85 | 55 | 0 | 0 | 40 | 18 | 50 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 15 | 22 | 27 | 33 | 33 | 50 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 130 | 0 | 0 |  | 12 | 57 | 84 | 22 | 30 | 44 | 6 | 22 | 0 | 0 | 0 | 285 | 0 | 184 | 158 | 0 | 42 | 0 | 0 | 43 | 0 | 39 | 52 | 16 | 6 | 25 | 20 | 136 | 82 | 0 | 18 | 0 | 43 | 30 | 50 | 50 | 0 | 0 | 62 | 77 | 0 | 212 | 17 | 0 | 10 | 290 | 16 | 11 | 0 | 195 | 0 | 0 | 84 | 0 | 133 | 0 | 25 | 17 | 155 | 322 | 89 | 88 | 87 | 0 | 279 | 17 | 106 | 17 | 96 | 25 | 400 | 53 | 0 | 108 | 17 | 0 | 35 | 0 | 115 | 34 | 0 | 163 | 0 |  | 802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 30 | 22 | 0 | 8 | 74 | 0 | 260 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 227 | 17 | 0 | 50 | 0 | 95 | 0 | 0 | 57 | 800 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 370 | 0 | 153 | 403 | 0 | 0 |  | 7332 | 4044 | 11376 | 3087 | 802 | 1907 | 0 | 2624 | 2060 | 25 | 130 | 605 | 136 | 0 | 0 | 73.76
22:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 333 | 353 |  | 0 | 450 | 130 | 9 | 55 | 0 | 0 | 0 | 41 | 18 | 50 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 15 | 22 | 27 | 33 | 33 | 42 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 150 | 0 | 0 |  | 12 | 57 | 84 | 10 | 30 | 44 | 6 | 29 | 0 | 0 | 0 | 280 | 0 | 180 | 158 | 0 | 42 | 0 | 0 | 43 | 0 | 39 | 52 | 17 | 6 | 25 | 18 | 140 | 72 | 0 | 0 | 0 | 43 | 30 | 50 | 50 | 0 | 0 | 63 | 77 | 0 | 212 | 17 | 0 | 10 | 295 | 16 | 11 | 0 | 195 | 0 | 0 | 84 | 0 | 132 | 0 | 25 | 17 | 155 | 343 | 89 | 88 | 87 | 0 | 122 | 17 | 106 | 17 | 103 | 25 | 400 | 36 | 0 | 108 | 17 | 0 | 35 | 0 | 115 | 34 | 0 | 36 | 0 |  | 802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 30 | 22 | 0 | 8 | 74 | 0 | 260 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 329 | 17 | 0 | 50 | 0 | 86 | 0 | 0 | 57 | 800 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 374 | 0 | 153 | 402 | 0 | 0 |  | 7010 | 4147 | 11157 | 3096 | 802 | 2022 | 0 | 2381 | 2063 | 25 | 150 | 478 | 140 | 0 | 0 | 73.76
23:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 404 | 350 |  | 0 | 450 | 150 | 8 | 17 | 0 | 0 | 0 | 102 | 10 | 24 | 98 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 15 | 22 | 27 | 33 | 33 | 42 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 150 | 0 | 0 |  | 12 | 57 | 84 | 22 | 21 | 44 | 6 | 29 | 0 | 0 | 0 | 335 | 0 | 209 | 168 | 0 | 42 | 0 | 0 | 43 | 0 | 39 | 52 | 17 | 6 | 25 | 15 | 138 | 74 | 0 | 18 | 0 | 43 | 30 | 50 | 50 | 0 | 0 | 63 | 78 | 0 | 211 | 17 | 0 | 10 | 290 | 16 | 11 | 0 | 195 | 0 | 0 | 28 | 0 | 56 | 0 | 12 | 17 | 62 | 390 | 49 | 88 | 87 | 0 | 88 | 17 | 106 | 114 | 32 | 12 | 400 | 26 | 0 | 79 | 17 | 0 | 35 | 0 | 57 | 35 | 0 | 36 | 0 |  | 802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 30 | 22 | 0 | 8 | 73 | 0 | 260 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 336 | 17 | 0 | 35 | 0 | 88 | 0 | 0 | 35 | 870 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 378 | 0 | 202 | 393 | 0 | 0 |  | 6756 | 4195 | 10951 | 3373 | 802 | 2050 | 0 | 1834 | 2176 | 0 | 150 | 428 | 138 | 0 | 0 | 73.76
24:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 405 | 350 |  | 0 | 450 | 145 | 9 | 17 | 0 | 0 | 0 | 102 | 9 | 24 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 15 | 23 | 27 | 33 | 33 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 |  | 12 | 57 | 84 | 10 | 0 | 6 | 6 | 38 | 0 | 0 | 0 | 315 | 0 | 198 | 168 | 0 | 42 | 0 | 0 | 43 | 0 | 39 | 52 | 17 | 6 | 25 | 18 | 134 | 74 | 0 | 18 | 0 | 43 | 30 | 50 | 50 | 0 | 0 | 62 | 78 | 0 | 208 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 195 | 0 | 0 | 28 | 0 | 17 | 0 | 12 | 17 | 20 | 375 | 49 | 88 | 87 | 0 | 87 | 17 | 67 | 114 | 9 | 12 | 400 | 17 | 0 | 17 | 17 | 0 | 35 | 0 | 36 | 21 | 0 | 36 | 0 |  | 804 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 180 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 16 | 0 | 0 | 30 | 22 | 0 | 5 | 74 | 0 | 260 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 330 | 17 | 0 | 35 | 0 | 88 | 0 | 0 | 35 | 1020 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 0 | 338 | 0 | 203 | 402 | 0 | 0 |  | 6265 | 4387 | 10652 | 3324 | 804 | 2048 | 0 | 1464 | 2297 | 0 | 151 | 430 | 134 | 0 | 0 | 73.76
KWH | 0 | 0 | 2796938 | 4258800 | 0 | 0 | 0 | 8286210 | 7888000 |  | 0 | 10164000 | 569396 | 201600 | 543900 | 160120 | 0 | 0 | 428000 | 214080 | 626112 | 1662720 | 60883 | 0 | 0 | 0 | 260280 | 606563 | 464284 | 314136 | 552000 | 540540 | 636200 | 692500 | 388800 | 0 | 0 | 304000 | 0 | 0 | 209451 | 0 | 2577305 | 0 | 0 |  | 253440 | 1017312 | 1623037 | 525120 | 227520 | 358080 | 198576 | 366720 | 0 | 0 | 0 | 7917100 | 0 | 4538000 | 3629818 | 0 | 956880 | 0 | 0 | 833556 | 0 | 872656 | 461698 | 121356 | 115920 | 172600 | 281750 | 2976000 | 1404480 | 0 | 317916 | 7900 | 1018000 | 658080 | 1020000 | 1085184 | 0 | 0 | 1364544 | 1492800 | 0 | 5229260 | 410000 | 0 | 237780 | 6831000 | 411648 | 168432 | 0 | 1836655 | 1158552 | 184716 | 1120800 | 201768 | 1170288 | 114615 | 426240 | 426240 | 1080581 | 8866000 | 1045200 | 1593734 | 1072218 | 24238 | 2529164 | 378500 | 1524684 | 1011180 | 714840 | 456960 | 9314700 | 714240 | 246270 | 1095840 | 426545 | 0 | 643320 | 181763 | 1114560 | 532440 | 0 | 981891 | 0 |  | 20850181 | 0 | 0 | 0 | 237120 | 0 | 0 | 0 | 0 | 0 | 94500 | 4342536 | 358587 | 92736 | 0 | 0 | 0 | 82640 | 213931 | 655096 | 332490 | 201650 | 344835 | 500770 | 424679 | 450960 | 0 | 98838 | 1746327 | 0 | 5792000 | 0 | 0 | 3957400 | 0 | 0 | 0 | 0 | 0 | 4004064 | 0 | 8494945 | 223200 | 0 | 662496 | 261792 | 747926 | 0 | 22701 | 650688 | 19408500 | 0 | 0 | 114000 | 30840 | 654480 | 664512 | 491949 | 0 | 8800000 | 156950 | 4014500 | 9741818 | 890080 | 0 |  | 136699723 | 100812717 | 237512440 | 74373404 | 20850181 | 43422746 | 1545036 | 31260040 | 49503145 | 304000 | 3069254 | 7878797 | 2976000 | 2329837 | 0
Fuel Cost | 0 | 0 | 4083529.48 | 6345612 | 0 | 0 | 0 | 8700520.5 | 8519040 |  | 0 | 11078760 | 632029.56 | 2253888 | 7206675 | 2121590 | 0 | 0 | 749000 | 3129849.6 | 8809395.84 | 26952691.2 | 561341.26 | 0 | 0 | 0 | 3310761.6 | 8188600.5 | 6226048.44 | 235602 | 414000 | 0 | 0 | 0 | 6613488 | 0 | 0 | 82080 | 0 | 0 | 3424523.85 | 0 | 44742014.8 | 0 | 0 |  | 3307392 | 16968764.16 | 27624089.74 | 7094371.2 | 2884953.6 | 4142985.6 | 252191.52 | 1221177.6 | 0 | 0 | 0 | 8787981 | 0 | 5264080 | 4682465.22 | 0 | 1081274.4 | 0 | 0 | 1392038.52 | 0 | 15070769.12 | 6209838.1 | 166257.72 | 86940 | 302050 | 211312.5 | 21367680 | 1530883.2 | 0 | 432365.76 | 125926 | 1394660 | 868665.6 | 1774800 | 1877368.32 | 0 | 0 | 2647215.36 | 3403584 | 0 | 5281552.6 | 881500 | 0 | 470804.4 | 6831000 | 308736 | 128008.32 | 0 | 25070340.75 | 24283249.92 | 3818079.72 | 15108384 | 4170544.56 | 16208488.8 | 1339849.35 | 4398796.8 | 5822438.4 | 14339309.87 | 8156720 | 12709632 | 23045393.64 | 13563557.7 | 0 | 29692385.36 | 4121865 | 16207390.92 | 13721712.6 | 9214287.6 | 5382988.8 | 8569524 | 9249408 | 3558601.5 | 13906209.6 | 4854082.1 | 0 | 8401759.2 | 2172067.85 | 16684963.2 | 7012234.8 | 0 | 0 | 0 |  | 62550543 | 0 | 0 | 0 | 2468419.2 | 0 | 0 | 0 | 0 | 0 | 1357965 | 4863640.32 | 695658.78 | 1010822.4 | 0 | 0 | 0 | 1385872.8 | 3741653.19 | 10245701.44 | 2560173 | 3339324 | 5831159.85 | 6825495.1 | 7164334.73 | 933487.2 | 0 | 74820.366 | 10146159.87 | 0 | 30639680 | 0 | 0 | 4590584 | 0 | 0 | 0 | 0 | 0 | 4644714.24 | 0 | 8409995.55 | 2999808 | 0 | 7837327.68 | 3782894.4 | 9498660.2 | 0 | 250846.05 | 7899352.32 | 174870585 | 0 | 0 | 843600 | 348800.4 | 7677050.4 | 10186968.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 645240989.23 | 399676097.446 | 1044917086.676 | 81053940.886 | 62550543 | 51922209.15 | 32271874.2 | 404812141.99 | 215656424.87 | 82080 | 44742014.8 | 114985036.23 | 21367680 | 15473141.55 | 0
Yesterday Day Peak | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 392 | 342 |  | 0 | 450 | 0 | 8 | 5 | 5 | 0 | 0 | 0 | 7 | 24 | 48 | 4 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 23 | 17 | 25 | 22 | 0 | 0 | 0 | 25 | 0 | 0 | 8 | 0 | 71 | 0 | 0 |  | 5 | 34 | 82 | 92 | 0 | 6 | 11 | 2 | 0 | 0 | 0 | 310 | 0 | 178 | 120 | 0 | 39 | 0 | 0 | 25 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 108 | 43 | 0 | 0 | 2 | 43 | 30 | 50 | 40 | 0 | 0 | 63 | 72 | 0 | 207 | 17 | 0 | 9 | 290 | 16 | 0 | 0 | 32 | 0 | 0 | 47 | 0 | 86 | 19 | 25 | 17 | 16 | 367 | 47 | 50 | 34 | 5 | 86 | 17 | 54 | 0 | 26 | 25 | 400 | 17 | 55 | 54 | 17 | 0 | 17 | 35 | 54 | 17 | 0 | 36 | 0 |  | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 5 | 75 | 0 | 220 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 500 | 0 | 0 | 0 | 3 | 105 | 0 | 181 | 0 | 318 | 35 | 153 | 397 | 166 | 0 |  | 9376 | DayPeak
Yesterday Evening Peak | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 401 | 313 | 0 | 0 | 450 | 52 | 8 | 79 | 15 | 0 | 0 | 103 | 18 | 50 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 15 | 22 | 20 | 33 | 33 | 50 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 151 | 0 | 0 | 0 | 12 | 66 | 84 | 22 | 30 | 44 | 6 | 17 | 0 | 0 | 0 | 310 | 0 | 180 | 148 | 0 | 40 | 0 | 0 | 43 | 0 | 36 | 52 | 14 | 6 | 25 | 18 | 144 | 52 | 0 | 18 | 0 | 43 | 30 | 50 | 50 | 0 | 0 | 63 | 77 | 0 | 207 | 17 | 0 | 9 | 290 | 16 | 11 | 0 | 195 | 0 | 0 | 84 | 0 | 132 | 0 | 25 | 17 | 150 | 367 | 88 | 88 | 87 | 0 | 275 | 17 | 106 | 70 | 95 | 25 | 378 | 50 | 0 | 108 | 17 | 0 | 35 | 0 | 108 | 34 | 0 | 78 | 0 |  | 910 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 25 | 16 | 0 | 0 | 0 | 0 | 13 | 82 | 28 | 0 | 40 | 52 | 30 | 21 | 0 | 8 | 73 | 0 | 260 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 313 | 17 | 0 | 50 | 50 | 78 | 0 | 0 | 57 | 1020 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0 | 370 | 0 | 152 | 400 | 0 | 0 |  | 11950 | EvPeak
Forecast for Evening | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 380 | 340 | 0 | 0 | 450 | 320 | 8 | 85 | 55 | 0 | 0 | 0 | 17 | 50 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 23 | 25 | 33 | 20 | 48 | 0 | 25 | 25 | 0 | 0 | 25 | 0 | 150 | 0 | 0 | 0 | 12 | 58 | 84 | 22 | 30 | 40 | 11 | 10 | 0 | 0 | 0 | 350 | 0 | 200 | 125 | 0 | 40 | 0 | 0 | 43 | 0 | 35 | 52 | 18 | 7 | 25 | 21 | 152 | 80 | 0 | 17 | 0 | 43 | 29 | 51 | 50 | 0 | 0 | 61 | 84 | 0 | 210 | 18 | 0 | 10 | 300 | 8 | 8 | 0 | 195 | 300 | 40 | 85 | 50 | 149 | 0 | 25 | 17 | 150 | 400 | 88 | 88 | 87 | 0 | 300 | 17 | 105 | 114 | 113 | 25 | 400 | 53 | 0 | 162 | 17 | 0 | 35 |  | 115 | 34 | 0 | 163 |  |  | 925 | 0 | 0 |  | 83 | 0 | 0 | 0 | 43 | 70 | 40 | 130 | 35 | 16 | 0 | 0 | 0 | 28 | 35 | 80 | 21 | 42 | 40 | 52 | 34 | 20 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 170 |  | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 17 | 0 | 50 | 105 | 107 | 0 | 0 | 55 | 1244 | 0 |  | 150 |  |  | 115 | 0 |  | 330 |  | 150 | 0 |  | 0
Forecast for Day | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 380 | 340 | 0 | 0 | 450 | 320 | 8 | 17 | 0 | 0 | 0 | 0 | 16 | 24 | 100 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 19 | 23 | 25 | 33 | 20 | 16 | 0 | 25 | 0 | 0 | 0 | 25 | 0 | 145 | 0 | 0 | 0 | 12 | 54 | 67 | 100 | 0 | 6 | 10 | 5 | 0 | 0 | 0 | 350 | 0 | 200 | 120 | 0 | 40 | 0 | 0 | 43 | 0 | 35 | 0 | 18 | 5 | 25 | 21 | 129 | 42 | 0 | 17 | 1.6 | 43 | 0 | 51 | 44 | 0 | 0 | 61 | 84 | 0 | 210 | 17 | 0 | 10 | 290 | 8 | 3 | 0 | 45 | 300 | 40 | 48 | 40 | 149 | 20 | 25 | 17 | 20 | 400 | 47 | 88 | 17 | 5 | 88 | 17 | 54 | 114 | 26 | 25 | 400 | 17 | 50 | 72 | 17 | 0 | 35 | 30 | 54 | 17 | 0 | 35 |  |  | 925 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 20 | 60 | 24 | 130 | 22 | 0 | 0 | 0 | 0 | 28 | 15 | 80 | 21 | 42 | 24 | 30 | 28 | 20 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 17 | 0 | 35 | 85 | 34 | 0 | 8 | 35 | 1244 | 0 |  | 17 | 6 | 100 | 115 | 0 |  | 330 | 30 | 150 | 0 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 299 | 315 | 0 | 0 | 380 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 7 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 6 | 6 | 15 | 0 | 0 | 0 | 320 | 0 | 154 | 8 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 48 | 0 | 0 | 1 | 40 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 155 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 12 | 17 | 0 | 323 | 0 | 0 | 0 | 1 | 50 | 0 | 17 | 17 | 8 | 12 | 300 | 17 | 14 | 0 | 17 | 0 | 13 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 418 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 500 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 330 | 4 | 154 | 0 | 17 | 0 | 0 |  |  |  | 117.7961 | 20.8502 | 43.7531 | 49.5031 | 0.304 | 2.976 | 2.3298
237.5124
| Minimum Generation |  | 8469 | 9:00
| Highest Generation |  | 11950 | 19:30
| Day Peak Generation |  | 9376 | 12:00
| Evening Peak Generation |  | 11950 | 19:30
| HVDC Max Flow |  | 911 | 3:00
| HVDC EvPeak Flow |  | 910 | 19:30
| Load factor L.F |  | 82.81% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-05-18
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-05-17 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9376 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 4959
Evening Peak Generation : |  |  | 11950 | MW Hour : | 19:30 | Available Max Generation : |  | 13254
E.P. Demand (at gen end) : |  |  | 11950 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 12500
Maximum Generation : |  |  | 11950 | MW Hour : | 19:30 | Reserve(Generation end) |  | 754
Total Gen. (MKWH) : |  |  | 237.5124 | System Load Factor : | 82.81% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 432 | MW at | 23:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-05-18
Actual : |  | 73.74 | Ft.(MSL) , | Rule curve : | 78.96 | Ft.( MSL )
Gas Consumed : |  | Total = | 860.58 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 132976150.036
: |  |  | Coal : | 215656424.87 | Oil : | 596811067.22 | Total : | 945443642.126
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4211.0089 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1154.9 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1617.1353 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1404.9812 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1156.3575 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 859.7216 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 482.2394 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 401.5794 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 785.4259 |  |  | 0 | 0%
Total |  | 0 |  | 12073.3492 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,7
3) Bhula Nuton Biddut
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj- 2
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
| 08:20 | Natore 132/33kV S/S TR-1 (405 T) HT is restored.
| 08:21 | Natore 132/33kV S/S TR-1 (405 T) LT is restored.
| 09:02 | Sirajganj 132/33kV S/S T4-(445) HT is restored.
| 09:03 | Sirajganj 132/33kV S/S T4-(445) LT is restored.
09:43 | 10:48 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Tripped from Brahmanbaria 132/33kV end showing Zone-1,A/R blocked relays
Due to Fault and from Shahjibazar 132/33kV end showing Distance Relay, Zone-01 Fault, 20.5 Km, Phase-C, R-0.34ohm relays.
09:51 | 10:50 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Scheduled S/D from Shahjibazar 132/33kV end Due to Due to remove fault.
09:55 | 09:59 | Ashuganj-Shahjibazar 132kV Ckt-1 Tripped from Shahjibazar 132/33kV end showing Distance Relay, A phase,5.9Km, Zone-01
Fault,Auto Reclose blocking relays.
10:01 | 10:13 | Ashuganj-Shahjibazar 132kV Ckt-1 Scheduled S/D from Shahjibazar 132/33kV end Due to Due to fault remove.
10:31 | 12:49 | Aminbazar 400/230/132kV S/S Gopalganj-1 Tripped showing 21-M1 relays.
12:16 | 12:49 | Bogura-Bogura (New)) 132 kV Ckt-1 Tripped from Bogura 132/33kV end showing Differential Protection Relay relays
Due to Trip and from Bogura 230/132kV end showing Busbar Protection Trip. (REB 500 Relay) relays.
12:29 | 17:27 | Tangail 132/33kV S/S RPCL-1 Forced S/D Due to Due to maintenance work at RPCl End.
12:40 |  | Khulna 330 MW P/S Shut-down.
| 12:49 | Bogura-Bogura (New)) 132 kV Ckt-1 is restored.
13:29 | 14:33 | Barishal-Bhola 230 kV Ckt-2 Tripped from Barishal 230/132kV end showing REL 670 relays Due to EFSTFW .
13:29 |  | Barishal North-Bhola 230kV ckt-2 tripped showing distance relay, zone-1, phase-Y from Barishal North end.
13:33 | 14:16 | Joydebpur-Kodda B 132 kV Ckt-2 Scheduled S/D from Joydebpur 132/33kV end Due to Installation of digital multi-function meter.
14:22 | 15:38 | Jaldhaka 132/33kV S/S 416T LT Forced S/D Due to Due to flasing in 33KV BUS section-1,maintenance work done by NESCO & PBS. | [5 empty] | 32 MW load interrup.
14:24 | 15:37 | Jaldhaka 132/33kV S/S 416T HT Forced S/D Due to Due to flasing in 33KV BUS section-1,maintenance work done by NESCO & PBS.
14:28 | 15:32 | Jaldhaka 132/33kV S/S 33 KV BUS Forced S/D Due to Due to flasing in 33KV BUS section-1,maintenance work done by NESCO & PBS.
14:35 | 15:06 | Joydebpur 132/33kV S/S GT-4 HT Scheduled S/D Due to Installation of digital multifunction meter.
14:42 | 16:18 | Jamalpur 132/33kV S/S T-1 HT Scheduled S/D Due to 33KV Sharishabari PDB Bus loop change. | [5 empty] | 15 MW load interrup.
14:42 | 16:23 | Jamalpur 132/33kV S/S T-2 HT Scheduled S/D Due to 33KV Sharishabari PDB Bus loop change.
14:42 | 16:18 | Jamalpur 132/33kV S/S T-1 LT Scheduled S/D Due to 33KV Sharishabari PDB Bus loop change.
14:42 | 16:23 | Jamalpur 132/33kV S/S T-2 LT Scheduled S/D Due to 33KV Sharishabari PDB Bus loop change.
15:39 | 17:29 | Aminbazar-Mirpur 132kV Ckt-2 Forced S/D from Mirpur 132/33kV end Due to Bill board banner remove works.
| 15:53 | Meghnaghat Summit CCPP GT2 was sync.
16:02 | 17:34 | Gollamari 132/33kV S/S Tr-1 LT Forced S/D Due to 33 kV bus DS red hot maintenance. | [5 empty] | 5 MW load interrup.
16:03 | 17:33 | Gollamari 132/33kV S/S Tr-1 HT Forced S/D Due to 33 kV bus DS red hot maintenance.
16:03 | 17:36 | Gollamari 132/33kV S/S Tr-2 LT Forced S/D Due to 33 kV bus DS red hot maintenance. | [5 empty] | 17 MW load interrup.
16:04 | 17:35 | Gollamari 132/33kV S/S Tr-2 HT Forced S/D Due to 33 kV bus DS red hot maintenance.
16:48 | 20:20 | Ullon-Dhanmondi 132kV ckt-2 was S/D for relay work.
| 18:43 | Ishurdi 230/132kV S/S 230/132 kV T-03 HT is restored.
| 19:10 | Meghnaghat Summit CCPP 305MW ST was sync.
| 19:22 | Ishurdi 230/132kV S/S 230/132 kV T-03 LT is restored.
22:15 |  | Kalyanpur-Lalbagh 132KV Ckt-2 tripped from Lalbagh(DPDC) end showing Lockout relay.
| 22:53 | Meghnaghat Summit CCPP GT1 was sync.
01:01 |  | Bogra west-Rohonpur 400 KV -1 trip.
01:03 |  | Siddhirganj GT-1 was shutdown due to gas shortage.
01:03 |  | Adani Power Jharkhand Ltd. unit-1 tripped at 1:03 hrs. due to the tripping of Bogura-Adani 400kV ckt-1 showing | [5 empty] | 400 MW generation interrup.
Distance relay (1km from Adani end)
03:18 |  | Adani-Bogra 400KV Ckt-1 was switched on
| 03:18 | Bogra west-Rohonpur 400 KV -1 syn.
03:32 | 03:45 | Purbasadipur 132/33kV S/S T-3 Transformer (423T) HT Tripped showing Alstom relays.
03:32 | 04:06 | Ishwardi-Natore 132kV Ckt-1 Tripped from Ishurdi 132/33kV end showing Lz32 relays. and from Natore 132/33kV end
showing General trip,Z1 Trip,Block AR relays.
04:15 | 06:46 | Bogura 230/132kV S/S Confidance UN-2 Tripped showing Over Voltage relays Due to Over Voltage.
04:34 | 04:46 | Jamalpur 132/33kV S/S T-2 HT Tripped showing over current protection P132 REF relays Due to 33kV Nandina feeder faulty. | [5 empty] | 2 MW load interrup.
04:34 | 04:46 | Jamalpur 132/33kV S/S T-2 LT Tripped showing over current protection P132 REF relays Due to 33kV Nandina feeder faulty.
04:34 | 04:46 | Jamalpur 132/33kV S/S T-1 HT Tripped showing over current protection P132 REF relays Due to 33kV Nandina feeder faulty.
04:34 | 04:46 | Jamalpur 132/33kV S/S T-1 LT Tripped showing over current protection P132 REF relays Due to 33kV Nandina feeder faulty.
04:53 | 05:25 | Barapukuria-Bogura 230 kV Ckt-2 Tripped from Bogura 230/132kV end showing REL 316*4(Auto Reclose Blocked,
Permit Close), REL 521(Earth Fault) relays Due to Rain.
04:53 | 05:24 | Barapukuria-Bogura 230 kV Ckt-1 Tripped from Bogura 230/132kV end showing REL 316*4(Auto Reclose Blocked,
Permit Close), REL 521(Earth Fault) relays Due to Rain.
05:30 |  | Ghorasal-4 was shutdown due to bad weather.
05:30 |  | Sikalbaha 225MW was shutdown due to low demand.
06:22 |  | Sirajganj unit-3 was shutdown due to low demand.
06:30 | 07:37 | Mahasthangarh 132/33kV S/S 416T MTR 2 LT Tripped showing Over current relays Due to Fasitola feeder fault. | [5 empty] | 5 MW load interrup.
06:30 | 07:37 | Mahasthangarh 132/33kV S/S 416T MTR 1 LT Tripped showing Over current relays Due to Fasitola feeder fault.
06:38 | 06:45 | Kabirpur - Manikganj 132kV Ckt-1 Tripped from Kabirpur 132/33kV end showing Distance protection relay, Zone-1, | [5 empty] | 10 MW load interrup
|  | Y-phase. relays. and from Manikganj 132/33kV end showing relays. | [5 empty] | Manikganj 132/33 kV end.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-05-17 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 120 | 2796938 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4258800
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 401 | 8286210
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 313 | 7888000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10164000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 8 | 201600 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 52 | 569396 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 79 | 543900 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 160120 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 20 | 0 | 60883 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 15 | 314136 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 103 | 428000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 18 | 214080 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 50 | 626112 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 260280 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1662720
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 606563
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 464284 | Fuel shortage
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 42 | 1092540 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 636200
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 692500
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 50 | 388800 | 0:00
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 195 | 1836655 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 1158552 | Reserved
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 184716 | Reserved
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 201768 | Reserved
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 1170288 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1593734 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 50 | 714240 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 1095840 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 181763
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 34 | 532440 | Fuel shortage
| Dhaka area Total |  |  |  | 5867 | 2826 | 50986058
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 209451
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 114615
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 44 | 358080 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 25 | 304000 | Low Water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 151 | 2577305 | Gas shortage
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 87 | 1072218 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 66 | 1017312 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 84 | 1623037 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 22 | 525120 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 426240 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 6 | 198576 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 17 | 366720
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 30 | 227520 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 24238
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 275 | 2529164
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 378500 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 106 | 1524684
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 456960
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 426545 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 78 | 981891 | Fuel shortage
| Chattogram area Total |  |  |  | 2545 | 1100 | 15342176
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 180 | 4538000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7917100 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 40 | 956880 | Machine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 148 | 3629818 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 833556 | Machine problem
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 150 | 1080581
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 872656 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 426240 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 14 | 121356 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 6 | 115920 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 144 | 2976000
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 172600 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 461698
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 18 | 281750 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 70 | 1011180 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 95 | 714840 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 643320 | Fuel shortage
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 108 | 1114560 | Fuel shortage
| Cumilla Area Total |  |  |  | 3096 | 1491 | 27868055
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 52 | 1404480 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 317916 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 7900
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 84 | 1120800 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 88 | 1045200 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 246270
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 253440 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 254 | 4396006
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1018000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 658080 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | ST under shut down
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1020000
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 50 | 1085184
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 168432
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1364544
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 77 | 1492800
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 207 | 5229260
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 410000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 411648 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 6831000 | Gas shortage
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 367 | 8866000 | Gas shortage
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 237780
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 378 | 9314700 | Gas shortage
| Sylhet Area Total |  |  |  | 2427 | 1608 | 38107428
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 910 | 20850181
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 237120 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserved
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserved
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 94500 | Reserved
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 223200 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 50 | 261792 | Low demand
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 654480
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 491949 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 370 | 8800000
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 2901 | 1363 | 31613222
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 92736 | Fuel shortage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 25 | 358587 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 163 | 4342536
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1020 | 19408500
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 0 | 0 | Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 114000
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 152 | 4014500
| Barisal Area Total |  |  |  | 2265 | 1376 | 28330859
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 82640 | Reserved
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 13 | 213931 | Low demand
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 28 | 28 | 332490 | Engine problem
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 201650 | Reserved
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 344835 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 160 | 3957400 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 158 | 4004064 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 313 | 8494945 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 424679 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 450960
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 98838 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 500770
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 82 | 655096 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 662496 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 57 | 650688 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 30840
| Adani Power Jharkhanda Ltd |  | Import | 748*1 | 748 | 400 | 9741818 | On test.
| Rajshahi Area Total |  |  |  | 2905 | 1412 | 30848140
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 73 | 1746327
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 260 | 5792000
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 78 | 747926 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 22701
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 109 | 664512
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 156950
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 890080
| Rangpur Area Total |  |  |  | 750 | 520 | 10020496
| Total |  |  |  | 23370 | 11950 | 237512440
| Eastern Grid Total |  |  |  | 14549 | 7279 | 136699723
| Western Grid Total |  |  |  | 8821 | 4671 | 100812717
| National Grid Total |  |  |  | 23370 | 11950 | 237512440
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-05-17
| (a) ENTIRE EASTERN GRID : |  | 7959.88 | MW | (b) ENTIRE WESTERN GRID : |  | 3409.6 | MW
| i) Dhaka area |  | 4429.18 | MW | i) Khulna area |  | 963.6 | MW
| ii) Chittagong area |  | 1118.7 | MW | ii) Rajshahi area |  | 1296.4 | MW
| iii) Comilla area |  | 1052 | MW | iii) Barisal area |  | 361.6 | MW
| iv) Mymensingh area |  | 905 | MW | iv) Rangpur area |  | 788 | MW
| v) Sylhet area |  | 455 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11369.48 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 16 | 17:00 | Chhatak | 27 | 23:00 | Kamrangirchar | 78 | 19:00 | Natore | 137 | 21:00 | Shitalakhya | 106 | 16:00
2 | AKSML | 10.6 | 15:00 | Chowmuhani | 168 | 19:30 | Kaptai | 5 | 19:00 | Nawabganj | 45.2 | 20:00 | Sholosohor | 29 | 13:00
3 | Aftabnagar | 46 | 16:00 | Chuadanga | 87 | 14:00 | Kazla | 87 | 18:30 | Netrakona | 124 | 20:00 | Shyampur | 158 | 09:00
4 | Agargaon | 68 | 09:00 | Coxsbazar | 104 | 19:00 | Keranigonj | 68 | 19:30 | New | 75 | 09:00 | Siddhirganj | 106 | 09:00
5 | Agrabad | 60 | 11:00 | Cumilla(N) | 123 | 01:00 | Khagrachori | 26 | 11:00 | Niamatpur | 78 | 20:00 | Sirajganj | 101 | 19:30
6 | Amnura | 55 | 21:00 | Cumilla(S) | 146 | 20:00 | Khulna | 111 | 12:00 | Noapara | 45 | 19:00 | Sonargaon | 80 | 21:00
7 | Ashuganj | 72 | 00:00 | Daudkandi | 118 | 19:30 | Khulshi | 127 | 21:00 | PHP | 3 | 04:00 | Sreemongol | 56 | 00:00
8 | BIPTC | N/A | N/A | Dhaka | 18 | 12:00 | Kishoreganj | 122 | 00:00 | Pabna | 99 | 19:30 | Sreepur | 60.88 | 19:00
9 | BSRM | 86 | 17:00 | Dhamrai | 100 | 19:30 | Kodda | 278 | 15:00 | Palashbari | 98 | 18:30 | Srinagar | 28.2 | 01:00
10 | Bagerhat | 100 | 19:30 | Dhanmondi | 123 | 13:00 | Kulaura | 32 | 20:00 | Panchagarh | 52 | 19:00 | Sunamganj | 44 | 22:00
11 | Bakulia | 85 | 11:00 | Dohazari | 92 | 00:00 | Kurigram | 46 | 19:00 | Patuakhali | 81 | 21:00 | Sylhet | 128 | 19:30
12 | Banani | 60 | 15:00 | Faridpur | 120 | 19:00 | Kushtia | 116 | 22:00 | Payra | 19 | 22:00 | TK | 16.8 | 22:00
13 | Bangabhaban | 14 | 10:00 | Fatullah | 61 | 00:00 | Lalbag | 83 | 19:00 | Postogola | 51 | 01:00 | Tangail | 196 | 19:30
14 | Barapukuria | 53 | 00:00 | Fenchuganj | 39 | 19:30 | Lalmonirhat | 39 | 19:00 | Purbachal | 17 | 00:00 | Thakurgaon | 80 | 00:00
15 | Barguna | 18 | 19:00 | Feni | 98 | 19:30 | Madanganj | 32 | 00:00 | Purbasadipur | 130 | 00:00 | Tongi | 90 | 12:00
16 | Barishal | 94 | 12:00 | GPH | 64 | 20:00 | Madaripur | 74 | 19:00 | Rahanpur_I | 0 | 00:00 | Ullon | 34 | 00:00
17 | Barishal-230 | 74 | 20:00 | Ghorashal | 69 | 18:30 | Madartek | 66 | 19:30 | Rahim | 43 | 16:00 | Uttara | 52 | 19:00
18 | Baroaulia | 65 | 11:00 | Goalpara | 42 | 19:00 | Madunaghat | 45 | 19:30 | Rajbari | 50 | 19:00 | UttaraNew | 41 | 09:00
19 | Baroirhat | 36 | 19:00 | Gollamari | 43 | 18:30 | Magura | 48 | 19:00 | Rajendrapur | 84 | 17:00 | Zigatola | 37 | 16:00
20 | Bashundhara | 196 | 19:00 | Gopalganj | 95.6 | 19:30 | Mahasthangarh | 66 | 20:00 | Rajshahi | 142 | 19:30
21 | BashundharaCement | 7 | 14:00 | Gulshan | 58 | 16:00 | Manikganj | 105 | 21:00 | Rajshahi-230 | 34 | 20:00
22 | Beanibazar | 56 | 19:30 | Halishahar | 98 | 14:00 | Maniknagar | 80 | 13:00 | Ramganj | 90 | 21:00
23 | Benapole | 48 | 15:00 | HaripurSBU | 152 | 15:00 | Matarbari | 45 | 00:00 | Rampur | 30 | 19:00
24 | Bhaluka | 140 | 00:00 | Hasnabad | 64 | 13:00 | Matuail | 61 | 09:00 | Rangamati | 12 | 19:00
25 | Bhandaria | 46 | 20:00 | Hathazari | 58 | 20:00 | Millgate | 89 | 16:00 | Rangpur | 110 | 19:00
26 | Bhangura | 33 | 19:30 | Ishurdi | 62 | 19:00 | Mirpur | 121 | 15:00 | Ruppur | 5.6 | 16:00
27 | Bheramara(GK) | 47 | 21:00 | Jaldhaka | 58 | 19:30 | Mirsorai | 4 | 12:00 | SSM | 14 | 09:00
28 | Bhulta | 245 | 16:00 | Jamalpur | 113 | 19:00 | Mithapukur | 46 | 19:00 | Saidpur | 97 | 19:30
29 | Bog-Sherpur | 58 | 00:00 | Jashore | 121 | 13:00 | Modern | 0 | 00:00 | Satkhira | 126 | 19:00
30 | Bogura | 149 | 20:00 | Jhenaidah | 102 | 18:00 | Mogbazar | 114 | 15:00 | Satmasjid | 85 | 19:00
31 | Borhanuddin | 50 | 21:00 | Joydebpur | 155 | 19:00 | Mongla | 34 | 12:00 | Savar | 172 | 09:00
32 | Brahmanbaria | 133 | 20:00 | Joypurhat | 52 | 20:00 | Motijheel | 34 | 13:00 | Shahjadpur | 86 | 19:00
33 | Cantonment | 116 | 19:30 | Juldah | 28 | 12:00 | Munshiganj | 89 | 19:30 | Shahjibazar | 119 | 00:00
34 | Chandpur | 50 | 19:00 | KSRM | 13 | 19:00 | Mymensingh | 164 | 19:30 | Shahmirpur | 31 | 16:00
35 | Chandraghona | 24 | 19:00 | Kabirpur | 262 | 19:00 | Naogaon | 118 | 22:00 | Shariatpur | 54 | 20:00
36 | Chapai | 63 | 22:00 | Kachua | 58 | 19:30 | Narail | 50 | 19:00 | Sherpur | 96 | 19:00
37 | Charsaidpur | 45 | 23:00 | Kallyanpur | 93 | 00:00 | Narinda | 61 | 14:00 | Shikalbaha | 30 | 21:00
38 | Chauddagram | 41 | 19:00 | Kalurghat | 30 | 12:00 | Narshingdi | 153 | 21:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-05-17 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 400 | 21:00 | 386 | 11:00 | Kaliakoir | 391 | 09:00 | 378 | 08:00
| Bhulta | 384 | 19:00 | 368 | 08:00 | Madunaghat_I | 420 | 19:30 | 393 | 06:00
| Bibiana | 407 | 18:30 | 397 | 05:00 | Payra | 413 | 12:00 | 408 | 14:00
| BIPTC | 398 | 21:00 | 387 | 15:00 | Rahanpur_I | 423 | 07:00 | 416 | 20:00
| Gopalganj | 404 | 21:00 | 392 | 14:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 231 | 21:00 | 222 | 08:00 | Hathazari | 241 | 19:00 | 210 | 08:00
| AKSML | 242 | 20:00 | 200 | 08:00 | Ishurdi | 235 | 19:30 | 226 | 11:00
| Aminbazar | 266 | 12:00 | 225 | 04:00 | Jhenaidah | 232 | 20:00 | 218 | 14:00
| Ashuganj | 238 | 19:00 | 225 | 08:00 | Kaliakoir | 228 | 09:00 | 221 | 08:00
| Baghabari | 231 | 18:00 | 222 | 16:00 | Keranigonj | 230 | 22:00 | 220 | 09:00
| Barapukuria | 228 | 05:00 | 218 | 12:00 | Khulna(S) | 234 | 20:00 | 221 | 15:00
| Barishal | 234 | 18:30 | 228 | 14:00 | Madunaghat_I | 241 | 20:00 | 227 | 06:00
| Bheramara | 255 | 15:00 | 224 | 11:00 | Maniknagar | 229 | 20:00 | 219 | 09:00
| Bhulta | 231 | 20:00 | 220 | 08:00 | Meghnaghat | 234 | 20:00 | 222 | 04:00
| Bibiana | 242 | 19:30 | 231 | 08:00 | Mirsorai | 242 | 20:00 | 215 | 09:00
| BIPTC | 236 | 19:00 | 224 | 00:00 | Rajshahi | 236 | 19:00 | 223 | 00:00
| Bogura | 232 | 08:00 | 223 | 11:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 234 | 02:00 | 231 | 14:00 | Rampura | 229 | 20:00 | 218 | 08:00
| BSRM | 242 | 20:00 | 219 | 09:00 | Shikalbaha | 240 | 19:30 | 213 | 09:00
| Cumilla(N) | 235 | 20:00 | 221 | 09:00 | Shyampur | 229 | 20:00 | 220 | 09:00
| Fenchuganj | 245 | 19:00 | 237 | 16:00 | Siddhirganj | 227 | 10:00 | 224 | 01:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 239 | 18:30 | 235 | 11:00
| GPH | 240 | 20:00 | 215 | 10:00 | Sreepur | 233 | 00:00 | 230 | 07:00
| Haripur | 229 | 20:00 | 219 | 09:00 | Tongi | 230 | 19:30 | 217 | 08:00
| Hasnabad | 231 | 22:00 | 221 | 07:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 22:00 | 127 | 15:00 | Lalbag | 137 | 18:00 | 131 | 14:00
| Agargaon | 132 | 21:00 | 127 | 09:00 | Lalmonirhat | 136 | 05:00 | 124 | 12:00
| Agrabad | 138 | 18:30 | 122 | 08:00 | Madanganj | 136 | 20:00 | 126 | 08:00
| AKS | 139 | 19:00 | 122 | 08:00 | Madaripur | 129 | 17:00 | 124 | 13:00
| Aminbazar | 132 | 20:00 | 125 | 07:00 | Madartek | 135 | 22:00 | 128 | 09:00
| Amnura | 140 | 18:30 | 126 | 00:00 | Madunaghat | 141 | 20:00 | 123 | 10:00
| Ashuganj | 139 | 10:00 | 135 | 00:00 | Magura | 138 | 19:30 | 125 | 14:00
| Bagerhat | 136 | 21:00 | 122 | 14:00 | Mahasthangarh | 139 | 07:00 | 129 | 23:00
| Bakulia | 140 | 20:00 | 124 | 08:00 | Manikganj | 137 | 09:00 | 126 | 08:00
| Banani | 135 | 20:00 | 128 | 15:00 | Maniknagar | 133 | 21:00 | 126 | 09:00
| Bangabhaban | 133 | 21:00 | 126 | 05:00 | Matarbari | 136 | 03:00 | 115 | 10:00
| Barapukuria | 142 | 05:00 | 132 | 12:00 | Matuail | 134.2 | 20:00 | 126 | 09:00
| Barguna | 140 | 22:00 | 132 | 20:00 | Millgate | 135 | 22:00 | 124 | 16:00
| Barishal | 139 | 22:00 | 125 | 13:00 | Mirpur | 131 | 22:00 | 123 | 08:00
| Barishal-230 | 130 | 04:00 | 126 | 13:00 | Mithapukur | 138 | 05:00 | 126 | 12:00
| Baroaulia | 140 | 19:00 | 122 | 08:00 | Modern | 140 | 17:00 | 123 | 10:00
| Baroirhat | 138 | 19:00 | 123 | 10:00 | Mogbazar | 165 | 23:00 | 130 | 08:00
| Bashundhara | 133 | 10:00 | 123 | 08:00 | Mongla | 134 | 20:00 | 122 | 14:00
| BashundharaCement | 136 | 20:00 | 126 | 08:00 | Motijheel | 133 | 21:00 | 126 | 04:00
| Beanibazar | 135 | 00:00 | 129 | 10:00 | Munshiganj | 135 | 21:00 | 125 | 07:00
| Benapole | 136 | 20:00 | 122 | 14:00 | Mymensingh | 141 | 09:00 | 114 | 01:00
| Bhaluka | 141 | 09:00 | 118 | 15:00 | Naogaon | 136 | 07:00 | 124 | 23:00
| Bhandaria | 137 | 22:00 | 125 | 20:00 | Narail | 138 | 20:00 | 123 | 14:00
| Bhangura | 136 | 07:00 | 132 | 09:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 132 | 18:30 | 127 | 11:00 | Narshingdi | 133 | 10:00 | 121 | 09:00
| Bheramara(GK) | 133 | 05:00 | 128 | 12:00 | Natore | 134 | 18:30 | 126 | 23:00
| Bhulta | 126 | 10:00 | 118 | 09:00 | Nawabganj | 137 | 22:00 | 131 | 08:00
| Bog-Sherpur | 138 | 08:00 | 129 | 12:00 | Netrakona | 140 | 09:00 | 121 | 13:00
| Bogura | 139 | 07:00 | 132 | 11:00 | New | 134 | 19:30 | 125 | 08:00
| Bogura-230 | 140 | 07:00 | 131 | 11:00 | Niamatpur | 135 | 06:00 | 120 | 13:00
| Brahmanbaria | 135 | 12:00 | 130 | 00:00 | Noapara | 137 | 20:00 | 126 | 11:00
| Cantonment | 133 | 22:00 | 127 | 09:00 | Pabna | 133 | 02:00 | 128 | 12:00
| Chandpur | 139 | 12:00 | 120 | 07:00 | Palashbari | 137 | 07:00 | 126 | 23:00
| Chandraghona | 139 | 00:00 | 129 | 00:00 | Panchagarh | 136 | 05:00 | 119 | 12:00
| Chapai | 134 | 01:00 | 130 | 23:00 | Patuakhali | 139 | 18:00 | 134 | 14:00
| Charsaidpur | 137 | 20:00 | 127 | 09:00 | Payra | 140 | 18:30 | 137 | 13:00
| Chauddagram | 137 | 19:00 | 121 | 08:00 | PHP | 139 | 19:00 | 122 | 08:00
| Chhatak | 135 | 00:00 | 129 | 23:00 | Postogola | 132 | 22:00 | 124 | 09:00
| Chowmuhani | 137 | 19:00 | 123 | 10:00 | Purbachal | 134 | 19:30 | 124 | 16:00
| Chuadanga | 137 | 20:00 | 118 | 14:00 | Purbasadipur | 131 | 06:00 | 120 | 12:00
| Coxsbazar | 133 | 20:00 | 114 | 08:00 | Rahim | 135 | 19:30 | 127 | 09:00
| Cumilla(N) | 139 | 19:00 | 129 | 07:00 | Rajbari | 128 | 04:00 | 124 | 13:00
| Cumilla(S) | 140 | 19:00 | 126 | 09:00 | Rajendrapur | 139 | 09:00 | 124 | 07:00
| Daudkandi | 134 | 19:00 | 126 | 09:00 | Rajshahi | 133 | 18:00 | 126 | 11:00
| Dhaka | 136 | 22:00 | 129 | 14:00 | Rajshahi-230 | 133 | 18:30 | 126 | 11:00
| Dhamrai | 137 | 10:00 | 129 | 07:00 | Ramganj | 139 | 12:00 | 120 | 08:00
| Dhanmondi | 135 | 21:00 | 126 | 15:00 | Rampur | 140 | 19:00 | 123 | 10:00
| Dohazari | 138 | 20:00 | 122 | 08:00 | Rampura | 134 | 19:30 | 128 | 08:00
| Faridpur | 129 | 19:30 | 125 | 13:00 | Rangamati | 139 | 00:00 | 123 | 10:00
| Fatullah | 133 | 22:00 | 125 | 09:00 | Rangpur | 138 | 08:00 | 125 | 12:00
| Fenchuganj | 138 | 19:00 | 134 | 08:00 | Ruppur | 135 | 20:00 | 129 | 10:00
| Feni | 139 | 19:00 | 124 | 08:00 | Saidpur | 136 | 05:00 | 124 | 12:00
| Ghorashal | 139 | 19:30 | 134 | 15:00 | Satkhira | 137 | 20:00 | 123 | 14:00
| Goalpara | 138 | 20:00 | 127 | 13:00 | Satmasjid | 133 | 22:00 | 126 | 15:00
| Gollamari | 137 | 20:00 | 128 | 14:00 | Savar | 132 | 22:00 | 123 | 08:00
| Gopalganj | 131 | 20:00 | 126 | 12:00 | Shahjadpur | 140 | 00:00 | 134 | 11:00
| Gopalganj-400 | 130 | 20:00 | 125 | 14:00 | Shahjibazar | 137 | 12:00 | 131 | 04:00
| Gulshan | 135 | 22:00 | 127 | 08:00 | Shahmirpur | 139 | 19:00 | 124 | 09:00
| Halishahar | 139 | 19:00 | 122 | 10:00 | Shariatpur | 129 | 20:00 | 124 | 23:00
| Haripur | 135 | 19:30 | 127 | 09:00 | Sherpur | 142 | 09:00 | 123 | 17:00
| HaripurSBU | 135 | 19:30 | 127 | 09:00 | Shikalbaha | 141 | 20:00 | 122 | 08:00
| Hasnabad | 132 | 10:00 | 123 | 07:00 | Shikalbaha-230 | 140 | 19:30 | 123 | 09:00
| Hathazari | 140 | 19:00 | 122 | 08:00 | Shitalakhya | 132 | 22:00 | 122 | 09:00
| Ishurdi | 135 | 18:30 | 129 | 12:00 | Sholosohor | 138 | 00:00 | 123 | 10:00
| Jaldhaka | 139 | 05:00 | 122 | 12:00 | Shyampur | 133 | 22:00 | 125 | 09:00
| Jamalpur | 140 | 09:00 | 126 | 14:00 | Shyampur-230 | 132 | 19:30 | 125 | 09:00
| Jashore | 137 | 19:30 | 122 | 14:00 | Siddhirganj | 135 | 20:00 | 127 | 09:00
| Jhenaidah | 139 | 19:30 | 127 | 14:00 | Sirajganj | 139 | 08:00 | 129 | 12:00
| Jhenaidah-230 | 138 | 19:30 | 127 | 15:00 | Sonargaon | 135 | 21:00 | 126 | 00:00
| Joydebpur | 141 | 18:30 | 128 | 08:00 | Sreemongol | 136 | 11:00 | 131 | 01:00
| Joypurhat | 135 | 07:00 | 124 | 12:00 | Sreepur | 133 | 20:00 | 130 | 07:00
| Juldah | 139 | 19:00 | 121 | 08:00 | Srinagar | 136 | 17:00 | 132 | 07:00
| Kabirpur | 140 | 09:00 | 122 | 16:00 | SSM | 143 | 19:00 | 124 | 08:00
| Kachua | 137 | 12:00 | 124 | 08:00 | Sunamganj | 131 | 00:00 | 127 | 23:00
| Kaliakoir | 141 | 09:00 | 130 | 08:00 | Sylhet | 134 | 00:00 | 131 | 10:00
| Kallyanpur | 128 | 10:00 | 124 | 08:00 | Tangail | 140 | 09:00 | 125 | 16:00
| Kalurghat | 138 | 18:00 | 122 | 09:00 | Thakurgaon | 137 | 05:00 | 118 | 12:00
| Kamrangirchar | 127 | 10:00 | 120 | 16:00 | TK | 140 | 19:00 | 125 | 09:00
| Kaptai | 137 | 19:00 | 123 | 08:00 | Tongi | 135 | 19:30 | 127 | 08:00
| Kazla | 132 | 21:00 | 126 | 09:00 | Ullon | 135 | 22:00 | 128 | 09:00
| Keranigonj | 137 | 22:00 | 131 | 09:00 | Uttara | 131 | 20:00 | 124 | 15:00
| Khagrachori | 138 | 00:00 | 121 | 10:00 | UttaraNew | 132 | 22:00 | 124 | 14:00
| Khulna | 138 | 20:00 | 126 | 14:00 | Zigatola | 138 | 10:00 | 132 | 09:00
| Khulna(S) | 138 | 20:00 | 128 | 14:00
| Khulshi | 137 | 19:00 | 122 | 08:00
| Kishoreganj | 134 | 09:00 | 124 | 00:00
| Kodda | 140 | 09:00 | 124 | 08:00
| KSRM | 139 | 19:00 | 123 | 09:00
| Kulaura | 137 | 04:00 | 134 | 10:00
| Kurigram | 138 | 05:00 | 123 | 12:00
| Kushtia | 135 | 19:30 | 126 | 14:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2023-05-17
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1076 | 6265 | 4387 | 10652 |  |  |  | QF-LDC-11
0:30 | 988 | 5961 | 4208.5 | 10169.5 | Date: | 2023-05-17
1:00 | 900 | 5657 | 4030 | 9687
1:30 | 875 | 5545 | 4093.5 | 9638.5
2:00 | 850 | 5433 | 4157 | 9590
2:30 | 808 | 5357 | 4160.5 | 9517.5 | [5 empty] | Gen. at Eve. Peak | 11950 | 11950 MW (19:30 )
3:00 | 766 | 5281 | 4164 | 9445 | [6 empty] | 19:30
3:30 | 763 | 5170 | 4060 | 9230 | [5 empty] | Gen. at Day Peak | 9376 | 9376 MW (12:00 )
4:00 | 760 | 5059 | 3956 | 9015 | [6 empty] | 12:00
4:30 | 755 | 4968.5 | 3833 | 8801.5 | [5 empty] | Highest Generation | 11950
5:00 | 750 | 4878 | 3710 | 8588 | [6 empty] | 19:30
5:30 | 745 | 4831 | 3703.5 | 8534.5
6:00 | 740 | 4784 | 3697 | 8481
6:30 | 750 | 4702.5 | 3774 | 8476.5
7:00 | 760 | 4621 | 3851 | 8472
7:30 | 822 | 4620 | 3920 | 8540
8:00 | 884 | 4619 | 3989 | 8608
8:30 | 927 | 4636 | 3902.5 | 8538.5
9:00 | 970 | 4653 | 3816 | 8469
9:30 | 915 | 4320.5 | 3776 | 8096.5
10:00 | 860 | 3988 | 3736 | 7724
10:30 | 862 | 4332 | 3790 | 8122
11:00 | 864 | 4676 | 3844 | 8520
11:30 | 845 | 5036.5 | 3911.5 | 8948
12:00 | 826 | 5397 | 3979 | 9376
12:30 | 841 | 5487.5 | 3990.5 | 9478
13:00 | 856 | 5578 | 4002 | 9580
13:30 | 871 | 5595 | 4167.5 | 9762.5
14:00 | 886 | 5612 | 4333 | 9945
14:30 | 855 | 5761.5 | 4406 | 10167.5
15:00 | 824 | 5911 | 4479 | 10390
15:30 | 825 | 6019.5 | 4485.5 | 10505
16:00 | 826 | 6128 | 4492 | 10620
16:30 | 763 | 6108.5 | 4493.5 | 10602
17:00 | 700 | 6089 | 4495 | 10584
17:30 | 1053 | 6014 | 4391.5 | 10405.5
18:00 | 1406 | 5939 | 4288 | 10227
18:30 | 1473 | 6542.5 | 4397.5 | 10940
19:00 | 1540 | 7146 | 4507 | 11653
19:30 | 1664 | 7279 | 4671 | 11950
20:00 | 780 | 7248 | 4321 | 11569 |  |  |  | Executive Engineer
20:30 | 893 | 7290 | 4182.5 | 11472.5 |  |  |  | Network Operation Division
21:00 | 1006 | 7332 | 4044 | 11376
21:30 | 1003 | 7171 | 4095.5 | 11266.5
22:00 | 1000 | 7010 | 4147 | 11157 |  |  |  |  | Page 6 of 7
22:30 | 716 | 6883 | 4171 | 11054
23:00 | 432 | 6756 | 4195 | 10951
23:30 | 754 | 6510.5 | 4291 | 10801.5
24:00 | 1076 | 6265 | 4387 | 10652
11950 MW (19:30 )
9376 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-05-17 |  | Energy |  | 237512440
[13 empty] | 2023-05-17 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3324 | 804 | 2048 | 0 | 1464 | 2297 | 0 | 151 | 430 | 134 | 0 | 0
0:30 | 3157 | 810 | 2008.5 | 167 | 1223 | 2196 | 0 | 151 | 325 | 132 | 0 | 0 |  | Date: | 43601
1:00 | 2990 | 816 | 1969 | 334 | 982 | 2095 | 0 | 151 | 220 | 130 | 0 | 0
1:30 | 2974 | 834.5 | 1961.5 | 271 | 964.5 | 2087.5 | 0 | 151 | 264.5 | 130 | 0 | 0 | [7 empty] | Total Energy | 237.5124 |  | Total Energy Gen MKWHr Energy Not Served MKWHr Energy Requirement MKWHr | Total Energy Gen 237.512 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 237.512 MKWHr
2:00 | 2958 | 853 | 1954 | 208 | 947 | 2080 | 0 | 151 | 309 | 130 | 0 | 0 | [7 empty] | Energy not Served | 0
2:30 | 2964.5 | 882 | 1963.5 | 114.5 | 922 | 2058 | 0 | 151 | 333 | 129 | 0 | 0 | [7 empty] | Energy Requirement | 237.5124
3:00 | 2971 | 911 | 1973 | 21 | 897 | 2036 | 0 | 151 | 357 | 128 | 0 | 0
3:30 | 2977.5 | 911 | 1975 | 10.5 | 800.5 | 1986 | 0 | 151 | 292.5 | 126 | 0 | 0
4:00 | 2984 | 911 | 1977 | 0 | 704 | 1936 | 0 | 151 | 228 | 124 | 0 | 0
4:30 | 2996.5 | 910.5 | 1900 | 0 | 641.5 | 1889.5 | 0 | 115.5 | 228 | 120 | 0 | 0
5:00 | 3009 | 910 | 1823 | 0 | 579 | 1843 | 0 | 80 | 228 | 116 | 0 | 0
5:30 | 3009.5 | 910.5 | 1815 | 0 | 568.5 | 1815.5 | 0 | 70.5 | 227.5 | 113 | 4.5 | 0
6:00 | 3010 | 911 | 1807 | 0 | 558 | 1788 | 0 | 61 | 227 | 110 | 9 | 0
6:30 | 2978 | 911 | 1801.5 | 0 | 581.5 | 1786 | 0 | 58.5 | 227 | 110 | 23 | 0 | [6 empty] | Coal
7:00 | 2946 | 911 | 1796 | 0 | 605 | 1784 | 0 | 56 | 227 | 110 | 37 | 0
7:30 | 2945 | 911 | 1791.5 | 0 | 628 | 1783.5 | 0 | 54.5 | 227 | 118 | 81.5 | 0 | [5 empty] | Oil
8:00 | 2944 | 911 | 1787 | 0 | 651 | 1783 | 0 | 53 | 227 | 126 | 126 | 0
8:30 | 2921.5 | 911 | 1717 | 0 | 630 | 1772 | 0 | 76.5 | 226 | 124 | 160.5 | 0
9:00 | 2899 | 911 | 1647 | 0 | 609 | 1761 | 0 | 100 | 225 | 122 | 195 | 0
9:30 | 2786 | 910.5 | 1434 | 0 | 527.5 | 1755 | 0 | 145 | 185.5 | 129 | 224 | 0
10:00 | 2673 | 910 | 1221 | 0 | 446 | 1749 | 0 | 190 | 146 | 136 | 253 | 0
10:30 | 2782 | 910.5 | 1384.5 | 0 | 568 | 1730.5 | 12.5 | 211.5 | 168 | 95 | 259.5 | 0
11:00 | 2891 | 911 | 1548 | 0 | 690 | 1712 | 25 | 233 | 190 | 54 | 266 | 0
11:30 | 2935.5 | 911 | 1691 | 0 | 813.5 | 1687.5 | 25 | 242.5 | 213.5 | 81 | 347.5 | 0
12:00 | 2980 | 911 | 1834 | 0 | 937 | 1663 | 25 | 252 | 237 | 108 | 429 | 0
12:30 | 3016 | 911 | 1839 | 0 | 1046 | 1726.5 | 25 | 161.5 | 265.5 | 110 | 377.5 | 0
13:00 | 3052 | 911 | 1844 | 0 | 1155 | 1790 | 25 | 71 | 294 | 112 | 326 | 0
13:30 | 3052 | 911 | 1844 | 0 | 1155 | 1790 | 25 | 71 | 294 | 112 | 326 | 0
14:00 | 3052 | 911 | 1844 | 0 | 1155 | 1790 | 25 | 71 | 294 | 112 | 326 | 0
14:30 | 3103 | 910 | 1820.5 | 135 | 1231.5 | 1945 | 25 | 111.5 | 296.5 | 118 | 289 | 0
15:00 | 3154 | 909 | 1797 | 270 | 1308 | 2100 | 25 | 152 | 299 | 124 | 252 | 0
15:30 | 3164 | 909.5 | 1787 | 325 | 1390.5 | 2127.5 | 25 | 151 | 309.5 | 126 | 190 | 0
16:00 | 3174 | 910 | 1777 | 380 | 1473 | 2155 | 25 | 150 | 320 | 128 | 128 | 0
16:30 | 3152 | 910 | 1784.5 | 305.5 | 1544.5 | 2132 | 25 | 150.5 | 376 | 126 | 96 | 0
17:00 | 3130 | 910 | 1792 | 231 | 1616 | 2109 | 25 | 151 | 432 | 124 | 64 | 0 | [9 empty] | 472
17:30 | 3098.5 | 910 | 1737.5 | 115.5 | 1680.5 | 2068 | 25 | 133 | 476 | 123 | 38.5 | 0 | [9 empty] | 100
18:00 | 3067 | 910 | 1683 | 0 | 1745 | 2027 | 25 | 115 | 520 | 122 | 13 | 0 | [9 empty] | 20
18:30 | 3161.5 | 910 | 1746 | 30 | 2197 | 2069 | 25 | 112.5 | 550.5 | 132 | 6.5 | 0 | [9 empty] | 592
19:00 | 3256 | 910 | 1809 | 60 | 2649 | 2111 | 25 | 110 | 581 | 142 | 0 | 0
19:30 | 3217 | 910 | 1858 | 0 | 2791 | 2275 | 25 | 151 | 579 | 144 | 0 | 0
20:00 | 3098 | 801 | 1827 | 0 | 2711 | 2157 | 25 | 150 | 654 | 146 | 0 | 0
20:30 | 3092.5 | 801.5 | 1867 | 0 | 2667.5 | 2108.5 | 25 | 140 | 629.5 | 141 | 0 | 0
21:00 | 3087 | 802 | 1907 | 0 | 2624 | 2060 | 25 | 130 | 605 | 136 | 0 | 0
21:30 | 3091.5 | 802 | 1964.5 | 0 | 2502.5 | 2061.5 | 25 | 140 | 541.5 | 138 | 0 | 0
22:00 | 3096 | 802 | 2022 | 0 | 2381 | 2063 | 25 | 150 | 478 | 140 | 0 | 0
22:30 | 3234.5 | 802 | 2036 | 0 | 2107.5 | 2119.5 | 12.5 | 150 | 453 | 139 | 0 | 0
23:00 | 3373 | 802 | 2050 | 0 | 1834 | 2176 | 0 | 150 | 428 | 138 | 0 | 0
23:30 | 3348.5 | 803 | 2049 | 0 | 1649 | 2236.5 | 0 | 150.5 | 429 | 136 | 0 | 0 |  | Max Temp. in Dhaka |  | 31.1° C
24:00 | 3324 | 804 | 2048 | 0 | 1464 | 2297 | 0 | 151 | 430 | 134 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 237.512 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 237.512 MKWHr
Note on W13: Author:

## Generation
g | 2023-05-17
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | [10 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 0 |  | 304000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP |  | 4 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 |  |  |  | 0 | 1 |  | 18 | 25 | 25 | 25 | 25 | 13 | 8 | 209451
| Teknaf 20MW PP (Solartech) | [7 empty] | 8 | 15 | 16 |  | 19 | 18 | 14 | 13 | 7 | 1 | 0 | [8 empty] | 114615
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil) | 151 | 151 | 151 | 151 | 80 | 61 | 31 | 31 | 31 | 76 | 50 | 71 | 71 | 71 | 152 | 150 | 151 | 115 |  | 110 | 151 | 150 | 130 | 150 | 150 | 151 | 2577305
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 79 | 84 | 84 | 34 | 34 | 33 | 33 | 33 | 33 | 52 | 84 | 82 | 83 | 77 | 84 | 67 | 84 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1623037
12 | Hathazari 100 MW peaking PP | 55 | 55 | 55 | 24 | 24 | 24 | 24 | 24 | 32 | 40 | 32 | 34 | 40 | 48 | 40 | 32 | 32 | 56 |  | 66 | 66 | 66 | 57 | 57 | 57 | 57 | 1017312
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 24 | 34 | 34 | 34 | 34 | 34 | 51 | 51 | 75 |  | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 1072218
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 36 | 37 | 38 | 37 | 37 | 37 | 37 | 37 | 30 | 30 |  | 30 | 36 | 39 | 39 | 39 | 39 | 39 | 872656
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [17 empty] | 0 |  | 105 | 103 | 62 | 40 | 41 | 102 | 102 | 428000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 47 | 47 | 47 | 15 | 15 | 15 | 15 | 15 | 37 | 15 | 15 | 32 | 47 | 47 | 47 | 47 | 47 | 57 |  | 190 | 195 | 195 | 195 | 195 | 195 | 195 | 1836655
19 | Ashuganj 195MW PP (APSCL-United) | 197 | 197 | 199 | 199 | 199 | 189 | 138 | 138 | 138 | 68 | 70 | 120 | 120 | 128 | 128 | 128 | 147 | 147 |  | 147 | 148 | 148 | 158 | 158 | 168 | 168 | 3629818
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 120 | 120 | 120 | 119 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2796938
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4258800
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 42 | 42 | 42 | 42 | 43 | 42 | 42 | 42 | 38 | 38 | 36 | 39 | 42 | 41 | 40 | 37 | 37 | 37 |  | 40 | 40 | 41 | 42 | 42 | 42 | 42 | 956880
33 | Ashuganj 225 MW CCPP | 202 | 179 | 179 | 180 | 180 | 191 | 186 | 179 | 150 | 152 | 183 | 178 | 182 | 198 | 203 | 205 | 183 | 180 |  | 180 | 180 | 180 | 184 | 180 | 209 | 198 | 4538000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 340 | 310 | 310 | 310 | 310 | 325 | 310 | 305 | 280 | 280 | 310 | 310 | 315 | 335 | 345 | 350 | 320 | 290 |  | 310 | 310 | 275 | 285 | 280 | 335 | 315 | 7917100
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 146 | 202 | 205 | 248 | 318 | 322 | 322 | 322 | 359 | 329 | 346 | 392 | 394 | 397 | 399 | 403 | 405 | 402 |  | 402 | 401 | 383 | 315 | 333 | 404 | 405 | 8286210
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 400 | 330 | 420 | 450 | 450 | 450 | 450 | 450 | 450 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 10164000
41 | Haripur 360MW CCPP(HPL) | 341 | 336 | 343 | 352 | 351 | 302 | 302 | 302 | 297 | 272 | 353 | 342 | 331 | 326 | 327 | 328 | 327 | 273 |  | 293 | 313 | 312 | 353 | 353 | 350 | 350 | 7888000
42 | RPCL 210MW CCPP | 85 | 85 | 98 | 99 | 99 | 99 | 46 | 46 | 47 | 46 | 44 | 43 | 43 | 33 | 33 | 33 | 44 | 44 |  | 50 | 52 | 56 | 82 | 72 | 74 | 74 | 1404480
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 5 | 3 | 0 | 1 | 5 | 11 | 55 | 52 | 47 | 37 | 14 | 7 | 1 |  | 0 | [6 empty] | 246270
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1018000
45 | Fenchugonj CCPP Phase-2 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 29 | 29 | 29 | 30 | 30 | 29 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 658080
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 56 | 57 | 57 | 57 | 45 | 45 | 45 | 45 | 63 | 40 | 57 | 63 | 63 | 61 | 61 | 61 | 59 | 62 |  | 62 | 63 | 63 | 62 | 63 | 63 | 62 | 1364544
48 | Shahjibazar 86MW PP (Shahjibazar) | 72 | 72 | 72 | 72 | 30 | 30 | 30 | 30 | 66 |  | 50 | 72 | 74 | 74 | 74 | 74 | 74 | 77 |  | 77 | 77 | 77 | 77 | 77 | 78 | 78 | 1492800
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 204 | 204 | 203 | 203 | 205 | 206 | 207 | 207 | 207 | 200 | 209 | 207 | 207 | 207 | 202 | 200 | 200 | 201 |  | 207 | 207 | 209 | 212 | 212 | 211 | 208 | 5229260
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 410000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 10 | 9 | 10 | 10 | 10 | 10 | 10 | 237780
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [6 empty] | 2 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 168432
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 22 | 22 | 22 | 22 | 47 | 5 | 22 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1020000
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 411648
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 285 | 290 | 285 | 285 | 290 | 290 | 285 | 265 | 210 | 220 | 290 | 285 | 285 | 285 | 285 | 285 | 285 |  | 290 | 290 | 290 | 290 | 295 | 290 | 290 | 6831000
| Bibiyana South 400 MW | 400 | 400 | 400 | 386 | 400 | 360 | 400 | 400 | 400 | 340 | 400 | 400 | 400 | 395 | 390 | 385 | 394 | 400 |  | 400 | 378 | 370 | 400 | 400 | 400 | 400 | 9314700
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | [9 empty] | 10 | 35 | 35 | 35 | 0 |  |  | 17 | 17 | 17 | 17 | 55 | 55 | 55 | 464284
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  |  |  | 5 | 8 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 253440
60 | Barabkunda 22 MW PP (Regent) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 10 | 8 | 10 | 5 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 198576
61 | Narshingdi 22 MW PP (Doreen) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  |  |  |  | 19 | 19 | 20 | 20 | 20 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 314136
62 | Tangail 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 |  |  |  |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 18 | 18 | 18 | 18 |  | 18 | 18 | 317916
63 | Impoprt (Tripura) | 130 | 130 | 128 | 124 | 116 | 110 | 110 | 126 | 122 | 136 | 54 | 108 | 112 | 114 | 124 | 128 | 124 | 122 |  | 142 | 144 | 146 | 136 | 140 | 138 | 134 | 2976000
64 | Malancha, Ctg. EPZ (United) | 26 | 20 | 25 | 26 | 33 | 33 | 17 | 7 | 5 | 2 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 4 |  | 10 | 17 | 17 | 22 | 29 | 29 | 38 | 366720
65 | Feni 22MW PP (Doreen) | [15 empty] | 0 | 9 | 14 |  | 14 | 14 | 16 | 16 | 17 | 17 | 17 | 121356
66 | Feni 11 MW PP (Doreen) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 6 |  |  | 0 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 115920
67 | Jangalia 33MW PP (Summit) | [16 empty] | 0 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 172600
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 18 | 18 | 20 | 9 | 21 | 21 | 12 |  |  | 3 | 3 | 9 | 9 | 9 | 9 |  | 18 | 18 | 18 | 20 | 18 | 15 | 18 | 281750
69 | Summit Ashulia | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 22 | 22 | 22 | 22 | 22 | 23 | 552000
70 | Summit Madhabdi | 27 | 27 | 25 | 25 | 25 | 25 | 25 | 25 | 27 | 0 | 0 | 17 | 25 | 27 | 27 | 27 | 27 | 20 |  | 20 | 20 | 27 | 27 | 27 | 27 | 27 | 540540
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 25 | 25 | 25 | 33 | 33 | 0 | 25 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 636200
72 | Rupganj 33 MW PP(Summit) | 32 | 32 | 32 | 32 | 32 | 32 | 25 | 30 | 28 |  | 15 | 22 | 22 | 30 | 30 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 692500
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 52 | 52 | 52 | 52 | 52 | 17 | 17 | 17 | 52 | 38 | 17 |  |  |  | 0 | 17 | 114 | 114 |  | 114 | 70 | 17 | 17 | 17 | 114 | 114 | 1011180
| Chowmuhani 113 MW | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 15 | 26 | 26 | 26 | 28 | 28 | 28 | 28 | 28 |  | 95 | 95 | 94 | 96 | 103 | 32 | 9 | 714840
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 108 | 108 | 108 | 108 | 108 | 79 | 17 | 1095840
77 | Siddhirganj 100 PP(Dutch Bangla) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  |  | 7 | 9 | 9 | 9 | 9 | 9 | 10 |  | 18 | 18 | 18 | 18 | 18 | 10 | 9 | 214080
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  |  | 6 | 8 | 8 | 8 | 8 | 50 |  | 50 | 50 | 50 | 50 | 42 | 42 | 8 | 388800
79 | Kodda 150 MW PP | 32 | 64 | 64 | 16 | 16 | 16 | 16 | 16 | 32 |  |  | 48 | 98 | 98 | 98 | 98 | 98 | 115 |  | 150 | 150 | 150 | 150 | 150 | 98 | 100 | 1662720
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [13 empty] | 6 | 12 | 36 | 50 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 461698
| Gazipur 100 MW PP | 88 | 88 | 88 | 51 | 17 | 17 | 17 | 17 | 30 | 2 | 11 | 50 | 88 | 88 | 88 | 88 | 88 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 1593734
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 4 | 4 | 5 | 5 | 2 | 0 |  | 0 | 0 | [9 empty] | 24238
| Jodiac Power | 17 |  |  |  | 3 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 378500
| Karnaphuli Power Ltd. | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 19 | 51 | 51 | 54 | 54 | 54 | 54 | 66 | 93 | 94 |  | 106 | 106 | 106 | 106 | 106 | 106 | 67 | 1524684
82 | Madanganj 102 PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 7 |  | 5 | 17 | 17 | 17 | 17 | 17 | 20 |  | 70 | 79 | 81 | 85 | 55 | 17 | 17 | 543900
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [8 empty] | 11 | 7 |  | 4 | 18 | 0 | 8 | 0 | [9 empty] | 0 | 60883
86 | Meghnaghat CCPP ( Summit) | [14 empty] | 0 | 10 | 10 | 10 |  | 25 | 52 | 80 | 130 | 130 | 150 | 145 | 569396
87 | Meghnaghat 100 MW(IEL) | 8 | 9 | 8 | 9 | 9 | 8 | 9 | 8 | 9 | 8 | 9 | 8 | 12 | 11 | 8 | 9 | 8 | 9 |  | 8 | 8 | 9 | 8 | 9 | 8 | 9 | 201600
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 22 | 17 | 17 | 17 | 17 | 17 | 19 | 33 | 43 | 53 | 53 | 53 |  | 48 | 50 | 53 | 53 | 36 | 26 | 17 | 714240
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 100 | 92 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 10 | 22 | 10 | 525120
92 | Fenchuganj 44MW (Energyprima) | 50 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 46 | 5 | 17 | 40 | 47 | 50 | 47 | 47 | 47 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1085184
93 | Ashuganj 51 MW PP (Midland) | 43 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 5 | 17 | 25 | 34 | 34 | 34 | 34 | 34 | 34 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 833556
94 | Gagnagar 102 MW PP (Digital Power) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 24 | 24 | 24 | 24 | 24 | 32 | 33 | 33 |  | 50 | 50 | 50 | 50 | 50 | 24 | 24 | 626112
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 2 | 12 | 19 | 0 |  | 44 | 44 | 44 | 44 | 44 | 44 | 6 | 358080
96 | Chattogram 108 MW PP (ECPV) | [13 empty] | 12 | 12 | 12 | 17 | 30 |  | 30 | 30 | 30 | 30 | 30 | 21 | 0 | 227520
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [11 empty] | 5 | 15 | 0 |  |  |  | 0 |  | 12 | 15 | 55 | 55 |  |  | 0 | 160120
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 17 |  | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 0 | 606563
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | [5 empty] | 2 | 2 | 2 | 1 | 1 | 1 | 0 | [8 empty] | 7900
103 | Kamalaghat 54 MW PP(Banco Energy) | [14 empty] | 0 | 17 | 17 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 0 | 260280
104 | Keranigonj 300 MW PP (APR) | 254 | 140 | 10 | [10 empty] | 0 | 270 | 300 | 151 | 0 |  | 20 | 0 |  |  |  |  | 0 | 1158552
105 | Bramhangoan 100 MW PP (Aggreko) | 40 | 28 | 11 | [11 empty] | 0 | 40 | 40 | 0 |  | 40 | 0 |  |  |  |  | 0 | 184716
106 | Mymensingh 200 MW PP (United) | 47 | 47 | 47 | 46 | 46 | 46 | 46 | 46 | 8 |  | 16 | 47 | 47 | 47 | 47 | 47 | 47 | 56 |  | 84 | 84 | 84 | 84 | 84 | 28 | 28 | 1120800
112 | Aurahati 100MW PP (Aggreko) | 40 | 40 | [12 empty] | 0 | 40 | 40 | 0 | [7 empty] | 0 | 201768
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 24 | 20 | 86 | 133 | 48 | 17 | 17 | 17 | 40 |  | 132 | 132 | 132 | 133 | 132 | 56 | 17 | 1170288
115 | Juldah 100 MW PP Unit-3 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 12 | 12 | 426240
116 | Chandpur 200MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 426240
117 | Ashuganj 150MW PP (Midland) | 80 | 18 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 10 | 10 | 16 | 20 | 20 | 20 | 20 | 25 | 37 |  | 115 | 150 | 150 | 155 | 155 | 62 | 20 | 1080581
118 | Bibiyana-III 400 MW CCPP | 400 | 366 | 366 | 367 | 367 | 375 | 367 | 367 | 367 | 317 | 366 | 367 | 356 | 397 | 402 | 404 | 380 | 319 |  | 366 | 367 | 318 | 322 | 343 | 390 | 375 | 8866000
| Jamalpur 115 MW PP (United) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 8 |  | 14 | 47 | 47 | 47 | 47 | 47 | 58 | 58 |  | 88 | 88 | 88 | 89 | 89 | 49 | 49 | 1045200
| Anwara 300 MW PP (United) | 87 | 87 | 87 | 87 | 45 | 45 | 45 | 45 | 85 | 85 | 85 | 86 | 87 | 86 | 87 | 88 | 87 | 121 |  | 273 | 275 | 278 | 279 | 122 | 88 | 87 | 2529164
| Juldah unit-2 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 12 | 12 | 456960
| Anlima Energy Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 426545
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 20 | 17 | 17 |  | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 24 | 35 | 35 | 35 | 35 | 35 | 35 | 643320
| Spectra Solar Plant Ltd. | [5 empty] | 2 | 5 | 6 | 1 | 30 | 34 | 35 | 33 | 29 | 0 | 13 | 6 | 0 | [8 empty] | 181763
| Chandpur 115(Doreen) | 22 | 18 | 18 | 18 | 17 | 18 | 18 | 18 | 18 | 19 | 50 | 54 | 55 | 59 | 55 | 54 | 54 | 54 |  | 61 | 108 | 100 | 115 | 115 | 57 | 36 | 1114560
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 2 | 17 | 17 | 17 | 17 | 17 | 30 | 34 |  | 34 | 34 | 34 | 34 | 34 | 35 | 21 | 532440
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 43 | 78 | 163 | 163 | 36 | 36 | 36 | 981891
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 5657 | 5433 | 5281 | 5059 | 4878 | 4784 | 4621 | 4619 | 4653 | 3988 | 4676 | 5397 | 5578 | 5612 | 5911 | 6128 | 6089 | 5939 |  | 7146 | 7279 | 7248 | 7332 | 7010 | 6756 | 6265 | 136699723
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [12 empty] | 16 | 28 | 44 | 46 | 46 | 18 |  | 16 | 16 | 0 |  |  |  | 16 | 237120
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL) | [6 empty] | 25 | 22 | 69 | 114 | 183 | 181 | [14 empty] | 491949
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [12 empty] | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 223200
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 2 | 14 | 51 | 65 | 82 | 98 | 105 | 83 | 67 | 73 | 27 | 24 | 5 |  | 0 | [5 empty] | 0 | 654480
131 | Rampal 1320 MW (BIFPCL) | 373 | 373 | 373 | 373 | 372 | 372 | 372 | 371 | 372 | 372 | 368 | 318 | 370 | 372 | 369 | 375 | 370 | 375 |  | 377 | 370 | 370 | 370 | 374 | 378 | 338 | 8800000
132 | United Payra Power Ltd. | [13 empty] | 0 | 3 | 17 | 17 | 35 |  | 35 | 0 |  |  |  |  | 0 | 114000
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [14 empty] | 0 | 16 | 16 | 16 |  | 16 | 16 | 16 | 0 |  |  | 0 | 92736
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 203 | 221 | 202 | 201 | 153 | 152 | 152 | 154 | 152 | 152 | 155 | 153 | 153 | 153 | 152 | 153 | 153 | 153 |  | 152 | 152 | 153 | 153 | 153 | 202 | 203 | 4014500
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 184 | 184 | 184 | 166 | 183 | 184 | 184 | 184 | 183 | 180 | 180 | 180 | 180 | 179 | 180 | 180 | 180 | 180 |  | 180 | 163 | 180 | 180 | 180 | 180 | 180 | 4342536
140 | Bhola 33 MW PP (Venture) |  | 10 | 11 | 11 | 11 | 11 | 10 | 10 | 10 | 7 | 12 | 14 | 8 | 6 | 12 | 13 | 19 | 17 |  | 25 | 25 | 25 | 25 | 26 | 24 | 24 | 358587
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [12 empty] | 16 | 16 | 16 | 16 | 16 | 8 |  | 8 | 0 |  |  |  |  | 8 | 94500
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [13 empty] | 34 | 50 | 50 | 50 | 15 |  | 22 | 50 | 15 | 0 |  |  | 0 | 261792
146 | Bheramara HVDC | 816 | 853 | 911 | 911 | 910 | 911 | 911 | 911 | 911 | 910 | 911 | 911 | 911 | 909 | 909 | 910 | 910 | 910 |  | 910 | 910 | 801 | 802 | 802 | 802 | 804 | 20850181
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 750 | 770 | 720 | 620 | 580 | 520 | 520 | 510 | 500 | 500 | 500 | 500 | 580 | 840 | 950 | 980 | 930 | 800 |  | 850 | 1020 | 900 | 800 | 800 | 870 | 1020 | 19408500
149
150 | Barapukuria TPP Unit-1 | 73 | 72 | 74 | 76 | 76 | 77 | 77 | 76 | 75 | 76 | 76 | 75 | 72 | 72 | 70 | 70 | 70 | 70 |  | 73 | 73 | 73 | 74 | 74 | 73 | 74 | 1746327
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 249 | 220 | 220 | 220 | 220 | 170 | 170 | 170 | 225 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 5792000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [15 empty] | 0 | 28 | 28 |  | 28 | 0 | [5 empty] | 82640
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 0 | 0 | 4 | 3 | 3 | 5 | 3 | 3 | 2 | 0 | 0 | [8 empty] | 30840
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 166 | 166 | 166 | 166 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 152 | 172 | 171 | 172 | 169 | 165 | 163 |  | 160 | 160 | 160 | 160 | 163 | 163 | 163 | 3957400
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 174 | 172 | 172 | 172 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 153 | 166 | 166 | 162 | 160 | 160 |  | 158 | 158 | 157 | 157 | 160 | 158 | 156 | 4004064
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 415 | 418 | 417 | 416 | 329 | 367 | 430 | 436 | 308 | 303 | 350 | 401 | 416 | 390 | 360 | 328 | 319 | 258 |  | 319 | 313 | 253 | 227 | 329 | 336 | 330 | 8494945
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP |  |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  |  |  |  | 0 | 4 | 6 | 17 | 28 |  | 28 | 13 | 0 |  |  |  |  | 213931
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 16 | 16 | 21 | 5 | 5 | 19 | 18 | 18 | 19 | 19 | 19 | 19 |  | 20 | 21 | 22 | 22 | 22 | 22 | 22 | 450960
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 98838
165 | Amnura 50 MW PP(Sinha) |  | 21 | 21 | 21 | 21 | 21 | 28 | 28 |  |  |  |  | 3 | 14 | 28 | 28 | 28 | 28 |  | 28 | 28 | 0 |  |  |  | 0 | 332490
166 | Katakhali 50 MW PP (Northern) | 34 | 34 | 34 | 8 | 8 | 8 | 8 | 8 | [6 empty] | 0 | 25 | 25 | 8 |  | 8 | 0 |  |  |  |  | 16 | 201650
167 | Katakhali 50 MW Peaking PP |  | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 15 | [6 empty] | 0 | 24 | 40 |  | 40 | 40 | 40 | 0 |  |  |  | 344835
168 | Santahar 50 MW Peaking PP |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | [6 empty] | 0 | 10 | 29 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 424679
169 | Natore 52 MW PP (Rajlanka) | 16 | 43 | 52 | 8 | 8 | 8 | 8 | 8 |  |  |  |  | 18 | 25 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 0 |  |  | 0 | 500770
170 | Chapainawabganj 100 MW Peaking PP | [14 empty] | 0 | 44 | 73 | 74 |  | 82 | 82 | 82 | 82 | 82 | 84 | 84 | 655096
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 |  |  |  |  | 14 | 35 |  |  |  |  | 10 | 35 | 35 | 35 | 35 | 35 |  | 40 | 50 | 50 | 50 | 50 | 35 | 35 | 662496
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 |  |  |  |  | 35 | 35 |  |  |  |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 57 | 57 | 57 | 57 | 57 | 35 | 35 | 650688
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 33 | 27 | 33 | 14 |  |  |  | 34 | 34 |  |  |  |  | 5 | 33 | 33 | 33 | 33 |  | 45 | 78 | 86 | 95 | 86 | 88 | 88 | 747926
177 | Sympa Solar Power 8MW | [9 empty] | 1 | 1 | 4 | 5 | 5 | 0 | 3 | 2 | 1 |  | 0 | [6 empty] | 22701
178 | Energypac Power Venture Thakurgaon Ltd. | [12 empty] | 12 | 35 | 35 | 35 | 35 | 35 |  | 64 | 109 | 113 | 72 | 72 | 37 | 77 | 664512
| Intraco Solar 30 MW | [7 empty] | 9 | 15 | 14 | 17 | 35 | 21 | 22 | 16 | 6 | 4 | 1 |  | 0 | [6 empty] | 156950
| Adani Power Jharkhanda Ltd | 436 | 384 | 407 | 406 | 402 | 407 | 403 | 412 | 402 | 400 | 393 | 397 | 395 | 393 | 389 | 407 | 416 | 404 |  | 399 | 400 | 401 | 403 | 402 | 393 | 402 | 9741818
178 | Teesta Solar Limited | [6 empty] | 14 | 49 | 94 | 97 | 97 | 166 | 105 | 95 | 109 | 55 | 19 | 5 |  | 0 | [6 empty] | 890080