## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-05-19 | Friday
|  | Date (day): | 2023-05-19 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11402.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14052 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-05-18 | 2023-05-19 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 100 | 120 | 120 | 60 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 392 | 398 | 400 | 400 | 12 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 346 | 348 | 350 | 350 | 10 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 9 | 8 | 8 | 92 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 317 | 270 | 320 | 320 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 17 | 85 | 17 | 85 |  | 17 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 30 | 0 | 25
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 20 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 10 | 10 | 19 | 19
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | GT-1 Under maint & Gas Shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 9 | 17 | 9 | 40 | 60 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 41 | 24 | 50 | 52 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 0 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 100 | 82 | 100 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 28 | 49 | 47 | 47 |  | 33 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 31 | 25 | 25 |  | 8 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 49 | 16 | 48
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 47 | 195 | 45 | 195 | 105 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 290 | 0 | 300 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 40 | 0 | 40 | 40 | 60 |  | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 40 | 0 | 40 | 50 |  | 50 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 116 | 114 | 17 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 88 | 88 | 88 |  | 17 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 53 | 17 | 53 | 51 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 72 | 108 | 72 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 19 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 34 | 17 | 34 | 21 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5867 | 2850 | 2899 | 2854 | 3566 | 1036 | 1200
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 25 | 25 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 0 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 44 | 6 | 40 | 10 |  | Fuel shortage
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 25 | 25 | 25 | 25 | 205 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 211 | 220 | 220 | 5 |  | Gas shortage
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 87 | 17 | 87 | 18 |  | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 20 | 66 | 54 | 58 |  | 40 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 84 | 67 | 84 |  | 18 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 100 | 33 | 22 | 33 | 67 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 38 | 38 | 38 | 38 | 62 |  | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 7 | 0 | 10 | 11 | 11 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 7 | 15 | 20
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 30 | 0 | 30 | 78 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 87 | 290 | 88 | 300
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 54 | 92 | 54 | 105 |  | 5 | Engine problem
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 38 | 38 | 25 | 25 | 75 |  | Fuel shortage
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 17 | 99 |  | Fuel shortage
| Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 35 | 62 | 35 | 163 |  |  | On test.
| Chattogram area Total |  |  |  |  | 2605 | 2545 | 508 | 1166 | 760 | 1298 | 847 | 393
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 207 | 212 | 200 | 200 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 350 | 310 | 350 | 350 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 250 |  | 110 | ST synchronization process
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 34 | 35 | 40 | 40
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 130 | 167 | 130 | 150 | 45 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 21 | 150 | 20 | 150
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 38 | 35 | 35 |  | 17 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 17 | 17 | 17 | 183 |  | Fuel shortage
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 5 | 5 | 7 |  | 4 | Engine problem
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 118 | 138 | 129 | 152
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 52
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 6 | 12 | 21 | 21 |  | 4 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Contract Expired
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 98 | 67 | 114 | 114
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 95 | 26 | 113
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 35 | 35 | 35 |  | 19 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 54 | 102 | 54 | 115
| Cumilla Area Total |  |  |  |  | 3159 | 3096 | 1147 | 1477 | 1262 | 1887 | 228 | 737
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 44 | 49 | 42 | 80 | 122 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 15 | 17 | 17 | 5 |  | Gas shortage
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 88 | 68 | 85 | 115 |  | Fuel shortage
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 88 | 18 | 88 | 27 |  | Fuel shortage
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 53 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 | 10 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 234 | 252 | 208.6 | 282 | 127 | 0
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 50 | 51 | 51
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 48 | 48 | 48 | 48
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 80 | 84 | 84
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 50 | 135 | 135 | 135 |  | 96 | ST under maint.
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 0 | 17 | 18
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 16 | 16 | 16 | 9 |  | Gas shortage
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 250 | 290 | 300 |  |  | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 404 | 367 | 400 | 400 |  |  | FGMO
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 330 | 315 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1362 | 1325 | 1505 | 1516 | 9 | 806
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 907 | 905 | 928 | 928
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 66 | 66 | 83 |  | 32 | Engine problem
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 25 | 20 | 43 |  | 11 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 60 | 70 |  | 39 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 24 | 40
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 17 | 17 | 88 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 50 | 85 | 105
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 35 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 328 | 326 | 330 | 330 |  |  | Coal Shortage.
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 2905 | 2901 | 1270 | 1397 | 1630 | 1616 | 744 | 82
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 0 | 16 | 94 |  | Fuel shortage
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 19 | 23 | 22 | 35 |  | 5 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 137 | 106 | 130 | 130
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 760 | 1060 | 700 | 1244
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maintenance
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 17 | 150
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 152 | 182 | 150 | 150
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1068 | 1404 | 1019 | 1725 | 94 | 225
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 28 | 28 | 28 |  | 24 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 28 | 15 | 35 |  | 36 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 28 | 28 | 14 | 21 | 21
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 8 | 42 | 42 |  | 8 | Engine problem
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 32 | 40 | 24 | 40 |  | 10 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 178 | 177 | 170 | 170 | 40 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 170 | 170 | 50 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 416 | 418 | 400 | 400
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 22 | 28 | 28 | 34 |  | 16 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 20 | 20
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 8 | 8 |  | 3 | Engine problem
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 43 | 30 | 52
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 54 | 54 | 80 | 80 |  | 24 | Enginr problem
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 50 | 35 | 50 | 63 |  | Fuel shortage
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 55 | 35 | 55 | 58 |  | Fuel shortage
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 748*1 | 748 | 748 | 0 | 400 | 400 | 400 |  |  | On test.
| Rajshahi Area Total |  |  |  |  | 2927 | 2905 | 928 | 1373 | 1512 | 1605 | 802 | 121
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 76 | 74 | 75 | 75 | 10 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 260 | 260 | 260 | 260
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 33 | 81 | 34 | 107 | 6 |  | Fuel shortage
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 115 | 115 | 115
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 24 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 58 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 488 | 530 | 652 | 557 | 56 | 85
| Total |  |  |  |  | 24143 | 23370 | 9855 | 11823 | 11402.6 | 14052 | 3943 | 3649
A. |  | 2023-05-18 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 11823 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 4959 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11823 | MW
3 | Day peak Generation : |  |  | 9855 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11271.4 | MW
4 | Evening peak Generation : |  |  | 11823 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 226.2974 | MKWHr | By Solar | 1.9616 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 112.2063 | MKWHr |  | By Oil: | 43.7665 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 45.3238 | MKWHr |  | By Hydro: | 0.3 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3943 | MW | Dhaka | 4518.9 | 4518.9 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3649 | MW | Chittagong | 1033.9 | 1033.9 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 7592 | MW | Khulna | 953 | 953 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 871.67 | MMCFD |  |  | Rajshahi | 1237.6 | 1237.6 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 125694737.306 | ii) Oil : | Taka | 606801021.52 | Comilla | 1046 | 1046 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 246647340.9 | Total | Taka | 979143099.726 | Mymensingh | 938 | 938 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 444 | 444 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 712 | MW (E to W) at | 19:30 | hrs | Barisal | 335 | 335 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 460 | MW at | 6:00 | hrs | Rangpur | 765 | 765 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 32.1° C |  |  | Total | 11271.4 | 11271.4 |  | 0
B. |  | 2023-05-19 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 32.1° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14052 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10500 | MW
4 | Reserve(Generation end) |  |  |  | 2052 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 229.6853 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8700 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.9898 | MKWHr. | ii) HVDC Flow at Peak Time |  | 905 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.7494 | MKWHr. | iii) Maximum HVDC Flow : |  | 948 | MW at | 13:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 73.74 |  | (b) Today: | 73.7 |  | (c) Rule Curve: |  | 78.96
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-05-18 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 404 | 310 |  | 0 | 450 | 268 | 8 | 17 | 0 | 0 | 0 | 57 | 9 | 16 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 15 | 23 | 27 | 33 | 33 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 152 | 0 | 0 |  | 12 | 57 | 84 | 10 | 0 | 6 | 6 | 34 | 0 | 0 | 0 | 280 | 0 | 197 | 170 | 0 | 42 | 0 | 0 | 43 | 0 | 39 | 52 | 17 | 6 | 25 | 18 | 124 | 75 | 0 | 18 | 0 | 43 | 30 | 50 | 50 | 0 | 0 | 62 | 78 | 0 | 210 | 18 | 0 | 10 | 290 | 16 | 0 | 0 | 72 | 0 | 0 | 27 | 0 | 17 | 0 | 12 | 17 | 18 | 344 | 49 | 88 | 17 | 0 | 88 | 17 | 70 | 114 | 9 | 12 | 350 | 17 | 0 | 17 | 17 | 0 | 35 | 0 | 20 | 17 | 0 | 17 | 0 |  | 860 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 34 | 0 | 52 | 30 | 22 | 0 | 5 | 75 | 0 | 260 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 331 | 17 | 0 | 35 | 0 | 33 | 0 | 0 | 35 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 203 | 405 | 0 | 0 |  | 5856 | 4347 | 10203 | 3156 | 860 | 2129 | 0 | 1169 | 2268 | 0 | 152 | 345 | 124 | 0 | 0 | 73.75
2:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 403 | 305 |  | 0 | 450 | 279 | 9 | 17 | 0 | 0 | 0 | 0 | 9 | 16 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 15 | 23 | 25 | 33 | 33 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 152 | 0 | 0 |  | 12 | 57 | 84 | 10 | 0 | 6 | 6 | 39 | 0 | 0 | 0 | 280 | 0 | 178 | 170 | 0 | 42 | 0 | 0 | 43 | 0 | 39 | 43 | 17 | 6 | 25 | 18 | 126 | 75 | 0 | 18 | 0 | 43 | 30 | 50 | 50 | 0 | 0 | 62 | 75 | 0 | 210 | 18 | 0 | 10 | 275 | 16 | 0 | 0 | 47 | 0 | 0 | 28 | 0 | 17 | 0 | 12 | 17 | 20 | 344 | 49 | 88 | 17 | 0 | 88 | 0 | 54 | 114 | 9 | 12 | 340 | 17 | 0 | 17 | 17 | 0 | 35 | 0 | 18 | 17 | 0 | 17 | 0 |  | 860 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 42 | 0 | 43 | 30 | 22 | 0 | 5 | 75 | 0 | 260 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 286 | 17 | 0 | 35 | 0 | 32 | 0 | 0 | 35 | 980 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 203 | 0 | 0 | 0 |  | 5697 | 3864 | 9561 | 3062 | 860 | 2076 | 0 | 1102 | 1839 | 0 | 152 | 344 | 126 | 0 | 0 | 73.75
3:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 362 | 305 |  | 0 | 400 | 270 | 8 | 12 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 15 | 23 | 25 | 33 | 33 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 |  | 12 | 57 | 84 | 10 | 0 | 6 | 6 | 39 | 0 | 0 | 0 | 280 | 0 | 180 | 130 | 0 | 43 | 0 | 0 | 5 | 0 | 39 | 52 | 17 | 6 | 25 | 18 | 124 | 74 | 0 | 19 | 0 | 43 | 30 | 50 | 50 | 0 | 0 | 63 | 40 | 0 | 210 | 18 | 0 | 10 | 280 | 16 | 8 | 0 | 0 | 0 | 0 | 28 | 0 | 17 | 0 | 12 | 17 | 18 | 343 | 49 | 17 | 17 | 0 | 88 | 0 | 54 | 20 | 9 | 12 | 340 | 17 | 0 | 0 | 17 | 0 | 35 | 0 | 17 | 17 | 0 | 0 | 0 |  | 860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 5 | 76 | 0 | 260 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 159 | 0 | 0 | 0 |  | 5208 | 3423 | 8631 | 3037 | 860 | 1912 | 0 | 628 | 1723 | 0 | 151 | 196 | 124 | 0 | 0 | 73.75
4:00 | 0 | 0 | 100 | 180 | 0 | 0 | 0 | 357 | 305 |  | 0 | 320 | 282 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 23 | 25 | 33 | 33 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 150 | 0 | 0 |  | 11 | 57 | 84 | 10 | 0 | 6 | 6 | 40 | 0 | 0 | 0 | 280 | 0 | 181 | 108 | 0 | 43 | 0 | 0 | 5 | 0 | 39 | 52 | 17 | 6 | 25 | 18 | 112 | 74 | 0 | 19 | 0 | 43 | 30 | 11 | 10 | 0 | 0 | 40 | 10 | 0 | 211 | 18 | 0 | 10 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 28 | 0 | 17 | 0 | 12 | 17 | 0 | 342 | 49 | 17 | 17 | 0 | 88 | 0 | 54 | 17 | 9 | 12 | 340 | 17 | 0 | 0 | 17 | 0 | 35 | 0 | 18 | 17 | 0 | 0 | 0 |  | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 76 | 0 | 260 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 152 | 0 | 0 | 0 |  | 4886 | 2972 | 7858 | 2935 | 895 | 1644 | 0 | 561 | 1365 | 0 | 150 | 196 | 112 | 0 | 0 | 73.75
5:00 | 0 | 0 | 93 | 180 | 0 | 0 | 0 | 352 | 275 |  | 0 | 320 | 256 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 23 | 27 | 0 | 33 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 |  | 0 | 0 | 17 | 22 | 0 | 6 | 6 | 41 | 0 | 0 | 0 | 280 | 0 | 180 | 108 | 0 | 43 | 0 | 0 | 5 | 0 | 0 | 0 | 17 | 6 | 25 | 18 | 110 | 74 | 0 | 0 | 0 | 43 | 30 | 11 | 10 | 0 | 0 | 40 | 10 | 0 | 211 | 18 | 0 | 10 | 270 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 17 | 0 | 339 | 0 | 0 | 17 | 0 | 88 | 0 | 54 | 0 | 9 | 12 | 300 | 17 | 0 | 0 | 17 | 0 | 35 | 0 | 18 | 17 | 0 | 0 | 0 |  | 821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 76 | 0 | 185 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 154 | 0 | 0 | 0 |  | 4308 | 2746 | 7054 | 2805 | 821 | 1572 | 0 | 365 | 1244 | 0 | 120 | 17 | 110 | 0 | 0 | 73.75
6:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 289 | 230 |  | 0 | 280 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 22 | 0 | 6 | 6 | 41 | 0 | 0 | 0 | 280 | 0 | 138 | 16 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 16 | 102 | 36 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 160 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 17 | 0 | 240 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 9 | 12 | 260 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 |  | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 76 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 111 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 308 | 0 | 155 | 0 | 0 | 0 |  | 2922 | 2037 | 4959 | 2065 | 151 | 1281 | 0 | 160 | 1199 | 0 | 0 | 0 | 102 | 1 | 0 | 73.74
7:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 278 | 232 |  | 0 | 280 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 100 | 0 | 6 | 6 | 34 | 0 | 0 | 0 | 280 | 0 | 139 | 8 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 30 | 36 | 0 | 0 | 1 | 40 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 0 | 150 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 12 | 17 | 0 | 240 | 0 | 0 | 0 | 1 | 30 | 0 | 16 | 17 | 9 | 12 | 260 | 17 | 4 | 0 | 17 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 |  | 601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 153 | 0 | 18 | 0 |  | 2910 | 2430 | 5340 | 1913 | 601 | 1304 | 0 | 271 | 1195 | 0 | 0 | 0 | 30 | 26 | 0 | 73.74
8:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 299 | 315 |  | 0 | 380 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 7 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 100 | 0 | 6 | 6 | 15 | 0 | 0 | 0 | 320 | 0 | 154 | 8 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 48 | 0 | 0 | 1 | 40 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 155 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 12 | 17 | 0 | 323 | 0 | 0 | 0 | 1 | 50 | 0 | 17 | 17 | 8 | 12 | 300 | 17 | 14 | 0 | 17 | 0 | 13 | 0 | 17 | 0 | 0 | 0 | 0 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 418 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 500 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 330 | 4 | 154 | 0 | 17 | 0 |  | 3470 | 2825 | 6295 | 2141 | 907 | 1606 | 0 | 303 | 1220 | 0 | 0 | 0 | 72 | 46 | 0 | 73.74
9:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 391 | 346 |  | 0 | 450 | 283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 8 | 17 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 100 | 0 | 6 | 0 | 5 | 0 | 0 | 0 | 275 | 0 | 179 | 110 | 0 | 38 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 44 | 0 | 0 | 1 | 39 | 0 | 14 | 10 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 5 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 13 | 12 | 17 | 0 | 300 | 24 | 0 | 15 | 0 | 84 | 0 | 44 | 17 | 9 | 12 | 400 | 17 | 33 | 0 | 17 | 0 | 17 | 12 | 18 | 0 | 0 | 0 | 0 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 76 | 0 | 220 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 436 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 500 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 325 | 5 | 154 | 0 | 68 | 0 |  | 4046 | 2969 | 7015 | 2176 | 908 | 2001 | 0 | 436 | 1275 | 0 | 0 | 0 | 82 | 137 | 0 | 73.74
10:00 | 0 | 0 | 80 | 180 | 0 | 0 | 0 | 399 | 301 |  | 0 | 450 | 310 | 2 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 5 | 0 | 22 | 8 | 17 | 33 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 0 | 0 | 100 | 0 | 6 | 7 | 6 | 0 | 0 | 0 | 360 | 0 | 180 | 128 | 0 | 31 | 0 | 0 | 20 | 0 | 0 | 0 | 8 | 0 | 0 | 6 | 92 | 44 | 0 | 16 | 2 | 43 | 0 | 48 | 20 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 5 | 0 | 7 | 0 | 0 | 26 | 0 | 2 | 17 | 38 | 17 | 7 | 367 | 47 | 3 | 17 | 0 | 87 | 6 | 51 | 17 | 9 | 24 | 400 | 17 | 36 | 0 | 17 | 0 | 17 | 32 | 18 | 7 | 0 | 12 | 0 |  | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 21 | 0 | 0 | 76 | 0 | 260 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 0 | 10 | 0 | 3 | 35 | 560 | 0 | 0 | 0 | 4 | 8 | 15 | 0 | 0 | 325 | 15 | 150 | 0 | 179 | 0 |  | 4658 | 3249 | 7907 | 2463 | 906 | 2091 | 0 | 660 | 1371 | 0 | 0 | 28 | 92 | 296 | 0 | 73.74
11:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 373 | 302 |  | 0 | 450 | 321 | 9 | 12 | 0 | 0 | 0 | 0 | 9 | 16 | 100 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 22 | 6 | 25 | 33 | 8 | 0 | 0 | 25 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 100 | 0 | 6 | 7 | 9 | 0 | 0 | 0 | 340 | 0 | 213 | 128 | 0 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 17 | 0 | 25 | 6 | 114 | 44 | 0 | 16 | 2 | 43 | 0 | 48 | 47 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 0 | 9 | 300 | 8 | 5 | 0 | 47 | 0 | 0 | 46 | 0 | 59 | 11 | 38 | 17 | 15 | 399 | 58 | 51 | 24 | 1 | 87 | 17 | 52 | 41 | 9 | 38 | 400 | 17 | 49 | 72 | 17 | 0 | 17 | 24 | 42 | 17 | 0 | 35 | 0 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 28 | 16 | 24 | 26 | 0 | 21 | 0 | 0 | 76 | 0 | 260 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 425 | 0 | 0 | 5 | 0 | 33 | 0 | 2 | 55 | 640 | 0 | 0 | 0 | 2 | 51 | 95 | 0 | 0 | 325 | 18 | 154 | 0 | 48 | 0 |  | 5440 | 3560 | 9000 | 2623 | 907 | 2189 | 0 | 1289 | 1455 | 25 | 0 | 190 | 114 | 208 | 0 | 73.73
12:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 392 | 346 |  | 0 | 450 | 317 | 8 | 17 | 0 | 0 | 0 | 0 | 9 | 16 | 100 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 10 | 22 | 6 | 0 | 33 | 8 | 0 | 0 | 25 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 12 | 20 | 17 | 100 | 0 | 6 | 7 | 3 | 0 | 0 | 0 | 350 | 0 | 207 | 130 | 0 | 34 | 0 | 0 | 43 | 0 | 0 | 0 | 18 | 0 | 25 | 6 | 118 | 44 | 0 | 16 | 2 | 43 | 0 | 48 | 48 | 0 | 0 | 0 | 76 | 0 | 50 | 18 | 0 | 9 | 320 | 8 | 8 | 0 | 47 | 290 | 40 | 48 | 40 | 116 | 0 | 38 | 17 | 21 | 404 | 59 | 88 | 34 | 2 | 87 | 17 | 54 | 98 | 9 | 38 | 330 | 17 | 53 | 72 | 17 | 0 | 17 | 19 | 54 | 17 | 0 | 35 | 0 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 28 | 34 | 32 | 43 | 22 | 21 | 0 | 5 | 76 | 0 | 260 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416 | 0 | 0 | 35 | 0 | 33 | 0 | 2 | 55 | 760 | 0 | 0 | 0 | 5 | 35 | 35 | 0 | 0 | 328 | 24 | 152 | 0 | 58 | 0 |  | 6101 | 3754 | 9855 | 2651 | 907 | 2246 | 370 | 1482 | 1576 | 25 | 0 | 280 | 118 | 200 | 68 | 73.73
13:00 | 0 | 0 | 115 | 180 | 0 | 0 | 0 | 405 | 322 |  | 0 | 450 | 301 | 8 | 17 | 0 | 0 | 0 | 0 | 9 | 16 | 100 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 10 | 22 | 18 | 33 | 33 | 8 | 0 | 0 | 25 | 0 | 0 | 8 | 0 | 27 | 0 | 0 |  | 11 | 20 | 34 | 100 | 0 | 6 | 7 | 2 | 0 | 0 | 0 | 305 | 0 | 186 | 138 | 0 | 33 | 0 | 0 | 43 | 0 | 29 | 0 | 18 | 0 | 25 | 12 | 128 | 44 | 0 | 16 | 2 | 43 | 0 | 50 | 50 | 0 | 0 | 0 | 77 | 0 | 50 | 18 | 0 | 7 | 305 | 7 | 8 | 0 | 47 | 302 | 44 | 65 | 40 | 121 | 1 | 38 | 17 | 17 | 367 | 50 | 88 | 34 | 0 | 87 | 17 | 54 | 98 | 9 | 38 | 310 | 17 | 49 | 72 | 17 | 0 | 17 | 18 | 54 | 17 | 0 | 54 | 0 |  | 948 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 135 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 28 | 34 | 0 | 43 | 34 | 21 | 0 | 0 | 76 | 0 | 260 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 35 | 0 | 33 | 0 | 6 | 55 | 920 | 0 | 0 | 0 | 5 | 68 | 35 | 0 | 0 | 328 | 8 | 154 | 0 | 165 | 0 |  | 6092 | 4086 | 10178 | 2578 | 948 | 2205 | 386 | 1496 | 1738 | 25 | 27 | 325 | 128 | 322 | 192.91 | 73.73
14:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 406 | 322 |  | 0 | 450 | 310 | 9 | 17 | 0 | 0 | 0 | 0 | 9 | 16 | 100 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 10 | 22 | 20 | 33 | 33 | 8 | 0 | 0 | 25 | 0 | 0 | 8 | 0 | 27 | 0 | 0 |  | 12 | 48 | 51 | 76 | 6 | 6 | 7 | 2 | 0 | 0 | 0 | 345 | 0 | 201 | 138 | 0 | 37 | 0 | 0 | 43 | 0 | 30 | 0 | 18 | 6 | 25 | 12 | 128 | 44 | 0 | 16 | 2 | 43 | 0 | 50 | 48 | 0 | 0 | 0 | 77 | 0 | 50 | 18 | 0 | 7 | 285 | 7 | 8 | 0 | 47 | 225 | 74 | 65 | 40 | 40 | 1 | 38 | 17 | 12 | 414 | 49 | 88 | 34 | 1 | 87 | 17 | 54 | 17 | 9 | 38 | 310 | 17 | 38 | 72 | 17 | 0 | 17 | 17 | 54 | 17 | 0 | 54 | 0 |  | 907 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 127 | 18 | 0 | 0 | 0 | 0 | 0 | 5 | 54 | 28 | 34 | 0 | 43 | 35 | 21 | 0 | 0 | 75 | 0 | 260 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 35 | 0 | 33 | 0 | 3 | 55 | 1020 | 0 | 0 | 0 | 4 | 23 | 36 | 0 | 0 | 321 | 9 | 150 | 0 | 98 | 0 |  | 6031 | 4027 | 10058 | 2700 | 907 | 2185 | 339 | 1348 | 1826 | 25 | 27 | 377 | 128 | 196 | 347.62 | 73.73
15:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 404 | 323 |  | 0 | 450 | 307 | 8 | 17 | 0 | 0 | 0 | 0 | 9 | 16 | 100 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 10 | 22 | 20 | 33 | 33 | 8 | 0 | 0 | 25 | 0 | 0 | 8 | 0 | 26 | 0 | 0 |  | 12 | 54 | 51 | 66 | 5 | 6 | 0 | 2 | 0 | 0 | 0 | 340 | 0 | 190 | 138 | 0 | 37 | 0 | 0 | 43 | 0 | 36 | 0 | 18 | 5 | 25 | 0 | 132 | 43 | 0 | 16 | 2 | 43 | 0 | 50 | 43 | 0 | 0 | 0 | 80 | 0 | 50 | 0 | 0 | 7 | 310 | 8 | 8 | 0 | 47 | 308 | 74 | 65 | 40 | 17 | 1 | 38 | 17 | 13 | 388 | 49 | 88 | 34 | 2 | 87 | 17 | 54 | 17 | 9 | 38 | 310 | 17 | 37 | 72 | 17 | 0 | 17 | 9 | 54 | 17 | 0 | 54 | 0 |  | 907 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 8 | 132 | 18 | 0 | 0 | 0 | 0 | 0 | 6 | 55 | 28 | 34 | 16 | 43 | 35 | 19 | 0 | 5 | 73 | 0 | 260 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 35 | 0 | 33 | 0 | 3 | 55 | 1060 | 0 | 0 | 0 | 2 | 19 | 36 | 0 | 0 | 322 | 14 | 150 | 0 | 76 | 0 |  | 5991 | 4086 | 10077 | 2628 | 907 | 2204 | 422 | 1296 | 1865 | 25 | 26 | 407 | 132 | 165 | 403.965 | 73.73
16:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 406 | 322 |  | 0 | 450 | 309 | 9 | 17 | 0 | 0 | 0 | 0 | 9 | 16 | 100 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 10 | 22 | 27 | 33 | 17 | 8 | 0 | 0 | 25 | 0 | 0 | 8 | 0 | 26 | 0 | 0 |  | 12 | 64 | 84 | 33 | 5 | 6 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 182 | 138 | 0 | 33 | 0 | 0 | 43 | 0 | 38 | 0 | 17 | 5 | 25 | 12 | 142 | 43 | 0 | 16 | 1 | 43 | 0 | 50 | 45 | 0 | 0 | 0 | 79 | 0 | 90 | 0 | 0 | 10 | 280 | 8 | 8 | 0 | 47 | 304 | 74 | 65 | 40 | 16 | 2 | 38 | 17 | 13 | 366 | 49 | 88 | 34 | 2 | 87 | 17 | 60 | 17 | 24 | 38 | 310 | 17 | 25 | 72 | 17 | 0 | 19 | 11 | 54 | 17 | 0 | 54 | 0 |  | 895 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 8 | 132 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 54 | 28 | 34 | 24 | 43 | 35 | 20 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415 | 17 | 0 | 35 | 0 | 33 | 0 | 3 | 55 | 1030 | 0 | 0 | 0 | 1 | 55 | 36 | 0 | 0 | 322 | 5 | 155 | 88 | 82 | 0 |  | 6001 | 4215 | 10216 | 2601 | 895 | 2183 | 418 | 1336 | 1930 | 25 | 26 | 473 | 142 | 187 | 223.47 | 73.72
17:00 | 0 | 0 | 100 | 180 | 0 | 0 | 0 | 410 | 322 |  | 0 | 450 | 304 | 8 | 17 | 0 | 0 | 0 | 0 | 9 | 24 | 100 | 8 | 0 | 0 | 0 | 17 | 55 | 35 | 10 | 22 | 27 | 33 | 33 | 8 | 0 | 0 | 25 | 0 | 0 | 8 | 0 | 32 | 0 | 0 |  | 12 | 65 | 84 | 33 | 5 | 15 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 183 | 138 | 0 | 32 | 0 | 0 | 43 | 0 | 30 | 0 | 17 | 5 | 25 | 12 | 134 | 43 | 0 | 14 | 0 | 43 | 0 | 51 | 49 | 0 | 0 | 0 | 76 | 0 | 135 | 0 | 0 | 10 | 295 | 8 | 8 | 0 | 47 | 248 | 74 | 68 | 40 | 16 | 3 | 38 | 17 | 12 | 367 | 49 | 88 | 35 | 1 | 87 | 17 | 76 | 52 | 27 | 38 | 310 | 28 | 7 | 72 | 17 | 0 | 35 | 5 | 53 | 30 | 0 | 54 | 0 |  | 894 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 4 | 0 | 8 | 127 | 19 | 0 | 0 | 0 | 0 | 28 | 28 | 54 | 28 | 34 | 24 | 43 | 28 | 20 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416 | 17 | 0 | 35 | 0 | 82 | 0 | 3 | 55 | 1000 | 0 | 0 | 0 | 0 | 27 | 36 | 0 | 0 | 323 | 4 | 152 | 139 | 24 | 0 |  | 6125 | 4236 | 10361 | 2640 | 894 | 2195 | 362 | 1557 | 1949 | 25 | 32 | 499 | 134 | 74 | 0 | 73.72
18:00 | 0 | 0 | 100 | 180 | 0 | 0 | 0 | 409 | 303 |  | 0 | 400 | 311 | 9 | 48 | 0 | 0 | 0 | 0 | 9 | 16 | 133 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 10 | 22 | 27 | 33 | 31 | 28 | 0 | 0 | 25 | 0 | 0 | 9 | 0 | 58 | 0 | 0 |  | 12 | 56 | 84 | 33 | 21 | 30 | 0 | 8 | 0 | 0 | 0 | 310 | 0 | 181 | 167 | 0 | 36 | 0 | 0 | 43 | 0 | 30 | 0 | 17 | 5 | 25 | 12 | 114 | 43 | 0 | 14 | 0 | 43 | 0 | 51 | 50 | 0 | 0 | 0 | 80 | 0 | 135 | 0 | 0 | 10 | 280 | 16 | 8 | 0 | 55 | 0 | 25 | 68 | 25 | 35 | 0 | 38 | 17 | 50 | 367 | 49 | 88 | 87 | 0 | 121 | 17 | 94 | 77 | 57 | 38 | 310 | 49 | 1 | 72 | 17 | 0 | 35 | 0 | 54 | 34 | 0 | 36 | 0 |  | 902 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 21 | 0 | 8 | 105 | 17 | 0 | 0 | 0 | 0 | 28 | 28 | 54 | 28 | 34 | 40 | 43 | 28 | 21 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 391 | 17 | 0 | 35 | 1 | 81 | 0 | 1 | 55 | 960 | 0 | 0 | 2 | 0 | 1 | 36 | 0 | 0 | 323 | 2 | 153 | 212 | 5 | 0 |  | 6116 | 4219 | 10335 | 2625 | 902 | 2132 | 50 | 1898 | 1983 | 25 | 58 | 538 | 114 | 10 | 0 | 73.72
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 95 | 180 | 0 | 0 | 0 | 379 | 342 |  | 0 | 450 | 319 | 8 | 85 | 12 | 0 | 0 | 0 | 17 | 41 | 133 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 10 | 22 | 20 | 33 | 31 | 48 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 170 | 0 | 0 |  | 12 | 58 | 84 | 33 | 30 | 44 | 0 | 12 | 0 | 0 | 0 | 310 | 0 | 186 | 167 | 0 | 33 | 0 | 0 | 43 | 0 | 35 | 5 | 18 | 5 | 25 | 12 | 138 | 43 | 0 | 15 | 0 | 43 | 0 | 50 | 48 | 0 | 0 | 0 | 80 | 0 | 135 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 193 | 0 | 25 | 88 | 25 | 112 | 0 | 38 | 17 | 130 | 367 | 88 | 88 | 87 | 0 | 200 | 17 | 92 | 74 | 95 | 38 | 330 | 53 | 0 | 108 | 17 | 0 | 35 | 0 | 68 | 34 | 0 | 36 | 0 |  | 902 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 25 | 0 | 40 | 135 | 23 | 0 | 0 | 0 | 0 | 27 | 28 | 54 | 28 | 34 | 40 | 43 | 28 | 22 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 419 | 17 | 0 | 35 | 33 | 81 | 0 | 0 | 55 | 950 | 0 | 0 | 17 | 0 | 0 | 109 | 0 | 0 | 320 | 0 | 185 | 400 | 0 | 0 |  | 7013 | 4627 | 11640 | 2627 | 902 | 2275 | 50 | 2715 | 2190 | 25 | 170 | 548 | 138 | 0 | 0 | 73.71
19:30 | 0 | 0 | 100 | 180 | 0 | 0 | 0 | 398 | 348 |  | 0 | 450 | 270 | 9 | 85 | 30 | 0 | 0 | 0 | 17 | 41 | 82 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 10 | 22 | 27 | 33 | 31 | 49 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 211 | 0 | 0 |  | 12 | 66 | 84 | 33 | 30 | 44 | 0 | 7 | 0 | 0 | 0 | 310 | 0 | 212 | 167 | 0 | 35 | 0 | 0 | 43 | 0 | 38 | 8 | 18 | 5 | 25 | 12 | 138 | 49 | 0 | 15 | 0 | 43 | 0 | 50 | 48 | 0 | 0 | 0 | 80 | 0 | 135 | 0 | 0 | 10 | 250 | 16 | 11 | 0 | 195 | 0 | 0 | 88 | 0 | 114 | 0 | 38 | 17 | 150 | 367 | 88 | 88 | 87 | 0 | 290 | 17 | 92 | 67 | 95 | 38 | 315 | 53 | 0 | 108 | 17 | 0 | 35 | 0 | 102 | 34 | 0 | 62 | 0 |  | 905 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 25 | 0 | 8 | 106 | 23 | 16 | 0 | 0 | 0 | 28 | 28 | 54 | 14 | 8 | 40 | 43 | 28 | 22 | 0 | 8 | 74 | 0 | 260 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 418 | 17 | 0 | 50 | 50 | 81 | 0 | 0 | 55 | 1060 | 0 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 326 | 0 | 182 | 400 | 0 | 0 |  | 7119 | 4704 | 11823 | 2660 | 905 | 2186 | 0 | 2861 | 2302 | 25 | 211 | 535 | 138 | 0 | 0 | 0
20:00 | 0 | 0 | 100 | 180 | 0 | 0 | 0 | 401 | 348 |  | 0 | 450 | 296 | 9 | 74 | 30 | 0 | 0 | 0 | 17 | 41 | 32 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 15 | 22 | 27 | 33 | 31 | 49 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 224 | 0 | 0 |  | 12 | 66 | 84 | 33 | 30 | 44 | 0 | 14 | 0 | 0 | 0 | 310 | 0 | 211 | 167 | 0 | 38 | 0 | 0 | 34 | 0 | 38 | 52 | 18 | 5 | 25 | 15 | 136 | 59 | 0 | 15 | 0 | 43 | 0 | 50 | 48 | 0 | 0 | 0 | 80 | 0 | 135 | 18 | 0 | 10 | 250 | 16 | 11 | 0 | 195 | 0 | 0 | 87 | 0 | 115 | 0 | 38 | 17 | 150 | 368 | 88 | 88 | 87 | 0 | 296 | 17 | 92 | 17 | 95 | 38 | 330 | 53 | 0 | 108 | 17 | 0 | 35 | 0 | 97 | 34 | 0 | 90 | 0 |  | 810 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 24 | 0 | 8 | 122 | 22 | 16 | 0 | 0 | 0 | 28 | 0 | 54 | 14 | 8 | 40 | 24 | 28 | 22 | 0 | 8 | 74 | 0 | 260 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 418 | 17 | 0 | 50 | 15 | 81 | 0 | 0 | 55 | 1080 | 0 | 0 | 0 | 0 | 0 | 114 | 0 | 0 | 326 | 0 | 182 | 407 | 0 | 0 |  | 7193 | 4501 | 11694 | 2732 | 810 | 2209 | 0 | 2745 | 2329 | 25 | 224 | 484 | 136 | 0 | 0 | 73.72
21:00 | 0 | 0 | 100 | 180 | 0 | 0 | 0 | 405 | 340 |  | 0 | 450 | 297 | 9 | 32 | 30 | 0 | 0 | 0 | 17 | 41 | 32 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 15 | 22 | 27 | 33 | 31 | 49 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 226 | 0 | 0 |  | 12 | 66 | 84 | 33 | 30 | 44 | 0 | 14 | 0 | 0 | 0 | 310 | 0 | 210 | 170 | 0 | 40 | 0 | 0 | 34 | 0 | 38 | 52 | 18 | 5 | 25 | 15 | 138 | 65 | 0 | 17 | 0 | 43 | 0 | 50 | 48 | 0 | 0 | 0 | 80 | 0 | 135 | 18 | 0 | 10 | 270 | 16 | 11 | 0 | 195 | 0 | 0 | 88 | 0 | 80 | 0 | 38 | 17 | 150 | 367 | 89 | 88 | 87 | 0 | 296 | 17 | 92 | 17 | 95 | 38 | 330 | 53 | 0 | 108 | 17 | 0 | 35 | 0 | 115 | 34 | 0 | 163 | 0 |  | 810 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 19 | 0 | 8 | 132 | 24 | 16 | 0 | 0 | 0 | 28 | 0 | 54 | 14 | 8 | 40 | 24 | 28 | 22 | 0 | 8 | 73 | 0 | 260 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 419 | 17 | 0 | 50 | 15 | 81 | 0 | 0 | 55 | 1130 | 0 | 0 | 0 | 0 | 0 | 114 | 0 | 0 | 320 | 0 | 182 | 407 | 0 | 0 |  | 7241 | 4548 | 11789 | 2752 | 810 | 2228 | 0 | 2686 | 2372 | 25 | 226 | 552 | 138 | 0 | 0 | 73.71
22:00 | 0 | 0 | 100 | 180 | 0 | 0 | 0 | 406 | 338 |  | 0 | 450 | 309 | 8 | 17 | 15 | 0 | 0 | 0 | 18 | 41 | 32 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 15 | 22 | 27 | 33 | 31 | 49 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 227 | 0 | 0 |  | 12 | 66 | 84 | 33 | 30 | 44 | 0 | 22 | 0 | 0 | 0 | 310 | 0 | 213 | 170 | 0 | 41 | 0 | 0 | 34 | 0 | 38 | 52 | 18 | 5 | 25 | 17 | 138 | 80 | 0 | 18 | 0 | 43 | 0 | 50 | 50 | 0 | 0 | 0 | 77 | 0 | 135 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 195 | 0 | 0 | 88 | 0 | 50 | 0 | 38 | 17 | 150 | 367 | 89 | 88 | 87 | 0 | 122 | 17 | 92 | 17 | 98 | 38 | 330 | 36 | 0 | 108 | 17 | 0 | 35 | 0 | 115 | 34 | 0 | 163 | 0 |  | 810 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 19 | 0 | 8 | 133 | 24 | 16 | 0 | 0 | 0 | 28 | 0 | 54 | 14 | 8 | 40 | 24 | 28 | 22 | 0 | 8 | 74 | 0 | 260 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 419 | 17 | 0 | 50 | 15 | 74 | 0 | 0 | 55 | 1150 | 0 | 0 | 0 | 0 | 0 | 114 | 0 | 0 | 326 | 0 | 200 | 408 | 0 | 0 |  | 7054 | 4589 | 11643 | 2777 | 810 | 2265 | 0 | 2431 | 2418 | 25 | 227 | 552 | 138 | 0 | 0 | 73.71
23:00 | 0 | 0 | 100 | 180 | 0 | 0 | 0 | 406 | 338 |  | 0 | 450 | 310 | 9 | 19 | 0 | 0 | 0 | 0 | 18 | 16 | 64 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 15 | 22 | 27 | 33 | 31 | 49 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 222 | 0 | 0 |  | 12 | 66 | 84 | 22 | 20 | 44 | 0 | 25 | 0 | 0 | 0 | 350 | 0 | 207 | 170 | 0 | 41 | 0 | 0 | 34 | 0 | 38 | 52 | 18 | 5 | 25 | 20 | 138 | 80 | 0 | 18 | 0 | 43 | 0 | 50 | 50 | 0 | 0 | 0 | 77 | 0 | 135 | 17 | 0 | 10 | 290 | 16 | 11 | 0 | 195 | 0 | 0 | 68 | 0 | 50 | 0 | 38 | 17 | 60 | 400 | 18 | 88 | 84 | 0 | 87 | 17 | 93 | 88 | 36 | 38 | 330 | 17 | 0 | 89 | 17 | 0 | 35 | 0 | 74 | 35 | 0 | 57 | 0 |  | 795 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 19 | 0 | 8 | 132 | 24 | 0 | 0 | 0 | 0 | 28 | 0 | 54 | 21 | 25 | 40 | 43 | 28 | 22 | 0 | 8 | 74 | 0 | 260 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417 | 17 | 0 | 35 | 15 | 33 | 0 | 0 | 35 | 1190 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 322 | 0 | 202 | 411 | 0 | 0 |  | 6641 | 4533 | 11174 | 2845 | 795 | 2267 | 0 | 1970 | 2459 | 0 | 222 | 478 | 138 | 0 | 0 | 73.71
24:00 | 0 | 0 | 120 | 100 | 0 | 0 | 0 | 394 | 338 |  | 0 | 450 | 310 | 8 | 51 | 0 | 0 | 0 | 0 | 18 | 16 | 100 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 15 | 23 | 27 | 33 | 32 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 224 | 0 | 0 |  | 12 | 66 | 78 | 22 | 13 | 6 | 0 | 23 | 0 | 0 | 0 | 305 | 0 | 212 | 170 | 0 | 41 | 0 | 0 | 43 | 0 | 39 | 52 | 18 | 5 | 25 | 20 | 126 | 80 | 0 | 18 | 0 | 43 | 0 | 50 | 50 | 0 | 0 | 0 | 77 | 0 | 135 | 17 | 0 | 10 | 290 | 16 | 11 | 0 | 195 | 108 | 40 | 67 | 40 | 50 | 0 | 38 | 17 | 11 | 366 | 18 | 88 | 36 | 0 | 87 | 17 | 76 | 114 | 8 | 38 | 330 | 17 | 0 | 17 | 17 | 0 | 35 | 0 | 36 | 17 | 0 | 17 | 0 |  | 795 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 19 | 0 | 8 | 135 | 22 | 0 | 0 | 0 | 0 | 28 | 0 | 54 | 21 | 34 | 40 | 43 | 28 | 22 | 0 | 8 | 74 | 0 | 260 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 426 | 17 | 0 | 35 | 15 | 33 | 0 | 0 | 35 | 1212 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 322 | 0 | 202 | 412 | 0 | 0 |  | 6300 | 4580 | 10880 | 2705 | 795 | 2281 | 188 | 1610 | 2482 | 0 | 224 | 469 | 126 | 0 | 0 | 73.71
KWH | 0 | 0 | 2195594 | 3969000 | 0 | 0 | 0 | 9248760 | 7556000 |  | 0 | 9670000 | 6981295 | 162240 | 440397 | 95242 | 0 | 0 | 98000 | 185386 | 430992 | 1315200 | 16281 | 0 | 0 | 0 | 255240 | 623333 | 636434 | 225684 | 552000 | 439560 | 636840 | 656100 | 396480 | 0 | 0 | 300000 | 0 | 0 | 229192 | 0 | 2158058 | 0 | 0 |  | 225360 | 924048 | 1222724 | 1220520 | 201600 | 371040 | 78192 | 466080 | 0 | 0 | 0 | 7793900 | 0 | 4543000 | 3094545 | 0 | 802584 | 0 | 0 | 755952 | 0 | 576240 | 439824 | 336168 | 92340 | 483600 | 297460 | 2749440 | 1290240 | 0 | 297000 | 14200 | 1006000 | 230400 | 940200 | 900144 | 0 | 0 | 298368 | 1426560 | 0 | 2372160 | 228000 | 0 | 190800 | 6626000 | 248448 | 181305 | 0 | 1726253 | 1708430 | 449532 | 1120800 | 317109 | 982512 | 53325 | 654720 | 424800 | 916654 | 8534000 | 1075200 | 1437974 | 960145 | 12961 | 2546727 | 287888 | 1496248 | 1092120 | 623280 | 644160 | 7971200 | 586560 | 319410 | 1118880 | 417764 | 0 | 676800 | 167130 | 1118400 | 488880 | 0 | 950109 | 0 |  | 19989818 | 0 | 0 | 0 | 497280 | 0 | 0 | 0 | 140160 | 0 | 125625 | 3322437 | 425600 | 59040 | 0 | 0 | 0 | 204880 | 100281 | 857744 | 301820 | 421568 | 295035 | 616738 | 418779 | 383760 | 0 | 93528 | 1736290 | 0 | 5964000 | 0 | 0 | 4193082 | 0 | 0 | 0 | 0 | 0 | 945545 | 0 | 9128909 | 226080 | 0 | 652032 | 119664 | 829094 | 0 | 30979 | 861024 | 22753600 | 0 | 0 | 27600 | 25980 | 327600 | 1064256 | 0 | 0 | 7760000 | 119037 | 4011700 | 3098182 | 890980 | 0 |  | 133277721 | 93019727 | 226297448 | 63660495 | 19989818 | 48545845 | 2475071 | 32128147 | 45323772 | 300000 | 2158058 | 7005200 | 2749440 | 1961602 | 0
Fuel Cost | 0 | 0 | 3205567.24 | 5913810 | 0 | 0 | 0 | 9711198 | 8160480 |  | 0 | 10540300 | 7749237.45 | 1813843.2 | 5835260.25 | 1261956.5 | 0 | 0 | 171500 | 2710343.32 | 6064057.44 | 21319392 | 150110.82 | 0 | 0 | 0 | 3246652.8 | 8414995.5 | 8534579.94 | 169263 | 414000 | 0 | 0 | 0 | 6744124.8 | 0 | 0 | 81000 | 0 | 0 | 3747289.2 | 0 | 37463886.88 | 0 | 0 |  | 2940948 | 15413120.64 | 20810762.48 | 16489225.2 | 2556288 | 4292932.8 | 99303.84 | 1552046.4 | 0 | 0 | 0 | 8651229 | 0 | 5269880 | 3991963.05 | 0 | 906919.92 | 0 | 0 | 1262439.84 | 0 | 9951664.8 | 5915632.8 | 460550.16 | 69255 | 846300 | 223095 | 19740979.2 | 1406361.6 | 0 | 403920 | 226348 | 1378220 | 304128 | 1635948 | 1557249.12 | 0 | 0 | 578833.92 | 3252556.8 | 0 | 2395881.6 | 490200 | 0 | 377784 | 6626000 | 186336 | 137791.8 | 0 | 23563353.45 | 35808692.8 | 9291826.44 | 15108384 | 6554643.03 | 13607791.2 | 623369.25 | 6756710.4 | 5802768 | 12163998.58 | 7851280 | 13074432 | 20793104.04 | 12145834.25 | 0 | 29898574.98 | 3135100.32 | 15905116.24 | 14820068.4 | 8034079.2 | 7588204.8 | 7333504 | 7595952 | 4615474.5 | 14198587.2 | 4754154.32 | 0 | 8839008 | 1997203.5 | 16742448 | 6438549.6 | 0 | 0 | 0 |  | 59969454 | 0 | 0 | 0 | 5176684.8 | 0 | 0 | 0 | 2524281.6 | 0 | 1805231.25 | 3721129.44 | 825664 | 643536 | 0 | 0 | 0 | 3435837.6 | 1753914.69 | 13415116.16 | 2324014 | 6981166.08 | 4989041.85 | 8406138.94 | 7064801.73 | 794383.2 | 0 | 70800.696 | 10087844.9 | 0 | 31549560 | 0 | 0 | 4863975.12 | 0 | 0 | 0 | 0 | 0 | 1096832.2 | 0 | 9037619.91 | 3038515.2 | 0 | 7713538.56 | 1729144.8 | 10529493.8 | 0 | 342317.95 | 10452831.36 | 205009936 | 0 | 0 | 204240 | 293833.8 | 3842748 | 16315044.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 630867155.81 | 440008672.116 | 1070875827.926 | 68331065.536 | 59969454 | 57363671.77 | 51655162.27 | 417004038.82 | 246647340.9 | 81000 | 37463886.88 | 100677933.55 | 19740979.2 | 11941295 | 0
Yesterday Day Peak | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 392 | 346 |  | 0 | 450 | 317 | 8 | 17 | 0 | 0 | 0 | 0 | 9 | 16 | 100 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 10 | 22 | 6 | 0 | 33 | 8 | 0 | 0 | 25 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 12 | 20 | 17 | 100 | 0 | 6 | 7 | 3 | 0 | 0 | 0 | 350 | 0 | 207 | 130 | 0 | 34 | 0 | 0 | 43 | 0 | 0 | 0 | 18 | 0 | 25 | 6 | 118 | 44 | 0 | 16 | 2 | 43 | 0 | 48 | 48 | 0 | 0 | 0 | 76 | 0 | 50 | 18 | 0 | 9 | 320 | 8 | 8 | 0 | 47 | 290 | 40 | 48 | 40 | 116 | 0 | 38 | 17 | 21 | 404 | 59 | 88 | 34 | 2 | 87 | 17 | 54 | 98 | 9 | 38 | 330 | 17 | 53 | 72 | 17 | 0 | 17 | 19 | 54 | 17 | 0 | 35 | 0 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 28 | 34 | 32 | 43 | 22 | 21 | 0 | 5 | 76 | 0 | 260 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416 | 0 | 0 | 35 | 0 | 33 | 0 | 2 | 55 | 760 | 0 | 0 | 0 | 5 | 35 | 35 | 0 | 0 | 328 | 24 | 152 | 0 | 58 | 0 |  | 9855 | DayPeak
Yesterday Evening Peak | 0 | 0 | 100 | 180 | 0 | 0 | 0 | 398 | 348 | 0 | 0 | 450 | 270 | 9 | 85 | 30 | 0 | 0 | 0 | 17 | 41 | 82 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 10 | 22 | 27 | 33 | 31 | 49 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 211 | 0 | 0 | 0 | 12 | 66 | 84 | 33 | 30 | 44 | 0 | 7 | 0 | 0 | 0 | 310 | 0 | 212 | 167 | 0 | 35 | 0 | 0 | 43 | 0 | 38 | 8 | 18 | 5 | 25 | 12 | 138 | 49 | 0 | 15 | 0 | 43 | 0 | 50 | 48 | 0 | 0 | 0 | 80 | 0 | 135 | 0 | 0 | 10 | 250 | 16 | 11 | 0 | 195 | 0 | 0 | 88 | 0 | 114 | 0 | 38 | 17 | 150 | 367 | 88 | 88 | 87 | 0 | 290 | 17 | 92 | 67 | 95 | 38 | 315 | 53 | 0 | 108 | 17 | 0 | 35 | 0 | 102 | 34 | 0 | 62 | 0 |  | 905 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 25 | 0 | 8 | 106 | 23 | 16 | 0 | 0 | 0 | 28 | 28 | 54 | 14 | 8 | 40 | 43 | 28 | 22 | 0 | 8 | 74 | 0 | 260 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 418 | 17 | 0 | 50 | 50 | 81 | 0 | 0 | 55 | 1060 | 0 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 326 | 0 | 182 | 400 | 0 | 0 |  | 11823 | EvPeak
Forecast for Evening | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 400 | 350 | 0 | 0 | 450 | 320 | 8 | 85 | 25 | 0 | 0 | 0 | 40 | 50 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 22 | 25 | 33 | 25 | 48 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 220 | 0 | 0 | 0 | 12 | 58 | 84 | 33 | 30 | 40 | 11 | 20 | 0 | 0 | 0 | 350 | 250 | 200 | 150 | 0 | 40 | 0 | 0 | 43 | 0 | 35 | 52 | 18 | 7 | 25 | 21 | 152 | 80 | 0 | 17 | 0 | 43 | 0 | 51 | 48 | 0 | 0 | 0 | 84 | 0 | 135 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 195 | 300 | 40 | 85 | 50 | 149 | 0 | 38 | 17 | 150 | 400 | 88 | 88 | 87 | 0 | 300 | 17 | 105 | 114 | 113 | 25 | 400 | 53 | 0 | 162 | 17 | 0 | 35 |  | 115 | 34 | 0 | 163 |  |  | 928 | 0 | 0 |  | 83 | 0 | 0 | 0 | 43 | 70 | 40 | 130 | 35 | 16 | 0 | 0 | 0 | 28 | 35 | 80 | 21 | 42 | 40 | 52 | 34 | 20 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 170 |  | 170 | 0 | 0 | 0 | 0 | 0 | 400 | 17 | 0 | 50 | 105 | 107 | 0 | 0 | 55 | 1244 | 0 |  | 150 |  |  | 115 | 0 |  | 330 |  | 150 | 400 |  | 0
Forecast for Day | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 400 | 350 | 0 | 0 | 450 | 320 | 8 | 17 | 0 | 0 | 0 | 0 | 9 | 24 | 100 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 19 | 22 | 25 | 33 | 25 | 16 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 220 | 0 | 0 | 0 | 12 | 54 | 67 | 22 | 0 | 6 | 10 | 15 | 0 | 0 | 0 | 350 | 0 | 200 | 130 | 0 | 40 | 0 | 0 | 43 | 0 | 35 | 0 | 18 | 5 | 25 | 21 | 129 | 42 | 0 | 17 | 1.6 | 43 | 0 | 51 | 48 | 0 | 0 | 0 | 84 | 0 | 135 | 17 | 0 | 10 | 290 | 16 | 11 | 0 | 45 | 300 | 40 | 68 | 40 | 17 | 20 | 38 | 17 | 20 | 400 | 18 | 88 | 17 | 5 | 88 | 17 | 54 | 114 | 26 | 25 | 400 | 17 | 50 | 72 | 17 | 0 | 35 | 30 | 54 | 17 | 0 | 35 |  |  | 928 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 20 | 60 | 24 | 130 | 22 | 0 | 0 | 0 | 0 | 28 | 15 | 80 | 21 | 42 | 24 | 30 | 28 | 20 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 170 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 400 | 17 | 0 | 35 | 85 | 34 | 0 | 8 | 35 | 700 | 0 |  | 17 | 6 | 100 | 115 | 0 |  | 330 | 30 | 150 | 400 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 120 | 100 | 0 | 0 | 0 | 396 | 306 | 0 | 0 | 350 | 309 | 9 | 17 | 0 | 0 | 0 | 0 | 9 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 22 | 26 | 33 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 221 | 0 | 0 | 0 | 12 | 24 | 17 | 22 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 305 | 0 | 211 | 170 | 0 | 41 | 0 | 0 | 43 | 0 | 39 | 0 | 18 | 5 | 25 | 18 | 90 | 53 | 0 | 19 | 0 | 43 | 0 | 50 | 47 | 0 | 0 | 0 | 78 | 0 | 137 | 17 | 0 | 10 | 280 | 16 | 11 | 0 | 45 | 0 | 0 | 68 | 0 | 17 | 0 | 12 | 17 | 13 | 381 | 18 | 52 | 17 | 2 | 87 | 17 | 54 | 17 | 9 | 12 | 330 | 17 | 14 | 17 | 17 | 0 | 35 | 15 | 17 | 17 | 0 | 18 | 0 | 0 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 73 | 0 | 260 | 0 | 0 | 140 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 425 | 17 | 0 | 0 | 0 | 26 | 0 | 2 | 0 | 600 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 324 | 9 | 154 | 409 | 18 | 0 | 0 |  |  |  | 112.2063 | 19.9898 | 43.7665 | 45.3238 | 0.3 | 2.7494 | 1.9616
226.2974
| Minimum Generation |  | 4959 | 6:00
| Highest Generation |  | 11823 | 19:30
| Day Peak Generation |  | 9855 | 12:00
| Evening Peak Generation |  | 11823 | 19:30
| HVDC Max Flow |  | 948 | 13:00
| HVDC EvPeak Flow |  | 905 | 19:30
| Load factor L.F |  | 79.75% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-05-19
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-05-18 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9855 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8700
Evening Peak Generation : |  |  | 11823 | MW Hour : | 19:30 | Available Max Generation : |  | 14052
E.P. Demand (at gen end) : |  |  | 11823 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 12000
Maximum Generation : |  |  | 11823 | MW Hour : | 19:30 | Reserve(Generation end) |  | 2052
Total Gen. (MKWH) : |  |  | 226.2974 | System Load Factor : | 79.75% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 460 | MW at | 6:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-05-19
Actual : |  | 73.7 | Ft.(MSL) , | Rule curve : | 78.96 | Ft.( MSL )
Gas Consumed : |  | Total = | 871.67 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 125694737.306
: |  |  | Coal : | 246647340.9 | Oil : | 606801021.52 | Total : | 979143099.726
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4049.3685 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1109.504 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1553.2499 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1349.182 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1110.5832 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 825.5327 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 463.2298 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 385.5962 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 754.1689 |  |  | 0 | 0%
Total |  | 0 |  | 11600.4152 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,7
3) Bhula Nuton Biddut
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj- 2
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
8:01 | - | Sylhet CCPP 225 MW tripped at 08:01 hrs. | [5 empty] | 212MW generation interrup.
8:03 | 12:58 | Sylhet 132/33kV S/S T2 HT Tripped showing 87,o/c relays Due to 33kv Bus section -2 - Bus PT (R-phase) burst. | [5 empty] | 34.0MW load interrup.
8:03 | 12:58 | Sylhet 132/33kV S/S T2 LT Tripped showing o/c relays Due to 33kv Bus section -2 - Bus PT (R-phase) burst. | [5 empty] | 34.0MW load interrup.
8:03 | 9:35 | Sylhet 132/33kV S/S T1 LT Tripped showing o/c relays Due to 33kv Bus section -2 - Bus PT (R-phase) burst. | [5 empty] | 19.0MW load interrup.
8:03 | 9:34 | Sylhet 132/33kV S/S T4 LT Tripped showing 51/50 relays Due to 33kv Bus section -2 - Bus PT (R-phase) burst. | [5 empty] | 22.0MW load interrup.
8:31 | 10:13 | NWPGCL(P/s)-Goalpara Line tripped From NWPGCL(P/s).
- | 8:54 | Bagerhat-Mongla 132 kV Ckt-2 is restored.
9:02 | - | Bhola CCPP ST tripped.
- | 9:49 | Ghorasal-4 was sync.
9:59 | - | Rampura-Ullon-2 132kV Ckt-2 Forced S/D from Rampura 230/132kV end Due to Shutdown For NLCD.
10:38 | 14:25 | Ishurdi 132/33kV S/S 132 kV Bus-1 Forced S/D Due to Red hot maintenance in 132 kv Ishwardi-Bheramara ckt-2 ( Bus-1).
10:40 | 14:33 | Ishurdi 132/33kV S/S 230/132 kV T02 Incoming Forced S/D Due to Red hot maintenance in 132 kv Ishwardi-Bheramara ckt-2 ( Bus-1).
10:40 | 14:33 | Ishurdi 230/132kV S/S 230/132 kV T-02 LT Forced S/D Due to Red hot maintenance in 132 kv Ishwardi-Bheramara ckt-2 ( Bus-1).
11:00 | 14:31 | Ishurdi 230/132kV S/S 230/132 kV T-02 HT Forced S/D Due to Red hot maintenance in 132 kv Ishwardi-Bheramara ckt-2 ( Bus-1).
- | 11:15 | Madunaghat-Sikalbaha 132kV Ckt-2 is restored.
- | 11:16 | Madunaghat-TKCL 132kV Ckt-1 is restored.
- | 11:51 | Sylhet CCPP 225 MW GT was sync.
11:54 | 14:40 | Bheramara P/S-Ishurdi 132 kV Ckt-2 Tripped from Bheramara 230/132kV end showing Distance Protection relays Due to Distance,
Zone-2, 9.79km, Over current,,, and from Ishurdi 132/33kV end showing SIEMENS SIPROTEC (7SA87) relays.
12:16 | 13:50 | Rajshahi 132/33kV S/S 132 kV PPP 50 Mw Forced S/D Due to Oil leakage by CVT(Y-Phase). | [5 empty] | 22.0MW load interrup.
- | 12:34 | Sikalbaha 225MW GT was sync.
13:55 | - | Sreepur-Bhaluka 132 ckt 1 was charged from Sreepur end for the first time.
14:59 | - | Sreepur-Bhaluka 132 ckt 2 was charged from Sreepur end for the first time.
- | 15:12 | Adani Power Jharkhand Ltd. unit-1 was sync.
15:56 | 18:31 | Jaldhaka 132/33kV S/S 406T HT Forced S/D Due to Heavy flashing and Red hot on 33kv T-1 Bus. | [5 empty] | 13.5MW load interrup.
15:56 | 18:32 | Jaldhaka 132/33kV S/S 406T LT Forced S/D Due to Heavy flashing and Red hot on 33kv T-1 Bus. | [5 empty] | 13.5MW load interrup.
15:57 | - | Load flow through Sreepur-Bhaluka 132 KV ckt 1 & 2 was started for the first time.
16:00 | 18:28 | Jaldhaka 132/33kV S/S 33 KV BUS Forced S/D Due to Heavy flashing and Red hot on 33kv T-1 Bus.
- | 17:19 | Chandraghona-Kaptai 132 kV Ckt-1 is restored.
- | 17:20 | Sikalbaha 225MW ST was sync.
19:29 | 20:11 | Gollamari 132/33kV S/S Tr-1 LT Tripped showing Over Current& earth fault Relay relays Due to 33kv Cement factory feeder Trip & 33kv Bus Isolator loop open. | [5 empty] | 30.0MW load interrup.
19:29 | 22:24 | Gollamari 132/33kV S/S Tr-2 HT Tripped showing Over Current & Earth fault Relay relays Due to 33 kv Cement Factory Trip & 33 kv Bus Isolator loop open. | [5 empty] | 13.0MW load interrup.
19:29 | 22:40 | Gollamari 132/33kV S/S Tr-2 LT Forced S/D Due to 33 kv bus DS loop change. | [5 empty] | 43.0MW load interrup.
21:15 | 22:23 | Gollamari 132/33kV S/S Tr-1 HT Forced S/D Due to 33 kv bus DS loop change | 30.0MW load interrup.
21:15 | 22:28 | Gollamari 132/33kV S/S Tr-1 LT Forced S/D Due to 33 bus Ds loop change. | 30.0MW load interrup.
21:16 | 22:24 | Gollamari 132/33kV S/S Tr-2 HT Forced S/D Due to 33 kv bus DS loop change | 13.0MW load interrup.
- | 2:10 | Sirajgonj 225MW Unit-2 GT was sync.
4:03 | - | Mirpur-Uttara 3PH 132kV Ckt-1 Project Work S/D from Mirpur 132/33kV end Due to Old tower dismantling work in Switch yard.
4:03 | - | Mirpur-Uttara 132kV Ckt-1 Project Work S/D from Mirpur 132/33kV end Due to Old tower dismantling work in Switch yard.
4:47 | 7:24 | Mirpur 132/33kV S/S T2 LT Project Work S/D Due to Old tower dismantling work in Switch yard.
4:47 | 7:23 | Mirpur 132/33kV S/S T1 LT Project Work S/D Due to Old tower dismantling work.
4:48 | - | Mirpur 132/33kV S/S T3 LT Project Work S/D Due to Old tower dismantling work in Switch yard.
4:50 | 7:23 | Mirpur 132/33kV S/S T1 HT Project Work S/D Due to Old tower dismantling work in Switch yard.
4:50 | 7:24 | Mirpur 132/33kV S/S T2 HT Project Work S/D Due to Old tower dismantling work in Switch yard.
4:51 | - | Mirpur 132/33kV S/S T3 HT Project Work S/D Due to Old tower dismantling work in Switch yard.
4:54 | - | Aminbazar-Mirpur 132kV Ckt-1 Project Work S/D from Mirpur 132/33kV end Due to Old tower dismantling work in Switch yard.
4:56 | - | Aminbazar-Mirpur 132kV Ckt-2 Project Work S/D from Mirpur 132/33kV end Due to Old tower dismantling work in Switch yard.
6:17 | 6:28 | Kishoreganj 132/33kV S/S Tr-2 (414T) LT Forced S/D.
6:17 | 6:28 | Kishoreganj 132/33kV S/S Tr-2 (414T) HT Forced S/D Due to T-2 ,33Kv Bushing Side yarn is Remove From Y-B,Phase.
6:17 | 6:28 | Kishoreganj 132/33kV S/S Tr-2 (414T) LT Forced S/D.
6:20 | 7:46 | Coxsbazar 132/33kV S/S Main Bus Project Work S/D | 70.0MW load interrup.
6:25 | - | Narshingdi 132/33kV S/S T-2 HT Scheduled S/D Due to T-2 Transformer Bay XLPE Cable relocate | 25.0MW load interrup.
- | 6:41 | Sirajgonj 225MW Unit-2 ST was sync.
7:10 | - | Narail 132/33kV S/S TR2 (413-T) LT Scheduled S/D Due to 33 KV T2 and busbar shutdown for Red Hot maintenance. | [5 empty] | 15.0MW load interrup.
7:10 | - | Narail 132/33kV S/S TR2 (413-T) HT Scheduled S/D Due to 33 KV T2 and busbar shutdown for Red Hot maintenance.
7:10 | - | Narail 132/33kV S/S TR2 (413-T) HT Scheduled S/D Due to 33 KV T2 and busbar shutdown for Red Hot maintenance.
7:21 | - | Faridpur 132/33kV S/S Transformer-1 LT Scheduled S/D Due to 33 kv Bus section-1 red hot maintenance. | [5 empty] | 40.0MW load interrup.
7:22 | - | Aminbazar 400/230/132kV S/S ATR-02 LT Scheduled S/D Due to Redhot Maintenance.
7:22 | - | Aminbazar 400/230/132kV S/S ATR-02 HT Scheduled S/D Due to Red hot maintenance.
7:22 | - | Faridpur 132/33kV S/S Transformer-1 HT Scheduled S/D Due to 33 kv Bus section-1 red hot maintenance. | [5 empty] | 40.0MW load interrup.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-05-18 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 100 | 2195594 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 3969000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 398 | 9248760 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 348 | 7556000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9670000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 9 | 162240 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 270 | 6981295 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 85 | 440397 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 30 | 95242 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 20 | 0 | 16281 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 10 | 225684 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 98000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 17 | 185386 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 41 | 430992 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 255240 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 82 | 1315200 | High voltage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 623333
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 636434 | Fuel shortage
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 49 | 991560 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 636840
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 31 | 656100
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 396480 | 0:00
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 195 | 1726253 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 1708430 | Reserved
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 449532 | Reserved
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 317109 | Reserved
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 114 | 982512 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1437974 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 53 | 586560 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 1118880 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 167130
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 34 | 488880 | Fuel shortage
| Dhaka area Total |  |  |  | 5867 | 2899 | 55769318
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 229192
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 53325
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 44 | 371040 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 25 | 300000 | Low Water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 211 | 2158058 | Gas shortage
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 87 | 960145 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 66 | 924048 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 84 | 1222724 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 33 | 1220520 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 38 | 654720 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 78192 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 7 | 466080
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 30 | 201600 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 12961
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 290 | 2546727
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 287888 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 92 | 1496248 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 38 | 644160
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 417764 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 62 | 950109 | Fuel shortage
| Chattogram area Total |  |  |  | 2545 | 1166 | 15195501
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 212 | 4543000 | 0
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7793900
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 35 | 802584 | Machine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 167 | 3094545 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 755952 | Machine problem
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 150 | 916654
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 38 | 576240 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 424800 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 336168 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 5 | 92340 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 138 | 2749440
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 483600 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 439824 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 12 | 297460 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 67 | 1092120 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 95 | 623280 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 676800 | Fuel shortage
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 102 | 1118400 | Fuel shortage
| Cumilla Area Total |  |  |  | 3096 | 1477 | 26817107
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 49 | 1290240 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 15 | 297000 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14200
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 88 | 1120800 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 88 | 1075200 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 319410
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 225360 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 252 | 4342210
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1006000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 230400 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 940200
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 48 | 900144
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 181305
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 298368 | Under maint.
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1426560
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 135 | 2372160 | ST Under maint.
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 228000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 248448 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 250 | 6626000 | Gas shortage
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 367 | 8534000 | Gas shortage
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 190800
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 315 | 7971200 | Gas shortage
| Sylhet Area Total |  |  |  | 2427 | 1325 | 31153585
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 905 | 19989818
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 66 | 497280 | High voltage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 25 | 140160 | High voltage
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserved
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 125625 | High voltage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 226080 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 50 | 119664 | High voltage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 327600
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 326 | 7760000
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 2901 | 1397 | 29186227
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 59040 | Fuel shortage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 23 | 425600 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 106 | 3322437 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1060 | 22753600 | Transformer O/L.
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 0 | 0 | Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 27600 | Transformer O/L.
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 182 | 4011700 | Transformer O/L.
| Barisal Area Total |  |  |  | 2265 | 1404 | 30599977
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 28 | 204880 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 28 | 100281 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 28 | 14 | 301820 | High voltage
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 421568 | High voltage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 295035 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 177 | 4193082 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 945545 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 418 | 9128909
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 418779 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 383760
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 93528 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 616738 | Engine problem
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 54 | 857744 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 652032 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 55 | 861024 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 25980
| Adani Power Jharkhanda Ltd |  | Import | 748*1 | 748 | 400 | 3098182 | On test.
| Rajshahi Area Total |  |  |  | 2905 | 1373 | 22598887
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 74 | 1736290
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 260 | 5964000
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 81 | 829094 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 30979
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1064256
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 119037
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 890980
| Rangpur Area Total |  |  |  | 750 | 530 | 10634636
| Total |  |  |  | 23370 | 11823 | 226297448
| Eastern Grid Total |  |  |  | 14549 | 7119 | 133277721
| Western Grid Total |  |  |  | 8821 | 4704 | 93019727
| National Grid Total |  |  |  | 23370 | 11823 | 226297448
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-05-18
| (a) ENTIRE EASTERN GRID : |  | 7980.8 | MW | (b) ENTIRE WESTERN GRID : |  | 3290.6 | MW
| i) Dhaka area |  | 4518.9 | MW | i) Khulna area |  | 953 | MW
| ii) Chittagong area |  | 1033.9 | MW | ii) Rajshahi area |  | 1237.6 | MW
| iii) Comilla area |  | 1046 | MW | iii) Barisal area |  | 335 | MW
| iv) Mymensingh area |  | 938 | MW | iv) Rangpur area |  | 765 | MW
| v) Sylhet area |  | 444 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11271.4 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 12 | 01:00 | Chhatak | 23 | 00:00 | Kamrangirchar | 78 | 19:30 | Natore | 130 | 22:00 | Shitalakhya | 109 | 16:00
2 | AKSML | 7.2 | 08:00 | Chowmuhani | 164 | 19:30 | Kaptai | 4 | 19:00 | Nawabganj | 42.6 | 19:00 | Sholosohor | 26 | 12:00
3 | Aftabnagar | 46 | 13:00 | Chuadanga | 82 | 22:00 | Kazla | 82 | 12:00 | Netrakona | 126 | 19:30 | Shyampur | 164 | 13:00
4 | Agargaon | 68 | 13:00 | Coxsbazar | 99 | 19:00 | Keranigonj | 58 | 19:00 | New | 74 | 15:00 | Siddhirganj | 92 | 23:00
5 | Agrabad | 48 | 12:00 | Cumilla(N) | 131 | 18:30 | Khagrachori | 26 | 19:00 | Niamatpur | 74 | 00:00 | Sirajganj | 97 | 21:00
6 | Amnura | 49 | 01:00 | Cumilla(S) | 142 | 16:00 | Khulna | 85 | 23:00 | Noapara | 47 | 19:00 | Sonargaon | 82 | 00:00
7 | Ashuganj | 63 | 23:00 | Daudkandi | 127 | 19:30 | Khulshi | 153 | 19:00 | PHP | 3 | 18:30 | Sreemongol | 49 | 19:00
8 | BIPTC | N/A | N/A | Dhaka | 18 | 12:00 | Kishoreganj | 120 | 19:00 | Pabna | 91 | 22:00 | Sreepur | 60 | 19:00
9 | BSRM | 81 | 01:00 | Dhamrai | 106 | 14:00 | Kodda | 299 | 18:30 | Palashbari | 108 | 19:00 | Srinagar | 39 | 21:00
10 | Bagerhat | 76 | 19:00 | Dhanmondi | 120.4 | 13:00 | Kulaura | 34 | 19:00 | Panchagarh | 50 | 19:30 | Sunamganj | 39 | 19:30
11 | Bakulia | 74 | 19:30 | Dohazari | 68 | 00:00 | Kurigram | 52 | 19:00 | Patuakhali | 83 | 21:00 | Sylhet | 116 | 18:30
12 | Banani | 80 | 17:00 | Faridpur | 128 | 19:00 | Kushtia | 124 | 21:00 | Payra | 16 | 19:00 | TK | 23 | 19:00
13 | Bangabhaban | 14 | 10:00 | Fatullah | 60 | 15:00 | Lalbag | 86 | 13:00 | Postogola | 49 | 13:00 | Tangail | 203 | 19:00
14 | Barapukuria | 54 | 20:00 | Fenchuganj | 37 | 19:30 | Lalmonirhat | 38 | 19:00 | Purbachal | 16 | 12:00 | Thakurgaon | 73 | 19:30
15 | Barguna | 16 | 21:00 | Feni | 92 | 19:00 | Madanganj | 30 | 19:00 | Purbasadipur | 110 | 00:00 | Tongi | 92 | 12:00
16 | Barishal | 81 | 19:30 | GPH | 85 | 15:00 | Madaripur | 82 | 21:00 | Rahanpur_I | 19 | 03:00 | Ullon | 33 | 19:30
17 | Barishal-230 | 72 | 19:30 | Ghorashal | 68 | 00:00 | Madartek | 64 | 21:00 | Rahim | 44 | 10:00 | Uttara | 56 | 19:00
18 | Baroaulia | 57 | 00:00 | Goalpara | 38 | 19:00 | Madunaghat | 46 | 21:00 | Rajbari | 56 | 19:00 | UttaraNew | 44 | 14:00
19 | Baroirhat | 44 | 19:00 | Gollamari | 39 | 13:00 | Magura | 46 | 18:30 | Rajendrapur | 78 | 22:00 | Zigatola | 37 | 13:00
20 | Bashundhara | 140 | 19:00 | Gopalganj | 81 | 19:30 | Mahasthangarh | 62 | 19:30 | Rajshahi | 142 | 22:00
21 | BashundharaCement | 6 | 16:00 | Gulshan | 58 | 15:00 | Manikganj | 105 | 19:00 | Rajshahi-230 | 34 | 00:00
22 | Beanibazar | 51 | 20:00 | Halishahar | 79.5 | 14:00 | Maniknagar | 74 | 13:00 | Ramganj | 84 | 19:00
23 | Benapole | 48 | 15:00 | HaripurSBU | 150 | 10:00 | Matarbari | 33 | 00:00 | Rampur | 27 | 00:00
24 | Bhaluka | 148 | 22:00 | Hasnabad | 82 | 22:00 | Matuail | 62 | 15:00 | Rangamati | 14 | 19:30
25 | Bhandaria | 40 | 19:30 | Hathazari | 56 | 20:00 | Millgate | 92 | 15:00 | Rangpur | 99 | 20:00
26 | Bhangura | 36 | 20:00 | Ishurdi | 55 | 13:00 | Mirpur | 113 | 15:00 | Ruppur | 6 | 14:00
27 | Bheramara(GK) | 51 | 21:00 | Jaldhaka | 60 | 19:30 | Mirsorai | 4 | 20:00 | SSM | 16 | 12:00
28 | Bhulta | 254 | 23:00 | Jamalpur | 109 | 20:00 | Mithapukur | 44 | 19:30 | Saidpur | 93 | 19:30
29 | Bog-Sherpur | 58 | 21:00 | Jashore | 86 | 18:30 | Modern | 0 | 00:00 | Satkhira | 94 | 00:00
30 | Bogura | 145 | 20:00 | Jhenaidah | 90 | 21:00 | Mogbazar | 114 | 15:00 | Satmasjid | 85 | 14:00
31 | Borhanuddin | 45 | 21:00 | Joydebpur | 152 | 19:00 | Mongla | 24 | 15:00 | Savar | 169 | 19:30
32 | Brahmanbaria | 144 | 22:00 | Joypurhat | 52 | 20:00 | Motijheel | 34 | 13:00 | Shahjadpur | 93 | 19:30
33 | Cantonment | 116 | 13:00 | Juldah | 27 | 01:00 | Munshiganj | 91 | 17:00 | Shahjibazar | 104 | 22:00
34 | Chandpur | 61 | 20:00 | KSRM | 13 | 10:00 | Mymensingh | 170 | 19:30 | Shahmirpur | 45 | 00:00
35 | Chandraghona | 26 | 18:30 | Kabirpur | 252 | 19:30 | Naogaon | 118 | 22:00 | Shariatpur | 59 | 22:00
36 | Chapai | 67 | 00:00 | Kachua | 62 | 22:00 | Narail | 41 | 19:00 | Sherpur | 110 | 19:30
37 | Charsaidpur | 45 | 02:00 | Kallyanpur | 96 | 22:00 | Narinda | 64 | 13:00 | Shikalbaha | 27 | 00:00
38 | Chauddagram | 46 | 20:00 | Kalurghat | 30 | 10:00 | Narshingdi | 152 | 21:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-05-18 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 410 | 06:00 | 392 | 00:00 | Kaliakoir | N/A | N/A | N/A | N/A
| Bhulta | 393 | 06:00 | 377 | 12:00 | Madunaghat_I | 420 | 19:30 | 389 | 06:00
| Bibiana | 408 | 04:00 | 400 | 15:00 | Payra | 419 | 06:00 | 408 | 23:00
| BIPTC | 408 | 06:00 | 394 | 15:00 | Rahanpur_I | 423 | 17:00 | 387 | 09:00
| Gopalganj | 414 | 06:00 | 396 | 00:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 239 | 08:00 | 226 | 15:00 | Hathazari | 243 | 21:00 | 210 | 08:00
| AKSML | 243 | 19:00 | 195 | 06:00 | Ishurdi | 242 | 06:00 | 225 | 12:00
| Aminbazar | 237 | 07:00 | 228 | 00:00 | Jhenaidah | 239 | 06:00 | 220 | 12:00
| Ashuganj | 237 | 18:00 | 230 | 08:00 | Kaliakoir | N/A | N/A | N/A | N/A
| Baghabari | 235 | 05:00 | 227 | 11:00 | Keranigonj | 234 | 06:00 | 225 | 00:00
| Barapukuria | 229 | 03:00 | 218 | 12:00 | Khulna(S) | 239 | 06:00 | 225 | 12:00
| Barishal | 240 | 07:00 | 227 | 23:00 | Madunaghat_I | 242 | 19:30 | 222 | 06:00
| Bheramara | 241 | 06:00 | 223 | 12:00 | Maniknagar | 232 | 07:00 | 223 | 12:00
| Bhulta | 236 | 06:00 | 226 | 11:00 | Meghnaghat | 234 | 00:00 | 231 | 05:00
| Bibiana | 240 | 10:00 | 234 | 06:00 | Mirsorai | 242 | 22:00 | 212 | 08:00
| BIPTC | 241 | 06:00 | 222 | 12:00 | Rajshahi | 243 | 06:00 | 226 | 00:00
| Bogura | 236 | 05:00 | 220 | 12:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 241 | 07:00 | 229 | 23:00 | Rampura | 236 | 05:00 | 224 | 14:00
| BSRM | 241 | 21:00 | 206 | 06:00 | Shikalbaha | 241 | 19:30 | 209 | 06:00
| Cumilla(N) | 235 | 19:30 | 225 | 08:00 | Shyampur | 230 | 18:00 | 225 | 00:00
| Fenchuganj | 243 | 22:00 | 237 | 03:00 | Siddhirganj | 232 | 18:00 | 227 | 11:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 242 | 05:00 | 233 | 11:00
| GPH | 241 | 19:30 | 198 | 06:00 | Sreepur | 234 | 18:30 | 229 | 14:00
| Haripur | 233 | 04:00 | 224 | 12:00 | Tongi | 234 | 05:00 | 222 | 12:00
| Hasnabad | 236 | 05:00 | 226 | 01:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 140 | 06:00 | 131 | 12:00 | Lalbag | 138 | 18:00 | 133 | 09:00
| Agargaon | 137 | 06:00 | 129 | 15:00 | Lalmonirhat | 143 | 05:00 | 127 | 12:00
| Agrabad | 140 | 19:00 | 114 | 06:00 | Madanganj | 137 | 06:00 | 126 | 00:00
| AKS | 137 | 19:30 | 115 | 05:00 | Madaripur | 133 | 07:00 | 126 | 23:00
| Aminbazar | 134 | 07:00 | 128 | 00:00 | Madartek | 138 | 06:00 | 130 | 12:00
| Amnura | 138 | 04:00 | 129 | 08:00 | Madunaghat | 140 | 18:30 | 116 | 06:00
| Ashuganj | 140 | 06:00 | 135 | 12:00 | Magura | 143 | 06:00 | 124 | 05:00
| Bagerhat | 140 | 07:00 | 125 | 14:00 | Mahasthangarh | 142 | 04:00 | 130 | 12:00
| Bakulia | 140 | 19:30 | 122 | 06:00 | Manikganj | 140 | 06:00 | 128 | 00:00
| Banani | 139 | 06:00 | 130 | 12:00 | Maniknagar | 138 | 06:00 | 128 | 12:00
| Bangabhaban | 138 | 06:00 | 129 | 12:00 | Matarbari | 137 | 12:00 | 114 | 06:00
| Barapukuria | 143 | 02:00 | 127 | 14:00 | Matuail | 137.4 | 06:00 | 129 | 12:00
| Barguna | 141 | 07:00 | 133 | 23:00 | Millgate | 139 | 05:00 | 128 | 16:00
| Barishal | 141 | 09:00 | 124 | 23:00 | Mirpur | 135 | 05:00 | 127 | 00:00
| Barishal-230 | 135 | 07:00 | 125 | 23:00 | Mithapukur | 142 | 04:00 | 129 | 12:00
| Baroaulia | 141 | 22:00 | 122 | 06:00 | Modern | 141 | 22:00 | 119 | 06:00
| Baroirhat | 137 | 19:00 | 115 | 06:00 | Mogbazar | 139 | 07:00 | 131 | 15:00
| Bashundhara | 139 | 05:00 | 128 | 15:00 | Mongla | 139 | 07:00 | 127 | 13:00
| BashundharaCement | 137 | 06:00 | 128 | 12:00 | Motijheel | 138 | 06:00 | 129 | 12:00
| Beanibazar | 135 | 09:00 | 128 | 18:30 | Munshiganj | 137 | 06:00 | 129 | 00:00
| Benapole | 141 | 05:00 | 126 | 12:00 | Mymensingh | 140 | 06:00 | 109 | 22:00
| Bhaluka | 136 | 06:00 | 123 | 00:00 | Naogaon | 141 | 05:00 | 125 | 00:00
| Bhandaria | 140 | 09:00 | 129 | 23:00 | Narail | 142 | 05:00 | 127 | 14:00
| Bhangura | 144 | 06:00 | 132 | 11:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 138 | 06:00 | 127 | 12:00 | Narshingdi | 137 | 06:00 | 123 | 01:00
| Bheramara(GK) | 139 | 06:00 | 127 | 12:00 | Natore | 139 | 05:00 | 128 | 00:00
| Bhulta | 132 | 06:00 | 121 | 00:00 | Nawabganj | 138 | 05:00 | 133 | 00:00
| Bog-Sherpur | 143 | 04:00 | 131 | 12:00 | Netrakona | 138 | 05:00 | 122 | 08:00
| Bogura | 143 | 04:00 | 130 | 12:00 | New | 135 | 06:00 | 129 | 16:00
| Bogura-230 | 143 | 05:00 | 131 | 12:00 | Niamatpur | 141 | 04:00 | 121 | 00:00
| Brahmanbaria | 135 | 18:00 | 130 | 23:00 | Noapara | 140 | 06:00 | 129 | 12:00
| Cantonment | 136 | 06:00 | 129 | 15:00 | Pabna | 140 | 05:00 | 129 | 11:00
| Chandpur | 137 | 19:00 | 122 | 03:00 | Palashbari | 142 | 05:00 | 128 | 12:00
| Chandraghona | 141 | 22:00 | 119 | 06:00 | Panchagarh | 141 | 04:00 | 124 | 12:00
| Chapai | 138 | 05:00 | 129 | 09:00 | Patuakhali | 140 | 03:00 | 135 | 22:00
| Charsaidpur | 139 | 06:00 | 129 | 00:00 | Payra | 141 | 06:00 | 137 | 00:00
| Chauddagram | 135 | 19:30 | 123 | 05:00 | PHP | 137 | 19:30 | 115 | 06:00
| Chhatak | 135 | 08:00 | 128 | 22:00 | Postogola | 135 | 06:00 | 128 | 11:00
| Chowmuhani | 135 | 09:00 | 114 | 05:00 | Purbachal | 139 | 05:00 | 128 | 16:00
| Chuadanga | 141 | 06:00 | 124 | 14:00 | Purbasadipur | 142 | 04:00 | 125 | 12:00
| Coxsbazar | 138 | 12:00 | 101 | 06:00 | Rahim | 138 | 06:00 | 130 | 12:00
| Cumilla(N) | 137 | 07:00 | 132 | 00:00 | Rajbari | 136 | 06:00 | 124 | 15:00
| Cumilla(S) | 138 | 22:00 | 124 | 16:00 | Rajendrapur | 141 | 06:00 | 128 | 04:00
| Daudkandi | 134 | 09:00 | 126 | 04:00 | Rajshahi | 139.5 | 05:00 | 127 | 00:00
| Dhaka | 140 | 06:00 | 131 | 12:00 | Rajshahi-230 | 138 | 05:00 | 127 | 00:00
| Dhamrai | 140 | 06:00 | 130 | 14:00 | Ramganj | 134 | 18:00 | 114 | 06:00
| Dhanmondi | 139 | 06:00 | 128 | 12:00 | Rampur | 139 | 19:30 | 116 | 06:00
| Dohazari | 140 | 11:00 | 116 | 06:00 | Rampura | 137 | 7:00 | 131 | 12:00
| Faridpur | 135 | 05:00 | 125 | 14:00 | Rangamati | 140 | 19:30 | 116 | 06:00
| Fatullah | 135 | 06:00 | 129 | 00:00 | Rangpur | 144 | 04:00 | 130 | 21:00
| Fenchuganj | 138 | 09:00 | 134 | 04:00 | Ruppur | 140 | 04:00 | 130 | 11:00
| Feni | 137 | 19:30 | 120 | 06:00 | Saidpur | 142 | 04:00 | 126 | 00:00
| Ghorashal | 140 | 07:00 | 136 | 09:00 | Satkhira | 140 | 07:00 | 126 | 12:00
| Goalpara | 140 | 07:00 | 130 | 03:00 | Satmasjid | 136 | 06:00 | 129 | 15:00
| Gollamari | 139 | 06:00 | 130 | 00:00 | Savar | 134 | 06:00 | 126 | 00:00
| Gopalganj | 136 | 06:00 | 127 | 12:00 | Shahjadpur | 146 | 06:00 | 135 | 00:00
| Gopalganj-400 | 134 | 06:00 | 127 | 00:00 | Shahjibazar | 136 | 18:00 | 132 | 23:00
| Gulshan | 138 | 06:00 | 130 | 09:00 | Shahmirpur | 140 | 22:00 | 120 | 06:00
| Halishahar | 140 | 19:30 | 121 | 06:00 | Shariatpur | 134 | 06:00 | 125 | 14:00
| Haripur | 138 | 06:00 | 130 | 12:00 | Sherpur | 138 | 05:00 | 122 | 23:00
| HaripurSBU | 138 | 06:00 | 130 | 12:00 | Shikalbaha | 142 | 19:30 | 121 | 06:00
| Hasnabad | 134 | 06:00 | 127 | 12:00 | Shikalbaha-230 | 141 | 19:30 | 122 | 06:00
| Hathazari | 140 | 19:30 | 122 | 08:00 | Shitalakhya | 134 | 06:00 | 124 | 01:00
| Ishurdi | 140 | 05:00 | 130 | 00:00 | Sholosohor | 140 | 19:30 | 114 | 06:00
| Jaldhaka | 143 | 04:00 | 126 | 12:00 | Shyampur | 136 | 06:00 | 128 | 01:00
| Jamalpur | 139 | 04:00 | 124 | 08:00 | Shyampur-230 | 133 | 18:00 | 129 | 00:00
| Jashore | 140 | 06:00 | 126 | 12:00 | Siddhirganj | 137 | 06:00 | 129 | 12:00
| Jhenaidah | 143 | 06:00 | 130 | 13:00 | Sirajganj | 141 | 04:00 | 131 | 01:00
| Jhenaidah-230 | 142 | 06:00 | 130 | 12:00 | Sonargaon | 133 | 07:00 | 129 | 23:00
| Joydebpur | 142 | 06:00 | 133 | 17:00 | Sreemongol | 135 | 01:00 | 131 | 23:00
| Joypurhat | 141 | 05:00 | 124 | 00:00 | Sreepur | 135 | 13:00 | 129 | 22:00
| Juldah | 140 | 19:00 | 111 | 06:00 | Srinagar | 138 | 18:00 | 134 | 00:00
| Kabirpur | 141 | 06:00 | 126 | 14:00 | SSM | 142 | 19:00 | 125 | 06:00
| Kachua | 136 | 07:00 | 120 | 06:00 | Sunamganj | 134 | 09:00 | 127 | 19:00
| Kaliakoir | N/A | N/A | N/A | N/A | Sylhet | 133 | 01:00 | 130 | 11:00
| Kallyanpur | 135 | 06:00 | 125 | 12:00 | Tangail | 141 | 06:00 | 128 | 00:00
| Kalurghat | 140 | 19:00 | 116 | 06:00 | Thakurgaon | 140 | 03:00 | 123 | 12:00
| Kamrangirchar | 137 | 19:30 | 122 | 00:00 | TK | 140 | 18:00 | 113 | 06:00
| Kaptai | 140 | 18:30 | 130 | 00:00 | Tongi | 139 | 05:00 | 131 | 12:00
| Kazla | 136 | 06:00 | 128 | 12:00 | Ullon | 138 | 05:00 | 131 | 12:00
| Keranigonj | 138 | 05:00 | 132 | 09:00 | Uttara | 135 | 06:00 | 127 | 00:00
| Khagrachori | 140 | 22:00 | 117 | 06:00 | UttaraNew | 133 | 06:00 | 127 | 00:00
| Khulna | 139 | 06:00 | 129 | 12:00 | Zigatola | 138 | 06:00 | 134 | 00:00
| Khulna(S) | 140 | 06:00 | 130 | 12:00
| Khulshi | 139 | 19:00 | 117 | 06:00
| Kishoreganj | 133 | 07:00 | 120 | 21:00
| Kodda | 140 | 06:00 | 129 | 01:00
| KSRM | 140 | 19:00 | 114 | 06:00
| Kulaura | 137 | 01:00 | 133 | 23:00
| Kurigram | 144 | 05:00 | 126 | 12:00
| Kushtia | 140 | 05:00 | 128 | 12:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2023-05-18
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 700 | 6300 | 4580 | 10880 |  |  |  | QF-LDC-11
0:30 | 740 | 6078 | 4463.5 | 10541.5 | Date: | 2023-05-18
1:00 | 780 | 5856 | 4347 | 10203
1:30 | 788 | 5776.5 | 4105.5 | 9882
2:00 | 796 | 5697 | 3864 | 9561
2:30 | 818 | 5452.5 | 3643.5 | 9096 | [5 empty] | Gen. at Eve. Peak | 11823 | 11823 MW (19:30 )
3:00 | 840 | 5208 | 3423 | 8631 | [6 empty] | 19:30
3:30 | 880 | 5047 | 3197.5 | 8244.5 | [5 empty] | Gen. at Day Peak | 9855 | 9855 MW (12:00 )
4:00 | 920 | 4886 | 2972 | 7858 | [6 empty] | 12:00
4:30 | 755 | 4597 | 2859 | 7456 | [5 empty] | Highest Generation | 11823
5:00 | 590 | 4308 | 2746 | 7054 | [6 empty] | 19:30
5:30 | 525 | 3615 | 2391.5 | 6006.5
6:00 | 460 | 2922 | 2037 | 4959
6:30 | 650 | 2916 | 2233.5 | 5149.5
7:00 | 840 | 2910 | 2430 | 5340
7:30 | 860 | 3190 | 2627.5 | 5817.5
8:00 | 880 | 3470 | 2825 | 6295
8:30 | 885 | 3758 | 2897 | 6655
9:00 | 890 | 4046 | 2969 | 7015
9:30 | 965 | 4352 | 3109 | 7461
10:00 | 1040 | 4658 | 3249 | 7907
10:30 | 995 | 5049 | 3404.5 | 8453.5
11:00 | 950 | 5440 | 3560 | 9000
11:30 | 865 | 5770.5 | 3657 | 9427.5
12:00 | 780 | 6101 | 3754 | 9855
12:30 | 810 | 6096.5 | 3920 | 10016.5
13:00 | 840 | 6092 | 4086 | 10178
13:30 | 830 | 6061.5 | 4056.5 | 10118
14:00 | 820 | 6031 | 4027 | 10058
14:30 | 840 | 6011 | 4056.5 | 10067.5
15:00 | 860 | 5991 | 4086 | 10077
15:30 | 885 | 5996 | 4150.5 | 10146.5
16:00 | 910 | 6001 | 4215 | 10216
16:30 | 895 | 6063 | 4225.5 | 10288.5
17:00 | 880 | 6125 | 4236 | 10361
17:30 | 800 | 6120.5 | 4227.5 | 10348
18:00 | 720 | 6116 | 4219 | 10335
18:30 | 745 | 6564.5 | 4423 | 10987.5
19:00 | 770 | 7013 | 4627 | 11640
19:30 | 712 | 7119 | 4704 | 11823
20:00 | 570 | 7193 | 4501 | 11694 |  |  |  | Executive Engineer
20:30 | 555 | 7217 | 4524.5 | 11741.5 |  |  |  | Network Operation Division
21:00 | 540 | 7241 | 4548 | 11789
21:30 | 545 | 7147.5 | 4568.5 | 11716
22:00 | 550 | 7054 | 4589 | 11643 |  |  |  |  | Page 6 of 7
22:30 | 615 | 6847.5 | 4561 | 11408.5
23:00 | 680 | 6641 | 4533 | 11174
23:30 | 690 | 6470.5 | 4556.5 | 11027
24:00 | 700 | 6300 | 4580 | 10880
11823 MW (19:30 )
9855 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-05-18 |  | Energy |  | 226297448
[13 empty] | 2023-05-18 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 2705 | 795 | 2281 | 188 | 1610 | 2482 | 0 | 224 | 469 | 126 | 0 | 0
0:30 | 2930.5 | 827.5 | 2205 | 94 | 1389.5 | 2375 | 0 | 188 | 407 | 125 | 0 | 0 |  | Date: | 43602
1:00 | 3156 | 860 | 2129 | 0 | 1169 | 2268 | 0 | 152 | 345 | 124 | 0 | 0
1:30 | 3109 | 860 | 2102.5 | 0 | 1135.5 | 2053.5 | 0 | 152 | 344.5 | 125 | 0 | 0 | [8 empty] | Total Energy | 226.2974 |  | Total Energy Gen MKWHr Energy Not Served MKWHr Energy Requirement MKWHr | Total Energy Gen 226.297 MKWHr Energy Not Served 1.335 MKWHr Energy Requirement 227.632 MKWHr
2:00 | 3062 | 860 | 2076 | 0 | 1102 | 1839 | 0 | 152 | 344 | 126 | 0 | 0 | [8 empty] | Energy not Served | 1.335
2:30 | 3049.5 | 860 | 1994 | 0 | 865 | 1781 | 0 | 151.5 | 270 | 125 | 0 | 0 | [8 empty] | Energy Requirement | 227.6325
3:00 | 3037 | 860 | 1912 | 0 | 628 | 1723 | 0 | 151 | 196 | 124 | 0 | 0
3:30 | 2986 | 877.5 | 1778 | 0 | 594.5 | 1544 | 0 | 150.5 | 196 | 118 | 0 | 0 | [7 empty] | Shortage
4:00 | 2935 | 895 | 1644 | 0 | 561 | 1365 | 0 | 150 | 196 | 112 | 0 | 0
4:30 | 2870 | 858 | 1608 | 0 | 463 | 1304.5 | 0 | 135 | 106.5 | 111 | 0 | 0
5:00 | 2805 | 821 | 1572 | 0 | 365 | 1244 | 0 | 120 | 17 | 110 | 0 | 0
5:30 | 2435 | 486 | 1426.5 | 0 | 262.5 | 1221.5 | 0 | 60 | 8.5 | 106 | 0.5 | 0
6:00 | 2065 | 151 | 1281 | 0 | 160 | 1199 | 0 | 0 | 0 | 102 | 1 | 0
6:30 | 1989 | 376 | 1292.5 | 0 | 215.5 | 1197 | 0 | 0 | 0 | 66 | 13.5 | 0 | [6 empty] | Coal
7:00 | 1913 | 601 | 1304 | 0 | 271 | 1195 | 0 | 0 | 0 | 30 | 26 | 0
7:30 | 2027 | 754 | 1455 | 0 | 287 | 1207.5 | 0 | 0 | 0 | 51 | 36 | 0 | [5 empty] | Oil
8:00 | 2141 | 907 | 1606 | 0 | 303 | 1220 | 0 | 0 | 0 | 72 | 46 | 0
8:30 | 2158.5 | 907.5 | 1803.5 | 0 | 369.5 | 1247.5 | 0 | 0 | 0 | 77 | 91.5 | 0
9:00 | 2176 | 908 | 2001 | 0 | 436 | 1275 | 0 | 0 | 0 | 82 | 137 | 0
9:30 | 2319.5 | 907 | 2046 | 0 | 548 | 1323 | 0 | 0 | 14 | 87 | 216.5 | 0
10:00 | 2463 | 906 | 2091 | 0 | 660 | 1371 | 0 | 0 | 28 | 92 | 296 | 0
10:30 | 2543 | 906.5 | 2140 | 0 | 974.5 | 1413 | 12.5 | 0 | 109 | 103 | 252 | 0
11:00 | 2623 | 907 | 2189 | 0 | 1289 | 1455 | 25 | 0 | 190 | 114 | 208 | 0
11:30 | 2637 | 907 | 2217.5 | 185 | 1385.5 | 1515.5 | 25 | 0 | 235 | 116 | 204 | 34
12:00 | 2651 | 907 | 2246 | 370 | 1482 | 1576 | 25 | 0 | 280 | 118 | 200 | 68
12:30 | 2614.5 | 927.5 | 2225.5 | 378 | 1489 | 1657 | 25 | 13.5 | 302.5 | 123 | 261 | 207.81
13:00 | 2578 | 948 | 2205 | 386 | 1496 | 1738 | 25 | 27 | 325 | 128 | 322 | 347.62
13:30 | 2578 | 948 | 2205 | 386 | 1496 | 1738 | 25 | 27 | 325 | 128 | 322 | 347.62
14:00 | 2578 | 948 | 2205 | 386 | 1496 | 1738 | 25 | 27 | 325 | 128 | 322 | 347.62
14:30 | 2603 | 927.5 | 2204.5 | 404 | 1396 | 1801.5 | 25 | 26.5 | 366 | 130 | 243.5 | 375.7925
15:00 | 2628 | 907 | 2204 | 422 | 1296 | 1865 | 25 | 26 | 407 | 132 | 165 | 403.965
15:30 | 2614.5 | 901 | 2193.5 | 420 | 1316 | 1897.5 | 25 | 26 | 440 | 137 | 176 | 313.7175
16:00 | 2601 | 895 | 2183 | 418 | 1336 | 1930 | 25 | 26 | 473 | 142 | 187 | 223.47
16:30 | 2620.5 | 894.5 | 2189 | 390 | 1446.5 | 1939.5 | 25 | 29 | 486 | 138 | 130.5 | 111.735
17:00 | 2640 | 894 | 2195 | 362 | 1557 | 1949 | 25 | 32 | 499 | 134 | 74 | 0 | [10 empty] | 472
17:30 | 2632.5 | 898 | 2163.5 | 206 | 1727.5 | 1966 | 25 | 45 | 518.5 | 124 | 42 | 0 | [10 empty] | 100
18:00 | 2625 | 902 | 2132 | 50 | 1898 | 1983 | 25 | 58 | 538 | 114 | 10 | 0 | [10 empty] | 20
18:30 | 2626 | 902 | 2203.5 | 50 | 2306.5 | 2086.5 | 25 | 114 | 543 | 126 | 5 | 0 | [10 empty] | 592
19:00 | 2627 | 902 | 2275 | 50 | 2715 | 2190 | 25 | 170 | 548 | 138 | 0 | 0
19:30 | 2660 | 905 | 2186 | 0 | 2861 | 2302 | 25 | 211 | 535 | 138 | 0 | 0
20:00 | 2732 | 810 | 2209 | 0 | 2745 | 2329 | 25 | 224 | 484 | 136 | 0 | 0
20:30 | 2742 | 810 | 2218.5 | 0 | 2715.5 | 2350.5 | 25 | 225 | 518 | 137 | 0 | 0
21:00 | 2752 | 810 | 2228 | 0 | 2686 | 2372 | 25 | 226 | 552 | 138 | 0 | 0
21:30 | 2764.5 | 810 | 2246.5 | 0 | 2558.5 | 2395 | 25 | 226.5 | 552 | 138 | 0 | 0
22:00 | 2777 | 810 | 2265 | 0 | 2431 | 2418 | 25 | 227 | 552 | 138 | 0 | 0
22:30 | 2811 | 802.5 | 2266 | 0 | 2200.5 | 2438.5 | 12.5 | 224.5 | 515 | 138 | 0 | 0
23:00 | 2845 | 795 | 2267 | 0 | 1970 | 2459 | 0 | 222 | 478 | 138 | 0 | 0
23:30 | 2775 | 795 | 2274 | 94 | 1790 | 2470.5 | 0 | 223 | 473.5 | 132 | 0 | 0 |  | Max Temp. in Dhaka |  | 32.1° C
24:00 | 2705 | 795 | 2281 | 188 | 1610 | 2482 | 0 | 224 | 469 | 126 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 226.297 MKWHr Energy Not Served 1.335 MKWHr Energy Requirement 227.632 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-05-18
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | [10 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 0 |  | 300000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | [6 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 |  | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 229192
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 6 | 13 | 17 | 11 | 0 | 1 | 1 | 1 | 2 | 3 | 0 | [8 empty] | 53325
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil) | 152 | 152 | 151 | 150 | 120 | [6 empty] | 0 | 27 | 27 | 26 | 26 | 32 | 58 |  | 170 | 211 | 224 | 226 | 227 | 222 | 224 | 2158058
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 84 | 84 | 84 | 84 | 17 | [6 empty] | 17 | 34 | 51 | 51 | 84 | 84 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 78 | 1222724
12 | Hathazari 100 MW peaking PP | 57 | 57 | 57 | 57 | [7 empty] | 20 | 20 | 48 | 54 | 64 | 65 | 56 |  | 58 | 66 | 66 | 66 | 66 | 66 | 66 | 924048
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 |  |  |  | 15 | 17 | 24 | 34 | 34 | 34 | 34 | 34 | 35 | 87 |  | 87 | 87 | 87 | 87 | 87 | 84 | 36 | 960145
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 39 | 39 | 39 | 39 | [8 empty] | 29 | 30 | 36 | 38 | 30 | 30 |  | 35 | 38 | 38 | 38 | 38 | 38 | 39 | 576240
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 57 | [24 empty] | 0 | 98000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 72 | 47 | [7 empty] | 7 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 55 |  | 193 | 195 | 195 | 195 | 195 | 195 | 195 | 1726253
19 | Ashuganj 195MW PP (APSCL-United) | 170 | 170 | 130 | 108 | 108 | 16 | 8 | 8 | 110 | 128 | 128 | 130 | 138 | 138 | 138 | 138 | 138 | 167 |  | 167 | 167 | 167 | 170 | 170 | 170 | 170 | 3094545
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 120 | 120 | 120 | 100 | 93 |  |  |  |  | 80 | 120 | 120 | 115 | 130 | 130 | 120 | 100 | 100 |  | 95 | 100 | 100 | 100 | 100 | 100 | 120 | 2195594
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 110 | 110 | 110 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 100 | 3969000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 42 | 42 | 43 | 43 | 43 | 5 | 5 | 5 | 38 | 31 | 33 | 34 | 33 | 37 | 37 | 33 | 32 | 36 |  | 33 | 35 | 38 | 40 | 41 | 41 | 41 | 802584
33 | Ashuganj 225 MW CCPP | 197 | 178 | 180 | 181 | 180 | 138 | 139 | 154 | 179 | 180 | 213 | 207 | 186 | 201 | 190 | 182 | 183 | 181 |  | 186 | 212 | 211 | 210 | 213 | 207 | 212 | 4543000
34 | Ashuganj 450 MW CCPP(South) | [25 empty] | 0 | 0
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 320 | 275 | 360 | 340 | 350 | 305 | 345 | 340 | 310 | 310 | 310 |  | 310 | 310 | 310 | 310 | 310 | 350 | 305 | 7793900
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 404 | 403 | 362 | 357 | 352 | 289 | 278 | 299 | 391 | 399 | 373 | 392 | 405 | 406 | 404 | 406 | 410 | 409 |  | 379 | 398 | 401 | 405 | 406 | 406 | 394 | 9248760
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 400 | 320 | 320 | 280 | 280 | 380 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 400 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 9670000
41 | Haripur 360MW CCPP(HPL) | 310 | 305 | 305 | 305 | 275 | 230 | 232 | 315 | 346 | 301 | 302 | 346 | 322 | 322 | 323 | 322 | 322 | 303 |  | 342 | 348 | 348 | 340 | 338 | 338 | 338 | 7556000
42 | RPCL 210MW CCPP | 75 | 75 | 74 | 74 | 74 | 36 | 36 | 48 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 43 | 43 |  | 43 | 49 | 59 | 65 | 80 | 80 | 80 | 1290240
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 4 | 14 | 33 | 36 | 49 | 53 | 49 | 38 | 37 | 25 | 7 | 1 |  | 0 | [6 empty] | 319410
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 40 | 40 | 39 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1006000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 20 | 20 | [18 empty] | 230400
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 63 | 40 | 40 | 0 | 0 | [18 empty] | 0 | 298368
48 | Shahjibazar 86MW PP (Shahjibazar) | 78 | 75 | 40 | 10 | 10 |  |  |  | 40 | 75 | 76 | 76 | 77 | 77 | 80 | 79 | 76 | 80 |  | 80 | 80 | 80 | 80 | 77 | 77 | 77 | 1426560
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 210 | 210 | 210 | 211 | 211 | 206 | 207 | 212 |  |  |  | 50 | 50 | 50 | 50 | 90 | 135 | 135 |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 2372160
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | [6 empty] | 18 | 18 | 18 | 0 | [6 empty] | 18 | 18 | 18 | 17 | 17 | 228000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | [5 empty] | 9 | 9 | 7 | 7 | 7 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 190800
54 | Hobiganj 11MW PP Cofidence-E |  |  | 8 | 11 | 11 | 11 | 11 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 181305
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 11 | 11 |  |  |  | 14 | 48 | 48 | 48 | 50 | 50 | 50 | 50 | 51 | 51 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 940200
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | [5 empty] | 8 | 8 | 7 | 7 | 8 | 8 | 8 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 248448
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 275 | 280 | 280 | 270 | 160 | 150 | 155 | 270 | 295 | 300 | 320 | 305 | 285 | 310 | 280 | 295 | 280 |  | 290 | 250 | 250 | 270 | 290 | 290 | 290 | 6626000
| Bibiyana South 400 MW | 350 | 340 | 340 | 340 | 300 | 260 | 260 | 300 | 400 | 400 | 400 | 330 | 310 | 310 | 310 | 310 | 310 | 310 |  | 330 | 315 | 330 | 330 | 330 | 330 | 330 | 7971200
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | [6 empty] | 5 | 35 | 35 | 35 | 35 | 0 | 17 | 35 | 35 |  | 35 | 35 | 55 | 55 | 55 | 35 | 35 | 636434
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 11 | [5 empty] | 2 | 12 | 12 | 11 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 225360
60 | Barabkunda 22 MW PP (Regent) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 0 | 7 | 7 | 7 | 7 | 7 | 0 | [10 empty] | 0 | 78192
61 | Narshingdi 22 MW PP (Doreen) | 15 | 15 | 15 | 15 | 15 | [6 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 15 | 15 | 15 | 15 | 15 | 225684
62 | Tangail 22 MW PP (Doreen) | 18 | 18 | 19 | 19 | [5 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 14 | 14 |  | 15 | 15 | 15 | 17 | 18 | 18 | 18 | 297000
63 | Impoprt (Tripura) | 124 | 126 | 124 | 112 | 110 | 102 | 30 | 72 | 82 | 92 | 114 | 118 | 128 | 128 | 132 | 142 | 134 | 114 |  | 138 | 138 | 136 | 138 | 138 | 138 | 126 | 2749440
64 | Malancha, Ctg. EPZ (United) | 34 | 39 | 39 | 40 | 41 | 41 | 34 | 15 | 5 | 6 | 9 | 3 | 2 | 2 | 2 | 2 | 2 | 8 |  | 12 | 7 | 14 | 14 | 22 | 25 | 23 | 466080
65 | Feni 22MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 0 |  |  |  | 8 | 17 | 18 | 18 | 18 | 18 | 17 | 17 | 17 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 336168
66 | Feni 11 MW PP (Doreen) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | [6 empty] | 6 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 92340
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | [5 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 483600
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 18 | 18 | 16 |  |  |  | 6 | 6 | 6 | 12 | 12 | 0 | 12 | 12 | 12 |  | 12 | 12 | 15 | 15 | 17 | 20 | 20 | 297460
69 | Summit Ashulia | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 23 | 552000
70 | Summit Madhabdi | 27 | 25 | 25 | 25 | 27 | 0 | 0 | 7 | 8 | 8 | 6 | 6 | 18 | 20 | 20 | 27 | 27 | 27 |  | 20 | 27 | 27 | 27 | 27 | 27 | 27 | 439560
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 0 | 0 |  | 0 | 17 | 17 | 25 | 0 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 636840
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 |  |  | 17 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 33 | 31 |  | 31 | 31 | 31 | 31 | 31 | 31 | 32 | 656100
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 114 | 114 | 20 | 17 |  |  | 17 | 17 | 17 | 17 | 41 | 98 | 98 | 17 | 17 | 17 | 52 | 77 |  | 74 | 67 | 17 | 17 | 17 | 88 | 114 | 1092120
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 24 | 27 | 57 |  | 95 | 95 | 95 | 95 | 98 | 36 | 8 | 623280
| Manikgonj 162MW PP(MPGL) | 17 | 17 | [8 empty] | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 |  | 108 | 108 | 108 | 108 | 108 | 89 | 17 | 1118880
77 | Siddhirganj 100 PP(Dutch Bangla) | 9 | 9 | [7 empty] | 3 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 17 | 17 | 17 | 17 | 18 | 18 | 18 | 185386
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 |  |  |  |  | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 28 |  | 48 | 49 | 49 | 49 | 49 | 49 | 8 | 396480
79 | Kodda 150 MW PP | 50 | 50 | 16 | 16 | [5 empty] | 16 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 133 |  | 133 | 82 | 32 | 32 | 32 | 64 | 100 | 1315200
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 43 | 52 | 52 | [15 empty] | 5 | 8 | 52 | 52 | 52 | 52 | 52 | 439824
| Gazipur 100 MW PP | 88 | 88 | 17 | 17 | [5 empty] | 3 | 51 | 88 | 88 | 88 | 88 | 88 | 88 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 1437974
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 1 | 0 | 0 | 1 | 2 | 0 | 1 | 2 | 2 | 1 | 0 | [8 empty] | 12961
| Jodiac Power | 17 | [8 empty] | 6 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 287888
| Karnaphuli Power Ltd. | 70 | 54 | 54 | 54 | 54 | 0 | 16 | 17 | 44 | 51 | 52 | 54 | 54 | 54 | 54 | 60 | 76 | 94 |  | 92 | 92 | 92 | 92 | 92 | 93 | 76 | 1496248
82 | Madanganj 102 PP(Summit) | 17 | 17 | 12 | [7 empty] | 12 | 17 | 17 | 17 | 17 | 17 | 17 | 48 |  | 85 | 85 | 74 | 32 | 17 | 19 | 51 | 440397
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [16 empty] | 8 | 0 | [8 empty] | 16281
86 | Meghnaghat CCPP ( Summit) | 268 | 279 | 270 | 282 | 256 | 234 | 237 | 312 | 283 | 310 | 321 | 317 | 301 | 310 | 307 | 309 | 304 | 311 |  | 319 | 270 | 296 | 297 | 309 | 310 | 310 | 6981295
87 | Meghnaghat 100 MW(IEL) | 8 | 9 | 8 | 9 | 8 |  | 0 |  |  | 2 | 9 | 8 | 8 | 9 | 8 | 9 | 8 | 9 |  | 8 | 9 | 9 | 9 | 8 | 9 | 8 | 162240
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 28 | 49 |  | 53 | 53 | 53 | 53 | 36 | 17 | 17 | 586560
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 22 | 22 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 76 | 66 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 22 | 22 | 1220520
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 10 | 10 |  |  |  | 10 | 20 | 47 | 48 | 50 | 48 | 43 | 45 | 49 | 50 |  | 48 | 48 | 48 | 48 | 50 | 50 | 50 | 900144
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 5 | 5 | 5 |  |  |  | 10 | 20 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 34 | 34 | 34 | 34 | 43 | 755952
94 | Gagnagar 102 MW PP (Digital Power) | 16 | 16 | 16 | 16 | 8 |  |  |  |  | 3 | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 16 |  | 41 | 41 | 41 | 41 | 41 | 16 | 16 | 430992
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 15 | 30 |  | 44 | 44 | 44 | 44 | 44 | 44 | 6 | 371040
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 |  |  | 6 | 5 | 5 | 5 | 21 |  | 30 | 30 | 30 | 30 | 30 | 20 | 13 | 201600
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [19 empty] | 12 | 30 | 30 | 30 | 15 |  | 0 | 95242
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 17 | 35 | 35 | 35 | 17 | 35 | 35 | 35 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 0 | 623333
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 14200
103 | Kamalaghat 54 MW PP(Banco Energy) | [15 empty] | 17 | 17 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 255240
104 | Keranigonj 300 MW PP (APR) | [11 empty] | 290 | 302 | 225 | 308 | 304 | 248 | 0 | [7 empty] | 108 | 1708430
105 | Bramhangoan 100 MW PP (Aggreko) | [11 empty] | 40 | 44 | 74 | 74 | 74 | 74 | 25 |  | 25 | 0 |  |  |  |  | 40 | 449532
106 | Mymensingh 200 MW PP (United) | 27 | 28 | 28 | 28 |  |  |  |  | 10 | 26 | 46 | 48 | 65 | 65 | 65 | 65 | 68 | 68 |  | 88 | 88 | 87 | 88 | 88 | 68 | 67 | 1120800
112 | Aurahati 100MW PP (Aggreko) | [11 empty] | 40 | 40 | 40 | 40 | 40 | 40 | 25 |  | 25 | 0 |  |  |  |  | 40 | 317109
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | 17 | 17 | [5 empty] | 2 | 59 | 116 | 121 | 40 | 17 | 16 | 16 | 35 |  | 112 | 114 | 115 | 80 | 50 | 50 | 50 | 982512
115 | Juldah 100 MW PP Unit-3 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 654720
116 | Chandpur 200MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 424800
117 | Ashuganj 150MW PP (Midland) | 18 | 20 | 18 | [6 empty] | 7 | 15 | 21 | 17 | 12 | 13 | 13 | 12 | 50 |  | 130 | 150 | 150 | 150 | 150 | 60 | 11 | 916654
118 | Bibiyana-III 400 MW CCPP | 344 | 344 | 343 | 342 | 339 | 240 | 240 | 323 | 300 | 367 | 399 | 404 | 367 | 414 | 388 | 366 | 367 | 367 |  | 367 | 367 | 368 | 367 | 367 | 400 | 366 | 8534000
| Jamalpur 115 MW PP (United) | 49 | 49 | 49 | 49 |  |  |  |  | 24 | 47 | 58 | 59 | 50 | 49 | 49 | 49 | 49 | 49 |  | 88 | 88 | 88 | 89 | 89 | 18 | 18 | 1075200
| Anwara 300 MW PP (United) | 88 | 88 | 88 | 88 | 88 | 30 | 30 | 50 | 84 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 121 |  | 200 | 290 | 296 | 296 | 122 | 87 | 87 | 2546727
| Juldah unit-2 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 24 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 644160
| Anlima Energy Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 417764
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 |  |  | 13 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 19 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 676800
| Spectra Solar Plant Ltd. | [8 empty] | 12 | 32 | 24 | 19 | 18 | 17 | 9 | 11 | 5 | 0 | [8 empty] | 167130
| Chandpur 115(Doreen) | 20 | 18 | 17 | 18 | 18 | 18 | 18 | 17 | 18 | 18 | 42 | 54 | 54 | 54 | 54 | 54 | 53 | 54 |  | 68 | 102 | 97 | 115 | 115 | 74 | 36 | 1118400
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 |  |  |  |  | 7 | 17 | 17 | 17 | 17 | 17 | 17 | 30 | 34 |  | 34 | 34 | 34 | 34 | 34 | 35 | 17 | 488880
| Mirsharai 150 MW (Oil) | 17 | 17 | [7 empty] | 12 | 35 | 35 | 54 | 54 | 54 | 54 | 54 | 36 |  | 36 | 62 | 90 | 163 | 163 | 57 | 17 | 950109
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 5856 | 5697 | 5208 | 4886 | 4308 | 2922 | 2910 | 3470 | 4046 | 4658 | 5440 | 6101 | 6092 | 6031 | 5991 | 6001 | 6125 | 6116 |  | 7013 | 7119 | 7193 | 7241 | 7054 | 6641 | 6300 | 133277721
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 32 | 32 | [10 empty] | 16 | 16 | 33 | 49 | 63 | 66 |  | 66 | 66 | 18 | 16 | 16 | 45 | 49 | 497280
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 4 | 21 |  | 25 | 25 | 24 | 19 | 19 | 19 | 19 | 140160
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | [11 empty] | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 226080
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 1 | 0 | 1 | 0 | 8 | 51 | 35 | 68 | 23 | 19 | 55 | 27 | 1 |  | 0 | [6 empty] | 327600
131 | Rampal 1320 MW (BIFPCL) | 325 | 321 | 328 | 327 | 329 | 308 | 305 | 330 | 325 | 325 | 325 | 328 | 328 | 321 | 322 | 322 | 323 | 323 |  | 320 | 326 | 326 | 320 | 326 | 322 | 322 | 7760000
132 | United Payra Power Ltd. | [17 empty] | 2 |  | 17 | 17 | 0 |  |  |  | 0 | 27600
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [20 empty] | 16 | 16 | 16 | 16 |  | 0 | 59040
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 203 | 203 | 159 | 152 | 154 | 155 | 153 | 154 | 154 | 150 | 154 | 152 | 154 | 150 | 150 | 155 | 152 | 153 |  | 185 | 182 | 182 | 182 | 200 | 202 | 202 | 4011700
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 184 | 183 | 184 | 184 | 160 | 120 | 122 | 123 | 80 | 80 | 130 | 137 | 135 | 127 | 132 | 132 | 127 | 105 |  | 135 | 106 | 122 | 132 | 133 | 132 | 135 | 3322437
140 | Bhola 33 MW PP (Venture) | 23 | 22 | 21 | 20 | 17 | 16 | 3 | 3 | 10 | 9 | 10 | 19 | 19 | 18 | 18 | 20 | 19 | 17 |  | 23 | 23 | 22 | 24 | 24 | 24 | 22 | 425600
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [12 empty] | 8 | 8 | 8 | 8 | 8 | 8 |  | 40 | 8 | 8 | 8 | 8 | 8 | 8 | 125625
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [17 empty] | 1 |  | 33 | 50 | 15 | 15 | 15 | 15 | 15 | 119664
146 | Bheramara HVDC | 860 | 860 | 860 | 895 | 821 | 151 | 601 | 907 | 908 | 906 | 907 | 907 | 948 | 907 | 907 | 895 | 894 | 902 |  | 902 | 905 | 810 | 810 | 810 | 795 | 795 | 19989818
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 1000 | 980 | 900 | 550 | 500 | 500 | 500 | 500 | 500 | 560 | 640 | 760 | 920 | 1020 | 1060 | 1030 | 1000 | 960 |  | 950 | 1060 | 1080 | 1130 | 1150 | 1190 | 1212 | 22753600
149
150 | Barapukuria TPP Unit-1 | 75 | 75 | 76 | 76 | 76 | 76 | 77 | 76 | 76 | 76 | 76 | 76 | 76 | 75 | 73 | 75 | 75 | 75 |  | 75 | 74 | 74 | 73 | 74 | 74 | 74 | 1736290
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 260 | 260 | 260 | 260 | 185 | 160 | 160 | 160 | 220 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 5964000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [16 empty] | 28 | 28 |  | 27 | 28 | 28 | 28 | 28 | 28 | 28 | 204880
| Sirajgonj 6.55 MW Solar | [7 empty] | 0 | 3 | 4 | 2 | 5 | 5 | 4 | 2 | 1 | 0 | [9 empty] | 25980
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 162 | 158 | 160 | 130 | 130 | 130 | 130 | 130 | 165 | 177 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 |  | 168 | 177 | 176 | 174 | 175 | 175 | 176 | 4193082
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 156 | 156 | 158 | 130 | 130 | 111 | [19 empty] | 0 | 945545
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 331 | 286 | 292 | 243 | 239 | 304 | 360 | 418 | 436 | 408 | 425 | 416 | 420 | 414 | 414 | 415 | 416 | 391 |  | 419 | 418 | 418 | 419 | 419 | 417 | 426 | 9128909
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [13 empty] | 5 | 6 | 20 | 28 | 28 |  | 28 | 28 | 0 |  |  |  |  | 100281
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 20 | 0 | 0 | 0 | 0 | 0 | 17 | 21 | 21 | 21 | 21 | 21 | 19 | 20 | 20 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 383760
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | [5 empty] | 5 |  |  | 5 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 93528
165 | Amnura 50 MW PP(Sinha) | [10 empty] | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 14 | 14 | 14 | 14 | 21 | 21 | 301820
166 | Katakhali 50 MW PP (Northern) | 34 | 42 | [7 empty] | 8 | 16 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 8 | 8 | 8 | 8 | 25 | 34 | 421568
167 | Katakhali 50 MW Peaking PP | [10 empty] | 24 | 32 |  |  | 16 | 24 | 24 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 295035
168 | Santahar 50 MW Peaking PP | 30 | 30 | [9 empty] | 22 | 34 | 35 | 35 | 35 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 418779
169 | Natore 52 MW PP (Rajlanka) | 52 | 43 | [8 empty] | 26 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 24 | 24 | 24 | 43 | 43 | 616738
170 | Chapainawabganj 100 MW Peaking PP | 68 | 67 |  |  |  |  | 0 |  |  |  | 31 | 54 | 54 | 54 | 55 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 857744
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | [8 empty] | 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 50 | 50 | 50 | 50 | 35 | 35 | 652032
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | [7 empty] | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 861024
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 33 | 32 | [7 empty] | 10 | 33 | 33 | 33 | 33 | 33 | 33 | 82 | 81 |  | 81 | 81 | 81 | 81 | 74 | 33 | 33 | 829094
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 2 | 3 | 2 | 2 | 6 | 3 | 3 | 3 | 3 | 1 |  | 0 | [6 empty] | 30979
178 | Energypac Power Venture Thakurgaon Ltd. | [9 empty] | 15 | 95 | 35 | 35 | 36 | 36 | 36 | 36 | 36 |  | 109 | 115 | 114 | 114 | 114 | 55 | 55 | 1064256
| Intraco Solar 30 MW | [7 empty] | 4 | 5 | 15 | 18 | 24 | 8 | 9 | 14 | 5 | 4 | 2 |  | 0 | [6 empty] | 119037
| Adani Power Jharkhanda Ltd | 405 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 88 | 139 | 212 |  | 400 | 400 | 407 | 407 | 408 | 411 | 412 | 3098182
178 | Teesta Solar Limited | [5 empty] | 0 | 18 | 17 | 68 | 179 | 48 | 58 | 165 | 98 | 76 | 82 | 24 | 5 |  | 0 | [6 empty] | 890980