## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2019-04-27 | Saturday
|  | Date (day): | 2019-04-27 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13093 | MW |  |  | (b) At Evening Peak Hour : |  | 13839 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-04-26 | 2019-04-27 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 36 | 36 | 36 | 36 |  | 49 | Unit-1 under maint.
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 78 | 79 | 79 | 79 |  |  | On test.
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  |  | On test.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 110 | 110 | 110
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 117 | 325 | 412 | 412 | 0
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 70 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 340 | 350 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 430 | 430 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 30 | 50 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 305 | 235 | 335 | 335
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 15 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 30 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 70 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 14 | 0 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 100 | 100 | 110 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract expired
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 15 | 100 | 100
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
0 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
21 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 102 | 102 | 102
22 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 6 | 30 | 49 | 49
23 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 54 | 54
24 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 149 | 149 | 149
25 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 18 | 56 | 55 | 55
26 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
27 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 57 | 60 | 60 | 60 |  | 48 | Engine problem
28 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 37 | 30 | 57 | 57 |  | 23 | Engine problem
29 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
30 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 16 | 33 | 33 | 33
31 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 24 | 50 | 51 | 51
32 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
33 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 22 | 300 | 300
34 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 77 | 300 | 300
35 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
36 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 51 | 100 | 100
37 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 0 | 100 | 149 | 149
| Gazipur 100 MW |  | HFO | RPCL | 100 MW | 0 | 0 | 90 | 90 | 100 | 100
| Dhaka area Total |  |  |  |  | 6034 | 5798 | 2101 | 3099 | 4516 | 4516 | 891 | 120
38 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
39 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 8 | 25 | 25 | 25
40 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18.6 | 0 | 20 | 0
41 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 39 | 40 | 46 | 46 |  | 4 | Engine problem
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 0 | 66 | 110 | 110 |  | 120 | Low water lavel
43 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
44 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 220 | 204 | 225 | 225
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 140 | 145 | 150 | 150
46 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 0 | 0 | 0 | 0 |  | 51 | Under S/D
47 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 66 | 70 | 70
48 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 83 | 85 | 85
49 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 60 | 100 | 100
50 | Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
51 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 0 | 0 | 20
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 9 | 33 | 13 | 33
52 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 74 | 104 | 10 | 101
| Chattogram area Total |  |  |  |  | 1761 | 1681 | 734.6 | 1026 | 1054 | 1165 | 260 | 215
53 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
54 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 208 | 181 | 221 | 221
55 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 330 | 360 | 360 | 360
56 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 349 | 360 | 360
57 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 20 | 20 | 23 | 23 | 22 |  | Gas Shortage
58 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 25 | 25 | 53 | 53
59 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage
60 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 117 | 125 | 125 | 125 | 70 |  | Gas shortage
61 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 20 | 35 | 35 |  | 16 | Engine problem
62 | Midland 150MW |  | HFO | IPP | 23*7.015 | 150 | 150 | 50 | 150 | 150 | 150
63 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
64 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 0 | 50
65 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 0 | 100 | 100
66 | Chandpur Desh 200MW |  | HFO | IPP | 0 | 200 | 200 | 50 | 17 | 200 | 200
67 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
68 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 130 | 172 | 137 | 174
69 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
70 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 43 | 43
71 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 21 | 21
72 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 200 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1456 | 1595 | 2099 | 2186 | 538 | 16
73 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 97 | 101 | 202 | 202
74 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
75 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 60 | 60 | 93 | 93 |  | 2
76 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 0.6 | 0 | 2 | 0
77 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 90 | 194 | 200 | 200
78 | United Jamalpur PPL |  | HFO | IPP | 115 MW | 115 | 115 | 110 | 110 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 377.6 | 485 | 632 | 630 | 0 | 2
79 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 55 | 54 | 60 | 60
80 | Fenchugonj CCPP-2 |  | Gas | PDB | !F71 | 104 | 90 | 59 | 58 | 60 | 60
81 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
82 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 117 | 214 | 217 | 217 |  |  | FGMO, GT-2 under maint.
83 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 53 | 53
84 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 50 | 50
85 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
86 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 63 | 66 | 66 |  |  | FGMO
87 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 81 | 86 | 86
88 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 44 | 44 | 44 | 44 |  | 6 | Engine problem
89 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 120
90 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20
91 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 38 | 41 | 41 | 41
92 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 25 | 25
93 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 265 | 341 | 341 |  |  | FGMO
| Bibiyana-3 285 MW |  | Gas | PDB | 285 MW | 0 | 0 | 287 | 292 | 50 | 285 |  |  | On test
94 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1342 | 1441 | 1297 | 1652 | 0 | 6
95 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 40 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 792 | 845 | 861 | 960
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
96 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 115 | 115 | 115
97 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 20 | 40 | 40
98 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 |  |  | Reserve
99 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 2 | 67 | 50 | 80
100 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint.
101 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 24 | 40 | 40 | 40
0 | Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
102 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 30 | 100 | 100
103 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 90 | 105 | 105
| Madhumati Power Plant |  | HFO | IPP | 100 MW | 0 | 0 | 34 | 90 | 108 | 108 |  |  | On Test
| Khulna Area Total |  |  |  |  | 2223 | 2209 | 905 | 1337 | 1419 | 1588 | 0 | 410
104 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 90 | 110 | 110
105 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 18 | 0 | 26
106 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 24 | 34 | 33 | 33
107 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 178 | 178 | 178 | 178
108 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 91 | 95 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 293 | 415 | 416 | 442 | 0 | 0
109 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
110 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 50 | 50 | 50 | 50
111 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 47 | 39 | 40 | 40
112 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 6 | 35 | 35 | 35 |  | 15 | Engine problem
113 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 43 | 40 | 50 | 50
114 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 43 | 34 | 48 | 48
115 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 158 | 176 | 200 | 200 |  |  | FGMO
116 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 134 | 160 | 200 | 200 |  |  | FGMO
117 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 172 | 126 | 200 | 200 |  |  | FGMO
118 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282 | 282 | 282 | 280 | 285 | 282 | 282 |  |  | ON test
119 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 19 | 34 | 35 | 35
120 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 0 | 22 | 22 | 22
121 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 17 | 17 | 17 | 17
122 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
123 | Rajlanka 52 MW |  | HFO | IPP | 52 | 52 | 52 | 42 | 43 | 43 | 43 |  | 9 | Engine problem
124 | Chapainawabganj-100 MW |  | HFO | PDB | 104 | 104 | 104 | 85 | 95 | 100 | 100
125 | Paramount Baghabari |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Reserve
126 | Confidence CPBL-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 108 | 108 | 108 |  |  | On test
| Rajshahi Area Total |  |  |  |  | 1948 | 1938 | 1107 | 1275 | 1441 | 1441 | 171 | 24
127 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under overhauling
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maintenance
128 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 184 | 184 | 184 | 184 | 90
129 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 14 | 17 | 17 | 17
130 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 15 | 17 | 18 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 213 | 218 | 219 | 219 | 90 | 170
| Total |  |  |  |  | 18192 | 17649 | 8529.2 | 10891 | 13093 | 13839 | 1950 | 963
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8165.8221 | 10427 | 12535.186 | 13249.4035
A. |  | 2019-04-26 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 11297 | MW at | 1:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 7760 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10891 | MW
3 | Day peak Generation : |  |  | 8529.2 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10427 | MW
4 | Evening peak Generation : |  |  | 10891 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 230.6573 | MKWHr | By Solar | 0.08974 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 136.9884 | MKWHr |  | By Oil: | 65.5427 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 4.5017 | MKWHr |  | By Hydro: | 1.126 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1950 | MW | Dhaka | 3699 | 3699 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 963 | MW | Chittagong | 1151 | 1151 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2913 | MW | Khulna | 1076 | 1076 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1225.63 | MMCFD |  |  | Rajshahi | 1179 | 1179 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 92780533.958 | ii) Oil : | Taka | 493026914.92 | Comilla | 1056 | 1056 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 17376562 | Total | Taka | 603184010.878 | Mymensingh | 841 | 841 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 3.064 | MKWHr. | Sylhet | 463 | 463 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -260 | MW (E to W) at | 19:30 | hrs | Barisal | 283 | 283 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -630 | MW at | 1:00 | hrs | Rangpur | 679 | 679 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 36.2° C |  |  | Total | 10427 | 10427 |  | 0
B. |  | 2019-04-27 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 40.5° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13839 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10200 | MW
4 | Reserve(Generation end) |  |  |  | 1939 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 242.9691 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8240.9 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 18.7156 | MKWHr. | ii) HVDC Flow at Peak Time |  | 845 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.6931 | MKWHr. | iii) Maximum HVDC Flow : |  | 846 | MW at | 24:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 78.25 |  | (b) Today: | 77.92 |  | (c) Rule Curve: |  | 82.8
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-04-26
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285 MW | United Jamalpur PPL | Gazipur 100 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | Paramount Baghabari | Confidence CPBL-2 | Madhumati Power Plant | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 36 | 134 | 0 | 110 | 300 | 0 | 0 | 0 | 354 | 110 | 0 | 400 | 275 | 92 | 97 | 55 | 0 | 0 | 0 | 0 | 100 | 102 | 149 | 76 | 62 | 0 | 6 | 54 | 56 | 55 | 14 | 25 | 25 | 25 | 33 | 42 | 0 | 70 | 30 | 80 | 0 | 25 | 204 | 0 | 145 | 0 | 0 | 0 | 71 | 68 | 68 | 104 | 46 | 16 | 34 | 0 | 0 | 0 | 300 | 300 | 180 | 86 | 80 | 23 | 52 | 5 | 45 | 0 | 50 | 52 | 22 | 11 | 25 | 21 | 170 | 84 | 92 | 20 | 0 | 58 | 60 | 53 | 50 | 163 | 218 | 60 | 80 | 44 | 0 | 19 | 42 | 10 | 270 | 24 | 11 | 101 | 298 | 78 | 50 | 170 | 51 | 149 | 0 | 100 | 200 | 150 | 300 | 101 | 90 |  | 696 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 30 | 39 | 40 | 178 | 35 | 110 | 0 | 0 | 0 | 50 | 32 | 94 | 6 | 50 | 45 | 43 | 34 | 22 | 17 | 11 | 0 | 0 | 184 | 16 | 17 | 155 | 0 | 138 | 0 | 97 | 50 | 139 | 0 | 240 | 105 | 0 | 35 | 108 |  | 8366 | 2931 | 11297 | 3584 | 696 | 2099 | 3769 | 184 | 100 | 695 | 170 | 0 | 0 | 78.4
2:00 | 36 | 134 | 0 | 110 | 300 | 0 | 0 | 0 | 356 | 110 | 0 | 450 | 270 | 92 | 97 | 55 | 0 | 0 | 0 | 0 | 100 | 102 | 149 | 76 | 63 | 0 | 6 | 54 | 56 | 55 | 14 | 25 | 23 | 25 | 33 | 44 | 0 | 70 | 30 | 100 | 0 | 25 | 204 | 0 | 145 | 0 | 0 | 0 | 71 | 68 | 68 | 105 | 46 | 16 | 37 | 0 | 0 | 0 | 300 | 300 | 183 | 86 | 80 | 23 | 53 | 5 | 45 | 0 | 50 | 52 | 22 | 11 | 25 | 21 | 164 | 84 | 92 | 20 | 0 | 58 | 60 | 53 | 50 | 163 | 215 | 61 | 80 | 44 | 0 | 19 | 42 | 10 | 270 | 24 | 11 | 11 | 300 | 0 | 0 | 170 | 0 | 149 | 0 | 100 | 200 | 150 | 300 | 101 | 90 |  | 696 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 30 | 39 | 40 | 178 | 34 | 110 | 0 | 0 | 0 | 50 | 29 | 94 | 6 | 50 | 45 | 43 | 34 | 22 | 16 | 11 | 0 | 0 | 184 | 0 | 17 | 152 | 0 | 134 | 0 | 97 | 10 | 134 | 0 | 240 | 105 | 0 | 35 | 108 |  | 8167 | 2858 | 11025 | 3591 | 696 | 2153 | 3461 | 184 | 100 | 676 | 164 | 0 | 0 | 78.37
3:00 | 36 | 134 | 0 | 110 | 300 | 0 | 0 | 0 | 354 | 110 | 0 | 450 | 285 | 92 | 97 | 55 | 0 | 0 | 0 | 0 | 50 | 101 | 149 | 40 | 63 | 0 | 6 | 54 | 56 | 55 | 14 | 25 | 23 | 25 | 33 | 51 | 0 | 71 | 30 | 100 | 0 | 25 | 206 | 0 | 145 | 0 | 0 | 0 | 40 | 68 | 68 | 105 | 46 | 16 | 37 | 0 | 0 | 0 | 300 | 300 | 195 | 86 | 80 | 23 | 53 | 5 | 45 | 0 | 0 | 52 | 22 | 11 | 25 | 21 | 162 | 90 | 92 | 20 | 0 | 58 | 60 | 53 | 47 | 130 | 217 | 55 | 80 | 44 | 0 | 19 | 42 | 10 | 265 | 24 | 11 | 0 | 140 | 0 | 0 | 170 | 0 | 136 | 0 | 100 | 200 | 150 | 297 | 101 | 90 |  | 696 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 8 | 178 | 33 | 80 | 0 | 0 | 0 | 50 | 26 | 94 | 6 | 50 | 45 | 43 | 34 | 22 | 17 | 11 | 0 | 0 | 184 | 0 | 17 | 152 | 0 | 134 | 0 | 96 | 0 | 134 | 0 | 240 | 105 | 0 | 35 | 109 |  | 7806 | 2682 | 10488 | 3604 | 696 | 2109 | 3109 | 184 | 101 | 523 | 162 | 0 | 0 | 78.34
4:00 | 36 | 134 | 0 | 110 | 300 | 0 | 0 | 0 | 354 | 110 | 0 | 450 | 285 | 92 | 60 | 15 | 0 | 0 | 0 | 0 | 0 | 64 | 149 | 10 | 63 | 0 | 6 | 54 | 56 | 55 | 14 | 25 | 23 | 25 | 33 | 51 | 0 | 71 | 30 | 100 | 0 | 25 | 214 | 0 | 145 | 0 | 0 | 0 | 0 | 34 | 68 | 105 | 46 | 16 | 38 | 0 | 0 | 0 | 300 | 300 | 202 | 86 | 80 | 23 | 25 | 5 | 45 | 0 | 0 | 52 | 22 | 11 | 25 | 21 | 160 | 102 | 92 | 20 | 0 | 58 | 60 | 53 | 47 | 130 | 217 | 64 | 80 | 44 | 0 | 19 | 42 | 10 | 290 | 24 | 11 | 0 | 90 | 0 | 0 | 170 | 0 | 116 | 0 | 100 | 200 | 150 | 298 | 102 | 90 |  | 697 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 8 | 178 | 32 | 32 | 0 | 0 | 0 | 50 | 26 | 94 | 6 | 50 | 45 | 43 | 34 | 22 | 16 | 11 | 0 | 0 | 184 | 0 | 17 | 151 | 0 | 134 | 0 | 96 | 0 | 134 | 0 | 240 | 105 | 0 | 35 | 109 |  | 7502 | 2632 | 10134 | 3640 | 697 | 2105 | 2798 | 184 | 101 | 449 | 160 | 0 | 0 | 78.31
5:00 | 36 | 94 | 0 | 110 | 300 | 0 | 0 | 0 | 357 | 110 | 0 | 450 | 280 | 92 | 60 | 15 | 0 | 0 | 0 | 0 | 0 | 64 | 149 | 10 | 63 | 0 | 6 | 54 | 56 | 55 | 14 | 25 | 23 | 25 | 33 | 51 | 0 | 75 | 30 | 100 | 0 | 25 | 203 | 0 | 145 | 0 | 0 | 0 | 0 | 34 | 68 | 102 | 41 | 16 | 40 | 0 | 0 | 0 | 300 | 300 | 189 | 86 | 80 | 23 | 25 | 5 | 35 | 0 | 0 | 52 | 22 | 11 | 25 | 21 | 160 | 102 | 93 | 20 | 0 | 58 | 60 | 53 | 47 | 130 | 212 | 64 | 80 | 44 | 0 | 19 | 42 | 10 | 290 | 24 | 11 | 0 | 90 | 0 | 0 | 170 | 0 | 103 | 0 | 100 | 200 | 150 | 299 | 102 | 90 |  | 697 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 8 | 178 | 29 | 32 | 0 | 0 | 0 | 50 | 25 | 94 | 6 | 50 | 45 | 43 | 34 | 22 | 17 | 11 | 0 | 0 | 184 | 0 | 17 | 152 | 0 | 134 | 0 | 97 | 0 | 134 | 0 | 240 | 105 | 0 | 35 | 108 |  | 7408 | 2630 | 10038 | 3573 | 697 | 2099 | 2772 | 184 | 105 | 448 | 160 | 0 | 0 | 78.28
6:00 | 36 | 134 | 0 | 110 | 300 | 0 | 0 | 0 | 284 | 55 | 0 | 370 | 260 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 63 | 0 | 6 | 54 | 36 | 17 | 14 | 25 | 23 | 25 | 33 | 51 | 0 | 75 | 30 | 100 | 0 | 25 | 202 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 10 | 96 | 40 | 16 | 39 | 0 | 0 | 0 | 270 | 270 | 182 | 86 | 80 | 23 | 25 | 5 | 35 | 0 | 0 | 25 | 22 | 11 | 25 | 21 | 134 | 103 | 93 | 20 | 0 | 58 | 60 | 53 | 47 | 130 | 212 | 54 | 80 | 44 | 0 | 19 | 42 | 10 | 250 | 24 | 11 | 0 | 0 | 0 | 0 | 120 | 0 | 60 | 0 | 100 | 200 | 150 | 300 | 102 | 90 |  | 697 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 27 | 0 | 0 | 0 | 0 | 50 | 25 | 94 | 6 | 43 | 45 | 43 | 34 | 22 | 16 | 11 | 0 | 0 | 184 | 0 | 17 | 151 | 0 | 134 | 0 | 97 | 0 | 134 | 0 | 240 | 53 | 0 | 35 | 75 |  | 6512 | 2418 | 8930 | 3536 | 697 | 1902 | 2007 | 184 | 105 | 365 | 134 | 0 | 0 | 78.25
7:00 | 36 | 79 | 0 | 110 | 300 | 0 | 0 | 0 | 284 | 55 | 0 | 370 | 275 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 63 | 0 | 6 | 35 | 17 | 17 | 14 | 25 | 22 | 25 | 33 | 51 | 0 | 72 | 30 | 100 | 0 | 8 | 204 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 10 | 12 | 39 | 16 | 30 | 0 | 0 | 0 | 270 | 270 | 184 | 86 | 80 | 23 | 25 | 5 | 35 | 0 | 0 | 25 | 22 | 11 | 25 | 21 | 110 | 102 | 61 | 20 | 0 | 58 | 60 | 53 | 47 | 130 | 194 | 64 | 80 | 44 | 0 | 19 | 41 | 10 | 270 | 16 | 11 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 100 | 144 | 100 | 299 | 102 | 90 |  | 696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 23 | 0 | 0 | 0 | 0 | 50 | 26 | 94 | 6 | 43 | 45 | 43 | 34 | 0 | 17 | 11 | 0 | 0 | 184 | 17 | 18 | 151 | 0 | 134 | 0 | 91 | 0 | 133 | 0 | 240 | 17 | 0 | 0 | 72 |  | 5948 | 2323 | 8271 | 3465 | 696 | 1881 | 1533 | 184 | 102 | 300 | 110 | 0 | 0 | 78.22
8:00 | 36 | 79 | 0 | 110 | 300 | 0 | 0 | 0 | 284 | 27 | 0 | 370 | 285 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 61 | 0 | 6 | 35 | 18 | 17 | 14 | 25 | 22 | 25 | 17 | 24 | 0 | 0 | 0 | 100 | 0 | 8 | 206 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 10 | 12 | 26 | 16 | 23 | 0 | 0 | 0 | 270 | 270 | 201 | 86 | 100 | 23 | 25 | 5 | 27 | 0 | 0 | 8 | 22 | 11 | 25 | 21 | 104 | 102 | 71 | 20 | 0 | 58 | 60 | 53 | 47 | 130 | 132 | 62 | 40 | 44 | 0 | 19 | 40 | 10 | 250 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 70 | 70 | 50 | 298 | 102 | 90 |  | 795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 15 | 0 | 0 | 0 | 0 | 50 | 26 | 94 | 6 | 43 | 45 | 43 | 34 | 0 | 17 | 8 | 0 | 0 | 184 | 17 | 17 | 158 | 0 | 134 | 0 | 52 | 0 | 134 | 0 | 270 | 17 | 0 | 0 | 36 |  | 5388 | 2372 | 7760 | 3371 | 795 | 1788 | 1219 | 184 | 0 | 299 | 104 | 0 | 0 | 78.19
9:00 | 36 | 79 | 0 | 110 | 300 | 0 | 0 | 2 | 300 | 27 | 0 | 370 | 270 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 60 | 0 | 6 | 35 | 18 | 17 | 14 | 25 | 8 | 25 | 17 | 24 | 0 | 0 | 0 | 100 | 0 | 8 | 204 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 10 | 17 | 37 | 16 | 22 | 0 | 0 | 0 | 270 | 270 | 183 | 88 | 95 | 23 | 25 | 5 | 27 | 0 | 0 | 8 | 22 | 11 | 25 | 18 | 118 | 101 | 61 | 20 | 0 | 58 | 60 | 50 | 50 | 163 | 110 | 62 | 40 | 44 | 0 | 19 | 38 | 10 | 280 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 90 | 52 | 50 | 296 | 102 | 90 |  | 792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 15 | 0 | 0 | 0 | 0 | 50 | 26 | 94 | 6 | 43 | 45 | 43 | 34 | 0 | 17 | 8 | 0 | 0 | 184 | 14 | 17 | 165 | 0 | 134 | 0 | 52 | 0 | 134 | 0 | 270 | 17 | 0 | 0 | 36 |  | 5447 | 2374 | 7821 | 3359 | 792 | 1866 | 1206 | 184 | 0 | 296 | 118 | 0 | 0 | 78.16
10:00 | 36 | 79 | 0 | 110 | 300 | 0 | 0 | 15 | 300 | 27 | 0 | 370 | 270 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 59 | 0 | 6 | 35 | 0 | 17 | 14 | 25 | 8 | 25 | 17 | 24 | 0 | 0 | 0 | 100 | 0 | 8 | 205 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 10 | 48 | 30 | 16 | 12 | 0 | 0 | 0 | 270 | 270 | 183 | 88 | 100 | 23 | 25 | 5 | 35 | 0 | 0 | 8 | 22 | 11 | 25 | 18 | 120 | 100 | 60 | 20 | 0 | 60 | 60 | 50 | 50 | 130 | 113 | 60 | 40 | 44 | 0 | 18 | 37 | 10 | 270 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 95 | 52 | 50 | 294 | 101 | 90 |  | 792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 13 | 0 | 0 | 0 | 0 | 50 | 20 | 94 | 6 | 43 | 45 | 43 | 34 | 0 | 17 | 8 | 0 | 0 | 184 | 14 | 16 | 170 | 0 | 134 | 0 | 51 | 0 | 140 | 0 | 272 | 17 | 0 | 0 | 17 |  | 5428 | 2358 | 7786 | 3388 | 792 | 1819 | 1194 | 184 | 0 | 289 | 120 | 0 | 0 | 78.13
11:00 | 36 | 79 | 0 | 110 | 300 | 0 | 0 | 40 | 300 | 27 | 0 | 370 | 290 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 57 | 0 | 6 | 35 | 18 | 17 | 14 | 25 | 14 | 25 | 16 | 24 | 0 | 0 | 0 | 100 | 0 | 8 | 227 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 10 | 52 | 34 | 16 | 12 | 0 | 0 | 0 | 300 | 270 | 205 | 78 | 100 | 20 | 25 | 5 | 35 | 0 | 0 | 8 | 21 | 11 | 25 | 21 | 124 | 98 | 60 | 20 | 0.8 | 55 | 60 | 50 | 50 | 130 | 115 | 59 | 40 | 44 | 0 | 18 | 37 | 10 | 280 | 16 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 15.4 | 100 | 50 | 50 | 289 | 105 | 90 |  | 792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 178 | 17 | 0 | 0 | 0 | 0 | 50 | 21 | 85 | 6 | 43 | 43 | 42 | 20 | 0 | 17 | 11 | 0 | 0 | 184 | 14 | 16 | 164 | 0 | 134 | 0 | 51 | 0 | 166 | 0 | 300 | 17 | 0 | 0 | 17 |  | 5611.2 | 2390 | 8001.2 | 3498 | 792 | 1851 | 1269 | 184 | 0 | 267 | 124 | 16.2 | 0 | 78.1
12:00 | 36 | 78 | 0 | 110 | 300 | 0 | 0 | 117 | 340 | 0 | 0 | 430 | 305 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 57 | 0 | 6 | 35 | 18 | 17 | 14 | 25 | 12 | 25 | 16 | 24 | 0 | 0 | 0 | 100 | 0 | 8 | 220 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 10 | 74 | 39 | 16 | 9 | 0 | 0 | 0 | 330 | 300 | 208 | 117 | 100 | 20 | 25 | 5 | 35 | 0 | 0 | 8 | 21 | 11 | 25 | 21 | 130 | 97 | 60 | 20 | 0.6 | 55 | 59 | 50 | 50 | 163 | 117 | 58 | 77 | 44 | 0 | 18 | 38 | 10 | 300 | 16 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 18.6 | 100 | 50 | 50 | 287 | 110 | 90 |  | 792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 24 | 178 | 24 | 0 | 0 | 0 | 0 | 50 | 47 | 85 | 6 | 43 | 43 | 42 | 19 | 0 | 17 | 11 | 0 | 0 | 184 | 14 | 15 | 158 | 0 | 134 | 0 | 91 | 0 | 172 | 0 | 280 | 53 | 0 | 0 | 34 |  | 6011.2 | 2518 | 8529.2 | 3625 | 792 | 2105 | 1383 | 184 | 0 | 291 | 130 | 19.2 | 0 | 78.09
13:00 | 36 | 78 | 0 | 110 | 300 | 0 | 0 | 338 | 340 | 0 | 0 | 430 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 55 | 0 | 6 | 35 | 18 | 17 | 14 | 25 | 12 | 25 | 16 | 24 | 0 | 0 | 0 | 100 | 0 | 8 | 218 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 10 | 92 | 39 | 16 | 29 | 0 | 0 | 0 | 340 | 334 | 195 | 123 | 100 | 23 | 25 | 5 | 35 | 0 | 0 | 20 | 21 | 11 | 25 | 21 | 152 | 96 | 60 | 20 | 0.2 | 56 | 59 | 50 | 49 | 163 | 119 | 59 | 81 | 44 | 0 | 18 | 39 | 10 | 300 | 16 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 18 | 100 | 34 | 97 | 288 | 111 | 90 |  | 792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24 | 178 | 25 | 0 | 0 | 0 | 0 | 50 | 0 | 85 | 6 | 43 | 0 | 43 | 30 | 0 | 17 | 11 | 0 | 0 | 184 | 0 | 0 | 180 | 0 | 168 | 0 | 91 | 0 | 177 | 0 | 280 | 53 | 0 | 12 | 72 |  | 6364.2 | 2526 | 8890.2 | 3933 | 792 | 2136 | 1489 | 184 | 0 | 186 | 152 | 18.2 | 0 | 0
14:00 | 36 | 79 | 0 | 110 | 300 | 0 | 0 | 331 | 340 | 0 | 0 | 430 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 56 | 0 | 6 | 35 | 18 | 17 | 14 | 25 | 5 | 25 | 16 | 24 | 0 | 0 | 0 | 100 | 0 | 8 | 217 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 10 | 104 | 39 | 16 | 21 | 0 | 0 | 0 | 330 | 300 | 207 | 125 | 100 | 23 | 25 | 5 | 35 | 0 | 0 | 34 | 20 | 11 | 25 | 20 | 154 | 97 | 60 | 20 | 0.4 | 55 | 59 | 49 | 49 | 100 | 116 | 58 | 79 | 44 | 0 | 18 | 39 | 10 | 270 | 24 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 15.84 | 100 | 17 | 127 | 286 | 111 | 90 |  | 792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 24 | 178 | 25 | 0 | 0 | 0 | 0 | 50 | 0 | 85 | 6 | 24 | 0 | 42 | 27 | 7 | 17 | 11 | 0 | 0 | 184 | 0 | 0 | 180 | 0 | 165 | 0 | 91 | 0 | 163 | 0 | 280 | 53 | 0 | 70 | 90 |  | 6284.24 | 2571 | 8855.24 | 3883 | 792 | 2041 | 1600 | 184 | 0 | 185 | 154 | 16.24 | 0 | 0
15:00 | 36 | 79 | 0 | 110 | 300 | 0 | 0 | 374 | 342 | 27 | 0 | 430 | 250 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 32 | 5 | 54 | 0 | 6 | 54 | 35 | 48 | 12 | 25 | 5 | 0 | 16 | 30 | 0 | 0 | 0 | 90 | 0 | 9 | 214 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 33 | 104 | 39 | 16 | 15 | 0 | 0 | 0 | 360 | 338 | 185 | 125 | 98 | 20 | 25 | 5 | 35 | 0 | 0 | 36 | 20 | 11 | 25 | 20 | 166 | 97 | 60 | 20 | 0.5 | 53 | 58 | 48 | 49 | 130 | 122 | 59 | 78 | 44 | 0 | 17 | 39 | 10 | 300 | 16 | 0 | 0 | 0 | 0 | 0 | 168 | 51 | 3 | 12.6 | 100 | 17 | 150 | 286 | 111 | 90 |  | 796 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 8 | 40 | 178 | 27 | 0 | 0 | 0 | 0 | 50 | 0 | 85 | 6 | 24 | 0 | 43 | 27 | 18 | 16 | 11 | 0 | 0 | 184 | 0 | 0 | 174 | 0 | 171 | 0 | 91 | 0 | 156 | 0 | 280 | 90 | 0 | 108 | 91 |  | 6616.1 | 2727 | 9343.1 | 3914 | 796 | 2107 | 1961 | 184 | 0 | 202 | 166 | 13.1 | 0 | 0
16:00 | 36 | 79 | 0 | 110 | 300 | 0 | 0 | 325 | 300 | 27 | 0 | 430 | 250 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 24 | 98 | 50 | 56 | 0 | 6 | 54 | 46 | 55 | 0 | 25 | 5 | 25 | 24 | 38 | 0 | 0 | 0 | 90 | 0 | 25 | 203 | 0 | 145 | 0 | 0 | 0 | 0 | 16 | 50 | 104 | 39 | 16 | 16 | 0 | 0 | 0 | 330 | 330 | 182 | 125 | 0 | 20 | 25 | 5 | 35 | 0 | 0 | 43 | 20 | 11 | 25 | 20 | 158 | 99 | 60 | 20 | 0 | 50 | 58 | 52 | 49 | 165 | 118 | 42 | 79 | 44 | 0 | 18 | 40 | 10 | 250 | 16 | 5 | 0 | 10 | 0 | 0 | 192 | 0 | 45 | 7 | 100 | 17 | 150 | 290 | 101 | 91 |  | 796 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 12 | 40 | 178 | 26 | 0 | 0 | 0 | 0 | 50 | 0 | 85 | 6 | 24 | 0 | 43 | 31 | 21 | 17 | 11 | 0 | 0 | 184 | 0 | 0 | 176 | 0 | 146 | 0 | 91 | 0 | 136 | 0 | 280 | 90 | 0 | 108 | 90 |  | 6629 | 2707 | 9336 | 3684 | 796 | 2060 | 2155 | 184 | 0 | 292 | 158 | 7 | 0 | 0
17:00 | 36 | 79 | 0 | 110 | 300 | 0 | 0 | 326 | 300 | 13 | 0 | 430 | 265 | 12 | 0 | 15 | 0 | 0 | 0 | 0 | 7 | 24 | 48 | 10 | 56 | 0 | 6 | 54 | 56 | 35 | 12 | 25 | 5 | 25 | 33 | 50 | 0 | 0 | 0 | 90 | 0 | 25 | 203 | 0 | 145 | 0 | 0 | 0 | 0 | 17 | 50 | 104 | 41 | 0 | 20 | 0 | 0 | 0 | 330 | 330 | 181 | 125 | 0 | 20 | 25 | 5 | 35 | 0 | 0 | 43 | 20 | 11 | 25 | 20 | 150 | 99 | 60 | 20 | 0.4 | 51 | 58 | 52 | 49 | 163 | 120 | 40 | 79 | 10 | 0 | 18 | 39 | 10 | 95 | 16 | 5 | 0 | 12 | 0 | 0 | 194 | 0 | 24 | 2.78 | 100 | 17 | 150 | 290 | 111 | 90 |  | 796 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 24 | 20 | 178 | 23 | 0 | 0 | 0 | 0 | 50 | 0 | 85 | 12 | 24 | 0 | 24 | 34 | 21 | 16 | 11 | 0 | 0 | 184 | 0 | 0 | 175 | 0 | 149 | 0 | 94 | 0 | 128 | 0 | 280 | 90 | 0 | 108 | 54 |  | 6322.18 | 2596 | 8918.18 | 3684 | 796 | 1871 | 1972 | 184 | 0 | 258 | 150 | 3.18 | 0 | 0
18:00 | 36 | 78 | 0 | 110 | 300 | 0 | 0 | 324 | 270 | 13 | 0 | 430 | 255 | 7 | 0 | 15 | 0 | 0 | 0 | 0 | 7 | 24 | 48 | 10 | 56 | 0 | 6 | 54 | 56 | 35 | 12 | 25 | 5 | 25 | 33 | 50 | 0 | 0 | 0 | 90 | 0 | 25 | 204 | 0 | 146 | 0 | 0 | 0 | 0 | 31 | 50 | 104 | 39 | 0 | 30 | 0 | 0 | 0 | 300 | 300 | 181 | 125 | 0 | 20 | 25 | 5 | 10 | 0 | 0 | 43 | 21 | 11 | 25 | 20 | 144 | 99 | 60 | 20 | 0 | 50 | 58 | 14 | 15 | 100 | 144 | 40 | 40 | 10 | 0 | 18 | 11 | 10 | 165 | 24 | 11 | 0 | 12 | 0 | 0 | 194 | 0 | 15 | 0.25 | 100 | 17 | 150 | 290 | 110 | 91 |  | 795 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 7 | 33 | 16 | 178 | 23 | 0 | 0 | 0 | 0 | 50 | 10 | 92 | 12 | 24 | 0 | 24 | 34 | 21 | 17 | 11 | 0 | 0 | 184 | 0 | 0 | 183 | 0 | 146 | 0 | 96 | 0 | 127 | 0 | 115 | 90 | 0 | 108 | 53 |  | 6101.25 | 2465 | 8566.25 | 3665 | 795 | 1532 | 1941 | 184 | 0 | 305 | 144 | 0.25 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 36 | 78 | 0 | 110 | 300 | 0 | 0 | 347 | 348 | 27 | 0 | 430 | 275 | 26 | 1 | 15 | 0 | 0 | 0 | 0 | 7 | 102 | 133 | 22 | 56 | 0 | 6 | 54 | 56 | 55 | 12 | 25 | 5 | 25 | 33 | 50 | 0 | 36 | 30 | 100 | 0 | 25 | 214 | 0 | 145 | 0 | 0 | 0 | 66 | 83 | 60 | 104 | 40 | 0 | 33 | 0 | 0 | 0 | 360 | 340 | 203 | 125 | 0 | 20 | 25 | 5 | 15 | 0 | 50 | 43 | 21 | 11 | 25 | 21 | 174 | 99 | 60 | 20 | 0 | 51 | 58 | 53 | 38 | 130 | 221 | 61 | 81 | 44 | 0 | 18 | 41 | 10 | 260 | 24 | 11 | 0 | 13 | 77 | 0 | 194 | 52 | 33 | 0 | 100 | 17 | 150 | 288 | 110 | 91 |  | 845 | 27 | 0 | 0 | 115 | 0 | 0 | 0 | 17 | 70 | 40 | 178 | 34 | 80 | 10 | 0 | 0 | 50 | 45 | 93 | 35 | 24 | 32 | 43 | 34 | 21 | 16 | 11 | 0 | 0 | 184 | 17 | 17 | 176 | 0 | 159 | 0 | 96 | 6 | 126 | 0 | 280 | 90 | 0 | 108 | 91 |  | 7413 | 3170 | 10583 | 3932 | 845 | 2085 | 2553 | 184 | 66 | 744 | 174 | 0 | 0 | 78.02
19:30 | 36 | 79 | 0 | 110 | 300 | 0 | 0 | 325 | 350 | 70 | 0 | 430 | 235 | 50 | 15 | 30 | 0 | 0 | 0 | 0 | 15 | 102 | 149 | 70 | 60 | 0 | 30 | 54 | 56 | 55 | 0 | 25 | 5 | 25 | 33 | 50 | 0 | 36 | 30 | 100 | 0 | 25 | 204 | 0 | 145 | 0 | 0 | 0 | 66 | 83 | 60 | 104 | 40 | 0 | 33 | 0 | 0 | 0 | 360 | 349 | 181 | 125 | 0 | 20 | 25 | 5 | 20 | 0 | 50 | 43 | 21 | 11 | 25 | 21 | 172 | 101 | 60 | 20 | 0 | 54 | 58 | 53 | 50 | 163 | 214 | 63 | 81 | 44 | 0 | 18 | 41 | 10 | 265 | 24 | 11 | 0 | 22 | 77 | 0 | 194 | 51 | 100 | 0 | 100 | 17 | 150 | 292 | 110 | 90 |  | 845 | 40 | 0 | 0 | 115 | 0 | 0 | 0 | 20 | 67 | 40 | 178 | 34 | 90 | 18 | 0 | 0 | 50 | 39 | 95 | 35 | 40 | 34 | 43 | 34 | 22 | 17 | 11 | 0 | 0 | 184 | 17 | 17 | 176 | 0 | 160 | 0 | 95 | 30 | 126 | 0 | 285 | 90 | 0 | 108 | 90 |  | 7646 | 3245 | 10891 | 3881 | 845 | 2148 | 2816 | 184 | 66 | 779 | 172 | 0 | 0 | 0
20:00 | 36 | 79 | 0 | 110 | 300 | 0 | 0 | 335 | 300 | 70 | 0 | 430 | 230 | 86 | 15 | 45 | 0 | 0 | 0 | 0 | 35 | 102 | 149 | 65 | 60 | 0 | 36 | 54 | 56 | 55 | 0 | 25 | 9 | 25 | 24 | 50 | 0 | 36 | 30 | 100 | 0 | 25 | 204 | 0 | 145 | 0 | 0 | 0 | 66 | 83 | 60 | 104 | 40 | 0 | 41 | 0 | 0 | 0 | 320 | 300 | 181 | 125 | 0 | 20 | 25 | 5 | 20 | 0 | 50 | 43 | 0 | 11 | 25 | 21 | 172 | 101 | 60 | 20 | 0 | 56 | 58 | 53 | 50 | 100 | 214 | 63 | 81 | 46 | 0 | 18 | 41 | 10 | 240 | 24 | 11 | 0 | 33 | 0 | 0 | 194 | 0 | 109 | 0 | 100 | 0 | 150 | 290 | 111 | 91 |  | 845 | 43 | 0 | 0 | 115 | 0 | 0 | 0 | 25 | 62 | 24 | 178 | 33 | 110 | 22 | 0 | 0 | 50 | 32 | 95 | 35 | 50 | 36 | 43 | 34 | 22 | 17 | 11 | 0 | 0 | 184 | 17 | 18 | 175 | 0 | 153 | 0 | 96 | 0 | 125 | 0 | 200 | 90 | 0 | 108 | 90 |  | 7357 | 3138 | 10495 | 3767 | 845 | 1935 | 2744 | 184 | 66 | 782 | 172 | 0 | 0 | 78.02
21:00 | 36 | 134 | 0 | 110 | 300 | 0 | 0 | 353 | 351 | 26 | 0 | 430 | 295 | 100 | 15 | 55 | 0 | 0 | 0 | 0 | 80 | 101 | 149 | 81 | 59 | 0 | 48 | 54 | 56 | 55 | 0 | 25 | 24 | 25 | 24 | 50 | 0 | 36 | 30 | 100 | 0 | 25 | 216 | 0 | 145 | 0 | 0 | 0 | 66 | 84 | 72 | 105 | 40 | 0 | 41 | 0 | 0 | 0 | 330 | 330 | 199 | 125 | 0 | 23 | 25 | 5 | 35 | 0 | 0 | 43 | 22 | 11 | 25 | 0 | 178 | 98 | 60 | 20 | 0 | 53 | 60 | 53 | 50 | 100 | 216 | 61 | 81 | 46 | 0 | 18 | 41 | 10 | 270 | 25 | 11 | 0 | 45 | 0 | 0 | 194 | 0 | 149 | 0 | 100 | 0 | 150 | 289 | 111 | 91 |  | 845 | 43 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 24 | 178 | 34 | 110 | 0 | 0 | 0 | 50 | 32 | 97 | 35 | 50 | 48 | 43 | 34 | 22 | 17 | 11 | 0 | 0 | 184 | 17 | 17 | 176 | 0 | 162 | 0 | 97 | 0 | 122 | 0 | 253 | 90 | 0 | 108 | 0 |  | 7749 | 3014 | 10763 | 3932 | 845 | 2086 | 2835 | 184 | 66 | 637 | 178 | 0 | 0 | 78.01
22:00 | 36 | 134 | 0 | 110 | 300 | 0 | 0 | 370 | 350 | 26 | 0 | 430 | 295 | 100 | 15 | 55 | 0 | 0 | 0 | 0 | 100 | 101 | 149 | 81 | 60 | 0 | 48 | 54 | 56 | 55 | 16 | 25 | 24 | 25 | 33 | 51 | 0 | 36 | 30 | 100 | 0 | 25 | 212 | 0 | 145 | 0 | 0 | 0 | 66 | 84 | 75 | 105 | 40 | 0 | 42 | 0 | 0 | 0 | 330 | 330 | 203 | 125 | 0 | 23 | 25 | 5 | 35 | 0 | 0 | 43 | 22 | 11 | 25 | 0 | 172 | 119 | 60 | 20 | 0 | 54 | 60 | 53 | 50 | 100 | 223 | 61 | 82 | 45 | 0 | 18 | 40 | 10 | 290 | 24 | 11 | 0 | 45 | 0 | 0 | 194 | 0 | 149 | 0 | 100 | 3 | 150 | 289 | 111 | 91 |  | 845 | 43 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 24 | 178 | 36 | 110 | 20 | 0 | 0 | 50 | 32 | 97 | 35 | 50 | 44 | 43 | 34 | 22 | 17 | 11 | 0 | 0 | 184 | 17 | 18 | 175 | 0 | 168 | 0 | 22 | 0 | 126 | 0 | 282 | 90 | 0 | 108 | 0 |  | 7860 | 2996 | 10856 | 4011 | 845 | 2061 | 2863 | 184 | 66 | 654 | 172 | 0 | 0 | 78.01
23:00 | 36 | 134 | 0 | 110 | 300 | 0 | 0 | 340 | 354 | 26 | 0 | 430 | 275 | 100 | 15 | 55 | 0 | 0 | 0 | 0 | 100 | 101 | 149 | 70 | 61 | 0 | 47 | 54 | 56 | 55 | 16 | 25 | 24 | 25 | 33 | 51 | 0 | 39 | 30 | 100 | 0 | 26 | 203 | 0 | 145 | 0 | 0 | 0 | 66 | 84 | 78 | 98 | 40 | 0 | 42 | 0 | 0 | 0 | 330 | 330 | 185 | 138 | 0 | 23 | 25 | 5 | 35 | 0 | 0 | 43 | 22 | 11 | 25 | 0 | 178 | 153 | 60 | 20 | 0 | 59 | 60 | 53 | 50 | 130 | 216 | 63 | 82 | 45 | 0 | 18 | 40 | 10 | 270 | 25 | 11 | 0 | 45 | 0 | 0 | 194 | 0 | 151 | 0 | 100 | 17 | 150 | 294 | 111 | 91 |  | 845 | 44 | 0 | 0 | 115 | 0 | 0 | 0 | 15 | 6 | 24 | 178 | 37 | 110 | 26 | 0 | 0 | 50 | 32 | 96 | 6 | 50 | 44 | 43 | 34 | 22 | 17 | 11 | 0 | 0 | 184 | 17 | 18 | 183 | 0 | 185 | 0 | 53 | 0 | 122 | 0 | 282 | 105 | 0 | 108 | 69 |  | 7861 | 3131 | 10992 | 4015 | 845 | 2120 | 2900 | 184 | 69 | 681 | 178 | 0 | 0 | 78.01
24:00 | 36 | 133 | 0 | 110 | 300 | 0 | 0 | 325 | 354 | 13 | 0 | 430 | 270 | 97 | 24 | 55 | 0 | 0 | 96 | 0 | 7 | 101 | 149 | 81 | 61 | 0 | 13 | 54 | 56 | 55 | 16 | 25 | 24 | 25 | 33 | 51 | 0 | 39 | 30 | 100 | 0 | 25 | 204 | 0 | 130 | 0 | 0 | 0 | 66 | 84 | 80 | 98 | 40 | 0 | 42 | 0 | 0 | 0 | 300 | 300 | 181 | 138 | 50 | 23 | 49 | 5 | 35 | 0 | 0 | 43 | 22 | 11 | 25 | 21 | 180 | 153 | 60 | 20 | 0 | 59 | 60 | 53 | 50 | 130 | 213 | 62 | 82 | 45 | 0 | 18 | 38 | 10 | 265 | 25 | 11 | 0 | 45 | 0 | 0 | 194 | 0 | 149 | 0 | 100 | 17 | 142 | 297 | 111 | 91 |  | 846 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 39 | 25 | 24 | 178 | 23 | 110 | 0 | 0 | 0 | 50 | 27 | 96 | 6 | 50 | 44 | 43 | 34 | 22 | 16 | 11 | 0 | 0 | 184 | 0 | 0 | 177 | 0 | 193 | 0 | 97 | 0 | 125 | 0 | 280 | 105 | 0 | 108 | 90 |  | 7815 | 3118 | 10933 | 4092 | 846 | 2164 | 2784 | 184 | 69 | 614 | 180 | 0 | 0 | 78.01
KWH | 648000 | 2508100 | 0 | 2803500 | 7115390 | 0 | 0 | 4327430 | 7823000 | 1041600 | 0 | 8918750 | 6608611 | 1511040 | 556536 | 554190 | 0 | 0 | 71000 | 0 | 779520 | 1181376 | 2108640 | 765849 | 1417920 | 0 | 317376 | 1158480 | 973654 | 959000 | 264132 | 600000 | 362160 | 556400 | 645000 | 1003620 | 0 | 713984 | 412000 | 2200000 | 0 | 455194 | 4937856 | 0 | 3334240 | 0 | 0 | 14400 | 600610 | 823960 | 1028280 | 2100480 | 952800 | 269568 | 672000 | 0 | 0 | 0 | 7734000 | 7382500 | 4672000 | 2676363 | 1533520 | 501408 | 737760 | 120000 | 762474 | 0 | 192664 | 863971 | 491256 | 257040 | 615500 | 462850 | 3693120 | 2364280 | 1653120 | 456984 | 4150 | 1335000 | 1412732 | 1184400 | 1130000 | 3446926 | 3843000 | 1385952 | 1693440 | 968040 | 0 | 438000 | 918240 | 244260 | 6680700 | 491664 | 152016 | 151680 | 1440220 | 169710 | 66240 | 3568800 | 169215 | 1559520 | 85590 | 2384640 | 1855680 | 2910550 | 7091000 | 2548800 | 2172560 |  | 18715636 | 210300 | 0 | 0 | 1317120 | 0 | 0 | 0 | 157920 | 309376 | 434625 | 4328500 | 655130 | 1012800 | 75170 | 0 | 0 | 1206496 | 536506 | 2167516 | 281650 | 988924 | 762100 | 985920 | 766577 | 346320 | 388260 | 243684 | 0 | 0 | 4501700 | 190000 | 288000 | 4287400 | 0 | 3777245 | 0 | 1975433 | 109440 | 3532436 | 0 | 6214181 | 1769280 | 0 | 1363200 | 1989300 |  | 164769181 | 65888145 | 230657326 | 89432743 | 18715636 | 47555677 | 55146891 | 4501700 | 1125984 | 10395835 | 3693120 | 89740 | 0
Fuel Cost | 557280 | 2156966 | 0 | 2411010 | 4553849.6 | 0 | 0 | 2639732.3 | 4772030 | 10009776 | 0 | 5975562.5 | 100384801.09 | 9489331.2 | 3717660.48 | 3386100.9 | 0 | 0 | 78810 | 0 | 4872000 | 7785267.84 | 20390548.8 | 4878458.13 | 8493340.8 | 0 | 2116897.92 | 8259962.4 | 6085337.5 | 6012930 | 198099 | 450000 | 0 | 0 | 0 | 9494245.2 | 0 | 0 | 0 | 2420000 | 0 | 4310687.18 | 3258984.96 | 0 | 3834376 | 0 | 0 | 126576 | 6468569.7 | 8017130.8 | 6365053.2 | 13569100.8 | 6231312 | 229132.8 | 0 | 0 | 0 | 0 | 4795080 | 5093925 | 3270400 | 1846690.47 | 1472179.2 | 335943.36 | 634473.6 | 110400 | 625228.68 | 0 | 2088477.76 | 6410664.82 | 378267.12 | 192780 | 473935 | 347137.5 | 25260940.8 | 1773210 | 15192172.8 | 351877.68 | 0 | 1388400 | 1469241.28 | 1137024 | 1017000 | 2688602.28 | 2690100 | 1579985.28 | 1811980.8 | 1064844 | 0 | 560640 | 853963.2 | 227161.8 | 4275648 | 368748 | 115532.16 | 2628614.4 | 10455997.2 | 2941074.3 | 1129392 | 25516920 | 2885115.75 | 0 | 0 | 0 | 17332051.2 | 27184537 | 6169170 | 0 | 0 |  | 95449743.6 | 6130245 | 0 | 0 | 10918924.8 | 0 | 0 | 0 | 1778179.2 | 3644449.28 | 3424845 | 2986665 | 648578.7 | 7494720 | 2531725.6 | 0 | 0 | 13814379.2 | 5751344.32 | 19420943.36 | 2436272.5 | 8801423.6 | 8116365 | 9780326.4 | 9022611.29 | 380952 | 364964.4 | 184468.788 | 0 | 0 | 17376562 | 6123700 | 7709760 | 2915432 | 0 | 2644071.5 | 0 | 0 | 1896595.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 472146447.54 | 251748247.738 | 723894695.278 | 64345429.528 | 95449743.6 | 28435104.43 | 372018485.61 | 17376562 | 0 | 121008429.31 | 25260940.8 | 0 | 0
Yesterday Day Peak | 36 | 78 | 0 | 110 | 300 | 0 | 0 | 117 | 340 | 0 | 0 | 430 | 305 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 57 | 0 | 6 | 35 | 18 | 17 | 14 | 25 | 12 | 25 | 16 | 24 | 0 | 0 | 0 | 100 | 0 | 8 | 220 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 10 | 74 | 39 | 16 | 9 | 0 | 0 | 0 | 330 | 300 | 208 | 117 | 100 | 20 | 25 | 5 | 35 | 0 | 0 | 8 | 21 | 11 | 25 | 21 | 130 | 97 | 60 | 20 | 0.6 | 55 | 59 | 50 | 50 | 163 | 117 | 58 | 77 | 44 | 0 | 18 | 38 | 10 | 300 | 16 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 18.6 | 100 | 50 | 50 | 287 | 110 | 90 |  | 792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 24 | 178 | 24 | 0 | 0 | 0 | 0 | 50 | 47 | 85 | 6 | 43 | 43 | 42 | 19 | 0 | 17 | 11 | 0 | 0 | 184 | 14 | 15 | 158 | 0 | 134 | 0 | 91 | 0 | 172 | 0 | 280 | 53 | 0 | 0 | 34 |  | 8529.2 | DayPeak
Yesterday Evening Peak | 36 | 79 | 0 | 110 | 300 | 0 | 0 | 325 | 350 | 70 | 0 | 430 | 235 | 50 | 15 | 30 | 0 | 0 | 0 | 0 | 15 | 102 | 149 | 70 | 60 | 0 | 30 | 54 | 56 | 55 | 0 | 25 | 5 | 25 | 33 | 50 | 0 | 36 | 30 | 100 | 0 | 25 | 204 | 0 | 145 | 0 | 0 | 0 | 66 | 83 | 60 | 104 | 40 | 0 | 33 | 0 | 0 | 0 | 360 | 349 | 181 | 125 | 0 | 20 | 25 | 5 | 20 | 0 | 50 | 43 | 21 | 11 | 25 | 21 | 172 | 101 | 60 | 20 | 0 | 54 | 58 | 53 | 50 | 163 | 214 | 63 | 81 | 44 | 0 | 18 | 41 | 10 | 265 | 24 | 11 | 0 | 22 | 77 | 0 | 194 | 51 | 100 | 0 | 100 | 17 | 150 | 292 | 110 | 90 |  | 845 | 40 | 0 | 0 | 115 | 0 | 0 | 0 | 20 | 67 | 40 | 178 | 34 | 90 | 18 | 0 | 0 | 50 | 39 | 95 | 35 | 40 | 34 | 43 | 34 | 22 | 17 | 11 | 0 | 0 | 184 | 17 | 17 | 176 | 0 | 160 | 0 | 95 | 30 | 126 | 0 | 285 | 90 | 0 | 108 | 90 |  | 10891 | EvPeak
Forecast for Evening | 36 | 79 | 0 | 110 | 300 | 0 | 0 | 412 | 360 | 110 | 0 | 450 | 335 | 100 | 100 | 55 | 0 | 0 | 100 | 0 | 100 | 102 | 149 | 100 | 60 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 80 | 30 | 100 | 0 | 25 | 225 | 0 | 150 | 0 | 0 | 0 | 70 | 85 | 100 | 101 | 46 | 20 | 33 | 0 | 0 | 0 | 360 | 360 | 221 | 125 | 100 | 23 | 53 | 5 | 35 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 174 | 202 | 93 | 20 | 0 | 60 | 60 | 53 | 50 | 163 | 217 | 66 | 86 | 44 | 120 | 20 | 41 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 285 | 115 | 100 |  | 960 | 40 | 0 | 0 | 115 | 0 | 0 | 0 | 40 | 80 | 40 | 178 | 33 | 110 | 26 | 0 | 0 | 50 | 40 | 100 | 35 | 50 | 48 | 43 | 35 | 22 | 17 | 11 | 0 | 0 | 184 | 17 | 18 | 200 | 0 | 200 | 0 | 95 | 100 | 200 | 0 | 282 | 105 | 0 | 108 | 108
Forecast for Day | 36 | 79 | 0 | 110 | 300 | 0 | 0 | 412 | 360 | 110 | 0 | 450 | 335 | 100 | 100 | 55 | 0 | 0 | 100 | 0 | 100 | 102 | 149 | 100 | 60 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 80 | 30 | 100 | 0 | 25 | 225 | 0 | 150 | 0 | 0 | 0 | 70 | 85 | 100 | 10 | 46 | 0 | 13 | 0 | 0 | 0 | 360 | 360 | 221 | 125 | 100 | 23 | 53 | 5 | 35 | 0 | 0 | 43 | 22 | 11 | 33 | 21 | 137 | 202 | 93 | 20 | 2 | 60 | 60 | 53 | 50 | 163 | 217 | 66 | 86 | 44 | 0 | 20 | 41 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 20 | 100 | 200 | 150 | 50 | 115 | 100 |  | 861 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 40 | 50 | 40 | 178 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 35 | 50 | 48 | 43 | 35 | 22 | 17 | 11 | 0 | 0 | 184 | 17 | 18 | 200 | 0 | 200 | 0 | 95 | 100 | 200 | 0 | 282 | 105 | 0 | 108 | 108
Generation at 08:00(Today) | 36 | 54 | 0 | 110 | 250 | 0 | 0 | 329 | 279 | 0 | 0 | 320 | 290 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 16 | 0 | 61 | 0 | 6 | 35 | 18 | 17 | 16 | 25 | 22 | 25 | 33 | 48 | 0 | 40 | 30 | 100 | 0 | 25 | 216 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 90 | 98 | 42 | 0 | 13 | 0 | 0 | 0 | 270 | 280 | 201 | 110 | 50 | 23 | 53 | 5 | 35 | 0 | 0 | 8 | 22 | 11 | 0 | 18 | 118 | 209 | 8 | 20 | 0.3 | 60 | 60 | 50 | 50 | 130 | 217 | 62 | 83 | 45 | 0 | 18 | 38 | 10 | 255 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6 | 100 | 17 | 10 | 50 | 110 | 91 | 0 | 850 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 12 | 0 | 0 | 0 | 0 | 50 | 0 | 57 | 6 | 0 | 0 | 8 | 0 | 22 | 17 | 11 | 0 | 0 | 184 | 0 | 0 | 184 | 0 | 187 | 0 | 94 | 0 | 117 | 0 | 240 | 35 | 0 | 108 | 90 | 0
199
| Minimum Generation |  | 7760 | 8:00
| Highest Generation |  | 11297 | 1:00
| Day Peak Generation |  | 8529.2 | 12:00
| Evening Peak Generation |  | 10891 | 19:30
| HVDC Max Flow |  | 846 | 24:00
| HVDC EvPeak Flow |  | 845 | 19:30
| Load factor L.F |  | 85.07%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-04-27
Till now the maximum generation is : - |  |  | 12067 MW | 21:00 | Hrs on | 2019-04-25
The Summary of Yesterday's |  | 2019-04-26 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8529.2 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8240.9 | MW
Evening Peak Generation : |  | 10891 | MW Hour : | 19:30 | Available Max Generation : |  | 13839 | MW
E.P. Demand (at gen end) : |  | 10891 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 11900 | MW
Maximum Generation : |  | 11297 | MW Hour : | 1:00 | Reserve(Generation end) |  | 1939 | MW
Total Gen. (MKWH) : |  | 230.6573 | System Load Factor : | 85.07% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -630 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-04-27
Actual : | 77.92 | Ft.(MSL) , | Rule curve : | 82.8 | Ft.( MSL )
Gas Consumed : | Total = | 1225.63 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 92780533.958
|  | Coal : | 17376562 | Oil : | 493026914.92 | Total : | 603184010.878
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4237.856 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1443.2075 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1293.4406 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1168.8656 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 1056.2136 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 852.3323 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 473.8775 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 219.3811 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 657.374 |  |  | 0 | 0%
Total | 0 |  | 11402.5482 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1 | 7) Ghorashal Unit-1 |  | 13) Raozan # 2
|  |  |  | 2) Khulna ST 110 MW | 8) Haripur SBU-1,2 |  | 14) Sikalbaha 55 MW
|  |  |  | 3) Sikalbaha ST 60 MW | 9) Baghabari-71 & 100 MW
|  |  |  | 4) Bheramara 410 MW. | 10) Ghorasal Max & Regent
|  |  |  | 5) Siddhirganj ST | 11) Barapukuria ST: Unit-1,2
|  |  |  | 6) Ashuganj #3,4,5 | 12) Haripur 412 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) After maintenance Haripur CCPP GT & ST were synchronized at 09:00 to 11:11 respectively.
b) Hathazari 230/132 kV T1 transformer was under shut down from 08:52 to 12:19 for C/M.
c) Hasnabad 132/33 kV T2 transformer was under shut down from 05:50 to 09:22 for C/M.
d) Bakulia 132/33 kV T2 transformer was switched on at 09:18.
e) Kabirpur 132/33 kV T1 transformer was under shut down from 12:12 to 15:19 for C/M.
f) Tongi 132/33 kV T1 transformer was under shut down from 12:15 to 12:35 due to temperature
high at 33 kV B-phase CT.
g) Bagerhat 132/33 kV T2 transformer tripped at 16:56 showing inst E/F and was switched on at 17:04. |  |  |  |  | About 6 MW power interruption occurred under Bagerhat S/S
area from 16:56 to 17:04.
h) Madaripur-Gopalganj 132 kV Ckt tripped at 20:29 from both ends showing Dist 3-phase and
was switched on at 20:47. At the same time Gopalganj & Modhumoti P/S got tripped.
j) Narshingdi 132 kV T2 transformer tripped at 19:12 due to 33 kV feeder fault and was |  |  |  |  | About 40 MW power interruption occurred under Norsingdi S/S
switched on at 20:02. |  |  |  |  | area from 19:12 to 20:02.
k) Kaliakoir 400/230 kV T2(New) transformer was switched on at 15:29.
l) Cumilla(N)-Chandpur 132 kV Ckt-2 tripped at 19:49 from Cumilla(N) end showing Dir O/C and
was switched on at 20:02.
m) Feni-Chowmohoni 132 kV Ckt-1 & 2 tripped at 19:49 from Feni end showing Dir O/C at Ckt-1
and inst O/C of Ckt-2 and were switched on at 20:05.
n) Jamalpur-Mymensingh 132 kV Ckt-2 was shut down at 07:49 (27/04/2019) due to red hot at
dead end tower jumper at Mymensingh end.
o) Patuakhali 132/33 kV T1 & T2 transformers tripped at 01:56(27/04/2019) due to CT burst at |  |  |  |  | About 24 MW power interruption occurred under Patuakhali S/S
33 kV Patuakhali feeder and were switched on at 02:36 & 05:59 respectively. |  |  |  |  | area from 01:56 to 02:36(27/04/2019).
p) Mymensingh 132/33 kV T2 transformer was under shut down from 06:54 to 09:44(27/04/2019) |  |  |  |  | About 16 MW power interruption occurred under Mymensingh S/S
for red hot maintenance at 33 kV DS. |  |  |  |  | area from 06:54 to 09:44(27/04/2019).
q) Rampura-Gulshan 132 kV Ckt-1 was under shut down from 05:21 to 06:50(27/04/2019) for C/M.
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-04-26 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 36 | 648000 | Unit-1 under maint.
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 79 | 2508100 | Gas shortage
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 110 | 2803500 | Gas shortage
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7115390 | FGMO
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 325 | 4327430 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 70 | 1041600 | Low demand
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 350 | 7823000 | Frequency control
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 430 | 8918750
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 50 | 1511040 | Low demand
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 235 | 6608611 | FGMO
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 15 | 556536 | Low demand
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 30 | 554190 | Low demand
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 70 | 765849 | Low demand
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 264132 | Engine problem
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 0 | 71000 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 0 | Contract Expired
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 15 | 779520 | Low demand
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 0 | 0 | Gas shortage
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 102 | 1181376
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 30 | 317376 | Low demand
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 1158480
25 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 2108640
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 56 | 973654
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 959000
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 60 | 1417920 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 30 | 962160 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 25 | 556400 | Gas shortage
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 645000
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 50 | 1003620
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
34 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 22 | 1440220 | Low demand
35 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 77 | 169710 | Low demand
36 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 66240 | Reserve
37 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 51 | 169215 | Low demand
38 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 100 | 1559520 | Low demand
| Gazipur 100 MW |  | RPCL | 100 MW | 0 | 90 | 2172560 | on test
| Dhaka area Total |  |  |  | 5798 | 3099 | 63157739
39 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 100 | 2200000 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 455194
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 85590
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 40 | 952800 | Engine problem
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 66 | 1125984 | Low water level
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4937856 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 145 | 3334240 | FGMO
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 0 | 14400 | Engine problem
47 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 66 | 600610
48 | Dohazari Peaking |  | PDB | 6*17 | 102 | 83 | 823960
49 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 60 | 1028280 | Engine problem
| Juldah 100 MW Unit-3 |  | IPP | 0 | 100 | 100 | 2384640
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 269568 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 33 | 672000
51 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 104 | 2100480
| Chattogram area Total |  |  |  | 1681 | 1026 | 20985602
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 181 | 4672000 | FGMO
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 360 | 7734000
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 349 | 7382500
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 20 | 501408 | Gas shortage
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 25 | 737760 | Gas shortage
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 125 | 2676363 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 20 | 762474 | Engine problem
| Midland 150MW |  | IPP | 23*7.015 | 150 | 150 | 2910550
61 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
62 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 50 | 192664
63 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 1533520 | Machine problem
| Chandpur Desh 200MW |  | IPP | 0 | 200 | 17 | 1855680 | Low demand
64 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 21 | 491256
65 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 257040
** | Tripura |  | Imported power | 0 | 160 | 172 | 3693120
66 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 25 | 615500 | Engine problem
67 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 43 | 863971 | Engine problem
68 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 462850 | Engine problem
69 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 151680 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1595 | 37614336
70 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 101 | 2364280 | Gas shortage
71 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 20 | 456984
72 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 60 | 1653120 | Engine problem
73 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 4150
74 | United Mymensingh PPL |  | IPP | 200 | 200 | 194 | 3568800
| United Jamalpur PPL |  | IPP | 115 MW | 115 | 110 | 2548800
| Mymensingh Area Total |  |  |  | 637 | 485 | 10596134
75 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 54 | 1335000
76 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 58 | 1412732
77 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 163 | 3446926
78 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 214 | 3843000 | FGMO
79 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 53 | 1184400
80 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 50 | 1130000
81 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 152016
82 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 63 | 1385952 | FGMO
83 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 81 | 1693440
84 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 44 | 968040 | Gas shortage
85 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 0 | 0
86 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 18 | 438000
87 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 41 | 918240 | Engine problem
88 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 24 | 491664
89 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 265 | 6680700 | FGMO
| Bibiyana-3 285 MW |  | PDB | 285 MW | 0 | 292 | 7091000 | On test
90 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 244260
| Sylhet Area Total |  |  |  | 1549 | 1441 | 32415370
91 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 40 | 210300
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 845 | 18715636
92 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
93 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1317120
94 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 20 | 157920 | Low demand
95 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
96 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 67 | 309376
97 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
98 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 434625
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
99 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 30 | 109440 | Low demand
| Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 90 | 1769280 | Engine problem
| Madhumati Power Plant |  | IPP | 100 MW | 0 | 90 | 1989300 | Engine problem
| Khulna Area Total |  |  |  | 2209 | 1337 | 25012997
100 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 90 | 1012800 | Engine problem
101 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 18 | 75170
102 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 34 | 655130
103 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 178 | 4328500
104 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 95 | 1975433 | FGMO
| Barisal Area Total |  |  |  | 462 | 415 | 8047033
105 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
106 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 50 | 1206496
107 | Bera Peaking |  | PDB | 9*8.29 | 71 | 39 | 536506
108 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 35 | 281650 | Engine problem
109 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 40 | 988924
110 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 34 | 762100
111 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 176 | 4287400 | FGMO
112 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 160 | 3777245 | FGMO
113 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 126 | 3532436 | FGMO
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282 | 282 | 285 | 6214181
114 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 34 | 766577
115 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 346320
116 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 17 | 388260
117 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 243684
118 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 43 | 985920 | Engine problem
119 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 95 | 2167516
| Paramount Baghabari |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
| Confidence CPBL-2 |  | IPP | 113 MW | 113 | 108 | 1363200
| Rajshahi Area Total |  |  |  | 1938 | 1275 | 27848415
120 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
121 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 184 | 4501700
122 | Rangpur GT |  | PDB | 1*20 | 20 | 17 | 190000
123 | Saidpur GT |  | PDB | 1*20 | 20 | 17 | 288000
| Rangpur Area Total |  |  |  | 484 | 218 | 4979700
| Total |  |  |  | 17649 | 10891 | 230657326
| Eastern Grid Total |  |  |  | 12556 | 7646 | 164769181
| Western Grid Total |  |  |  | 5093 | 3245 | 65888145
| National Grid Total |  |  |  | 17649 | 10891 | 230657326
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2019-04-26 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 7210 | MW | (b) ENTIRE WESTERN GRID : |  |  | 3217 | MW
i) Dhaka area |  |  | 3699 | MW | i) Khulna area |  |  | 1076 | MW
ii) Chittagong area |  |  | 1151 | MW | ii) Rajshahi area |  |  | 1179 | MW
iii) Comilla area |  |  | 1056 | MW | iii) Barisal area |  |  | 283 | MW
iv) Mymensingh area |  |  | 841 | MW | iv) Rangpur area |  |  | 679 | MW
v) Sylhet area |  |  | 463 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 10427 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 110 | 300 | Netrokona | 98 | 1900 | Central s/s | 90 | 1930
Munsiganj | 118 | 2100 | Jamalpur | 128 | 2300 | Noapara | 91 | 1930
Sonargaon | 72 | 100 | Sherpur | 98 | 2300 | Jessore | 142 | 1900
Shyampur | 180 | 100 | Srimongal | 38 | 2100 | Jhenida | 90 | 100
Bhulta | 187 | 100 | Shahjibazar | 114 | 2200 | Bottail | 110 | 100
Madanganj | 52 | 100 | Fenchuganj | 45 | 2200 | G.K Project | 51 | 2100
Shitalakhya | 101 | 300 | Kulawara | 40 | 1930 | Faridpur | 150 | 1930
Rahim steel | 3 | 900 | Sylhet | 128 | 2000 | Madaripur | 126 | 100
Matuail | 81 | 100 | Chatak | 33 | 2000 | Gopalganj | 84 | 2000
Ghorasal | 80 | 100 | Sunamganj | 32 | 1930 | Bagerhat | 74 | 1900
Narsingdi | 122 | 100 | Biani Bazar | 43 | 1930 | Mongla | 26 | 900
Haripur (SBU) | 93 | 100 | Comilla (S) | 180 | 2400 | Satkhira | 89 | 1930
Ullon | 89 | 2000 | Comilla(N) | 109 | 2000 | Gallamari | 47 | 100
Hasnabad | 204 | 2100 | Chandpur | 96 | 1900 | Magura | 50 | 1930
Magbazar | 96 | 1500 | Feni | 139 | 2000 | Chuadanga | 80 | 100
Maniknagar | 92 | 2100 | Chowmuhani | 162 | 1900 | Barisal | 114 | 1930
Bangabhaban | 16 | 1900 | Ashuganj | 61 | 2300 | Patuakhali | 91 | 2200
Narinda | 80 | 2000 | Daudkandi | 128 | 2000 | Bhandaria | 84 | 2100
Dhanmondi | 131 | 1200 | B.Baria | 133 | 1930 | Ishurdi | 65 | 1930
Lalbag | 56 | 2100 | Ramganj | 74 | 1900 | Ruppur Paromanobik | 1 | 100
Madartek | 54 | 2100 | Madunaghat | 57 | 2100 | Natore | 119 | 2100
Mirpur | 104 | 1930 | Hathazari | 90 | 2000 | Bogra | 230 | 2000
Kalyanpur | 114 | 1900 | Khulshi | 194 | 1400 | Noagaon | 122 | 1930
Gulshan | 122 | 1900 | Halishahar | 129 | 2100 | Rajshahi | 148 | 1930
Uttara | 70 | 1900 | Baraulia | 169 | 100 | C.Nawabganj | 74 | 2000
Uttara(New) | 12 | 1900 | Sikalbaha | 34 | 2100 | Amnura | 34 | 1900
Kamrangirchar | 63 | 1900 | Dohazari | 94 | 100 | Pabna | 92 | 300
Savar | 119 | 1900 | Cox'sbazar | 93 | 1930 | Shahjadpur | 96 | 2000
Bhasantec | 158 | 2000 | Chandraghona | 30 | 1930 | Serajganj | 91 | 2000
Agargaon | 54 | 1930 | Kaptai | 0 | 0 | Niyamatpur | 85 | 2000
Satmosjid | 102 | 1930 | A. Khaer Stl. | 0 | 0 | Joypurhat | 48 | 400
Tongi | 112 | 2100 | Bakulia | 99 | 100 | Mohastangor | 13 | 1930
Kabirpur | 173 | 800 | Julda | 21 | 100 | Rangpur | 132 | 2000
Basundhara | 136 | 2100 | TK chemical | 4 | 1200 | Lalmonirhat | 89 | 1900
Manikganj | 100 | 100 | Modern Steel | 13 | 200 | Saidpur | 94 | 1930
Joydevpur | 216 | 2000 | Shahmirpur | 38 | 100 | Purbasadipur | 92 | 1930
New Tongi | 94 | 1000 | Khagrachhari | 20 | 1900 | Thakurgaon | 73 | 1930
Kodda | 232 | 1900 | Matarbari | 25 | 2000 | Palashbari | 112 | 2000
Dhamrai | 50 | 2100 | Baroiar Hat | 26 | 1930 | Barapukuria | 51 | 2000
Valuka | 79 | 2100 | Rangamati | 12 | 1900 | Panchagar | 34 | 1830
Tangail | 194 | 200 | Abul Khair 230 | 13 | 1800 | Joldhaka | 19 | 1930
Mymensing | 233 | 2200 | BSRM | 106 | 1000
Kishorganj | 119 | 2000 | Goalpara | 23 | 100
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-04-26
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 393 | 6:00 | 386 | 12:00 | Kaliakoir | 375 | 2:00 | 365 | 12:00
Bheramara | 402 | 1:00 | 387 | 15:00 | Bhulta | 402 | 1:00 | 389 | 10:00
Ashuganj(N) | 407 | 4:00 | 394 | 10:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 232 | 21:00 | 230 | 1:00 | Hathazari | 222 | 5:00 | 217 | 22:00
Ishurdi | 236 | 10:00 | 226 | 21:00 | Megnaghat | 227 | 7:00 | 222 | 12:00
Ashuganj | 242 | 19:30 | 236 | 9:00 | Fenchuganj | 237 | 1:00 | 232 | 10:00
Serajganj | 233 | 16:00 | 233 | 21:00 | Siddhirganj | 230 | 3:00 | 222 | 10:00
Baghabari | 230 | 4:00 | 224 | 22:00 | Maniknagar | 228 | 1:00 | 220 | 15:00
Barapukuria | 230 | 17:00 | 219 | 21:00 | Old Airport | 228 | 1:00 | 218 | 12:00
Bogra | 226 | 10:00 | 210 | 1:00 | Barisal | 239 | 2:00 | 225 | 22:00
Khulna South | 232 | 19:30 | 212 | 13:00 | AKSML | 220 | 9:00 | 215 | 15:00
Rampura | 228 | 2:00 | 221 | 10:00 | BSRM | 224 | 18:00 | 218 | 13:00
Haripur | 227 | 1:00 | 220 | 7:00 | Bibiyana | 236 | 6:00 | 230 | 24:00
Hasnabad | 230 | 1:00 | 220 | 11:00 | Bhulta | 230 | 1:00 | 221 | 11:00
Aminbazar | 230 | 1:00 | 220 | 11:00 | Ashuganj (S) | 241 | 2:00 | 234 | 11:00
Tongi | 228 | 4:00 | 214 | 9:00 | Kaliakoir | 232 | 1:00 | 221 | 12:00
Comilla (N) | 236 | 1:00 | 230 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 100 | 128 | 1000 | Madanhat | 132 | 200 | 128 | 1500
Munsiganj | 136 | 300 | 127 | 1100 | Hathazari | 132 | 300 | 127 | 1100
Megnaghat | 136 | 100 | 129 | 1000 | Khulshi | 129 | 600 | 124 | 1400
Shyampur | 134 | 700 | 129 | 1200 | Halishahar | 132 | 600 | 128 | 1100
Bhulta | 129 | 100 | 124 | 1100 | Baraulia | 131 | 700 | 126 | 1200
Madanganj | 137 | 2000 | 124 | 1100 | Sikalbaha | 132 | 200 | 129 | 1000
Shitalakhya | 140 | 100 | 126 | 1200 | Dohazari | 130 | 100 | 124 | 1300
Rahim steal | 134 | 100 | 129 | 700 | Cox'sbazar | 127 | 600 | 119 | 1400
Matuail | 134 | 100 | 127 | 800 | Chandraghona | 133 | 600 | 126 | 1400
Ghorasal | 138 | 1500 | 136 | 1100 | Kaptai | 0 | 0 | 0 | 0
Narsingdi | 129 | 1100 | 118 | 100 | A. Khaer Stl. | 130 | 100 | 125 | 1200
Haripur (SBU) | 135 | 300 | 129 | 1000 | Bakulia | 130 | 700 | 126 | 1400
Ullon | 134 | 400 | 128 | 1200 | Julda | 132 | 100 | 127 | 1400
Hasnabad | 136 | 500 | 129 | 1200 | TK Chemical | 133 | 300 | 127 | 1300
Magbazar | 135 | 600 | 128 | 1200 | Modern Steel | 130 | 2000 | 125 | 1500
Maniknagar | 135 | 600 | 131 | 1200 | Shahmirpur | 131 | 300 | 127 | 1200
Bangabhaban | 130 | 500 | 126 | 1200 | Khagrachhari | 132 | 600 | 125 | 1300
Narinda | 134 | 600 | 128 | 1200 | Matarbari | 128 | 600 | 120 | 1200
Dhanmondi | 135 | 600 | 131 | 1200 | Baroiar Hat | 131 | 700 | 122 | 1830
Lalbag | 130 | 500 | 126 | 1200 | Rangamati | 132 | 600 | 125 | 400
Madartek | 134 | 600 | 128 | 1200 | Goalpara | 139 | 100 | 128 | 1100
Mirpur | 135 | 300 | 127 | 1200 | Central s/s | 138 | 900 | 128 | 1100
Kalyanpur | 135 | 400 | 129 | 1200 | Noapara | 136 | 1000 | 123 | 1100
Gulshan | 134 | 300 | 128 | 1200 | Jessore | 133 | 1930 | 117 | 1300
Uttara | 132 | 300 | 125 | 1200 | Jhenida | 123 | 2000 | 118 | 1300
Uttara New | 133 | 200 | 125 | 1200 | Bottail | 135 | 1000 | 124 | 1300
Kamrangirchar | 135 | 200 | 125 | 1200 | G.K.Project | 139 | 900 | 131 | 1300
Savar | 132 | 400 | 125 | 1200 | Faridpur | 135 | 900 | 122 | 1300
Bhasantec | 136 | 400 | 129 | 1200 | Madaripur | 135 | 900 | 125 | 1300
Agargaon | 137 | 200 | 130 | 1200 | Gopalganj | 136 | 600 | 127 | 1100
Satmosjid | 136 | 400 | 129 | 1200 | Bagerhat | 131 | 1600 | 121 | 1100
Tongi | 139 | 400 | 131 | 1100 | Mongla | 135 | 1800 | 125 | 1300
Kabirpur | 133 | 500 | 128 | 1900 | Satkhira | 137 | 1100 | 125 | 1300
Basundhara | 130 | 300 | 124 | 1830 | Gallamari | 138 | 500 | 129 | 1100
Manikganj | 141 | 200 | 127 | 800 | Magura | 129 | 2000 | 115 | 1300
Joydevpur | 138 | 1830 | 132 | 1400 | Chuadanga | 131 | 1000 | 115 | 100
New Tongi | 138 | 200 | 130 | 1100 | Barisal | 140 | 1000 | 131 | 1300
Kodda | 139 | 100 | 126 | 1100 | Patuakhali | 135 | 500 | 125 | 2200
Dhamrai | 132 | 1800 | 128 | 1900 | Bhandaria | 136 | 1000 | 129 | 1400
Valuka | 129 | 1400 | 118 | 1900 | Ishurdi | 138 | 1000 | 130 | 2100
Tangail | 130 | 1200 | 126 | 1900 | Ruppur Paromanobik | 135 | 600 | 132 | 1300
Mymensing | 126 | 1300 | 116 | 1900 | Natore | 136 | 1000 | 126 | 1900
Kishorganj | 130 | 1700 | 120 | 100 | Bogra | 131 | 1700 | 121 | 100
Netrokona | 126 | 1700 | 117 | 1900 | Noagaon | 127 | 1800 | 113 | 100
Jamalpur | 137 | 1500 | 126 | 1900 | Rajshahi | 135 | 1000 | 123 | 1400
Sherpur | 134 | 300 | 123 | 1000 | C.Nawabganj | 134 | 1000 | 122 | 1400
Srimongal | 137 | 600 | 132 | 2000 | Amnura | 137 | 1000 | 124 | 1400
Shahjibazar | 135 | 700 | 130 | 1830 | Pabna | 132 | 1000 | 124 | 1900
Fenchuganj | 135 | 500 | 131 | 1830 | Shahjadpur | 140 | 1000 | 132 | 1900
Khulawara | 135 | 400 | 130 | 2100 | Serajganj | 133 | 1000 | 124 | 700
Sylhet | 134 | 700 | 128 | 1900 | Niyamatpur | 128 | 1000 | 109 | 100
Chatak | 133 | 500 | 125 | 2100 | Joypurhat | 125 | 700 | 110 | 100
Sunamganj | 133 | 600 | 124 | 2100 | Mohastangor | 132 | 1000 | 118 | 100
Biani Bazar | 133 | 700 | 125 | 2100 | Rangpur | 123 | 1700 | 109 | 100
Comilla(s) | 126 | 1800 | 120 | 1100 | Lalmonirhat | 120 | 1700 | 100 | 100
Comilla(n) | 138 | 700 | 135 | 1000 | Saidpur | 123 | 1700 | 111 | 800
Chandpur | 136 | 700 | 116 | 2100 | Purbasadipur | 125 | 1700 | 110 | 800
Feni | 134 | 600 | 120 | 1900 | Thakurgaon | 117 | 1800 | 100 | 100
Chowmuhani | 129 | 700 | 113 | 1930 | Palashbari | 124 | 1800 | 104 | 800
Ashuganj | 135 | 700 | 131 | 100 | Barapukuria | 130 | 1700 | 119 | 100
Daudkandi | 131 | 700 | 126 | 1500 | Panchagar | 114 | 1800 | 94 | 100
B.Baria | 132 | 1600 | 125 | 1900 | Joldhaka | 123 | 1700 | 108 | 800

## L-Curve
Date | 2019-04-26
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 200 | 7815 | 3118 | 10933 |  |  |  | QF-LDC-12
0:30 | 415 | 8090.5 | 3024.5 | 11115 | Date: | 2019-04-26
1:00 | 630 | 8366 | 2931 | 11297
1:30 | 620 | 8266.5 | 2894.5 | 11161
2:00 | 610 | 8167 | 2858 | 11025
2:30 | 585 | 7986.5 | 2770 | 10756.5 | [5 empty] | Gen. at Eve. Peak | 10891 | 10891 MW (19:30 )
3:00 | 560 | 7806 | 2682 | 10488 | [6 empty] | 19:30
3:30 | 520 | 7654 | 2657 | 10311 | [5 empty] | Gen. at Day Peak | 8529.2 | 8529.2 MW (12:00 )
4:00 | 480 | 7502 | 2632 | 10134 | [6 empty] | 12:00
4:30 | 455 | 7455 | 2631 | 10086 | [5 empty] | Highest Generation | 11297
5:00 | 430 | 7408 | 2630 | 10038 | [6 empty] | 1:00
5:30 | 370 | 6960 | 2524 | 9484
6:00 | 310 | 6512 | 2418 | 8930
6:30 | 220 | 6230 | 2370.5 | 8600.5
7:00 | 130 | 5948 | 2323 | 8271
7:30 | 190 | 5668 | 2347.5 | 8015.5
8:00 | 250 | 5388 | 2372 | 7760
8:30 | 285 | 5417.5 | 2373 | 7790.5
9:00 | 320 | 5447 | 2374 | 7821
9:30 | 370 | 5437.5 | 2366 | 7803.5
10:00 | 420 | 5428 | 2358 | 7786
10:30 | 330 | 5519.6 | 2374 | 7893.6
11:00 | 240 | 5611.2 | 2390 | 8001.2
11:30 | 190 | 5811.2 | 2454 | 8265.2
12:00 | 140 | 6011.2 | 2518 | 8529.2
12:30 | 135 | 6187.7 | 2522 | 8709.7
13:00 | 130 | 6364.2 | 2526 | 8890.2
13:30 | 130 | 6324.22 | 2548.5 | 8872.72
14:00 | 130 | 6284.24 | 2571 | 8855.24
14:30 | 145 | 6450.17 | 2649 | 9099.17
15:00 | 160 | 6616.1 | 2727 | 9343.1
15:30 | 170 | 6622.55 | 2717 | 9339.55
16:00 | 180 | 6629 | 2707 | 9336
16:30 | 160 | 6475.59 | 2651.5 | 9127.09
17:00 | 140 | 6322.18 | 2596 | 8918.18
17:30 | 150 | 6211.715 | 2530.5 | 8742.215
18:00 | 160 | 6101.25 | 2465 | 8566.25
18:30 | 220 | 6757.125 | 2817.5 | 9574.625
19:00 | 280 | 7413 | 3170 | 10583
19:30 | 260 | 7646 | 3245 | 10891
20:00 | 240 | 7357 | 3138 | 10495 |  |  |  | Executive Engineer
20:30 | 260 | 7553 | 3076 | 10629 |  |  |  | Network Operation Division
21:00 | 280 | 7749 | 3014 | 10763
21:30 | 300 | 7804.5 | 3005 | 10809.5
22:00 | 320 | 7860 | 2996 | 10856 |  |  |  |  | Page 6 of 7
22:30 | 285 | 7860.5 | 3063.5 | 10924
23:00 | 250 | 7861 | 3131 | 10992
23:30 | 225 | 7838 | 3124.5 | 10962.5
24:00 | 200 | 7815 | 3118 | 10933
10891 MW (19:30 )
8529.2 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-04-26 |  | Energy | 230657326
[10 empty] | 2019-04-26 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4092 | 846 | 2164 | 2784 | 184 | 69 | 614 | 0 | 180
0:30 | 3838 | 771 | 2131.5 | 3276.5 | 184 | 84.5 | 654.5 | 0 | 175 | Date: | 2019-04-26
1:00 | 3584 | 696 | 2099 | 3769 | 184 | 100 | 695 | 0 | 170
1:30 | 3587.5 | 696 | 2126 | 3615 | 184 | 100 | 685.5 | 0 | 167 | [7 empty] | Total Energy | 230.6573 | Total Energy Gen 230.657 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 230.657 MKWHr
2:00 | 3591 | 696 | 2153 | 3461 | 184 | 100 | 676 | 0 | 164 | [7 empty] | Energy not Served | 0
2:30 | 3597.5 | 696 | 2131 | 3285 | 184 | 100.5 | 599.5 | 0 | 163 | [7 empty] | Energy Requirement | 230.6573
3:00 | 3604 | 696 | 2109 | 3109 | 184 | 101 | 523 | 0 | 162
3:30 | 3622 | 696.5 | 2107 | 2953.5 | 184 | 101 | 486 | 0 | 161 | [6 empty] | Shortage
4:00 | 3640 | 697 | 2105 | 2798 | 184 | 101 | 449 | 0 | 160
4:30 | 3606.5 | 697 | 2102 | 2785 | 184 | 103 | 448.5 | 0 | 160
5:00 | 3573 | 697 | 2099 | 2772 | 184 | 105 | 448 | 0 | 160
5:30 | 3554.5 | 697 | 2000.5 | 2389.5 | 184 | 105 | 406.5 | 0 | 147
6:00 | 3536 | 697 | 1902 | 2007 | 184 | 105 | 365 | 0 | 134
6:30 | 3500.5 | 696.5 | 1891.5 | 1770 | 184 | 103.5 | 332.5 | 0 | 122 |  |  |  |  | Coal
7:00 | 3465 | 696 | 1881 | 1533 | 184 | 102 | 300 | 0 | 110
7:30 | 3418 | 745.5 | 1834.5 | 1376 | 184 | 51 | 299.5 | 0 | 107 |  |  |  | Oil |  |  |  | ,
8:00 | 3371 | 795 | 1788 | 1219 | 184 | 0 | 299 | 0 | 104
8:30 | 3365 | 793.5 | 1827 | 1212.5 | 184 | 0 | 297.5 | 0 | 111
9:00 | 3359 | 792 | 1866 | 1206 | 184 | 0 | 296 | 0 | 118
9:30 | 3373.5 | 792 | 1842.5 | 1200 | 184 | 0 | 292.5 | 0 | 119
10:00 | 3388 | 792 | 1819 | 1194 | 184 | 0 | 289 | 0 | 120
10:30 | 3443 | 792 | 1835 | 1231.5 | 184 | 0 | 278 | 0 | 122
11:00 | 3498 | 792 | 1851 | 1269 | 184 | 0 | 267 | 0 | 124
11:30 | 3561.5 | 792 | 1978 | 1326 | 184 | 0 | 279 | 0 | 127
12:00 | 3625 | 792 | 2105 | 1383 | 184 | 0 | 291 | 0 | 130
12:30 | 3779 | 792 | 2120.5 | 1436 | 184 | 0 | 238.5 | 0 | 141
13:00 | 3933 | 792 | 2136 | 1489 | 184 | 0 | 186 | 0 | 152
13:30 | 3933 | 792 | 2136 | 1489 | 184 | 0 | 186 | 0 | 152
14:00 | 3933 | 792 | 2136 | 1489 | 184 | 0 | 186 | 0 | 152
14:30 | 3923.5 | 794 | 2121.5 | 1725 | 184 | 0 | 194 | 0 | 159
15:00 | 3914 | 796 | 2107 | 1961 | 184 | 0 | 202 | 0 | 166
15:30 | 3799 | 796 | 2083.5 | 2058 | 184 | 0 | 247 | 0 | 162
16:00 | 3684 | 796 | 2060 | 2155 | 184 | 0 | 292 | 0 | 158
16:30 | 3684 | 796 | 1965.5 | 2063.5 | 184 | 0 | 275 | 0 | 154
17:00 | 3684 | 796 | 1871 | 1972 | 184 | 0 | 258 | 0 | 150
17:30 | 3674.5 | 795.5 | 1701.5 | 1956.5 | 184 | 0 | 281.5 | 0 | 147
18:00 | 3665 | 795 | 1532 | 1941 | 184 | 0 | 305 | 0 | 144
18:30 | 3798.5 | 820 | 1808.5 | 2247 | 184 | 33 | 524.5 | 0 | 159
19:00 | 3932 | 845 | 2085 | 2553 | 184 | 66 | 744 | 0 | 174
19:30 | 3881 | 845 | 2148 | 2816 | 184 | 66 | 779 | 0 | 172
20:00 | 3767 | 845 | 1935 | 2744 | 184 | 66 | 782 | 0 | 172
20:30 | 3849.5 | 845 | 2010.5 | 2789.5 | 184 | 66 | 709.5 | 0 | 175
21:00 | 3932 | 845 | 2086 | 2835 | 184 | 66 | 637 | 0 | 178
21:30 | 3971.5 | 845 | 2073.5 | 2849 | 184 | 66 | 645.5 | 0 | 175
22:00 | 4011 | 845 | 2061 | 2863 | 184 | 66 | 654 | 0 | 172
22:30 | 4013 | 845 | 2090.5 | 2881.5 | 184 | 67.5 | 667.5 | 0 | 175
23:00 | 4015 | 845 | 2120 | 2900 | 184 | 69 | 681 | 0 | 178
23:30 | 4053.5 | 845.5 | 2142 | 2842 | 184 | 69 | 647.5 | 0 | 179 | Max Temp. in Dhaka |  | 36.2° C
24:00 | 4092 | 846 | 2164 | 2784 | 184 | 69 | 614 | 0 | 180
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 230.657 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 230.657 MKWHr
Note on W13: Author:

## Generation
2019-04-26
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 70 | 70 | 71 | 71 | 75 | 75 | 72 | 0 | 0 | [8 empty] | 0 |  | 36 | 36 | 36 | 36 | 36 | 39 | 39 | 713984
2 | Kaptai Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | [8 empty] | 0 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 412000
3 | Chattogram ST-1 (Raozan) | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 90 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2200000
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 26 | 25 | 455194
| Teknaf Solartech 20MW | [10 empty] | 15.4 | 18.6 | 18 | 15.84 | 12.6 | 7 | 2.78 | 0.25 |  | 0 | [6 empty] | 85590
6 | Sikalbaha 225MW (Gas) | 204 | 204 | 206 | 214 | 203 | 202 | 204 | 206 | 204 | 205 | 227 | 220 | 218 | 217 | 214 | 203 | 203 | 204 |  | 214 | 204 | 204 | 216 | 212 | 203 | 204 | 4937856
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas) | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 100 | 145 | 145 | 140 | 140 | 130 | 143 | 142 | 145 | 145 | 146 |  | 145 | 145 | 145 | 145 | 145 | 145 | 130 | 3334240
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | 68 | 68 | 68 | 34 | 34 | 0 | [9 empty] | 16 | 17 | 31 |  | 83 | 83 | 83 | 84 | 84 | 84 | 84 | 823960
12 | Hathazari peaking | 71 | 71 | 40 | 0 | [13 empty] | 0 |  | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 600610
| Daudkandi bangla trak | 101 | 11 | 0 | [23 empty] | 151680
14 | Daudkandi Peaking 52MW | 50 | 50 | 0 | [14 empty] | 0 |  | 50 | 50 | 50 | 0 | 0 |  |  | 192664
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | [24 empty] | 0 | 96 | 71000
17 | Siddhirganj CCPP-335 MW
18 | Summit Gazipur -2 | 298 | 300 | 140 | 90 | 90 | 0 | [9 empty] | 10 | 12 | 12 |  | 13 | 22 | 33 | 45 | 45 | 45 | 45 | 1440220
19 | Ashuganj 195MW Modular | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 88 | 88 | 78 | 117 | 123 | 125 | 125 | 125 | 125 | 125 |  | 125 | 125 | 125 | 125 | 125 | 138 | 138 | 2676363
20 | Ghorasal ST: Unit-1,2 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 648000
21 | Ghorasal GT: Unit-3 | 134 | 134 | 134 | 134 | 94 | 134 | 79 | 79 | 79 | 79 | 79 | 78 | 78 | 79 | 79 | 79 | 79 | 78 |  | 78 | 79 | 79 | 134 | 134 | 134 | 133 | 2508100
22 | Ghorasal GT: Unit-4
23 | Ghorasal ST: Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2803500
24
25 | Ghorasal ST: Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7115390
26
28 | Ashuganj ST: Unit- 3
29 | Ashuganj ST: Unit- 4
30 | Ashuganj ST: Unit- 5
32 | Ashuganj Engines TSK | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 20 | 20 | 23 | 23 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 23 | 23 | 23 | 23 | 501408
33 | Ashuganj CCPP 225 MW | 180 | 183 | 195 | 202 | 189 | 182 | 184 | 201 | 183 | 183 | 205 | 208 | 195 | 207 | 185 | 182 | 181 | 181 |  | 203 | 181 | 181 | 199 | 203 | 185 | 181 | 4672000
34 | Ashuganj CCPP(South) | 300 | 300 | 300 | 300 | 300 | 270 | 270 | 270 | 270 | 270 | 270 | 300 | 334 | 300 | 338 | 330 | 330 | 300 |  | 340 | 349 | 300 | 330 | 330 | 330 | 300 | 7382500
| Ashuganj CCPP(North) | 300 | 300 | 300 | 300 | 300 | 270 | 270 | 270 | 270 | 270 | 300 | 330 | 340 | 330 | 360 | 330 | 330 | 300 |  | 360 | 360 | 320 | 330 | 330 | 330 | 300 | 7734000
35 | Ashuganj (Precision) 55MW | 52 | 53 | 53 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 49 | 737760
36 | Chandpur CCPP | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 95 | 100 | 100 | 100 | 100 | 100 | 98 | 0 | [8 empty] | 0 | 50 | 1533520
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | [7 empty] | 0 | 2 | 15 | 40 | 117 | 338 | 331 | 374 | 325 | 326 | 324 |  | 347 | 325 | 335 | 353 | 370 | 340 | 325 | 4327430
40 | Meghnaghat CCPP 450MW | 400 | 450 | 450 | 450 | 450 | 370 | 370 | 370 | 370 | 370 | 370 | 430 | 430 | 430 | 430 | 430 | 430 | 430 |  | 430 | 430 | 430 | 430 | 430 | 430 | 430 | 8918750
41 | Haripur Power CCPP 360MW | 354 | 356 | 354 | 354 | 357 | 284 | 284 | 284 | 300 | 300 | 300 | 340 | 340 | 340 | 342 | 300 | 300 | 270 |  | 348 | 350 | 300 | 351 | 350 | 354 | 354 | 7823000
42 | Mymensingh RPCL 210MW | 84 | 84 | 90 | 102 | 102 | 103 | 102 | 102 | 101 | 100 | 98 | 97 | 96 | 97 | 97 | 99 | 99 | 99 |  | 99 | 101 | 101 | 98 | 119 | 153 | 153 | 2364280
43 | Haripur NEPC 110MW | 110 | 110 | 110 | 110 | 110 | 55 | 55 | 27 | 27 | 27 | 27 | 0 | 0 |  | 27 | 27 | 13 | 13 |  | 27 | 70 | 70 | 26 | 26 | 26 | 13 | 1041600
44 | Fenchugonj CCPP-1 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 60 | 55 | 55 | 56 | 55 | 53 | 50 | 51 | 50 |  | 51 | 54 | 56 | 53 | 54 | 59 | 59 | 1335000
45 | Fenchugonj CCPP-2 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 59 | 59 | 59 | 58 | 58 | 58 | 58 |  | 58 | 58 | 58 | 60 | 60 | 60 | 60 | 1412732
46 | Shajibazar 330 MW | 218 | 215 | 217 | 217 | 212 | 212 | 194 | 132 | 110 | 113 | 115 | 117 | 119 | 116 | 122 | 118 | 120 | 144 |  | 221 | 214 | 214 | 216 | 223 | 216 | 213 | 3843000
47 | Shahjibazar GT: Unit- 8, 9 | 60 | 61 | 55 | 64 | 64 | 54 | 64 | 62 | 62 | 60 | 59 | 58 | 59 | 58 | 59 | 42 | 40 | 40 |  | 61 | 63 | 63 | 61 | 61 | 63 | 62 | 1385952
48 | Shahjibazar 86MW | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 40 | 40 | 40 | 40 | 77 | 81 | 79 | 78 | 79 | 79 | 40 |  | 81 | 81 | 81 | 81 | 82 | 82 | 82 | 1693440
49 | Shahjibazar (EPL) 50MW | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 10 | 10 |  | 44 | 44 | 46 | 46 | 45 | 45 | 45 | 968040
50 | Sylhet GT 150 MW
51 | Sylhet GT 20 MW | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 17 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 438000
52 | Sylhet (EPL) 50MW | 42 | 42 | 42 | 42 | 42 | 42 | 41 | 40 | 38 | 37 | 37 | 38 | 39 | 39 | 39 | 40 | 39 | 11 |  | 41 | 41 | 41 | 41 | 40 | 40 | 38 | 918240
53 | Sylhet (Desh) 10MW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 244260
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 0 | [6 empty] | 5 | 5 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 152016
55 | Fenchugonj (Barakatullah) 51MW | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 50 | 50 | 50 | 49 | 48 | 52 | 52 | 14 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1184400
56 | Shahjahanulla 25 MW | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 16 | 16 | 16 | 24 |  | 24 | 24 | 24 | 25 | 24 | 25 | 25 | 491664
57 | Summit Bibiana- 2 | 270 | 270 | 265 | 290 | 290 | 250 | 270 | 250 | 280 | 270 | 280 | 300 | 300 | 270 | 300 | 250 | 95 | 165 |  | 260 | 265 | 240 | 270 | 290 | 270 | 265 | 6680700
58 | Southern 55MW | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 48 | 55 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 959000
59 | Sikalbaha (Energis) | [26 empty] | 14400
60 | Barabkunda (Regent) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0 | [9 empty] | 269568
61 | Narshingdi (Doreen) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 12 | 0 | 12 | 12 |  | 12 | 0 |  | 0 | 16 | 16 | 16 | 264132
62 | Tangail (Doreen) 22MW | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 456984
63 | Tripura | 170 | 164 | 162 | 160 | 160 | 134 | 110 | 104 | 118 | 120 | 124 | 130 | 152 | 154 | 166 | 158 | 150 | 144 |  | 174 | 172 | 172 | 178 | 172 | 178 | 180 | 3693120
64 | Malancha, Ctg. EPZ (United) | 34 | 37 | 37 | 38 | 40 | 39 | 30 | 23 | 22 | 12 | 12 | 9 | 29 | 21 | 15 | 16 | 20 | 30 |  | 33 | 33 | 41 | 41 | 42 | 42 | 42 | 672000
65 | Feni (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 21 |  | 21 | 21 | 0 | 22 | 22 | 22 | 22 | 491256
66 | Feni, Mohipal (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 257040
67 | Jangalia (Summit) 33MW | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 615500
68 | Summit Cumilla 25MW | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 |  | 21 | 21 | 21 | 0 | 0 | 0 | 21 | 462850
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 25 | 23 | 23 | 23 | 23 | 23 | 22 | 22 | 8 | 8 | 14 | 12 | 12 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 9 | 24 | 24 | 24 | 24 | 362160
71 | Summit Maona | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 556400
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 17 | 17 | 16 | 16 | 16 | 16 | 16 | 24 | 33 | 33 |  | 33 | 33 | 24 | 24 | 33 | 33 | 33 | 645000
73 | Ghorashal (Regent)
76 | Siddhirganj (Desh)
77 | Siddhirganj (Dutch Bangla) | 100 | 100 | 50 | 0 | [11 empty] | 15 | 7 | 7 |  | 7 | 15 | 35 | 80 | 100 | 100 | 7 | 779520
78 | Gazipur (RPCL) | 42 | 44 | 51 | 51 | 51 | 51 | 51 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 38 | 50 | 50 |  | 50 | 50 | 50 | 50 | 51 | 51 | 51 | 1003620
79 | Kodda 149MW | 149 | 149 | 149 | 149 | 149 | 100 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 98 | 48 | 48 |  | 133 | 149 | 149 | 149 | 149 | 149 | 149 | 2108640
80 | Jamalpur 95MW | 92 | 92 | 92 | 92 | 93 | 93 | 61 | 71 | 61 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1653120
81 | Lakdhanvi 52 MW | 52 | 52 | 52 | 52 | 52 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 20 | 34 | 36 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 863971
| Gazipur 100 MW | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 91 | 90 | 91 |  | 91 | 90 | 91 | 91 | 91 | 91 | 91 | 2172560
82 | Madanganj 102MW | 97 | 97 | 97 | 60 | 60 | 0 | [13 empty] | 1 | 15 | 15 | 15 | 15 | 15 | 24 | 556536
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj (Powerpac) 100MW | 76 | 76 | 40 | 10 | 10 | 0 | [8 empty] | 5 | 50 | 10 | 10 |  | 22 | 70 | 65 | 81 | 81 | 70 | 81 | 765849
86 | Meghnaghat CCPP(Summit) | 275 | 270 | 285 | 285 | 280 | 260 | 275 | 285 | 270 | 270 | 290 | 305 | 285 | 285 | 250 | 250 | 265 | 255 |  | 275 | 235 | 230 | 295 | 295 | 275 | 270 | 6608611
87 | Meghnaghat (IEL) | 92 | 92 | 92 | 92 | 92 | 92 | 72 | 60 | 55 | 54 | 50 | 30 | 0 |  | 2 | 40 | 12 | 7 |  | 26 | 50 | 86 | 100 | 100 | 100 | 97 | 1511040
88 | Ghorashal 78MW (MAX)
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | 68 | 68 | 68 | 68 | 68 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 33 | 50 | 50 | 50 |  | 60 | 60 | 60 | 72 | 75 | 78 | 80 | 1028280
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 47 | 47 | 47 | 47 | 47 | 47 | 50 | 50 | 50 | 50 | 49 | 49 | 49 | 49 | 49 | 15 |  | 38 | 50 | 50 | 50 | 50 | 50 | 50 | 1130000
93 | Ashuganj (Midland) 51MW | 45 | 45 | 45 | 45 | 35 | 35 | 35 | 27 | 27 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 10 |  | 15 | 20 | 20 | 35 | 35 | 35 | 35 | 762474
94 | Gagnagar (Orion) | 102 | 102 | 101 | 64 | 64 | 0 | [7 empty] | 0 | 24 | 24 | 24 | 24 |  | 102 | 102 | 102 | 101 | 101 | 101 | 101 | 1181376
95 | Patenga 50MW | 46 | 46 | 46 | 46 | 41 | 40 | 39 | 26 | 37 | 30 | 34 | 39 | 39 | 39 | 39 | 39 | 41 | 39 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 952800
96 | Chattogram ECPV 108 MW | 104 | 105 | 105 | 105 | 102 | 96 | 12 | 12 | 17 | 48 | 52 | 74 | 92 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 105 | 105 | 98 | 98 | 2100480
97 | Katpotti 51 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 30 | 36 | 48 | 48 | 47 | 13 | 317376
98 | Bosila 108MW | 62 | 63 | 63 | 63 | 63 | 63 | 63 | 61 | 60 | 59 | 57 | 57 | 55 | 56 | 54 | 56 | 56 | 56 |  | 56 | 60 | 60 | 59 | 60 | 61 | 61 | 1417920
99 | Madanganj-55 MW | 55 | 55 | 55 | 15 | 15 | 0 | [9 empty] | 0 | 15 | 15 |  | 15 | 30 | 45 | 55 | 55 | 55 | 55 | 554190
100 | Northern 55 MW | 56 | 56 | 56 | 56 | 56 | 36 | 17 | 18 | 18 | 0 | 18 | 18 | 18 | 18 | 35 | 46 | 56 | 56 |  | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 973654
101 | Kushiara 163 MW CCPP GT | 163 | 163 | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 130 | 130 | 163 | 163 | 100 | 130 | 165 | 163 | 100 |  | 130 | 163 | 100 | 100 | 100 | 130 | 130 | 3446926
102 | Sarishabari (Solar) | [10 empty] | 0.8 | 0.6 | 0.2 | 0.4 | 0.5 |  | 0.4 | 0 | [8 empty] | 4150
103 | Banco Energy 54MW | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1158480
104 | APR Energy , Keranigonj | 78 | 0 | [17 empty] | 77 | 77 | 0 |  |  |  |  | 169710
105 | Bramhangoan 100 MW (Aggreko) | 50 | 0 | [24 empty] | 66240
106 | United Mymensingh PPL | 170 | 170 | 170 | 170 | 170 | 120 | 70 | 24 | 24 | 24 | 53 | 90 | 135 | 150 | 168 | 192 | 194 | 194 |  | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 3568800
112 | Aggreko Aurahati 100MW | 51 | 0 | [11 empty] | 0 | 51 | 0 |  |  |  | 52 | 51 | 0 |  |  |  |  | 169215
114 | Summit Gazipur-1 150MW | 149 | 149 | 136 | 116 | 103 | 60 | 0 | 0 | [6 empty] | 3 | 45 | 24 | 15 |  | 33 | 100 | 109 | 149 | 149 | 151 | 149 | 1559520
115 | Juldah 100 MW Unit-3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 90 | 95 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2384640
116 | Chandpur Desh 200MW | 200 | 200 | 200 | 200 | 200 | 200 | 144 | 70 | 52 | 52 | 50 | 50 | 34 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 0 | 0 | 3 | 17 | 17 | 1855680
117 | Midland 150MW | 150 | 150 | 150 | 150 | 150 | 150 | 100 | 50 | 50 | 50 | 50 | 50 | 97 | 127 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 142 | 2910550
118 | Bibiyana-3 285 MW | 300 | 300 | 297 | 298 | 299 | 300 | 299 | 298 | 296 | 294 | 289 | 287 | 288 | 286 | 286 | 290 | 290 | 290 |  | 288 | 292 | 290 | 289 | 289 | 294 | 297 | 7091000
| United Jamalpur PPL | 101 | 101 | 101 | 102 | 102 | 102 | 102 | 102 | 102 | 101 | 105 | 110 | 111 | 111 | 111 | 101 | 111 | 110 |  | 110 | 110 | 111 | 111 | 111 | 111 | 111 | 2548800
120 | Eastern Zone Total | 8366 | 8167 | 7806 | 7502 | 7408 | 6512 | 5948 | 5388 | 5447 | 5428 | 5611.2 | 6011.2 | 6364.2 | 6284.24 | 6616.1 | 6629 | 6322.18 | 6101.25 |  | 7413 | 7646 | 7357 | 7749 | 7860 | 7861 | 7815 | 164769181
121
122 | o
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | 115 | 115 | 83 | 83 | 83 | 7 | 0 | [7 empty] | 53 | 66 | 16 | 16 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1317120
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | 30 | 30 | 0 | [14 empty] | 7 |  | 17 | 20 | 25 | 0 |  | 15 | 39 | 157920
Khulna CCPP 225MW
129 | Labon Chora 105 MW | 105 | 105 | 105 | 105 | 105 | 53 | 17 | 17 | 17 | 17 | 17 | 53 | 53 | 53 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 105 | 105 | 1769280
130
131
132
133
| Summit Barisal 110 MW | 110 | 110 | 80 | 32 | 32 | 0 | [11 empty] | 0 |  | 80 | 90 | 110 | 110 | 110 | 110 | 110 | 1012800
136 | Barisal GT: Unit-1, 2 | [19 empty] | 10 | 18 | 22 | 0 | 20 | 26 | 0 | 75170
137 | Bhola Aggreko 95MW | 97 | 97 | 96 | 96 | 97 | 97 | 91 | 52 | 52 | 51 | 51 | 91 | 91 | 91 | 91 | 91 | 94 | 96 |  | 96 | 95 | 96 | 97 | 22 | 53 | 97 | 1975433
| Bhola CCPP 194MW | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 177 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 |  | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 4328500
140 | Bhola (Venture) 33MW | 35 | 34 | 33 | 32 | 29 | 27 | 23 | 15 | 15 | 13 | 17 | 24 | 25 | 25 | 27 | 26 | 23 | 23 |  | 34 | 34 | 33 | 34 | 36 | 37 | 23 | 655130
141 | Bangla Trak Noapara | 50 | 10 | 0 | [16 empty] | 6 | 30 | 0 |  |  |  |  | 109440
142 | Noapara (KZA) 40MW | 40 | 40 | 8 | 8 | 8 | 0 | [5 empty] | 24 | 24 | 24 | 40 | 40 | 20 | 16 |  | 40 | 40 | 24 | 24 | 24 | 24 | 24 | 434625
143 | Gopalganj Peaking | 39 | 39 | 0 | [7 empty] | 2 | 2 | 5 | 7 | 8 | 12 | 24 | 33 |  | 70 | 67 | 62 | 0 |  | 6 | 25 | 309376
144 | Bheramara GT-1,2,3 | [19 empty] | 27 | 40 | 43 | 43 | 43 | 44 | 0 | 210300
145 | Madhumati Power Plant | 108 | 108 | 109 | 109 | 108 | 75 | 72 | 36 | 36 | 17 | 17 | 34 | 72 | 90 | 91 | 90 | 54 | 53 |  | 91 | 90 | 90 | 0 |  | 69 | 90 | 1989300
146 | Bheramara HVDC | 696 | 696 | 696 | 697 | 697 | 697 | 696 | 795 | 792 | 792 | 792 | 792 | 792 | 792 | 796 | 796 | 796 | 795 |  | 845 | 845 | 845 | 845 | 845 | 845 | 846 | 18715636
147 | Bheramara 360 MW
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 |  | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 4501700
153 | Baghabari GT 71MW
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1206496
157 | Sirajgonj Unit-1 225MW (Gas) | 155 | 152 | 152 | 151 | 152 | 151 | 151 | 158 | 165 | 170 | 164 | 158 | 180 | 180 | 174 | 176 | 175 | 183 |  | 176 | 176 | 175 | 176 | 175 | 183 | 177 | 4287400
158 | Sirajgonj Unit-1 225MW (Oil)
| Sirajgonj Unit-2 225MW (Gas) | 138 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 168 | 165 | 171 | 146 | 149 | 146 |  | 159 | 160 | 153 | 162 | 168 | 185 | 193 | 3777245
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas) | 139 | 134 | 134 | 134 | 134 | 134 | 133 | 134 | 134 | 140 | 166 | 172 | 177 | 163 | 156 | 136 | 128 | 127 |  | 126 | 126 | 125 | 122 | 126 | 122 | 125 | 3532436
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 270 | 270 | 272 | 300 | 280 | 280 | 280 | 280 | 280 | 280 | 115 |  | 280 | 285 | 200 | 253 | 282 | 282 | 280 | 6214181
161 | Bera Peaking | 32 | 29 | 26 | 26 | 25 | 25 | 26 | 26 | 26 | 20 | 21 | 47 | 0 |  |  |  |  | 10 |  | 45 | 39 | 32 | 32 | 32 | 32 | 27 | 536506
162 | Bogra (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 0 | [5 empty] | 7 | 18 | 21 | 21 | 21 |  | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 346320
163 | Bogra (EPL) | 17 | 16 | 17 | 16 | 17 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 16 | 17 |  | 16 | 17 | 17 | 17 | 17 | 17 | 16 | 388260
164 | Ullapara (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 243684
165 | Amnura 50MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 12 | 12 |  | 35 | 35 | 35 | 35 | 35 | 6 | 6 | 281650
166 | Katakhali (Northern) | 50 | 50 | 50 | 50 | 50 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 24 | 24 | 24 | 24 | 24 |  | 24 | 40 | 50 | 50 | 50 | 50 | 50 | 988924
167 | Katakhali Peaking | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 43 | 43 | 0 | [6 empty] | 32 | 34 | 36 | 48 | 44 | 44 | 44 | 762100
168 | Santahar Peaking | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 20 | 19 | 30 | 27 | 27 | 31 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 766577
169 | Rajlanka 52 MW | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 43 | 42 | 43 | 43 | 24 | 24 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 985920
170 | Chapainawabganj-100 MW | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 92 |  | 93 | 95 | 95 | 97 | 97 | 96 | 96 | 2167516
171 | Paramount Baghabari
172 | Confidence CPBL-2 | 35 | 35 | 35 | 35 | 35 | 35 | 0 | 0 |  |  |  |  | 12 | 70 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 1363200
173 | Rangpur GT | 16 | 0 |  |  |  | 0 | 17 | 17 | 14 | 14 | 14 | 14 | 0 | [6 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 190000
175 | Saidpur GT | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 17 | 17 | 16 | 16 | 15 | 0 | [6 empty] | 17 | 17 | 18 | 17 | 18 | 18 | 0 | 288000
176
177
178
178 | Western Zone Total | 2931 | 2858 | 2682 | 2632 | 2630 | 2418 | 2323 | 2372 | 2374 | 2358 | 2390 | 2518 | 2526 | 2571 | 2727 | 2707 | 2596 | 2465 |  | 3170 | 3245 | 3138 | 3014 | 2996 | 3131 | 3118 | 65888145