## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-05-31 | Wednesday
|  | Date (day): | 2023-05-31 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13057.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15031 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-05-30 | 2023-05-31 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 130 | 130 | 130 | 130 | 50 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 190 | 180 | 190 | 190
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 22 | 22 | 22 | 22 | 86 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 386 | 399 | 400 | 400 | 12 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 327 | 322 | 330 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 18 | 8 | 18 | 82 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 296 | 288 | 300 | 300 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 70 | 82 | 85 | 85 |  | 17 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 20 | 0 | 0 | 0 | 12 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 95 | 190 | 130 | 150 |  | 60 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 9 | 18 | 8 | 16 | 84 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 185 | 190 | 210 | 210 |  | 125 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 16 | 8 | 16 | 86 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 0 | 17 | 37 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 64 | 150 | 64 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 38 | 43 | 42 | 42 |  | 38 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 31 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 40 | 8 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 55 | 260 | 296 | 300 | 0
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 20 | 300 | 300 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 23 | 51 | 50 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 149 | 17 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 82 | 88 | 88 |  | 17 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 17 | 17 | 87 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 54 | 17 | 54 | 108 |  | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 32 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 34 | 17 | 35 | 20 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5867 | 2707 | 3693 | 3390 | 3844 | 773 | 1222
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 25 | 8 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 19 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 9 | 20 | 18 | 40 | 10
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 25 | 25 | 25 | 25 | 205 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 222 | 225 | 225
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 51 | 17 | 51 | 54 |  | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 45 | 62 | 50 | 64 |  | 34 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 47 | 51 | 51 | 68 |  | 34 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 44 | 55 | 45 | 80 | 20 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 38 | 90 | 50 | 90 | 10 |  | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 10 | 10 | 12 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 24 | 5 | 20
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 16 | 92 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 69 | 300 | 87 | 300
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 54 | 54 | 54 | 54 | 56 |  | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 38 | 90 | 38 | 90 | 10 |  | Fuel shortage
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 34 | 34 | 34 | 34 | 82 |  | Fuel shortage
| Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 18 | 163 | 18 | 163 |  |  | On test.
| SS Power I |  | Coal | SS Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 1 | 1 | 0 | 0
| Chattogram area Total |  |  |  |  | 2605 | 2545 | 805 | 1384 | 877 | 1472 | 668 | 398
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 201 | 203 | 210 | 210 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 305 | 310 | 320 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 305 | 310 | 320 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 34 | 40 | 43 | 43
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 167 | 175 | 175 | 175 | 20 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 10 | 132 | 13 | 150
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 30 | 39 | 40 | 40 |  | 12 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 34 | 120 | 34 | 120 | 80 |  | Fuel shortage
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 11 | 16 | 16 |  | 6 | Engine problem
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 122 | 136 | 129 | 152
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 16 | 52
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 21 | 19 | 21 | 21 |  | 4 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Contract Expired
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 98 | 100 | 114
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 34 | 97 | 27 | 105 | 8 |  | Fuel shortage
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 22 | 97 | 18 | 115
| Cumilla Area Total |  |  |  |  | 3159 | 3096 | 1396 | 1950 | 1592 | 2083 | 108 | 604
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 33 | 80 | 45 | 90 | 112 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 19 | 19 | 19 | 3 |  | Gas shortage
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 68 | 88 | 68 | 88 | 112 |  | Fuel shortage
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 85 | 18 | 85 | 30 |  | Fuel shortage
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 35 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 3 | 12 | 12 | 12 | 10 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 176 | 284 | 213.6 | 294 | 115 | 0
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 42 | 43 | 43 | 43 |  | 27 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 39 | 39 | 40 | 40 |  | 50 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 112 | 112 |  | 51 | ST under maint.
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 50 | 50 | 50
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 47 | 44 | 44
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 54 | 55 | 60 | 60
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 81 | 84 | 84
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 190 | 189 | 200 | 202 |  | 29 | Machine problem
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 9 |  | Gas shortage
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 320 | 300 | 300 |  | 41 | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 369 | 368 | 400 | 400 |  |  | FGMO
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 350 | 380 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1633 | 1721 | 1770 | 1772 | 9 | 628
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 911 | 913 | 930 | 930
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 63 | 62 | 83 |  | 32 | Engine problem
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 34 | 22 | 40 |  | 14 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 34 | 81 | 60 | 80 |  | 29 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 185 | 205 | 310 | 310 | 100 |  | Gas shortage
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 8 | 40
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 35 | 17 | 55 | 50 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 105 | 105 | 105 | 105
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 93 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 324 | 323 | 330 | 330 | 287 |  | Coal Shortage.
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 2905 | 2901 | 1669 | 1767 | 1944 | 1973 | 683 | 75
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 16 | 16 | 16 | 94 |  | Fuel shortage
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 23 | 35 | 23 | 35 |  | 5 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 168 | 171 | 175 | 175
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 622 | 622 | 622 | 622 | 622 |  | Coal Shortage.
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maintenance
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 150 | 17 | 150
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 150 | 150 | 150 | 150
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 996 | 1144 | 1003 | 1148 | 716 | 225
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 30 | 25 | 30 |  | 22 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 35 |  | 36 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 28 | 21 | 28 | 28 | 28
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 34 | 34 | 34 |  | 16 | Engine problem
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 40 | 40 | 40 | 40 |  | 10 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 141 | 194 | 210 | 210 | 0 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 164 | 176 | 210 | 210 | 10 |  | Gas shortage
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 346 | 377 | 0 | 200 | 214 |  | Gas shortage
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 35 | 35 | 35 | 35 |  | 15 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 14 | 20 | 22 | 22
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 8 | 44 |  | Fuel shortage
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 46 | 88 | 80 | 90 |  | 14 | Fuel shortage
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 50 | 35 | 50 | 63 |  | Fuel shortage
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 55 | 35 | 55 | 58 |  | Fuel shortage
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 748*1 | 748 | 748 | 919 | 926 | 902 | 902 |  |  | On test.
| Rajshahi Area Total |  |  |  |  | 2927 | 2905 | 1843 | 2069 | 1670 | 1957 | 980 | 116
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 72 | 74 | 71 | 74 | 11 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 250 | 250 | 250
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 12 | 0 | 0 | 20 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 32 | 48 | 35 | 49 |  | 6 | Engine problem
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 115 | 74 | 115
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 196 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 625 | 499 | 598 | 488 | 51 | 91
| Total |  |  |  |  | 24143 | 23370 | 11850 | 14511 | 13057.6 | 15031 | 4103 | 3359
A. |  | 2023-05-30 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 14511 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 11306 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 15000 | MW
3 | Day peak Generation : |  |  | 11850 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14315.65 | MW
4 | Evening peak Generation : |  |  | 14511 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 467 | MW
5 | Total Energy Generation : |  | 296.7353 | MKWHr | By Solar | 3.3157 | MKWHr
| By Gas : | 155.5592 | MKWHr |  | By Oil: | 56.6391 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 55.9021 | MKWHr |  | By Hydro: | 0.30444 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.017424 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4103 | MW | Dhaka | 5157.85 | 5104.85 |  | 53 |  | 18:00 |  | 1128
|  |  | For Plants S/D or M/C prob = |  |  | 3359 | MW | Chittagong | 1472 | 1427 |  | 45 |  | 19:00 |  | 830.85
|  |  | Total = |  |  | 7462 | MW | Khulna | 1742.8 | 1669.8 |  | 73 |  | 19:30 |  | 685.69
7 | Total Gas Supplied : |  |  | 1212.08 | MMCFD |  |  | Rajshahi | 1443 | 1378 |  | 65 |  | 20:00 |  | 679.96
8 | Fuel Cost : | i) Gas : | Taka | 179049666.698 | ii) Oil : | Taka | 800812966.2 | Comilla | 1378 | 1283 |  | 95 |  | 21:00 |  | 466.995
|  | iii) Coal : | Taka | 182289704.29 | Total | Taka | 1162152337.188 | Mymensingh | 1150 | 1087 |  | 63 |  | 22:00 |  | 759.225
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 614 | 614 |  | 0 |  | 23:00 |  | 1355.145
| ii) During Peak Demand : |  |  | 700 | MW (E to W) at | 21:00 | hrs | Barisal | 448 | 405 |  | 43 |  | 24:00 |  | 1726.64
| iii) Maximum : |  |  | 660 | MW at | 22:00 | hrs | Rangpur | 910 | 880 |  | 30
10 | Maximum Temperature in Dhaka was |  |  |  | 37.2° C |  |  | Total | 14315.65 | 13848.65 |  | 467
B. |  | 2023-05-31 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 37.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 15200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 156 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15031 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 13600 | MW
4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 310.8247 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11312 | MW at | 7:00 | 40 | 22 | 21 | 20 | 15 | 14 | 10 | 0 | 14
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.6124 | MKWHr. | ii) HVDC Flow at Peak Time |  | 913 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.385 | MKWHr. | iii) Maximum HVDC Flow : |  | 913 | MW at | 10:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 72.87 |  | (b) Today: | 72.79 |  | (c) Rule Curve: |  | 76.2
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-05-30 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 130 | 180 | 0 | 22 | 0 | 405 | 325 |  | 0 | 450 | 310 | 8 | 82 | 15 | 190 | 0 | 97 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 20 | 22 | 33 | 32 | 8 | 0 | 0 | 0 | 100 | 0 | 8 | 221 | 0 | 0 | 0 |  | 12 | 65 | 51 | 66 | 0 | 6 | 0 | 37 | 0 | 0 | 0 | 335 | 335 | 205 | 165 | 0 | 41 | 0 | 0 | 51 | 0 | 32 | 43 | 13 | 0 | 33 | 17 | 168 | 84 | 0 | 19 | 0 | 43 | 39 | 50 | 0 | 112 | 0 | 50 | 81 | 0 | 190 | 0 | 0 | 10 | 325 | 16 | 5 | 0 | 82 | 301 | 0 | 68 | 95 | 17 | 0 | 50 | 18 | 13 | 404 | 18 | 82 | 17 | 0 | 70 | 17 | 72 | 114 | 9 | 38 | 350 | 0 | 0 | 17 | 34 | 0 | 35 | 0 | 22 | 17 | 0 | 18 | 0 | 0 | 0 |  | 862 | 0 | 170 | 0 | 47 | 0 | 0 | 0 | 19 | 84 | 0 | 172 | 32 | 16 | 0 | 0 | 0 | 21 | 0 | 82 | 21 | 34 | 32 | 0 | 35 | 21 | 0 | 8 | 73 | 0 | 250 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 299 | 35 | 0 | 35 | 105 | 34 | 0 | 0 | 35 | 622 | 0 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 324 | 0 | 150 | 858 | 0 | 0 |  | 7422 | 4834 | 12256 | 4287 | 862 | 2290 | 396 | 1489 | 2277 | 0 | 0 | 487 | 168 | 0 | 0 | 1665.52 | 72.89
2:00 | 0 | 0 | 130 | 180 | 0 | 22 | 0 | 407 | 325 |  | 0 | 450 | 305 | 8 | 72 | 0 | 188 | 0 | 97 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 20 | 25 | 33 | 32 | 8 | 0 | 0 | 0 | 100 | 0 | 8 | 223 | 0 | 0 | 0 |  | 12 | 65 | 51 | 66 | 0 | 6 | 0 | 36 | 0 | 0 | 0 | 325 | 330 | 206 | 165 | 0 | 41 | 0 | 0 | 51 | 0 | 32 | 43 | 13 | 11 | 33 | 21 | 162 | 84 | 0 | 19 | 0 | 43 | 39 | 50 | 0 | 112 | 0 | 50 | 81 | 0 | 190 | 0 | 0 | 10 | 325 | 16 | 5 | 0 | 47 | 301 | 0 | 68 | 95 | 17 | 0 | 38 | 17 | 12 | 388 | 18 | 82 | 17 | 0 | 70 | 17 | 54 | 114 | 9 | 38 | 377 | 0 | 0 | 17 | 34 | 0 | 35 | 0 | 18 | 17 | 0 | 18 | 0 | 0 | 0 |  | 861 | 0 | 170 | 0 | 47 | 0 | 0 | 0 | 19 | 84 | 0 | 170 | 31 | 16 | 0 | 0 | 0 | 21 | 0 | 82 | 21 | 34 | 24 | 0 | 35 | 21 | 0 | 8 | 73 | 0 | 250 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 321 | 35 | 0 | 35 | 105 | 34 | 0 | 0 | 35 | 622 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 150 | 858 | 0 | 0 |  | 7331 | 4802 | 12133 | 4302 | 861 | 2305 | 396 | 1358 | 2270 | 0 | 0 | 479 | 162 | 0 | 0 | 1448.735 | 72.88
3:00 | 0 | 0 | 130 | 180 | 0 | 22 | 0 | 409 | 330 |  | 0 | 450 | 300 | 9 | 55 | 0 | 175 | 0 | 97 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 25 | 33 | 33 | 8 | 0 | 0 | 0 | 100 | 0 | 8 | 223 | 0 | 0 | 0 |  | 12 | 56 | 51 | 44 | 0 | 6 | 0 | 37 | 0 | 0 | 0 | 300 | 305 | 206 | 165 | 0 | 41 | 0 | 0 | 51 | 0 | 32 | 43 | 13 | 11 | 33 | 21 | 164 | 86 | 0 | 19 | 0 | 43 | 39 | 50 | 0 | 112 | 0 | 51 | 82 | 0 | 190 | 0 | 0 | 10 | 310 | 16 | 5 | 0 | 47 | 275 | 0 | 68 | 95 | 17 | 0 | 38 | 17 | 13 | 376 | 18 | 82 | 17 | 0 | 70 | 17 | 54 | 114 | 9 | 38 | 381 | 0 | 0 | 17 | 34 | 0 | 35 | 0 | 18 | 17 | 0 | 18 | 0 | 0 | 0 |  | 908 | 0 | 170 | 0 | 31 | 0 | 0 | 0 | 19 | 78 | 0 | 174 | 30 | 16 | 0 | 0 | 0 | 21 | 0 | 75 | 21 | 34 | 24 | 0 | 35 | 21 | 0 | 8 | 74 | 0 | 250 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 338 | 35 | 0 | 35 | 105 | 34 | 0 | 0 | 0 | 622 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 150 | 856 | 0 | 0 |  | 7161 | 4813 | 11974 | 4221 | 908 | 2308 | 370 | 1270 | 2276 | 0 | 0 | 457 | 164 | 0 | 0 | 1361.83 | 72.88
4:00 | 0 | 0 | 130 | 180 | 0 | 22 | 0 | 411 | 334 |  | 0 | 450 | 295 | 8 | 66 | 0 | 165 | 0 | 98 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 20 | 22 | 33 | 33 | 8 | 0 | 0 | 0 | 100 | 0 | 8 | 223 | 0 | 0 | 0 |  | 12 | 56 | 51 | 44 | 0 | 6 | 0 | 38 | 0 | 0 | 0 | 305 | 315 | 205 | 165 | 0 | 41 | 0 | 0 | 51 | 0 | 32 | 43 | 13 | 11 | 33 | 20 | 158 | 86 | 0 | 19 | 0 | 43 | 39 | 50 | 0 | 112 | 0 | 51 | 82 | 0 | 190 | 0 | 0 | 10 | 310 | 16 | 5 | 0 | 47 | 250 | 0 | 68 | 95 | 17 | 0 | 38 | 17 | 12 | 347 | 18 | 82 | 17 | 0 | 70 | 17 | 54 | 114 | 9 | 38 | 383 | 0 | 0 | 17 | 34 | 0 | 35 | 0 | 18 | 17 | 0 | 18 | 0 | 0 | 0 |  | 910 | 0 | 180 | 0 | 31 | 0 | 0 | 0 | 19 | 73 | 0 | 176 | 29 | 0 | 0 | 0 | 0 | 21 | 0 | 75 | 21 | 34 | 24 | 0 | 35 | 21 | 0 | 8 | 73 | 0 | 250 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 348 | 35 | 0 | 35 | 105 | 34 | 0 | 0 | 0 | 622 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 150 | 860 | 0 | 0 |  | 7137 | 4822 | 11959 | 4235 | 910 | 2317 | 345 | 1263 | 2279 | 0 | 0 | 452 | 158 | 0 | 0 | 1089.655 | 72.88
5:00 | 0 | 0 | 130 | 180 | 0 | 22 | 0 | 413 | 333 |  | 0 | 450 | 282 | 9 | 66 | 0 | 160 | 0 | 99 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 20 | 22 | 33 | 33 | 8 | 0 | 0 | 0 | 100 | 0 | 8 | 225 | 0 | 0 | 0 |  | 12 | 56 | 51 | 44 | 0 | 6 | 0 | 37 | 0 | 0 | 0 | 300 | 305 | 208 | 165 | 0 | 41 | 0 | 0 | 51 | 0 | 32 | 43 | 13 | 11 | 33 | 21 | 144 | 86 | 0 | 19 | 0 | 43 | 39 | 50 | 0 | 112 | 0 | 52 | 82 | 0 | 190 | 0 | 0 | 10 | 300 | 16 | 0 | 0 | 47 | 169 | 0 | 68 | 95 | 17 | 0 | 38 | 17 | 12 | 343 | 18 | 82 | 17 | 0 | 70 | 17 | 54 | 114 | 9 | 38 | 385 | 11 | 0 | 17 | 34 | 0 | 35 | 0 | 17 | 17 | 0 | 18 | 0 | 0 | 0 |  | 910 | 0 | 190 | 0 | 31 | 0 | 0 | 0 | 19 | 73 | 0 | 176 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 21 | 34 | 24 | 0 | 35 | 21 | 0 | 8 | 72 | 0 | 250 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 354 | 17 | 0 | 35 | 105 | 0 | 0 | 0 | 0 | 622 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 150 | 859 | 0 | 0 |  | 6995 | 4763 | 11758 | 4231 | 910 | 2295 | 264 | 1222 | 2277 | 0 | 0 | 415 | 144 | 0 | 0 | 947.36 | 72.87
6:00 | 0 | 0 | 130 | 180 | 0 | 22 | 0 | 414 | 332 |  | 0 | 450 | 240 | 8 | 66 | 0 | 160 | 0 | 101 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 20 | 22 | 33 | 33 | 8 | 0 | 0 | 0 | 100 | 0 | 8 | 228 | 0 | 0 | 0 |  | 12 | 56 | 51 | 44 | 0 | 6 | 0 | 38 | 0 | 0 | 0 | 300 | 305 | 211 | 165 | 0 | 41 | 0 | 0 | 51 | 0 | 32 | 43 | 13 | 11 | 33 | 21 | 134 | 87 | 0 | 19 | 0 | 43 | 39 | 50 | 0 | 112 | 0 | 52 | 82 | 0 | 190 | 0 | 0 | 10 | 280 | 8 | 5 | 0 | 47 | 0 | 0 | 68 | 0 | 17 | 1 | 38 | 18 | 13 | 343 | 18 | 82 | 17 | 0 | 70 | 17 | 54 | 114 | 9 | 38 | 352 | 16 | 3 | 17 | 34 | 0 | 35 | 2 | 18 | 17 | 0 | 18 | 0 | 0 | 0 |  | 910 | 0 | 190 | 0 | 32 | 0 | 0 | 0 | 19 | 73 | 0 | 139 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 21 | 34 | 24 | 0 | 35 | 21 | 0 | 8 | 72 | 0 | 250 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 354 | 17 | 0 | 35 | 105 | 0 | 0 | 0 | 0 | 622 | 0 | 0 | 17 | 0 | 3 | 0 | 0 | 0 | 324 | 2 | 150 | 860 | 17 | 0 |  | 6646 | 4743 | 11389 | 4168 | 910 | 2231 | 0 | 1230 | 2278 | 0 | 0 | 410 | 134 | 28 | 0 | 870.005 | 72.87
7:00 | 0 | 0 | 130 | 180 | 0 | 22 | 0 | 414 | 301 |  | 0 | 450 | 260 | 9 | 70 | 0 | 160 | 0 | 39 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 20 | 22 | 33 | 33 | 8 | 0 | 0 | 0 | 100 | 0 | 8 | 224 | 0 | 0 | 0 |  | 12 | 56 | 51 | 44 | 0 | 6 | 0 | 33 | 0 | 0 | 0 | 280 | 275 | 207 | 165 | 0 | 41 | 0 | 0 | 51 | 0 | 32 | 43 | 13 | 11 | 33 | 21 | 132 | 33 | 0 | 19 | 1 | 43 | 39 | 50 | 0 | 80 | 0 | 51 | 81 | 0 | 190 | 0 | 0 | 10 | 280 | 16 | 5 | 0 | 47 | 0 | 0 | 68 | 0 | 17 | 5 | 38 | 17 | 12 | 343 | 18 | 82 | 17 | 1 | 70 | 17 | 54 | 114 | 9 | 38 | 352 | 0 | 14 | 17 | 34 | 0 | 35 | 6 | 18 | 17 | 0 | 18 | 0 | 0 | 0 |  | 910 | 0 | 200 | 0 | 32 | 0 | 0 | 0 | 19 | 73 | 0 | 174 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 21 | 34 | 24 | 0 | 35 | 21 | 0 | 8 | 72 | 0 | 250 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 348 | 17 | 0 | 35 | 105 | 0 | 0 | 1 | 35 | 600 | 0 | 0 | 17 | 1 | 25 | 0 | 0 | 0 | 324 | 8 | 150 | 869 | 54 | 0 |  | 6436 | 4870 | 11306 | 4049 | 910 | 2174 | 0 | 1252 | 2265 | 0 | 0 | 408 | 132 | 116 | 0 | 758.27 | 72.87
8:00 | 0 | 0 | 130 | 190 | 0 | 22 | 0 | 408 | 306 |  | 0 | 450 | 290 | 8 | 85 | 0 | 170 | 0 | 39 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 22 | 33 | 32 | 8 | 0 | 0 | 0 | 100 | 0 | 8 | 220 | 0 | 0 | 0 |  | 12 | 56 | 51 | 44 | 0 | 6 | 0 | 4 | 0 | 0 | 0 | 325 | 315 | 202 | 165 | 0 | 36 | 0 | 0 | 51 | 0 | 32 | 21 | 13 | 11 | 33 | 21 | 136 | 33 | 0 | 18 | 1 | 43 | 39 | 50 | 0 | 80 | 0 | 50 | 81 | 0 | 190 | 0 | 0 | 10 | 300 | 16 | 5 | 0 | 48 | 0 | 0 | 68 | 0 | 17 | 9 | 38 | 17 | 13 | 375 | 18 | 82 | 17 | 2 | 69 | 17 | 54 | 88 | 9 | 38 | 372 | 0 | 25 | 17 | 34 | 0 | 35 | 11 | 18 | 17 | 0 | 18 | 0 | 0 | 0 |  | 912 | 0 | 200 | 0 | 32 | 0 | 0 | 0 | 14 | 42 | 0 | 170 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 21 | 34 | 24 | 0 | 35 | 20 | 0 | 8 | 72 | 0 | 250 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 334 | 17 | 0 | 35 | 105 | 30 | 0 | 3 | 35 | 580 | 0 | 0 | 17 | 2 | 26 | 0 | 0 | 0 | 324 | 15 | 150 | 852 | 102 | 0 |  | 6585 | 4866 | 11451 | 4174 | 912 | 2184 | 0 | 1249 | 2228 | 0 | 0 | 372 | 136 | 196 | 0 | 810.795 | 72.86
9:00 | 0 | 0 | 130 | 190 | 0 | 22 | 0 | 401 | 306 |  | 0 | 450 | 274 | 9 | 85 | 0 | 175 | 0 | 98 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 20 | 33 | 30 | 8 | 0 | 0 | 0 | 100 | 0 | 8 | 223 | 0 | 0 | 0 |  | 12 | 56 | 49 | 44 | 0 | 6 | 0 | 3 | 0 | 0 | 0 | 280 | 305 | 205 | 165 | 0 | 32 | 0 | 0 | 51 | 0 | 30 | 16 | 0 | 11 | 33 | 21 | 142 | 44 | 0 | 18 | 1 | 43 | 39 | 47 | 0 | 80 | 0 | 51 | 78 | 0 | 190 | 0 | 0 | 10 | 300 | 16 | 5 | 0 | 50 | 0 | 0 | 68 | 0 | 17 | 14 | 38 | 24 | 12 | 368 | 18 | 70 | 17 | 3 | 69 | 17 | 54 | 34 | 9 | 38 | 364 | 0 | 39 | 17 | 34 | 0 | 6 | 23 | 18 | 17 | 0 | 18 | 0 | 0 | 0 |  | 912 | 0 | 195 | 0 | 32 | 0 | 0 | 0 | 14 | 41 | 0 | 170 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 53 | 21 | 34 | 24 | 0 | 35 | 18 | 0 | 8 | 72 | 0 | 250 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 328 | 17 | 0 | 35 | 105 | 34 | 0 | 5 | 35 | 610 | 0 | 0 | 17 | 3 | 68 | 0 | 0 | 0 | 324 | 0 | 150 | 850 | 139 | 0 |  | 6489 | 4951 | 11440 | 4154 | 912 | 2151 | 0 | 1178 | 2256 | 0 | 0 | 352 | 142 | 295 | 0 | 1203.3 | 72.86
10:00 | 0 | 0 | 130 | 190 | 0 | 22 | 0 | 358 | 307 |  | 0 | 400 | 280 | 8 | 85 | 0 | 140 | 0 | 37 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 20 | 33 | 28 | 8 | 0 | 25 | 0 | 100 | 0 | 8 | 220 | 0 | 0 | 0 |  | 0 | 56 | 33 | 44 | 0 | 6 | 0 | 3 | 0 | 0 | 0 | 280 | 270 | 202 | 165 | 0 | 31 | 0 | 0 | 51 | 0 | 30 | 16 | 0 | 11 | 33 | 21 | 130 | 44 | 0 | 16 | 2 | 43 | 39 | 47 | 0 | 80 | 0 | 60 | 78 | 0 | 191 | 0 | 0 | 10 | 280 | 16 | 5 | 0 | 47 | 0 | 0 | 68 | 0 | 17 | 17 | 38 | 34 | 13 | 319 | 18 | 70 | 17 | 4 | 69 | 17 | 54 | 34 | 28 | 38 | 375 | 0 | 40 | 17 | 34 | 0 | 32 | 28 | 17 | 17 | 0 | 18 | 0 | 0 | 0 |  | 913 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 170 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 53 | 21 | 34 | 24 | 0 | 35 | 14 | 0 | 8 | 73 | 0 | 250 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 287 | 17 | 0 | 35 | 105 | 36 | 0 | 7 | 35 | 622 | 0 | 0 | 17 | 3 | 87 | 0 | 0 | 0 | 330 | 29 | 150 | 833 | 172 | 0 |  | 6276 | 4947 | 11223 | 3939 | 913 | 2045 | 0 | 1187 | 2258 | 25 | 0 | 337 | 130 | 389 | 0 | 1506.035 | 72.86
11:00 | 0 | 0 | 130 | 190 | 0 | 22 | 0 | 354 | 327 |  | 0 | 400 | 301 | 9 | 82 | 0 | 140 | 0 | 37 | 9 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 17 | 5 | 19 | 20 | 18 | 33 | 28 | 12 | 0 | 25 | 0 | 100 | 0 | 8 | 215 | 0 | 0 | 0 |  | 0 | 45 | 49 | 44 | 0 | 6 | 0 | 3 | 0 | 0 | 0 | 290 | 275 | 200 | 167 | 0 | 34 | 0 | 0 | 51 | 0 | 30 | 16 | 6 | 11 | 33 | 21 | 128 | 44 | 0 | 16 | 2 | 43 | 39 | 50 | 0 | 80 | 0 | 60 | 80 | 0 | 191 | 0 | 0 | 10 | 300 | 16 | 11 | 0 | 52 | 0 | 0 | 68 | 0 | 17 | 0 | 38 | 34 | 12 | 320 | 19 | 70 | 17 | 5 | 69 | 17 | 54 | 17 | 37 | 38 | 345 | 11 | 49 | 17 | 34 | 0 | 35 | 31 | 18 | 17 | 0 | 18 | 0 | 0 | 1 |  | 911 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 163 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 46 | 21 | 34 | 24 | 0 | 35 | 14 | 0 | 8 | 73 | 0 | 250 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 288 | 17 | 0 | 35 | 105 | 30 | 0 | 7 | 35 | 622 | 0 | 0 | 17 | 5 | 84 | 27 | 0 | 0 | 324 | 14 | 150 | 867 | 194 | 0 |  | 6384 | 4968 | 11352 | 3902 | 911 | 2114 | 0 | 1244 | 2286 | 25 | 0 | 350 | 128 | 391 | 1 | 1479.295 | 72.86
12:00 | 0 | 0 | 130 | 190 | 0 | 22 | 0 | 386 | 327 |  | 0 | 450 | 296 | 8 | 70 | 0 | 185 | 0 | 95 | 9 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 22 | 20 | 18 | 33 | 28 | 8 | 0 | 25 | 0 | 100 | 0 | 8 | 215 | 0 | 0 | 0 |  | 3 | 45 | 47 | 44 | 0 | 9 | 0 | 2 | 0 | 0 | 0 | 280 | 270 | 201 | 167 | 0 | 34 | 0 | 0 | 51 | 0 | 30 | 8 | 16 | 11 | 33 | 21 | 122 | 33 | 0 | 16 | 2 | 42 | 39 | 50 | 0 | 112 | 0 | 54 | 80 | 0 | 190 | 0 | 0 | 10 | 310 | 16 | 11 | 0 | 55 | 20 | 0 | 68 | 23 | 17 | 19 | 38 | 34 | 10 | 369 | 19 | 70 | 17 | 5 | 69 | 17 | 54 | 17 | 34 | 38 | 350 | 17 | 35 | 17 | 34 | 0 | 35 | 32 | 22 | 17 | 0 | 18 | 0 | 0 | 1 |  | 911 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 168 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 46 | 21 | 34 | 40 | 0 | 35 | 14 | 0 | 8 | 72 | 0 | 250 | 0 | 0 | 141 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 346 | 17 | 0 | 35 | 105 | 32 | 0 | 7 | 35 | 622 | 0 | 0 | 17 | 5 | 93 | 35 | 0 | 0 | 324 | 33 | 150 | 919 | 196 | 0 |  | 6717 | 5133 | 11850 | 4074 | 911 | 2260 | 43 | 1291 | 2337 | 25 | 0 | 359 | 122 | 427 | 1 | 1385.705 | 72.85
13:00 | 0 | 0 | 130 | 190 | 0 | 22 | 0 | 398 | 322 |  | 0 | 450 | 299 | 8 | 75 | 0 | 184 | 0 | 92 | 9 | 8 | 64 | 8 | 0 | 0 | 0 | 0 | 35 | 35 | 22 | 20 | 18 | 33 | 28 | 8 | 0 | 25 | 0 | 100 | 0 | 8 | 214 | 0 | 0 | 0 |  | 12 | 50 | 35 | 44 | 0 | 12 | 0 | 6 | 0 | 0 | 0 | 285 | 275 | 200 | 167 | 0 | 36 | 0 | 0 | 51 | 0 | 33 | 8 | 16 | 11 | 33 | 21 | 124 | 33 | 0 | 15 | 1 | 42 | 39 | 50 | 0 | 112 | 0 | 53 | 78 | 0 | 191 | 0 | 0 | 10 | 310 | 16 | 11 | 0 | 42 | 303 | 0 | 68 | 94 | 17 | 19 | 38 | 34 | 12 | 376 | 18 | 70 | 17 | 4 | 69 | 17 | 40 | 17 | 28 | 38 | 343 | 17 | 24 | 17 | 34 | 0 | 35 | 31 | 36 | 17 | 0 | 18 | 0 | 0 | 2 |  | 913 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 169 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 46 | 21 | 34 | 40 | 0 | 28 | 16 | 0 | 8 | 72 | 0 | 250 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 334 | 17 | 0 | 35 | 85 | 40 | 0 | 7 | 35 | 622 | 0 | 0 | 17 | 5 | 88 | 35 | 0 | 0 | 324 | 22 | 150 | 905 | 178 | 0 |  | 7080 | 5093 | 12173 | 4124 | 913 | 2252 | 397 | 1286 | 2323 | 25 | 0 | 348 | 124 | 379 | 2 | 1269.195 | 72.85
14:00 | 0 | 0 | 130 | 190 | 0 | 22 | 0 | 399 | 321 |  | 0 | 450 | 300 | 9 | 78 | 0 | 184 | 0 | 191 | 9 | 8 | 64 | 12 | 0 | 0 | 0 | 0 | 35 | 35 | 22 | 20 | 18 | 33 | 28 | 8 | 0 | 25 | 0 | 100 | 0 | 15 | 217 | 0 | 0 | 0 |  | 12 | 52 | 46 | 44 | 0 | 19 | 0 | 2 | 0 | 0 | 0 | 280 | 270 | 200 | 167 | 0 | 36 | 0 | 0 | 51 | 0 | 35 | 8 | 15 | 11 | 32 | 0 | 120 | 33 | 0 | 15 | 2 | 43 | 39 | 50 | 0 | 112 | 0 | 53 | 78 | 0 | 189 | 0 | 0 | 10 | 290 | 16 | 11 | 0 | 47 | 302 | 0 | 68 | 94 | 17 | 15 | 38 | 44 | 12 | 369 | 18 | 70 | 17 | 4 | 68 | 17 | 54 | 17 | 28 | 38 | 344 | 14 | 48 | 17 | 34 | 0 | 35 | 25 | 36 | 17 | 0 | 18 | 0 | 0 | 3 |  | 912 | 0 | 185 | 0 | 29 | 0 | 0 | 0 | 0 | 32 | 0 | 168 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 46 | 21 | 34 | 40 | 0 | 28 | 16 | 0 | 8 | 70 | 0 | 250 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 321 | 17 | 0 | 35 | 85 | 39 | 0 | 7 | 35 | 622 | 0 | 0 | 17 | 4 | 83 | 35 | 0 | 0 | 330 | 28 | 150 | 919 | 145 | 0 |  | 7192 | 5090 | 12282 | 4187 | 912 | 2215 | 396 | 1361 | 2341 | 25 | 0 | 361 | 120 | 361 | 3 | 1309.305 | 72.86
15:00 | 0 | 0 | 130 | 180 | 0 | 22 | 0 | 399 | 322 |  | 0 | 450 | 299 | 8 | 78 | 0 | 185 | 0 | 184 | 9 | 8 | 64 | 11 | 0 | 0 | 0 | 0 | 35 | 35 | 22 | 20 | 16 | 33 | 14 | 8 | 0 | 25 | 0 | 100 | 0 | 16 | 217 | 0 | 0 | 0 |  | 12 | 44 | 46 | 44 | 0 | 19 | 0 | 2 | 0 | 0 | 0 | 315 | 305 | 198 | 167 | 0 | 33 | 0 | 0 | 51 | 0 | 27 | 8 | 15 | 11 | 32 | 21 | 138 | 31 | 0 | 15 | 2 | 42 | 39 | 47 | 0 | 112 | 0 | 53 | 78 | 0 | 189 | 0 | 0 | 10 | 295 | 16 | 11 | 0 | 47 | 302 | 0 | 67 | 94 | 15 | 14 | 38 | 51 | 12 | 385 | 18 | 70 | 17 | 4 | 69 | 17 | 54 | 17 | 28 | 38 | 344 | 17 | 38 | 17 | 34 | 0 | 35 | 22 | 36 | 17 | 0 | 18 | 0 | 0 | 2 |  | 913 | 0 | 175 | 0 | 39 | 0 | 0 | 0 | 0 | 32 | 0 | 168 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 46 | 21 | 34 | 40 | 0 | 28 | 16 | 0 | 8 | 71 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 318 | 17 | 0 | 35 | 85 | 39 | 0 | 7 | 35 | 622 | 0 | 0 | 17 | 3 | 72 | 35 | 0 | 0 | 324 | 25 | 150 | 908 | 141 | 0 |  | 7255 | 5053 | 12308 | 4243 | 913 | 2215 | 396 | 1378 | 2325 | 25 | 0 | 345 | 138 | 328 | 2 | 1379.02 | 72.84
16:00 | 0 | 0 | 130 | 180 | 0 | 22 | 0 | 394 | 317 |  | 0 | 450 | 283 | 9 | 78 | 0 | 185 | 0 | 186 | 14 | 8 | 64 | 12 | 0 | 0 | 0 | 0 | 35 | 35 | 22 | 20 | 16 | 33 | 28 | 8 | 0 | 25 | 0 | 100 | 0 | 16 | 217 | 0 | 0 | 0 |  | 12 | 44 | 49 | 44 | 0 | 19 | 0 | 2 | 0 | 0 | 0 | 305 | 305 | 199 | 175 | 0 | 33 | 0 | 0 | 51 | 0 | 27 | 11 | 13 | 11 | 32 | 12 | 122 | 46 | 0 | 15 | 2 | 42 | 39 | 47 | 0 | 112 | 0 | 54 | 79 | 0 | 188 | 0 | 0 | 10 | 290 | 16 | 11 | 0 | 47 | 254 | 0 | 68 | 90 | 15 | 3 | 38 | 51 | 12 | 369 | 18 | 70 | 17 | 2 | 69 | 17 | 54 | 0 | 28 | 38 | 360 | 17 | 16 | 17 | 34 | 0 | 35 | 16 | 36 | 17 | 0 | 18 | 0 | 0 | 1 |  | 913 | 0 | 180 | 0 | 41 | 0 | 0 | 0 | 0 | 25 | 0 | 168 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 46 | 21 | 34 | 24 | 0 | 28 | 8 | 0 | 8 | 71 | 0 | 250 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 309 | 17 | 0 | 35 | 85 | 39 | 0 | 5 | 35 | 622 | 0 | 0 | 17 | 2 | 51 | 35 | 0 | 0 | 323 | 16 | 150 | 909 | 101 | 0 |  | 7131 | 4945 | 12076 | 4255 | 913 | 2178 | 344 | 1374 | 2325 | 25 | 0 | 325 | 122 | 214 | 1 | 1458.285 | 72.84
17:00 | 0 | 0 | 130 | 180 | 0 | 22 | 0 | 398 | 316 |  | 0 | 450 | 280 | 8 | 78 | 0 | 185 | 0 | 120 | 18 | 8 | 64 | 11 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 20 | 18 | 33 | 28 | 8 | 0 | 25 | 0 | 100 | 0 | 25 | 221 | 0 | 0 | 0 |  | 12 | 37 | 49 | 44 | 0 | 19 | 0 | 2 | 0 | 0 | 0 | 305 | 305 | 201 | 175 | 0 | 36 | 0 | 0 | 51 | 0 | 28 | 22 | 13 | 11 | 31 | 21 | 130 | 46 | 0 | 15 | 1 | 44 | 39 | 50 | 0 | 112 | 0 | 54 | 79 | 0 | 189 | 0 | 0 | 10 | 290 | 16 | 11 | 0 | 62 | 0 | 0 | 68 | 0 | 17 | 0 | 38 | 64 | 13 | 369 | 18 | 70 | 23 | 0 | 69 | 17 | 58 | 0 | 28 | 38 | 365 | 17 | 12 | 17 | 34 | 0 | 35 | 6 | 36 | 30 | 0 | 18 | 0 | 0 | 0 |  | 912 | 0 | 180 | 0 | 44 | 0 | 0 | 0 | 15 | 25 | 0 | 161 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 46 | 28 | 25 | 24 | 0 | 28 | 16 | 0 | 8 | 71 | 0 | 250 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 326 | 17 | 0 | 35 | 85 | 47 | 0 | 3 | 35 | 622 | 0 | 0 | 17 | 1 | 29 | 35 | 0 | 0 | 323 | 8 | 150 | 913 | 51 | 0 |  | 6825 | 4911 | 11736 | 4215 | 912 | 2204 | 0 | 1476 | 2329 | 25 | 0 | 334 | 130 | 111 | 0 | 1452.555 | 72.83
18:00 | 0 | 0 | 128 | 180 | 0 | 22 | 0 | 404 | 322 |  | 0 | 400 | 274 | 12 | 78 | 0 | 151 | 0 | 121 | 18 | 8 | 64 | 4 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 20 | 23 | 33 | 28 | 14 | 0 | 25 | 0 | 100 | 0 | 25 | 222 | 0 | 0 | 0 |  | 12 | 43 | 50 | 44 | 0 | 31 | 0 | 2 | 0 | 0 | 0 | 305 | 305 | 203 | 175 | 0 | 36 | 0 | 0 | 51 | 0 | 28 | 25 | 14 | 11 | 31 | 19 | 134 | 47 | 0 | 15 | 0 | 43 | 39 | 50 | 0 | 112 | 0 | 56 | 80 | 0 | 190 | 0 | 0 | 10 | 280 | 16 | 11 | 0 | 72 | 0 | 0 | 68 | 0 | 29 | 0 | 38 | 117 | 20 | 369 | 18 | 70 | 51 | 0 | 120 | 17 | 54 | 5 | 41 | 38 | 340 | 17 | 3 | 17 | 34 | 0 | 35 | 1 | 44 | 36 | 0 | 18 | 0 | 0 | 0 |  | 913 | 0 | 195 | 0 | 47 | 0 | 0 | 0 | 29 | 45 | 8 | 169 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 52 | 28 | 34 | 24 | 0 | 32 | 16 | 0 | 8 | 74 | 0 | 250 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 304 | 17 | 0 | 35 | 105 | 48 | 0 | 1 | 35 | 540 | 0 | 0 | 17 | 0 | 8 | 40 | 0 | 0 | 323 | 2 | 150 | 947 | 13 | 0 |  | 6925 | 4894 | 11819 | 4201 | 913 | 2120 | 0 | 1729 | 2284 | 25 | 0 | 385 | 134 | 28 | 0 | 1128 | 72.83
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 130 | 180 | 0 | 22 | 0 | 380 | 291 |  | 0 | 370 | 303 | 17 | 80 | 17 | 189 | 0 | 125 | 18 | 16 | 150 | 11 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 20 | 23 | 33 | 30 | 39 | 0 | 25 | 0 | 100 | 0 | 25 | 221 | 0 | 0 | 0 |  | 12 | 63 | 51 | 55 | 0 | 35 | 0 | 6 | 0 | 0 | 0 | 330 | 330 | 199 | 175 | 0 | 37 | 0 | 0 | 51 | 0 | 34 | 43 | 15 | 11 | 32 | 19 | 144 | 48 | 0 | 19 | 0 | 43 | 39 | 50 | 47 | 80 | 0 | 55 | 81 | 0 | 192 | 0 | 0 | 10 | 275 | 8 | 11 | 0 | 230 | 214 | 0 | 87 | 40 | 148 | 0 | 90 | 120 | 77 | 393 | 85 | 82 | 51 | 0 | 291 | 17 | 54 | 70 | 61 | 90 | 370 | 17 | 0 | 54 | 34 | 0 | 35 | 0 | 98 | 35 | 0 | 49 | 0 | 0 | 1 |  | 913 | 0 | 200 | 0 | 63 | 0 | 0 | 0 | 31 | 60 | 8 | 169 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 87 | 28 | 34 | 40 | 8 | 35 | 17 | 0 | 8 | 74 | 0 | 250 | 18 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 363 | 20 | 0 | 35 | 105 | 48 | 0 | 0 | 55 | 510 | 0 | 0 | 150 | 0 | 0 | 103 | 0 | 0 | 324 | 0 | 150 | 899 | 0 | 0 |  | 8417 | 5213 | 13630 | 4344 | 913 | 2170 | 254 | 2954 | 2207 | 25 | 18 | 600 | 144 | 0 | 1 | 830.85 | 72.82
19:30 | 0 | 0 | 130 | 180 | 0 | 22 | 0 | 403 | 302 |  | 0 | 410 | 299 | 17 | 80 | 15 | 190 | 0 | 188 | 18 | 16 | 150 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 20 | 23 | 33 | 30 | 40 | 0 | 25 | 0 | 100 | 0 | 25 | 220 | 0 | 0 | 0 |  | 12 | 62 | 51 | 55 | 0 | 39 | 0 | 13 | 0 | 0 | 0 | 330 | 330 | 200 | 175 | 0 | 37 | 0 | 0 | 51 | 0 | 37 | 51 | 15 | 11 | 32 | 19 | 134 | 52 | 0 | 19 | 0 | 43 | 39 | 50 | 47 | 80 | 0 | 57 | 81 | 0 | 192 | 0 | 0 | 10 | 315 | 16 | 11 | 0 | 262 | 203 | 0 | 87 | 40 | 149 | 0 | 90 | 120 | 125 | 382 | 85 | 82 | 51 | 0 | 293 | 17 | 54 | 98 | 96 | 90 | 370 | 17 | 0 | 54 | 34 | 0 | 35 | 0 | 97 | 35 | 0 | 94 | 0 | 0 | 2 |  | 913 | 0 | 205 | 0 | 63 | 0 | 0 | 0 | 38 | 60 | 8 | 169 | 33 | 16 | 0 | 0 | 0 | 0 | 0 | 88 | 28 | 34 | 40 | 8 | 35 | 18 | 0 | 8 | 74 | 0 | 250 | 15 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 371 | 30 | 0 | 50 | 105 | 48 | 0 | 0 | 55 | 610 | 0 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 325 | 0 | 150 | 759 | 0 | 0 |  | 8793 | 5239 | 14032 | 4444 | 913 | 2277 | 243 | 3156 | 2168 | 25 | 15 | 655 | 134 | 0 | 2 | 685.69 | 0
20:00 | 0 | 0 | 130 | 180 | 0 | 22 | 0 | 401 | 335 |  | 0 | 410 | 308 | 17 | 82 | 15 | 190 | 0 | 188 | 18 | 16 | 150 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 20 | 23 | 33 | 30 | 40 | 0 | 25 | 0 | 100 | 0 | 25 | 221 | 0 | 0 | 0 |  | 12 | 62 | 51 | 55 | 0 | 21 | 0 | 14 | 0 | 0 | 0 | 305 | 310 | 202 | 175 | 0 | 40 | 0 | 0 | 51 | 0 | 37 | 51 | 15 | 11 | 32 | 19 | 136 | 78 | 0 | 19 | 0 | 43 | 39 | 50 | 47 | 80 | 0 | 55 | 80 | 0 | 190 | 0 | 0 | 10 | 290 | 16 | 11 | 0 | 260 | 203 | 0 | 88 | 40 | 149 | 0 | 90 | 120 | 122 | 370 | 85 | 82 | 51 | 0 | 300 | 17 | 54 | 99 | 95 | 90 | 370 | 17 | 0 | 54 | 34 | 0 | 35 | 0 | 97 | 34 | 0 | 163 | 0 | 0 | 4 |  | 913 | 0 | 205 | 0 | 64 | 0 | 0 | 0 | 34 | 76 | 8 | 169 | 32 | 16 | 0 | 0 | 0 | 0 | 0 | 88 | 28 | 34 | 40 | 8 | 35 | 18 | 0 | 8 | 74 | 0 | 250 | 15 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 372 | 31 | 0 | 50 | 105 | 48 | 0 | 0 | 55 | 610 | 0 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 324 | 0 | 150 | 854 | 0 | 0 |  | 8838 | 5350 | 14188 | 4416 | 913 | 2294 | 243 | 3144 | 2262 | 25 | 15 | 736 | 136 | 0 | 4 | 679.96 | 72.82
21:00 | 0 | 0 | 130 | 180 | 0 | 22 | 0 | 399 | 322 |  | 0 | 450 | 288 | 18 | 82 | 15 | 190 | 0 | 190 | 18 | 16 | 150 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 20 | 23 | 33 | 31 | 40 | 0 | 25 | 0 | 100 | 0 | 25 | 222 | 0 | 0 | 0 |  | 12 | 62 | 51 | 55 | 0 | 20 | 0 | 24 | 0 | 0 | 0 | 305 | 305 | 203 | 175 | 0 | 40 | 0 | 0 | 51 | 0 | 39 | 43 | 11 | 11 | 33 | 19 | 136 | 80 | 0 | 19 | 0 | 43 | 39 | 50 | 47 | 112 | 0 | 55 | 81 | 0 | 189 | 0 | 0 | 10 | 320 | 16 | 11 | 0 | 260 | 300 | 0 | 88 | 51 | 149 | 0 | 90 | 120 | 132 | 368 | 85 | 82 | 51 | 0 | 300 | 17 | 54 | 98 | 97 | 90 | 380 | 17 | 0 | 54 | 34 | 0 | 35 | 0 | 97 | 34 | 0 | 163 | 0 | 0 | 1 |  | 913 | 0 | 205 | 0 | 63 | 0 | 0 | 0 | 34 | 81 | 8 | 171 | 35 | 16 | 0 | 0 | 0 | 30 | 0 | 88 | 28 | 34 | 40 | 8 | 35 | 20 | 0 | 8 | 74 | 0 | 250 | 12 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 377 | 35 | 0 | 50 | 105 | 48 | 0 | 0 | 55 | 622 | 0 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 323 | 0 | 150 | 926 | 0 | 0 |  | 9032 | 5479 | 14511 | 4421 | 913 | 2384 | 351 | 3150 | 2345 | 25 | 12 | 773 | 136 | 0 | 1 | 466.995 | 72.82
22:00 | 0 | 0 | 130 | 180 | 0 | 22 | 0 | 403 | 322 |  | 0 | 450 | 310 | 17 | 82 | 15 | 180 | 0 | 188 | 18 | 16 | 150 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 20 | 24 | 33 | 31 | 40 | 0 | 25 | 0 | 100 | 0 | 25 | 221 | 0 | 0 | 0 |  | 12 | 54 | 51 | 55 | 0 | 40 | 0 | 26 | 0 | 0 | 0 | 330 | 330 | 202 | 185 | 0 | 41 | 0 | 0 | 51 | 0 | 40 | 43 | 17 | 11 | 33 | 20 | 150 | 81 | 0 | 19 | 0 | 43 | 39 | 50 | 48 | 112 | 0 | 55 | 81 | 0 | 188 | 0 | 0 | 10 | 315 | 16 | 11 | 0 | 260 | 300 | 0 | 88 | 93 | 149 | 0 | 90 | 120 | 139 | 376 | 85 | 82 | 51 | 0 | 122 | 17 | 54 | 98 | 89 | 90 | 375 | 17 | 0 | 54 | 34 | 0 | 35 | 0 | 97 | 34 | 0 | 18 | 0 | 0 | 1 |  | 798 | 0 | 210 | 0 | 63 | 0 | 0 | 0 | 34 | 75 | 8 | 171 | 35 | 16 | 0 | 0 | 0 | 30 | 0 | 80 | 28 | 34 | 40 | 8 | 35 | 20 | 0 | 8 | 73 | 0 | 250 | 16 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 302 | 35 | 0 | 50 | 105 | 48 | 0 | 0 | 55 | 622 | 0 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 323 | 0 | 150 | 907 | 0 | 0 |  | 8838 | 5267 | 14105 | 4481 | 798 | 2339 | 393 | 2970 | 2325 | 25 | 16 | 607 | 150 | 0 | 1 | 759.225 | 72.81
23:00 | 0 | 0 | 130 | 180 | 0 | 22 | 0 | 401 | 321 |  | 0 | 450 | 275 | 8 | 82 | 15 | 180 | 0 | 196 | 10 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 20 | 25 | 33 | 31 | 40 | 0 | 0 | 0 | 100 | 0 | 8 | 226 | 0 | 0 | 0 |  | 12 | 54 | 51 | 55 | 0 | 40 | 0 | 29 | 0 | 0 | 0 | 300 | 305 | 206 | 185 | 0 | 39 | 0 | 0 | 51 | 0 | 40 | 43 | 17 | 11 | 33 | 20 | 150 | 88 | 0 | 19 | 0 | 43 | 39 | 50 | 48 | 112 | 0 | 55 | 81 | 0 | 188 | 0 | 0 | 10 | 310 | 16 | 8 | 0 | 255 | 300 | 0 | 69 | 94 | 96 | 0 | 90 | 120 | 137 | 368 | 18 | 82 | 41 | 0 | 87 | 17 | 54 | 98 | 52 | 63 | 385 | 17 | 0 | 17 | 34 | 0 | 35 | 0 | 85 | 34 | 0 | 18 | 0 | 0 | 0 |  | 777 | 0 | 205 | 0 | 63 | 0 | 0 | 0 | 34 | 75 | 8 | 171 | 36 | 16 | 0 | 0 | 0 | 30 | 0 | 80 | 28 | 34 | 40 | 8 | 35 | 20 | 0 | 8 | 73 | 0 | 216 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 301 | 35 | 0 | 35 | 105 | 35 | 0 | 0 | 35 | 622 | 0 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 323 | 0 | 150 | 901 | 0 | 0 |  | 8292 | 5139 | 13431 | 4443 | 777 | 2301 | 394 | 2576 | 2285 | 0 | 0 | 505 | 150 | 0 | 0 | 1355.145 | 72.81
24:00 | 0 | 0 | 130 | 180 | 0 | 22 | 0 | 402 | 321 |  | 0 | 450 | 300 | 9 | 82 | 15 | 180 | 0 | 191 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 20 | 25 | 33 | 31 | 8 | 0 | 0 | 0 | 100 | 0 | 8 | 226 | 0 | 0 | 0 |  | 12 | 53 | 51 | 55 | 0 | 40 | 0 | 34 | 0 | 0 | 0 | 305 | 310 | 204 | 185 | 0 | 39 | 0 | 0 | 51 | 0 | 40 | 52 | 17 | 11 | 33 | 20 | 166 | 87 | 0 | 19 | 0 | 43 | 39 | 50 | 48 | 112 | 0 | 56 | 81 | 0 | 188 | 0 | 0 | 10 | 305 | 16 | 8 | 0 | 148 | 303 | 0 | 69 | 95 | 21 | 0 | 50 | 75 | 68 | 368 | 18 | 82 | 32 | 0 | 88 | 17 | 54 | 98 | 10 | 38 | 355 | 0 | 0 | 17 | 34 | 0 | 35 | 0 | 55 | 17 | 0 | 18 | 0 | 0 | 0 |  | 777 | 0 | 235 | 0 | 63 | 0 | 0 | 0 | 34 | 70 | 8 | 172 | 36 | 16 | 0 | 0 | 0 | 23 | 0 | 80 | 28 | 34 | 32 | 0 | 35 | 21 | 0 | 8 | 73 | 0 | 250 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 301 | 35 | 0 | 35 | 85 | 34 | 0 | 0 | 35 | 622 | 0 | 0 | 150 | 0 | 0 | 55 | 0 | 0 | 322 | 0 | 150 | 910 | 0 | 0 |  | 7777 | 5115 | 12892 | 4459 | 777 | 2327 | 398 | 1954 | 2327 | 0 | 0 | 484 | 166 | 0 | 0 | 1726.64 | 72.81
KWH | 0 | 0 | 3190219 | 4378500 | 0 | 518545 | 0 | 9658370 | 7704000 |  | 0 | 10086500 | 7026793 | 232320 | 1738967 | 120115 | 4277165 | 0 | 2985000 | 244800 | 225792 | 1602720 | 71869 | 0 | 0 | 0 | 127800 | 469277 | 462363 | 409140 | 460000 | 487260 | 822300 | 744200 | 370080 | 0 | 304440 | 0 | 2500000 | 0 | 322380 | 5124848 | 0 | 0 | 0 |  | 263040 | 1295232 | 1142287 | 1170480 | 0 | 392160 | 0 | 444960 | 0 | 0 | 0 | 7782100 | 7429000 | 4900000 | 4048000 | 0 | 894384 | 0 | 0 | 1152832 | 0 | 783536 | 739987 | 307332 | 237960 | 793100 | 463850 | 3384960 | 1378560 | 0 | 398772 | 15500 | 1019000 | 892440 | 1189800 | 289368 | 2357918 | 0 | 1262496 | 1886400 | 0 | 3911250 | 0 | 0 | 250200 | 7357000 | 354000 | 193248 | 0 | 2358545 | 4003561 | 0 | 1720800 | 1313700 | 1041408 | 111105 | 1147200 | 1320000 | 903272 | 8844000 | 708000 | 1851350 | 643999 | 33238 | 2406218 | 448341 | 1346540 | 1610820 | 755160 | 1123200 | 8738600 | 237120 | 357670 | 581760 | 839291 | 0 | 849600 | 236230 | 984960 | 559800 | 0 | 729309 | 0 | 0 | 17424 |  | 21612363 | 0 | 4780224 | 0 | 856320 | 0 | 0 | 0 | 369120 | 1327488 | 47625 | 4121613 | 646365 | 311520 | 0 | 0 | 0 | 192048 | 0 | 1554888 | 541900 | 770592 | 621806 | 40512 | 786600 | 414960 | 0 | 176094 | 1686109 | 0 | 5996100 | 46000 | 0 | 4263873 | 0 | 0 | 0 | 0 | 0 | 4208409 | 0 | 7798254 | 571680 | 0 | 967008 | 2463696 | 819072 | 0 | 59866 | 843456 | 15624200 | 0 | 0 | 1226400 | 38700 | 722880 | 1022208 | 0 | 0 | 7730909 | 234516 | 3628400 | 21236364 | 1506030 | 0 |  | 174869136 | 121866168 | 296735304 | 102387307 | 21612363 | 53171895 | 5317261 | 40870803 | 55902082 | 304440 | 46000 | 10405034 | 3384960 | 3315735 | 17424 | 0
Fuel Cost | 0 | 0 | 4657719.74 | 6523965 | 0 | 689664.85 | 0 | 10141288.5 | 8320320 |  | 0 | 10994285 | 7799740.23 | 2597337.6 | 23041312.75 | 1591523.75 | 4790424.8 | 0 | 5223750 | 3578976 | 3176893.44 | 25980091.2 | 662632.18 | 0 | 0 | 0 | 1625616 | 6335239.5 | 6200287.83 | 306855 | 345000 | 0 | 0 | 0 | 6295060.8 | 0 | 82198.8 | 0 | 4725000 | 0 | 5270913 | 5329841.92 | 0 | 0 | 0 |  | 3432672 | 21604469.76 | 19441724.74 | 15813184.8 | 0 | 4537291.2 | 0 | 1481716.8 | 0 | 0 | 0 | 8638131 | 8097610 | 5684000 | 5221920 | 0 | 1010653.92 | 0 | 0 | 1925229.44 | 0 | 13531666.72 | 9952825.15 | 421044.84 | 178470 | 1387925 | 347887.5 | 24304012.8 | 1502630.4 | 0 | 542329.92 | 247070 | 1396030 | 1178020.8 | 2070252 | 500606.64 | 2711605.7 | 0 | 2449242.24 | 4300992 | 0 | 3950362.5 | 0 | 0 | 495396 | 7357000 | 265500 | 146868.48 | 0 | 32194139.25 | 83914638.56 | 0 | 23196384 | 27154179 | 14423500.8 | 1298817.45 | 11839104 | 18031200 | 11986419.44 | 8136480 | 8609280 | 26770521 | 8146587.35 | 0 | 28248999.32 | 4882433.49 | 14313720.2 | 21858827.4 | 9734012.4 | 13231296 | 8039512 | 3070704 | 5168331.5 | 7382534.4 | 9551131.58 | 0 | 11095776 | 2822948.5 | 14744851.2 | 7372566 | 0 | 0 | 0 | 0 | 0 |  | 64837089 | 0 | 5353850.88 | 0 | 8914291.2 | 0 | 0 | 0 | 6647851.2 | 23894784 | 684371.25 | 4616206.56 | 1253948.1 | 3395568 | 0 | 0 | 0 | 3220644.96 | 0 | 24318448.32 | 4172630 | 12761003.52 | 10514739.46 | 552178.56 | 13269942 | 858967.2 | 0 | 133303.158 | 9796293.29 | 0 | 31719369 | 1932920 | 0 | 4946092.68 | 0 | 0 | 0 | 0 | 0 | 4881754.44 | 0 | 7720271.46 | 7683379.2 | 0 | 11439704.64 | 35600407.2 | 10402214.4 | 0 | 661519.3 | 10239555.84 | 140774042 | 0 | 0 | 9075360 | 437697 | 8479382.4 | 15670448.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 769631175.08 | 500860228.858 | 1270491403.938 | 115347751.278 | 64837089 | 63701915.42 | 111068817.56 | 525386866.28 | 182289704.29 | 82198.8 | 1932920 | 162424362.36 | 24304012.8 | 19115766.15 | 0 | 0
Yesterday Day Peak | 0 | 0 | 130 | 190 | 0 | 22 | 0 | 386 | 327 |  | 0 | 450 | 296 | 8 | 70 | 0 | 185 | 0 | 95 | 9 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 22 | 20 | 18 | 33 | 28 | 8 | 0 | 25 | 0 | 100 | 0 | 8 | 215 | 0 | 0 | 0 |  | 3 | 45 | 47 | 44 | 0 | 9 | 0 | 2 | 0 | 0 | 0 | 280 | 270 | 201 | 167 | 0 | 34 | 0 | 0 | 51 | 0 | 30 | 8 | 16 | 11 | 33 | 21 | 122 | 33 | 0 | 16 | 2 | 42 | 39 | 50 | 0 | 112 | 0 | 54 | 80 | 0 | 190 | 0 | 0 | 10 | 310 | 16 | 11 | 0 | 55 | 20 | 0 | 68 | 23 | 17 | 19 | 38 | 34 | 10 | 369 | 19 | 70 | 17 | 5 | 69 | 17 | 54 | 17 | 34 | 38 | 350 | 17 | 35 | 17 | 34 | 0 | 35 | 32 | 22 | 17 | 0 | 18 | 0 | 0 | 1 |  | 911 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 168 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 46 | 21 | 34 | 40 | 0 | 35 | 14 | 0 | 8 | 72 | 0 | 250 | 0 | 0 | 141 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 346 | 17 | 0 | 35 | 105 | 32 | 0 | 7 | 35 | 622 | 0 | 0 | 17 | 5 | 93 | 35 | 0 | 0 | 324 | 33 | 150 | 919 | 196 | 0 |  | 11850 | DayPeak
Yesterday Evening Peak | 0 | 0 | 130 | 180 | 0 | 22 | 0 | 399 | 322 | 0 | 0 | 450 | 288 | 18 | 82 | 15 | 190 | 0 | 190 | 18 | 16 | 150 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 20 | 23 | 33 | 31 | 40 | 0 | 25 | 0 | 100 | 0 | 25 | 222 | 0 | 0 | 0 | 0 | 12 | 62 | 51 | 55 | 0 | 20 | 0 | 24 | 0 | 0 | 0 | 305 | 305 | 203 | 175 | 0 | 40 | 0 | 0 | 51 | 0 | 39 | 43 | 11 | 11 | 33 | 19 | 136 | 80 | 0 | 19 | 0 | 43 | 39 | 50 | 47 | 112 | 0 | 55 | 81 | 0 | 189 | 0 | 0 | 10 | 320 | 16 | 11 | 0 | 260 | 300 | 0 | 88 | 51 | 149 | 0 | 90 | 120 | 132 | 368 | 85 | 82 | 51 | 0 | 300 | 17 | 54 | 98 | 97 | 90 | 380 | 17 | 0 | 54 | 34 | 0 | 35 | 0 | 97 | 34 | 0 | 163 | 0 | 0 | 1 |  | 913 | 0 | 205 | 0 | 63 | 0 | 0 | 0 | 34 | 81 | 8 | 171 | 35 | 16 | 0 | 0 | 0 | 30 | 0 | 88 | 28 | 34 | 40 | 8 | 35 | 20 | 0 | 8 | 74 | 0 | 250 | 12 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 377 | 35 | 0 | 50 | 105 | 48 | 0 | 0 | 55 | 622 | 0 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 323 | 0 | 150 | 926 | 0 | 0 |  | 14511 | EvPeak
Forecast for Evening | 0 | 0 | 130 | 190 | 0 | 22 | 0 | 400 | 330 | 0 | 0 | 450 | 300 | 18 | 85 | 15 | 210 | 0 | 150 | 16 | 16 | 150 | 12 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 20 | 22 | 33 | 33 | 50 | 0 | 25 | 0 | 100 | 0 | 25 | 225 |  | 0 | 0 | 0 | 12 | 64 | 68 | 80 | 16 | 40 | 10 | 20 | 0 | 0 | 0 | 320 | 320 | 210 | 175 | 0 | 43 | 0 | 0 | 51 | 0 | 40 | 52 | 16 | 11 | 33 | 21 | 152 | 90 | 0 | 19 | 0 | 43 | 40 | 50 | 44 | 112 | 0 | 60 | 84 | 0 | 202 | 0 | 0 | 10 | 300 | 16 | 11 | 0 | 300 | 300 | 0 | 88 | 100 | 149 | 0 | 90 | 120 | 150 | 400 | 85 | 88 | 51 | 0 | 300 | 17 | 54 | 114 | 105 | 90 | 400 | 17 | 0 | 54 | 34 | 0 | 35 |  | 115 | 35 | 0 | 163 |  | 0 |  |  | 930 | 0 | 310 |  | 83 | 0 | 0 | 0 | 40 | 80 | 40 | 175 | 35 | 16 | 0 | 0 | 0 | 30 | 35 | 90 | 28 | 34 | 40 | 8 | 35 | 22 | 0 | 8 | 74 | 0 | 250 | 0 | 0 | 210 |  | 0 | 0 | 0 | 0 | 210 | 0 | 200 | 55 | 0 | 50 | 105 | 49 | 0 | 0 | 55 | 622 | 0 |  | 150 |  |  | 115 | 0 |  | 330 |  | 150 | 902 |  | 0
Forecast for Day | 0 | 0 | 130 | 190 | 0 | 22 | 0 | 400 | 330 | 0 | 0 | 450 | 300 | 8 | 85 | 15 | 210 | 0 | 130 | 8 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 22 | 20 | 22 | 33 | 33 | 8 | 0 | 25 | 0 | 100 | 0 | 8 | 225 |  | 0 | 0 | 0 | 12 | 50 | 51 | 45 | 0 | 18 | 10 | 5 | 0 | 0 | 0 | 310 | 310 | 210 | 175 | 0 | 43 | 0 | 0 | 51 | 0 | 40 | 16 | 16 | 11 | 33 | 21 | 129 | 45 | 0 | 19 | 1.6 | 43 | 40 | 50 | 44 | 112 | 0 | 60 | 84 | 0 | 200 | 0 | 0 | 10 | 300 | 16 | 11 | 0 | 296 | 300 | 0 | 68 | 50 | 17 | 20 | 50 | 34 | 13 | 400 | 18 | 88 | 17 | 5 | 87 | 17 | 54 | 100 | 27 | 38 | 400 | 17 | 50 | 17 | 34 | 0 | 35 | 30 | 18 | 17 | 0 | 18 |  | 0 |  |  | 930 | 0 | 310 | 0 | 62 | 0 | 0 | 0 | 22 | 60 | 8 | 175 | 23 | 16 | 0 | 0 | 0 | 25 | 0 | 80 | 28 | 34 | 40 | 0 | 35 | 22 | 0 | 8 | 71 | 0 | 250 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 17 | 0 | 35 | 105 | 35 | 0 | 8 | 35 | 622 | 0 |  | 17 | 6 | 100 | 74 | 0 |  | 330 | 30 | 150 | 902 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 130 | 180 | 0 | 22 | 0 | 407 | 202 | 0 | 0 | 450 | 275 | 9 | 85 | 0 | 170 | 0 | 133 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 20 | 25 | 33 | 32 | 8 | 0 | 0 | 0 | 100 | 0 | 8 | 225 | 0 | 0 | 0 | 0 | 12 | 45 | 51 | 44 | 0 | 6 | 0 | 7 | 0 | 0 | 0 | 285 | 270 | 181 | 184 | 0 | 37 | 0 | 0 | 51 | 0 | 37 | 43 | 15 | 8 | 25 | 17 | 154 | 47 | 0 | 19 | 1 | 43 | 39 | 50 | 49 | 112 | 0 | 59 | 81 | 0 | 188 | 0 | 0 | 10 | 270 | 16 | 8 | 0 | 296 | 0 | 0 | 68 | 25 | 17 | 6 | 38 | 17 | 12 | 342 | 18 | 70 | 17 | 2 | 69 | 17 | 54 | 98 | 9 | 38 | 360 | 0 | 24 | 17 | 34 | 0 | 35 | 15 | 18 | 17 | 0 | 18 | 0 | 0 | 0 | 0 | 912 | 0 | 310 | 0 | 62 | 0 | 0 | 0 | 21 | 32 | 0 | 169 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 21 | 34 | 24 | 0 | 35 | 22 | 0 | 8 | 71 | 0 | 240 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 17 | 0 | 35 | 67 | 24 | 0 | 4 | 35 | 622 | 0 | 0 | 17 | 2 | 39 | 0 | 0 | 0 | 323 | 14 | 150 | 902 | 94 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
292.3904
| Minimum Generation |  | 11306 | 7:00
| Highest Generation |  | 14511 | 21:00
| Day Peak Generation |  | 11850 | 12:00
| Evening Peak Generation |  | 14511 | 21:00
| HVDC Max Flow |  | 913 | 10:00
| HVDC EvPeak Flow |  | 913 | 21:00
| Load factor L.F |  | 85.2% | [163 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-05-31
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-05-30 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 11850 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 11312
Evening Peak Generation : |  |  | 14511 | MW Hour : | 21:00 | Available Max Generation : |  | 15031
E.P. Demand (at gen end) : |  |  | 15000 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 15200
Maximum Generation : |  |  | 14511 | MW Hour : | 21:00 | Reserve(Generation end) |  | -
Total Gen. (MKWH) : |  |  | 296.7353 | System Load Factor : | 85.2% | Load Shed : |  | 156
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 660 | MW at | 22:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-05-31
Actual : |  | 72.79 | Ft.(MSL) , | Rule curve : | 76.2 | Ft.( MSL )
Gas Consumed : |  | Total = | 1212.08 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 179049666.698
: |  |  | Coal : | 182289704.29 | Oil : | 800812966.2 | Total : | 1162152337.188
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 53 | 1272:00 | 4534.2896 |  |  | 40 | 0.8822%
Chittagong Area |  | 45 | 1080:00 | 1245.692 |  |  | 22 | 1.766%
Khulna Area |  | 73 | 1752:00 | 1744.9061 |  |  | 21 | 1.204%
Rajshahi Area |  | 65 | 1560:00 | 1516.5797 |  |  | 20 | 1.319%
Cumilla Area |  | 95 | 2280:00 | 1247.9061 |  |  | 15 | 1.202%
Mymensingh Area |  | 63 | 1512:00 | 928.0993 |  |  | 14 | 1.508%
Sylhet Area |  | 0 | 0:00 | 520.2585 |  |  | 10 | 1.922%
Barisal Area |  | 43 | 1032:00 | 433.5457 |  |  | 0 | 0%
Rangpur Area |  | 30 | 720:00 | 847.94 |  |  | 14 | 1.651%
Total |  | 467 |  | 13019.2171 |  |  | 156
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,7
3) Bhula Nuton Biddut
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:07 | 08:27 | Ashuganj 230/132/33kV S/S T-3 Kalabagan LT Tripped showing O/C, E/F(50), O/C, E/F(67), A,B-phase relays Due to
Over Current, Earth fault
08:07 | 08:26 | Ashuganj 230/132/33kV S/S T-3 Kalabagan HT Tripped showing Lock out Realy relays.
08:10 | 10:12 | Dummy S/S 404T LT Scheduled S/D Due to yearly maintenance (updated)
| 08:11 | Kushtia 132/33kV S/S T2 HT is restored.
08:12 | 10:10 | Dummy S/S 404T HT Scheduled S/D Due to yearly maintenance
| 08:12 | Kushtia 132/33kV S/S T2 LT is restored.
08:17 | 20:52 | Gollamari 132/33kV S/S E01 Gollamari-Gopalgonj Line - 1 Project Work S/D Due to PW
08:18 | 20:51 | Gopalganj 132/33kV S/S Gallamari-1 Scheduled S/D Due to Aldc
| 08:40 | Lalmonirhat 132/33kV S/S Transformer T-1 425T LT is restored.
| 08:40 | Lalmonirhat 132/33kV S/S Transformer T-1 425T HT is restored.
08:49 | 19:38 | Fatullah 132/33kV S/S 132 kV Hasnabad Scheduled S/D Due to Removal of LILO between Hasnabad and Fatullah Grid at
Agreeko Powerpalnt. Shutdown was taken by NLDC.
08:49 |  | Fatullah-Brahmongaon ckt SD for D/W
08:54 |  | Brahmongaon(Aggreko)-Hasnabad 132 kV Ckt-2 Scheduled S/D from Hasnabad 132/33kV end Due to Remove Connection
Hasnabad -Aggreko Brahmangoan power station line at a time connect this line with Fatullah 132/33 kv Grid Sub-Station.
09:30 | 10:40 | Lalbag 132/33kV S/S Tr-Load LT Forced S/D Due to Maintenance
09:32 |  | Sonargaon 132/33kV S/S Tr-2 HT Tripped showing Main Relay: General Trip,Trafo Trabl Trip, No Voltage, Backup | [5 empty] | 36.0MW load interrup.
Protection :General Trip Diff Trip,Diff R,Diff Y relays Due to Auxiliary transformer -01-Trip, Due to Bird drop in
Fuse (Aux -01). R,Y phase Fuse loop out. Under Transformer -01.
09:32 | 10:58 | Sonargaon 132/33kV S/S Tr-1 LT Tripped showing DiR /C & E/F Fault Relay. relays Due to Auxiliary -01 trip due to Bird | [5 empty] | 31.0MW load interrup.
drop in Fuse, Fuse Phase R,Y loop out.
09:51 | 10:45 | Natore-Rajshahi 132kV Ckt-1 Scheduled S/D from Rajshahi 132/33kV end Due to Oil Leakage Maintenance Work.
10:09 |  | Matarbari PP 400/11 kv, 114 MVA, Start Up TR. (SUT) was switched on.
10:11 |  | Kazla-Maniknagar 132kV ckt-1 Tripped from Kazla 132/33kV end showing Over current relays Due to Unknown | [5 empty] | 45.0MW load interrup.
10:30 | 10:42 | Kamrangirchar-Zigatola 132kV ckt-1 Tripped from Dummy end showing distance relays Due to thundering
10:34 | 11:12 | Tangail 132/33kV S/S Tr-4 LT Forced S/D Due to Work on 33kv shakhipur feeder
10:35 | 11:12 | Tangail 132/33kV S/S Tr-4 HT Forced S/D Due to Work on 33kv shakhipur feeder
11:32 | 14:17 | Gollamari 132/33kV S/S Tr-2 LT Project Work S/D Due to SAS
11:33 | 14:16 | Gollamari 132/33kV S/S Tr-2 HT Project Work S/D Due to SAS
12:00 |  | Day Peak Gen. 11850 MW
12:29 |  | Ullon GT1 was switched on
12:46 | 12:51 | Lalbag 132/33kV S/S Tr-Load LT Tripped showing 86 relays Due to Overload | [5 empty] | 45.0MW load interrup.
13:40 |  | Siddhirganj GT2 was sync.
13:40 |  | Siddirganj GT-2 was synch.
13:56 | 14:23 | Sonargaon 132/33kV S/S Tr-1 LT Tripped showing Dir O/C trip relays Due to Over load | [5 empty] | 70.0MW load interrup.
21:00 |  | Evening Peak Generation = 14,511MW
04:17 | 04:58 | Kulaura 132/33kV S/S TR-2 LT Tripped showing over current protection relay relays Due to Due to 33kV comolganj feeder fault | [5 empty] | 30.0MW load interrup.
04:17 | 04:58 | Kulaura 132/33kV S/S TR-1 LT Tripped showing over current protection relay relays Due to Due to 33kV comolganj feeder fault | [5 empty] | 30.0MW load interrup.
05:31 | 06:48 | Khulshi 132/33kV S/S 405T (T1) HT Forced S/D Due to Due to red hot detection
05:31 | 06:48 | Khulshi 132/33kV S/S 405T (T1) LT Forced S/D Due to Due to red hot detection
05:49 |  | Sirajgonj unit-4 ST & GT were s/d at 05:49 hrs & 06:08 hrs due to red hot Maint. | [5 empty] | 300MW generation interrup.
06:05 |  | Maniknagar-Siddhirganj 230kV Ckt-2 Project Work S/D from Maniknagar 230/132kV end Due to For new tower re-routing
work & Line bypass work. and from Siddhirganj 230/132kV end Due to Devolopment Work
06:25 | 07:57 | Sylhet 132/33kV S/S T4 LT Scheduled S/D Due to Maintenance and Replacement of T9 X-Former PDB
06:26 | 07:57 | Sylhet 132/33kV S/S T4 HT Scheduled S/D Due to Maintenance and Replacement of T9 X-Former PDB
06:52 |  | Kodda 132/33kV S/S Tr-4 (436T) LT Scheduled S/D | [5 empty] | 50.0MW load interrup.
06:52 |  | Kodda 132/33kV S/S Tr-3 (426T) LT Scheduled S/D | [5 empty] | 50.0MW load interrup.
06:54 |  | Kodda 132/33kV S/S Tr-3 (426T) HT Scheduled S/D Due to None | [5 empty] | 50.0MW load interrup.
06:55 |  | Kodda 132/33kV S/S Tr-4 (436T) HT Scheduled S/D | [5 empty] | 50.0MW load interrup.
07:00 |  | Minimum generation: 11312 MW.
07:14 |  | Jamalpur 132/33kV S/S T-3 HT Scheduled S/D
07:14 |  | Jamalpur 132/33kV S/S T-3 LT Scheduled S/D
07:24 |  | Saidpur 132/33kV S/S TR-5 (434T) LT Scheduled S/D Due to 33Kv Bus Coupler DS Maintenance.
07:25 |  | Saidpur 132/33kV S/S TR-5 (434T) HT Scheduled S/D Due to 33Kv Bus Coupler DS Maintenance.
07:43 |  | Sirajgonj 230 S/S SNWPCL (Unit-04) Forced S/D Due to Bay ds Yellow Phase Red hot.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-05-30 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 130 | 3190219 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4378500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 22 | 518545 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 399 | 9658370
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 322 | 7704000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10086500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 18 | 232320 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 288 | 7026793 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 82 | 1738967 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 120115 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 20 | 0 | 71869
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 409140
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 190 | 2985000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 18 | 244800 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 190 | 4277165 | ST Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 16 | 225792 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 127800 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1602720
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 469277
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 462363 | Fuel shortage
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 43 | 947260 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 822300
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 31 | 744200
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 40 | 370080 | Engine problem
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 260 | 2358545 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 300 | 4003561
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 51 | 1313700 | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1041408
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 82 | 1851350 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 237120 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 581760 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 236230
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 34 | 559800 | Fuel shortage
| Dhaka area Total |  |  |  | 5867 | 3693 | 70597569
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2500000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 322380
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 111105
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 20 | 392160 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 25 | 304440 | Low Water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 222 | 5124848
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 643999 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 62 | 1295232 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 1142287 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 55 | 1170480 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 1147200 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 24 | 444960
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 33238
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 300 | 2406218
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 448341 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 54 | 1346540 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 90 | 1123200 | Engine problem
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 34 | 839291 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 163 | 729309
| SS Power I |  | SS Power | 0 | 0 | 0 | 0 | On test.
| Cox's Bazar Wind |  | IPP | 66 | 0 | 1 | 17424 | On test.
| Chattogram area Total |  |  |  | 2545 | 1384 | 21542652
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 203 | 4900000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 305 | 7782100 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7429000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 40 | 894384 | Machine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 175 | 4048000 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1152832
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 132 | 903272 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 39 | 783536 | Machine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 120 | 1320000 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 11 | 307332 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 237960
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 136 | 3384960
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 793100
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 739987
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 19 | 463850 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 98 | 1610820 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 97 | 755160 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 849600 | Fuel shortage
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 97 | 984960 | Fuel shortage
| Cumilla Area Total |  |  |  | 3096 | 1950 | 39340853
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 80 | 1378560 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 398772 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15500
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 88 | 1720800 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 85 | 708000 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 357670
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 263040 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 284 | 4842342
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1019000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 39 | 892440 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2357918 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1189800
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 47 | 289368
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 193248
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 55 | 1262496
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1886400
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 189 | 3911250 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 354000 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7357000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 368 | 8844000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 250200
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 380 | 8738600
| Sylhet Area Total |  |  |  | 2427 | 1721 | 38545720
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 913 | 21612363
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 63 | 856320 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 34 | 369120 | Fuel shortage
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 81 | 1327488 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 205 | 4780224 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 47625 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 571680 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 2463696
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 722880
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 323 | 7730909 | Coal shortage.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 2901 | 1767 | 40482305
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 311520 | Fuel shortage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 35 | 646365 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 171 | 4121613 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 622 | 15624200 | Coal shortage.
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 0 | 0 | Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1226400
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 150 | 3628400 | Coal shortage.
| Barisal Area Total |  |  |  | 2265 | 1144 | 25558498
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 30 | 192048 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 28 | 28 | 541900
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 770592 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 621806 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 194 | 4263873 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 176 | 4208409 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 377 | 7798254 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 786600 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 20 | 414960
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 176094 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 40512 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 88 | 1554888 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 967008 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 55 | 843456 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 38700
| Adani Power Jharkhanda Ltd |  | Import | 748*1 | 748 | 926 | 21236364 | On test.
| Rajshahi Area Total |  |  |  | 2905 | 2069 | 44455464
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 74 | 1686109
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 250 | 5996100
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 12 | 46000
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 48 | 819072 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 59866
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1022208
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 234516
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 1506030
| Rangpur Area Total |  |  |  | 750 | 499 | 11369901
| Total |  |  |  | 23370 | 14511 | 296735304
| Eastern Grid Total |  |  |  | 14549 | 9032 | 174869136
| Western Grid Total |  |  |  | 8821 | 5479 | 121866168
| National Grid Total |  |  |  | 23370 | 14511 | 296735304
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-05-30
| (a) ENTIRE EASTERN GRID : |  | 9515.85 | MW | (b) ENTIRE WESTERN GRID : |  | 4332.8 | MW
| i) Dhaka area |  | 5104.85 | MW | i) Khulna area |  | 1669.8 | MW
| ii) Chittagong area |  | 1427 | MW | ii) Rajshahi area |  | 1378 | MW
| iii) Comilla area |  | 1283 | MW | iii) Barisal area |  | 405 | MW
| iv) Mymensingh area |  | 1087 | MW | iv) Rangpur area |  | 880 | MW
| v) Sylhet area |  | 614 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 13848.65 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 23 | 21:00 | Kalurghat | 36 | 18:30 | Narshingdi | 166 | 19:00 | Shikalbaha-230 | N/A | N/A
2 | AKSML | 11.3 | 01:00 | Chowmuhani | 218 | 21:00 | Kamrangirchar | 66 | 13:00 | Natore | 133 | 20:00 | Shitalakhya | 96.5 | 16:00
3 | Aftabnagar | 55 | 17:00 | Chuadanga | 100 | 14:00 | Kaptai | N/A | N/A | Nawabganj | 52 | 21:00 | Sholosohor | 39 | 19:30
4 | Agargaon | 90 | 14:00 | Coxsbazar | 115 | 20:00 | Kazla | 166 | 06:00 | Netrakona | 136 | 21:00 | Shyampur | 150 | 01:00
5 | Agrabad | 80 | 19:30 | Cumilla(N) | 187 | 21:00 | Keranigonj | 72 | 23:00 | New | 84 | 18:30 | Siddhirganj | 120 | 21:00
6 | Amnura | 54 | 21:00 | Cumilla(S) | 168 | 00:00 | Khagrachori | 34 | 21:00 | Niamatpur | 84 | 23:00 | Sirajganj | 104 | 19:30
7 | Ashuganj | 75 | 21:00 | Daudkandi | 137 | 21:00 | Khulna | 101 | 19:00 | Noapara | 41 | 19:30 | Sonargaon | 73 | 07:00
8 | BIPTC | N/A | N/A | Dhaka | 32 | 13:00 | Khulshi | 196 | 20:00 | PHP | 9 | 18:30 | Sreemongol | 74 | 20:00
9 | BSRM | 166 | 13:00 | Dhamrai | 128 | 19:30 | Kishoreganj | 102 | 21:00 | Pabna | 110 | 19:00 | Sreepur | 61.54 | 21:00
10 | Bagerhat | 89 | 22:00 | Dhanmondi | 124.1 | 13:00 | Kodda | 282 | 19:00 | Palashbari | 130 | 21:00 | Srinagar | 48.7 | 21:00
11 | Bakulia | 115 | 20:00 | Dohazari | 92 | 20:00 | Kulaura | 48 | 21:00 | Panchagarh | 47 | 21:00 | Sunamganj | 54 | 21:00
12 | Banani | 66 | 13:00 | Dummy | 50 | 02:00 | Kurigram | 64 | 20:00 | Patuakhali | 105 | 19:30 | Sylhet | 177 | 20:00
13 | Bangabhaban | 23 | 10:00 | Faridpur | 158 | 19:00 | Kushtia | 138 | 21:00 | Payra | 20 | 01:00 | TK | 33 | 19:30
14 | Barapukuria | 66 | 20:00 | Fatullah | 66 | 23:00 | Lalbag | 88 | 20:00 | Postogola | 62 | 20:00 | Tangail | 242 | 22:00
15 | Barguna | 24 | 22:00 | Fenchuganj | 47 | 21:00 | Lalmonirhat | 44 | 00:00 | Purbachal | 23 | 19:00 | Thakurgaon | 94 | 19:30
16 | Barishal | 116 | 19:00 | Feni | 111 | 21:00 | Madanganj | 36 | 21:00 | Purbasadipur | 125 | 22:00 | Tongi | 113 | 21:00
17 | Barishal-230 | 96 | 19:00 | GPH | 92 | 00:00 | Madaripur | 103 | 22:00 | Rahanpur_I | 0 | 00:00 | Ullon | 45 | 00:00
18 | Baroaulia | 69 | 23:00 | Ghorashal | N/A | N/A | Madartek | 97.83 | 23:00 | Rahim | 40 | 13:00 | Uttara | 78 | 17:00
19 | Baroirhat | 64 | 20:00 | Goalpara | 38 | 21:00 | Madunaghat | 58 | 20:00 | Rajbari | 76 | 21:00 | UttaraNew | 57 | 23:00
20 | Bashundhara | 197 | 19:00 | Gollamari | 58 | 21:00 | Magura | 62 | 19:00 | Rajendrapur | 94 | 19:30 | Zigatola | 122 | 10:00
21 | BashundharaCement | 6 | 09:00 | Gopalganj | 99.4 | 20:00 | Mahasthangarh | 60 | 19:00 | Rajshahi | 174 | 21:00
22 | Beanibazar | 75 | 21:00 | Gulshan | 80 | 16:00 | Manikganj | 126 | 21:00 | Rajshahi-230 | 38 | 23:00
23 | Benapole | 62 | 22:00 | Halishahar | 84 | 19:30 | Maniknagar | 92 | 15:00 | Ramganj | 102 | 19:00
24 | Bhaluka | 186 | 21:00 | HaripurSBU | 155 | 21:00 | Matarbari | 38 | 20:00 | Rampur | 35 | 20:00
25 | Bhandaria | 52 | 19:30 | Hasnabad | 100 | 19:00 | Matuail | 66 | 17:00 | Rangamati | 16 | 19:00
26 | Bhangura | 40 | 20:00 | Hathazari | 83 | 21:00 | Millgate | 98 | 19:30 | Rangpur | 126 | 20:00
27 | Bheramara(GK) | 56 | 22:00 | Ishurdi | 60 | 19:00 | Mirpur | 166 | 19:00 | Ruppur | 6 | 11:00
28 | Bhulta | 270 | 21:00 | Jaldhaka | 65 | 22:00 | Mirsorai | 6 | 19:00 | SSM | 14 | 13:00
29 | Bog-Sherpur | 54 | 14:00 | Jamalpur | 153 | 20:00 | Mithapukur | 38 | 22:00 | Saidpur | 103 | 22:00
30 | Bogura | 160 | 22:00 | Jashore | 145 | 20:00 | Modern | 0 | 00:00 | Satkhira | 137 | 22:00
31 | Borhanuddin | 62 | 00:00 | Jhenaidah | 137 | 20:00 | Mogbazar | 137 | 14:00 | Satmasjid | 105 | 21:00
32 | Brahmanbaria | 151 | 22:00 | Joydebpur | 176 | 19:00 | Mongla | 30 | 11:00 | Savar | 193 | 20:00
33 | Cantonment | 148 | 18:30 | Joypurhat | 56 | 19:30 | Motijheel | 46 | 15:00 | Shahjadpur | 119 | 20:00
34 | Chandpur | 72 | 21:00 | Juldah | 27 | 07:00 | Munshiganj | 113 | 21:00 | Shahjibazar | 131 | 21:00
35 | Chandraghona | 34 | 19:30 | KSRM | 14 | 18:00 | Mymensingh | 170 | 19:30 | Shahmirpur | 50 | 00:00
36 | Chapai | 65 | 21:00 | Kabirpur | 287 | 20:00 | Naogaon | 125 | 21:00 | Shariatpur | 81 | 22:00
37 | Charsaidpur | 31 | 02:00 | Kachua | 73 | 21:00 | Narail | 58 | 19:30 | Sherpur | 140 | 19:00
38 | Chauddagram | 62 | 22:00 | Kallyanpur | 123 | 19:30 | Narinda | 71.5 | 13:00 | Shikalbaha | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-05-30 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 397 | 23:00 | 388 | 12:00 | Kaliakoir | 388 | 18:30 | 377 | 16:00
| Ashuganj | N/A | N/A | N/A | N/A | Madunaghat_I | 398 | 19:00 | 379 | 07:00
| Bhulta | 389 | 06:00 | 377 | 12:00 | Payra | 413 | 23:00 | 407 | 12:00
| Bibiana | 402 | 18:30 | 392 | 08:00 | Rahanpur_I | 418 | 07:00 | 412 | 02:00
| BIPTC | 397 | 07:00 | 387 | 16:00 | Rampal | 405 | 23:00 | 395.77 | 13:00
| Gopalganj | 404 | 06:00 | 396 | 13:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 231 | 23:00 | 224 | 12:00 | Hathazari | 232 | 21:00 | 220 | 05:00
| AKSML | 237 | 19:00 | 206 | 08:00 | Ishurdi | 235 | 23:00 | 224 | 12:00
| Aminbazar | 232 | 04:00 | 226 | 11:00 | Jhenaidah | 227 | 00:00 | 216 | 20:00
| Ashuganj | 235 | 23:00 | 227 | 12:00 | Kaliakoir | 230 | 22:00 | 223 | 15:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Keranigonj | 230 | 23:00 | 223 | 12:00
| Baghabari | 233 | 10:00 | 223 | 12:00 | Khulna(S) | 232 | 02:00 | 224 | 12:00
| Barapukuria | 220 | 18:00 | 212 | 07:00 | Madunaghat_I | 231 | 19:00 | 219 | 07:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Maniknagar | 229 | 02:00 | 223 | 12:00
| Barishal | 234 | 18:00 | 225 | 19:00 | Meghnaghat | 234 | 03:00 | 229 | 11:00
| Bheramara | 233 | 23:00 | 223 | 12:00 | Mirsorai | 233 | 19:30 | 217 | 13:00
| Bhulta | 231 | 06:00 | 224 | 12:00 | Rajshahi | 233 | 00:00 | 225 | 12:00
| Bibiana | 237 | 18:00 | 231 | 08:00 | Rampal | 232 | 00:00 | 223.93 | 13:00
| BIPTC | 234 | 23:00 | 222 | 12:00 | Rampur | N/A | N/A | N/A | N/A
| Bogura | 220 | 02:00 | 214 | 12:00 | Rampura | 229 | 07:00 | 221 | 15:00
| Borhanuddin | 233 | 06:00 | 229 | 01:00 | Shikalbaha | 233 | 19:30 | 220 | 09:00
| BSRM | 232 | 19:30 | 219 | 13:00 | Shyampur | 230 | 00:00 | 223 | 12:00
| Cumilla(N) | 230 | 19:30 | 223 | 08:00 | Siddhirganj | 230 | 04:00 | 224 | 12:00
| Fenchuganj | 242 | 06:00 | 234 | 14:00 | Sirajgonj | 234 | 03:00 | 230 | 12:00
| GPH | 231 | 21:00 | 219 | 09:00 | Sreepur | 231 | 23:00 | 225 | 12:00
| Haripur | 229 | 23:00 | 223 | 16:00 | Tongi | 226 | 00:00 | 220 | 11:00
| Hasnabad | 230 | 23:00 | 223 | 12:00
| 132 kV | KV |  | KV |  | Tongi | KV |  | KV
| Aftabnagar | 136 | 06:00 | 128 | 15:00 | Kushtia | 133 | 23:00 | 127 | 12:00
| Agargaon | 133 | 05:00 | 128 | 12:00 | Lalbag | 133 | 05:00 | 128 | 08:00
| Agrabad | 133 | 19:00 | 125 | 08:00 | Lalmonirhat | 130 | 18:00 | 120 | 01:00
| AKS | 133 | 18:30 | 125 | 07:00 | Madanganj | 134 | 23:00 | 129 | 12:00
| Aminbazar | 130 | 01:00 | 126 | 11:00 | Madaripur | 130 | 01:00 | 125 | 19:00
| Amnura | 141 | 23:00 | 130 | 19:00 | Madartek | 135 | 06:00 | 128 | 12:00
| Ashuganj | 136 | 06:00 | 133 | 08:00 | Madunaghat | 134 | 23:00 | 127 | 09:00
| Bagerhat | 132 | 00:00 | 123 | 13:00 | Magura | 133 | 23:00 | 123 | 12:00
| Bakulia | 135 | 19:00 | 126 | 08:00 | Mahasthangarh | 132 | 18:00 | 125 | 02:00
| Banani | 135 | 05:00 | 128 | 13:00 | Manikganj | 136 | 18:30 | 126 | 08:00
| Bangabhaban | 132 | 01:00 | 127 | 15:00 | Maniknagar | 133 | 04:00 | 128 | 13:00
| Barapukuria | 137 | 18:30 | 128 | 07:00 | Matarbari | 127 | 18:00 | 120 | 19:30
| Barguna | 138 | 21:00 | 133 | 01:00 | Matuail | 133 | 23:00 | 129 | 13:00
| Barishal | 137 | 18:30 | 123 | 19:00 | Millgate | 131 | 00:00 | 125 | 08:00
| Barishal-230 | 130 | 07:00 | 124 | 19:00 | Mirpur | 128 | 04:00 | 124 | 12:00
| Baroaulia | 134 | 19:00 | 125 | 08:00 | Mithapukur | 131 | 18:30 | 121 | 02:00
| Baroirhat | 134 | 19:30 | 122 | 13:00 | Modern | 135 | 19:00 | 126 | 08:00
| Bashundhara | 132 | 06:00 | 126 | 08:00 | Mogbazar | 136 | 05:00 | 130 | 13:00
| BashundharaCement | 134 | 23:00 | 129 | 12:00 | Mongla | 132 | 02:00 | 123 | 13:00
| Beanibazar | 129 | 06:00 | 125 | 15:00 | Motijheel | 133 | 06:00 | 127 | 15:00
| Benapole | 129 | 18:30 | 120 | 13:00 | Munshiganj | 134 | 19:00 | 130 | 15:00
| Bhaluka | 129 | 06:00 | 121 | 21:00 | Mymensingh | 134 | 18:30 | 106 | 01:00
| Bhandaria | 132 | 16:00 | 125 | 02:00 | Naogaon | 128 | 18:00 | 120 | 15:00
| Bhangura | 134 | 00:00 | 130 | 12:00 | Narail | 133 | 23:00 | 123 | 12:00
| Bheramara | 134 | 23:00 | 130 | 13:00 | Narshingdi | 130 | 23:00 | 124 | 03:00
| Bheramara(GK) | 134 | 00:00 | 130 | 19:00 | Natore | 132 | 00:00 | 127 | 12:00
| Bhulta | 125 | 01:00 | 121 | 12:00 | Nawabganj | 133 | 05:00 | 127 | 12:00
| Bog-Sherpur | 132 | 00:00 | 127 | 12:00 | Netrakona | 133 | 18:30 | 117 | 22:00
| Bogura | 133 | 18:00 | 128 | 20:00 | New | 133 | 03:00 | 126 | 08:00
| Bogura-230 | 133 | 01:00 | 127 | 20:00 | Niamatpur | 127 | 18:00 | 120 | 04:00
| Brahmanbaria | 132 | 06:00 | 128 | 12:00 | Noapara | 133 | 23:00 | 124 | 13:00
| Cantonment | 132 | 03:00 | 127 | 12:00 | Pabna | 133 | 23:00 | 128 | 12:00
| Chandpur | 138 | 18:00 | 118 | 07:00 | Palashbari | 130 | 18:00 | 120 | 06:00
| Chandraghona | 136 | 19:00 | 126 | 08:00 | Panchagarh | 139 | 18:30 | 115 | 02:00
| Chapai | 133 | 00:00 | 130 | 21:00 | Patuakhali | 139 | 21:00 | 134 | 02:00
| Charsaidpur | 134 | 00:00 | 130 | 12:00 | Payra | 139 | 00:00 | 137 | 01:00
| Chauddagram | 134 | 19:00 | 122 | 08:00 | PHP | 134 | 19:30 | 120 | 15:00
| Chhatak | 130 | 07:00 | 125 | 21:00 | Postogola | 136 | 03:00 | 131 | 08:00
| Chowmuhani | 132 | 19:00 | 115 | 08:00 | Purbachal | 131 | 04:00 | 125 | 12:00
| Chuadanga | 128 | 23:00 | 115 | 13:00 | Purbasadipur | 132 | 18:00 | 114 | 02:00
| Coxsbazar | 127 | 18:00 | 115 | 20:00 | Rahim | 134 | 23:00 | 131 | 09:00
| Cumilla(N) | 134 | 19:00 | 127 | 12:00 | Rajbari | 129 | 06:00 | 124 | 13:00
| Cumilla(S) | 135 | 19:30 | 125 | 13:00 | Rajendrapur | 136 | 19:00 | 126 | 09:00
| Daudkandi | 132 | 23:00 | 125 | 13:00 | Rajshahi | 132 | 00:00 | 127 | 19:00
| Dhaka | 135 | 04:00 | 129 | 13:00 | Rajshahi-230 | 134 | 23:00 | 127 | 12:00
| Dhamrai | 133 | 23:00 | 128 | 09:00 | Ramganj | 134 | 18:30 | 116 | 08:00
| Dhanmondi | 134 | 04:00 | 128.5 | 13:00 | Rampur | 134 | 19:00 | 126 | 15:00
| Dohazari | 131 | 19:00 | 122 | 06:00 | Rampura | 135 | 05:00 | 127 | 15:00
| Dummy | 132 | 02:00 | 132 | 02:00 | Rangamati | 133 | 18:30 | 126 | 08:00
| Faridpur | 130 | 06:00 | 125 | 13:00 | Rangpur | 132 | 16:00 | 123 | 07:00
| Fatullah | 135 | 23:00 | 128 | 12:00 | Ruppur | 134 | 00:00 | 130 | 12:00
| Fenchuganj | 136 | 06:00 | 132 | 13:00 | Saidpur | 134 | 18:00 | 117 | 02:00
| Feni | 135 | 19:30 | 122 | 13:00 | Satkhira | 132 | 00:00 | 122 | 20:00
| Ghorashal | N/A | N/A | N/A | N/A | Satmasjid | 132 | 04:00 | 127 | 18:30
| Goalpara | 136 | 00:00 | 129 | 12:00 | Savar | 130 | 23:00 | 123 | 08:00
| Gollamari | 136 | 00:00 | 129 | 12:00 | Shahjadpur | 140 | 03:00 | 135 | 15:00
| Gopalganj | 135 | 00:00 | 129 | 15:00 | Shahjibazar | 132 | 06:00 | 130 | 00:00
| Gopalganj-400 | 130 | 06:00 | 126 | 13:00 | Shahmirpur | 137 | 19:00 | 127 | 08:00
| Gulshan | 135 | 06:00 | 127 | 15:00 | Shariatpur | 137 | 02:00 | 124 | 19:00
| Halishahar | 134 | 19:00 | 126 | 08:00 | Sherpur | 129 | 18:30 | 111 | 13:00
| Haripur | 134 | 23:00 | 131 | 09:00 | Shikalbaha | N/A | N/A | N/A | N/A
| HaripurSBU | 134 | 23:00 | 131 | 09:00 | Shikalbaha-230 | 134 | 19:30 | 127 | 09:00
| Hasnabad | 137 | 03:00 | 133 | 16:00 | Shitalakhya | 134 | 04:00 | 131 | 08:00
| Hathazari | 135 | 21:00 | 130 | 00:00 | Sholosohor | 133 | 19:00 | 126 | 08:00
| Ishurdi | 135 | 23:00 | 130 | 12:00 | Shyampur | 134 | 23:00 | 129 | 08:00
| Jaldhaka | 132 | 18:00 | 117 | 02:00 | Shyampur-230 | 134 | 23:00 | 128 | 12:00
| Jamalpur | 131 | 18:30 | 115 | 13:00 | Siddhirganj | 134 | 23:00 | 129 | 12:00
| Jashore | 130 | 23:00 | 120 | 13:00 | Sirajganj | 132 | 03:00 | 127 | 12:00
| Jhenaidah | 134 | 23:00 | 124 | 12:00 | Sonargaon | 132 | 23:00 | 126 | 12:00
| Jhenaidah-230 | 135 | 23:00 | 124 | 13:00 | Sreemongol | 133 | 09:00 | 129 | 10:00
| Joydebpur | 140 | 06:00 | 131 | 15:00 | Sreepur | 129 | 00:00 | 126 | 11:00
| Joypurhat | 126 | 18:30 | 117 | 20:00 | Srinagar | 133 | 05:00 | 127 | 09:00
| Juldah | 137 | 19:00 | 127 | 15:00 | SSM | 137 | 19:00 | 128 | 08:00
| Kabirpur | 136 | 18:30 | 122 | 12:00 | Sunamganj | 128 | 18:00 | 122 | 21:00
| Kachua | 136 | 19:00 | 121 | 08:00 | Sylhet | 132 | 05:00 | 129 | 13:00
| Kaliakoir | 139 | 18:30 | 130 | 16:00 | Tangail | 133 | 18:30 | 123 | 21:00
| Kallyanpur | 128 | 09:00 | 123 | 19:30 | Thakurgaon | 138 | 18:30 | 111 | 02:00
| Kalurghat | 135 | 19:00 | 126 | 09:00 | TK | 134 | 19:00 | 127 | 08:00
| Kamrangirchar | 133 | 23:00 | 121 | 13:00 | Tongi | 133 | 00:00 | 129 | 11:00
| Kaptai | N/A | N/A | N/A | N/A | Ullon | 136 | 06:00 | 128 | 15:00
| Kazla | 132 | 03:00 | 127 | 13:00 | Uttara | 129 | 05:00 | 125 | 08:00
| Keranigonj | 134 | 05:00 | 128 | 08:00 | UttaraNew | 129 | 02:00 | 124 | 08:00
| Khagrachori | 132 | 18:30 | 126 | 09:00 | Zigatola | 133 | 04:00 | 127 | 09:00
| Khulna | 139 | 19:30 | 127 | 13:00
| Khulna(S) | 135 | 00:00 | 129 | 12:00
| Khulshi | 134 | 19:00 | 125 | 01:00
| Kishoreganj | 127 | 06:00 | 118 | 19:00
| Kodda | 138 | 18:30 | 123 | 08:00
| KSRM | 135 | 19:00 | 126 | 08:00
| Kulaura | 134 | 01:00 | 132 | 12:00
| Kurigram | 130 | 18:00 | 118 | 22:00

## L-Curve
Date | 2023-05-30
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1030 | 7777 | 5115 | 12892 |  |  |  | QF-LDC-11
0:30 | 995 | 7599.5 | 4974.5 | 12574 | Date: | 2023-05-30
1:00 | 960 | 7422 | 4834 | 12256
1:30 | 950 | 7376.5 | 4818 | 12194.5
2:00 | 940 | 7331 | 4802 | 12133
2:30 | 945 | 7246 | 4807.5 | 12053.5 | [5 empty] | Gen. at Eve. Peak | 14511 | 14511 MW (21:00 )
3:00 | 950 | 7161 | 4813 | 11974 | [6 empty] | 21:00
3:30 | 930 | 7149 | 4817.5 | 11966.5 | [5 empty] | Gen. at Day Peak | 11850 | 11850 MW (12:00 )
4:00 | 910 | 7137 | 4822 | 11959 | [6 empty] | 12:00
4:30 | 959 | 7066 | 4792.5 | 11858.5 | [5 empty] | Highest Generation | 14511
5:00 | 1008 | 6995 | 4763 | 11758 | [6 empty] | 21:00
5:30 | 984 | 6820.5 | 4753 | 11573.5
6:00 | 960 | 6646 | 4743 | 11389
6:30 | 1050 | 6541 | 4806.5 | 11347.5
7:00 | 1140 | 6436 | 4870 | 11306
7:30 | 1205 | 6510.5 | 4868 | 11378.5
8:00 | 1270 | 6585 | 4866 | 11451
8:30 | 1289 | 6537 | 4908.5 | 11445.5
9:00 | 1308 | 6489 | 4951 | 11440
9:30 | 1304 | 6382.5 | 4949 | 11331.5
10:00 | 1300 | 6276 | 4947 | 11223
10:30 | 1285 | 6330 | 4957.5 | 11287.5
11:00 | 1270 | 6384 | 4968 | 11352
11:30 | 1300 | 6550.5 | 5050.5 | 11601
12:00 | 1330 | 6717 | 5133 | 11850
12:30 | 1250 | 6898.5 | 5113 | 12011.5
13:00 | 1170 | 7080 | 5093 | 12173
13:30 | 1165 | 7136 | 5091.5 | 12227.5
14:00 | 1160 | 7192 | 5090 | 12282
14:30 | 1165 | 7223.5 | 5071.5 | 12295
15:00 | 1170 | 7255 | 5053 | 12308
15:30 | 1185 | 7193 | 4999 | 12192
16:00 | 1200 | 7131 | 4945 | 12076
16:30 | 1270 | 6978 | 4928 | 11906
17:00 | 1340 | 6825 | 4911 | 11736
17:30 | 1320 | 6875 | 4902.5 | 11777.5
18:00 | 1300 | 6925 | 4894 | 11819
18:30 | 1120 | 7671 | 5053.5 | 12724.5
19:00 | 940 | 8417 | 5213 | 13630
19:30 | 700 | 8793 | 5239 | 14032
20:00 | 760 | 8838 | 5350 | 14188 |  |  |  | Executive Engineer
20:30 | 730 | 8935 | 5414.5 | 14349.5 |  |  |  | Network Operation Division
21:00 | 700 | 9032 | 5479 | 14511
21:30 | 680 | 8935 | 5373 | 14308
22:00 | 660 | 8838 | 5267 | 14105 |  |  |  |  | Page 6 of 7
22:30 | 720 | 8565 | 5203 | 13768
23:00 | 780 | 8292 | 5139 | 13431
23:30 | 905 | 8034.5 | 5127 | 13161.5
24:00 | 1030 | 7777 | 5115 | 12892
14511 MW (21:00 )
11850 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-05-30 |  | Energy |  | 296735304
[15 empty] | 43614 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 4459 | 777 | 2327 | 398 | 1954 | 2327 | 0 | 0 | 484 | 166 | 0 | 0 | 1726.64
0:30 | 4373 | 819.5 | 2308.5 | 397 | 1721.5 | 2302 | 0 | 0 | 485.5 | 167 | 0 | 0 | 1696.08 |  |  | Date: | 43614
1:00 | 4287 | 862 | 2290 | 396 | 1489 | 2277 | 0 | 0 | 487 | 168 | 0 | 0 | 1665.52
1:30 | 4294.5 | 861.5 | 2297.5 | 396 | 1423.5 | 2273.5 | 0 | 0 | 483 | 165 | 0 | 0 | 832.76 | [9 empty] | Total Energy | 296.7353 |  | Total Energy Gen MKWHr Energy Not Served MKWHr Energy Requirement MKWHr | Total Energy Gen Total Energy MKWHr Energy Not Served Energy not Served MKWHr Energy Requirement Energy Requirement MKWHr
2:00 | 4302 | 861 | 2305 | 396 | 1358 | 2270 | 0 | 0 | 479 | 162 | 0 | 0 | 681 | [9 empty] | Energy not Served | 26.6845
2:30 | 4261.5 | 884.5 | 2306.5 | 383 | 1314 | 2273 | 0 | 0 | 468 | 163 | 0 | 0 | 680.915 | [9 empty] | Energy Requirement | 323.4198
3:00 | 4221 | 908 | 2308 | 370 | 1270 | 2276 | 0 | 0 | 457 | 164 | 0 | 0 | 1361.83
3:30 | 4228 | 909 | 2312.5 | 357.5 | 1266.5 | 2277.5 | 0 | 0 | 454.5 | 161 | 0 | 0 | 1225.7425 | [8 empty] | Shortage
4:00 | 4235 | 910 | 2317 | 345 | 1263 | 2279 | 0 | 0 | 452 | 158 | 0 | 0 | 1089.655
4:30 | 4233 | 910 | 2306 | 304.5 | 1242.5 | 2278 | 0 | 0 | 433.5 | 151 | 0 | 0 | 1018.5075
5:00 | 4231 | 910 | 2295 | 264 | 1222 | 2277 | 0 | 0 | 415 | 144 | 0 | 0 | 947.36
5:30 | 4199.5 | 910 | 2263 | 132 | 1226 | 2277.5 | 0 | 0 | 412.5 | 139 | 14 | 0 | 908.6825
6:00 | 4168 | 910 | 2231 | 0 | 1230 | 2278 | 0 | 0 | 410 | 134 | 28 | 0 | 870.005
6:30 | 4108.5 | 910 | 2202.5 | 0 | 1241 | 2271.5 | 0 | 0 | 409 | 133 | 72 | 0 | 814.1375 | [7 empty] | Coal
7:00 | 4049 | 910 | 2174 | 0 | 1252 | 2265 | 0 | 0 | 408 | 132 | 116 | 0 | 758.27
7:30 | 4111.5 | 911 | 2179 | 0 | 1250.5 | 2246.5 | 0 | 0 | 390 | 134 | 156 | 0 | 784.5325 | [6 empty] | Oil
8:00 | 4174 | 912 | 2184 | 0 | 1249 | 2228 | 0 | 0 | 372 | 136 | 196 | 0 | 810.795
8:30 | 4164 | 912 | 2167.5 | 0 | 1213.5 | 2242 | 0 | 0 | 362 | 139 | 245.5 | 0 | 1007.0475
9:00 | 4154 | 912 | 2151 | 0 | 1178 | 2256 | 0 | 0 | 352 | 142 | 295 | 0 | 1203.3
9:30 | 4046.5 | 912.5 | 2098 | 0 | 1182.5 | 2257 | 12.5 | 0 | 344.5 | 136 | 342 | 0 | 1354.6675
10:00 | 3939 | 913 | 2045 | 0 | 1187 | 2258 | 25 | 0 | 337 | 130 | 389 | 0 | 1506.035
10:30 | 3920.5 | 912 | 2079.5 | 0 | 1215.5 | 2272 | 25 | 0 | 343.5 | 129 | 390 | 0.5 | 1492.665
11:00 | 3902 | 911 | 2114 | 0 | 1244 | 2286 | 25 | 0 | 350 | 128 | 391 | 1 | 1479.295
11:30 | 3988 | 911 | 2187 | 21.5 | 1267.5 | 2311.5 | 25 | 0 | 354.5 | 125 | 409 | 1 | 1432.5
12:00 | 4074 | 911 | 2260 | 43 | 1291 | 2337 | 25 | 0 | 359 | 122 | 427 | 1 | 1385.705
12:30 | 4099 | 912 | 2256 | 220 | 1288.5 | 2330 | 25 | 0 | 353.5 | 123 | 403 | 1.5 | 1347.505
13:00 | 4124 | 913 | 2252 | 397 | 1286 | 2323 | 25 | 0 | 348 | 124 | 379 | 2 | 1309.305
13:30 | 4124 | 913 | 2252 | 397 | 1286 | 2323 | 25 | 0 | 348 | 124 | 379 | 2 | 1309.305
14:00 | 4124 | 913 | 2252 | 397 | 1286 | 2323 | 25 | 0 | 348 | 124 | 379 | 2 | 1309.305
14:30 | 4183.5 | 913 | 2233.5 | 396.5 | 1332 | 2324 | 25 | 0 | 346.5 | 131 | 353.5 | 2 | 1344.1625
15:00 | 4243 | 913 | 2215 | 396 | 1378 | 2325 | 25 | 0 | 345 | 138 | 328 | 2 | 1379.02
15:30 | 4249 | 913 | 2196.5 | 370 | 1376 | 2325 | 25 | 0 | 335 | 130 | 271 | 1.5 | 1418.6525
16:00 | 4255 | 913 | 2178 | 344 | 1374 | 2325 | 25 | 0 | 325 | 122 | 214 | 1 | 1458.285
16:30 | 4235 | 912.5 | 2191 | 172 | 1425 | 2327 | 25 | 0 | 329.5 | 126 | 162.5 | 0.5 | 1455.42
17:00 | 4215 | 912 | 2204 | 0 | 1476 | 2329 | 25 | 0 | 334 | 130 | 111 | 0 | 1452.555 | [11 empty] | 472
17:30 | 4208 | 912.5 | 2162 | 0 | 1602.5 | 2306.5 | 25 | 0 | 359.5 | 132 | 69.5 | 0 | 1290.2775 | [11 empty] | 100
18:00 | 4201 | 913 | 2120 | 0 | 1729 | 2284 | 25 | 0 | 385 | 134 | 28 | 0 | 1128 | [11 empty] | 20
18:30 | 4272.5 | 913 | 2145 | 127 | 2341.5 | 2245.5 | 25 | 9 | 492.5 | 139 | 14 | 0.5 | 979.425 | [11 empty] | 592
19:00 | 4344 | 913 | 2170 | 254 | 2954 | 2207 | 25 | 18 | 600 | 144 | 0 | 1 | 830.85
19:30 | 4444 | 913 | 2277 | 243 | 3156 | 2168 | 25 | 15 | 655 | 134 | 0 | 2 | 755.405
20:00 | 4416 | 913 | 2294 | 243 | 3144 | 2262 | 25 | 15 | 736 | 136 | 0 | 4 | 679.96
20:30 | 4418.5 | 913 | 2339 | 297 | 3147 | 2303.5 | 25 | 13.5 | 754.5 | 136 | 0 | 2.5 | 573.4775
21:00 | 4421 | 913 | 2384 | 351 | 3150 | 2345 | 25 | 12 | 773 | 136 | 0 | 1 | 466.995
21:30 | 4451 | 855.5 | 2361.5 | 372 | 3060 | 2335 | 25 | 14 | 690 | 143 | 0 | 1 | 613.11
22:00 | 4481 | 798 | 2339 | 393 | 2970 | 2325 | 25 | 16 | 607 | 150 | 0 | 1 | 759.225
22:30 | 4462 | 787.5 | 2320 | 393.5 | 2773 | 2305 | 12.5 | 8 | 556 | 150 | 0 | 0.5 | 1057.185
23:00 | 4443 | 777 | 2301 | 394 | 2576 | 2285 | 0 | 0 | 505 | 150 | 0 | 0 | 1355.145
23:30 | 4451 | 777 | 2314 | 396 | 2265 | 2306 | 0 | 0 | 494.5 | 158 | 0 | 0 | 1540.8925 |  |  | Max Temp. in Dhaka |  | 37.2° C
24:00 | 4459 | 777 | 2327 | 398 | 1954 | 2327 | 0 | 0 | 484 | 166 | 0 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen Total Energy MKWHr Energy Not Served Energy not Served MKWHr Energy Requirement Energy Requirement MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-05-30
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | [8 empty] | 0 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 0 |  | 304440
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2500000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 15 | 16 | 16 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 322380
| Teknaf 20MW PP (Solartech) |  |  |  |  | 0 | 1 | 5 | 9 | 14 | 17 |  | 19 | 19 | 15 | 14 | 3 | 0 | [9 empty] | 111105
6 | Sikalbaha 225MW CCPP (Gas) | 221 | 223 | 223 | 223 | 225 | 228 | 224 | 220 | 223 | 220 | 215 | 215 | 214 | 217 | 217 | 217 | 221 | 222 |  | 221 | 220 | 221 | 222 | 221 | 226 | 226 | 5124848
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 49 | 33 | 49 | 47 | 35 | 46 | 46 | 49 | 49 | 50 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1142287
12 | Hathazari 100 MW peaking PP | 65 | 65 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 45 | 45 | 50 | 52 | 44 | 44 | 37 | 43 |  | 63 | 62 | 62 | 62 | 54 | 54 | 53 | 1295232
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 23 | 51 |  | 51 | 51 | 51 | 51 | 51 | 41 | 32 | 643999
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 30 | 30 | 30 | 30 | 33 | 35 | 27 | 27 | 28 | 28 |  | 34 | 37 | 37 | 39 | 40 | 40 | 40 | 783536
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 97 | 97 | 97 | 98 | 99 | 101 | 39 | 39 | 98 | 37 | 37 | 95 | 92 | 191 | 184 | 186 | 120 | 121 |  | 125 | 188 | 188 | 190 | 188 | 196 | 191 | 2985000
17 | Siddhirganj 335 MW CCPP | 190 | 188 | 175 | 165 | 160 | 160 | 160 | 170 | 175 | 140 | 140 | 185 | 184 | 184 | 185 | 185 | 185 | 151 |  | 189 | 190 | 190 | 190 | 180 | 180 | 180 | 4277165
18 | Kodda 300 MW PP Unit-2 (Summit) | 82 | 47 | 47 | 47 | 47 | 47 | 47 | 48 | 50 | 47 | 52 | 55 | 42 | 47 | 47 | 47 | 62 | 72 |  | 230 | 262 | 260 | 260 | 260 | 255 | 148 | 2358545
19 | Ashuganj 195MW PP (APSCL-United) | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 167 | 167 | 167 | 167 | 167 | 175 | 175 | 175 |  | 175 | 175 | 175 | 175 | 185 | 185 | 185 | 4048000
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 128 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3190219
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4378500
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 36 | 32 | 31 | 34 | 34 | 36 | 36 | 33 | 33 | 36 | 36 |  | 37 | 37 | 40 | 40 | 41 | 39 | 39 | 894384
33 | Ashuganj 225 MW CCPP | 205 | 206 | 206 | 205 | 208 | 211 | 207 | 202 | 205 | 202 | 200 | 201 | 200 | 200 | 198 | 199 | 201 | 203 |  | 199 | 200 | 202 | 203 | 202 | 206 | 204 | 4900000
34 | Ashuganj 450 MW CCPP(South) | 335 | 330 | 305 | 315 | 305 | 305 | 275 | 315 | 305 | 270 | 275 | 270 | 275 | 270 | 305 | 305 | 305 | 305 |  | 330 | 330 | 310 | 305 | 330 | 305 | 310 | 7429000
| Ashuganj 450 MW CCPP(North) | 335 | 325 | 300 | 305 | 300 | 300 | 280 | 325 | 280 | 280 | 290 | 280 | 285 | 280 | 315 | 305 | 305 | 305 |  | 330 | 330 | 305 | 305 | 330 | 300 | 305 | 7782100
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 405 | 407 | 409 | 411 | 413 | 414 | 414 | 408 | 401 | 358 | 354 | 386 | 398 | 399 | 399 | 394 | 398 | 404 |  | 380 | 403 | 401 | 399 | 403 | 401 | 402 | 9658370
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 400 | 400 | 450 | 450 | 450 | 450 | 450 | 450 | 400 |  | 370 | 410 | 410 | 450 | 450 | 450 | 450 | 10086500
41 | Haripur 360MW CCPP(HPL) | 325 | 325 | 330 | 334 | 333 | 332 | 301 | 306 | 306 | 307 | 327 | 327 | 322 | 321 | 322 | 317 | 316 | 322 |  | 291 | 302 | 335 | 322 | 322 | 321 | 321 | 7704000
42 | RPCL 210MW CCPP | 84 | 84 | 86 | 86 | 86 | 87 | 33 | 33 | 44 | 44 | 44 | 33 | 33 | 33 | 31 | 46 | 46 | 47 |  | 48 | 52 | 78 | 80 | 81 | 88 | 87 | 1378560
43 | Sutiakhali 50 MW Solar PP |  |  |  |  | 0 | 3 | 14 | 25 | 39 | 40 | 49 | 35 | 24 | 48 | 38 | 16 | 12 | 3 |  | 0 | [6 empty] | 357670
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 43 | 42 | 42 | 44 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1019000
45 | Fenchugonj CCPP Phase-2 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 892440
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 50 | 50 | 51 | 51 | 52 | 52 | 51 | 50 | 51 | 60 | 60 | 54 | 53 | 53 | 53 | 54 | 54 | 56 |  | 55 | 57 | 55 | 55 | 55 | 55 | 56 | 1262496
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 82 | 82 | 82 | 82 | 81 | 81 | 78 | 78 | 80 | 80 | 78 | 78 | 78 | 79 | 79 | 80 |  | 81 | 81 | 80 | 81 | 81 | 81 | 81 | 1886400
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 191 | 191 | 190 | 191 | 189 | 189 | 188 | 189 | 190 |  | 192 | 192 | 190 | 189 | 188 | 188 | 188 | 3911250
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 250200
54 | Hobiganj 11MW PP Cofidence-E | 5 | 5 | 5 | 5 | 0 | 5 | 5 | 5 | 5 | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 193248
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 50 | 50 | 50 | 50 | 47 | 47 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1189800
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 354000
57 | Bibiana-II 341 MW CCPP (Summit) | 325 | 325 | 310 | 310 | 300 | 280 | 280 | 300 | 300 | 280 | 300 | 310 | 310 | 290 | 295 | 290 | 290 | 280 |  | 275 | 315 | 290 | 320 | 315 | 310 | 305 | 7357000
| Bibiyana South 400 MW | 350 | 377 | 381 | 383 | 385 | 352 | 352 | 372 | 364 | 375 | 345 | 350 | 343 | 344 | 344 | 360 | 365 | 340 |  | 370 | 370 | 370 | 380 | 375 | 385 | 355 | 8738600
58 | Nababganj 55 MW PP (Southern power ) | [10 empty] | 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 462363
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  |  | 3 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 263040
60 | Barabkunda 22 MW PP (Regent) | [26 empty] | 0
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 0 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 409140
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 16 | 16 | 16 | 15 | 15 | 15 | 15 | 15 | 15 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 398772
63 | Impoprt (Tripura) | 168 | 162 | 164 | 158 | 144 | 134 | 132 | 136 | 142 | 130 | 128 | 122 | 124 | 120 | 138 | 122 | 130 | 134 |  | 144 | 134 | 136 | 136 | 150 | 150 | 166 | 3384960
64 | Malancha, Ctg. EPZ (United) | 37 | 36 | 37 | 38 | 37 | 38 | 33 | 4 | 3 | 3 | 3 | 2 | 6 | 2 | 2 | 2 | 2 | 2 |  | 6 | 13 | 14 | 24 | 26 | 29 | 34 | 444960
65 | Feni 22MW PP (Doreen) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  |  | 6 | 16 | 16 | 15 | 15 | 13 | 13 | 14 |  | 15 | 15 | 15 | 11 | 17 | 17 | 17 | 307332
66 | Feni 11 MW PP (Doreen) | 0 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 237960
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 32 | 32 | 31 | 31 |  | 32 | 32 | 32 | 33 | 33 | 33 | 33 | 793100
68 | Cumilla 25 MW PP (Summit) | 17 | 21 | 21 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 0 | 21 | 12 | 21 | 19 |  | 19 | 19 | 19 | 19 | 20 | 20 | 20 | 463850
69 | Summit Ashulia | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 460000
70 | Summit Madhabdi | 22 | 25 | 25 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 18 | 18 | 18 | 18 | 16 | 16 | 18 | 23 |  | 23 | 23 | 23 | 23 | 24 | 25 | 25 | 487260
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 822300
72 | Rupganj 33 MW PP(Summit) | 32 | 32 | 33 | 33 | 33 | 33 | 33 | 32 | 30 | 28 | 28 | 28 | 28 | 28 | 14 | 28 | 28 | 28 |  | 30 | 30 | 30 | 31 | 31 | 31 | 31 | 744200
73 | Ghorashal 108MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 518545
| Feni Lanka Power | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 88 | 34 | 34 | 17 | 17 | 17 | 17 | 17 | 0 | 0 | 5 |  | 70 | 98 | 99 | 98 | 98 | 98 | 98 | 1610820
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 28 | 37 | 34 | 28 | 28 | 28 | 28 | 28 | 41 |  | 61 | 96 | 95 | 97 | 89 | 52 | 10 | 755160
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 581760
77 | Siddhirganj 100 PP(Dutch Bangla) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 14 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 10 | 9 | 244800
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 12 | 8 | 8 | 8 | 8 | 8 | 8 | 14 |  | 39 | 40 | 40 | 40 | 40 | 40 | 8 | 370080
79 | Kodda 150 MW PP | 48 | 48 | 48 | 48 | 32 | 32 | 32 | 32 | 32 | 48 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 |  | 150 | 150 | 150 | 150 | 150 | 48 | 48 | 1602720
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 21 | 16 | 16 | 16 | 8 | 8 | 8 | 8 | 11 | 22 | 25 |  | 43 | 51 | 51 | 43 | 43 | 43 | 52 | 739987
| Gazipur 100 MW PP | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 1851350
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 5 | 4 | 4 | 4 | 2 | 0 | 0 | [8 empty] | 33238
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 448341
| Karnaphuli Power Ltd. | 72 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 40 | 54 | 54 | 54 | 58 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1346540
82 | Madanganj 102 PP(Summit) | 82 | 72 | 55 | 66 | 66 | 66 | 70 | 85 | 85 | 85 | 82 | 70 | 75 | 78 | 78 | 78 | 78 | 78 |  | 80 | 80 | 82 | 82 | 82 | 82 | 82 | 1738967
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [12 empty] | 8 | 12 | 11 | 12 | 11 | 4 |  | 11 | 0 | [5 empty] | 71869
86 | Meghnaghat CCPP ( Summit) | 310 | 305 | 300 | 295 | 282 | 240 | 260 | 290 | 274 | 280 | 301 | 296 | 299 | 300 | 299 | 283 | 280 | 274 |  | 303 | 299 | 308 | 288 | 310 | 275 | 300 | 7026793
87 | Meghnaghat 100 MW(IEL) | 8 | 8 | 9 | 8 | 9 | 8 | 9 | 8 | 9 | 8 | 9 | 8 | 8 | 9 | 8 | 9 | 8 | 12 |  | 17 | 17 | 17 | 18 | 17 | 8 | 9 | 232320
| Meghnaghat 104 MW PP (OPCL) |  |  |  | 0 | 11 | 16 |  |  |  |  | 11 | 17 | 17 | 14 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 |  | 237120
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 66 | 66 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1170480
92 | Fenchuganj 44MW (Energyprima) | [17 empty] | 0 |  | 47 | 47 | 47 | 47 | 48 | 48 | 48 | 289368
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1152832
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 225792
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 9 | 12 | 19 | 19 | 19 | 19 | 31 |  | 35 | 39 | 21 | 20 | 40 | 40 | 40 | 392160
96 | Chattogram 108 MW PP (ECPV) | [26 empty] | 0
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 0 | [15 empty] | 0 |  | 17 | 15 | 15 | 15 | 15 | 15 | 15 | 120115
100 | Manikganj 55 MW PP (Northern) | [10 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 55 | 55 | 55 | 35 | 35 |  | 469277
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 112 | 112 | 80 | 80 | 80 | 80 | 80 | 112 | 112 | 112 | 112 | 112 | 112 | 112 |  | 80 | 80 | 80 | 112 | 112 | 112 | 112 | 2357918
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 1 | 1 | 1 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 1 | 0 | [8 empty] | 15500
103 | Kamalaghat 54 MW PP(Banco Energy) | [15 empty] | 0 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 127800
104 | Keranigonj 300 MW PP (APR) | 301 | 301 | 275 | 250 | 169 | 0 | [5 empty] | 20 | 303 | 302 | 302 | 254 | 0 | 0 |  | 214 | 203 | 203 | 300 | 300 | 300 | 303 | 4003561
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 67 | 68 | 68 | 68 |  | 87 | 87 | 88 | 88 | 88 | 69 | 69 | 1720800
112 | Aurahati 100MW PP (Aggreko) | 95 | 95 | 95 | 95 | 95 | 0 | [5 empty] | 23 | 94 | 94 | 94 | 90 | 0 | 0 |  | 40 | 40 | 40 | 51 | 93 | 94 | 95 | 1313700
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 15 | 15 | 17 | 29 |  | 148 | 149 | 149 | 149 | 149 | 96 | 21 | 1041408
115 | Juldah 100 MW PP Unit-3 (Acorn) | 50 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 90 | 90 | 90 | 90 | 90 | 90 | 50 | 1147200
116 | Chandpur 200MW (Desh energy) | 18 | 17 | 17 | 17 | 17 | 18 | 17 | 17 | 24 | 34 | 34 | 34 | 34 | 44 | 51 | 51 | 64 | 117 |  | 120 | 120 | 120 | 120 | 120 | 120 | 75 | 1320000
117 | Ashuganj 150MW PP (Midland) | 13 | 12 | 13 | 12 | 12 | 13 | 12 | 13 | 12 | 13 | 12 | 10 | 12 | 12 | 12 | 12 | 13 | 20 |  | 77 | 125 | 122 | 132 | 139 | 137 | 68 | 903272
118 | Bibiyana-III 400 MW CCPP | 404 | 388 | 376 | 347 | 343 | 343 | 343 | 375 | 368 | 319 | 320 | 369 | 376 | 369 | 385 | 369 | 369 | 369 |  | 393 | 382 | 370 | 368 | 376 | 368 | 368 | 8844000
| Jamalpur 115 MW PP (United) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 |  | 85 | 85 | 85 | 85 | 85 | 18 | 18 | 708000
| Anwara 300 MW PP (United) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 69 | 69 | 69 | 69 | 69 | 69 | 68 | 69 | 69 | 69 | 120 |  | 291 | 293 | 300 | 300 | 122 | 87 | 88 | 2406218
| Juldah unit-2 (Acorn) | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 90 | 90 | 90 | 90 | 90 | 63 | 38 | 1123200
| Anlima Energy Ltd. | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 839291
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 6 | 32 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 849600
| Spectra Solar Plant Ltd. |  |  |  |  | 0 | 2 | 6 | 11 | 23 | 28 | 31 | 32 | 31 | 25 | 22 | 16 | 6 | 1 |  | 0 | [6 empty] | 236230
| Chandpur 115(Doreen) | 22 | 18 | 18 | 18 | 17 | 18 | 18 | 18 | 18 | 17 | 18 | 22 | 36 | 36 | 36 | 36 | 36 | 44 |  | 98 | 97 | 97 | 97 | 97 | 85 | 55 | 984960
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 30 | 36 |  | 35 | 35 | 34 | 34 | 34 | 34 | 17 | 559800
| Mirsharai 150 MW (Oil) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 49 | 94 | 163 | 163 | 18 | 18 | 18 | 729309
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 3 | 2 | 1 | 0 | 0 |  | 1 | 2 | 4 | 1 | 1 | 0 |  | 17424
120 | Eastern Zone Total | 7422 | 7331 | 7161 | 7137 | 6995 | 6646 | 6436 | 6585 | 6489 | 6276 | 6384 | 6717 | 7080 | 7192 | 7255 | 7131 | 6825 | 6925 |  | 8417 | 8793 | 8838 | 9032 | 8838 | 8292 | 7777 | 174869136
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 47 | 47 | 31 | 31 | 31 | 32 | 32 | 32 | 32 |  |  |  | 0 | 29 | 39 | 41 | 44 | 47 |  | 63 | 63 | 64 | 63 | 63 | 63 | 63 | 856320
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 14 | 14 | [6 empty] | 0 | 15 | 29 |  | 31 | 38 | 34 | 34 | 34 | 34 | 34 | 369120
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 20 | 30 | 31 | 35 | 35 | 35 | 35 | 571680
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 3 | 25 | 26 | 68 | 87 | 84 | 93 | 88 | 83 | 72 | 51 | 29 | 8 |  | 0 | [6 empty] | 722880
131 | Rampal 1320 MW (BIFPCL) | 324 | 317 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 330 | 324 | 324 | 324 | 330 | 324 | 323 | 323 | 323 |  | 324 | 325 | 324 | 323 | 323 | 323 | 322 | 7730909
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 1226400
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 0 |  |  |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 311520
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3628400
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 172 | 170 | 174 | 176 | 176 | 139 | 174 | 170 | 170 | 170 | 163 | 168 | 169 | 168 | 168 | 168 | 161 | 169 |  | 169 | 169 | 169 | 171 | 171 | 171 | 172 | 4121613
140 | Bhola 33 MW PP (Venture) | 32 | 31 | 30 | 29 | 26 | 24 | 22 | 21 | 19 | 21 | 21 | 23 | 25 | 25 | 26 | 23 | 25 | 22 |  | 29 | 33 | 32 | 35 | 35 | 36 | 36 | 646365
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [16 empty] | 0 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 47625
143 | Gopalganj 100 MW Peaking PP | 84 | 84 | 78 | 73 | 73 | 73 | 73 | 42 | 41 | 40 | 39 | 34 | 34 | 32 | 32 | 25 | 25 | 45 |  | 60 | 60 | 76 | 81 | 75 | 75 | 70 | 1327488
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 85 | 85 | 85 | 85 | 85 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 85 | 2463696
146 | Bheramara HVDC | 862 | 861 | 908 | 910 | 910 | 910 | 910 | 912 | 912 | 913 | 911 | 911 | 913 | 912 | 913 | 913 | 912 | 913 |  | 913 | 913 | 913 | 913 | 798 | 777 | 777 | 21612363
147 | Bheramara 410 MW CCPP | 170 | 170 | 170 | 180 | 190 | 190 | 200 | 200 | 195 | 190 | 190 | 185 | 185 | 185 | 175 | 180 | 180 | 195 |  | 200 | 205 | 205 | 205 | 210 | 205 | 235 | 4780224
148 | Payra 1320 MW | 622 | 622 | 622 | 622 | 622 | 622 | 600 | 580 | 610 | 622 | 622 | 622 | 622 | 622 | 622 | 622 | 622 | 540 |  | 510 | 610 | 610 | 622 | 622 | 622 | 622 | 15624200
149
150 | Barapukuria TPP Unit-1 | 73 | 73 | 74 | 73 | 72 | 72 | 72 | 72 | 72 | 73 | 73 | 72 | 72 | 70 | 71 | 71 | 71 | 74 |  | 74 | 74 | 74 | 74 | 73 | 73 | 73 | 1686109
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 216 | 250 | 5996100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 21 | 21 | 21 | 21 | 0 | [17 empty] | 30 | 30 | 30 | 23 | 192048
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 2 | 3 | 3 | 5 | 5 | 5 | 4 | 3 | 2 | 1 | 0 | [8 empty] | 38700
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 150 | 155 | 156 | 138 | 141 | 177 | 181 | 180 | 179 | 178 | 182 |  | 193 | 193 | 194 | 194 | 197 | 199 | 203 | 4263873
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 157 | 157 | 159 | 163 | 166 | 166 | 169 | 166 | 162 | 164 | 164 | 164 | 160 | 157 | 157 | 159 | 162 | 165 |  | 170 | 175 | 177 | 176 | 176 | 176 | 183 | 4208409
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 299 | 321 | 338 | 348 | 354 | 354 | 348 | 334 | 328 | 287 | 288 | 346 | 334 | 321 | 318 | 309 | 326 | 304 |  | 363 | 371 | 372 | 377 | 302 | 301 | 301 | 7798254
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [26 empty] | 0
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 18 | 14 | 14 | 14 | 16 | 16 | 16 | 8 | 16 | 16 |  | 17 | 18 | 18 | 20 | 20 | 20 | 21 | 414960
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 176094
165 | Amnura 50 MW PP(Sinha) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 541900
166 | Katakhali 50 MW PP (Northern) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 25 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 770592
167 | Katakhali 50 MW Peaking PP | 32 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 40 | 40 | 40 | 40 | 24 | 24 | 24 |  | 40 | 40 | 40 | 40 | 40 | 40 | 32 | 621806
168 | Santahar 50 MW Peaking PP | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 28 | 28 | 28 | 28 | 28 | 32 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 786600
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 0 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 40512
170 | Chapainawabganj 100 MW Peaking PP | 82 | 82 | 75 | 75 | 75 | 70 | 68 | 68 | 53 | 53 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 52 |  | 87 | 88 | 88 | 88 | 80 | 80 | 80 | 1554888
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 50 | 50 | 50 | 50 | 35 | 35 | 967008
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 0 |  |  |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 843456
173 | Rangpur 20 MW GTPP | [17 empty] | 0 |  | 18 | 15 | 15 | 12 | 16 | 0 | 0 | 46000
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 | 0 |  |  | 30 | 34 | 36 | 30 | 32 | 40 | 39 | 39 | 39 | 47 | 48 |  | 48 | 48 | 48 | 48 | 48 | 35 | 34 | 819072
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 3 | 5 | 7 | 7 | 7 | 7 | 7 | 7 | 5 | 3 | 1 |  | 0 | [6 empty] | 59866
178 | Energypac Power Venture Thakurgaon Ltd. | 35 | 0 | [8 empty] | 27 | 35 | 35 | 35 | 35 | 35 | 35 | 40 |  | 103 | 115 | 115 | 115 | 115 | 115 | 55 | 1022208
| Intraco Solar 30 MW |  |  |  |  | 0 | 2 | 8 | 15 |  | 29 | 14 | 33 | 22 | 28 | 25 | 16 | 8 | 2 |  | 0 | 0 | [5 empty] | 234516
| Adani Power Jharkhanda Ltd | 858 | 858 | 856 | 860 | 859 | 860 | 869 | 852 | 850 | 833 | 867 | 919 | 905 | 919 | 908 | 909 | 913 | 947 |  | 899 | 759 | 854 | 926 | 907 | 901 | 910 | 21236364
178 | Teesta Solar Limited |  |  |  |  | 0 | 17 | 54 | 102 | 139 | 172 | 194 | 196 | 178 | 145 | 141 | 101 | 51 | 13 |  | 0 | [6 empty] | 1506030