## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-06-03 | Saturday
|  | Date (day): | 2023-06-03 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12524.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14567 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-06-02 | 2023-06-03 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 130 | 130 | 130 | 130 | 50 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 42 | 75 | 78 | 78 | 30 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 398 | 398 | 400 | 400 | 12 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 332 | 332 | 330 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 9 | 21 | 8 | 25 | 75 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 293 | 279 | 300 | 300 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 53 | 80 | 80 | 80 |  | 22 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 30 | 0 | 30 | 25 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 20 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 15 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 187 | 194 | 190 | 195 | 15 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 17 | 26 | 16 | 32 | 68 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 16 | 8 | 16 | 86 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 0 | 17 | 37 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 64 | 150 | 64 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 36 | 45 | 42 | 45 |  | 35 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 22 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 48 | 8 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 60 | 60 | 60 | 60 | 45 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 47 | 145 | 47 | 145 | 155 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 12 | 233 | 300 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 85 | 97 | 100 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 131 | 17 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 86 | 86 | 88 | 88 |  | 17 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 17 | 17 | 87 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 54 | 18 | 54 | 108 |  | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 31 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 34 | 17 | 35 | 20 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5867 | 2739 | 3515 | 3136 | 3654 | 894 | 1269
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 25 | 8 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 19 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 44 | 6 | 44 | 6
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 25 | 25 | 25 | 25 | 205 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 224 | 225 | 225
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 51 | 17 | 51 | 54 |  | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 30 | 60 | 50 | 64 |  | 34 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 50 | 68 | 51 | 68 |  | 34 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 44 | 66 | 44 | 66 | 34 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 38 | 90 | 38 | 90 |  | 10 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 7 | 9 | 10 | 10 | 12 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 17 | 42 | 10 | 30
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 69 | 300 | 69 | 300 |  |  | Fuel shortage
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 54 | 54 | 54 | 54 | 56 |  | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 38 | 90 | 38 | 90 |  | 10 | Engine problem
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 34 | 17 | 34 | 82 |  | Fuel shortage
| Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 18 | 163 | 18 | 163 |  |  | On test.
| SS Power I |  | Coal | SS Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 2 | 3 | 0 | 0
| Chattogram area Total |  |  |  |  | 2605 | 2545 | 794 | 1465 | 822 | 1456 | 674 | 418
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 197 | 154 | 200 | 200 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 305 | 310 | 320 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 270 | 150 | 320 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 35 | 41 | 40 | 40
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 192 | 178 | 190 | 185
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 5 | 134 | 6 | 150
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 40 | 41 | 40 | 46 |  | 6 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 52 | 120 | 51 | 120 | 80 |  | Fuel shortage
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 18 | 17 | 17 |  | 5 | Engine problem
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 146 | 150 | 129 | 152
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 20 | 21 | 21 |  | 4 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Contract Expired
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 52 | 52 | 98 |  | 16 | Engine problem
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 95 | 26 | 94 | 19 |  | Fuel shortage
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 34 | 35 | 35 | 35 |  | 19 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 97 | 18 | 97 | 18 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 3159 | 3096 | 1466 | 1797 | 1372 | 2032 | 117 | 613
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 31 | 103 | 45 | 100 | 102 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 16 | 19 | 19 | 3 |  | Gas shortage
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 67 | 87 | 68 | 84 | 116 |  | Fuel shortage
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 18 | 85 | 18 | 84 | 31 |  | Fuel shortage
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 47 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 | 10 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 196 | 303 | 213.6 | 299 | 105 | 0
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 39 | 38 | 40 | 40 |  | 50 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 112 | 112 |  | 51 | ST under maint.
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 50 | 50 | 50
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 48 | 49 | 48 | 48
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 11 | 11
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 54 | 55 | 60 | 60
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 81 | 84 | 84
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 191 | 187 | 190 | 190 |  | 41 | Machine problem
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 17 | 17 | 17
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 9 |  | Gas shortage
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 300 | 300 | 305 |  | 36 | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 398 | 398 | 400 | 400 |  |  | FGMO
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 354 | 392 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1689 | 1753 | 1781 | 1786 | 9 | 635
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 909 | 803 | 927 | 927
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 44 | 80 | 83 | 83 |  | 32 | Engine problem
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 11 | 21 | 22 | 35 |  | 19 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 30 | 68 | 60 | 80 |  | 29 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 160 | 225 | 200 | 200 | 210 |  | Gas shortage
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 16 | 40 | 16 | 40
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 17 | 17 | 17 | 88 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 105 | 105 | 105 | 105
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 87 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 318 | 325 | 320 | 320 | 297 |  | Coal Shortage.
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 2905 | 2901 | 1697 | 1684 | 1850 | 1807 | 841 | 80
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 16 | 16 | 16 | 94 |  | Fuel shortage
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 28 | 35 | 23 | 35 |  | 5 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 164 | 170 | 170 | 170
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 410 | 610 | 622 | 622 | 622 |  | Coal Shortage.
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maintenance
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 150 | 17 | 150
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 150 | 150 | 150 | 150 | 157 |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 785 | 1131 | 998 | 1143 | 873 | 225
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 28 | 25 | 30 |  | 22 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 13 | 13 | 0 | 0 |  | 71 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 28 | 28 | 28 | 21 | 28
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 25 | 25 | 25 | 25 |  | 25 | Engine problem
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 30 | 37 | 40 | 40 |  | 10 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 155 | 199 | 160 | 160 | 50 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 143 | 176 | 170 | 170 | 50 |  | Gas shortage
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 415 | 400 | 400 | 14 |  | Gas shortage
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 35 | 35 |  | 15 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 13 | 19 | 22 | 22
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 34 | 0 | 52
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 32 | 84 | 80 | 90 |  | 14 | Engine problem
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 50 | 35 | 50 | 63 |  | Fuel shortage
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 55 | 35 | 57 | 56 |  | Fuel shortage
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 748*1 | 748 | 748 | 1067 | 1053 | 748 | 748 |  |  | On test.
| Rajshahi Area Total |  |  |  |  | 2927 | 2905 | 2002 | 2254 | 1810 | 1915 | 824 | 160
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 76 | 75 | 75 | 75 | 10 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 230 | 230 | 230 | 230
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 33 | 56 | 35 | 55 | 58 |  | Fuel shortage
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 114 | 34 | 115
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 22 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 189 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 592 | 475 | 542 | 475 | 108 | 85
| Total |  |  |  |  | 24143 | 23370 | 11960 | 14377 | 12524.6 | 14567 | 4445 | 3485
A. |  | 2023-06-02 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 14377 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 11153 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14770 | MW
3 | Day peak Generation : |  |  | 11960 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14210.1 | MW
4 | Evening peak Generation : |  |  | 14377 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 375 | MW
5 | Total Energy Generation : |  | 294.4692 | MKWHr | By Solar | 3.218 | MKWHr
| By Gas : | 158.1139 | MKWHr |  | By Oil: | 53.4829 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 54.496 | MKWHr |  | By Hydro: | 0.30684 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.037488 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4445 | MW | Dhaka | 5050 | 5050 |  | 0 |  | 18:00 |  | 690.465
|  |  | For Plants S/D or M/C prob = |  |  | 3485 | MW | Chittagong | 1425 | 1425 |  | 0 |  | 19:00 |  | 479.41
|  |  | Total = |  |  | 7930 | MW | Khulna | 1663 | 1533 |  | 130 |  | 19:30 |  | 375.315
7 | Total Gas Supplied : |  |  | 1200.86 | MMCFD |  |  | Rajshahi | 1506.6 | 1471.6 |  | 35 |  | 20:00 |  | 359.08
8 | Fuel Cost : | i) Gas : | Taka | 184909651.502 | ii) Oil : | Taka | 740073056.66 | Comilla | 1366 | 1256 |  | 110 |  | 21:00 |  | 375.315
|  | iii) Coal : | Taka | 132253079.9 | Total | Taka | 1057235788.062 | Mymensingh | 1221 | 1171 |  | 50 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 560 | 560 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 880 | MW (E to W) at | 21:00 | hrs | Barisal | 465.5 | 465.5 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 840 | MW at | 19:30 | hrs | Rangpur | 953 | 903 |  | 50
10 | Maximum Temperature in Dhaka was |  |  |  | 37.5° C |  |  | Total | 14210.1 | 13835.1 |  | 375
B. |  | 2023-06-03 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 37.5° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 15500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 860 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14567 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 13800 | MW
4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 317.4705 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11234 | MW at | 8:00 | 170 | 120 | 120 | 110 | 90 | 120 | 50 | 0 | 80
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.2247 | MKWHr. | ii) HVDC Flow at Peak Time |  | 803 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.5894 | MKWHr. | iii) Maximum HVDC Flow : |  | 910 | MW at | 4:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 72.64 |  | (b) Today: | 72.58 |  | (c) Rule Curve: |  | 76.52
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-06-02 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 130 | 180 | 0 | 42 | 0 | 395 | 327 |  | 0 | 450 | 297 | 8 | 80 | 0 | 160 | 0 | 195 | 16 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 26 | 33 | 31 | 8 | 0 | 0 | 0 | 100 | 0 | 8 | 225 | 0 | 0 | 0 |  | 12 | 48 | 50 | 55 | 0 | 6 | 5 | 30 | 0 | 0 | 0 | 315 | 305 | 202 | 195 | 0 | 39 | 0 | 0 | 51 | 0 | 39 | 51 | 17 | 11 | 33 | 21 | 162 | 110 | 0 | 19 | 0 | 43 | 40 | 50 | 46 | 112 | 0 | 55 | 75 | 0 | 187 | 0 | 0 | 10 | 315 | 16 | 5 | 0 | 55 | 300 | 0 | 68 | 93 | 17 | 0 | 50 | 17 | 5 | 369 | 18 | 88 | 17 | 0 | 68 | 17 | 54 | 62 | 9 | 50 | 380 | 0 | 0 | 17 | 17 | 0 | 35 | 0 | 23 | 17 | 0 | 18 | 0 | 0 | 2 |  | 838 | 0 | 155 | 0 | 79 | 0 | 0 | 0 | 14 | 49 | 16 | 172 | 36 | 16 | 0 | 0 | 0 | 27 | 18 | 70 | 21 | 25 | 22 | 0 | 0 | 22 | 0 | 8 | 73 | 0 | 250 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 364 | 17 | 0 | 35 | 105 | 34 | 0 | 0 | 35 | 300 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 150 | 1060 | 0 | 0 |  | 7387 | 4668 | 12055 | 4337 | 838 | 2422 | 393 | 1356 | 2158 | 0 | 0 | 387 | 162 | 0 | 2 | 2525.975 | 72.65
2:00 | 0 | 0 | 130 | 180 | 0 | 42 | 0 | 397 | 328 |  | 0 | 450 | 282 | 8 | 80 | 0 | 154 | 0 | 197 | 17 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 26 | 33 | 31 | 8 | 0 | 0 | 0 | 100 | 0 | 8 | 225 | 0 | 0 | 0 |  | 12 | 48 | 50 | 55 | 0 | 6 | 5 | 30 | 0 | 0 | 0 | 310 | 305 | 205 | 197 | 0 | 39 | 0 | 0 | 51 | 0 | 43 | 51 | 17 | 11 | 33 | 21 | 156 | 154 | 0 | 19 | 0 | 43 | 40 | 50 | 46 | 112 | 0 | 56 | 75 | 0 | 185 | 0 | 0 | 10 | 300 | 16 | 5 | 0 | 47 | 240 | 0 | 68 | 92 | 17 | 0 | 38 | 17 | 5 | 366 | 18 | 88 | 17 | 0 | 69 | 17 | 46 | 62 | 9 | 38 | 384 | 0 | 0 | 17 | 17 | 0 | 35 | 0 | 18 | 17 | 0 | 18 | 0 | 0 | 1 |  | 839 | 0 | 155 | 0 | 79 | 0 | 0 | 0 | 14 | 49 | 16 | 172 | 35 | 16 | 0 | 0 | 0 | 27 | 18 | 56 | 21 | 25 | 21 | 0 | 0 | 22 | 0 | 8 | 73 | 0 | 250 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 363 | 17 | 0 | 35 | 105 | 34 | 0 | 0 | 35 | 290 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 150 | 1060 | 0 | 0 |  | 7293 | 4645 | 11938 | 4380 | 839 | 2393 | 332 | 1313 | 2148 | 0 | 0 | 376 | 156 | 0 | 1 | 2447.665 | 72.65
3:00 | 0 | 0 | 130 | 180 | 0 | 42 | 0 | 400 | 327 |  | 0 | 450 | 294 | 8 | 80 | 0 | 138 | 0 | 195 | 17 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 26 | 33 | 31 | 8 | 0 | 0 | 0 | 100 | 0 | 8 | 225 | 0 | 0 | 0 |  | 12 | 48 | 50 | 55 | 0 | 6 | 5 | 35 | 0 | 0 | 0 | 310 | 305 | 204 | 197 | 0 | 40 | 0 | 0 | 51 | 0 | 43 | 52 | 17 | 11 | 33 | 21 | 162 | 147 | 0 | 19 | 0 | 43 | 40 | 50 | 46 | 112 | 0 | 56 | 75 | 0 | 185 | 0 | 0 | 10 | 310 | 16 | 5 | 0 | 47 | 300 | 0 | 68 | 79 | 17 | 0 | 38 | 17 | 5 | 377 | 18 | 88 | 17 | 0 | 69 | 17 | 54 | 62 | 9 | 38 | 381 | 0 | 0 | 17 | 17 | 0 | 35 | 0 | 17 | 17 | 0 | 18 | 0 | 0 | 0 |  | 909 | 0 | 154 | 0 | 80 | 0 | 0 | 0 | 14 | 49 | 16 | 174 | 34 | 0 | 0 | 0 | 0 | 27 | 18 | 56 | 21 | 25 | 21 | 0 | 0 | 22 | 0 | 8 | 73 | 0 | 240 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 370 | 17 | 0 | 35 | 105 | 34 | 0 | 0 | 0 | 290 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 150 | 1062 | 0 | 0 |  | 7365 | 4667 | 12032 | 4370 | 909 | 2425 | 379 | 1271 | 2140 | 0 | 0 | 376 | 162 | 0 | 0 | 2261.44 | 72.65
4:00 | 0 | 0 | 130 | 180 | 0 | 42 | 0 | 402 | 327 |  | 0 | 450 | 274 | 8 | 80 | 0 | 140 | 0 | 198 | 17 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 26 | 33 | 31 | 8 | 0 | 0 | 0 | 100 | 0 | 8 | 226 | 0 | 0 | 0 |  | 12 | 48 | 50 | 55 | 0 | 6 | 5 | 33 | 0 | 0 | 0 | 310 | 305 | 206 | 195 | 0 | 42 | 0 | 0 | 51 | 0 | 43 | 52 | 17 | 11 | 33 | 21 | 160 | 137 | 0 | 19 | 0 | 43 | 40 | 50 | 46 | 112 | 0 | 57 | 75 | 0 | 184 | 0 | 0 | 10 | 320 | 16 | 5 | 0 | 47 | 301 | 0 | 68 | 50 | 17 | 0 | 38 | 17 | 6 | 377 | 18 | 88 | 17 | 0 | 69 | 17 | 54 | 62 | 9 | 38 | 386 | 0 | 0 | 17 | 17 | 0 | 35 | 0 | 18 | 17 | 0 | 18 | 0 | 0 | 0 |  | 910 | 0 | 160 | 0 | 80 | 0 | 0 | 0 | 14 | 49 | 16 | 173 | 32 | 0 | 0 | 0 | 0 | 27 | 13 | 56 | 21 | 25 | 21 | 0 | 0 | 22 | 0 | 8 | 73 | 0 | 230 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 382 | 17 | 0 | 35 | 105 | 34 | 0 | 0 | 0 | 300 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 150 | 1049 | 0 | 0 |  | 7330 | 4669 | 11999 | 4386 | 910 | 2421 | 351 | 1273 | 2127 | 0 | 0 | 371 | 160 | 0 | 0 | 2197.455 | 72.65
5:00 | 0 | 0 | 130 | 180 | 0 | 42 | 0 | 406 | 328 |  | 0 | 450 | 299 | 8 | 80 | 0 | 0 | 0 | 197 | 17 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 22 | 33 | 31 | 8 | 0 | 0 | 0 | 100 | 0 | 8 | 225 | 0 | 0 | 0 |  | 12 | 48 | 50 | 55 | 0 | 6 | 5 | 33 | 0 | 0 | 0 | 310 | 305 | 206 | 197 | 0 | 42 | 0 | 0 | 51 | 0 | 37 | 52 | 17 | 11 | 33 | 21 | 152 | 137 | 0 | 19 | 0 | 43 | 40 | 50 | 46 | 112 | 0 | 57 | 75 | 0 | 187 | 0 | 0 | 10 | 300 | 16 | 5 | 0 | 47 | 305 | 0 | 68 | 54 | 17 | 0 | 38 | 17 | 5 | 377 | 18 | 88 | 17 | 0 | 69 | 17 | 54 | 62 | 9 | 38 | 367 | 4 | 0 | 17 | 17 | 0 | 35 | 0 | 17 | 17 | 0 | 18 | 0 | 0 | 0 |  | 909 | 0 | 165 | 0 | 64 | 0 | 0 | 0 | 14 | 49 | 16 | 173 | 31 | 0 | 0 | 0 | 0 | 27 | 13 | 56 | 21 | 25 | 21 | 0 | 0 | 22 | 0 | 8 | 73 | 0 | 230 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 388 | 17 | 0 | 35 | 105 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 150 | 1054 | 0 | 0 |  | 7176 | 4633 | 11809 | 4233 | 909 | 2434 | 359 | 1225 | 2132 | 0 | 0 | 365 | 152 | 0 | 0 | 2187.905 | 72.64
6:00 | 0 | 0 | 130 | 180 | 0 | 42 | 0 | 405 | 327 |  | 0 | 450 | 294 | 8 | 80 | 0 | 0 | 0 | 197 | 17 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 26 | 33 | 32 | 8 | 0 | 0 | 0 | 100 | 0 | 8 | 226 | 0 | 0 | 0 |  | 12 | 48 | 50 | 55 | 0 | 6 | 5 | 34 | 0 | 0 | 0 | 310 | 305 | 206 | 197 | 0 | 42 | 0 | 0 | 51 | 0 | 37 | 52 | 17 | 11 | 33 | 20 | 160 | 137 | 0 | 19 | 0 | 43 | 40 | 50 | 46 | 112 | 0 | 56 | 75 | 0 | 188 | 0 | 0 | 10 | 290 | 16 | 5 | 0 | 47 | 0 | 0 | 68 | 54 | 17 | 3 | 38 | 17 | 5 | 377 | 18 | 88 | 17 | 0 | 69 | 17 | 54 | 62 | 9 | 38 | 360 | 15 | 3 | 17 | 17 | 0 | 35 | 2 | 18 | 17 | 0 | 18 | 0 | 0 | 0 |  | 908 | 0 | 165 | 0 | 80 | 0 | 0 | 0 | 14 | 49 | 16 | 172 | 28 | 0 | 0 | 0 | 0 | 0 | 13 | 35 | 21 | 25 | 21 | 0 | 0 | 22 | 0 | 0 | 75 | 0 | 230 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 388 | 17 | 0 | 35 | 105 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 17 | 0 | 6 | 0 | 0 | 0 | 325 | 2 | 150 | 1053 | 13 | 0 |  | 6881 | 4611 | 11492 | 4222 | 908 | 2416 | 54 | 1253 | 2133 | 0 | 0 | 317 | 160 | 29 | 0 | 2013.14 | 72.64
7:00 | 0 | 0 | 130 | 180 | 0 | 42 | 0 | 405 | 331 |  | 0 | 450 | 303 | 8 | 80 | 0 | 0 | 0 | 193 | 17 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 20 | 26 | 33 | 31 | 8 | 0 | 0 | 0 | 100 | 0 | 8 | 224 | 0 | 0 | 0 |  | 12 | 40 | 50 | 44 | 0 | 6 | 5 | 34 | 0 | 0 | 0 | 310 | 320 | 204 | 197 | 0 | 42 | 0 | 0 | 51 | 0 | 36 | 52 | 17 | 11 | 33 | 20 | 148 | 100 | 0 | 19 | 0 | 43 | 40 | 50 | 46 | 112 | 0 | 56 | 75 | 0 | 188 | 0 | 0 | 10 | 295 | 16 | 5 | 0 | 47 | 0 | 0 | 68 | 0 | 16 | 6 | 38 | 17 | 5 | 378 | 18 | 88 | 17 | 1 | 69 | 17 | 54 | 34 | 9 | 38 | 360 | 0 | 6 | 17 | 17 | 0 | 35 | 7 | 18 | 17 | 0 | 18 | 0 | 0 | 0 |  | 908 | 0 | 165 | 0 | 79 | 0 | 0 | 0 | 14 | 49 | 16 | 172 | 25 | 0 | 0 | 0 | 0 | 0 | 13 | 35 | 21 | 25 | 21 | 0 | 0 | 20 | 0 | 8 | 74 | 0 | 230 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 377 | 17 | 0 | 35 | 105 | 0 | 0 | 1 | 35 | 300 | 0 | 0 | 17 | 1 | 23 | 0 | 0 | 0 | 325 | 7 | 150 | 1051 | 48 | 0 |  | 6753 | 4695 | 11448 | 4204 | 908 | 2418 | 0 | 1232 | 2130 | 0 | 0 | 308 | 148 | 100 | 0 | 1482.16 | 72.64
8:00 | 0 | 0 | 130 | 180 | 0 | 42 | 0 | 406 | 314 |  | 0 | 450 | 253 | 8 | 80 | 0 | 0 | 0 | 116 | 17 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 20 | 26 | 33 | 31 | 8 | 0 | 0 | 0 | 105 | 0 | 8 | 225 | 0 | 0 | 0 |  | 12 | 40 | 50 | 44 | 0 | 6 | 5 | 27 | 0 | 0 | 0 | 275 | 280 | 206 | 195 | 0 | 40 | 0 | 0 | 51 | 0 | 36 | 50 | 17 | 11 | 33 | 17 | 148 | 98 | 0 | 19 | 1 | 43 | 40 | 50 | 43 | 112 | 0 | 61 | 75 | 0 | 188 | 0 | 0 | 10 | 290 | 16 | 5 | 0 | 47 | 0 | 0 | 68 | 0 | 17 | 11 | 38 | 17 | 5 | 377 | 18 | 88 | 17 | 2 | 69 | 17 | 54 | 34 | 9 | 38 | 354 | 0 | 25 | 17 | 17 | 0 | 35 | 14 | 18 | 17 | 0 | 18 | 0 | 0 | 0 |  | 909 | 0 | 160 | 0 | 80 | 0 | 0 | 0 | 14 | 35 | 16 | 169 | 22 | 0 | 0 | 0 | 0 | 0 | 13 | 35 | 21 | 25 | 21 | 0 | 0 | 19 | 0 | 8 | 75 | 0 | 230 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 344 | 17 | 0 | 35 | 105 | 28 | 0 | 1 | 35 | 300 | 0 | 0 | 17 | 2 | 38 | 0 | 0 | 0 | 325 | 15 | 150 | 1055 | 94 | 0 |  | 6542 | 4739 | 11281 | 4035 | 909 | 2297 | 0 | 1260 | 2135 | 0 | 0 | 294 | 148 | 203 | 0 | 1737.145 | 72.64
9:00 | 0 | 0 | 130 | 180 | 0 | 42 | 0 | 378 | 308 |  | 0 | 450 | 275 | 8 | 65 | 0 | 0 | 0 | 127 | 17 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 22 | 33 | 31 | 8 | 0 | 0 | 0 | 100 | 0 | 8 | 221 | 0 | 0 | 0 |  | 12 | 40 | 50 | 44 | 0 | 6 | 5 | 25 | 0 | 0 | 0 | 295 | 290 | 202 | 195 | 0 | 39 | 0 | 0 | 51 | 0 | 36 | 37 | 17 | 11 | 32 | 17 | 136 | 68 | 0 | 19 | 2 | 43 | 40 | 50 | 46 | 80 | 0 | 42 | 75 | 0 | 193 | 0 | 0 | 10 | 280 | 16 | 5 | 0 | 47 | 0 | 0 | 68 | 0 | 16 | 12 | 38 | 17 | 5 | 377 | 18 | 88 | 17 | 3 | 69 | 17 | 54 | 0 | 9 | 38 | 380 | 0 | 34 | 17 | 17 | 0 | 35 | 22 | 18 | 17 | 0 | 18 | 0 | 0 | 0 |  | 909 | 0 | 160 | 0 | 32 | 0 | 0 | 0 | 16 | 35 | 16 | 167 | 23 | 16 | 0 | 0 | 0 | 0 | 13 | 35 | 21 | 8 | 22 | 0 | 0 | 17 | 0 | 8 | 75 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 336 | 17 | 0 | 35 | 105 | 33 | 0 | 6 | 35 | 300 | 0 | 0 | 17 | 3 | 62 | 0 | 0 | 0 | 325 | 23 | 150 | 1057 | 136 | 0 |  | 6440 | 4713 | 11153 | 3955 | 909 | 2263 | 0 | 1153 | 2137 | 0 | 0 | 297 | 136 | 303 | 0 | 1907.135 | 72.64
10:00 | 0 | 0 | 130 | 180 | 0 | 42 | 0 | 351 | 307 |  | 0 | 450 | 280 | 8 | 48 | 0 | 0 | 0 | 127 | 17 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 22 | 33 | 31 | 8 | 0 | 25 | 0 | 100 | 0 | 8 | 218 | 0 | 0 | 0 |  | 12 | 40 | 50 | 44 | 0 | 6 | 5 | 25 | 0 | 0 | 0 | 305 | 300 | 199 | 195 | 0 | 39 | 0 | 0 | 51 | 0 | 35 | 8 | 17 | 8 | 32 | 17 | 148 | 68 | 0 | 19 | 2 | 43 | 40 | 47 | 46 | 80 | 0 | 42 | 78 | 0 | 193 | 0 | 0 | 9 | 305 | 16 | 5 | 0 | 47 | 0 | 0 | 69 | 0 | 14 | 15 | 38 | 17 | 5 | 378 | 18 | 88 | 17 | 4 | 69 | 17 | 54 | 0 | 9 | 38 | 380 | 0 | 40 | 17 | 17 | 0 | 35 | 28 | 18 | 17 | 0 | 18 | 0 | 0 | 0 |  | 909 | 0 | 165 | 0 | 32 | 0 | 0 | 0 | 13 | 35 | 16 | 167 | 27 | 16 | 0 | 0 | 0 | 0 | 13 | 35 | 21 | 8 | 32 | 0 | 0 | 15 | 0 | 8 | 75 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 336 | 17 | 0 | 35 | 85 | 34 | 0 | 7 | 35 | 300 | 0 | 0 | 17 | 4 | 81 | 0 | 0 | 0 | 324 | 28 | 150 | 1053 | 169 | 0 |  | 6474 | 4762 | 11236 | 3945 | 909 | 2293 | 0 | 1087 | 2132 | 25 | 0 | 319 | 148 | 378 | 0 | 1780.12 | 72.63
11:00 | 0 | 0 | 130 | 180 | 0 | 42 | 0 | 356 | 333 |  | 0 | 450 | 254 | 8 | 50 | 0 | 0 | 0 | 161 | 17 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 15 | 22 | 14 | 33 | 28 | 8 | 0 | 25 | 0 | 100 | 0 | 8 | 218 | 0 | 0 | 0 |  | 12 | 30 | 50 | 44 | 0 | 6 | 7 | 25 | 0 | 0 | 0 | 325 | 320 | 196 | 195 | 0 | 38 | 0 | 0 | 51 | 0 | 42 | 8 | 17 | 8 | 25 | 17 | 138 | 53 | 0 | 19 | 2 | 43 | 40 | 47 | 49 | 80 | 0 | 50 | 78 | 0 | 192 | 0 | 0 | 10 | 310 | 16 | 5 | 0 | 47 | 0 | 0 | 68 | 0 | 18 | 20 | 38 | 33 | 5 | 389 | 18 | 88 | 17 | 2 | 69 | 17 | 56 | 0 | 9 | 38 | 370 | 6 | 34 | 17 | 17 | 0 | 35 | 30 | 18 | 17 | 0 | 18 | 0 | 0 | 2 |  | 909 | 0 | 160 | 0 | 32 | 0 | 0 | 0 | 13 | 30 | 16 | 164 | 27 | 16 | 0 | 0 | 0 | 0 | 13 | 34 | 21 | 8 | 22 | 0 | 0 | 15 | 0 | 8 | 75 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 338 | 17 | 0 | 35 | 102 | 33 | 0 | 7 | 35 | 300 | 0 | 0 | 17 | 4 | 91 | 35 | 0 | 0 | 324 | 32 | 150 | 1054 | 187 | 0 |  | 6593 | 4824 | 11417 | 3989 | 909 | 2304 | 0 | 1192 | 2133 | 25 | 0 | 316 | 138 | 409 | 2 | 1702.765 | 72.63
12:00 | 0 | 0 | 130 | 180 | 0 | 42 | 0 | 398 | 332 |  | 0 | 450 | 293 | 9 | 53 | 0 | 0 | 0 | 187 | 17 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 15 | 22 | 14 | 33 | 25 | 8 | 60 | 25 | 0 | 100 | 0 | 8 | 216 | 0 | 0 | 0 |  | 12 | 30 | 50 | 44 | 0 | 6 | 7 | 17 | 0 | 0 | 0 | 290 | 280 | 197 | 192 | 0 | 35 | 0 | 0 | 51 | 0 | 40 | 0 | 17 | 8 | 25 | 17 | 146 | 31 | 0 | 19 | 2 | 43 | 39 | 50 | 48 | 112 | 0 | 54 | 79 | 0 | 191 | 0 | 0 | 10 | 290 | 16 | 5 | 0 | 47 | 12 | 0 | 67 | 85 | 17 | 19 | 38 | 52 | 5 | 398 | 18 | 86 | 17 | 2 | 69 | 17 | 54 | 34 | 9 | 38 | 354 | 17 | 47 | 17 | 17 | 0 | 34 | 31 | 34 | 17 | 0 | 18 | 0 | 0 | 2 |  | 909 | 0 | 160 | 0 | 44 | 0 | 0 | 0 | 11 | 30 | 16 | 164 | 28 | 16 | 0 | 0 | 0 | 0 | 13 | 32 | 28 | 25 | 30 | 0 | 0 | 13 | 0 | 8 | 76 | 0 | 230 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 414 | 17 | 0 | 35 | 105 | 33 | 0 | 7 | 35 | 410 | 0 | 0 | 17 | 4 | 87 | 35 | 0 | 0 | 318 | 22 | 150 | 1067 | 189 | 0 |  | 6884 | 5076 | 11960 | 4036 | 909 | 2421 | 97 | 1345 | 2251 | 25 | 0 | 318 | 146 | 410 | 2 | 1470.7 | 72.63
13:00 | 0 | 0 | 130 | 180 | 0 | 42 | 0 | 397 | 317 |  | 0 | 450 | 242 | 9 | 61 | 0 | 0 | 0 | 191 | 17 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 15 | 22 | 16 | 33 | 25 | 8 | 60 | 25 | 0 | 100 | 0 | 8 | 218 | 0 | 0 | 0 |  | 12 | 30 | 50 | 44 | 0 | 14 | 7 | 28 | 0 | 0 | 0 | 275 | 275 | 201 | 192 | 0 | 35 | 0 | 0 | 51 | 0 | 34 | 0 | 17 | 11 | 25 | 17 | 160 | 53 | 0 | 17 | 2 | 43 | 38 | 50 | 47 | 112 | 0 | 52 | 77 | 0 | 190 | 0 | 0 | 10 | 300 | 16 | 5 | 0 | 47 | 106 | 0 | 67 | 93 | 17 | 20 | 38 | 78 | 5 | 398 | 18 | 86 | 17 | 4 | 69 | 17 | 54 | 51 | 9 | 38 | 335 | 17 | 45 | 17 | 17 | 0 | 33 | 31 | 36 | 17 | 0 | 18 | 0 | 0 | 6 |  | 909 | 0 | 160 | 0 | 72 | 0 | 0 | 0 | 11 | 40 | 16 | 168 | 29 | 16 | 0 | 0 | 0 | 0 | 13 | 32 | 28 | 25 | 30 | 0 | 0 | 11 | 0 | 8 | 73 | 0 | 230 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 374 | 17 | 0 | 35 | 105 | 33 | 0 | 7 | 35 | 560 | 0 | 0 | 17 | 4 | 95 | 35 | 0 | 0 | 325 | 31 | 150 | 1067 | 181 | 0 |  | 7002 | 5265 | 12267 | 4056 | 909 | 2332 | 199 | 1433 | 2405 | 25 | 0 | 322 | 160 | 420 | 6 | 1273.015 | 72.62
14:00 | 0 | 0 | 130 | 180 | 0 | 42 | 0 | 402 | 323 |  | 0 | 450 | 299 | 8 | 61 | 0 | 0 | 0 | 154 | 17 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 15 | 20 | 16 | 33 | 26 | 8 | 60 | 25 | 0 | 100 | 0 | 8 | 217 | 0 | 0 | 0 |  | 12 | 30 | 50 | 44 | 0 | 19 | 7 | 23 | 0 | 0 | 0 | 315 | 310 | 196 | 192 | 0 | 34 | 0 | 0 | 51 | 0 | 34 | 0 | 17 | 11 | 25 | 17 | 162 | 36 | 0 | 17 | 2 | 43 | 38 | 50 | 47 | 112 | 0 | 50 | 76 | 0 | 190 | 0 | 0 | 10 | 270 | 16 | 5 | 0 | 47 | 0 | 0 | 66 | 0 | 16 | 16 | 38 | 106 | 5 | 389 | 18 | 86 | 17 | 2 | 69 | 17 | 54 | 51 | 9 | 38 | 360 | 17 | 41 | 17 | 17 | 0 | 32 | 28 | 36 | 17 | 0 | 18 | 0 | 0 | 4 |  | 909 | 0 | 160 | 0 | 76 | 0 | 0 | 0 | 11 | 25 | 16 | 168 | 32 | 16 | 0 | 0 | 0 | 0 | 13 | 32 | 28 | 25 | 30 | 0 | 0 | 11 | 0 | 8 | 74 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 326 | 17 | 0 | 35 | 105 | 33 | 0 | 7 | 35 | 622 | 0 | 0 | 17 | 4 | 85 | 35 | 0 | 0 | 325 | 28 | 150 | 1075 | 168 | 0 |  | 6878 | 5201 | 12079 | 4035 | 909 | 2314 | 0 | 1466 | 2476 | 25 | 0 | 307 | 162 | 381 | 4 | 1357.055 | 72.63
15:00 | 0 | 0 | 130 | 180 | 0 | 42 | 0 | 395 | 322 |  | 0 | 450 | 269 | 8 | 61 | 0 | 0 | 0 | 150 | 17 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 15 | 20 | 15 | 33 | 26 | 8 | 60 | 25 | 0 | 100 | 0 | 11 | 222 | 0 | 0 | 0 |  | 0 | 30 | 45 | 44 | 0 | 19 | 7 | 20 | 0 | 0 | 0 | 275 | 270 | 199 | 192 | 0 | 34 | 0 | 0 | 51 | 0 | 34 | 0 | 15 | 11 | 25 | 17 | 166 | 20 | 0 | 0 | 0 | 40 | 38 | 50 | 48 | 112 | 0 | 49 | 75 | 0 | 180 | 0 | 0 | 10 | 290 | 16 | 5 | 0 | 47 | 0 | 0 | 0 | 0 | 15 | 11 | 38 | 100 | 5 | 387 | 9 | 70 | 17 | 2 | 69 | 17 | 54 | 52 | 9 | 38 | 362 | 17 | 31 | 17 | 17 | 0 | 33 | 25 | 36 | 17 | 0 | 18 | 0 | 0 | 4 |  | 906 | 0 | 165 | 0 | 75 | 0 | 0 | 0 | 12 | 25 | 16 | 150 | 33 | 16 | 0 | 0 | 0 | 0 | 13 | 32 | 28 | 25 | 35 | 0 | 0 | 10 | 0 | 8 | 74 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 285 | 17 | 0 | 35 | 105 | 32 | 0 | 7 | 35 | 410 | 0 | 0 | 17 | 3 | 70 | 35 | 0 | 0 | 323 | 22 | 150 | 1073 | 134 | 0 |  | 6605 | 4876 | 11481 | 3889 | 906 | 2259 | 0 | 1359 | 2260 | 25 | 0 | 308 | 166 | 305 | 4 | 1928.145 | 72.62
16:00 | 0 | 0 | 130 | 180 | 0 | 42 | 0 | 399 | 322 |  | 0 | 450 | 299 | 8 | 61 | 0 | 0 | 0 | 189 | 17 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 15 | 20 | 17 | 25 | 20 | 8 | 60 | 25 | 0 | 100 | 0 | 16 | 218 | 0 | 0 | 0 |  | 1 | 30 | 50 | 44 | 0 | 19 | 8 | 20 | 0 | 0 | 0 | 275 | 270 | 197 | 185 | 0 | 34 | 0 | 0 | 51 | 0 | 34 | 0 | 17 | 8 | 25 | 20 | 164 | 43 | 0 | 15 | 1 | 40 | 38 | 46 | 48 | 80 | 0 | 57 | 77 | 0 | 179 | 0 | 0 | 10 | 280 | 16 | 5 | 0 | 47 | 0 | 0 | 62 | 0 | 15 | 3 | 38 | 100 | 3 | 403 | 17 | 70 | 17 | 2 | 69 | 17 | 54 | 52 | 8 | 38 | 340 | 17 | 26 | 17 | 17 | 0 | 31 | 16 | 36 | 17 | 0 | 18 | 0 | 0 | 2 |  | 908 | 0 | 185 | 0 | 75 | 0 | 0 | 0 | 12 | 25 | 16 | 166 | 33 | 16 | 0 | 0 | 0 | 0 | 13 | 38 | 28 | 25 | 22 | 0 | 0 | 11 | 0 | 8 | 74 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 295 | 17 | 0 | 35 | 105 | 31 | 0 | 5 | 35 | 300 | 0 | 0 | 17 | 0 | 42 | 35 | 0 | 0 | 321 | 15 | 150 | 1055 | 91 | 0 |  | 6702 | 4704 | 11406 | 3992 | 908 | 2249 | 0 | 1429 | 2130 | 25 | 0 | 306 | 164 | 201 | 2 | 1665.52 | 72.62
17:00 | 0 | 0 | 130 | 180 | 0 | 42 | 0 | 399 | 322 |  | 0 | 450 | 257 | 11 | 61 | 0 | 0 | 0 | 193 | 17 | 8 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 15 | 20 | 18 | 25 | 20 | 8 | 60 | 25 | 0 | 100 | 0 | 16 | 218 | 0 | 0 | 0 |  | 12 | 30 | 67 | 44 | 0 | 26 | 8 | 29 | 0 | 0 | 0 | 275 | 270 | 200 | 185 | 0 | 34 | 0 | 0 | 51 | 0 | 35 | 0 | 17 | 8 | 25 | 20 | 160 | 48 | 0 | 15 | 1 | 43 | 38 | 50 | 48 | 112 | 0 | 59 | 80 | 0 | 180 | 0 | 0 | 10 | 285 | 16 | 5 | 0 | 47 | 0 | 0 | 66 | 0 | 15 | 5 | 38 | 105 | 5 | 403 | 17 | 70 | 17 | 1 | 69 | 17 | 54 | 52 | 9 | 38 | 380 | 17 | 13 | 17 | 17 | 0 | 32 | 6 | 36 | 26 | 0 | 18 | 0 | 0 | 1 |  | 909 | 0 | 195 | 0 | 75 | 0 | 0 | 0 | 15 | 25 | 16 | 159 | 28 | 16 | 0 | 0 | 0 | 0 | 13 | 40 | 28 | 25 | 22 | 0 | 0 | 13 | 0 | 8 | 75 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 325 | 17 | 0 | 35 | 105 | 47 | 0 | 3 | 35 | 300 | 0 | 0 | 17 | 1 | 3 | 35 | 0 | 0 | 321 | 7 | 150 | 1056 | 46 | 0 |  | 6823 | 4665 | 11488 | 4054 | 909 | 2287 | 0 | 1505 | 2132 | 25 | 0 | 329 | 160 | 86 | 1 | 1300.71 | 72.61
18:00 | 0 | 0 | 130 | 180 | 0 | 42 | 0 | 398 | 282 |  | 0 | 400 | 266 | 22 | 70 | 0 | 0 | 0 | 132 | 18 | 8 | 98 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 15 | 20 | 18 | 25 | 20 | 24 | 60 | 25 | 0 | 100 | 0 | 16 | 224 | 0 | 0 | 0 |  | 12 | 62 | 67 | 44 | 0 | 44 | 9 | 31 | 0 | 0 | 0 | 275 | 270 | 201 | 194 | 0 | 35 | 0 | 0 | 51 | 0 | 34 | 0 | 17 | 11 | 25 | 20 | 148 | 64 | 0 | 15 | 0 | 43 | 38 | 50 | 47 | 112 | 0 | 40 | 40 | 0 | 180 | 17 | 0 | 10 | 270 | 16 | 5 | 0 | 50 | 0 | 0 | 68 | 0 | 21 | 1 | 38 | 105 | 20 | 353 | 17 | 70 | 32 | 0 | 120 | 17 | 54 | 52 | 56 | 38 | 362 | 17 | 3 | 17 | 18 | 0 | 33 | 2 | 44 | 34 | 0 | 18 | 0 | 0 | 0 |  | 909 | 0 | 205 | 0 | 76 | 0 | 0 | 0 | 17 | 35 | 16 | 159 | 27 | 16 | 0 | 0 | 0 | 0 | 13 | 40 | 28 | 25 | 32 | 43 | 0 | 16 | 0 | 8 | 74 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 287 | 17 | 0 | 35 | 105 | 60 | 0 | 1 | 35 | 300 | 0 | 0 | 17 | 0 | 0 | 39 | 0 | 0 | 321 | 2 | 150 | 1071 | 11 | 0 |  | 6837 | 4690 | 11527 | 3960 | 909 | 2125 | 0 | 1778 | 2146 | 25 | 0 | 416 | 148 | 20 | 0 | 690.465 | 72.61
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1373.29 | 0
19:00 | 0 | 0 | 130 | 180 | 0 | 42 | 0 | 366 | 333 |  | 0 | 450 | 303 | 22 | 80 | 0 | 0 | 0 | 191 | 26 | 16 | 150 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 15 | 20 | 18 | 33 | 20 | 48 | 60 | 25 | 0 | 100 | 0 | 24 | 219 | 0 | 0 | 0 |  | 12 | 62 | 67 | 66 | 0 | 44 | 9 | 31 | 0 | 0 | 0 | 340 | 330 | 194 | 195 | 0 | 37 | 0 | 0 | 51 | 0 | 35 | 5 | 17 | 11 | 25 | 20 | 138 | 55 | 0 | 15 | 0 | 43 | 38 | 50 | 48 | 112 | 0 | 58 | 81 | 0 | 181 | 17 | 0 | 10 | 295 | 16 | 3 | 0 | 137 | 130 | 0 | 86 | 55 | 107 | 0 | 90 | 105 | 87 | 390 | 85 | 70 | 51 | 0 | 290 | 17 | 54 | 52 | 95 | 90 | 380 | 17 | 0 | 54 | 34 | 0 | 35 | 0 | 97 | 34 | 0 | 18 | 0 | 0 | 0 |  | 909 | 0 | 220 | 0 | 79 | 0 | 0 | 0 | 26 | 65 | 40 | 167 | 32 | 16 | 0 | 0 | 0 | 0 | 13 | 58 | 28 | 8 | 37 | 25 | 0 | 17 | 0 | 8 | 74 | 0 | 230 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 382 | 17 | 0 | 35 | 105 | 62 | 0 | 0 | 55 | 300 | 0 | 0 | 80 | 0 | 0 | 80 | 0 | 0 | 320 | 0 | 150 | 1056 | 0 | 0 |  | 8369 | 4979 | 13348 | 4211 | 909 | 2432 | 185 | 2787 | 2130 | 25 | 0 | 531 | 138 | 0 | 0 | 479.41 | 72.6
19:30 | 0 | 0 | 130 | 180 | 0 | 42 | 0 | 397 | 332 |  | 0 | 450 | 301 | 24 | 69 | 15 | 0 | 0 | 192 | 26 | 16 | 150 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 15 | 20 | 18 | 33 | 28 | 48 | 60 | 25 | 0 | 100 | 0 | 25 | 222 | 0 | 0 | 0 |  | 12 | 62 | 68 | 66 | 0 | 44 | 9 | 41 | 0 | 0 | 0 | 305 | 275 | 179 | 195 | 0 | 39 | 0 | 0 | 51 | 0 | 35 | 8 | 17 | 11 | 25 | 20 | 138 | 54 | 0 | 16 | 0 | 43 | 38 | 50 | 48 | 112 | 0 | 60 | 81 | 0 | 180 | 17 | 0 | 10 | 290 | 16 | 3 | 0 | 147 | 300 | 0 | 87 | 85 | 120 | 0 | 90 | 120 | 120 | 404 | 85 | 86 | 51 | 0 | 290 | 17 | 54 | 52 | 95 | 90 | 390 | 17 | 0 | 54 | 34 | 0 | 35 | 0 | 97 | 34 | 0 | 140 | 0 | 0 | 1 |  | 804 | 0 | 220 | 0 | 79 | 0 | 0 | 0 | 27 | 65 | 40 | 167 | 32 | 16 | 0 | 0 | 0 | 28 | 13 | 80 | 28 | 25 | 37 | 34 | 5 | 19 | 0 | 8 | 75 | 0 | 230 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 414 | 17 | 0 | 50 | 105 | 62 | 0 | 0 | 55 | 390 | 0 | 0 | 150 | 0 | 0 | 110 | 0 | 0 | 310 | 0 | 150 | 1056 | 0 | 0 |  | 8758 | 5249 | 14007 | 4239 | 804 | 2468 | 385 | 3026 | 2211 | 25 | 0 | 710 | 138 | 0 | 1 | 375.315 | 0
20:00 | 0 | 0 | 130 | 180 | 0 | 55 | 0 | 397 | 332 |  | 0 | 450 | 296 | 24 | 69 | 15 | 0 | 0 | 193 | 26 | 16 | 150 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 15 | 20 | 25 | 33 | 28 | 48 | 60 | 25 | 0 | 100 | 0 | 25 | 224 | 0 | 0 | 0 |  | 12 | 62 | 68 | 66 | 0 | 44 | 9 | 42 | 0 | 0 | 0 | 305 | 275 | 170 | 177 | 0 | 39 | 0 | 0 | 51 | 0 | 35 | 8 | 18 | 11 | 25 | 20 | 150 | 80 | 0 | 16 | 0 | 43 | 38 | 50 | 48 | 112 | 0 | 60 | 81 | 0 | 181 | 17 | 0 | 10 | 300 | 16 | 5 | 0 | 147 | 251 | 0 | 87 | 90 | 131 | 0 | 90 | 120 | 119 | 403 | 85 | 86 | 51 | 0 | 294 | 17 | 54 | 52 | 95 | 90 | 396 | 17 | 0 | 54 | 34 | 0 | 35 | 0 | 97 | 34 | 0 | 163 | 0 | 0 | 1 |  | 804 | 0 | 220 | 0 | 79 | 0 | 0 | 0 | 20 | 73 | 40 | 170 | 33 | 16 | 0 | 0 | 0 | 28 | 13 | 84 | 28 | 25 | 40 | 34 | 15 | 19 | 0 | 8 | 75 | 0 | 230 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 414 | 17 | 0 | 50 | 105 | 55 | 0 | 0 | 55 | 440 | 0 | 0 | 150 | 0 | 0 | 114 | 0 | 0 | 303 | 0 | 150 | 1054 | 0 | 0 |  | 8800 | 5324 | 14124 | 4293 | 804 | 2470 | 341 | 3037 | 2252 | 25 | 0 | 751 | 150 | 0 | 1 | 359.08 | 72.61
21:00 | 0 | 0 | 130 | 180 | 0 | 75 | 0 | 398 | 332 |  | 0 | 450 | 279 | 21 | 80 | 30 | 0 | 0 | 194 | 26 | 16 | 150 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 20 | 25 | 33 | 22 | 48 | 60 | 25 | 0 | 100 | 0 | 25 | 224 | 0 | 0 | 0 |  | 12 | 60 | 68 | 66 | 0 | 44 | 9 | 42 | 0 | 0 | 0 | 305 | 270 | 154 | 178 | 0 | 41 | 0 | 0 | 51 | 0 | 41 | 0 | 18 | 11 | 25 | 20 | 150 | 103 | 0 | 16 | 0 | 43 | 38 | 50 | 49 | 112 | 0 | 55 | 81 | 0 | 187 | 17 | 0 | 10 | 300 | 16 | 5 | 0 | 145 | 233 | 0 | 87 | 97 | 131 | 0 | 90 | 120 | 134 | 398 | 85 | 86 | 51 | 0 | 300 | 17 | 54 | 52 | 95 | 90 | 392 | 17 | 0 | 54 | 34 | 0 | 35 | 0 | 97 | 34 | 0 | 163 | 0 | 0 | 3 |  | 803 | 0 | 225 | 0 | 80 | 0 | 0 | 0 | 21 | 68 | 40 | 170 | 35 | 16 | 0 | 0 | 0 | 28 | 13 | 84 | 28 | 25 | 37 | 34 | 30 | 19 | 0 | 8 | 75 | 0 | 230 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 415 | 17 | 0 | 50 | 105 | 56 | 0 | 0 | 55 | 610 | 0 | 0 | 150 | 0 | 0 | 114 | 0 | 0 | 325 | 0 | 150 | 1053 | 0 | 0 |  | 8833 | 5544 | 14377 | 4309 | 803 | 2478 | 330 | 3073 | 2443 | 25 | 0 | 763 | 150 | 0 | 3 | 375.315 | 72.6
22:00 | 0 | 0 | 130 | 180 | 0 | 78 | 0 | 406 | 322 |  | 0 | 450 | 281 | 24 | 80 | 15 | 0 | 0 | 195 | 26 | 16 | 150 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 20 | 25 | 33 | 22 | 48 | 60 | 25 | 0 | 100 | 0 | 25 | 225 | 0 | 0 | 0 |  | 12 | 61 | 68 | 66 | 0 | 44 | 9 | 42 | 0 | 0 | 0 | 280 | 270 | 155 | 178 | 0 | 41 | 0 | 0 | 51 | 0 | 45 | 0 | 18 | 11 | 25 | 20 | 154 | 104 | 0 | 16 | 0 | 43 | 40 | 49 | 49 | 112 | 0 | 56 | 81 | 0 | 187 | 17 | 0 | 10 | 290 | 16 | 5 | 0 | 145 | 233 | 0 | 87 | 94 | 131 | 0 | 90 | 120 | 140 | 404 | 85 | 86 | 34 | 0 | 123 | 17 | 54 | 52 | 96 | 90 | 390 | 17 | 0 | 54 | 34 | 0 | 35 | 0 | 96 | 34 | 0 | 163 | 0 | 0 | 3 |  | 803 | 0 | 225 | 0 | 80 | 0 | 0 | 0 | 23 | 68 | 40 | 170 | 36 | 16 | 0 | 0 | 0 | 28 | 13 | 84 | 28 | 25 | 37 | 0 | 30 | 19 | 0 | 8 | 75 | 0 | 230 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 414 | 17 | 0 | 50 | 105 | 49 | 0 | 0 | 55 | 622 | 0 | 0 | 150 | 0 | 0 | 114 | 0 | 0 | 325 | 0 | 150 | 1062 | 0 | 0 |  | 8577 | 5523 | 14100 | 4300 | 803 | 2462 | 327 | 2792 | 2464 | 25 | 0 | 770 | 154 | 0 | 3 | 0 | 72.6
23:00 | 0 | 0 | 130 | 180 | 0 | 77 | 0 | 407 | 322 |  | 0 | 450 | 274 | 24 | 80 | 15 | 0 | 0 | 200 | 26 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 22 | 20 | 25 | 33 | 30 | 48 | 60 | 0 | 0 | 100 | 0 | 8 | 225 | 0 | 0 | 0 |  | 9 | 53 | 68 | 66 | 0 | 44 | 9 | 42 | 0 | 0 | 0 | 280 | 270 | 157 | 178 | 0 | 41 | 0 | 0 | 51 | 0 | 45 | 0 | 18 | 11 | 25 | 20 | 164 | 106 | 0 | 16 | 0 | 43 | 40 | 50 | 49 | 112 | 0 | 57 | 81 | 0 | 187 | 17 | 0 | 10 | 280 | 16 | 5 | 0 | 147 | 150 | 0 | 68 | 95 | 79 | 0 | 90 | 120 | 140 | 403 | 18 | 87 | 34 | 0 | 87 | 17 | 54 | 52 | 52 | 38 | 384 | 0 | 0 | 46 | 34 | 0 | 35 | 0 | 72 | 34 | 0 | 18 | 0 | 0 | 3 |  | 804 | 0 | 215 | 0 | 80 | 0 | 0 | 0 | 22 | 50 | 40 | 158 | 35 | 16 | 0 | 0 | 0 | 28 | 13 | 76 | 28 | 25 | 37 | 0 | 29 | 20 | 0 | 8 | 73 | 0 | 230 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 421 | 17 | 0 | 35 | 105 | 34 | 0 | 0 | 35 | 580 | 0 | 0 | 150 | 0 | 0 | 55 | 0 | 0 | 333 | 0 | 150 | 1051 | 0 | 0 |  | 7841 | 5325 | 13166 | 4290 | 804 | 2452 | 245 | 2304 | 2417 | 0 | 0 | 487 | 164 | 0 | 3 | 0 | 72.6
24:00 | 0 | 0 | 130 | 180 | 0 | 75 | 0 | 400 | 327 |  | 0 | 450 | 303 | 24 | 80 | 15 | 0 | 0 | 191 | 26 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 20 | 25 | 33 | 31 | 8 | 60 | 0 | 0 | 100 | 0 | 8 | 220 | 0 | 0 | 0 |  | 12 | 39 | 68 | 66 | 0 | 6 | 9 | 42 | 0 | 0 | 0 | 335 | 320 | 152 | 147 | 0 | 41 | 0 | 0 | 51 | 0 | 45 | 0 | 18 | 11 | 25 | 20 | 140 | 104 | 0 | 16 | 0 | 43 | 40 | 50 | 49 | 112 | 0 | 55 | 81 | 0 | 183 | 17 | 0 | 10 | 320 | 16 | 5 | 0 | 145 | 290 | 0 | 68 | 95 | 29 | 0 | 50 | 17 | 25 | 383 | 18 | 88 | 34 | 0 | 87 | 17 | 61 | 52 | 9 | 38 | 384 | 0 | 0 | 17 | 34 | 0 | 35 | 0 | 54 | 19 | 0 | 18 | 0 | 0 | 4 |  | 803 | 0 | 210 | 0 | 80 | 0 | 0 | 0 | 17 | 50 | 40 | 169 | 36 | 16 | 0 | 0 | 0 | 28 | 13 | 76 | 28 | 25 | 37 | 0 | 29 | 21 | 0 | 8 | 74 | 0 | 230 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 414 | 17 | 0 | 35 | 105 | 34 | 0 | 0 | 35 | 320 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 150 | 1061 | 0 | 0 |  | 7520 | 5002 | 12522 | 4347 | 803 | 2488 | 385 | 1732 | 2155 | 0 | 0 | 468 | 140 | 0 | 4 | 0 | 72.6
KWH | 0 | 0 | 3042375 | 4284000 | 0 | 1140590 | 0 | 9601030 | 7752000 |  | 0 | 10194500 | 6958545 | 292800 | 1616124 | 93594 | 864800 | 0 | 4474000 | 433920 | 224640 | 1536480 | 0 | 0 | 0 | 0 | 128736 | 468960 | 464438 | 405576 | 460000 | 478620 | 773900 | 691200 | 384000 | 765030 | 306840 | 0 | 2400000 | 0 | 286731 | 5231896 | 0 | 0 | 0 |  | 277440 | 1045104 | 1308344 | 1253880 | 0 | 439200 | 159216 | 732480 | 0 | 0 | 0 | 7691000 | 7215000 | 4676000 | 4549818 | 0 | 913536 | 0 | 0 | 1134806 | 0 | 925264 | 477600 | 410112 | 240480 | 674300 | 431750 | 3589440 | 1937280 | 0 | 365688 | 14200 | 1017000 | 900360 | 1193400 | 1132776 | 2435073 | 0 | 1281888 | 1812480 | 0 | 4860700 | 100000 | 0 | 251460 | 7237000 | 372336 | 126712 | 0 | 1758872 | 2939811 | 0 | 1636800 | 1061807 | 918576 | 142020 | 1146240 | 1513440 | 749381 | 9261000 | 694800 | 2005181 | 602181 | 30480 | 2428800 | 450900 | 1339850 | 1136580 | 590520 | 1132800 | 8875100 | 234240 | 341310 | 581760 | 523145 | 0 | 855000 | 240586 | 981120 | 549360 | 0 | 874836 | 0 | 0 | 37488 |  | 21224727 | 0 | 4478976 | 0 | 1674240 | 0 | 0 | 0 | 338400 | 1003392 | 512625 | 4075559 | 730689 | 296256 | 0 | 0 | 0 | 285936 | 260770 | 1179776 | 577490 | 527665 | 611487 | 136099 | 115199 | 399360 | 0 | 172206 | 1736290 | 0 | 5674000 | 0 | 0 | 4192400 | 0 | 0 | 0 | 0 | 0 | 3882273 | 0 | 8675600 | 416640 | 0 | 967968 | 2539008 | 813628 | 0 | 58505 | 823200 | 10227500 | 0 | 0 | 1191600 | 36240 | 685440 | 848256 | 0 | 0 | 7709091 | 203942 | 3621800 | 25527273 | 1465270 | 0 |  | 174572432 | 119896776 | 294469208 | 101783299 | 21224727 | 56330577 | 4001618 | 39996284 | 54495954 | 306840 | 0 | 9484988 | 3589440 | 3217993 | 37488 | 0
Fuel Cost | 0 | 0 | 4441867.5 | 6383160 | 0 | 1516984.7 | 0 | 10081081.5 | 8372160 |  | 0 | 11112005 | 7723984.95 | 3273504 | 21413643 | 1240120.5 | 968576 | 0 | 7829500 | 6343910.4 | 3160684.8 | 24906340.8 | 0 | 0 | 0 | 0 | 1637521.92 | 6330960 | 6228113.58 | 304182 | 345000 | 0 | 0 | 0 | 6531840 | 1866673.2 | 82846.8 | 0 | 4536000 | 0 | 4688051.85 | 5441171.84 | 0 | 0 | 0 |  | 3620592 | 17432334.72 | 22268014.88 | 16939918.8 | 0 | 5081544 | 202204.32 | 2439158.4 | 0 | 0 | 0 | 8537010 | 7864350 | 5424160 | 5869265.22 | 0 | 1032295.68 | 0 | 0 | 1895126.02 | 0 | 15979309.28 | 6423720 | 561853.44 | 180360 | 1180025 | 323812.5 | 25772179.2 | 2111635.2 | 0 | 497335.68 | 226348 | 1393290 | 1188475.2 | 2076516 | 1959702.48 | 2800333.95 | 0 | 2486862.72 | 4132454.4 | 0 | 4909307 | 215000 | 0 | 497890.8 | 7237000 | 279252 | 96301.12 | 0 | 24008602.8 | 61618438.56 | 0 | 22064064 | 21947550.69 | 12722277.6 | 1660213.8 | 11829196.8 | 20673590.4 | 9944285.87 | 8520120 | 8448768 | 28994917.26 | 7617589.65 | 0 | 28514112 | 4910301 | 14242605.5 | 15423390.6 | 7611802.8 | 13344384 | 8165092 | 3033408 | 4931929.5 | 7382534.4 | 5953390.1 | 0 | 11166300 | 2875002.7 | 14687366.4 | 7235071.2 | 0 | 0 | 0 | 0 | 0 |  | 63674181 | 0 | 5016453.12 | 0 | 17428838.4 | 0 | 0 | 0 | 6094584 | 18061056 | 7366421.25 | 4564626.08 | 1417536.66 | 3229190.4 | 0 | 0 | 0 | 4795146.72 | 4560867.3 | 18451696.64 | 4446673 | 8738132.4 | 10340245.17 | 1855029.37 | 1943407.13 | 826675.2 | 0 | 130359.942 | 10087844.9 | 0 | 30015460 | 0 | 0 | 4863184 | 0 | 0 | 0 | 0 | 0 | 4503436.68 | 0 | 8588844 | 5599641.6 | 0 | 11451061.44 | 36688665.6 | 10333075.6 | 0 | 646480.25 | 9993648 | 92149775 | 0 | 0 | 8817840 | 409874.4 | 8040211.2 | 13003764.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 727421127.98 | 438133926.932 | 1165555054.912 | 116444013.722 | 63674181 | 68465637.78 | 83565989.25 | 511674064.77 | 132253079.9 | 82846.8 | 0 | 144833002.64 | 25772179.2 | 18790059.85 | 0 | 0
Yesterday Day Peak | 0 | 0 | 130 | 180 | 0 | 42 | 0 | 398 | 332 |  | 0 | 450 | 293 | 9 | 53 | 0 | 0 | 0 | 187 | 17 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 15 | 22 | 14 | 33 | 25 | 8 | 60 | 25 | 0 | 100 | 0 | 8 | 216 | 0 | 0 | 0 |  | 12 | 30 | 50 | 44 | 0 | 6 | 7 | 17 | 0 | 0 | 0 | 290 | 280 | 197 | 192 | 0 | 35 | 0 | 0 | 51 | 0 | 40 | 0 | 17 | 8 | 25 | 17 | 146 | 31 | 0 | 19 | 2 | 43 | 39 | 50 | 48 | 112 | 0 | 54 | 79 | 0 | 191 | 0 | 0 | 10 | 290 | 16 | 5 | 0 | 47 | 12 | 0 | 67 | 85 | 17 | 19 | 38 | 52 | 5 | 398 | 18 | 86 | 17 | 2 | 69 | 17 | 54 | 34 | 9 | 38 | 354 | 17 | 47 | 17 | 17 | 0 | 34 | 31 | 34 | 17 | 0 | 18 | 0 | 0 | 2 |  | 909 | 0 | 160 | 0 | 44 | 0 | 0 | 0 | 11 | 30 | 16 | 164 | 28 | 16 | 0 | 0 | 0 | 0 | 13 | 32 | 28 | 25 | 30 | 0 | 0 | 13 | 0 | 8 | 76 | 0 | 230 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 414 | 17 | 0 | 35 | 105 | 33 | 0 | 7 | 35 | 410 | 0 | 0 | 17 | 4 | 87 | 35 | 0 | 0 | 318 | 22 | 150 | 1067 | 189 | 0 |  | 11960 | DayPeak
Yesterday Evening Peak | 0 | 0 | 130 | 180 | 0 | 75 | 0 | 398 | 332 | 0 | 0 | 450 | 279 | 21 | 80 | 30 | 0 | 0 | 194 | 26 | 16 | 150 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 20 | 25 | 33 | 22 | 48 | 60 | 25 | 0 | 100 | 0 | 25 | 224 | 0 | 0 | 0 | 0 | 12 | 60 | 68 | 66 | 0 | 44 | 9 | 42 | 0 | 0 | 0 | 305 | 270 | 154 | 178 | 0 | 41 | 0 | 0 | 51 | 0 | 41 | 0 | 18 | 11 | 25 | 20 | 150 | 103 | 0 | 16 | 0 | 43 | 38 | 50 | 49 | 112 | 0 | 55 | 81 | 0 | 187 | 17 | 0 | 10 | 300 | 16 | 5 | 0 | 145 | 233 | 0 | 87 | 97 | 131 | 0 | 90 | 120 | 134 | 398 | 85 | 86 | 51 | 0 | 300 | 17 | 54 | 52 | 95 | 90 | 392 | 17 | 0 | 54 | 34 | 0 | 35 | 0 | 97 | 34 | 0 | 163 | 0 | 0 | 3 |  | 803 | 0 | 225 | 0 | 80 | 0 | 0 | 0 | 21 | 68 | 40 | 170 | 35 | 16 | 0 | 0 | 0 | 28 | 13 | 84 | 28 | 25 | 37 | 34 | 30 | 19 | 0 | 8 | 75 | 0 | 230 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 415 | 17 | 0 | 50 | 105 | 56 | 0 | 0 | 55 | 610 | 0 | 0 | 150 | 0 | 0 | 114 | 0 | 0 | 325 | 0 | 150 | 1053 | 0 | 0 |  | 14377 | EvPeak
Forecast for Evening | 0 | 0 | 130 | 180 | 0 | 78 | 0 | 400 | 330 | 0 | 0 | 450 | 300 | 25 | 80 | 30 | 0 | 0 | 195 | 32 | 16 | 150 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 20 | 25 | 33 | 33 | 50 | 60 | 25 | 0 | 100 | 0 | 25 | 225 |  | 0 | 0 | 0 | 12 | 64 | 68 | 66 | 0 | 44 | 10 | 30 | 0 | 0 | 0 | 320 | 320 | 200 | 185 | 0 | 40 | 0 | 0 | 51 | 0 | 46 | 50 | 17 | 11 | 25 | 21 | 152 | 100 | 0 | 19 | 0 | 43 | 40 | 50 | 48 | 112 | 0 | 60 | 84 | 0 | 190 | 17 | 0 | 10 | 305 | 16 | 11 | 0 | 145 | 300 | 0 | 84 | 100 | 149 | 0 | 90 | 120 | 150 | 400 | 84 | 88 | 51 | 0 | 300 | 17 | 54 | 98 | 94 | 90 | 400 | 17 | 0 | 54 | 34 | 0 | 35 |  | 97 | 35 | 0 | 163 |  | 0 |  |  | 927 | 0 | 200 |  | 83 | 0 | 0 | 0 | 35 | 80 | 40 | 170 | 35 | 16 | 0 | 0 | 0 | 30 | 0 | 90 | 28 | 25 | 40 | 52 | 35 | 22 | 0 | 8 | 75 | 0 | 230 | 0 | 0 | 160 |  | 0 | 0 | 0 | 0 | 170 | 0 | 400 | 17 | 0 | 50 | 105 | 55 | 0 | 0 | 57 | 622 | 0 |  | 150 |  |  | 115 | 0 |  | 320 |  | 150 | 748 |  | 0
Forecast for Day | 0 | 0 | 130 | 180 | 0 | 78 | 0 | 400 | 330 | 0 | 0 | 450 | 300 | 8 | 80 | 0 | 0 | 0 | 190 | 16 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 22 | 20 | 22 | 33 | 33 | 8 | 60 | 25 | 0 | 100 | 0 | 8 | 225 |  | 0 | 0 | 0 | 12 | 50 | 51 | 44 | 0 | 6 | 10 | 10 | 0 | 0 | 0 | 310 | 150 | 200 | 190 | 0 | 40 | 0 | 0 | 51 | 0 | 40 | 0 | 17 | 11 | 25 | 21 | 129 | 45 | 0 | 19 | 1.6 | 43 | 40 | 50 | 48 | 112 | 0 | 60 | 84 | 0 | 190 | 17 | 0 | 10 | 300 | 16 | 11 | 0 | 47 | 300 | 0 | 68 | 100 | 17 | 20 | 38 | 51 | 6 | 400 | 18 | 88 | 17 | 5 | 69 | 17 | 54 | 52 | 26 | 38 | 400 | 17 | 50 | 18 | 17 | 0 | 35 | 30 | 18 | 17 | 0 | 18 |  | 0 |  |  | 927 | 0 | 200 | 0 | 83 | 0 | 0 | 0 | 22 | 60 | 16 | 170 | 23 | 16 | 0 | 0 | 0 | 25 | 0 | 80 | 21 | 25 | 40 | 0 | 35 | 22 | 0 | 8 | 75 | 0 | 230 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 400 | 17 | 0 | 35 | 105 | 35 | 0 | 8 | 35 | 622 | 0 |  | 17 | 6 | 100 | 34 | 0 |  | 320 | 30 | 150 | 748 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 130 | 180 | 0 | 78 | 0 | 405 | 330 | 0 | 0 | 450 | 295 | 9 | 80 | 0 | 0 | 0 | 193 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 20 | 7 | 33 | 32 | 8 | 60 | 0 | 0 | 100 | 0 | 8 | 222 | 0 | 0 | 0 | 0 | 12 | 31 | 51 | 44 | 0 | 6 | 9 | 4 | 0 | 0 | 0 | 315 | 315 | 200 | 88 | 0 | 38 | 0 | 0 | 51 | 0 | 38 | 0 | 15 | 8 | 25 | 20 | 146 | 103 | 0 | 14 | 1 | 43 | 40 | 50 | 49 | 112 | 0 | 55 | 81 | 0 | 187 | 17 | 0 | 10 | 285 | 16 | 5 | 0 | 47 | 11 | 0 | 68 | 26 | 17 | 10 | 38 | 17 | 6 | 404 | 19 | 88 | 17 | 2 | 70 | 17 | 54 | 0 | 9 | 38 | 380 | 0 | 23 | 17 | 17 | 0 | 35 | 12 | 18 | 17 | 0 | 18 | 0 | 0 | 0 | 0 | 910 | 0 | 195 | 0 | 80 | 0 | 0 | 0 | 9 | 32 | 8 | 172 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 28 | 0 | 21 | 0 | 0 | 20 | 0 | 8 | 71 | 0 | 230 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 415 | 17 | 0 | 35 | 105 | 33 | 0 | 3 | 35 | 300 | 0 | 0 | 17 | 2 | 43 | 0 | 0 | 0 | 327 | 13 | 150 | 753 | 85 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
292.3904
| Minimum Generation |  | 11153 | 9:00
| Highest Generation |  | 14377 | 21:00
| Day Peak Generation |  | 11960 | 12:00
| Evening Peak Generation |  | 14377 | 21:00
| HVDC Max Flow |  | 910 | 4:00
| HVDC EvPeak Flow |  | 803 | 21:00
| Load factor L.F |  | 85.34% | [163 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-06-03
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-06-02 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 11960 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 11234
Evening Peak Generation : |  |  | 14377 | MW Hour : | 21:00 | Available Max Generation : |  | 14567
E.P. Demand (at gen end) : |  |  | 14770 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 15500
Maximum Generation : |  |  | 14377 | MW Hour : | 21:00 | Reserve(Generation end) |  | -
Total Gen. (MKWH) : |  |  | 294.4692 | System Load Factor : | 85.34% | Load Shed : |  | 860
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 840 | MW at | 19:30 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-06-03
Actual : |  | 72.58 | Ft.(MSL) , | Rule curve : | 76.52 | Ft.( MSL )
Gas Consumed : |  | Total = | 1200.86 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 184909651.502
: |  |  | Coal : | 132253079.9 | Oil : | 740073056.66 | Total : | 1057235788.062
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 5180.851 |  |  | 170 | 3.281%
Chittagong Area |  | 0 | 0:00 | 1427.276 |  |  | 120 | 8.408%
Khulna Area |  | 130 | 3120:00 | 2000.4478 |  |  | 120 | 5.999%
Rajshahi Area |  | 35 | 840:00 | 1739.7767 |  |  | 110 | 6.323%
Cumilla Area |  | 110 | 2640:00 | 1431.0033 |  |  | 90 | 6.289%
Mymensingh Area |  | 50 | 1200:00 | 1064.8547 |  |  | 120 | 11.27%
Sylhet Area |  | 0 | 0:00 | 596.2968 |  |  | 50 | 8.385%
Barisal Area |  | 0 | 0:00 | 497.4784 |  |  | 0 | 0%
Rangpur Area |  | 50 | 1200:00 | 972.9682 |  |  | 80 | 8.222%
Total |  | 375 |  | 14910.953 |  |  | 860
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,7
3) Bhula Nuton Biddut
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
9:23 | - | Ghorashal 230/132 kV AT-1 Transformer was switched on.
9:58 | 12:10 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T LT Project Work S/D Due to Isolator maintenance by NESCO entity at 33 KV | [5 empty] | 40.0MW load interrupt.
NESCO switching SS.
10:03 | 12:09 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T HT Project Work S/D. | [5 empty] | 40.0MW load interrupt.
- | 11:08 | Tongi GT 80 MW was sync.
12:00 | - | Day Peak Generation:11961 MW Load shed about 1471 MW.
14:32 | 15:05 | Kaliakoir-Tangail 132kV Ckt-1 Tripped from Kaliakoir 400/230/132kV end showing REC 650 relays Due to None. | [5 empty] | 157.0MW load interrupt.
14:32 | 14:55 | Kaliakoir-Tangail 132kV Ckt-2 Tripped from Kaliakoir 400/230/132kV end showing REC 650 relays. | [5 empty] | Kaliakoir 400/230/132kV end.
14:45 | - | Mymensingh SS bus coupler was closed.
14:45 | - | About 472 MW load interruption occurred under Tangail, Netrokona, Jamalpur, and Sherpur grid SS and 185 MW generation interruption | [5 empty] | 185MW generation interrupt.
|  | occurred under Mymensingh zone from 14:32 hrs to 14:45 hrs due to tripping of Kaliakoir-Tangail both Ckt. Bus coupler was closed at | [5 empty] | and 472MW load interrupt.
14:45 hrs at Mymensingh SS. Tangail-Kaliakoir 132kV ckt-2 was switched on at 14:55 hrs.
14:45 | - | 132kV Bus Coupler GCB Closed Due to RPCL, Jamalpur, Net & Sherpur Side energized ( cause of Tangail-Kaliakoir Both Ckt Tripped).
15:59 | 17:53 | BIPTC S/S 10CF15 Tripped showing Differential relays Due to Capacitor Unbalance.
16:09 | - | Mymensingh SS bus coupler was opened.
16:09 | - | 132kV Bus Coupler GCB(903B) Open Due to Ash-Sreepur Side( Mymensingh(T1&T2), Bhaluka Grid , Kish Grid ) Separate From
Kaliakoir Side by direction NLDC & XEN,GMD,Mym.----Low voltage <110KV in Mym Grid.
17:21 | 17:53 | BIPTC S/S 10CF15 Forced S/D Due to Rectification work due to the trip.
- | 17:53 | BIPTC S/S 10CF25 is restored.
18:32 | - | Mymensingh-Bhaluka 132kV ckt-1 was opened from Mymensingh end.
18:32 | - | 132kV Mym-Bhaluka Ckt-1 GCB(303B) Open Due to 132kV Sreepur- Bhaluka Line Over Load. Direction by NLDC.
21:00 | - | Evening Peak Generation: 14377 MW.
4:53 | 5:08 | Cumilla(N)-Meghnaghat 230 kV Ckt-1 Tripped from Cumilla(N) 230/132/33kV end showing Dist. Prot. Relay relays. and from
Meghnaghat 230/132kV end showing Distance Relay relays Due to Distance Tripped.
- | 5:08 | Cumilla(N)-Meghnaghat 230 kV Ckt-1 is restored.
6:58 | - | Adani Power Jharkhand Ltd. unit-2 was forced shutdown due to ESP Ash Evacuation problem. | [5 empty] | 748MW generation interrupt.
7:00 | - | Minimum generation 11388 MW.
7:20 | - | Chandpur 132/33kV S/S 422T LT Scheduled S/D Due to 33KV Side T-5 Incoming DS Red Hot Removing works. | [5 empty] | 25.0MW load interrupt.
7:20 | - | Chandpur 132/33kV S/S 422T HT Scheduled S/D Due to 33KV Side Incoming DS Red Hot Removing works. | [5 empty] | 25.0MW load interrupt.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-06-02 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 130 | 3042375 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4284000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 75 | 1140590 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 398 | 9601030 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 332 | 7752000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10194500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 21 | 292800 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 279 | 6958545 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 80 | 1616124 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 30 | 93594 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 20 | 0 | 0
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 405576
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 194 | 4474000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 26 | 433920 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 864800 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 16 | 224640 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 128736 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1536480
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 468960
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 464438
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 45 | 938620 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 773900
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 22 | 691200 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 48 | 384000
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 60 | 765030 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 145 | 1758872 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 233 | 2939811 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 97 | 1061807
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 131 | 918576 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 86 | 2005181 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 234240 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 581760 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 240586
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 34 | 549360 | Fuel shortage
| Dhaka area Total |  |  |  | 5867 | 3515 | 67820051
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 286731
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 142020
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 44 | 439200 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 25 | 306840 | Low Water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 224 | 5231896
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 602181 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 60 | 1045104 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 1308344 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 66 | 1253880 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 1146240 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 9 | 159216 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 732480
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30480
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 300 | 2428800
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 450900 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 54 | 1339850 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 90 | 1132800
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 34 | 523145 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 163 | 874836
| SS Power I |  | SS Power | 0 | 0 | 0 | 0 | On test.
| Cox's Bazar Wind |  | IPP | 66 | 0 | 3 | 37488 | On test.
| Chattogram area Total |  |  |  | 2545 | 1465 | 21872431
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 154 | 4676000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 305 | 7691000 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 7215000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 41 | 913536
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 178 | 4549818 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1134806
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 134 | 749381 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 41 | 925264 | Machine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 120 | 1513440 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 410112 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 240480
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 150 | 3589440
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 674300 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 477600 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 431750 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 52 | 1136580 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 95 | 590520 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 855000 | Fuel shortage
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 97 | 981120 | Fuel shortage
| Cumilla Area Total |  |  |  | 3096 | 1797 | 38755147
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 103 | 1937280 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 365688 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14200
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 87 | 1636800 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 85 | 694800 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 341310
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 277440 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 303 | 5267518
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1017000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 38 | 900360 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2435073 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1193400
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 49 | 1132776
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 126712 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 55 | 1281888
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1812480
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 187 | 4860700 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 100000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 372336 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7237000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 398 | 9261000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 251460
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 392 | 8875100
| Sylhet Area Total |  |  |  | 2427 | 1753 | 40857285
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 803 | 21224727
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 80 | 1674240 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 21 | 338400 | Fuel shortage
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 68 | 1003392 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 225 | 4478976 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 40 | 512625
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 416640 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 2539008
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 685440
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 325 | 7709091 | Coal shortage.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 2901 | 1684 | 40582539
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 296256 | Fuel shortage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 35 | 730689 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 170 | 4075559 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 610 | 10227500 | Coal shortage.
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 0 | 0 | Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1191600
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 150 | 3621800 | Coal shortage.
| Barisal Area Total |  |  |  | 2265 | 1131 | 20143404
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 28 | 285936 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 13 | 260770 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 28 | 28 | 577490
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 25 | 527665 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 611487 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 199 | 4192400 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 176 | 3882273 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 415 | 8675600
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 115199 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 19 | 399360 | Engine problem
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 172206 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 34 | 136099 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 84 | 1179776 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 967968 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 55 | 823200 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 36240
| Adani Power Jharkhanda Ltd |  | Import | 748*1 | 748 | 1053 | 25527273
| Rajshahi Area Total |  |  |  | 2905 | 2254 | 48370942
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 75 | 1736290
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 230 | 5674000
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 56 | 813628 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 58505
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 114 | 848256
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 203942
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 1465270
| Rangpur Area Total |  |  |  | 750 | 475 | 10799891
| Total |  |  |  | 23370 | 14377 | 294469208
| Eastern Grid Total |  |  |  | 14549 | 8833 | 174572432
| Western Grid Total |  |  |  | 8821 | 5544 | 119896776
| National Grid Total |  |  |  | 23370 | 14377 | 294469208
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-06-02
| (a) ENTIRE EASTERN GRID : |  | 9462 | MW | (b) ENTIRE WESTERN GRID : |  | 4373.1 | MW
| i) Dhaka area |  | 5050 | MW | i) Khulna area |  | 1533 | MW
| ii) Chittagong area |  | 1425 | MW | ii) Rajshahi area |  | 1471.6 | MW
| iii) Comilla area |  | 1256 | MW | iii) Barisal area |  | 465.5 | MW
| iv) Mymensingh area |  | 1171 | MW | iv) Rangpur area |  | 903 | MW
| v) Sylhet area |  | 560 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 13835.1 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 34 | 20:00 | Kalurghat | 28 | 02:00 | Narshingdi | 181 | 21:00 | Shikalbaha-230 | N/A | N/A
2 | AKSML | 10 | 12:00 | Chowmuhani | 196 | 19:00 | Kamrangirchar | 62.28 | 00:00 | Natore | 152 | 21:00 | Shitalakhya | 91.8 | 00:00
3 | Aftabnagar | 60 | 00:00 | Chuadanga | 86 | 22:00 | Kaptai | N/A | N/A | Nawabganj | 66.4 | 22:00 | Sholosohor | 34 | 19:00
4 | Agargaon | 91 | 00:00 | Coxsbazar | 128 | 19:00 | Kazla | 100 | 00:00 | Netrakona | 135 | 21:00 | Shyampur | 154 | 12:00
5 | Agrabad | 64 | 18:30 | Cumilla(N) | 172 | 19:00 | Keranigonj | 70 | 00:00 | New | 138 | 00:00 | Siddhirganj | 114 | 23:00
6 | Amnura | 58 | 23:00 | Cumilla(S) | 166 | 15:00 | Khagrachori | 28 | 15:00 | Niamatpur | 89 | 21:00 | Sirajganj | 113 | 21:00
7 | Ashuganj | 77 | 21:00 | Daudkandi | 114 | 19:00 | Khulna | 96 | 01:00 | Noapara | 41 | 06:00 | Sonargaon | 61 | 21:00
8 | BIPTC | N/A | N/A | Dhaka | 14 | 00:00 | Khulshi | 186 | 23:00 | PHP | 9 | 06:00 | Sreemongol | 59 | 21:00
9 | BSRM | 170 | 20:00 | Dhamrai | 104 | 19:30 | Kishoreganj | 120 | 11:00 | Pabna | 115 | 22:00 | Sreepur | 61.9 | 15:00
10 | Bagerhat | 82 | 22:00 | Dhanmondi | 128 | 19:00 | Kodda | 267 | 22:00 | Palashbari | 139 | 23:00 | Srinagar | 50.8 | 22:00
11 | Bakulia | 95 | 20:00 | Dohazari | 96 | 21:00 | Kulaura | 48 | 19:30 | Panchagarh | 53 | 20:00 | Sunamganj | 60 | 20:00
12 | Banani | 58 | 19:00 | Dummy | N/A | N/A | Kurigram | 66 | 20:00 | Patuakhali | 118 | 22:00 | Sylhet | 155 | 00:00
13 | Bangabhaban | 6 | 11:00 | Faridpur | 137 | 19:00 | Kushtia | 120 | 19:00 | Payra | 22 | 22:00 | TK | 34 | 19:30
14 | Barapukuria | 58 | 22:00 | Fatullah | 68 | 00:00 | Lalbag | 87 | 00:00 | Postogola | 69 | 00:00 | Tangail | 248 | 21:00
15 | Barguna | 20 | 19:30 | Fenchuganj | 48 | 19:30 | Lalmonirhat | 54 | 20:00 | Purbachal | 23 | 00:00 | Thakurgaon | 98 | 20:00
16 | Barishal | 108 | 22:00 | Feni | 109 | 18:30 | Madanganj | 40 | 20:00 | Purbasadipur | 134 | 19:30 | Tongi | 112 | 12:00
17 | Barishal-230 | 102 | 19:30 | GPH | 92 | 13:00 | Madaripur | 97 | 22:00 | Rahanpur_I | 0 | 00:00 | Ullon | 48 | 19:00
18 | Baroaulia | 70 | 11:00 | Ghorashal | N/A | N/A | Madartek | 109.34 | 00:00 | Rahim | 35 | 16:00 | Uttara | 77 | 19:00
19 | Baroirhat | 64 | 19:00 | Goalpara | 36 | 00:00 | Madunaghat | 56 | 20:00 | Rajbari | 66 | 05:00 | UttaraNew | 60 | 00:00
20 | Bashundhara | 192 | 19:00 | Gollamari | 60 | 00:00 | Magura | 48 | 19:00 | Rajendrapur | 100 | 12:00 | Zigatola | 76 | 20:00
21 | BashundharaCement | 0 | 00:00 | Gopalganj | 108 | 22:00 | Mahasthangarh | 74 | 20:00 | Rajshahi | 170 | 21:00
22 | Beanibazar | 76 | 19:00 | Gulshan | 62 | 19:00 | Manikganj | 121 | 20:00 | Rajshahi-230 | 43 | 23:00
23 | Benapole | 60 | 21:00 | Halishahar | 77.5 | 21:00 | Maniknagar | 82 | 00:00 | Ramganj | 86 | 19:00
24 | Bhaluka | 156 | 04:00 | HaripurSBU | 146 | 21:00 | Matarbari | 47 | 21:00 | Rampur | 32 | 21:00
25 | Bhandaria | 50 | 20:00 | Hasnabad | 104 | 00:00 | Matuail | 68 | 00:00 | Rangamati | 16 | 19:00
26 | Bhangura | 47 | 21:00 | Hathazari | 82 | 19:00 | Millgate | 91 | 00:00 | Rangpur | 139 | 19:30
27 | Bheramara(GK) | 59 | 04:00 | Ishurdi | 59 | 05:00 | Mirpur | 157 | 19:30 | Ruppur | 5.6 | 11:00
28 | Bhulta | 225 | 22:00 | Jaldhaka | 78 | 19:30 | Mirsorai | 6 | 23:00 | SSM | 5 | 11:00
29 | Bog-Sherpur | 66 | 21:00 | Jamalpur | 168 | 19:00 | Mithapukur | 40 | 21:00 | Saidpur | 102 | 19:30
30 | Bogura | 160 | 20:00 | Jashore | 130 | 22:00 | Modern | 0 | 00:00 | Satkhira | 120 | 23:00
31 | Borhanuddin | 57 | 19:00 | Jhenaidah | 122 | 22:00 | Mogbazar | 129 | 19:00 | Satmasjid | 120 | 00:00
32 | Brahmanbaria | 195 | 22:00 | Joydebpur | 162 | 15:00 | Mongla | 26 | 12:00 | Savar | 186 | 15:00
33 | Cantonment | 164 | 19:30 | Joypurhat | 64 | 21:00 | Motijheel | 43 | 00:00 | Shahjadpur | 116 | 20:00
34 | Chandpur | 63 | 19:00 | Juldah | 24 | 19:30 | Munshiganj | 116 | 13:00 | Shahjibazar | 99 | 21:00
35 | Chandraghona | 34 | 19:30 | KSRM | 12 | 10:00 | Mymensingh | 182 | 23:00 | Shahmirpur | 39.2 | 22:00
36 | Chapai | 77 | 00:00 | Kabirpur | 264 | 11:00 | Naogaon | 132 | 19:30 | Shariatpur | 69 | 19:00
37 | Charsaidpur | 43 | 23:00 | Kachua | 64 | 21:00 | Narail | 49 | 21:00 | Sherpur | 130 | 19:30
38 | Chauddagram | 54 | 19:30 | Kallyanpur | 129 | 19:30 | Narinda | 64 | 00:00 | Shikalbaha | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-06-02 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 398 | 06:00 | 384 | 12:00 | Kaliakoir | N/A | N/A | N/A | N/A
| Ashuganj | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Bhulta | 391 | 04:00 | 376 | 12:00 | Payra | 414 | 08:00 | 407 | 12:00
| Bibiana | 404 | 18:00 | 391 | 14:00 | Rahanpur_I | 413 | 18:00 | 409 | 03:00
| BIPTC | 399 | 07:00 | 389 | 15:00 | Rampal | 407.29 | 18:00 | 395 | 14:00
| Gopalganj | 405 | 18:00 | 394 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 231 | 04:00 | 220 | 14:00 | Hasnabad | 232 | 05:00 | 221 | 11:00
| AKSML | 235 | 19:00 | 207 | 11:00 | Hathazari | 236 | 21:00 | 224 | 10:00
| Aminbazar | 233 | 05:00 | 224 | 11:00 | Ishurdi | 233 | 18:00 | 225 | 12:00
| Ashuganj | 234 | 18:30 | 225 | 12:00 | Jhenaidah | 226 | 00:00 | 217 | 12:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | N/A | N/A | N/A | N/A
| Baghabari | 228 | 00:00 | 223 | 13:00 | Keranigonj | 230 | 02:00 | 221 | 11:00
| Barapukuria | 217 | 16:00 | 207 | 04:00 | Khulna(S) | 234 | 08:00 | 225 | 12:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 236 | 17:00 | 226 | 22:00 | Maniknagar | 230 | 06:00 | 222 | 11:00
| Bheramara | 231 | 00:00 | 223 | 12:00 | Meghnaghat | 232 | 00:00 | 228 | 11:00
| Bhulta | 233 | 06:00 | 223 | 12:00 | Mirsorai | 237 | 21:00 | 219 | 11:00
| Bibiana | 238 | 01:00 | 232 | 10:00 | Rajshahi | 234 | 18:00 | 225 | 12:00
| BIPTC | 233 | 00:00 | 223 | 11:00 | Rampal | 233.13 | 18:00 | 224 | 12:00
| Bogura | 217 | 18:00 | 208 | 05:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 233 | 08:00 | 227 | 22:00 | Rampura | 230 | 05:00 | 221 | 12:00
| BSRM | 236 | 21:00 | 222 | 11:00 | Shikalbaha | 235 | 19:30 | 224 | 11:00
| Cumilla(N) | 231 | 21:00 | 222 | 11:00 | Shyampur | 230 | 02:00 | 226 | 09:00
| Fenchuganj | 242 | 08:00 | 236 | 10:00 | Siddhirganj | 232 | 04:00 | 223 | 12:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 232 | 00:00 | 228 | 12:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 229 | 08:00 | 222 | 12:00
| GPH | 232 | 21:00 | 221 | 11:00 | Tongi | 225 | 04:00 | 215 | 12:00
| Haripur | 231 | 03:00 | 220 | 12:00
| 132 kV | KV |  | KV |  | Tongi | KV |  | KV
| Aftabnagar | 138 | 05:00 | 127 | 18:00 | Kushtia | 133 | 18:00 | 129 | 06:00
| Agargaon | 133 | 06:00 | 126 | 14:00 | Lalbag | 134 | 23:00 | 126 | 14:00
| Agrabad | 135 | 19:30 | 128 | 11:00 | Lalmonirhat | 126 | 15:00 | 117 | 19:30
| AKS | 133 | 20:00 | 127 | 11:00 | Madanganj | 134 | 04:00 | 129 | 11:00
| Aminbazar | 132 | 03:00 | 124 | 11:00 | Madaripur | 130 | 04:00 | 126 | 11:00
| Amnura | 139 | 23:00 | 128 | 01:00 | Madartek | 137 | 06:00 | 130 | 11:00
| Ashuganj | 136 | 18:30 | 132 | 11:00 | Madunaghat | 136 | 21:00 | 129 | 14:00
| Bagerhat | 135 | 18:00 | 127 | 12:00 | Magura | 134 | 00:00 | 128 | 14:00
| Bakulia | 135 | 18:00 | 128 | 11:00 | Mahasthangarh | 128 | 01:00 | 120 | 04:00
| Banani | 138 | 06:00 | 130 | 11:00 | Manikganj | 134 | 18:30 | 123 | 12:00
| Bangabhaban | 133 | 02:00 | 127 | 12:00 | Maniknagar | 137 | 12:00 | 128 | 11:00
| Barapukuria | 134 | 15:00 | 126 | 03:00 | Matarbari | 130 | 08:00 | 114 | 22:00
| Barguna | 137 | 00:00 | 133 | 02:00 | Matuail | 134.5 | 06:00 | 129 | 12:00
| Barishal | 137 | 00:00 | 124 | 01:00 | Millgate | 131 | 06:00 | 121 | 12:00
| Barishal-230 | 132 | 17:00 | 124 | 22:00 | Mirpur | 128 | 05:00 | 122 | 12:00
| Baroaulia | 136 | 20:00 | 129 | 14:00 | Mithapukur | 128 | 17:00 | 119 | 22:00
| Baroirhat | 134 | 18:00 | 123 | 11:00 | Modern | 136 | 20:00 | 127 | 14:00
| Bashundhara | 138 | 05:00 | 120 | 12:00 | Mogbazar | 139 | 06:00 | 131 | 07:00
| BashundharaCement | 135 | 06:00 | 129 | 11:00 | Mongla | 134 | 15:00 | 127 | 12:00
| Beanibazar | 132 | 07:00 | 126 | 19:00 | Motijheel | 133 | 02:00 | 127 | 12:00
| Benapole | 132 | 00:00 | 124 | 12:00 | Munshiganj | 134 | 04:00 | 129 | 11:00
| Bhaluka | 127 | 08:00 | 121 | 12:00 | Mymensingh | 135 | 22:00 | 102 | 11:00
| Bhandaria | 134 | 18:00 | 125 | 04:00 | Naogaon | 124 | 18:00 | 113 | 03:00
| Bhangura | 135 | 00:00 | 130 | 13:00 | Narail | 136 | 18:00 | 129 | 19:00
| Bheramara | 133 | 00:00 | 130 | 11:00 | Narshingdi | 131 | 08:00 | 123 | 12:00
| Bheramara(GK) | 134 | 00:00 | 130 | 12:00 | Natore | 133 | 18:00 | 125 | 22:00
| Bhulta | 127 | 17:00 | 121 | 11:00 | Nawabganj | 134 | 23:00 | 125 | 14:00
| Bog-Sherpur | 131 | 18:00 | 124 | 19:30 | Netrakona | 134 | 22:00 | 115 | 12:00
| Bogura | 131 | 01:00 | 124 | 06:00 | New | 131 | 06:00 | 122 | 12:00
| Bogura-230 | 131 | 18:00 | 123 | 05:00 | Niamatpur | 122 | 18:00 | 108 | 19:30
| Brahmanbaria | 132 | 18:00 | 127 | 11:00 | Noapara | 138 | 08:00 | 130 | 11:00
| Cantonment | 132 | 06:00 | 124 | 12:00 | Pabna | 132 | 00:00 | 128 | 06:00
| Chandpur | 137 | 18:00 | 119 | 10:00 | Palashbari | 125 | 18:00 | 115 | 19:30
| Chandraghona | 136 | 18:00 | 129 | 11:00 | Panchagarh | 135 | 18:00 | 114 | 03:00
| Chapai | 133 | 18:00 | 128 | 00:00 | Patuakhali | 140 | 23:00 | 133 | 14:00
| Charsaidpur | 135 | 04:00 | 129 | 14:00 | Payra | 140 | 00:00 | 137 | 12:00
| Chauddagram | 133 | 00:00 | 123 | 11:00 | PHP | 134 | 18:00 | 123 | 10:00
| Chhatak | 132 | 05:00 | 126 | 20:00 | Postogola | 136 | 06:00 | 130 | 11:00
| Chowmuhani | 132 | 19:00 | 119 | 10:00 | Purbachal | 138 | 05:00 | 121 | 11:00
| Chuadanga | 130 | 01:00 | 122 | 12:00 | Purbasadipur | 129 | 18:00 | 113 | 04:00
| Coxsbazar | 128 | 08:00 | 115 | 19:30 | Rahim | 135 | 03:00 | 130 | 12:00
| Cumilla(N) | 136 | 18:00 | 127 | 11:00 | Rajbari | 129 | 08:00 | 124 | 22:00
| Cumilla(S) | 135 | 18:00 | 124 | 15:00 | Rajendrapur | 136 | 19:00 | 121 | 13:00
| Daudkandi | 133 | 18:00 | 127 | 12:00 | Rajshahi | 132 | 18:00 | 126 | 22:00
| Dhaka | 138 | 04:00 | 130 | 12:00 | Rajshahi-230 | 132 | 00:00 | 120 | 08:00
| Dhamrai | 134 | 23:00 | 125 | 12:00 | Ramganj | 134 | 18:00 | 118 | 03:00
| Dhanmondi | 135 | 06:00 | 129 | 12:00 | Rampur | 135 | 19:30 | 128 | 11:00
| Dohazari | 135 | 08:00 | 125 | 13:00 | Rampura | 137 | 05:00 | 130 | 11:00
| Dummy | N/A | N/A | N/A | N/A | Rangamati | 135 | 18:00 | 128 | 11:00
| Faridpur | 129 | 08:00 | 126 | 12:00 | Rangpur | 127 | 01:00 | 116 | 19:30
| Fatullah | 135 | 05:00 | 129 | 12:00 | Ruppur | 134 | 00:00 | 130 | 12:00
| Fenchuganj | 137 | 07:00 | 135 | 00:00 | Saidpur | 128 | 15:00 | 118 | 06:00
| Feni | 135 | 18:00 | 124 | 11:00 | Satkhira | 133 | 18:00 | 125 | 14:00
| Ghorashal | N/A | N/A | N/A | N/A | Satmasjid | 135 | 06:00 | 125 | 12:00
| Goalpara | 138 | 18:00 | 131 | 12:00 | Savar | 128 | 02:00 | 122 | 12:00
| Gollamari | 138 | 18:00 | 131 | 12:00 | Shahjadpur | 138 | 04:00 | 133 | 05:00
| Gopalganj | 135 | 08:00 | 131 | 11:00 | Shahjibazar | 135 | 18:00 | 130 | 00:00
| Gopalganj-400 | 130 | 08:00 | 126 | 11:00 | Shahmirpur | 136 | 21:00 | 128 | 14:00
| Gulshan | 137 | 06:00 | 129 | 12:00 | Shariatpur | 130 | 15:00 | 125 | 12:00
| Halishahar | 136 | 19:00 | 128 | 11:00 | Sherpur | 131 | 22:00 | 110 | 01:00
| Haripur | 135 | 03:00 | 130 | 12:00 | Shikalbaha | N/A | N/A | N/A | N/A
| HaripurSBU | 135 | 03:00 | 130 | 12:00 | Shikalbaha-230 | 136 | 19:30 | 130 | 11:00
| Hasnabad | 135 | 06:00 | 130 | 11:00 | Shitalakhya | 135 | 04:00 | 130 | 11:00
| Hathazari | 137 | 20:00 | 130 | 09:00 | Sholosohor | 135 | 18:30 | 128 | 10:00
| Ishurdi | 135 | 23:00 | 130 | 12:00 | Shyampur | 135 | 05:00 | 128 | 11:00
| Jaldhaka | 128 | 15:00 | 116 | 19:30 | Shyampur-230 | 135 | 04:00 | 128 | 11:00
| Jamalpur | 134 | 22:00 | 112 | 00:00 | Siddhirganj | 135 | 05:00 | 130 | 11:00
| Jashore | 132 | 00:00 | 125 | 12:00 | Sirajganj | 132 | 18:00 | 126 | 06:00
| Jhenaidah | 135 | 00:00 | 129 | 12:00 | Sonargaon | 132 | 06:00 | 127 | 14:00
| Jhenaidah-230 | 136 | 18:00 | 130 | 12:00 | Sreemongol | 133 | 15:00 | 130 | 00:00
| Joydebpur | 140 | 05:00 | 132 | 12:00 | Sreepur | 128 | 02:00 | 124 | 12:00
| Joypurhat | 123 | 18:00 | 110 | 19:30 | Srinagar | 134 | 23:00 | 124 | 14:00
| Juldah | 137 | 19:30 | 129 | 14:00 | SSM | 140 | 23:00 | 130 | 14:00
| Kabirpur | 137 | 18:30 | 119 | 12:00 | Sunamganj | 131 | 08:00 | 122 | 20:00
| Kachua | 135 | 19:00 | 122 | 10:00 | Sylhet | 133 | 05:00 | 130 | 20:00
| Kaliakoir | N/A | N/A | N/A | N/A | Tangail | 133 | 22:00 | 121 | 19:30
| Kallyanpur | 129 | 06:00 | 123 | 14:00 | Thakurgaon | 128 | 18:00 | 110 | 03:00
| Kalurghat | 135 | 00:00 | 128 | 11:00 | TK | 136 | 20:00 | 128 | 14:00
| Kamrangirchar | 135 | 23:00 | 121 | 12:00 | Tongi | 131 | 04:00 | 125 | 12:00
| Kaptai | N/A | N/A | N/A | N/A | Ullon | 137 | 05:00 | 130 | 12:00
| Kazla | 133 | 03:00 | 128 | 12:00 | Uttara | 129 | 04:00 | 123 | 11:00
| Keranigonj | 134 | 23:00 | 125 | 14:00 | UttaraNew | 129 | 05:00 | 122 | 12:00
| Khagrachori | 135 | 18:30 | 128 | 12:00 | Zigatola | 134 | 02:00 | 127 | 11:00
| Khulna | 137 | 18:00 | 130 | 12:00
| Khulna(S) | 137 | 02:00 | 131 | 12:00
| Khulshi | 135 | 20:00 | 127 | 11:00
| Kishoreganj | 130 | 15:00 | 113 | 11:00
| Kodda | 139 | 22:00 | 123 | 12:00
| KSRM | 136 | 21:00 | 128 | 11:00
| Kulaura | 136 | 18:00 | 134 | 00:00
| Kurigram | 128 | 17:00 | 115 | 04:00

## L-Curve
Date | 2023-06-02
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1122 | 7520 | 5002 | 12522 |  |  |  | QF-LDC-11
0:30 | 1116 | 7453.5 | 4835 | 12288.5 | Date: | 2023-06-02
1:00 | 1110 | 7387 | 4668 | 12055
1:30 | 1095 | 7340 | 4656.5 | 11996.5
2:00 | 1080 | 7293 | 4645 | 11938
2:30 | 1070 | 7329 | 4656 | 11985 | [5 empty] | Gen. at Eve. Peak | 14377 | 14377 MW (21:00 )
3:00 | 1060 | 7365 | 4667 | 12032 | [6 empty] | 21:00
3:30 | 1000 | 7347.5 | 4668 | 12015.5 | [5 empty] | Gen. at Day Peak | 11960 | 11960 MW (12:00 )
4:00 | 940 | 7330 | 4669 | 11999 | [6 empty] | 12:00
4:30 | 925 | 7253 | 4651 | 11904 | [5 empty] | Highest Generation | 14377
5:00 | 910 | 7176 | 4633 | 11809 | [6 empty] | 21:00
5:30 | 910 | 7028.5 | 4622 | 11650.5
6:00 | 910 | 6881 | 4611 | 11492
6:30 | 945 | 6817 | 4653 | 11470
7:00 | 980 | 6753 | 4695 | 11448
7:30 | 1120 | 6647.5 | 4717 | 11364.5
8:00 | 1260 | 6542 | 4739 | 11281
8:30 | 1280 | 6491 | 4726 | 11217
9:00 | 1300 | 6440 | 4713 | 11153
9:30 | 1380 | 6457 | 4737.5 | 11194.5
10:00 | 1460 | 6474 | 4762 | 11236
10:30 | 1475 | 6533.5 | 4793 | 11326.5
11:00 | 1490 | 6593 | 4824 | 11417
11:30 | 1495 | 6738.5 | 4950 | 11688.5
12:00 | 1500 | 6884 | 5076 | 11960
12:30 | 1440 | 6943 | 5170.5 | 12113.5
13:00 | 1380 | 7002 | 5265 | 12267
13:30 | 1410 | 6940 | 5233 | 12173
14:00 | 1440 | 6878 | 5201 | 12079
14:30 | 1330 | 6741.5 | 5038.5 | 11780
15:00 | 1220 | 6605 | 4876 | 11481
15:30 | 1210 | 6653.5 | 4790 | 11443.5
16:00 | 1200 | 6702 | 4704 | 11406
16:30 | 1222 | 6762.5 | 4684.5 | 11447
17:00 | 1244 | 6823 | 4665 | 11488
17:30 | 1232 | 6830 | 4677.5 | 11507.5
18:00 | 1220 | 6837 | 4690 | 11527
18:30 | 1110 | 7603 | 4834.5 | 12437.5
19:00 | 1000 | 8369 | 4979 | 13348
19:30 | 840 | 8758 | 5249 | 14007
20:00 | 880 | 8800 | 5324 | 14124 |  |  |  | Executive Engineer
20:30 | 880 | 8816.5 | 5434 | 14250.5 |  |  |  | Network Operation Division
21:00 | 880 | 8833 | 5544 | 14377
21:30 | 860 | 8705 | 5533.5 | 14238.5
22:00 | 840 | 8577 | 5523 | 14100 |  |  |  |  | Page 6 of 7
22:30 | 935 | 8209 | 5424 | 13633
23:00 | 1030 | 7841 | 5325 | 13166
23:30 | 1076 | 7680.5 | 5163.5 | 12844
24:00 | 1122 | 7520 | 5002 | 12522
14377 MW (21:00 )
11960 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-06-02 |  | Energy |  | 294469208
[15 empty] | 43617 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 4347 | 803 | 2488 | 385 | 1732 | 2155 | 0 | 0 | 468 | 140 | 0 | 4 | 1697.99
0:30 | 4342 | 820.5 | 2455 | 389 | 1544 | 2156.5 | 0 | 0 | 427.5 | 151 | 0 | 3 | 2111.9825 |  |  | Date: | 43617
1:00 | 4337 | 838 | 2422 | 393 | 1356 | 2158 | 0 | 0 | 387 | 162 | 0 | 2 | 2525.975
1:30 | 4358.5 | 838.5 | 2407.5 | 362.5 | 1334.5 | 2153 | 0 | 0 | 381.5 | 159 | 0 | 1.5 | 2486.82 | [8 empty] | 294.4692 | 294.4692 |  | Total Energy Gen MKWHr Energy Not Served MKWHr Energy Requirement MKWHr | Total Energy Gen 294.469 MKWHr Energy Not Served 31.897 MKWHr Energy Requirement 326.367 MKWHr
2:00 | 4380 | 839 | 2393 | 332 | 1313 | 2148 | 0 | 0 | 376 | 156 | 0 | 1 | 2447.665 | [8 empty] | 31.8973 | 31.8973
2:30 | 4375 | 874 | 2409 | 355.5 | 1292 | 2144 | 0 | 0 | 376 | 159 | 0 | 0.5 | 2354.5525 | [8 empty] | 326.3665 | 326.3665
3:00 | 4370 | 909 | 2425 | 379 | 1271 | 2140 | 0 | 0 | 376 | 162 | 0 | 0 | 2261.44
3:30 | 4378 | 909.5 | 2423 | 365 | 1272 | 2133.5 | 0 | 0 | 373.5 | 161 | 0 | 0 | 2229.4475
4:00 | 4386 | 910 | 2421 | 351 | 1273 | 2127 | 0 | 0 | 371 | 160 | 0 | 0 | 2197.455
4:30 | 4309.5 | 909.5 | 2427.5 | 355 | 1249 | 2129.5 | 0 | 0 | 368 | 156 | 0 | 0 | 2192.68
5:00 | 4233 | 909 | 2434 | 359 | 1225 | 2132 | 0 | 0 | 365 | 152 | 0 | 0 | 2187.905
5:30 | 4227.5 | 908.5 | 2425 | 206.5 | 1239 | 2132.5 | 0 | 0 | 341 | 156 | 14.5 | 0 | 2100.5225
6:00 | 4222 | 908 | 2416 | 54 | 1253 | 2133 | 0 | 0 | 317 | 160 | 29 | 0 | 2013.14
6:30 | 4213 | 908 | 2417 | 27 | 1242.5 | 2131.5 | 0 | 0 | 312.5 | 154 | 64.5 | 0 | 1747.65 | [7 empty] | Coal
7:00 | 4204 | 908 | 2418 | 0 | 1232 | 2130 | 0 | 0 | 308 | 148 | 100 | 0 | 1482.16
7:30 | 4119.5 | 908.5 | 2357.5 | 0 | 1246 | 2132.5 | 0 | 0 | 301 | 148 | 151.5 | 0 | 1609.6525 | [6 empty] | Oil
8:00 | 4035 | 909 | 2297 | 0 | 1260 | 2135 | 0 | 0 | 294 | 148 | 203 | 0 | 1737.145
8:30 | 3995 | 909 | 2280 | 0 | 1206.5 | 2136 | 0 | 0 | 295.5 | 142 | 253 | 0 | 1822.14
9:00 | 3955 | 909 | 2263 | 0 | 1153 | 2137 | 0 | 0 | 297 | 136 | 303 | 0 | 1907.135
9:30 | 3950 | 909 | 2278 | 0 | 1120 | 2134.5 | 12.5 | 0 | 308 | 142 | 340.5 | 0 | 1843.6275
10:00 | 3945 | 909 | 2293 | 0 | 1087 | 2132 | 25 | 0 | 319 | 148 | 378 | 0 | 1780.12
10:30 | 3967 | 909 | 2298.5 | 0 | 1139.5 | 2132.5 | 25 | 0 | 317.5 | 143 | 393.5 | 1 | 1741.4425
11:00 | 3989 | 909 | 2304 | 0 | 1192 | 2133 | 25 | 0 | 316 | 138 | 409 | 2 | 1702.765
11:30 | 4012.5 | 909 | 2362.5 | 48.5 | 1268.5 | 2192 | 25 | 0 | 317 | 142 | 409.5 | 2 | 1586.7325
12:00 | 4036 | 909 | 2421 | 97 | 1345 | 2251 | 25 | 0 | 318 | 146 | 410 | 2 | 1470.7
12:30 | 4046 | 909 | 2376.5 | 148 | 1389 | 2328 | 25 | 0 | 320 | 153 | 415 | 4 | 1413.8775
13:00 | 4056 | 909 | 2332 | 199 | 1433 | 2405 | 25 | 0 | 322 | 160 | 420 | 6 | 1357.055
13:30 | 4056 | 909 | 2332 | 199 | 1433 | 2405 | 25 | 0 | 322 | 160 | 420 | 6 | 1357.055
14:00 | 4056 | 909 | 2332 | 199 | 1433 | 2405 | 25 | 0 | 322 | 160 | 420 | 6 | 1357.055
14:30 | 3972.5 | 907.5 | 2295.5 | 99.5 | 1396 | 2332.5 | 25 | 0 | 315 | 163 | 362.5 | 5 | 1642.6
15:00 | 3889 | 906 | 2259 | 0 | 1359 | 2260 | 25 | 0 | 308 | 166 | 305 | 4 | 1928.145
15:30 | 3940.5 | 907 | 2254 | 0 | 1394 | 2195 | 25 | 0 | 307 | 165 | 253 | 3 | 1796.8325
16:00 | 3992 | 908 | 2249 | 0 | 1429 | 2130 | 25 | 0 | 306 | 164 | 201 | 2 | 1665.52
16:30 | 4023 | 908.5 | 2268 | 0 | 1467 | 2131 | 25 | 0 | 317.5 | 162 | 143.5 | 1.5 | 1483.115
17:00 | 4054 | 909 | 2287 | 0 | 1505 | 2132 | 25 | 0 | 329 | 160 | 86 | 1 | 1300.71 | [10 empty] | 472
17:30 | 4007 | 909 | 2206 | 0 | 1641.5 | 2139 | 25 | 0 | 372.5 | 154 | 53 | 0.5 | 995.5875 | [10 empty] | 100
18:00 | 3960 | 909 | 2125 | 0 | 1778 | 2146 | 25 | 0 | 416 | 148 | 20 | 0 | 690.465 | [10 empty] | 20
18:30 | 4085.5 | 909 | 2278.5 | 92.5 | 2282.5 | 2138 | 25 | 0 | 473.5 | 143 | 10 | 0 | 584.9375 | [10 empty] | 592
19:00 | 4211 | 909 | 2432 | 185 | 2787 | 2130 | 25 | 0 | 531 | 138 | 0 | 0 | 479.41
19:30 | 4239 | 804 | 2468 | 385 | 3026 | 2211 | 25 | 0 | 710 | 138 | 0 | 1 | 419.245
20:00 | 4293 | 804 | 2470 | 341 | 3037 | 2252 | 25 | 0 | 751 | 150 | 0 | 1 | 359.08
20:30 | 4301 | 803.5 | 2474 | 335.5 | 3055 | 2347.5 | 25 | 0 | 757 | 150 | 0 | 2 | 367.1975
21:00 | 4309 | 803 | 2478 | 330 | 3073 | 2443 | 25 | 0 | 763 | 150 | 0 | 3 | 375.315
21:30 | 4304.5 | 803 | 2470 | 328.5 | 2932.5 | 2453.5 | 25 | 0 | 766.5 | 152 | 0 | 3 | 474.1575
22:00 | 4300 | 803 | 2462 | 327 | 2792 | 2464 | 25 | 0 | 770 | 154 | 0 | 3 | 573
22:30 | 4295 | 803.5 | 2457 | 286 | 2548 | 2440.5 | 12.5 | 0 | 628.5 | 159 | 0 | 3 | 971.235
23:00 | 4290 | 804 | 2452 | 245 | 2304 | 2417 | 0 | 0 | 487 | 164 | 0 | 3 | 1369.47
23:30 | 4318.5 | 803.5 | 2470 | 315 | 2018 | 2286 | 0 | 0 | 477.5 | 152 | 0 | 3.5 | 1533.73 |  |  | Max Temp. in Dhaka |  | 37.5° C
24:00 | 4347 | 803 | 2488 | 385 | 1732 | 2155 | 0 | 0 | 468 | 140 | 0 | 4 | 1697.99
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 294.469 MKWHr Energy Not Served 31.897 MKWHr Energy Requirement 326.367 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-06-02
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | [8 empty] | 0 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 0 | 0 | 306840
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 105 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 16 | 16 | 16 |  | 24 | 25 | 25 | 25 | 25 | 8 | 8 | 286731
| Teknaf 20MW PP (Solartech) |  |  |  |  | 0 | 3 | 6 | 11 | 12 | 15 | 20 | 19 | 20 | 16 | 11 | 3 | 5 | 1 | [8 empty] | 142020
6 | Sikalbaha 225MW CCPP (Gas) | 225 | 225 | 225 | 226 | 225 | 226 | 224 | 225 | 221 | 218 | 218 | 216 | 218 | 217 | 222 | 218 | 218 | 224 |  | 219 | 222 | 224 | 224 | 225 | 225 | 220 | 5231896
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 45 | 50 | 67 | 67 |  | 67 | 68 | 68 | 68 | 68 | 68 | 68 | 1308344
12 | Hathazari 100 MW peaking PP | 48 | 48 | 48 | 48 | 48 | 48 | 40 | 40 | 40 | 40 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 62 |  | 62 | 62 | 62 | 60 | 61 | 53 | 39 | 1045104
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 32 |  | 51 | 51 | 51 | 51 | 34 | 34 | 34 | 602181
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 39 | 43 | 43 | 43 | 37 | 37 | 36 | 36 | 36 | 35 | 42 | 40 | 34 | 34 | 34 | 34 | 35 | 34 |  | 35 | 35 | 35 | 41 | 45 | 45 | 45 | 925264
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 195 | 197 | 195 | 198 | 197 | 197 | 193 | 116 | 127 | 127 | 161 | 187 | 191 | 154 | 150 | 189 | 193 | 132 |  | 191 | 192 | 193 | 194 | 195 | 200 | 191 | 4474000
17 | Siddhirganj 335 MW CCPP | 160 | 154 | 138 | 140 | 0 | [20 empty] | 0 | 864800
18 | Kodda 300 MW PP Unit-2 (Summit) | 55 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 50 |  | 137 | 147 | 147 | 145 | 145 | 147 | 145 | 1758872
19 | Ashuganj 195MW PP (APSCL-United) | 195 | 197 | 197 | 195 | 197 | 197 | 197 | 195 | 195 | 195 | 195 | 192 | 192 | 192 | 192 | 185 | 185 | 194 |  | 195 | 195 | 177 | 178 | 178 | 178 | 147 | 4549818
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3042375
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4284000
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | [20 empty] | 0
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 39 | 39 | 40 | 42 | 42 | 42 | 42 | 40 | 39 | 39 | 38 | 35 | 35 | 34 | 34 | 34 | 34 | 35 |  | 37 | 39 | 39 | 41 | 41 | 41 | 41 | 913536
33 | Ashuganj 225 MW CCPP | 202 | 205 | 204 | 206 | 206 | 206 | 204 | 206 | 202 | 199 | 196 | 197 | 201 | 196 | 199 | 197 | 200 | 201 |  | 194 | 179 | 170 | 154 | 155 | 157 | 152 | 4676000
34 | Ashuganj 450 MW CCPP(South) | 305 | 305 | 305 | 305 | 305 | 305 | 320 | 280 | 290 | 300 | 320 | 280 | 275 | 310 | 270 | 270 | 270 | 270 |  | 330 | 275 | 275 | 270 | 270 | 270 | 320 | 7215000
| Ashuganj 450 MW CCPP(North) | 315 | 310 | 310 | 310 | 310 | 310 | 310 | 275 | 295 | 305 | 325 | 290 | 275 | 315 | 275 | 275 | 275 | 275 |  | 340 | 305 | 305 | 305 | 280 | 280 | 335 | 7691000
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP | [11 empty] | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 765030
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 395 | 397 | 400 | 402 | 406 | 405 | 405 | 406 | 378 | 351 | 356 | 398 | 397 | 402 | 395 | 399 | 399 | 398 |  | 366 | 397 | 397 | 398 | 406 | 407 | 400 | 9601030
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 400 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 10194500
41 | Haripur 360MW CCPP(HPL) | 327 | 328 | 327 | 327 | 328 | 327 | 331 | 314 | 308 | 307 | 333 | 332 | 317 | 323 | 322 | 322 | 322 | 282 |  | 333 | 332 | 332 | 332 | 322 | 322 | 327 | 7752000
42 | RPCL 210MW CCPP | 110 | 154 | 147 | 137 | 137 | 137 | 100 | 98 | 68 | 68 | 53 | 31 | 53 | 36 | 20 | 43 | 48 | 64 |  | 55 | 54 | 80 | 103 | 104 | 106 | 104 | 1937280
43 | Sutiakhali 50 MW Solar PP |  |  |  |  | 0 | 3 | 6 | 25 | 34 | 40 | 34 | 47 | 45 | 41 | 31 | 26 | 13 | 3 |  | 0 | [6 empty] | 341310
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 40 | 40 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1017000
45 | Fenchugonj CCPP Phase-2 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 39 | 38 | 38 | 38 | 38 | 38 | 38 |  | 38 | 38 | 38 | 38 | 40 | 40 | 40 | 900360
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 55 | 56 | 56 | 57 | 57 | 56 | 56 | 61 | 42 | 42 | 50 | 54 | 52 | 50 | 49 | 57 | 59 | 40 |  | 58 | 60 | 60 | 55 | 56 | 57 | 55 | 1281888
48 | Shahjibazar 86MW PP (Shahjibazar) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 78 | 78 | 79 | 77 | 76 | 75 | 77 | 80 | 40 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1812480
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 187 | 185 | 185 | 184 | 187 | 188 | 188 | 188 | 193 | 193 | 192 | 191 | 190 | 190 | 180 | 179 | 180 | 180 |  | 181 | 180 | 181 | 187 | 187 | 187 | 183 | 4860700
51 | Sylhet 20 MW GTPP | [17 empty] | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 100000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 251460
54 | Hobiganj 11MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 3 | 3 | 5 | 5 | 5 | 5 | 5 | 126712
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 50 | 50 | 50 | 50 | 46 | 50 | 50 |  | 50 | 50 | 50 | 50 | 49 | 50 | 50 | 1193400
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 372336
57 | Bibiana-II 341 MW CCPP (Summit) | 315 | 300 | 310 | 320 | 300 | 290 | 295 | 290 | 280 | 305 | 310 | 290 | 300 | 270 | 290 | 280 | 285 | 270 |  | 295 | 290 | 300 | 300 | 290 | 280 | 320 | 7237000
| Bibiyana South 400 MW | 380 | 384 | 381 | 386 | 367 | 360 | 360 | 354 | 380 | 380 | 370 | 354 | 335 | 360 | 362 | 340 | 380 | 362 |  | 380 | 390 | 396 | 392 | 390 | 384 | 384 | 8875100
58 | Nababganj 55 MW PP (Southern power ) | [9 empty] | 0 | 8 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 35 |  | 0 | 464438
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 1 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 9 | 12 | 277440
60 | Barabkunda 22 MW PP (Regent) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 7 | 7 | 7 | 7 | 7 | 8 | 8 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 159216
61 | Narshingdi 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 22 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 22 | 22 | 22 | 22 | 405576
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 17 | 17 |  | 15 | 15 | 15 |  | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 365688
63 | Impoprt (Tripura) | 162 | 156 | 162 | 160 | 152 | 160 | 148 | 148 | 136 | 148 | 138 | 146 | 160 | 162 | 166 | 164 | 160 | 148 |  | 138 | 138 | 150 | 150 | 154 | 164 | 140 | 3589440
64 | Malancha, Ctg. EPZ (United) | 30 | 30 | 35 | 33 | 33 | 34 | 34 | 27 | 25 | 25 | 25 | 17 | 28 | 23 | 20 | 20 | 29 | 31 |  | 31 | 41 | 42 | 42 | 42 | 42 | 42 | 732480
65 | Feni 22MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 15 | 17 | 17 | 17 |  | 17 | 17 | 18 | 18 | 18 | 18 | 18 | 410112
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 11 | 11 | 11 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 240480
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 32 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 674300
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 431750
69 | Summit Ashulia | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 460000
70 | Summit Madhabdi | 26 | 26 | 26 | 26 | 22 | 26 | 26 | 26 | 22 | 22 | 14 | 14 | 16 | 16 | 15 | 17 | 18 | 18 |  | 18 | 18 | 25 | 25 | 25 | 25 | 25 | 478620
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 773900
72 | Rupganj 33 MW PP(Summit) | 31 | 31 | 31 | 31 | 31 | 32 | 31 | 31 | 31 | 31 | 28 | 25 | 25 | 26 | 26 | 20 | 20 | 20 |  | 20 | 28 | 28 | 22 | 22 | 30 | 31 | 691200
73 | Ghorashal 108MW PP (Regent) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 55 | 75 | 78 | 77 | 75 | 1140590
| Feni Lanka Power | 62 | 62 | 62 | 62 | 62 | 62 | 34 | 34 | 0 |  |  | 34 | 51 | 51 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1136580
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 9 | 56 |  | 95 | 95 | 95 | 95 | 96 | 52 | 9 | 590520
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 54 | 54 | 54 | 54 | 54 | 46 | 17 | 581760
77 | Siddhirganj 100 PP(Dutch Bangla) | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 433920
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 24 |  | 48 | 48 | 48 | 48 | 48 | 48 | 8 | 384000
79 | Kodda 150 MW PP | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 48 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 98 |  | 150 | 150 | 150 | 150 | 150 | 48 | 48 | 1536480
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 51 | 51 | 52 | 52 | 52 | 52 | 52 | 50 | 37 | 8 | 8 | 0 | [7 empty] | 5 | 8 | 8 | 0 |  |  |  | 477600
| Gazipur 100 MW PP | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 86 | 86 | 86 | 70 | 70 | 70 | 70 |  | 70 | 86 | 86 | 86 | 86 | 87 | 88 | 2005181
| Kaptai 7 MW Solar PP |  |  |  |  | 0 | 0 | 1 | 2 | 3 | 4 | 2 | 2 | 4 | 2 | 2 | 2 | 1 | 0 | [8 empty] | 30480
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 450900
| Karnaphuli Power Ltd. | 54 | 46 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 56 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 61 | 1339850
82 | Madanganj 102 PP(Summit) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 65 | 48 | 50 | 53 | 61 | 61 | 61 | 61 | 61 | 70 |  | 80 | 69 | 69 | 80 | 80 | 80 | 80 | 1616124
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 297 | 282 | 294 | 274 | 299 | 294 | 303 | 253 | 275 | 280 | 254 | 293 | 242 | 299 | 269 | 299 | 257 | 266 |  | 303 | 301 | 296 | 279 | 281 | 274 | 303 | 6958545
87 | Meghnaghat 100 MW(IEL) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 9 | 8 | 8 | 8 | 11 | 22 |  | 22 | 24 | 24 | 21 | 24 | 24 | 24 | 292800
| Meghnaghat 104 MW PP (OPCL) |  |  |  | 0 | 4 | 15 | 0 |  |  | 0 | 6 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 234240
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 55 | 55 | 55 | 55 | 55 | 55 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 |  | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 1253880
92 | Fenchuganj 44MW (Energyprima) | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 43 | 46 | 46 | 49 | 48 | 47 | 47 | 48 | 48 | 48 | 47 |  | 48 | 48 | 48 | 49 | 49 | 49 | 49 | 1132776
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1134806
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 224640
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 14 | 19 | 19 | 19 | 26 | 44 |  | 44 | 44 | 44 | 44 | 44 | 44 | 6 | 439200
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [19 empty] | 0 | 15 | 15 | 30 | 15 | 15 | 15 | 93594
100 | Manikganj 55 MW PP (Northern) | [9 empty] | 0 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 35 | 35 | 0 | 468960
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 80 | 80 | 80 | 112 | 112 | 112 | 112 | 80 | 112 | 112 |  | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 2435073
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 |  | 1 | 1 | 0 | [8 empty] | 14200
103 | Kamalaghat 54 MW PP(Banco Energy) | [16 empty] | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 128736
104 | Keranigonj 300 MW PP (APR) | 300 | 240 | 300 | 301 | 305 | 0 |  |  |  |  | 0 | 12 | 106 | [6 empty] | 130 | 300 | 251 | 233 | 233 | 150 | 290 | 2939811
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 69 | 68 | 67 | 67 | 66 |  | 62 | 66 | 68 |  | 86 | 87 | 87 | 87 | 87 | 68 | 68 | 1636800
112 | Aurahati 100MW PP (Aggreko) | 93 | 92 | 79 | 50 | 54 | 54 | 0 |  |  |  | 0 | 85 | 93 | [6 empty] | 55 | 85 | 90 | 97 | 94 | 95 | 95 | 1061807
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 16 | 14 | 18 | 17 | 17 | 16 | 15 | 15 | 15 | 21 |  | 107 | 120 | 131 | 131 | 131 | 79 | 29 | 918576
115 | Juldah 100 MW PP Unit-3 (Acorn) | 50 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 90 | 90 | 90 | 90 | 90 | 90 | 50 | 1146240
116 | Chandpur 200MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 33 | 52 | 78 | 106 | 100 | 100 | 105 | 105 |  | 105 | 120 | 120 | 120 | 120 | 120 | 17 | 1513440
117 | Ashuganj 150MW PP (Midland) | 5 | 5 | 5 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 3 | 5 | 20 |  | 87 | 120 | 119 | 134 | 140 | 140 | 25 | 749381
118 | Bibiyana-III 400 MW CCPP | 369 | 366 | 377 | 377 | 377 | 377 | 378 | 377 | 377 | 378 | 389 | 398 | 398 | 389 | 387 | 403 | 403 | 353 |  | 390 | 404 | 403 | 398 | 404 | 403 | 383 | 9261000
| Jamalpur 115 MW PP (United) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 9 | 17 | 17 | 17 |  | 85 | 85 | 85 | 85 | 85 | 18 | 18 | 694800
| Anwara 300 MW PP (United) | 68 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 120 |  | 290 | 290 | 294 | 300 | 123 | 87 | 87 | 2428800
| Juldah unit-2 (Acorn) | 50 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 90 | 90 | 90 | 90 | 90 | 38 | 38 | 1132800
| Anlima Energy Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 523145
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 34 | 33 | 32 | 33 | 31 | 32 | 33 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 855000
| Spectra Solar Plant Ltd. |  |  |  |  | 0 | 2 | 7 | 14 | 22 | 28 | 30 | 31 | 31 | 28 | 25 | 16 | 6 | 2 |  | 0 | [6 empty] | 240586
| Chandpur 115(Doreen) | 23 | 18 | 17 | 18 | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 34 | 36 | 36 | 36 | 36 | 36 | 44 |  | 97 | 97 | 97 | 97 | 96 | 72 | 54 | 981120
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 26 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 19 | 549360
| Mirsharai 150 MW (Oil) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 140 | 163 | 163 | 163 | 18 | 18 | 874836
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 6 | 4 | 4 | 2 | 1 | 0 |  | 0 | 1 | 1 | 3 | 3 | 3 | 4 | 37488
120 | Eastern Zone Total | 7387 | 7293 | 7365 | 7330 | 7176 | 6881 | 6753 | 6542 | 6440 | 6474 | 6593 | 6884 | 7002 | 6878 | 6605 | 6702 | 6823 | 6837 |  | 8369 | 8758 | 8800 | 8833 | 8577 | 7841 | 7520 | 174572432
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 79 | 79 | 80 | 80 | 64 | 80 | 79 | 80 | 32 | 32 | 32 | 44 | 72 | 76 | 75 | 75 | 75 | 76 |  | 79 | 79 | 79 | 80 | 80 | 80 | 80 | 1674240
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 16 | 13 | 13 | 11 | 11 | 11 | 12 | 12 | 15 | 17 |  | 26 | 27 | 20 | 21 | 23 | 22 | 17 | 338400
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 416640
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 6 | 23 | 38 | 62 | 81 | 91 | 87 | 95 | 85 | 70 | 42 | 3 | 0 | [8 empty] | 685440
131 | Rampal 1320 MW (BIFPCL) | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 324 | 324 | 318 | 325 | 325 | 323 | 321 | 321 | 321 |  | 320 | 310 | 303 | 325 | 325 | 333 | 320 | 7709091
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 80 | 150 | 150 | 150 | 150 | 150 | 150 | 1191600
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 0 |  |  |  |  | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 296256
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3621800
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 172 | 172 | 174 | 173 | 173 | 172 | 172 | 169 | 167 | 167 | 164 | 164 | 168 | 168 | 150 | 166 | 159 | 159 |  | 167 | 167 | 170 | 170 | 170 | 158 | 169 | 4075559
140 | Bhola 33 MW PP (Venture) | 36 | 35 | 34 | 32 | 31 | 28 | 25 | 22 | 23 | 27 | 27 | 28 | 29 | 32 | 33 | 33 | 28 | 27 |  | 32 | 32 | 33 | 35 | 36 | 35 | 36 | 730689
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 512625
143 | Gopalganj 100 MW Peaking PP | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 35 | 35 | 35 | 30 | 30 | 40 | 25 | 25 | 25 | 25 | 35 |  | 65 | 65 | 73 | 68 | 68 | 50 | 50 | 1003392
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 85 | 102 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2539008
146 | Bheramara HVDC | 838 | 839 | 909 | 910 | 909 | 908 | 908 | 909 | 909 | 909 | 909 | 909 | 909 | 909 | 906 | 908 | 909 | 909 |  | 909 | 804 | 804 | 803 | 803 | 804 | 803 | 21224727
147 | Bheramara 410 MW CCPP | 155 | 155 | 154 | 160 | 165 | 165 | 165 | 160 | 160 | 165 | 160 | 160 | 160 | 160 | 165 | 185 | 195 | 205 |  | 220 | 220 | 220 | 225 | 225 | 215 | 210 | 4478976
148 | Payra 1320 MW | 300 | 290 | 290 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 410 | 560 | 622 | 410 | 300 | 300 | 300 |  | 300 | 390 | 440 | 610 | 622 | 580 | 320 | 10227500
149
150 | Barapukuria TPP Unit-1 | 73 | 73 | 73 | 73 | 73 | 75 | 74 | 75 | 75 | 75 | 75 | 76 | 73 | 74 | 74 | 74 | 75 | 74 |  | 74 | 75 | 75 | 75 | 75 | 73 | 74 | 1736290
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 250 | 250 | 240 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5674000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 27 | 27 | 27 | 27 | 27 | 0 | [13 empty] | 0 | 28 | 28 | 28 | 28 | 28 | 28 | 285936
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 4 | 4 | 3 | 0 | 1 | 0 | [8 empty] | 36240
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 163 | 164 | 167 | 171 | 170 | 170 | 171 | 170 | 140 | 140 | 140 | 155 | 170 | 140 | 140 | 140 | 140 | 140 |  | 145 | 188 | 194 | 199 | 198 | 201 | 201 | 4192400
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 152 | 154 | 154 | 154 | 155 | 156 | 157 | 156 | 130 | 130 | 130 | 143 | 153 | 130 | 130 | 130 | 130 | 130 |  | 140 | 160 | 169 | 176 | 174 | 171 | 170 | 3882273
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 364 | 363 | 370 | 382 | 388 | 388 | 377 | 344 | 336 | 336 | 338 | 414 | 374 | 326 | 285 | 295 | 325 | 287 |  | 382 | 414 | 414 | 415 | 414 | 421 | 414 | 8675600
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 18 | 18 | 18 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 260770
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 19 | 17 | 15 | 15 | 13 | 11 | 11 | 10 | 11 | 13 | 16 |  | 17 | 19 | 19 | 19 | 19 | 20 | 21 | 399360
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 172206
165 | Amnura 50 MW PP(Sinha) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 577490
166 | Katakhali 50 MW PP (Northern) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 8 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 8 | 25 | 25 | 25 | 25 | 25 | 25 | 527665
167 | Katakhali 50 MW Peaking PP | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 32 | 22 | 30 | 30 | 30 | 35 | 22 | 22 | 32 |  | 37 | 37 | 40 | 37 | 37 | 37 | 37 | 611487
168 | Santahar 50 MW Peaking PP | [19 empty] | 0 | 5 | 15 | 30 | 30 | 29 | 29 | 115199
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 43 |  | 25 | 34 | 34 | 34 |  |  | 0 | 136099
170 | Chapainawabganj 100 MW Peaking PP | 70 | 56 | 56 | 56 | 56 | 35 | 35 | 35 | 35 | 35 | 34 | 32 | 32 | 32 | 32 | 38 | 40 | 40 |  | 58 | 80 | 84 | 84 | 84 | 76 | 76 | 1179776
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 50 | 50 | 50 | 50 | 35 | 35 | 967968
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 0 |  |  | 0 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 823200
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 | 0 |  |  | 28 | 33 | 34 | 33 | 33 | 33 | 33 | 32 | 31 | 47 | 60 |  | 62 | 62 | 55 | 56 | 49 | 34 | 34 | 813628
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 1 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 5 | 3 | 1 |  | 0 | [6 empty] | 58505
178 | Energypac Power Venture Thakurgaon Ltd. | [9 empty] | 0 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 39 |  | 80 | 110 | 114 | 114 | 114 | 55 | 0 | 848256
| Intraco Solar 30 MW |  |  |  |  | 0 | 2 | 7 | 15 | 23 | 28 | 32 | 22 | 31 | 28 | 22 | 15 | 7 | 2 |  | 0 | [6 empty] | 203942
| Adani Power Jharkhanda Ltd | 1060 | 1060 | 1062 | 1049 | 1054 | 1053 | 1051 | 1055 | 1057 | 1053 | 1054 | 1067 | 1067 | 1075 | 1073 | 1055 | 1056 | 1071 |  | 1056 | 1056 | 1054 | 1053 | 1062 | 1051 | 1061 | 25527273
178 | Teesta Solar Limited |  |  |  |  | 0 | 13 | 48 | 94 | 136 | 169 | 187 | 189 | 181 | 168 | 134 | 91 | 46 | 11 | [8 empty] | 1465270