## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-06-10 | Saturday
|  | Date (day): | 2023-06-10 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12752.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15281 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-06-09 | 2023-06-10 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 110 | 110 | 110 | 70 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 370 | 402 | 400 | 400 |  |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 280 | 350 | 330 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 52 | 83 | 50 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 281 | 275 | 280 | 280 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 17 | 17 | 17 |  | 85 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 0 | 25 | 30 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 20 | 0 | 0 | 0 | 11 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 15 | 10 | 19 | 19 |  | 3 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 187 | 163 | 100 | 100 | 110 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 58 | 10 | 75 | 75 | 25 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 1 | 218 | 218 | 218 |  | 117 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 50 | 50 | 74 | 28 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 0 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 32 | 82 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 35 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 45 | 47 | 48 | 48 |  | 32 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 25 | 25 | 25 |  |  | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 32 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 8 | 8 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 47 | 15 | 45 | 145 | 155 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 102 | 17 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 70 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 72 | 72 | 72 | 32 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 108 | 35 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 7 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 17 | 35 | 20 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5867 | 2369 | 3005 | 3266 | 3908 | 783 | 1097
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 114 | 113 | 120 | 120 | 60 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 0 | 8 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 8 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 22 | 50 | 50
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 0 | 25 | 25 | 25 | 205 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 222 | 226 | 225 | 225
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 51 | 51 | 51 | 54 |  | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 33 | 55 | 73 |  | 25 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 34 | 34 | 51 | 51 |  | 51 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 33 | 33 | 33 | 33 | 67 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 63 | 25 | 63 | 37 |  | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 9 | 11 | 11 | 11 | 11 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 35 | 42 | 10 | 25
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 70 | 205 | 70 | 300
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 34 | 51 | 51 | 74 | 36 |  | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 63 | 25 | 63 | 50 |  | Fuel shortage
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 68 | 34 | 68 | 48 |  | Fuel shortage
| Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 18 | 163 | 72 | 163 |  |  | On test.
| SS Power I |  | Coal | SS Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 1 | 5 | 5 | 0
| Chattogram area Total |  |  |  |  | 2605 | 2545 | 697 | 1225 | 963 | 1437 | 713 | 406
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 179 | 207 | 200 | 200 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 285 | 280 | 300 | 310 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 275 | 275 | 300 | 300 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 248 | 295 | 270 | 295 | 105 |  | Gas shortage
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 42 | 43 | 40 | 40 |  |  | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 6 | 150 | 12 | 150
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 37 | 46 | 45 | 45 |  | 7 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 100 | 51 | 100 | 100 |  | Fuel shortage
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 20 | 20 |  | 2 | Engine problem
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 122 | 140 | 129 | 152
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 32 | 33 | 33 | 33
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 52 | 26 | 52
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 14 | 20 | 20 |  | 5 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Contract Expired
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 0 | 17 | 114
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 95 | 9 | 98 |  | 15 | Engine problem
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 17 | 17 | 35 |  | 19 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 36 | 115 | 72 | 95 |  |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 3159 | 3096 | 1474 | 1951 | 1631 | 2129 | 392 | 211
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 33 | 102 | 30 | 102 | 100 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 0 | 18 | 18 | 4 |  | Gas shortage
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 68 | 87 | 68 | 86 | 114 |  | Fuel shortage
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 18 | 85 | 18 | 86 | 29 |  | Fuel shortage
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 13 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 0 | 12 | 12 | 10 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 162 | 274 | 197.6 | 304 | 104 | 0
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 39 | 40 | 40 |  | 50 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 80 | 112 | 112 | 112 |  | 51 | ST under maint.
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 50 | 50 | 50
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 50 | 47 | 50 | 50
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 56 | 56 | 56
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 72 | 74 | 76 | 76
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 181 | 180 | 195 | 195 |  | 36
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 9 |  | Gas shortage
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 265 | 300 | 300 | 310 |  |  | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 334 | 365 | 400 | 400 |  |  | FGMO
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 260 | 260 | 50 | 200 |  | 183 | ST under maint.
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1465 | 1563 | 1409 | 1569 | 9 | 777
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 910 | 766 | 929 | 929
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 0 | 16 | 49 |  | 66 | Engine problem
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 15 | 0 | 20 | 30 |  | 24 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 205 | 120 | 170 | 205 | 25
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 23 | 0 | 60 | 70 |  | 39 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 190 | 265 | 230 | 250 | 160 |  | Gas shortage
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 8 | 0 | 8 | 40
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 0 | 54 | 70 | 35 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 50 | 0 | 50 | 85
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 39 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 235 | 0 | 0 | 220 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 375 | 376 | 370 | 370 | 247 |  | Coal Shortage.
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 2905 | 2901 | 2119 | 1527 | 2007 | 2318 | 483 | 129
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 32 | 16 | 48 | 46 |  | Fuel shortage
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 22 | 33 | 21 | 33 |  | 7 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 172 | 156 | 170 | 170 |  | 24 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 0 | 0 | 0 | 0 | 1244 |  | Coal Shortage.
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 40 | 110 | 110 | 110 |  | 220 | ST Under maintenance
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 17 | 150
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 250 | 225 | 307 | 307
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 517 | 573 | 641 | 818 | 1290 | 251
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 27 | 0 | 28 | 28 |  | 24 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 |  | 41 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 28 | 28 | 0 | 28 | 28
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 0 | 25 | 34 |  | 16 | Engine problem
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 22 | 0 | 36 | 36 |  | 14 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 160 | 202 | 180 | 190 | 20 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 169 | 176 | 150 | 170 | 50 |  | Gas shortage
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 285 | 426 | 380 | 400 | 14 |  | Gas shortage
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 35 | 35 |  | 15 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 19 | 22 | 22 | 22
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 52
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 40 | 26 | 40 | 90 |  | 14 | Engine problem
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 40 | 35 | 57 | 56 |  | Fuel shortage
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 113 | 35 | 56 | 57 |  | Fuel shortage
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 1 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 748*1 | 748 | 748 | 1082 | 1052 | 1060 | 1060
| Rajshahi Area Total |  |  |  |  | 2927 | 2905 | 1945 | 2093 | 2098 | 2296 | 788 | 127
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 64 | 72 | 72 | 72 | 13
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 230 | 250 | 230 | 250
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 16 | 4 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 35 | 56 | 35 | 49 | 64 |  | Fuel shortage
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 110 | 35 | 115
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 0 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 8 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 341 | 488 | 540 | 502 | 101 | 85
| Total |  |  |  |  | 24143 | 23370 | 11089 | 12699 | 12752.6 | 15281 | 4663 | 3083
A. |  | 2023-06-09 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 12699 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 11089 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12699 | MW
3 | Day peak Generation : |  |  | 11089 | MW at | 9:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12097.77 | MW
4 | Evening peak Generation : |  |  | 12699 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 275.5955 | MKWHr | By Solar | 1.214 | MKWHr
| By Gas : | 146.1267 | MKWHr |  | By Oil: | 57.4791 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 45.7425 | MKWHr |  | By Hydro: | 0.33192 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.07128 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4663 | MW | Dhaka | 4102.67 | 4102.67 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3083 | MW | Chittagong | 1185.5 | 1185.5 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 7746 | MW | Khulna | 1372.4 | 1372.4 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 1200.35 | MMCFD |  |  | Rajshahi | 1343.2 | 1343.2 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 161034962.616 | ii) Oil : | Taka | 718755762.27 | Comilla | 1254 | 1254 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 40001798.13 | Total | Taka | 919792523.016 | Mymensingh | 968 | 968 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 567 | 567 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 730 | MW (E to W) at | 21:00 | hrs | Barisal | 408 | 408 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 710 | MW at | 20:00 | hrs | Rangpur | 897 | 897 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 32.1° C |  |  | Total | 12097.77 | 12097.77 |  | 0
B. |  | 2023-06-10 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 32.1° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 14000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15281 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 12000 | MW
4 | Reserve(Generation end) |  |  |  | 1281 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 303.83 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10176 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.5389 | MKWHr. | ii) HVDC Flow at Peak Time |  | 766 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.0912 | MKWHr. | iii) Maximum HVDC Flow : |  | 911 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 72.46 |  | (b) Today: | 72.55 |  | (c) Rule Curve: |  | 78.34
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-06-09 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 100 | 170 | 0 | 0 | 0 | 406 | 337 |  | 0 | 450 | 308 | 50 | 0 | 0 | 0 | 0 | 195 | 50 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 20 | 25 | 33 | 32 | 8 | 0 | 0 | 0 | 120 | 0 | 8 | 219 | 0 | 0 | 0 |  | 9 | 73 | 46 | 33 | 0 | 12 | 9 | 33 | 0 | 0 | 0 | 320 | 300 | 139 | 8 | 0 | 44 | 0 | 0 | 51 | 0 | 46 | 26 | 19 | 11 | 33 | 20 | 156 | 72 | 0 | 10 | 0 | 43 | 40 | 50 | 44 | 112 | 0 | 56 | 76 | 0 | 181 | 0 | 0 | 10 | 320 | 16 | 8 | 0 | 55 | 0 | 0 | 68 | 40 | 17 | 0 | 25 | 17 | 5 | 371 | 19 | 105 | 17 | 0 | 69 | 17 | 41 | 17 | 9 | 25 | 257 | 17 | 0 | 17 | 17 | 0 | 35 | 0 | 71 | 17 | 223 | 18 | 0 | 0 | 0 |  | 911 | 0 | 170 | 0 | 16 | 200 | 0 | 0 | 15 | 45 | 8 | 172 | 36 | 16 | 0 | 0 | 0 | 27 | 14 | 72 | 28 | 34 | 23 | 0 | 35 | 20 | 0 | 8 | 66 | 0 | 230 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 414 | 54 | 0 | 35 | 50 | 34 | 0 | 0 | 35 | 0 | 26 | 0 | 17 | 0 | 0 | 0 | 234 | 0 | 376 | 0 | 250 | 1072 | 0 | 0 |  | 6601 | 5078 | 11679 | 4192 | 911 | 2295 | 40 | 1211 | 1994 | 0 | 434 | 446 | 156 | 0 | 0 | 2312.055 | 72.43
2:00 | 0 | 0 | 100 | 170 | 0 | 0 | 0 | 404 | 332 |  | 0 | 450 | 305 | 50 | 0 | 0 | 0 | 0 | 196 | 50 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 20 | 25 | 33 | 32 | 8 | 0 | 0 | 0 | 120 | 0 | 8 | 220 | 0 | 0 | 0 |  | 12 | 34 | 47 | 33 | 0 | 6 | 9 | 34 | 0 | 0 | 0 | 320 | 285 | 136 | 8 | 0 | 43 | 0 | 0 | 51 | 0 | 46 | 25 | 19 | 11 | 33 | 20 | 152 | 72 | 0 | 10 | 0 | 43 | 40 | 50 | 44 | 112 | 0 | 56 | 76 | 0 | 181 | 0 | 0 | 10 | 330 | 16 | 11 | 0 | 47 | 0 | 0 | 68 | 0 | 17 | 0 | 25 | 17 | 6 | 371 | 19 | 105 | 17 | 0 | 70 | 17 | 34 | 17 | 9 | 25 | 260 | 0 | 0 | 17 | 17 | 0 | 35 | 0 | 20 | 17 | 217 | 18 | 0 | 0 | 0 |  | 910 | 0 | 170 | 0 | 16 | 200 | 0 | 0 | 15 | 31 | 8 | 172 | 35 | 16 | 0 | 0 | 0 | 27 | 14 | 72 | 28 | 34 | 22 | 0 | 35 | 20 | 0 | 8 | 65 | 0 | 230 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 414 | 54 | 0 | 35 | 50 | 34 | 0 | 0 | 35 | 0 | 27 | 0 | 17 | 0 | 0 | 0 | 233 | 0 | 376 | 0 | 250 | 1074 | 0 | 0 |  | 6418 | 5063 | 11481 | 4174 | 910 | 2298 | 0 | 1126 | 1995 | 0 | 433 | 393 | 152 | 0 | 0 | 2214.645 | 72.44
3:00 | 0 | 0 | 100 | 170 | 0 | 0 | 0 | 403 | 333 |  | 0 | 450 | 310 | 50 | 0 | 0 | 0 | 0 | 193 | 50 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 20 | 25 | 33 | 32 | 8 | 0 | 0 | 0 | 120 | 0 | 8 | 220 | 0 | 0 | 0 |  | 12 | 34 | 50 | 33 | 0 | 6 | 9 | 33 | 0 | 0 | 0 | 320 | 305 | 132 | 8 | 0 | 43 | 0 | 0 | 51 | 0 | 46 | 25 | 19 | 11 | 33 | 20 | 148 | 72 | 0 | 10 | 0 | 43 | 40 | 50 | 50 | 112 | 0 | 56 | 76 | 0 | 181 | 0 | 0 | 10 | 330 | 16 | 11 | 0 | 47 | 0 | 0 | 68 | 0 | 17 | 0 | 25 | 17 | 6 | 372 | 19 | 105 | 17 | 0 | 69 | 17 | 34 | 17 | 9 | 25 | 258 | 0 | 0 | 17 | 17 | 0 | 35 | 0 | 17 | 17 | 218 | 18 | 0 | 0 | 1 |  | 911 | 0 | 170 | 0 | 16 | 200 | 0 | 0 | 15 | 31 | 8 | 172 | 35 | 16 | 0 | 0 | 0 | 27 | 14 | 72 | 28 | 34 | 22 | 0 | 35 | 21 | 0 | 8 | 63 | 0 | 230 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 414 | 54 | 0 | 35 | 50 | 34 | 0 | 0 | 0 | 0 | 25 | 0 | 17 | 0 | 0 | 0 | 233 | 0 | 376 | 0 | 250 | 1067 | 0 | 0 |  | 6437 | 5022 | 11459 | 4189 | 911 | 2308 | 0 | 1087 | 1986 | 0 | 433 | 396 | 148 | 0 | 1 | 2092.405 | 72.44
4:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 404 | 332 |  | 0 | 450 | 308 | 50 | 0 | 0 | 0 | 0 | 192 | 50 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 20 | 26 | 33 | 32 | 8 | 0 | 0 | 0 | 119 | 0 | 8 | 223 | 0 | 0 | 0 |  | 12 | 34 | 50 | 33 | 0 | 6 | 9 | 35 | 0 | 0 | 0 | 320 | 310 | 129 | 8 | 0 | 43 | 0 | 0 | 51 | 0 | 46 | 25 | 19 | 11 | 33 | 20 | 150 | 82 | 0 | 10 | 0 | 43 | 40 | 50 | 50 | 112 | 0 | 56 | 76 | 0 | 181 | 0 | 0 | 10 | 330 | 16 | 11 | 0 | 47 | 0 | 0 | 68 | 0 | 17 | 0 | 25 | 17 | 6 | 347 | 19 | 105 | 17 | 0 | 69 | 17 | 34 | 17 | 9 | 25 | 260 | 0 | 0 | 17 | 17 | 0 | 35 | 0 | 18 | 17 | 218 | 18 | 0 | 0 | 0 |  | 911 | 0 | 170 | 0 | 16 | 200 | 0 | 0 | 15 | 27 | 8 | 170 | 34 | 16 | 0 | 0 | 0 | 27 | 0 | 72 | 28 | 34 | 22 | 0 | 35 | 21 | 0 | 8 | 66 | 0 | 230 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 414 | 54 | 0 | 35 | 50 | 34 | 0 | 0 | 0 | 0 | 12 | 0 | 17 | 0 | 0 | 0 | 234 | 0 | 376 | 0 | 250 | 1062 | 0 | 0 |  | 6440 | 4992 | 11432 | 4194 | 911 | 2293 | 0 | 1088 | 1984 | 0 | 434 | 378 | 150 | 0 | 0 | 1974.94 | 72.45
5:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 404 | 331 |  | 0 | 450 | 310 | 50 | 0 | 0 | 0 | 0 | 196 | 50 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 20 | 26 | 33 | 32 | 8 | 0 | 0 | 0 | 116 | 0 | 8 | 223 | 0 | 0 | 0 |  | 12 | 34 | 50 | 33 | 0 | 6 | 9 | 36 | 0 | 0 | 0 | 320 | 275 | 140 | 8 | 0 | 43 | 0 | 0 | 51 | 0 | 46 | 25 | 19 | 11 | 33 | 20 | 144 | 82 | 0 | 10 | 0 | 43 | 40 | 50 | 50 | 112 | 0 | 56 | 76 | 0 | 181 | 0 | 0 | 10 | 335 | 16 | 11 | 0 | 47 | 0 | 0 | 68 | 0 | 17 | 0 | 25 | 17 | 5 | 347 | 19 | 105 | 17 | 0 | 69 | 17 | 34 | 17 | 9 | 25 | 260 | 15 | 0 | 17 | 17 | 0 | 35 | 0 | 17 | 17 | 218 | 18 | 0 | 0 | 0 |  | 911 | 0 | 190 | 0 | 16 | 200 | 0 | 0 | 15 | 21 | 8 | 170 | 33 | 16 | 0 | 0 | 0 | 27 | 0 | 72 | 28 | 34 | 22 | 0 | 35 | 21 | 0 | 8 | 66 | 0 | 230 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 415 | 54 | 0 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 17 | 0 | 0 | 0 | 235 | 0 | 376 | 0 | 250 | 1058 | 0 | 0 |  | 6431 | 4972 | 11403 | 4195 | 911 | 2299 | 0 | 1067 | 1980 | 0 | 435 | 372 | 144 | 0 | 0 | 1859.385 | 72.45
6:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 409 | 333 |  | 0 | 450 | 305 | 50 | 0 | 0 | 6 | 0 | 177 | 50 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 20 | 26 | 33 | 32 | 8 | 0 | 0 | 0 | 112 | 0 | 8 | 226 | 0 | 0 | 0 |  | 12 | 34 | 50 | 33 | 0 | 6 | 9 | 36 | 0 | 0 | 0 | 320 | 265 | 154 | 8 | 0 | 42 | 0 | 0 | 51 | 0 | 46 | 25 | 19 | 11 | 19 | 20 | 130 | 72 | 0 | 10 | 0 | 43 | 40 | 50 | 50 | 112 | 0 | 28 | 76 | 0 | 181 | 0 | 0 | 10 | 310 | 16 | 11 | 0 | 47 | 0 | 0 | 68 | 0 | 17 | 1 | 25 | 17 | 6 | 347 | 19 | 105 | 17 | 0 | 70 | 17 | 34 | 17 | 9 | 25 | 260 | 17 | 1 | 17 | 17 | 0 | 35 | 1 | 18 | 17 | 218 | 18 | 0 | 0 | 1 |  | 911 | 0 | 190 | 0 | 16 | 200 | 0 | 0 | 15 | 22 | 8 | 172 | 30 | 16 | 0 | 0 | 0 | 27 | 0 | 60 | 28 | 34 | 22 | 0 | 0 | 21 | 0 | 8 | 63 | 0 | 230 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 418 | 54 | 0 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 17 | 0 | 1 | 0 | 235 | 0 | 376 | 0 | 250 | 1056 | 1 | 0 |  | 6340 | 4930 | 11270 | 4143 | 911 | 2272 | 0 | 1072 | 1975 | 0 | 435 | 326 | 130 | 5 | 1 | 1556.65 | 72.46
7:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 411 | 332 |  | 0 | 450 | 305 | 50 | 0 | 0 | 2 | 0 | 194 | 50 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 20 | 26 | 0 | 32 | 8 | 0 | 0 | 0 | 117 | 0 | 8 | 225 | 0 | 0 | 0 |  | 12 | 0 | 50 | 33 | 0 | 6 | 9 | 36 | 0 | 0 | 0 | 310 | 265 | 167 | 8 | 0 | 42 | 0 | 0 | 51 | 0 | 45 | 25 | 19 | 11 | 32 | 20 | 112 | 34 | 0 | 13 | 0 | 43 | 40 | 50 | 50 | 112 | 0 | 58 | 76 | 0 | 181 | 0 | 0 | 10 | 285 | 16 | 11 | 0 | 47 | 0 | 0 | 68 | 0 | 17 | 5 | 25 | 17 | 6 | 347 | 19 | 105 | 17 | 1 | 69 | 17 | 34 | 17 | 9 | 25 | 260 | 17 | 1 | 17 | 17 | 0 | 35 | 4 | 18 | 17 | 236 | 18 | 0 | 0 | 0 |  | 911 | 0 | 190 | 0 | 16 | 205 | 0 | 0 | 15 | 22 | 8 | 172 | 27 | 16 | 0 | 0 | 0 | 27 | 0 | 40 | 28 | 34 | 22 | 0 | 0 | 20 | 0 | 8 | 63 | 0 | 230 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 354 | 53 | 0 | 35 | 50 | 0 | 0 | 0 | 35 | 0 | 11 | 0 | 17 | 0 | 8 | 0 | 236 | 0 | 376 | 1 | 250 | 1066 | 7 | 0 |  | 6282 | 4910 | 11192 | 4163 | 911 | 2177 | 0 | 1105 | 1985 | 0 | 441 | 271 | 112 | 27 | 0 | 1440.14 | 72.46
8:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 406 | 307 |  | 0 | 450 | 263 | 51 | 0 | 0 | 1 | 0 | 198 | 50 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 20 | 26 | 33 | 32 | 8 | 0 | 0 | 0 | 112 | 0 | 8 | 227 | 0 | 0 | 0 |  | 12 | 0 | 50 | 33 | 0 | 6 | 9 | 36 | 0 | 0 | 0 | 305 | 275 | 167 | 8 | 0 | 42 | 0 | 0 | 51 | 0 | 45 | 25 | 19 | 11 | 32 | 20 | 114 | 34 | 0 | 17 | 1 | 43 | 40 | 50 | 50 | 80 | 0 | 59 | 76 | 0 | 181 | 0 | 0 | 10 | 270 | 16 | 11 | 0 | 47 | 0 | 0 | 68 | 0 | 17 | 5 | 25 | 17 | 5 | 347 | 19 | 105 | 17 | 2 | 69 | 17 | 34 | 17 | 3 | 25 | 260 | 17 | 5 | 17 | 17 | 0 | 35 | 12 | 20 | 17 | 242 | 18 | 0 | 0 | 1 |  | 911 | 0 | 190 | 0 | 16 | 205 | 0 | 0 | 15 | 22 | 8 | 172 | 25 | 16 | 0 | 0 | 0 | 27 | 0 | 40 | 28 | 34 | 22 | 0 | 0 | 20 | 0 | 8 | 63 | 0 | 230 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 357 | 53 | 0 | 35 | 50 | 40 | 0 | 0 | 35 | 0 | 17 | 0 | 17 | 1 | 20 | 0 | 235 | 0 | 376 | 0 | 250 | 1061 | 1 | 0 |  | 6225 | 4962 | 11187 | 4212 | 911 | 2070 | 0 | 1141 | 1980 | 0 | 440 | 271 | 114 | 47 | 1 | 1444.915 | 72.47
9:00 | 0 | 0 | 110 | 180 | 0 | 0 | 0 | 370 | 280 |  | 0 | 450 | 281 | 52 | 0 | 0 | 1 | 0 | 187 | 58 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 20 | 25 | 33 | 32 | 8 | 0 | 0 | 0 | 114 | 0 | 8 | 222 | 0 | 0 | 0 |  | 12 | 0 | 34 | 33 | 0 | 6 | 9 | 35 | 0 | 0 | 0 | 285 | 275 | 179 | 8 | 0 | 42 | 0 | 0 | 51 | 0 | 37 | 25 | 19 | 11 | 32 | 20 | 122 | 33 | 0 | 17 | 1 | 43 | 40 | 44 | 50 | 80 | 0 | 59 | 72 | 0 | 181 | 0 | 0 | 10 | 265 | 16 | 11 | 0 | 47 | 0 | 0 | 68 | 0 | 17 | 8 | 25 | 17 | 6 | 334 | 18 | 105 | 17 | 4 | 70 | 17 | 34 | 17 | 9 | 25 | 260 | 17 | 13 | 17 | 17 | 0 | 35 | 7 | 36 | 17 | 248 | 18 | 0 | 0 | 1 |  | 910 | 0 | 190 | 0 | 16 | 205 | 0 | 0 | 15 | 23 | 8 | 172 | 22 | 16 | 0 | 0 | 0 | 27 | 0 | 40 | 28 | 34 | 22 | 0 | 0 | 19 | 0 | 8 | 64 | 0 | 230 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 285 | 53 | 0 | 35 | 50 | 35 | 0 | 4 | 35 | 0 | 40 | 0 | 17 | 1 | 39 | 0 | 235 | 0 | 375 | 0 | 250 | 1082 | 8 | 0 |  | 6167 | 4922 | 11089 | 4122 | 910 | 1992 | 0 | 1168 | 2001 | 0 | 440 | 248 | 122 | 85 | 1 | 1347.505 | 72.47
10:00 | 0 | 0 | 110 | 180 | 0 | 0 | 0 | 371 | 285 |  | 0 | 450 | 283 | 50 | 10 | 0 | 1 | 0 | 193 | 59 | 8 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 20 | 22 | 33 | 32 | 8 | 0 | 25 | 0 | 120 | 0 | 8 | 223 | 0 | 0 | 0 |  | 12 | 0 | 34 | 33 | 0 | 6 | 9 | 35 | 0 | 0 | 0 | 280 | 275 | 183 | 8 | 0 | 42 | 0 | 0 | 51 | 0 | 29 | 25 | 15 | 5 | 32 | 13 | 104 | 31 | 0 | 19 | 1 | 43 | 40 | 44 | 50 | 80 | 0 | 59 | 74 | 0 | 181 | 0 | 0 | 10 | 270 | 15 | 11 | 0 | 47 | 0 | 0 | 68 | 0 | 17 | 11 | 25 | 38 | 6 | 340 | 18 | 105 | 17 | 2 | 70 | 17 | 34 | 17 | 9 | 25 | 260 | 17 | 28 | 17 | 15 | 0 | 33 | 13 | 39 | 17 | 248 | 36 | 0 | 0 | 2 |  | 911 | 0 | 200 | 0 | 16 | 205 | 0 | 0 | 15 | 23 | 8 | 172 | 21 | 16 | 0 | 0 | 0 | 27 | 0 | 31 | 28 | 8 | 22 | 0 | 0 | 18 | 0 | 8 | 65 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 230 | 17 | 0 | 35 | 35 | 35 | 0 | 4 | 0 | 0 | 75 | 0 | 17 | 1 | 36 | 0 | 234 | 0 | 369 | 0 | 250 | 1068 | 2 | 0 |  | 6266 | 4752 | 11018 | 4101 | 911 | 1984 | 0 | 1085 | 2002 | 25 | 439 | 267 | 104 | 98 | 2 | 937.81 | 72.48
11:00 | 0 | 0 | 110 | 180 | 0 | 0 | 0 | 387 | 300 |  | 0 | 450 | 260 | 53 | 17 | 0 | 1 | 0 | 196 | 63 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 15 | 20 | 22 | 25 | 32 | 8 | 0 | 25 | 0 | 117 | 0 | 8 | 222 | 0 | 0 | 0 |  | 12 | 0 | 33 | 33 | 0 | 6 | 9 | 35 | 0 | 0 | 0 | 285 | 275 | 186 | 8 | 0 | 42 | 0 | 0 | 51 | 0 | 29 | 25 | 15 | 5 | 33 | 13 | 108 | 30 | 0 | 19 | 0 | 43 | 40 | 42 | 49 | 112 | 0 | 59 | 74 | 0 | 181 | 0 | 0 | 10 | 270 | 15 | 11 | 0 | 47 | 0 | 0 | 68 | 0 | 17 | 2 | 25 | 51 | 5 | 351 | 18 | 105 | 17 | 1 | 70 | 17 | 34 | 17 | 9 | 25 | 260 | 52 | 45 | 90 | 17 | 0 | 17 | 17 | 67 | 17 | 249 | 36 | 0 | 0 | 1 |  | 911 | 0 | 205 | 0 | 16 | 205 | 0 | 0 | 18 | 30 | 8 | 173 | 21 | 16 | 0 | 0 | 0 | 27 | 0 | 31 | 28 | 8 | 36 | 0 | 0 | 20 | 0 | 8 | 66 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 210 | 17 | 0 | 35 | 15 | 34 | 0 | 6 | 0 | 0 | 30 | 0 | 17 | 2 | 22 | 0 | 235 | 0 | 369 | 0 | 250 | 918 | 18 | 0 |  | 6523 | 4555 | 11078 | 4134 | 911 | 1942 | 0 | 1229 | 1853 | 25 | 440 | 322 | 108 | 113 | 1 | 498.51 | 72.48
12:00 | 0 | 0 | 110 | 180 | 0 | 0 | 0 | 344 | 246 |  | 0 | 450 | 270 | 67 | 17 | 0 | 12 | 0 | 205 | 60 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 15 | 0 | 20 | 25 | 33 | 8 | 0 | 25 | 0 | 116 | 0 | 8 | 221 | 0 | 0 | 0 |  | 12 | 0 | 34 | 33 | 0 | 10 | 9 | 35 | 0 | 0 | 0 | 285 | 275 | 184 | 8 | 0 | 41 | 0 | 0 | 51 | 0 | 30 | 25 | 19 | 5 | 33 | 12 | 112 | 31 | 0 | 19 | 0 | 43 | 40 | 42 | 49 | 112 | 0 | 59 | 74 | 0 | 174 | 0 | 0 | 10 | 275 | 15 | 11 | 0 | 47 | 0 | 0 | 68 | 0 | 17 | 0 | 25 | 51 | 6 | 390 | 18 | 105 | 17 | 2 | 69 | 17 | 34 | 17 | 9 | 25 | 260 | 54 | 14 | 90 | 17 | 0 | 17 | 9 | 73 | 17 | 248 | 36 | 0 | 0 | 2 |  | 911 | 0 | 210 | 0 | 16 | 205 | 0 | 0 | 0 | 0 | 8 | 173 | 22 | 16 | 0 | 0 | 0 | 27 | 0 | 38 | 28 | 8 | 36 | 0 | 0 | 20 | 0 | 0 | 66 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 210 | 17 | 0 | 35 | 15 | 34 | 0 | 6 | 0 | 0 | 26 | 0 | 17 | 0 | 22 | 0 | 230 | 0 | 366 | 23 | 150 | 911 | 133 | 0 |  | 6495 | 4529 | 11024 | 4117 | 911 | 1900 | 0 | 1287 | 1743 | 25 | 435 | 283 | 112 | 209 | 2 | 263.58 | 72.49
13:00 | 0 | 0 | 110 | 180 | 0 | 0 | 0 | 314 | 246 |  | 0 | 370 | 258 | 67 | 17 | 0 | 216 | 0 | 145 | 60 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 15 | 25 | 33 | 8 | 0 | 30 | 0 | 110 | 0 | 8 | 225 | 0 | 0 | 0 |  | 0 | 25 | 33 | 33 | 0 | 44 | 9 | 40 | 0 | 0 | 0 | 285 | 275 | 185 | 8 | 0 | 41 | 0 | 0 | 51 | 0 | 34 | 14 | 19 | 8 | 33 | 12 | 120 | 30 | 0 | 19 | 0 | 43 | 39 | 42 | 49 | 112 | 0 | 58 | 74 | 0 | 174 | 0 | 0 | 10 | 275 | 15 | 11 | 0 | 47 | 0 | 0 | 67 | 0 | 17 | 0 | 25 | 51 | 5 | 403 | 18 | 105 | 17 | 3 | 69 | 17 | 34 | 17 | 9 | 38 | 256 | 73 | 1 | 90 | 17 | 0 | 25 | 2 | 72 | 17 | 248 | 36 | 0 | 0 | 2 |  | 909 | 0 | 225 | 0 | 16 | 205 | 0 | 0 | 0 | 0 | 8 | 173 | 24 | 16 | 0 | 0 | 0 | 27 | 10 | 31 | 28 | 8 | 36 | 0 | 0 | 20 | 0 | 0 | 69 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 220 | 17 | 0 | 35 | 15 | 34 | 0 | 6 | 0 | 0 | 26 | 0 | 17 | 0 | 46 | 8 | 230 | 0 | 372 | 19 | 150 | 908 | 81 | 0 |  | 6598 | 4539 | 11137 | 4234 | 909 | 1825 | 0 | 1361 | 1749 | 30 | 435 | 314 | 120 | 158 | 2 | 0 | 72.49
14:00 | 0 | 0 | 110 | 180 | 0 | 0 | 0 | 284 | 233 |  | 0 | 270 | 269 | 67 | 17 | 0 | 60 | 0 | 98 | 40 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 20 | 15 | 25 | 33 | 8 | 0 | 30 | 0 | 119 | 0 | 8 | 225 | 0 | 0 | 0 |  | 0 | 32 | 34 | 33 | 0 | 40 | 9 | 25 | 0 | 0 | 0 | 285 | 275 | 151 | 8 | 0 | 41 | 0 | 0 | 51 | 0 | 38 | 8 | 19 | 11 | 33 | 12 | 124 | 27 | 0 | 0 | 0 | 43 | 39 | 24 | 48 | 80 | 0 | 40 | 20 | 0 | 175 | 0 | 0 | 10 | 255 | 8 | 11 | 0 | 15 | 0 | 0 | 68 | 0 | 17 | 0 | 25 | 51 | 6 | 291 | 19 | 17 | 17 | 1 | 69 | 17 | 34 | 17 | 9 | 38 | 220 | 74 | 5 | 17 | 17 | 0 | 35 | 0 | 72 | 17 | 249 | 36 | 0 | 0 | 3 |  | 911 | 0 | 235 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 172 | 22 | 0 | 0 | 0 | 0 | 27 | 12 | 23 | 28 | 0 | 36 | 0 | 0 | 20 | 0 | 8 | 67 | 0 | 250 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 27 | 0 | 0 | 0 | 51 | 35 | 230 | 0 | 372 | 20 | 150 | 909 | 75 | 0 |  | 5654 | 4353 | 10007 | 3803 | 911 | 1590 | 0 | 1013 | 1748 | 30 | 390 | 238 | 124 | 157 | 3 | 0 | 72.48
15:00 | 0 | 0 | 110 | 180 | 0 | 0 | 0 | 270 | 235 |  | 0 | 300 | 307 | 68 | 17 | 0 | 60 | 0 | 125 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 20 | 15 | 17 | 16 | 8 | 0 | 30 | 0 | 121 | 0 | 8 | 225 | 0 | 0 | 0 |  | 0 | 32 | 34 | 33 | 0 | 40 | 9 | 36 | 0 | 0 | 0 | 295 | 285 | 150 | 8 | 0 | 41 | 0 | 0 | 51 | 0 | 38 | 16 | 19 | 11 | 33 | 12 | 122 | 31 | 0 | 0 | 0 | 39 | 39 | 22 | 47 | 80 | 0 | 40 | 20 | 0 | 172 | 0 | 0 | 10 | 295 | 8 | 11 | 0 | 15 | 0 | 0 | 68 | 0 | 17 | 0 | 25 | 51 | 5 | 303 | 19 | 17 | 17 | 1 | 69 | 17 | 31 | 17 | 9 | 38 | 220 | 74 | 10 | 17 | 17 | 0 | 27 | 3 | 72 | 17 | 271 | 36 | 0 | 0 | 5 |  | 911 | 0 | 235 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 170 | 20 | 0 | 0 | 0 | 0 | 27 | 12 | 27 | 28 | 0 | 35 | 0 | 0 | 21 | 0 | 8 | 70 | 0 | 250 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 27 | 0 | 0 | 0 | 27 | 35 | 232 | 0 | 373 | 20 | 150 | 895 | 38 | 0 |  | 5794 | 4390 | 10184 | 3841 | 911 | 1814 | 0 | 987 | 1738 | 30 | 392 | 241 | 122 | 103 | 5 | 0 | 72.5
16:00 | 0 | 0 | 110 | 180 | 0 | 0 | 0 | 270 | 235 |  | 0 | 300 | 275 | 32 | 17 | 0 | 60 | 0 | 119 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 20 | 15 | 17 | 33 | 8 | 0 | 30 | 0 | 117 | 0 | 8 | 225 | 0 | 0 | 0 |  | 0 | 32 | 34 | 33 | 0 | 40 | 9 | 36 | 0 | 0 | 0 | 280 | 275 | 150 | 8 | 0 | 42 | 0 | 0 | 51 | 0 | 43 | 16 | 19 | 11 | 33 | 14 | 112 | 32 | 0 | 0 | 0 | 42 | 39 | 22 | 47 | 80 | 0 | 40 | 20 | 0 | 175 | 0 | 0 | 10 | 300 | 16 | 11 | 0 | 15 | 0 | 0 | 68 | 0 | 17 | 4 | 25 | 51 | 6 | 303 | 19 | 17 | 17 | 1 | 69 | 17 | 39 | 17 | 9 | 38 | 220 | 74 | 6 | 17 | 0 | 0 | 17 | 4 | 72 | 17 | 283 | 18 | 0 | 0 | 11 |  | 910 | 0 | 235 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 172 | 19 | 0 | 0 | 0 | 0 | 27 | 32 | 27 | 28 | 0 | 21 | 0 | 0 | 22 | 0 | 8 | 71 | 0 | 250 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 27 | 0 | 0 | 0 | 44 | 35 | 232 | 0 | 378 | 13 | 150 | 897 | 27 | 0 |  | 5709 | 4405 | 10114 | 3855 | 910 | 1787 | 0 | 933 | 1746 | 30 | 392 | 234 | 112 | 104 | 11 | 0 | 72.5
17:00 | 0 | 0 | 110 | 180 | 0 | 0 | 0 | 270 | 245 |  | 0 | 300 | 291 | 9 | 17 | 0 | 60 | 0 | 127 | 17 | 8 | 0 | 9 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 20 | 15 | 17 | 33 | 8 | 0 | 30 | 0 | 118 | 0 | 0 | 222 | 0 | 0 | 0 |  | 0 | 32 | 34 | 10 | 0 | 23 | 9 | 42 | 0 | 0 | 0 | 280 | 275 | 150 | 8 | 0 | 40 | 0 | 0 | 51 | 0 | 46 | 16 | 19 | 11 | 33 | 14 | 116 | 33 | 0 | 0 | 0 | 43 | 39 | 22 | 48 | 80 | 0 | 40 | 20 | 0 | 175 | 0 | 0 | 9 | 285 | 16 | 11 | 0 | 15 | 0 | 0 | 68 | 0 | 17 | 2 | 25 | 51 | 13 | 303 | 19 | 17 | 17 | 0 | 15 | 17 | 50 | 17 | 9 | 12 | 220 | 48 | 4 | 17 | 5 | 0 | 17 | 4 | 72 | 17 | 296 | 18 | 0 | 0 | 4 |  | 910 | 0 | 235 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 172 | 19 | 0 | 0 | 0 | 0 | 27 | 32 | 24 | 28 | 0 | 21 | 0 | 0 | 22 | 0 | 8 | 70 | 0 | 250 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 375 | 7 | 150 | 906 | 21 | 0 |  | 5595 | 4308 | 9903 | 3874 | 910 | 1799 | 0 | 753 | 1751 | 30 | 391 | 234 | 116 | 41 | 4 | 0 | 72.51
18:00 | 0 | 0 | 110 | 180 | 0 | 0 | 0 | 270 | 245 |  | 0 | 300 | 304 | 8 | 17 | 10 | 60 | 0 | 127 | 9 | 8 | 0 | 11 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 20 | 6 | 0 | 33 | 8 | 0 | 25 | 0 | 117 | 0 | 0 | 222 | 0 | 0 | 0 |  | 0 | 40 | 34 | 10 | 0 | 19 | 9 | 42 | 0 | 0 | 0 | 280 | 275 | 151 | 8 | 0 | 43 | 0 | 0 | 51 | 0 | 43 | 8 | 19 | 11 | 33 | 14 | 116 | 32 | 0 | 0 | 0 | 43 | 39 | 25 | 10 | 80 | 0 | 40 | 10 | 0 | 179 | 0 | 0 | 10 | 275 | 16 | 11 | 0 | 15 | 0 | 0 | 45 | 0 | 17 | 0 | 25 | 54 | 41 | 303 | 19 | 17 | 17 | 0 | 15 | 17 | 17 | 17 | 25 | 12 | 225 | 35 | 2 | 17 | 18 | 0 | 17 | 1 | 91 | 17 | 252 | 18 | 0 | 0 | 4 |  | 908 | 0 | 200 | 0 | 0 | 160 | 0 | 0 | 20 | 26 | 0 | 152 | 20 | 0 | 0 | 0 | 0 | 27 | 32 | 34 | 28 | 0 | 32 | 0 | 0 | 22 | 0 | 8 | 72 | 0 | 250 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 292 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 1 | 0 | 231 | 0 | 376 | 2 | 150 | 905 | 9 | 0 |  | 5489 | 4265 | 9754 | 3760 | 908 | 1720 | 0 | 756 | 1753 | 25 | 391 | 306 | 116 | 15 | 4 | 0 | 72.51
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 110 | 180 | 0 | 0 | 0 | 284 | 340 |  | 0 | 300 | 306 | 9 | 17 | 30 | 140 | 0 | 127 | 9 | 16 | 48 | 11 | 0 | 0 | 0 | 17 | 55 | 35 | 0 | 20 | 15 | 17 | 33 | 8 | 0 | 25 | 0 | 119 | 0 | 1 | 225 | 0 | 0 | 0 |  | 0 | 62 | 34 | 33 | 0 | 19 | 11 | 42 | 0 | 0 | 0 | 280 | 275 | 204 | 8 | 0 | 43 | 0 | 0 | 51 | 0 | 41 | 12 | 19 | 11 | 33 | 14 | 140 | 44 | 0 | 0 | 0 | 43 | 39 | 50 | 40 | 80 | 0 | 58 | 74 | 0 | 180 | 0 | 0 | 10 | 290 | 16 | 11 | 0 | 16 | 0 | 0 | 58 | 0 | 74 | 0 | 63 | 72 | 75 | 352 | 85 | 30 | 23 | 0 | 100 | 17 | 25 | 52 | 35 | 12 | 258 | 41 | 0 | 108 | 62 | 0 | 17 | 0 | 115 | 22 | 271 | 18 | 0 | 0 | 3 |  | 908 | 0 | 225 | 0 | 31 | 160 | 0 | 0 | 20 | 30 | 16 | 174 | 28 | 16 | 0 | 0 | 0 | 27 | 32 | 84 | 28 | 8 | 36 | 0 | 30 | 22 | 0 | 8 | 72 | 0 | 250 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 292 | 0 | 0 | 3 | 30 | 34 | 0 | 0 | 25 | 0 | 55 | 0 | 18 | 0 | 0 | 35 | 100 | 0 | 376 | 0 | 150 | 912 | 0 | 0 |  | 6768 | 4515 | 11283 | 4119 | 908 | 1988 | 0 | 1618 | 1760 | 25 | 260 | 462 | 140 | 0 | 3 | 0 | 72.52
19:30 | 0 | 0 | 110 | 180 | 0 | 0 | 0 | 397 | 352 |  | 0 | 350 | 270 | 50 | 17 | 30 | 220 | 0 | 75 | 9 | 33 | 48 | 11 | 0 | 0 | 0 | 25 | 55 | 35 | 0 | 20 | 22 | 25 | 33 | 8 | 0 | 25 | 0 | 118 | 0 | 25 | 227 | 0 | 0 | 0 |  | 0 | 64 | 34 | 33 | 0 | 19 | 11 | 42 | 0 | 0 | 0 | 280 | 275 | 206 | 8 | 0 | 43 | 0 | 0 | 51 | 0 | 43 | 25 | 19 | 11 | 33 | 14 | 136 | 45 | 0 | 0 | 0 | 43 | 39 | 50 | 44 | 112 | 0 | 59 | 74 | 0 | 178 | 0 | 0 | 10 | 265 | 16 | 11 | 0 | 16 | 0 | 0 | 86 | 0 | 149 | 0 | 63 | 100 | 110 | 402 | 85 | 50 | 34 | 0 | 205 | 17 | 51 | 52 | 93 | 12 | 256 | 74 | 0 | 108 | 68 | 0 | 17 | 0 | 115 | 35 | 295 | 103 | 0 | 0 | 7 |  | 909 | 0 | 255 | 0 | 49 | 160 | 0 | 0 | 20 | 30 | 16 | 156 | 28 | 16 | 0 | 0 | 0 | 0 | 12 | 84 | 28 | 8 | 15 | 8 | 35 | 22 | 0 | 8 | 72 | 0 | 250 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 353 | 7 | 0 | 35 | 32 | 34 | 0 | 0 | 35 | 0 | 95 | 0 | 54 | 0 | 0 | 40 | 100 | 0 | 376 | 0 | 150 | 956 | 0 | 0 |  | 7666 | 4743 | 12409 | 4377 | 909 | 2126 | 0 | 2277 | 1804 | 25 | 260 | 488 | 136 | 0 | 7 | 0 | 0
20:00 | 0 | 0 | 110 | 180 | 0 | 0 | 0 | 393 | 352 |  | 0 | 350 | 290 | 44 | 17 | 30 | 218 | 0 | 105 | 9 | 33 | 32 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 20 | 26 | 25 | 33 | 8 | 0 | 25 | 0 | 120 | 0 | 8 | 225 | 0 | 0 | 0 |  | 0 | 33 | 34 | 33 | 0 | 19 | 11 | 42 | 0 | 0 | 0 | 285 | 275 | 204 | 8 | 0 | 43 | 0 | 0 | 51 | 0 | 46 | 52 | 19 | 11 | 33 | 14 | 140 | 48 | 0 | 0 | 0 | 43 | 39 | 50 | 47 | 112 | 0 | 58 | 74 | 0 | 180 | 0 | 0 | 10 | 265 | 16 | 11 | 0 | 16 | 0 | 0 | 86 | 0 | 132 | 0 | 63 | 100 | 105 | 403 | 85 | 60 | 51 | 0 | 205 | 17 | 51 | 17 | 93 | 12 | 260 | 68 | 0 | 108 | 68 | 0 | 17 | 0 | 109 | 35 | 296 | 163 | 0 | 0 | 3 |  | 908 | 0 | 265 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 174 | 29 | 32 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 35 | 22 | 0 | 8 | 72 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 395 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 0 | 110 | 0 | 17 | 0 | 0 | 72 | 50 | 0 | 376 | 0 | 150 | 994 | 0 | 0 |  | 7707 | 4535 | 12242 | 4455 | 908 | 2207 | 0 | 2101 | 1842 | 25 | 185 | 376 | 140 | 0 | 3 | 0 | 72.52
21:00 | 0 | 0 | 110 | 180 | 0 | 0 | 0 | 402 | 350 |  | 0 | 450 | 275 | 83 | 17 | 15 | 218 | 0 | 163 | 10 | 50 | 32 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 10 | 20 | 27 | 25 | 33 | 8 | 0 | 25 | 0 | 113 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 33 | 34 | 33 | 0 | 22 | 11 | 42 | 0 | 0 | 0 | 280 | 275 | 207 | 8 | 0 | 43 | 0 | 0 | 51 | 0 | 46 | 52 | 19 | 11 | 33 | 14 | 140 | 102 | 0 | 0 | 0 | 43 | 39 | 50 | 47 | 112 | 0 | 56 | 74 | 0 | 180 | 0 | 0 | 10 | 300 | 16 | 11 | 0 | 15 | 0 | 0 | 87 | 0 | 102 | 0 | 63 | 100 | 150 | 365 | 85 | 70 | 51 | 0 | 205 | 17 | 51 | 0 | 95 | 63 | 260 | 72 | 0 | 108 | 68 | 0 | 17 | 0 | 115 | 35 | 295 | 163 | 0 | 0 | 5 |  | 766 | 0 | 265 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 156 | 33 | 32 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 28 | 22 | 0 | 8 | 72 | 0 | 250 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 426 | 0 | 0 | 40 | 0 | 56 | 0 | 0 | 113 | 0 | 110 | 0 | 17 | 0 | 0 | 110 | 0 | 0 | 376 | 0 | 225 | 1052 | 0 | 0 |  | 8018 | 4681 | 12699 | 4594 | 766 | 2360 | 0 | 2352 | 1975 | 25 | 120 | 362 | 140 | 0 | 5 | 0 | 72.52
22:00 | 0 | 0 | 110 | 180 | 0 | 0 | 0 | 413 | 342 |  | 0 | 450 | 270 | 84 | 0 | 15 | 220 | 0 | 162 | 50 | 75 | 16 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 10 | 20 | 27 | 25 | 33 | 8 | 0 | 25 | 0 | 110 | 0 | 1 | 227 | 0 | 0 | 0 |  | 0 | 33 | 34 | 33 | 0 | 45 | 11 | 42 | 0 | 0 | 0 | 285 | 275 | 210 | 8 | 0 | 43 | 0 | 0 | 51 | 0 | 46 | 52 | 19 | 11 | 33 | 14 | 138 | 98 | 0 | 0 | 0 | 43 | 40 | 50 | 50 | 112 | 0 | 56 | 74 | 0 | 182 | 0 | 0 | 10 | 265 | 16 | 11 | 0 | 22 | 0 | 0 | 88 | 0 | 102 | 0 | 63 | 100 | 150 | 365 | 85 | 105 | 51 | 0 | 126 | 17 | 51 | 0 | 96 | 63 | 95 | 72 | 0 | 108 | 68 | 0 | 17 | 0 | 114 | 35 | 296 | 163 | 0 | 0 | 5 |  | 765 | 0 | 260 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 173 | 35 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 22 | 0 | 8 | 72 | 0 | 240 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 429 | 0 | 0 | 50 | 18 | 90 | 0 | 0 | 113 | 0 | 110 | 0 | 17 | 0 | 0 | 114 | 0 | 0 | 374 | 0 | 307 | 1056 | 0 | 0 |  | 7825 | 4837 | 12662 | 4485 | 765 | 2320 | 0 | 2435 | 2049 | 25 | 120 | 320 | 138 | 0 | 5 | 0 | 72.52
23:00 | 0 | 0 | 110 | 180 | 0 | 0 | 0 | 412 | 342 |  | 0 | 450 | 281 | 84 | 0 | 15 | 222 | 0 | 162 | 75 | 75 | 38 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 20 | 26 | 25 | 33 | 50 | 0 | 0 | 0 | 120 | 0 | 8 | 227 | 0 | 0 | 0 |  | 3 | 57 | 34 | 33 | 0 | 46 | 11 | 42 | 0 | 0 | 0 | 280 | 275 | 208 | 8 | 0 | 43 | 0 | 0 | 51 | 0 | 46 | 52 | 19 | 11 | 33 | 20 | 140 | 95 | 0 | 13 | 0 | 43 | 40 | 50 | 50 | 112 | 0 | 55 | 74 | 0 | 182 | 0 | 0 | 10 | 270 | 16 | 11 | 0 | 128 | 0 | 0 | 68 | 0 | 102 | 0 | 63 | 100 | 150 | 365 | 19 | 105 | 51 | 0 | 100 | 17 | 51 | 52 | 50 | 63 | 15 | 68 | 0 | 108 | 68 | 0 | 17 | 0 | 115 | 35 | 296 | 54 | 0 | 0 | 10 |  | 766 | 0 | 260 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 173 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 22 | 0 | 8 | 71 | 0 | 240 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 393 | 5 | 0 | 35 | 85 | 92 | 0 | 0 | 113 | 0 | 111 | 0 | 72 | 0 | 0 | 114 | 0 | 0 | 377 | 0 | 307 | 1057 | 0 | 0 |  | 7782 | 4908 | 12690 | 4437 | 766 | 2300 | 0 | 2608 | 2052 | 0 | 120 | 257 | 140 | 0 | 10 | 0 | 72.53
24:00 | 0 | 0 | 110 | 180 | 0 | 0 | 0 | 408 | 342 |  | 0 | 450 | 279 | 83 | 0 | 15 | 218 | 0 | 164 | 75 | 75 | 98 | 4 | 0 | 0 | 0 | 35 | 0 | 35 | 19 | 20 | 27 | 25 | 33 | 8 | 0 | 0 | 0 | 120 | 0 | 8 | 223 | 0 | 0 | 0 |  | 12 | 65 | 34 | 33 | 0 | 46 | 11 | 42 | 0 | 0 | 0 | 310 | 275 | 193 | 0 | 0 | 43 | 0 | 0 | 51 | 0 | 46 | 52 | 20 | 11 | 33 | 20 | 142 | 95 | 0 | 13 | 0 | 43 | 40 | 50 | 50 | 112 | 0 | 55 | 74 | 0 | 182 | 0 | 0 | 10 | 300 | 16 | 11 | 0 | 148 | 0 | 0 | 68 | 0 | 40 | 0 | 25 | 65 | 21 | 365 | 19 | 105 | 44 | 0 | 100 | 17 | 34 | 52 | 9 | 63 | 50 | 54 | 0 | 99 | 68 | 0 | 17 | 0 | 91 | 17 | 296 | 54 | 0 | 0 | 16 |  | 766 | 0 | 260 | 0 | 16 | 170 | 0 | 0 | 0 | 0 | 40 | 173 | 33 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 28 | 22 | 0 | 8 | 70 | 0 | 240 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 425 | 30 | 0 | 35 | 85 | 92 | 0 | 0 | 113 | 0 | 110 | 0 | 72 | 0 | 0 | 114 | 0 | 0 | 377 | 0 | 307 | 1057 | 0 | 0 |  | 7481 | 5087 | 12568 | 4482 | 766 | 2350 | 0 | 2266 | 2051 | 0 | 170 | 325 | 142 | 0 | 16 | 0 | 72.53
KWH | 0 | 0 | 2590094 | 4205250 | 0 | 0 | 0 | 8845310 | 7272000 |  | 0 | 9324000 | 6998022 | 1251840 | 175631 | 139256 | 1791283 | 0 | 4209 | 987840 | 442800 | 832320 | 46084 | 0 | 0 | 0 | 181080 | 463278 | 442011 | 231300 | 480000 | 508320 | 637200 | 782300 | 237120 | 0 | 331920 | 0 | 2800000 | 0 | 177076 | 5116021 | 0 | 0 | 0 |  | 161760 | 695088 | 934636 | 744240 | 0 | 492480 | 225120 | 915360 | 0 | 0 | 0 | 7494000 | 6929000 | 4069000 | 200727 | 0 | 1001448 | 0 | 0 | 1182806 | 0 | 1001840 | 653501 | 445316 | 244620 | 772900 | 392690 | 3091200 | 1221120 | 0 | 167868 | 3050 | 1016000 | 890040 | 1039800 | 1129248 | 2339100 | 0 | 1245600 | 1533120 | 0 | 3739080 | 0 | 0 | 251280 | 7090000 | 349800 | 261461 | 0 | 1109018 | 0 | 0 | 1660800 | 65127 | 8712000 | 43470 | 756480 | 1158720 | 807927 | 8368000 | 699600 | 2045760 | 604690 | 17398 | 2029855 | 446150 | 918323 | 498180 | 555240 | 720960 | 5449800 | 950400 | 115390 | 1152000 | 716345 | 0 | 659880 | 81523 | 1534080 | 508320 | 6097300 | 1042109 | 0 | 0 | 71280 |  | 21538909 | 0 | 5315904 | 0 | 256320 | 4374893 | 0 | 0 | 201120 | 368896 | 130500 | 4057723 | 652154 | 369024 | 0 | 0 | 0 | 513184 | 143317 | 968808 | 538340 | 364236 | 483300 | 4934 | 332280 | 487440 | 0 | 179748 | 1565673 | 0 | 5842200 | 0 | 0 | 4401145 | 0 | 0 | 0 | 0 | 0 | 4111455 | 0 | 8244872 | 618240 | 0 | 738336 | 777744 | 711523 | 0 | 50267 | 638688 | 0 | 1029355 | 0 | 516000 | 7560 | 357840 | 593088 | 4424447 | 0 | 8923636 | 111596 | 5236400 | 24174546 | 425880 | 0 |  | 160813989 | 114781521 | 275595510 | 96437425 | 21538909 | 49689284 | 65127 | 41097698 | 45742455 | 331920 | 8799340 | 7516898 | 3091200 | 1213974 | 71280 | 0
Fuel Cost | 0 | 0 | 3781537.24 | 6265822.5 | 0 | 0 | 0 | 9287575.5 | 7853760 |  | 0 | 10163160 | 7767804.42 | 13995571.2 | 2327110.75 | 1845142 | 2006236.96 | 0 | 7365.75 | 14442220.8 | 6230196 | 13491907.2 | 424894.48 | 0 | 0 | 0 | 2303337.6 | 6254253 | 5927367.51 | 173475 | 360000 | 0 | 0 | 0 | 4033411.2 | 0 | 89618.4 | 0 | 5292000 | 0 | 2895192.6 | 5320661.84 | 0 | 0 | 0 |  | 2110968 | 11594067.84 | 15907504.72 | 10054682.4 | 0 | 5697993.6 | 285902.4 | 3048148.8 | 0 | 0 | 0 | 8318340 | 7552610 | 4720040 | 258937.83 | 0 | 1131636.24 | 0 | 0 | 1975286.02 | 0 | 17301776.8 | 8789588.45 | 610082.92 | 183465 | 1352575 | 294517.5 | 22194816 | 1331020.8 | 0 | 228300.48 | 48617 | 1391920 | 1174852.8 | 1809252 | 1953599.04 | 2689965 | 0 | 2416464 | 3495513.6 | 0 | 3776470.8 | 0 | 0 | 497534.4 | 7090000 | 262350 | 198710.36 | 0 | 15138095.7 | 0 | 0 | 22387584 | 1346175.09 | 120661200 | 508164.3 | 7806873.6 | 15828115.2 | 10721191.29 | 7698560 | 8507136 | 29581689.6 | 7649328.5 | 0 | 23830497.7 | 4858573.5 | 9761773.49 | 6760302.6 | 7157043.6 | 8492908.8 | 5013816 | 12307680 | 1667385.5 | 14618880 | 8152006.1 | 0 | 8618032.8 | 974199.85 | 22965177.6 | 6694574.4 | 0 | 0 | 0 | 0 | 0 |  | 64616727 | 0 | 5953812.48 | 0 | 2668291.2 | 72185734.5 | 0 | 0 | 3622171.2 | 6640128 | 1875285 | 4544649.76 | 1265178.76 | 4022361.6 | 0 | 0 | 0 | 8606095.68 | 2506614.33 | 15152157.12 | 4145218 | 6031748.16 | 8172603 | 67250.42 | 5605563.6 | 1009000.8 | 0 | 136069.236 | 9096560.13 | 0 | 30905238 | 0 | 0 | 5105328.2 | 0 | 0 | 0 | 0 | 0 | 4769287.8 | 0 | 8162423.28 | 8309145.6 | 0 | 8734514.88 | 11238400.8 | 9036342.1 | 0 | 555450.35 | 7753672.32 | 0 | 1049942.1 | 0 | 3818400 | 85503.6 | 4197463.2 | 9092039.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 673994096.97 | 340736371.246 | 1014730468.216 | 100945456.566 | 64616727 | 60089506.05 | 1346175.09 | 536623263.19 | 40001798.13 | 89618.4 | 72185734.5 | 108600589.49 | 22194816 | 8036783.8 | 0 | 0
Yesterday Day Peak | 0 | 0 | 110 | 180 | 0 | 0 | 0 | 370 | 280 |  | 0 | 450 | 281 | 52 | 0 | 0 | 1 | 0 | 187 | 58 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 20 | 25 | 33 | 32 | 8 | 0 | 0 | 0 | 114 | 0 | 8 | 222 | 0 | 0 | 0 |  | 12 | 0 | 34 | 33 | 0 | 6 | 9 | 35 | 0 | 0 | 0 | 285 | 275 | 179 | 8 | 0 | 42 | 0 | 0 | 51 | 0 | 37 | 25 | 19 | 11 | 32 | 20 | 122 | 33 | 0 | 17 | 1 | 43 | 40 | 44 | 50 | 80 | 0 | 59 | 72 | 0 | 181 | 0 | 0 | 10 | 265 | 16 | 11 | 0 | 47 | 0 | 0 | 68 | 0 | 17 | 8 | 25 | 17 | 6 | 334 | 18 | 105 | 17 | 4 | 70 | 17 | 34 | 17 | 9 | 25 | 260 | 17 | 13 | 17 | 17 | 0 | 35 | 7 | 36 | 17 | 248 | 18 | 0 | 0 | 1 |  | 910 | 0 | 190 | 0 | 16 | 205 | 0 | 0 | 15 | 23 | 8 | 172 | 22 | 16 | 0 | 0 | 0 | 27 | 0 | 40 | 28 | 34 | 22 | 0 | 0 | 19 | 0 | 8 | 64 | 0 | 230 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 285 | 53 | 0 | 35 | 50 | 35 | 0 | 4 | 35 | 0 | 40 | 0 | 17 | 1 | 39 | 0 | 235 | 0 | 375 | 0 | 250 | 1082 | 8 | 0 |  | 11089 | DayPeak
Yesterday Evening Peak | 0 | 0 | 110 | 180 | 0 | 0 | 0 | 402 | 350 | 0 | 0 | 450 | 275 | 83 | 17 | 15 | 218 | 0 | 163 | 10 | 50 | 32 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 10 | 20 | 27 | 25 | 33 | 8 | 0 | 25 | 0 | 113 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 0 | 33 | 34 | 33 | 0 | 22 | 11 | 42 | 0 | 0 | 0 | 280 | 275 | 207 | 8 | 0 | 43 | 0 | 0 | 51 | 0 | 46 | 52 | 19 | 11 | 33 | 14 | 140 | 102 | 0 | 0 | 0 | 43 | 39 | 50 | 47 | 112 | 0 | 56 | 74 | 0 | 180 | 0 | 0 | 10 | 300 | 16 | 11 | 0 | 15 | 0 | 0 | 87 | 0 | 102 | 0 | 63 | 100 | 150 | 365 | 85 | 70 | 51 | 0 | 205 | 17 | 51 | 0 | 95 | 63 | 260 | 72 | 0 | 108 | 68 | 0 | 17 | 0 | 115 | 35 | 295 | 163 | 0 | 0 | 5 |  | 766 | 0 | 265 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 156 | 33 | 32 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 28 | 22 | 0 | 8 | 72 | 0 | 250 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 426 | 0 | 0 | 40 | 0 | 56 | 0 | 0 | 113 | 0 | 110 | 0 | 17 | 0 | 0 | 110 | 0 | 0 | 376 | 0 | 225 | 1052 | 0 | 0 |  | 12699 | EvPeak
Forecast for Evening | 0 | 0 | 110 | 180 | 0 | 0 | 0 | 400 | 330 | 0 | 0 | 450 | 280 | 100 | 17 | 25 | 218 | 0 | 100 | 75 | 74 | 150 | 11 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 20 | 28 | 25 | 33 | 50 | 0 | 25 | 0 | 120 | 0 | 25 | 225 |  | 0 | 0 | 0 | 12 | 73 | 51 | 33 | 0 | 50 | 11 | 25 | 0 | 0 | 0 | 310 | 300 | 200 | 8 | 0 | 40 | 0 | 0 | 51 | 0 | 45 | 52 | 20 | 11 | 33 | 20 | 152 | 102 | 0 | 18 | 0 | 43 | 40 | 50 | 50 | 112 | 0 | 56 | 76 | 0 | 195 | 0 | 0 | 10 | 310 | 16 | 11 | 0 | 145 | 300 | 0 | 86 | 100 | 149 | 0 | 63 | 100 | 150 | 400 | 86 | 105 | 51 | 0 | 300 | 17 | 74 | 114 | 98 | 63 | 200 | 72 | 0 | 162 | 68 | 0 | 35 |  | 95 | 35 | 295 | 163 |  | 0 |  |  | 929 | 0 | 250 |  | 49 | 205 | 0 | 0 | 30 | 70 | 40 | 170 | 33 | 48 | 0 | 0 | 0 | 28 | 30 | 90 | 28 | 34 | 36 | 52 | 35 | 22 | 0 | 8 | 72 | 0 | 250 | 16 | 0 | 190 |  | 0 | 0 | 0 | 0 | 170 | 0 | 400 | 70 | 0 | 57 | 85 | 49 | 0 | 0 | 56 | 0 | 110 |  | 150 |  |  | 115 | 220 |  | 370 |  | 307 | 1060 |  | 0
Forecast for Day | 0 | 0 | 110 | 180 | 0 | 0 | 0 | 400 | 330 | 0 | 0 | 450 | 280 | 50 | 17 | 0 | 218 | 0 | 100 | 75 | 50 | 82 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 19 | 20 | 28 | 25 | 33 | 8 | 0 | 25 | 0 | 120 | 0 | 8 | 225 |  | 0 | 0 | 0 | 12 | 55 | 51 | 33 | 0 | 50 | 11 | 10 | 0 | 0 | 0 | 300 | 300 | 200 | 8 | 0 | 40 | 0 | 0 | 51 | 0 | 45 | 26 | 20 | 11 | 33 | 20 | 129 | 30 | 0 | 18 | 1.6 | 43 | 40 | 50 | 50 | 112 | 0 | 56 | 76 | 0 | 195 | 0 | 0 | 10 | 300 | 16 | 11 | 0 | 45 | 300 | 0 | 68 | 100 | 17 | 20 | 25 | 51 | 12 | 400 | 18 | 105 | 51 | 5 | 70 | 17 | 51 | 17 | 9 | 25 | 50 | 72 | 50 | 35 | 34 | 0 | 17 | 30 | 72 | 17 | 270 | 72 |  | 0 | 5 |  | 929 | 0 | 230 | 0 | 16 | 170 | 0 | 0 | 20 | 60 | 8 | 170 | 21 | 16 | 0 | 0 | 0 | 28 | 30 | 40 | 28 | 25 | 36 | 0 | 35 | 22 | 0 | 8 | 72 | 0 | 230 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 380 | 54 | 0 | 35 | 50 | 35 | 0 | 8 | 35 | 0 | 110 |  | 17 | 6 | 100 | 35 | 0 |  | 370 | 30 | 307 | 1060 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 110 | 180 | 0 | 0 | 0 | 367 | 346 | 0 | 0 | 450 | 306 | 9 | 0 | 0 | 218 | 0 | 118 | 9 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 28 | 25 | 33 | 8 | 0 | 0 | 0 | 118 | 0 | 8 | 225 | 0 | 0 | 0 | 0 | 12 | 32 | 34 | 33 | 0 | 0 | 11 | 10 | 0 | 0 | 0 | 305 | 295 | 183 | 0 | 0 | 39 | 0 | 0 | 51 | 0 | 36 | 25 | 20 | 11 | 33 | 20 | 126 | 33 | 0 | 18 | 1 | 43 | 40 | 50 | 49 | 80 | 0 | 28 | 74 | 0 | 188 | 0 | 0 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 68 | 0 | 17 | 0 | 25 | 17 | 13 | 367 | 19 | 17 | 17 | 0 | 68 | 17 | 34 | 17 | 9 | 25 | 50 | 18 | 10 | 17 | 17 | 0 | 17 | 13 | 22 | 17 | 271 | 18 | 0 | 0 | 20 | 0 | 911 | 0 | 230 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 172 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 72 | 0 | 230 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 354 | 17 | 0 | 0 | 0 | 25 | 0 | 1 | 0 | 0 | 110 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 377 | 7 | 150 | 1067 | 12 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
292.3904
| Minimum Generation |  | 11089 | 9:00
| Highest Generation |  | 12699 | 21:00
| Day Peak Generation |  | 11089 | 9:00
| Evening Peak Generation |  | 12699 | 21:00
| HVDC Max Flow |  | 911 | 1:00
| HVDC EvPeak Flow |  | 766 | 21:00
| Load factor L.F |  | 90.43% | [163 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-06-10
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-06-09 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 11089 | MW Hour : | 9:00 | Min. Gen. at | 7:00 | 10176
Evening Peak Generation : |  |  | 12699 | MW Hour : | 21:00 | Available Max Generation : |  | 15281
E.P. Demand (at gen end) : |  |  | 12699 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14000
Maximum Generation : |  |  | 12699 | MW Hour : | 21:00 | Reserve(Generation end) |  | 1281
Total Gen. (MKWH) : |  |  | 275.5955 | System Load Factor : | 90.43% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 710 | MW at | 20:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-06-10
Actual : |  | 72.55 | Ft.(MSL) , | Rule curve : | 78.34 | Ft.( MSL )
Gas Consumed : |  | Total = | 1200.35 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 161034962.616
: |  |  | Coal : | 40001798.13 | Oil : | 718755762.27 | Total : | 919792523.016
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 5083.8668 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1400.0384 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1962.1165 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1706.2972 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1403.5387 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 1044.3414 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 584.8911 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 487.8885 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 954.2139 |  |  | 0 | 0%
Total |  | 0 |  | 14627.1926 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Bhula Nuton Biddut
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:27 | 15:20 | Sherpur 132/33kV S/S Transformer- 03 HT Scheduled S/D Due to Tr-04 X former loop connection
| 08:34 | Kulaura 132/33kV S/S TR-1 HT is restored.
| 08:35 | Kulaura 132/33kV S/S TR-1 LT is restored.
| 08:35 | Ishurdi 132/33kV S/S 132/33 kV T-2 LT is restored.
| 08:35 | Ishurdi 132/33kV S/S 132/33 kV T-2 HT is restored.
08:35 |  | Bhola Natun Biddut BD LTD ST was sync.
08:39 |  | Baghabari 230/132kV S/S Bus-1 Project Work S/D Due to Project Work Development (Ruppur Evacuation)
08:40 | 09:52 | Bhandaria 132/33kV S/S Transformer-1 LT Project Work S/D Due to G to G project work | [5 empty] | 6.0MW load interrup.
08:40 | 10:50 | Bhandaria 132/33kV S/S Transformer-1 HT Project Work S/D Due to G to G project work | [5 empty] | 6.0MW load interrup.
08:45 | 09:43 | Naogaon 132/33kV S/S T-2 LT Scheduled S/D Due to red hot maintenance | [5 empty] | 20.0MW load interrup.
08:46 |  | Shahmirpur 132/33kV S/S 406T LT Scheduled S/D Due to Tr-01 Incoming faulty GIS beaker maintenance
08:46 | 09:42 | Naogaon 132/33kV S/S T-2 HT Scheduled S/D Due to red hot maintenance | [5 empty] | 20.0MW load interrup.
08:47 |  | Shahmirpur 132/33kV S/S 406T HT Scheduled S/D Due to 33kv GIS Incoming 01 faulty breaker maintenance
| 08:57 | Gollamari 132/33kV S/S Tr-1 HT is restored.
| 08:59 | Gollamari 132/33kV S/S Tr-1 LT is restored.
09:55 |  | Gopalganj 400/132kV S/S 400kV Payra Ckt-1 Scheduled S/D
10:10 |  | Bhola Natun Biddut BD LTD ST tripped due to turbine bearing temperature high.
10:31 | 18:02 | Madanganj 132/33kV S/S Madanganj -Shitalakhya 132 kv Ckt Forced S/D Due to Overload
11:13 |  | Siddirganj CCPP 335MW ST was sync.
11:15 | 12:41 | Juldah 132/33kV S/S 133/33 KV T-2 416T HT Forced S/D Due to Testing purpose
11:18 | 12:46 | Juldah 132/33kV S/S 133/33 KV T-2 416T LT Forced S/D Due to Testing Purpose
| 11:24 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 HT is restored.
| 11:26 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 LT is restored.
11:58 | 12:08 | Aminbazar-Kallyanpur 132kV Ckt-1 Tripped from Aminbazar 400/230/132kV end showing 1. General Trip 2. Dist Trip
(R,S,T ph) relays Due to Strom and from Kallyanpur 132/33kV end showing General Trip, Distance R,S,T Trip (REL316*4)
relays Due to Due to Bad Weather.
| 11:59 | Ramganj 132/33kV S/S Transformer -02 LT is restored.
12:09 |  | Siddirganj CCPP 335MW ST tripped.
12:32 |  | Ghorashal 230/132 kv AT-2 was switched on.
12:40 | 13:39 | Tangail 132/33kV S/S Tr-2 LT Tripped showing REF615 relays Due to 33 kv Ghatail Feeder CB not operated | [5 empty] | 15.0MW load interrup.
12:40 | 13:40 | Tangail 132/33kV S/S Tr-1 LT Tripped showing REF615 relays Due to 33 kv Ghatail Feeder CB not operated | [5 empty] | 15.0MW load interrup.
13:54 | 14:34 | Monakasha-Rahanpur 400kV Ckt-1 Tripped from Rahanpur_I 400/132kV end showing Siemens siprotec7sA87 relays Due to | [5 empty] | 87.0MW load interrup.
|  | 21 Aided,92km | [5 empty] | Rahanpur_I 400/132kV end
15:53 |  | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-01 LT Project Work S/D Due to CSD 100 SAS Integration
15:54 |  | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-01 HT Project Work S/D Due to CSD-100 SAS Integration
18:04 |  | Bhola Natun Biddut BD LTD ST was sync.
21:00 |  | Evening Peak generation = 12,699MW
| 21:33 | Fatullah-Madanganj 132 kV Ckt-2 is restored.
00:23 |  | Shahjibazar GT9 tripped due to flame detector alarm.
00:58 | 01:10 | Joypurhat 132/33kV S/S Transformer T-4 (437 T) HT Tripped showing No relays Due to No
01:03 | 01:12 | Joypurhat 132/33kV S/S Transformer T-4 (437 T) LT Tripped showing No relays Due to No
01:20 |  | Joypurhat 132/33kV S/S Transformer T-4 (437 T) LT Forced S/D Due to 132kv circuit breaker closing problem
06:00 |  | Minimum generation: 10213 MW.
06:42 |  | Ramganj 132/33kV S/S Transformer -02 LT Scheduled S/D Due to Extended shutdown of the previous day working of PDB on | [5 empty] | 38.0MW load interrup.
their feeder bus DS.
07:20 |  | Bogura 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Junction point temperature reduce work. | [5 empty] | 12.0MW load interrup.
07:21 |  | Bogura 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Junction point temperature reduce work. | [5 empty] | 12.0MW load interrup.
07:23 |  | Halishahar 132/33kV S/S 413T(TR-2) HT Tripped showing Over Current Relay relays Due to Due to baraka potenga trip | [5 empty] | 23.0MW load interrup.
07:23 |  | Halishahar 132/33kV S/S 413T(TR-2) LT Tripped showing Over Current Relay relays Due to Due to baraka potenga trip | [5 empty] | 23.0MW load interrup.
07:27 |  | Fatullah-Madanganj 132 kV Ckt-2 Scheduled S/D from Fatullah 132/33kV end Due to Due to change damage Disc Insulator in
Tower. Shutdown is taken by Madanganj.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-06-09 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 110 | 2590094 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4205250
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 402 | 8845310
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 350 | 7272000 | Bad weather
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9324000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 83 | 1251840 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 275 | 6998022 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 17 | 175631
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 139256 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 20 | 0 | 46084
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 10 | 231300 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 163 | 4209 | Machine problem
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 10 | 987840 | Bad weather
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 218 | 1791283 | ST Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 50 | 442800 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 181080 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 832320 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 463278
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 442011 | Fuel shortage
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 47 | 988320 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 637200 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 782300
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 237120 | low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 15 | 1109018 | low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 65127 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 102 | 8712000 | low demand
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 2045760 | low demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 72 | 950400 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 1152000 | low demand
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 81523
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 508320 | Fuel shortage
| Dhaka area Total |  |  |  | 5867 | 3005 | 63492696
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 113 | 2800000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 177076 | Reserve
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 43470
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 22 | 492480 | low demand
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 25 | 331920 | Low Water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 226 | 5116021
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 604690 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 33 | 695088 | low demand
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 934636 | low demand
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 33 | 744240 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 63 | 756480 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 11 | 225120 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 915360
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 17398
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 205 | 2029855 | low demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 446150 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 51 | 918323 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 63 | 720960 | low demand
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 68 | 716345 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 163 | 1042109
| SS Power I |  | SS Power | 0 | 0 | 0 | 0 | On test.
| Cox's Bazar Wind |  | IPP | 66 | 0 | 5 | 71280 | On test.
| Chattogram area Total |  |  |  | 2545 | 1225 | 19799001
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 207 | 4069000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7494000 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 275 | 6929000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 295 | 6097300 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 43 | 1001448
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1182806
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 150 | 807927
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 46 | 1001840
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 100 | 1158720 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 445316
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 244620
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 140 | 3091200
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 772900
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 653501
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 14 | 392690 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 498180 | low demand
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 95 | 555240 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 659880 | low demand
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1534080
| Cumilla Area Total |  |  |  | 3096 | 1951 | 38790375
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 102 | 1221120 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 167868 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 3050
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 87 | 1660800 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 85 | 699600 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 115390
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 161760 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 274 | 4029588
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1016000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 39 | 890040 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2339100 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1039800
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 47 | 1129248
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 261461
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 56 | 1245600
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 74 | 1533120
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 180 | 3739080 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 349800 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7090000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 365 | 8368000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 251280
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 260 | 5449800 | ST Under maint.
| Sylhet Area Total |  |  |  | 2427 | 1563 | 34702329
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 766 | 21538909
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 256320 | low demand
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 201120 | low demand
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 120 | 4374893 | low demand
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 368896 | Reserve
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 265 | 5315904 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 130500 | Reserve
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 618240 | low demand
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 777744 | low demand
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 357840
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 4424447 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 376 | 8923636 | Coal shortage.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 2901 | 1527 | 47288449
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 369024
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 33 | 652154
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 156 | 4057723 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 0 | 0 | Coal shortage.
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 110 | 1029355 | Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 516000 | low demand
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 225 | 5236400 | Engine problem
| Barisal Area Total |  |  |  | 2265 | 573 | 11860656
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 513184 | Reserve
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 143317 | Reserve
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 28 | 0 | 538340 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 364236 | Reserve
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 483300 | Reserve
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 202 | 4401145 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 176 | 4111455 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 426 | 8244872
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 332280 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 487440
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 179748 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 4934 | Reserve
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 26 | 968808 | low demand
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 40 | 738336 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 638688
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 7560
| Adani Power Jharkhanda Ltd |  | Import | 748*1 | 748 | 1052 | 24174546
| Rajshahi Area Total |  |  |  | 2905 | 2093 | 46332189
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 72 | 1565673
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 250 | 5842200
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 56 | 711523 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 50267
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 110 | 593088
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 111596
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 425880
| Rangpur Area Total |  |  |  | 750 | 488 | 9300227
| Total |  |  |  | 23370 | 12699 | 275595510
| Eastern Grid Total |  |  |  | 14549 | 8018 | 160813989
| Western Grid Total |  |  |  | 8821 | 4681 | 114781521
| National Grid Total |  |  |  | 23370 | 12699 | 275595510
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-06-09
| (a) ENTIRE EASTERN GRID : |  | 8077.17 | MW | (b) ENTIRE WESTERN GRID : |  | 4020.6 | MW
| i) Dhaka area |  | 4102.67 | MW | i) Khulna area |  | 1372.4 | MW
| ii) Chittagong area |  | 1185.5 | MW | ii) Rajshahi area |  | 1343.2 | MW
| iii) Comilla area |  | 1254 | MW | iii) Barisal area |  | 408 | MW
| iv) Mymensingh area |  | 968 | MW | iv) Rangpur area |  | 897 | MW
| v) Sylhet area |  | 567 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 12097.77 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 35 | 22:00 | Kalurghat | 28 | 12:00 | Narshingdi | 158 | 00:00 | Shikalbaha-230 | N/A | N/A
2 | AKSML | 6 | 05:00 | Chowmuhani | 212 | 19:30 | Kamrangirchar | 63 | 11:00 | Natore | 141 | 19:30 | Shitalakhya | 82.2 | 00:00
3 | Aftabnagar | 50 | 00:00 | Chuadanga | 113 | 14:00 | Kaptai | N/A | N/A | Nawabganj | 41.9 | 00:00 | Sholosohor | 31 | 12:00
4 | Agargaon | 83 | 00:00 | Coxsbazar | 107 | 23:00 | Kazla | 94 | 00:00 | Netrakona | 129 | 20:00 | Shyampur | 160 | 00:00
5 | Agrabad | 52 | 12:00 | Cumilla(N) | 157 | 21:00 | Keranigonj | 64 | 00:00 | New | 76 | 00:00 | Siddhirganj | 106 | 00:00
6 | Amnura | 60 | 00:00 | Cumilla(S) | 162 | 00:00 | Khagrachori | 32 | 19:00 | Niamatpur | 85 | 21:00 | Sirajganj | 92 | 21:00
7 | Ashuganj | 67 | 23:00 | Daudkandi | 133 | 21:00 | Khulna | 99 | 13:00 | Noapara | 37 | 13:00 | Sonargaon | 62 | 09:00
8 | BIPTC | N/A | N/A | Dhaka | 14 | 10:00 | Khulshi | 166 | 19:30 | PHP | 9 | 10:00 | Sreemongol | 63 | 19:30
9 | BSRM | 120 | 20:00 | Dhamrai | 106 | 00:00 | Kishoreganj | 138 | 22:00 | Pabna | 106 | 20:00 | Sreepur | 56 | 00:00
10 | Bagerhat | 79 | 21:00 | Dhanmondi | 99 | 11:00 | Kodda | 276 | 00:00 | Palashbari | 118 | 00:00 | Srinagar | 40.78 | 00:00
11 | Bakulia | 84 | 21:00 | Dohazari | 90 | 19:00 | Kulaura | 46 | 20:00 | Panchagarh | 60 | 20:00 | Sunamganj | 54 | 19:30
12 | Banani | 44 | 11:00 | Dummy | N/A | N/A | Kurigram | 60 | 21:00 | Patuakhali | 104 | 23:00 | Sylhet | 164 | 00:00
13 | Bangabhaban | 5 | 00:00 | Faridpur | 123 | 13:00 | Kushtia | 152 | 12:00 | Payra | 18 | 19:00 | TK | 30 | 19:30
14 | Barapukuria | 57 | 21:00 | Fatullah | 63 | 00:00 | Lalbag | 84 | 00:00 | Postogola | 58 | 00:00 | Tangail | 171 | 10:00
15 | Barguna | 18 | 19:00 | Fenchuganj | 49 | 19:30 | Lalmonirhat | 45 | 22:00 | Purbachal | 20 | 00:00 | Thakurgaon | 97 | 23:00
16 | Barishal | 93 | 21:00 | Feni | 107 | 22:00 | Madanganj | 44 | 13:00 | Purbasadipur | 143 | 22:00 | Tongi | 102 | 09:00
17 | Barishal-230 | 84 | 21:00 | GPH | 88 | 00:00 | Madaripur | 92 | 22:00 | Rahanpur_I | 0 | 00:00 | Ullon | 42 | 00:00
18 | Baroaulia | 81 | 00:00 | Ghorashal | N/A | N/A | Madartek | 89.98 | 00:00 | Rahim | 41 | 09:00 | Uttara | 60 | 00:00
19 | Baroirhat | 53 | 21:00 | Goalpara | 36 | 13:00 | Madunaghat | 47 | 19:00 | Rajbari | 56 | 21:00 | UttaraNew | 51 | 00:00
20 | Bashundhara | 161 | 00:00 | Gollamari | 54 | 00:00 | Magura | 56 | 13:00 | Rajendrapur | 86 | 00:00 | Zigatola | 77 | 11:00
21 | BashundharaCement | 0 | 00:00 | Gopalganj | 82.4 | 19:30 | Mahasthangarh | 62 | 03:00 | Rajshahi | 162 | 13:00
22 | Beanibazar | 72 | 22:00 | Gulshan | 52 | 12:00 | Manikganj | 93 | 21:00 | Rajshahi-230 | 56 | 15:00
23 | Benapole | 58 | 13:00 | Halishahar | 67.5 | 19:30 | Maniknagar | 74 | 00:00 | Ramganj | 106 | 22:00
24 | Bhaluka | 128 | 22:00 | HaripurSBU | 157 | 01:00 | Matarbari | 42 | 20:00 | Rampur | 39 | 00:00
25 | Bhandaria | 46 | 19:00 | Hasnabad | 92 | 00:00 | Matuail | 62 | 00:00 | Rangamati | 16 | 19:00
26 | Bhangura | 38 | 20:00 | Hathazari | 71 | 22:00 | Millgate | 90 | 00:00 | Rangpur | 131 | 19:30
27 | Bheramara(GK) | 57 | 11:00 | Ishurdi | 60 | 12:00 | Mirpur | 146 | 11:00 | Ruppur | 4.8 | 09:00
28 | Bhulta | 272 | 00:00 | Jaldhaka | 75 | 22:00 | Mirsorai | 4 | 00:00 | SSM | 4 | 12:00
29 | Bog-Sherpur | 58 | 19:30 | Jamalpur | 135 | 22:00 | Mithapukur | 34 | 20:00 | Saidpur | 102 | 21:00
30 | Bogura | 151 | 21:00 | Jashore | 139 | 13:00 | Modern | 0 | 00:00 | Satkhira | 125 | 13:00
31 | Borhanuddin | 57 | 22:00 | Jhenaidah | 121 | 13:00 | Mogbazar | 110.1 | 11:00 | Satmasjid | 88 | 00:00
32 | Brahmanbaria | 165 | 21:00 | Joydebpur | 159 | 00:00 | Mongla | 32 | 11:00 | Savar | 178 | 11:00
33 | Cantonment | 132 | 00:00 | Joypurhat | 56 | 22:00 | Motijheel | 37 | 00:00 | Shahjadpur | 82 | 11:00
34 | Chandpur | 64 | 21:00 | Juldah | 22 | 23:00 | Munshiganj | 101 | 00:00 | Shahjibazar | 123 | 22:00
35 | Chandraghona | 29 | 19:00 | KSRM | 15 | 03:00 | Mymensingh | 197 | 03:00 | Shahmirpur | 41 | 02:00
36 | Chapai | 77 | 00:00 | Kabirpur | 276 | 00:00 | Naogaon | 135 | 21:00 | Shariatpur | 69 | 22:00
37 | Charsaidpur | 43 | 01:00 | Kachua | 68 | 21:00 | Narail | 50 | 13:00 | Sherpur | 128 | 19:30
38 | Chauddagram | 54 | 20:00 | Kallyanpur | 120 | 00:00 | Narinda | 54 | 00:00 | Shikalbaha | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-06-09 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 398 | 19:30 | 385 | 10:00 | Kaliakoir | 394 | 14:00 | 376 | 09:00
| Ashuganj | N/A | N/A | N/A | N/A | Madunaghat_I | 402 | 19:00 | 390 | 17:00
| Bhulta | 395 | 19:30 | 385 | 01:00 | Payra | 414 | 18:30 | 405 | 00:00
| Bibiana | 405 | 14:00 | 394 | 01:00 | Rahanpur_I | 416 | 13:00 | 408 | 04:00
| BIPTC | 405 | 21:00 | 393 | 01:00 | Rampal | 406 | 18:30 | 397 | 03:00
| Gopalganj | 405 | 19:30 | 395 | 10:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 232 | 14:00 | 225 | 01:00 | Hasnabad | 233 | 19:30 | 224 | 01:00
| AKSML | 233 | 00:00 | 209 | 09:00 | Hathazari | 236 | 20:00 | 224 | 17:00
| Aminbazar | 235 | 18:00 | 228 | 00:00 | Ishurdi | 233 | 00:00 | 226 | 12:00
| Ashuganj | 234 | 22:00 | 227 | 01:00 | Jhenaidah | 228 | 16:00 | 218 | 12:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 231 | 14:00 | 221 | 09:00
| Baghabari | 228 | 00:00 | 222 | 09:00 | Keranigonj | 232 | 14:00 | 224 | 01:00
| Barapukuria | 219 | 10:00 | 208 | 19:30 | Khulna(S) | 235 | 00:00 | 230 | 11:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | 231 | 07:00 | 224 | 11:00
| Barishal | 235 | 07:00 | 232 | 21:00 | Maniknagar | 231 | 14:00 | 225 | 09:00
| Bheramara | 232 | 00:00 | 224 | 10:00 | Meghnaghat | 236 | 13:00 | 230 | 00:00
| Bhulta | 234 | 14:00 | 226 | 01:00 | Mirsorai | 239 | 19:30 | 221 | 02:00
| Bibiana | 240 | 12:00 | 235 | 01:00 | Rajshahi | 233 | 00:00 | 222 | 13:00
| BIPTC | 233 | 00:00 | 223 | 10:00 | Rampal | 234 | 19:30 | 227.73 | 12:00
| Bogura | 217 | 11:00 | 209 | 07:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 238 | 10:00 | 230 | 01:00 | Rampura | 232 | 13:00 | 226 | 09:00
| BSRM | 237 | 21:00 | 222 | 09:00 | Shikalbaha | 235 | 21:00 | 224 | 10:00
| Cumilla(N) | 232 | 19:30 | 224 | 01:00 | Shyampur | 232 | 14:00 | 224 | 01:00
| Fenchuganj | 243 | 21:00 | 237 | 01:00 | Siddhirganj | 233 | 14:00 | 227 | 01:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 233 | 00:00 | 230 | 04:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 231 | 13:00 | 220 | 23:00
| GPH | 235 | 21:00 | 222 | 17:00 | Tongi | 228 | 14:00 | 220 | 01:00
| Haripur | 231 | 13:00 | 226 | 07:00
| 132 kV | KV |  | KV |  | Tongi | KV |  | KV
| Aftabnagar | 138 | 11:00 | 134 | 01:00 | Kushtia | 134 | 00:00 | 127 | 12:00
| Agargaon | 139 | 19:30 | 134 | 01:00 | Lalbag | 135 | 12:00 | 129 | 01:00
| Agrabad | 136 | 21:00 | 128 | 08:00 | Lalmonirhat | 131 | 09:00 | 117 | 19:30
| AKS | 134 | 00:00 | 127 | 01:00 | Madanganj | 136 | 12:00 | 131 | 00:00
| Aminbazar | 135 | 18:00 | 128 | 00:00 | Madaripur | 130 | 19:00 | 127 | 21:00
| Amnura | 138 | 01:00 | 127 | 00:00 | Madartek | 138 | 13:00 | 134 | 02:00
| Ashuganj | 137 | 14:00 | 125 | 04:00 | Madunaghat | 138 | 20:00 | 129 | 17:00
| Bagerhat | 135 | 00:00 | 128 | 21:00 | Magura | 138 | 16:00 | 125 | 12:00
| Bakulia | 136 | 00:00 | 128 | 12:00 | Mahasthangarh | 131 | 11:00 | 123 | 07:00
| Banani | 139 | 14:00 | 134 | 01:00 | Manikganj | 138 | 14:00 | 125 | 00:00
| Bangabhaban | 135 | 19:30 | 130 | 09:00 | Maniknagar | 135 | 14:00 | 130 | 01:00
| Barapukuria | 135 | 10:00 | 126 | 19:30 | Matarbari | 128 | 02:00 | 114 | 13:00
| Barguna | 137 | 18:30 | 131 | 04:00 | Matuail | 136 | 13:00 | 131.2 | 02:00
| Barishal | 136 | 18:30 | 126 | 01:00 | Millgate | 135 | 14:00 | 127 | 08:00
| Barishal-230 | 131 | 16:00 | 128 | 15:00 | Mirpur | 133 | 19:00 | 125 | 10:00
| Baroaulia | 136 | 00:00 | 129 | 01:00 | Mithapukur | 131 | 11:00 | 120 | 19:30
| Baroirhat | 132 | 10:00 | 124 | 13:00 | Modern | 135 | 00:00 | 129 | 09:00
| Bashundhara | 139 | 14:00 | 126 | 09:00 | Mogbazar | 140 | 13:00 | 135 | 01:00
| BashundharaCement | 136 | 12:00 | 131 | 00:00 | Mongla | 134 | 17:00 | 128 | 21:00
| Beanibazar | 131 | 11:00 | 126 | 22:00 | Motijheel | 135 | 19:30 | 130 | 09:00
| Benapole | 134 | 17:00 | 124 | 12:00 | Munshiganj | 135 | 12:00 | 130 | 01:00
| Bhaluka | 129 | 13:00 | 121 | 01:00 | Mymensingh | 140 | 13:00 | 115 | 03:00
| Bhandaria | 134 | 11:00 | 124 | 22:00 | Naogaon | 126 | 00:00 | 116 | 06:00
| Bhangura | 136 | 00:00 | 131 | 10:00 | Narail | 139 | 16:00 | 123 | 12:00
| Bheramara | 134 | 00:00 | 130 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara(GK) | 134 | 00:00 | 131 | 09:00 | Narshingdi | 132 | 12:00 | 125 | 00:00
| Bhulta | 128 | 14:00 | 121 | 00:00 | Natore | 131 | 00:00 | 125 | 20:00
| Bog-Sherpur | 132 | 11:00 | 126 | 06:00 | Nawabganj | 134 | 14:00 | 128 | 02:00
| Bogura | 133 | 11:00 | 126 | 04:00 | Netrakona | 137 | 14:00 | 118 | 22:00
| Bogura-230 | 131 | 00:00 | 124 | 06:00 | New | 134 | 13:00 | 128 | 00:00
| Brahmanbaria | 131 | 06:00 | 129 | 00:00 | Niamatpur | 125 | 00:00 | 113 | 06:00
| Cantonment | 138 | 14:00 | 132 | 01:00 | Noapara | 136 | 00:00 | 129 | 12:00
| Chandpur | 134 | 12:00 | 117 | 01:00 | Pabna | 133 | 00:00 | 129 | 06:00
| Chandraghona | 136 | 00:00 | 129 | 09:00 | Palashbari | 130 | 09:00 | 117 | 20:00
| Chapai | 135 | 13:00 | 129 | 00:00 | Panchagarh | 130 | 23:00 | 112 | 19:30
| Charsaidpur | 137 | 19:30 | 130 | 02:00 | Patuakhali | 137 | 18:30 | 133 | 01:00
| Chauddagram | 133 | 19:00 | 124 | 01:00 | Payra | 139 | 18:30 | 135 | 04:00
| Chhatak | 131 | 04:00 | 126 | 22:00 | PHP | 131 | 19:30 | 121 | 01:00
| Chowmuhani | 131 | 11:00 | 117 | 01:00 | Postogola | 139 | 12:00 | 132 | 09:00
| Chuadanga | 136 | 16:00 | 116 | 12:00 | Purbachal | 139 | 12:00 | 125 | 10:00
| Coxsbazar | 129 | 00:00 | 118 | 13:00 | Purbasadipur | 127 | 11:00 | 116 | 20:00
| Cumilla(N) | 136 | 19:30 | 129 | 01:00 | Rahim | 136 | 12:00 | 132 | 00:00
| Cumilla(S) | 134 | 11:00 | 127 | 19:30 | Rajbari | 129 | 00:00 | 124 | 12:00
| Daudkandi | 134 | 11:00 | 128 | 01:00 | Rajendrapur | 139 | 14:00 | 125 | 04:00
| Dhaka | 139 | 14:00 | 135 | 01:00 | Rajshahi | 133 | 00:00 | 125 | 20:00
| Dhamrai | 137 | 14:00 | 128 | 09:00 | Rajshahi-230 | 132 | 00:00 | 125 | 20:00
| Dhanmondi | 136 | 12:00 | 132 | 01:00 | Ramganj | 131 | 11:00 | 116 | 02:00
| Dohazari | 134 | 20:00 | 125 | 13:00 | Rampur | 133 | 00:00 | 129 | 02:00
| Dummy | N/A | N/A | N/A | N/A | Rampura | 138 | 13:00 | 135 | 00:00
| Faridpur | 129 | 00:00 | 125 | 12:00 | Rangamati | 135 | 21:00 | 128 | 13:00
| Fatullah | 134 | 14:00 | 128 | 01:00 | Rangpur | 131 | 11:00 | 116 | 19:30
| Fenchuganj | 136 | 00:00 | 134 | 02:00 | Ruppur | 134 | 00:00 | 131 | 10:00
| Feni | 131 | 11:00 | 122 | 06:00 | Saidpur | 130 | 09:00 | 117 | 20:00
| Ghorashal | N/A | N/A | N/A | N/A | Satkhira | 136 | 18:30 | 125 | 13:00
| Goalpara | 137 | 00:00 | 133 | 12:00 | Satmasjid | 138 | 14:00 | 133 | 01:00
| Gollamari | 136 | 19:00 | 132 | 10:00 | Savar | 134 | 13:00 | 124 | 10:00
| Gopalganj | 133 | 00:00 | 127 | 12:00 | Shahjadpur | 138 | 18:00 | 134 | 07:00
| Gopalganj-400 | 159 | 18:30 | 126 | 10:00 | Shahjibazar | 133 | 00:00 | 130 | 15:00
| Gulshan | 137 | 12:00 | 134 | 01:00 | Shahmirpur | 136 | 20:00 | 129 | 17:00
| Halishahar | 137 | 21:00 | 128 | 16:00 | Shariatpur | 128 | 00:00 | 125 | 22:00
| Haripur | 136 | 12:00 | 132 | 00:00 | Sherpur | 139 | 12:00 | 110 | 18:00
| HaripurSBU | 136 | 12:00 | 132 | 00:00 | Shikalbaha | N/A | N/A | N/A | N/A
| Hasnabad | 139 | 13:00 | 133 | 09:00 | Shikalbaha-230 | 136 | 21:00 | 129 | 13:00
| Hathazari | 138 | 00:00 | 131 | 08:00 | Shitalakhya | 138 | 14:00 | 129 | 00:00
| Ishurdi | 135 | 00:00 | 131 | 07:00 | Sholosohor | 135 | 00:00 | 128 | 13:00
| Jaldhaka | 130 | 11:00 | 114 | 19:30 | Shyampur | 134 | 19:30 | 128 | 10:00
| Jamalpur | 139 | 12:00 | 115 | 18:00 | Shyampur-230 | 134 | 14:00 | 129 | 01:00
| Jashore | 134 | 00:00 | 125 | 12:00 | Siddhirganj | 137 | 19:30 | 132 | 00:00
| Jhenaidah | 137 | 00:00 | 127 | 12:00 | Sirajganj | 134 | 21:00 | 127 | 06:00
| Jhenaidah-230 | 137 | 16:00 | 128 | 12:00 | Sonargaon | 136 | 12:00 | 130 | 00:00
| Joydebpur | 140 | 14:00 | 133 | 07:00 | Sreemongol | 132 | 00:00 | 130 | 19:30
| Joypurhat | 125 | 11:00 | 113 | 04:00 | Sreepur | 130 | 13:00 | 125 | 02:00
| Juldah | 137 | 21:00 | 130 | 01:00 | Srinagar | 135 | 19:30 | 128 | 10:00
| Kabirpur | 140 | 14:00 | 125 | 01:00 | SSM | 138 | 00:00 | 129 | 16:00
| Kachua | 135 | 19:30 | 121 | 03:00 | Sunamganj | 129 | 08:00 | 120 | 22:00
| Kaliakoir | 139 | 14:00 | 134 | 01:00 | Sylhet | 132 | 00:00 | 130 | 20:00
| Kallyanpur | 129 | 14:00 | 124 | 01:00 | Tangail | 140 | 13:00 | 123 | 18:00
| Kalurghat | 136 | 00:00 | 129 | 13:00 | Thakurgaon | 127 | 23:00 | 110 | 19:30
| Kamrangirchar | 135 | 14:00 | 122 | 01:00 | TK | 137 | 21:00 | 129 | 17:00
| Kaptai | N/A | N/A | N/A | N/A | Tongi | 136 | 14:00 | 130 | 01:00
| Kazla | 134 | 19:30 | 127 | 00:00 | Ullon | 138 | 12:00 | 134 | 01:00
| Keranigonj | 134 | 14:00 | 129 | 09:00 | Uttara | 133 | 13:00 | 126 | 09:00
| Khagrachori | 135 | 00:00 | 127 | 09:00 | UttaraNew | 134 | 13:00 | 125 | 10:00
| Khulna | 136 | 00:00 | 132 | 10:00 | Zigatola | 135 | 14:00 | 129 | 02:00
| Khulna(S) | 137 | 18:30 | 132 | 11:00
| Khulshi | 134 | 00:00 | 127 | 09:00
| Kishoreganj | 130 | 13:00 | 123 | 23:00
| Kodda | 138 | 14:00 | 126 | 03:00
| KSRM | 136 | 19:30 | 128 | 09:00
| Kulaura | 135 | 07:00 | 133 | 01:00
| Kurigram | 131 | 09:00 | 114 | 19:30

## L-Curve
Date | 2023-06-09
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1088 | 7481 | 5087 | 12568 |  |  |  | QF-LDC-11
0:30 | 1154 | 7041 | 5082.5 | 12123.5 | Date: | 2023-06-09
1:00 | 1220 | 6601 | 5078 | 11679
1:30 | 1230 | 6509.5 | 5070.5 | 11580
2:00 | 1240 | 6418 | 5063 | 11481
2:30 | 1220 | 6427.5 | 5042.5 | 11470 | [5 empty] | Gen. at Eve. Peak | 12699 | 12699 MW (21:00 )
3:00 | 1200 | 6437 | 5022 | 11459 | [6 empty] | 21:00
3:30 | 1198 | 6438.5 | 5007 | 11445.5 | [5 empty] | Gen. at Day Peak | 11089 | 11089 MW (09:00 )
4:00 | 1196 | 6440 | 4992 | 11432 | [6 empty] | 9:00
4:30 | 1206 | 6435.5 | 4982 | 11417.5 | [5 empty] | Highest Generation | 12699
5:00 | 1216 | 6431 | 4972 | 11403 | [6 empty] | 21:00
5:30 | 1213 | 6385.5 | 4951 | 11336.5
6:00 | 1210 | 6340 | 4930 | 11270
6:30 | 1198 | 6311 | 4920 | 11231
7:00 | 1186 | 6282 | 4910 | 11192
7:30 | 1271 | 6253.5 | 4936 | 11189.5
8:00 | 1356 | 6225 | 4962 | 11187
8:30 | 1388 | 6196 | 4942 | 11138
9:00 | 1420 | 6167 | 4922 | 11089
9:30 | 1395 | 6216.5 | 4837 | 11053.5
10:00 | 1370 | 6266 | 4752 | 11018
10:30 | 1321 | 6394.5 | 4653.5 | 11048
11:00 | 1272 | 6523 | 4555 | 11078
11:30 | 1206 | 6509 | 4542 | 11051
12:00 | 1140 | 6495 | 4529 | 11024
12:30 | 1060 | 6546.5 | 4534 | 11080.5
13:00 | 980 | 6598 | 4539 | 11137
13:30 | 1040 | 6126 | 4446 | 10572
14:00 | 1100 | 5654 | 4353 | 10007
14:30 | 1227 | 5724 | 4371.5 | 10095.5
15:00 | 1354 | 5794 | 4390 | 10184
15:30 | 1394 | 5751.5 | 4397.5 | 10149
16:00 | 1434 | 5709 | 4405 | 10114
16:30 | 1452 | 5652 | 4356.5 | 10008.5
17:00 | 1470 | 5595 | 4308 | 9903
17:30 | 1415 | 5542 | 4286.5 | 9828.5
18:00 | 1360 | 5489 | 4265 | 9754
18:30 | 1170 | 6128.5 | 4390 | 10518.5
19:00 | 980 | 6768 | 4515 | 11283
19:30 | 726 | 7666 | 4743 | 12409
20:00 | 710 | 7707 | 4535 | 12242 |  |  |  | Executive Engineer
20:30 | 720 | 7862.5 | 4608 | 12470.5 |  |  |  | Network Operation Division
21:00 | 730 | 8018 | 4681 | 12699
21:30 | 753 | 7921.5 | 4759 | 12680.5
22:00 | 776 | 7825 | 4837 | 12662 |  |  |  |  | Page 6 of 7
22:30 | 838 | 7803.5 | 4872.5 | 12676
23:00 | 900 | 7782 | 4908 | 12690
23:30 | 994 | 7631.5 | 4997.5 | 12629
24:00 | 1088 | 7481 | 5087 | 12568
12699 MW (21:00 )
11089 MW (09:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-06-09 |  | Energy |  | 275595510
[15 empty] | 43624 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 4482 | 766 | 2350 | 0 | 2266 | 2051 | 0 | 170 | 325 | 142 | 0 | 16 | 0
0:30 | 4337 | 838.5 | 2322.5 | 20 | 1738.5 | 2022.5 | 0 | 302 | 385.5 | 149 | 0 | 8 | 1156.0275 |  |  | Date: | 43624
1:00 | 4192 | 911 | 2295 | 40 | 1211 | 1994 | 0 | 434 | 446 | 156 | 0 | 0 | 2312.055
1:30 | 4183 | 910.5 | 2296.5 | 20 | 1168.5 | 1994.5 | 0 | 433.5 | 419.5 | 154 | 0 | 0 | 2263.35 | [9 empty] | 275.5955 | 275.5955 |  | Total Energy Gen MKWHr Energy Not Served MKWHr Energy Requirement MKWHr | Total Energy Gen 275.596 MKWHr Energy Not Served 17.225 MKWHr Energy Requirement 292.820 MKWHr
2:00 | 4174 | 910 | 2298 | 0 | 1126 | 1995 | 0 | 433 | 393 | 152 | 0 | 0 | 2214.645 | [9 empty] | 17.2248 | 17.2248
2:30 | 4181.5 | 910.5 | 2303 | 0 | 1106.5 | 1990.5 | 0 | 433 | 394.5 | 150 | 0 | 0.5 | 2153.525 | [9 empty] | 292.8203 | 292.8203
3:00 | 4189 | 911 | 2308 | 0 | 1087 | 1986 | 0 | 433 | 396 | 148 | 0 | 1 | 2092.405
3:30 | 4191.5 | 911 | 2300.5 | 0 | 1087.5 | 1985 | 0 | 433.5 | 387 | 149 | 0 | 0.5 | 2033.6725 | [8 empty] | Shortage
4:00 | 4194 | 911 | 2293 | 0 | 1088 | 1984 | 0 | 434 | 378 | 150 | 0 | 0 | 1974.94
4:30 | 4194.5 | 911 | 2296 | 0 | 1077.5 | 1982 | 0 | 434.5 | 375 | 147 | 0 | 0 | 1917.1625
5:00 | 4195 | 911 | 2299 | 0 | 1067 | 1980 | 0 | 435 | 372 | 144 | 0 | 0 | 1859.385
5:30 | 4169 | 911 | 2285.5 | 0 | 1069.5 | 1977.5 | 0 | 435 | 349 | 137 | 2.5 | 0.5 | 1708.0175
6:00 | 4143 | 911 | 2272 | 0 | 1072 | 1975 | 0 | 435 | 326 | 130 | 5 | 1 | 1556.65
6:30 | 4153 | 911 | 2224.5 | 0 | 1088.5 | 1980 | 0 | 438 | 298.5 | 121 | 16 | 0.5 | 1498.395 | [7 empty] | Coal
7:00 | 4163 | 911 | 2177 | 0 | 1105 | 1985 | 0 | 441 | 271 | 112 | 27 | 0 | 1440.14
7:30 | 4187.5 | 911 | 2123.5 | 0 | 1123 | 1982.5 | 0 | 440.5 | 271 | 113 | 37 | 0.5 | 1442.5275 | [6 empty] | Oil
8:00 | 4212 | 911 | 2070 | 0 | 1141 | 1980 | 0 | 440 | 271 | 114 | 47 | 1 | 1444.915
8:30 | 4167 | 910.5 | 2031 | 0 | 1154.5 | 1990.5 | 0 | 440 | 259.5 | 118 | 66 | 1 | 1396.21
9:00 | 4122 | 910 | 1992 | 0 | 1168 | 2001 | 0 | 440 | 248 | 122 | 85 | 1 | 1347.505
9:30 | 4111.5 | 910.5 | 1988 | 0 | 1126.5 | 2001.5 | 12.5 | 439.5 | 257.5 | 113 | 91.5 | 1.5 | 1142.6575
10:00 | 4101 | 911 | 1984 | 0 | 1085 | 2002 | 25 | 439 | 267 | 104 | 98 | 2 | 937.81
10:30 | 4117.5 | 911 | 1963 | 0 | 1157 | 1927.5 | 25 | 439.5 | 294.5 | 106 | 105.5 | 1.5 | 718.16
11:00 | 4134 | 911 | 1942 | 0 | 1229 | 1853 | 25 | 440 | 322 | 108 | 113 | 1 | 498.51
11:30 | 4125.5 | 911 | 1921 | 0 | 1258 | 1798 | 25 | 437.5 | 302.5 | 110 | 161 | 1.5 | 381.045
12:00 | 4117 | 911 | 1900 | 0 | 1287 | 1743 | 25 | 435 | 283 | 112 | 209 | 2 | 263.58
12:30 | 4175.5 | 910 | 1862.5 | 0 | 1324 | 1746 | 27.5 | 435 | 298.5 | 116 | 183.5 | 2 | 131.79
13:00 | 4234 | 909 | 1825 | 0 | 1361 | 1749 | 30 | 435 | 314 | 120 | 158 | 2 | 0
13:30 | 4234 | 909 | 1825 | 0 | 1361 | 1749 | 30 | 435 | 314 | 120 | 158 | 2 | 0
14:00 | 4234 | 909 | 1825 | 0 | 1361 | 1749 | 30 | 435 | 314 | 120 | 158 | 2 | 0
14:30 | 4037.5 | 910 | 1819.5 | 0 | 1174 | 1743.5 | 30 | 413.5 | 277.5 | 121 | 130.5 | 3.5 | 0
15:00 | 3841 | 911 | 1814 | 0 | 987 | 1738 | 30 | 392 | 241 | 122 | 103 | 5 | 0
15:30 | 3848 | 910.5 | 1800.5 | 0 | 960 | 1742 | 30 | 392 | 237.5 | 117 | 103.5 | 8 | 0
16:00 | 3855 | 910 | 1787 | 0 | 933 | 1746 | 30 | 392 | 234 | 112 | 104 | 11 | 0
16:30 | 3864.5 | 910 | 1793 | 0 | 843 | 1748.5 | 30 | 391.5 | 234 | 114 | 72.5 | 7.5 | 0
17:00 | 3874 | 910 | 1799 | 0 | 753 | 1751 | 30 | 391 | 234 | 116 | 41 | 4 | 0 | [11 empty] | 472
17:30 | 3817 | 909 | 1759.5 | 0 | 754.5 | 1752 | 27.5 | 391 | 270 | 116 | 28 | 4 | 0 | [11 empty] | 100
18:00 | 3760 | 908 | 1720 | 0 | 756 | 1753 | 25 | 391 | 306 | 116 | 15 | 4 | 0 | [11 empty] | 20
18:30 | 3939.5 | 908 | 1854 | 0 | 1187 | 1756.5 | 25 | 325.5 | 384 | 128 | 7.5 | 3.5 | 0 | [11 empty] | 592
19:00 | 4119 | 908 | 1988 | 0 | 1618 | 1760 | 25 | 260 | 462 | 140 | 0 | 3 | 0
19:30 | 4377 | 909 | 2126 | 0 | 2277 | 1804 | 25 | 260 | 488 | 136 | 0 | 7 | 0
20:00 | 4455 | 908 | 2207 | 0 | 2101 | 1842 | 25 | 185 | 376 | 140 | 0 | 3 | 0
20:30 | 4524.5 | 837 | 2283.5 | 0 | 2226.5 | 1908.5 | 25 | 152.5 | 369 | 140 | 0 | 4 | 0
21:00 | 4594 | 766 | 2360 | 0 | 2352 | 1975 | 25 | 120 | 362 | 140 | 0 | 5 | 0
21:30 | 4539.5 | 765.5 | 2340 | 0 | 2393.5 | 2012 | 25 | 120 | 341 | 139 | 0 | 5 | 0
22:00 | 4485 | 765 | 2320 | 0 | 2435 | 2049 | 25 | 120 | 320 | 138 | 0 | 5 | 0
22:30 | 4461 | 765.5 | 2310 | 0 | 2521.5 | 2050.5 | 12.5 | 120 | 288.5 | 139 | 0 | 7.5 | 0
23:00 | 4437 | 766 | 2300 | 0 | 2608 | 2052 | 0 | 120 | 257 | 140 | 0 | 10 | 0
23:30 | 4459.5 | 766 | 2325 | 0 | 2437 | 2051.5 | 0 | 145 | 291 | 141 | 0 | 13 | 0 |  |  | Max Temp. in Dhaka |  | 32.1° C
24:00 | 4482 | 766 | 2350 | 0 | 2266 | 2051 | 0 | 170 | 325 | 142 | 0 | 16 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 275.596 MKWHr Energy Not Served 17.225 MKWHr Energy Requirement 292.820 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-06-09
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | [8 empty] | 0 | 25 | 25 | 25 | 30 | 30 | 30 | 30 | 30 | 25 |  | 25 | 25 | 25 | 25 | 25 |  |  | 331920
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 120 | 120 | 120 | 119 | 116 | 112 | 117 | 112 | 114 | 120 | 117 | 116 | 110 | 119 | 121 | 117 | 118 | 117 |  | 119 | 118 | 120 | 113 | 110 | 120 | 120 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  |  | 1 | 25 | 8 |  | 1 | 8 | 8 | 177076
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 5 | 5 | 8 | 11 | 2 | 0 |  |  |  | 4 | 2 | 0 | [8 empty] | 43470
6 | Sikalbaha 225MW CCPP (Gas) | 219 | 220 | 220 | 223 | 223 | 226 | 225 | 227 | 222 | 223 | 222 | 221 | 225 | 225 | 225 | 225 | 222 | 222 |  | 225 | 227 | 225 | 226 | 227 | 227 | 223 | 5116021
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 46 | 47 | 50 | 50 | 50 | 50 | 50 | 50 | 34 | 34 | 33 | 34 | 33 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 934636
12 | Hathazari 100 MW peaking PP | 73 | 34 | 34 | 34 | 34 | 34 | [5 empty] | 0 | 25 | 32 | 32 | 32 | 32 | 40 |  | 62 | 64 | 33 | 33 | 33 | 57 | 65 | 695088
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 23 | 34 | 51 | 51 | 51 | 51 | 44 | 604690
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 46 | 46 | 46 | 46 | 46 | 46 | 45 | 45 | 37 | 29 | 29 | 30 | 34 | 38 | 38 | 43 | 46 | 43 |  | 41 | 43 | 46 | 46 | 46 | 46 | 46 | 1001840
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 195 | 196 | 193 | 192 | 196 | 177 | 194 | 198 | 187 | 193 | 196 | 205 | 145 | 98 | 125 | 119 | 127 | 127 |  | 127 | 75 | 105 | 163 | 162 | 162 | 164 | 4209
17 | Siddhirganj 335 MW CCPP | [5 empty] | 6 | 2 | 1 | 1 | 1 | 1 | 12 | 216 | 60 | 60 | 60 | 60 | 60 |  | 140 | 220 | 218 | 218 | 220 | 222 | 218 | 1791283
18 | Kodda 300 MW PP Unit-2 (Summit) | 55 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 15 | 15 | 15 | 15 | 15 |  | 16 | 16 | 16 | 15 | 22 | 128 | 148 | 1109018
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 100 | 100 | 100 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2590094
23 | Ghorasal TPP Unit-5 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4205250
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 44 | 43 | 43 | 43 | 43 | 42 | 42 | 42 | 42 | 42 | 42 | 41 | 41 | 41 | 41 | 42 | 40 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1001448
33 | Ashuganj 225 MW CCPP | 139 | 136 | 132 | 129 | 140 | 154 | 167 | 167 | 179 | 183 | 186 | 184 | 185 | 151 | 150 | 150 | 150 | 151 |  | 204 | 206 | 204 | 207 | 210 | 208 | 193 | 4069000
34 | Ashuganj 450 MW CCPP(South) | 300 | 285 | 305 | 310 | 275 | 265 | 265 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 285 | 275 | 275 | 275 |  | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 6929000
| Ashuganj 450 MW CCPP(North) | 320 | 320 | 320 | 320 | 320 | 320 | 310 | 305 | 285 | 280 | 285 | 285 | 285 | 285 | 295 | 280 | 280 | 280 |  | 280 | 280 | 285 | 280 | 285 | 280 | 310 | 7494000
| Ashuganj 420 MW CCPP(East) | 223 | 217 | 218 | 218 | 218 | 218 | 236 | 242 | 248 | 248 | 249 | 248 | 248 | 249 | 271 | 283 | 296 | 252 |  | 271 | 295 | 296 | 295 | 296 | 296 | 296 | 6097300
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 406 | 404 | 403 | 404 | 404 | 409 | 411 | 406 | 370 | 371 | 387 | 344 | 314 | 284 | 270 | 270 | 270 | 270 |  | 284 | 397 | 393 | 402 | 413 | 412 | 408 | 8845310
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 370 | 270 | 300 | 300 | 300 | 300 |  | 300 | 350 | 350 | 450 | 450 | 450 | 450 | 9324000
41 | Haripur 360MW CCPP(HPL) | 337 | 332 | 333 | 332 | 331 | 333 | 332 | 307 | 280 | 285 | 300 | 246 | 246 | 233 | 235 | 235 | 245 | 245 |  | 340 | 352 | 352 | 350 | 342 | 342 | 342 | 7272000
42 | RPCL 210MW CCPP | 72 | 72 | 72 | 82 | 82 | 72 | 34 | 34 | 33 | 31 | 30 | 31 | 30 | 27 | 31 | 32 | 33 | 32 |  | 44 | 45 | 48 | 102 | 98 | 95 | 95 | 1221120
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 1 | 5 | 13 | 28 | 45 | 14 | 1 | 5 | 10 | 6 | 4 | 2 | [8 empty] | 115390
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 39 | 42 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1016000
45 | Fenchugonj CCPP Phase-2 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 39 | 39 | 39 | 39 | 39 | 39 |  | 39 | 39 | 39 | 39 | 40 | 40 | 40 | 890040
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 56 | 56 | 56 | 56 | 56 | 28 | 58 | 59 | 59 | 59 | 59 | 59 | 58 | 40 | 40 | 40 | 40 | 40 |  | 58 | 59 | 58 | 56 | 56 | 55 | 55 | 1245600
48 | Shahjibazar 86MW PP (Shahjibazar) | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 72 | 74 | 74 | 74 | 74 | 20 | 20 | 20 | 20 | 10 |  | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 1533120
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 174 | 174 | 175 | 172 | 175 | 175 | 179 |  | 180 | 178 | 180 | 180 | 182 | 182 | 182 | 3739080
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 251280
54 | Hobiganj 11MW PP Cofidence-E | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 261461
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 44 | 44 | 42 | 42 | 42 | 24 | 22 | 22 | 22 | 25 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1039800
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 15 | 15 | 15 | 15 | 8 | 8 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 349800
57 | Bibiana-II 341 MW CCPP (Summit) | 320 | 330 | 330 | 330 | 335 | 310 | 285 | 270 | 265 | 270 | 270 | 275 | 275 | 255 | 295 | 300 | 285 | 275 |  | 290 | 265 | 265 | 300 | 265 | 270 | 300 | 7090000
| Bibiyana South 400 MW | 257 | 260 | 258 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 256 | 220 | 220 | 220 | 220 | 225 |  | 258 | 256 | 260 | 260 | 95 | 15 | 50 | 5449800
58 | Nababganj 55 MW PP (Southern power ) | [10 empty] | 0 | 17 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 442011
59 | Tangail Palli Power Gen 22 MW | 9 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 0 | [11 empty] | 3 | 12 | 161760
60 | Barabkunda 22 MW PP (Regent) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 225120
61 | Narshingdi 22 MW PP (Doreen) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 0 | [9 empty] | 10 | 10 | 19 | 19 | 231300
62 | Tangail 22 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 13 | 17 | 17 | 19 | 19 | 19 | 19 | [11 empty] | 13 | 13 | 167868
63 | Impoprt (Tripura) | 156 | 152 | 148 | 150 | 144 | 130 | 112 | 114 | 122 | 104 | 108 | 112 | 120 | 124 | 122 | 112 | 116 | 116 |  | 140 | 136 | 140 | 140 | 138 | 140 | 142 | 3091200
64 | Malancha, Ctg. EPZ (United) | 33 | 34 | 33 | 35 | 36 | 36 | 36 | 36 | 35 | 35 | 35 | 35 | 40 | 25 | 36 | 36 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 915360
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15 | 15 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 445316
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 5 | 5 | 8 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 244620
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 19 | 32 | 32 | 32 | 32 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 772900
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 13 | 13 | 12 | 12 | 12 | 12 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 20 | 20 | 392690
69 | Summit Ashulia | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 480000
70 | Summit Madhabdi | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 26 | 25 | 22 | 22 | 20 | 15 | 15 | 15 | 15 | 15 | 6 |  | 15 | 22 | 26 | 27 | 27 | 26 | 27 | 508320
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 17 | 17 | 17 | 0 |  | 17 | 25 | 25 | 25 | 25 | 25 | 25 | 637200
72 | Rupganj 33 MW PP(Summit) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 33 | 33 | 33 | 16 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 782300
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 52 | 52 | 17 |  |  | 52 | 52 | 498180
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 3 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 25 |  | 35 | 93 | 93 | 95 | 96 | 50 | 9 | 555240
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 90 | 90 | 90 | 17 | 17 | 17 | 17 | 17 |  | 108 | 108 | 108 | 108 | 108 | 108 | 99 | 1152000
77 | Siddhirganj 100 PP(Dutch Bangla) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 58 | 59 | 63 | 60 | 60 | 40 | 17 | 17 | 17 | 9 |  | 9 | 9 | 9 | 10 | 50 | 75 | 75 | 987840
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 50 | 8 | 237120
79 | Kodda 150 MW PP | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 50 | 82 | 82 | 82 | [6 empty] | 48 | 48 | 32 | 32 | 16 | 38 | 98 | 832320
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 26 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 14 | 8 | 16 | 16 | 16 | 8 |  | 12 | 25 | 52 | 52 | 52 | 52 | 52 | 653501
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 17 | 17 | 17 | 17 | 17 |  | 30 | 50 | 60 | 70 | 105 | 105 | 105 | 2045760
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 2 | 4 | 2 | 1 | 2 | 3 | 1 | 1 | 1 | 0 | [9 empty] | 17398
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 446150
| Karnaphuli Power Ltd. | 41 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 31 | 39 | 50 | 17 |  | 25 | 51 | 51 | 51 | 51 | 51 | 34 | 918323
82 | Madanganj 102 PP(Summit) | [9 empty] | 10 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 |  |  | 0 | 175631
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [16 empty] | 9 | 11 |  | 11 | 11 |  |  |  |  | 4 | 46084
86 | Meghnaghat CCPP ( Summit) | 308 | 305 | 310 | 308 | 310 | 305 | 305 | 263 | 281 | 283 | 260 | 270 | 258 | 269 | 307 | 275 | 291 | 304 |  | 306 | 270 | 290 | 275 | 270 | 281 | 279 | 6998022
87 | Meghnaghat 100 MW(IEL) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 51 | 52 | 50 | 53 | 67 | 67 | 67 | 68 | 32 | 9 | 8 |  | 9 | 50 | 44 | 83 | 84 | 84 | 83 | 1251840
| Meghnaghat 104 MW PP (OPCL) | 17 |  |  |  | 15 | 17 | 17 | 17 | 17 | 17 | 52 | 54 | 73 | 74 | 74 | 74 | 48 | 35 |  | 41 | 74 | 68 | 72 | 72 | 68 | 54 | 950400
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 10 | 10 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 744240
92 | Fenchuganj 44MW (Energyprima) | 44 | 44 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 49 | 49 | 49 | 48 | 47 | 47 | 48 | 10 |  | 40 | 44 | 47 | 47 | 50 | 50 | 50 | 1129248
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1182806
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 16 | 33 | 33 | 50 | 75 | 75 | 75 | 442800
95 | Patenga 50MW PP (Baraka) | 12 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 10 | 44 | 40 | 40 | 40 | 23 | 19 |  | 19 | 19 | 19 | 22 | 45 | 46 | 46 | 492480
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 10 |  | 30 | 30 | 30 | 15 | 15 | 15 | 15 | 139256
100 | Manikganj 55 MW PP (Northern) | [10 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 35 | 35 | 0 | 463278
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 80 | 80 | 80 | 112 | 112 | 112 | 80 | 80 | 80 | 80 | 80 |  | 80 | 112 | 112 | 112 | 112 | 112 | 112 | 2339100
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 3050
103 | Kamalaghat 54 MW PP(Banco Energy) | [19 empty] | 17 | 25 | 35 | 35 | 35 | 35 | 35 | 181080
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 67 | 68 | 68 | 68 | 68 | 45 |  | 58 | 86 | 86 | 87 | 88 | 68 | 68 | 1660800
112 | Aurahati 100MW PP (Aggreko) | 40 | [24 empty] | 0 | 65127
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 74 | 149 | 132 | 102 | 102 | 102 | 40 | 8712000
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 63 | 63 | 63 | 63 | 63 | 63 | 25 | 756480
116 | Chandpur 200MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 38 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 54 |  | 72 | 100 | 100 | 100 | 100 | 100 | 65 | 1158720
117 | Ashuganj 150MW PP (Midland) | 5 | 6 | 6 | 6 | 5 | 6 | 6 | 5 | 6 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | 13 | 41 |  | 75 | 110 | 105 | 150 | 150 | 150 | 21 | 807927
118 | Bibiyana-III 400 MW CCPP | 371 | 371 | 372 | 347 | 347 | 347 | 347 | 347 | 334 | 340 | 351 | 390 | 403 | 291 | 303 | 303 | 303 | 303 |  | 352 | 402 | 403 | 365 | 365 | 365 | 365 | 8368000
| Jamalpur 115 MW PP (United) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 19 |  | 85 | 85 | 85 | 85 | 85 | 19 | 19 | 699600
| Anwara 300 MW PP (United) | 69 | 70 | 69 | 69 | 69 | 70 | 69 | 69 | 70 | 70 | 70 | 69 | 69 | 69 | 69 | 69 | 15 | 15 |  | 100 | 205 | 205 | 205 | 126 | 100 | 100 | 2029855
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 38 | 38 | 38 | 38 | 12 | 12 |  | 12 | 12 | 12 | 63 | 63 | 63 | 63 | 720960
| Anlima Energy Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 15 | 17 | 17 | 17 | 17 | 17 |  | 5 | 18 |  | 62 | 68 | 68 | 68 | 68 | 68 | 68 | 716345
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 33 | 17 | 17 | 25 | 35 | 27 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 659880
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 4 | 12 | 7 | 13 | 17 | 9 | 2 | 0 | 3 | 4 | 4 | 1 | [8 empty] | 81523
| Chandpur 115(Doreen) | 71 | 20 | 17 | 18 | 17 | 18 | 18 | 20 | 36 | 39 | 67 | 73 | 72 | 72 | 72 | 72 | 72 | 91 |  | 115 | 115 | 109 | 115 | 114 | 115 | 91 | 1534080
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 22 | 35 | 35 | 35 | 35 | 35 | 17 | 508320
| Mirsharai 150 MW (Oil) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 36 | 36 | 36 | 36 | 36 | 36 | 18 | 18 | 18 |  | 18 | 103 | 163 | 163 | 163 | 54 | 54 | 1042109
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 2 | 1 | 2 | 2 | 3 | 5 | 11 | 4 | 4 |  | 3 | 7 | 3 | 5 | 5 | 10 | 16 | 71280
120 | Eastern Zone Total | 6601 | 6418 | 6437 | 6440 | 6431 | 6340 | 6282 | 6225 | 6167 | 6266 | 6523 | 6495 | 6598 | 5654 | 5794 | 5709 | 5595 | 5489 |  | 6768 | 7666 | 7707 | 8018 | 7825 | 7782 | 7481 | 160813989
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [6 empty] | 31 | 49 |  |  |  |  | 16 | 256320
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL) | 234 | 233 | 233 | 234 | 235 | 235 | 236 | 235 | 235 | 234 | 235 | 230 | 230 | 230 | 232 | 232 | 231 | 231 |  | 100 | 100 | 50 |  |  |  |  | 4424447
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 18 | 0 | [5 empty] | 20 |  | 20 | 20 | [5 empty] | 201120
| Khulna 225 MW CCPP | 200 | 200 | 200 | 200 | 200 | 200 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 160 | 160 | 160 | 160 | 160 |  | 160 | 160 | 135 | 120 | 120 | 120 | 170 | 4374893
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 54 | 54 | 54 | 54 | 54 | 54 | 53 | 53 | 53 | 17 | 17 | 17 | 17 | [7 empty] | 7 |  |  |  | 5 | 30 | 618240
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 1 | 8 | 20 | 39 | 36 | 22 | 22 | 46 | 51 | 27 | 44 | 0 | 1 | [8 empty] | 357840
131 | Rampal 1320 MW (BIFPCL) | 376 | 376 | 376 | 376 | 376 | 376 | 376 | 376 | 375 | 369 | 369 | 366 | 372 | 372 | 373 | 378 | 375 | 376 |  | 376 | 376 | 376 | 376 | 374 | 377 | 377 | 8923636
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [6 empty] | 18 | 54 | 17 | 17 | 17 | 72 | 72 | 516000
133 | Bhola Nutan Biddut BD LTD (GAS) | 26 | 27 | 25 | 12 | 11 | 12 | 11 | 17 | 40 | 75 | 30 | 26 | 26 | 27 | 27 | 27 | 26 | 26 |  | 55 | 95 | 110 | 110 | 110 | 111 | 110 | 1029355
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [6 empty] | 16 | 16 | 32 | 32 | 32 | 16 | 16 | 369024
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 225 | 307 | 307 | 307 | 5236400
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 172 | 172 | 172 | 170 | 170 | 172 | 172 | 172 | 172 | 172 | 173 | 173 | 173 | 172 | 170 | 172 | 172 | 152 |  | 174 | 156 | 174 | 156 | 173 | 173 | 173 | 4057723
140 | Bhola 33 MW PP (Venture) | 36 | 35 | 35 | 34 | 33 | 30 | 27 | 25 | 22 | 21 | 21 | 22 | 24 | 22 | 20 | 19 | 19 | 20 |  | 28 | 28 | 29 | 33 | 35 | 34 | 33 | 652154
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [6 empty] | 16 | 16 |  |  |  |  | 40 | 130500
143 | Gopalganj 100 MW Peaking PP | 45 | 31 | 31 | 27 | 21 | 22 | 22 | 22 | 23 | 23 | 30 | 0 | [5 empty] | 26 |  | 30 | 30 |  |  |  |  | 0 | 368896
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 35 | 15 | 15 | 15 | [6 empty] | 30 | 32 |  |  | 18 | 85 | 85 | 777744
146 | Bheramara HVDC | 911 | 910 | 911 | 911 | 911 | 911 | 911 | 911 | 910 | 911 | 911 | 911 | 909 | 911 | 911 | 910 | 910 | 908 |  | 908 | 909 | 908 | 766 | 765 | 766 | 766 | 21538909
147 | Bheramara 410 MW CCPP | 170 | 170 | 170 | 170 | 190 | 190 | 190 | 190 | 190 | 200 | 205 | 210 | 225 | 235 | 235 | 235 | 235 | 200 |  | 225 | 255 | 265 | 265 | 260 | 260 | 260 | 5315904
148 | Payra 1320 MW
149
150 | Barapukuria TPP Unit-1 | 66 | 65 | 63 | 66 | 66 | 63 | 63 | 63 | 64 | 65 | 66 | 66 | 69 | 67 | 70 | 71 | 70 | 72 |  | 72 | 72 | 72 | 72 | 72 | 71 | 70 | 1565673
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 240 | 240 | 240 | 5842200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 |  | 27 | [6 empty] | 513184
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 1 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 7560
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 179 | 180 | 181 | 183 | 186 | 187 | 189 | 193 | 160 | 160 | 160 | 160 | 160 | 140 | 140 | 140 | 140 | 140 |  | 140 | 155 | 160 | 202 | 205 | 210 | 214 | 4401145
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 156 | 156 | 158 | 161 | 162 | 165 | 168 | 169 | 169 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 144 | 176 | 199 | 199 | 198 | 4111455
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 414 | 414 | 414 | 415 | 418 | 354 | 357 | 285 | 230 | 210 | 210 | 220 | 228 | 335 | 335 | 331 | 292 |  | 292 | 353 | 395 | 426 | 429 | 393 | 425 | 8244872
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 14 | 14 | 14 | [9 empty] | 10 | 12 | 12 | 32 | 32 | 32 |  | 32 | 12 | [5 empty] | 143317
162 | Bogra 22 MW PP (GBB) | 20 | 20 | 21 | 21 | 21 | 21 | 20 | 20 | 19 | 18 | 20 | 20 | 20 | 20 | 21 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 487440
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 179748
165 | Amnura 50 MW PP(Sinha) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 |  |  |  |  | 0 | 538340
166 | Katakhali 50 MW PP (Northern) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 8 | 8 | 8 | 8 | [6 empty] | 8 | 8 |  |  |  |  | 16 | 364236
167 | Katakhali 50 MW Peaking PP | 23 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 36 | 36 | 36 | 36 | 35 | 21 | 21 | 32 |  | 36 | 15 | [5 empty] | 483300
168 | Santahar 50 MW Peaking PP | 35 | 35 | 35 | 35 | 35 | [14 empty] | 30 | 35 | 35 | 28 | 28 | 28 | 28 | 332280
169 | Natore 52 MW PP (Rajlanka) | [20 empty] | 8 |  |  |  |  | 0 | 4934
170 | Chapainawabganj 100 MW Peaking PP | 72 | 72 | 72 | 72 | 72 | 60 | 40 | 40 | 40 | 31 | 31 | 38 | 31 | 23 | 27 | 27 | 24 | 34 |  | 84 | 84 | 33 | 26 |  |  | 0 | 968808
171 | Baghabari 200 MW PP (Paramount) | [10 empty] | 0
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [6 empty] | 3 | 35 | 35 | 40 | 50 | 35 | 35 | 738336
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 |  |  |  |  | 35 | 35 | 35 | 0 | [9 empty] | 25 | 35 | 35 | 113 | 113 | 113 | 113 | 638688
173 | Rangpur 20 MW GTPP | [15 empty] | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 |  |  |  | 40 | 35 | 35 | 34 | 34 | 34 |  |  |  |  | 2 |  | 34 | 34 | 34 | 56 | 90 | 92 | 92 | 711523
177 | Sympa Solar Power 8MW | [8 empty] | 4 | 4 | 6 | 6 | 6 | 5 | 4 | 5 | 3 | 0 | [8 empty] | 50267
178 | Energypac Power Venture Thakurgaon Ltd. | [12 empty] | 8 | 35 | 35 | 35 |  |  |  | 35 | 40 | 72 | 110 | 114 | 114 | 114 | 593088
| Intraco Solar 30 MW | [5 empty] | 0 | 1 | 0 |  |  | 0 | 23 | 19 | 20 | 20 | 13 | 7 | 2 |  | 0 | [6 empty] | 111596
| Adani Power Jharkhanda Ltd | 1072 | 1074 | 1067 | 1062 | 1058 | 1056 | 1066 | 1061 | 1082 | 1068 | 918 | 911 | 908 | 909 | 895 | 897 | 906 | 905 |  | 912 | 956 | 994 | 1052 | 1056 | 1057 | 1057 | 24174546
178 | Teesta Solar Limited | [5 empty] | 1 | 7 | 1 | 8 | 2 | 18 | 133 | 81 | 75 | 38 | 27 | 21 | 9 | [8 empty] | 425880