## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-06-15 | Thursday
|  | Date (day): | 2023-06-15 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12492.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14803 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-06-14 | 2023-06-15 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 170 | 160 | 160 | 160
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 396 | 390 | 400 | 400 |  |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 322 | 332 | 330 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 73 | 73 | 66 | 93 |  | 7 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 300 | 304 | 305 | 305 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 95 | 94 | 96 | 97 | 5 |  | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 15 | 0 | 30 | 25 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 20 | 51 | 59 | 44 | 59 |  | 41 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 19 | 19 |  | 3 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 182 | 191 | 190 | 190 | 20 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 75 | 75 | 68 | 92 | 8 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 312 | 324 | 320 | 320
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 74 | 91 | 92 | 92 | 10 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 0 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 115 | 32 | 115
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 35 | 55 | 0
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 20 | 44 | 44 | 44 |  | 36 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 30 | 30 | 24 | 30
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 24 | 8 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 47 | 147 | 45 | 145 | 155 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 300 | 300 | 300 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 95 | 97 | 100 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 135 | 17 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 88 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 72 | 92 | 53 | 92 | 12 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 90 | 35 | 90 | 72 |  | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 31 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 17 | 35 | 20 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5867 | 3423 | 4052 | 3553 | 4170 | 720 | 947
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 85 | 105 | 110 | 110 | 70 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 25 | 8 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 9 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 10 | 46 | 50 | 50
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 50 | 50 | 50 | 55 | 180 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 219 | 225 | 225
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 68 | 34 | 105
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 16 | 40 | 30 | 40 |  | 58 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 48 | 51 | 51 | 51 |  | 51 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 10 | 23 | 33 | 33 | 67 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 38 | 25 | 50 | 50 |  | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 9 | 9 | 9 | 9 | 13 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 24 | 10 | 25
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 70 | 300 | 70 | 285 |  | 15 | Engine problem
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 34 | 17 | 34 | 76 |  | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 38 | 25 | 50 | 50 |  | Fuel shortage
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 68 | 34 | 68 | 48 |  | Fuel shortage
| Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 36 | 163 | 72 | 163 |  |  | On test.
| SS Power I |  | Coal | SS Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 18 | 7 | 13 | 10
| Chattogram area Total |  |  |  |  | 2605 | 2545 | 724 | 1325 | 908 | 1405 | 699 | 454
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 104 | 120 | 110 | 120 |  |  | ST Under maint.
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 280 | 300 | 300 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 260 | 260 | 280 | 80 |  | Gas shortage
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 227 | 228 | 225 | 230 | 170 |  | Gas shortage
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 35 | 39 | 40 | 40 |  |  | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 5 | 125 | 5 | 150
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 36 | 40 | 40 |  | 12 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 17 | 17 | 17 | 183 |  | Fuel shortage
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 174 | 160 | 135 | 152
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 43 | 8 | 43 |  | 9 | Engine problem
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 21 | 20 | 20 | 20 |  | 5 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Contract Expired
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 79 | 34 | 100 | 114 | 0
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 95 | 9 | 115
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 52 | 94 | 72 | 97 | 18 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 3159 | 3096 | 1407 | 1691 | 1481 | 1858 | 638 | 226
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 24 | 48 | 50 | 50 | 152 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 19 | 19 | 19 | 3 |  | Gas shortage
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 68 | 87 | 68 | 86 | 114 |  | Fuel shortage
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 85 | 19 | 85 | 30 |  | Fuel shortage
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 22 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 | 10 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 163 | 251 | 219.6 | 252 | 155 | 0
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 112 | 112 |  | 51 | ST under maint.
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 50 | 50
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 43 | 46 | 45 | 45
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 48 | 50 | 60 | 60
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 73 | 69 | 72 | 76
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 126 | 126 | 125 | 125 |  | 106 | ST under maint.
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 13 | 13 | 13 | 12 |  | Gas shortage
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 325 | 300 | 300 | 320 |  |  | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 303 | 309 | 0 | 0 |  |  | Machine triped at 10:41
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 355 | 260 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1523 | 1429 | 1271 | 1295 | 12 | 674
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 912 | 807 | 918 | 918
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 92 | 46 | 92 | 23 |  | Fuel shortage
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 14 | 24 | 15 | 25 |  | 29 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 194 | 200 | 200 | 200 | 30
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 25 | 70 | 36 | 72 |  | 37 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 145 | 150 | 185 | 185 | 225 |  | Gas shortage
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 32 | 8 | 40
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 54 | 73 | 72 | 73 | 32 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 50 | 85 | 50 | 85
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 78 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 222 | 229 | 200 | 330 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 371 | 376 | 370 | 376 | 241 |  | Coal Shortage.
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 2905 | 2901 | 2081 | 2138 | 2200 | 2396 | 567 | 66
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 32 | 48 | 16 | 48 | 46 |  | Fuel shortage
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 25 | 35 | 21 | 35 |  | 5 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 81 | 173 | 170 | 170 |  | 24 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 0 | 0 | 0 | 0 | 1244 |  | Coal Shortage.
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 108 | 109 | 110 | 110 |  | 110 | ST Under maintenance
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 150 | 17 | 150
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 307 | 307 | 200 | 200
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 570 | 822 | 534 | 713 | 1290 | 139
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 4 | 0 | 25 |  | 27 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 28 | 30 | 35 |  | 36 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 28 | 14 | 14 | 28 | 28 |  |  | Engine problem
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 34 | 25 | 34 |  | 16 | Engine problem
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 36 | 35 | 35 | 35 |  | 15 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 168 | 167 | 165 | 165
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 143 | 144 | 162 | 150 | 70 |  | Gas shortage
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 377 | 379 | 414 | 414
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 35 | 35 |  | 15 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 17 | 21 | 22 | 22
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 43 | 0 | 43 | 9 |  | Fuel shortage
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 80 | 40 | 80 |  | 24 | Engine problem
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 108 | 0 | 200
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 50 | 35 | 95 | 18 |  | Fuel shortage
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 55 | 35 | 95 | 18 |  | Fuel shortage
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 748*1 | 748 | 748 | 683 | 748 | 748 | 748
| Rajshahi Area Total |  |  |  |  | 2927 | 2905 | 1521 | 1953 | 1788 | 2212 | 506 | 136
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 62 | 67 | 70 | 70 | 15
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 230 | 230 | 230 | 230
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 16 | 4
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 56 | 35 | 71 | 42 |  | Fuel shortage
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 115 | 35 | 115
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 21 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 175 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 564 | 468 | 538 | 502 | 81 | 85
| Total |  |  |  |  | 24143 | 23370 | 11976 | 14129 | 12492.6 | 14803 | 4668 | 2727
A. |  | 2023-06-14 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 14129 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 10443 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 15000 | MW
3 | Day peak Generation : |  |  | 11976 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14380.63 | MW
4 | Evening peak Generation : |  |  | 14129 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 832 | MW
5 | Total Energy Generation : |  | 284.3755 | MKWHr | By Solar | 2.5026 | MKWHr
| By Gas : | 156.6574 | MKWHr |  | By Oil: | 65.6425 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 32.9999 | MKWHr |  | By Hydro: | 1.159 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.29621 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4668 | MW | Dhaka | 5422.33 | 5369.33 |  | 53 |  | 18:00 |  | 1338.91
|  |  | For Plants S/D or M/C prob = |  |  | 2727 | MW | Chittagong | 1339.5 | 1339.5 |  | 0 |  | 19:00 |  | 912.025
|  |  | Total = |  |  | 7395 | MW | Khulna | 1878 | 1628 |  | 250 |  | 19:30 |  | 1024.715
7 | Total Gas Supplied : |  |  | 1212.78 | MMCFD |  |  | Rajshahi | 1548.8 | 1461.8 |  | 87 |  | 20:00 |  | 1068.645
8 | Fuel Cost : | i) Gas : | Taka | 173729569.634 | ii) Oil : | Taka | 857828617.03 | Comilla | 1432 | 1224 |  | 208 |  | 21:00 |  | 831.805
|  | iii) Coal : | Taka | 38288811.9 | Total | Taka | 1069846998.564 | Mymensingh | 1019 | 951 |  | 68 |  | 22:00 |  | 963.595
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 270 | 270 |  | 0 |  | 23:00 |  | 1686.53
| ii) During Peak Demand : |  |  | 630 | MW (E to W) at | 21:00 | hrs | Barisal | 505 | 458 |  | 47 |  | 24:00 |  | 1950.11
| iii) Maximum : |  |  | 630 | MW at | 21:00 | hrs | Rangpur | 966 | 847 |  | 119
10 | Maximum Temperature in Dhaka was |  |  |  | 36.8° C |  |  | Total | 14380.63 | 13548.63 |  | 832
B. |  | 2023-06-15 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 36.8° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 14800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14803 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 12700 | MW
4 | Reserve(Generation end) |  |  |  | 3 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 297.8808 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10800 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.2625 | MKWHr. | ii) HVDC Flow at Peak Time |  | 807 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.8554 | MKWHr. | iii) Maximum HVDC Flow : |  | 913 | MW at | 10:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 73.24 |  | (b) Today: | 73.02 |  | (c) Rule Curve: |  | 79.68
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-06-14 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 100 | 170 | 0 | 0 | 0 | 403 | 342 |  | 0 | 450 | 303 | 54 | 97 | 0 | 330 | 0 | 195 | 65 | 50 | 16 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 25 | 33 | 24 | 8 | 0 | 25 | 25 | 110 | 0 | 8 | 218 | 0 | 0 | 0 |  | 12 | 16 | 51 | 22 | 0 | 50 | 9 | 35 | 0 | 0 | 0 | 285 | 260 | 104 | 8 | 0 | 44 | 0 | 0 | 51 | 0 | 0 | 25 | 20 | 8 | 0 | 20 | 166 | 47 | 0 | 13 | 0 | 43 | 30 | 50 | 45 | 112 | 0 | 60 | 72 | 0 | 125 | 0 | 0 | 10 | 310 | 16 | 8 | 0 | 62 | 277 | 0 | 68 | 96 | 17 | 0 | 25 | 17 | 30 | 402 | 18 | 35 | 21 | 0 | 70 | 17 | 17 | 114 | 8 | 25 | 390 | 53 | 0 | 17 | 17 | 0 | 17 | 0 | 48 | 17 | 234 | 18 | 0 | 0 | 17 |  | 789 | 0 | 150 | 0 | 0 | 207 | 0 | 0 | 21 | 46 | 8 | 173 | 31 | 16 | 0 | 0 | 0 | 0 | 28 | 8 | 14 | 0 | 35 | 0 | 35 | 0 | 0 | 8 | 69 | 0 | 229 | 0 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 414 | 54 | 133 | 35 | 50 | 34 | 0 | 0 | 35 | 0 | 111 | 0 | 17 | 0 | 0 | 0 | 237 | 0 | 370 | 0 | 200 | 0 | 0 | 0 |  | 7410 | 3811 | 11221 | 4350 | 789 | 2344 | 506 | 1413 | 868 | 50 | 444 | 274 | 166 | 0 | 17 | 1889.945 | 73.29
2:00 | 0 | 0 | 100 | 170 | 0 | 0 | 0 | 403 | 340 |  | 0 | 450 | 307 | 58 | 97 | 0 | 325 | 0 | 191 | 65 | 50 | 16 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 25 | 33 | 24 | 8 | 0 | 25 | 25 | 110 | 0 | 8 | 221 | 0 | 0 | 0 |  | 12 | 16 | 51 | 22 | 0 | 6 | 9 | 39 | 0 | 0 | 0 | 335 | 260 | 98 | 8 | 0 | 44 | 0 | 0 | 51 | 0 | 0 | 25 | 20 | 8 | 0 | 20 | 166 | 47 | 0 | 13 | 0 | 43 | 30 | 50 | 45 | 112 | 0 | 60 | 72 | 0 | 124 | 0 | 0 | 10 | 315 | 16 | 8 | 0 | 47 | 290 | 0 | 68 | 97 | 17 | 0 | 25 | 17 | 5 | 395 | 18 | 35 | 17 | 0 | 70 | 17 | 17 | 114 | 9 | 25 | 382 | 53 | 0 | 17 | 17 | 0 | 17 | 0 | 21 | 17 | 234 | 18 | 0 | 0 | 17 |  | 790 | 0 | 150 | 0 | 0 | 205 | 0 | 0 | 21 | 46 | 8 | 170 | 30 | 16 | 0 | 0 | 0 | 0 | 28 | 0 | 14 | 0 | 35 | 0 | 0 | 18 | 0 | 8 | 67 | 0 | 230 | 0 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 414 | 36 | 161 | 35 | 50 | 34 | 0 | 0 | 35 | 0 | 111 | 0 | 17 | 0 | 0 | 0 | 235 | 0 | 377 | 0 | 200 | 0 | 0 | 0 |  | 7344 | 3799 | 11143 | 4373 | 790 | 2372 | 548 | 1282 | 874 | 50 | 440 | 231 | 166 | 0 | 17 | 1773.435 | 73.28
3:00 | 0 | 0 | 100 | 170 | 0 | 0 | 0 | 402 | 322 |  | 0 | 450 | 300 | 58 | 97 | 0 | 330 | 0 | 194 | 65 | 50 | 16 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 25 | 33 | 24 | 8 | 0 | 25 | 25 | 100 | 0 | 8 | 222 | 0 | 0 | 0 |  | 12 | 17 | 51 | 22 | 0 | 6 | 9 | 39 | 0 | 0 | 0 | 285 | 260 | 100 | 8 | 0 | 44 | 0 | 0 | 51 | 0 | 0 | 25 | 20 | 8 | 0 | 20 | 162 | 47 | 0 | 13 | 0 | 43 | 30 | 50 | 45 | 112 | 0 | 59 | 72 | 0 | 124 | 0 | 0 | 10 | 320 | 24 | 8 | 0 | 47 | 226 | 0 | 68 | 95 | 17 | 0 | 25 | 17 | 5 | 396 | 18 | 35 | 17 | 0 | 70 | 17 | 17 | 114 | 9 | 25 | 390 | 53 | 0 | 17 | 17 | 0 | 17 | 0 | 18 | 17 | 234 | 18 | 0 | 0 | 15 |  | 911 | 0 | 150 | 0 | 0 | 205 | 0 | 0 | 21 | 41 | 8 | 170 | 29 | 16 | 0 | 0 | 0 | 0 | 28 | 0 | 14 | 0 | 34 | 0 | 0 | 22 | 0 | 8 | 68 | 0 | 230 | 0 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 418 | 36 | 190 | 35 | 50 | 34 | 0 | 0 | 0 | 0 | 110 | 0 | 17 | 0 | 0 | 0 | 234 | 0 | 370 | 0 | 200 | 0 | 0 | 0 |  | 7219 | 3909 | 11128 | 4341 | 911 | 2358 | 511 | 1247 | 868 | 50 | 439 | 226 | 162 | 0 | 15 | 1644.51 | 73.27
4:00 | 0 | 0 | 100 | 170 | 0 | 0 | 0 | 404 | 322 |  | 0 | 450 | 304 | 58 | 97 | 0 | 333 | 0 | 193 | 65 | 50 | 16 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 25 | 33 | 24 | 8 | 0 | 25 | 25 | 102 | 0 | 8 | 222 | 0 | 0 | 0 |  | 12 | 17 | 51 | 22 | 0 | 6 | 9 | 40 | 0 | 0 | 0 | 300 | 260 | 102 | 8 | 0 | 44 | 0 | 0 | 51 | 0 | 0 | 25 | 17 | 8 | 0 | 20 | 164 | 47 | 0 | 13 | 0 | 43 | 30 | 47 | 45 | 112 | 0 | 60 | 72 | 0 | 124 | 0 | 0 | 10 | 310 | 24 | 8 | 0 | 47 | 113 | 0 | 68 | 94 | 17 | 0 | 25 | 17 | 6 | 377 | 18 | 35 | 17 | 0 | 70 | 17 | 17 | 114 | 9 | 25 | 383 | 53 | 0 | 17 | 17 | 0 | 17 | 0 | 18 | 17 | 234 | 18 | 0 | 0 | 15 |  | 912 | 0 | 165 | 0 | 0 | 205 | 0 | 0 | 20 | 41 | 8 | 168 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 36 | 0 | 0 | 22 | 0 | 8 | 68 | 0 | 230 | 0 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 417 | 54 | 190 | 35 | 50 | 34 | 0 | 0 | 0 | 0 | 110 | 0 | 17 | 0 | 0 | 0 | 233 | 0 | 377 | 0 | 200 | 0 | 0 | 0 |  | 7095 | 3921 | 11016 | 4351 | 912 | 2349 | 397 | 1266 | 875 | 50 | 438 | 199 | 164 | 0 | 15 | 1560.47 | 73.26
5:00 | 0 | 0 | 100 | 170 | 0 | 0 | 0 | 402 | 327 |  | 0 | 450 | 307 | 66 | 97 | 0 | 328 | 0 | 191 | 65 | 50 | 16 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 25 | 33 | 24 | 8 | 0 | 25 | 25 | 110 | 0 | 8 | 221 | 0 | 0 | 0 |  | 12 | 17 | 51 | 22 | 0 | 6 | 9 | 40 | 0 | 0 | 0 | 325 | 260 | 99 | 8 | 0 | 44 | 0 | 0 | 51 | 0 | 0 | 25 | 17 | 8 | 0 | 20 | 160 | 47 | 0 | 13 | 0 | 43 | 30 | 47 | 42 | 112 | 0 | 58 | 72 | 0 | 125 | 0 | 0 | 0 | 330 | 0 | 8 | 0 | 47 | 68 | 0 | 68 | 94 | 17 | 0 | 25 | 17 | 5 | 377 | 19 | 35 | 17 | 0 | 70 | 17 | 17 | 114 | 9 | 25 | 375 | 53 | 0 | 17 | 17 | 0 | 17 | 0 | 18 | 17 | 235 | 18 | 0 | 0 | 11 |  | 912 | 0 | 180 | 0 | 0 | 204 | 0 | 0 | 20 | 41 | 8 | 167 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 36 | 0 | 0 | 22 | 0 | 8 | 68 | 0 | 230 | 0 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 414 | 36 | 100 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 111 | 0 | 17 | 0 | 0 | 0 | 233 | 0 | 377 | 0 | 307 | 0 | 0 | 0 |  | 7051 | 3895 | 10946 | 4353 | 912 | 2360 | 262 | 1220 | 982 | 50 | 437 | 199 | 160 | 0 | 11 | 1436.32 | 73.25
6:00 | 0 | 0 | 100 | 170 | 0 | 0 | 0 | 401 | 327 |  | 0 | 450 | 302 | 67 | 97 | 0 | 326 | 0 | 189 | 65 | 50 | 16 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 18 | 33 | 24 | 8 | 0 | 25 | 25 | 110 | 0 | 8 | 220 | 0 | 0 | 0 |  | 12 | 17 | 51 | 22 | 0 | 6 | 9 | 38 | 0 | 0 | 0 | 340 | 260 | 93 | 8 | 0 | 44 | 0 | 0 | 51 | 0 | 0 | 25 | 17 | 8 | 0 | 20 | 142 | 47 | 0 | 13 | 0 | 43 | 30 | 47 | 45 | 112 | 0 | 57 | 72 | 0 | 125 | 0 | 0 | 0 | 325 | 0 | 8 | 0 | 47 | 0 | 0 | 68 | 0 | 17 | 0 | 25 | 17 | 6 | 378 | 19 | 35 | 17 | 0 | 70 | 17 | 17 | 44 | 9 | 12 | 349 | 53 | 0 | 17 | 17 | 0 | 17 | 2 | 18 | 17 | 222 | 18 | 0 | 0 | 7 |  | 912 | 0 | 185 | 0 | 0 | 203 | 0 | 0 | 15 | 41 | 8 | 165 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 35 | 0 | 0 | 22 | 0 | 8 | 66 | 0 | 230 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 414 | 36 | 0 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 111 | 0 | 17 | 0 | 3 | 0 | 231 | 0 | 377 | 0 | 307 | 0 | 0 | 0 |  | 6716 | 3750 | 10466 | 4256 | 912 | 2349 | 0 | 1138 | 980 | 50 | 434 | 193 | 142 | 5 | 7 | 1369.47 | 73.24
7:00 | 0 | 0 | 100 | 180 | 0 | 0 | 0 | 395 | 322 |  | 0 | 450 | 303 | 67 | 97 | 0 | 325 | 0 | 187 | 65 | 50 | 16 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 26 | 33 | 24 | 8 | 0 | 25 | 25 | 107 | 0 | 8 | 220 | 0 | 0 | 0 |  | 12 | 15 | 51 | 22 | 0 | 6 | 9 | 37 | 0 | 0 | 0 | 335 | 260 | 90 | 8 | 0 | 44 | 0 | 0 | 51 | 0 | 0 | 25 | 17 | 8 | 0 | 20 | 142 | 30 | 0 | 13 | 0 | 43 | 30 | 47 | 45 | 112 | 0 | 58 | 72 | 0 | 125 | 0 | 0 | 10 | 330 | 16 | 8 | 0 | 47 | 0 | 0 | 68 | 0 | 17 | 2 | 25 | 17 | 2 | 378 | 19 | 35 | 17 | 1 | 70 | 17 | 17 | 17 | 9 | 12 | 345 | 53 | 1 | 17 | 17 | 0 | 0 | 5 | 18 | 17 | 222 | 18 | 0 | 0 | 3 |  | 912 | 0 | 185 | 0 | 0 | 200 | 0 | 0 | 15 | 41 | 0 | 163 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 35 | 0 | 0 | 21 | 0 | 8 | 63 | 0 | 230 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 414 | 36 | 0 | 35 | 50 | 0 | 0 | 0 | 35 | 0 | 107 | 0 | 17 | 0 | 20 | 0 | 228 | 0 | 377 | 3 | 307 | 22 | 1 | 0 |  | 6673 | 3770 | 10443 | 4216 | 912 | 2352 | 0 | 1117 | 999 | 50 | 428 | 191 | 142 | 33 | 3 | 1439.185 | 73.23
8:00 | 0 | 0 | 100 | 180 | 0 | 0 | 0 | 397 | 322 |  | 0 | 450 | 299 | 66 | 96 | 0 | 320 | 0 | 183 | 65 | 50 | 16 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 26 | 33 | 24 | 8 | 0 | 25 | 25 | 110 | 0 | 8 | 218 | 0 | 0 | 0 |  | 12 | 15 | 51 | 22 | 0 | 6 | 9 | 8 | 0 | 0 | 0 | 335 | 260 | 93 | 8 | 0 | 43 | 0 | 0 | 51 | 0 | 0 | 25 | 20 | 8 | 0 | 19 | 158 | 30 | 0 | 19 | 0 | 43 | 30 | 47 | 45 | 112 | 0 | 57 | 72 | 0 | 126 | 0 | 0 | 10 | 320 | 16 | 8 | 0 | 47 | 0 | 0 | 68 | 0 | 17 | 4 | 25 | 17 | 3 | 378 | 19 | 35 | 17 | 2 | 70 | 17 | 17 | 17 | 9 | 12 | 345 | 53 | 1 | 17 | 17 | 0 | 0 | 13 | 17 | 17 | 222 | 18 | 0 | 0 | 13 |  | 912 | 0 | 180 | 0 | 0 | 200 | 0 | 0 | 15 | 25 | 0 | 163 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 35 | 0 | 0 | 19 | 0 | 8 | 65 | 0 | 230 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 414 | 36 | 0 | 35 | 50 | 17 | 0 | 1 | 35 | 0 | 107 | 0 | 17 | 0 | 39 | 0 | 226 | 0 | 377 | 14 | 307 | 72 | 13 | 0 |  | 6670 | 3901 | 10571 | 4261 | 912 | 2305 | 0 | 1133 | 1051 | 50 | 426 | 175 | 158 | 87 | 13 | 1364.695 | 73.22
9:00 | 0 | 0 | 100 | 180 | 0 | 0 | 0 | 396 | 321 |  | 0 | 450 | 307 | 64 | 96 | 0 | 325 | 0 | 190 | 70 | 74 | 16 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 25 | 33 | 24 | 8 | 0 | 25 | 25 | 111 | 0 | 8 | 220 | 0 | 0 | 0 |  | 12 | 16 | 51 | 22 | 0 | 6 | 9 | 2 | 0 | 0 | 0 | 280 | 260 | 107 | 8 | 0 | 37 | 0 | 0 | 51 | 0 | 0 | 0 | 20 | 8 | 0 | 20 | 158 | 27 | 0 | 16 | 0 | 43 | 30 | 47 | 46 | 112 | 0 | 58 | 72 | 0 | 126 | 0 | 0 | 10 | 320 | 16 | 8 | 0 | 47 | 0 | 0 | 67 | 0 | 17 | 4 | 25 | 17 | 5 | 378 | 19 | 35 | 17 | 1 | 70 | 17 | 17 | 17 | 9 | 12 | 351 | 53 | 4 | 17 | 17 | 0 | 10 | 17 | 18 | 17 | 232 | 18 | 0 | 0 | 14 |  | 912 | 0 | 180 | 0 | 0 | 200 | 0 | 0 | 14 | 25 | 0 | 92 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 27 | 0 | 0 | 19 | 0 | 8 | 66 | 0 | 230 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 414 | 36 | 0 | 35 | 50 | 33 | 0 | 2 | 35 | 0 | 108 | 0 | 17 | 0 | 67 | 0 | 230 | 0 | 372 | 22 | 307 | 159 | 49 | 0 |  | 6672 | 4096 | 10768 | 4266 | 912 | 2308 | 0 | 1163 | 1134 | 50 | 430 | 167 | 158 | 166 | 14 | 1558.56 | 73.21
10:00 | 0 | 0 | 99 | 180 | 0 | 0 | 0 | 398 | 322 |  | 0 | 450 | 310 | 60 | 96 | 0 | 320 | 0 | 189 | 75 | 74 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 18 | 33 | 30 | 8 | 0 | 25 | 25 | 110 | 0 | 8 | 219 | 0 | 0 | 0 |  | 12 | 16 | 51 | 22 | 0 | 6 | 9 | 2 | 0 | 0 | 0 | 280 | 260 | 86 | 8 | 0 | 38 | 0 | 0 | 51 | 0 | 0 | 0 | 20 | 8 | 0 | 20 | 156 | 25 | 0 | 16 | 1 | 43 | 30 | 47 | 46 | 112 | 0 | 60 | 72 | 0 | 126 | 0 | 0 | 10 | 300 | 0 | 0 | 0 | 47 | 0 | 0 | 68 | 0 | 17 | 13 | 25 | 17 | 5 | 352 | 19 | 35 | 17 | 0 | 70 | 17 | 17 | 80 | 9 | 12 | 351 | 70 | 11 | 17 | 17 | 0 | 17 | 21 | 18 | 17 | 218 | 36 | 0 | 0 | 14 |  | 913 | 0 | 175 | 0 | 0 | 200 | 0 | 0 | 14 | 25 | 0 | 85 | 23 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 22 | 0 | 0 | 17 | 0 | 8 | 67 | 0 | 230 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 414 | 50 | 0 | 35 | 50 | 34 | 0 | 5 | 35 | 0 | 107 | 0 | 17 | 3 | 73 | 0 | 229 | 0 | 371 | 28 | 307 | 269 | 112 | 0 |  | 6693 | 4298 | 10991 | 4160 | 913 | 2291 | 0 | 1287 | 1244 | 50 | 429 | 180 | 156 | 267 | 14 | 1536.595 | 73.2
11:00 | 0 | 0 | 100 | 170 | 0 | 0 | 0 | 393 | 322 |  | 0 | 450 | 305 | 72 | 96 | 12 | 316 | 0 | 185 | 75 | 74 | 16 | 55 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 18 | 33 | 30 | 8 | 0 | 25 | 25 | 100 | 0 | 8 | 219 | 0 | 0 | 0 |  | 12 | 20 | 51 | 22 | 0 | 6 | 9 | 2 | 0 | 0 | 0 | 280 | 260 | 90 | 8 | 0 | 35 | 0 | 0 | 51 | 0 | 0 | 0 | 20 | 8 | 0 | 12 | 170 | 24 | 0 | 16 | 1 | 43 | 30 | 47 | 43 | 112 | 0 | 48 | 72 | 0 | 126 | 0 | 0 | 10 | 290 | 0 | 0 | 0 | 47 | 0 | 0 | 68 | 0 | 20 | 13 | 25 | 17 | 6 | 314 | 19 | 35 | 17 | 0 | 70 | 17 | 17 | 98 | 9 | 25 | 351 | 72 | 14 | 35 | 17 | 0 | 17 | 30 | 19 | 17 | 208 | 36 | 0 | 0 | 16 |  | 911 | 0 | 155 | 0 | 0 | 200 | 0 | 0 | 14 | 25 | 0 | 81 | 22 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 30 | 0 | 0 | 17 | 0 | 8 | 62 | 0 | 230 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 414 | 53 | 0 | 35 | 50 | 28 | 0 | 7 | 35 | 0 | 107 | 0 | 17 | 3 | 93 | 5 | 226 | 0 | 371 | 30 | 307 | 486 | 179 | 0 |  | 6711 | 4565 | 11276 | 4020 | 911 | 2272 | 0 | 1393 | 1456 | 50 | 426 | 192 | 170 | 370 | 16 | 1550.92 | 73.19
12:00 | 0 | 0 | 100 | 170 | 0 | 0 | 0 | 396 | 322 |  | 0 | 450 | 300 | 73 | 95 | 15 | 312 | 0 | 182 | 75 | 74 | 16 | 51 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 20 | 0 | 33 | 30 | 8 | 0 | 25 | 25 | 85 | 0 | 8 | 215 | 0 | 0 | 0 |  | 12 | 16 | 48 | 10 | 0 | 10 | 9 | 2 | 0 | 0 | 0 | 320 | 260 | 104 | 8 | 0 | 35 | 0 | 0 | 51 | 0 | 0 | 0 | 20 | 8 | 0 | 21 | 174 | 24 | 0 | 16 | 2 | 43 | 30 | 47 | 43 | 112 | 0 | 48 | 73 | 0 | 126 | 0 | 0 | 10 | 325 | 0 | 8 | 0 | 47 | 300 | 0 | 68 | 95 | 17 | 9 | 25 | 17 | 5 | 303 | 19 | 35 | 34 | 3 | 70 | 17 | 17 | 79 | 9 | 25 | 355 | 72 | 22 | 35 | 17 | 0 | 17 | 31 | 52 | 17 | 227 | 36 | 0 | 0 | 18 |  | 912 | 0 | 145 | 0 | 16 | 194 | 0 | 0 | 14 | 25 | 0 | 81 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 36 | 0 | 0 | 17 | 0 | 8 | 62 | 0 | 230 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 377 | 54 | 0 | 35 | 50 | 34 | 0 | 7 | 35 | 0 | 108 | 0 | 17 | 5 | 78 | 35 | 222 | 0 | 371 | 21 | 307 | 683 | 175 | 0 |  | 7240 | 4736 | 11976 | 4045 | 912 | 2270 | 395 | 1499 | 1653 | 50 | 416 | 191 | 174 | 353 | 18 | 1264.42 | 73.18
13:00 | 0 | 0 | 100 | 160 | 0 | 0 | 0 | 393 | 322 |  | 0 | 450 | 300 | 73 | 95 | 15 | 312 | 0 | 183 | 75 | 74 | 16 | 55 | 0 | 0 | 0 | 0 | 35 | 17 | 19 | 20 | 10 | 33 | 30 | 8 | 0 | 25 | 25 | 90 | 0 | 8 | 214 | 0 | 0 | 0 |  | 12 | 16 | 48 | 22 | 0 | 32 | 9 | 5 | 0 | 0 | 0 | 310 | 260 | 113 | 8 | 0 | 35 | 0 | 0 | 51 | 0 | 0 | 0 | 20 | 11 | 0 | 18 | 170 | 12 | 0 | 16 | 2 | 43 | 30 | 47 | 46 | 112 | 0 | 48 | 72 | 0 | 126 | 0 | 0 | 10 | 325 | 0 | 8 | 0 | 47 | 301 | 0 | 68 | 97 | 17 | 12 | 25 | 17 | 5 | 314 | 19 | 35 | 34 | 1 | 70 | 17 | 17 | 98 | 9 | 25 | 360 | 72 | 31 | 35 | 17 | 0 | 17 | 30 | 54 | 17 | 227 | 36 | 0 | 0 | 16 |  | 913 | 0 | 135 | 0 | 16 | 193 | 0 | 0 | 14 | 20 | 8 | 81 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 35 | 0 | 0 | 17 | 0 | 8 | 62 | 0 | 230 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 365 | 54 | 119 | 35 | 50 | 28 | 0 | 5 | 35 | 0 | 108 | 0 | 17 | 4 | 93 | 35 | 221 | 0 | 371 | 26 | 307 | 687 | 108 | 0 |  | 7334 | 4779 | 12113 | 4055 | 913 | 2264 | 517 | 1560 | 1657 | 50 | 414 | 185 | 170 | 312 | 16 | 1372.335 | 73.18
14:00 | 0 | 0 | 100 | 160 | 0 | 0 | 0 | 393 | 322 |  | 0 | 450 | 305 | 72 | 92 | 15 | 309 | 0 | 183 | 75 | 74 | 16 | 55 | 0 | 0 | 0 | 0 | 35 | 35 | 19 | 20 | 23 | 33 | 28 | 8 | 0 | 25 | 25 | 90 | 0 | 8 | 219 | 0 | 0 | 0 |  | 12 | 16 | 48 | 22 | 0 | 37 | 9 | 3 | 0 | 0 | 0 | 280 | 260 | 103 | 8 | 0 | 43 | 0 | 0 | 51 | 0 | 14 | 0 | 20 | 11 | 17 | 20 | 182 | 12 | 0 | 16 | 1 | 43 | 30 | 47 | 50 | 112 | 0 | 48 | 73 | 0 | 126 | 0 | 0 | 10 | 330 | 16 | 8 | 0 | 47 | 301 | 0 | 68 | 95 | 17 | 10 | 25 | 17 | 6 | 300 | 19 | 35 | 47 | 5 | 70 | 17 | 17 | 98 | 9 | 25 | 370 | 72 | 35 | 35 | 17 | 0 | 17 | 27 | 54 | 17 | 227 | 36 | 0 | 0 | 17 |  | 913 | 0 | 130 | 0 | 0 | 190 | 0 | 0 | 0 | 20 | 0 | 82 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 35 | 0 | 0 | 17 | 0 | 8 | 60 | 0 | 230 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 347 | 54 | 188 | 35 | 50 | 34 | 0 | 5 | 35 | 0 | 108 | 0 | 17 | 4 | 83 | 36 | 219 | 0 | 371 | 26 | 307 | 750 | 155 | 0 |  | 7419 | 4885 | 12304 | 4060 | 913 | 2259 | 584 | 1576 | 1718 | 50 | 409 | 185 | 182 | 351 | 17 | 1333.18 | 73.19
15:00 | 0 | 0 | 100 | 160 | 0 | 0 | 0 | 391 | 321 |  | 0 | 450 | 300 | 72 | 90 | 15 | 306 | 0 | 183 | 75 | 74 | 16 | 54 | 0 | 0 | 0 | 0 | 35 | 35 | 19 | 20 | 23 | 33 | 28 | 8 | 0 | 25 | 25 | 90 | 0 | 8 | 217 | 0 | 0 | 0 |  | 12 | 16 | 51 | 22 | 0 | 39 | 9 | 2 | 0 | 0 | 0 | 300 | 260 | 108 | 8 | 0 | 42 | 0 | 0 | 51 | 0 | 31 | 1 | 20 | 11 | 17 | 15 | 166 | 15 | 0 | 16 | 2 | 43 | 30 | 44 | 46 | 112 | 0 | 50 | 73 | 0 | 126 | 0 | 0 | 10 | 334 | 16 | 8 | 0 | 47 | 205 | 0 | 68 | 60 | 17 | 7 | 25 | 17 | 5 | 324 | 19 | 35 | 68 | 2 | 70 | 17 | 17 | 98 | 9 | 25 | 391 | 72 | 9 | 35 | 17 | 0 | 17 | 20 | 58 | 17 | 227 | 36 | 0 | 0 | 12 |  | 913 | 0 | 130 | 0 | 21 | 192 | 0 | 0 | 0 | 20 | 0 | 82 | 28 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 29 | 0 | 0 | 15 | 0 | 8 | 62 | 0 | 230 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 338 | 54 | 150 | 35 | 50 | 34 | 0 | 5 | 35 | 0 | 106 | 0 | 17 | 3 | 68 | 36 | 219 | 0 | 371 | 19 | 307 | 756 | 108 | 0 |  | 7325 | 4790 | 12115 | 4121 | 913 | 2238 | 415 | 1621 | 1726 | 50 | 411 | 199 | 166 | 243 | 12 | 1656.925 | 0
16:00 | 0 | 0 | 100 | 160 | 0 | 0 | 0 | 392 | 311 |  | 0 | 450 | 305 | 73 | 90 | 30 | 310 | 0 | 187 | 75 | 74 | 16 | 53 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 20 | 23 | 33 | 28 | 8 | 0 | 25 | 25 | 85 | 0 | 8 | 218 | 0 | 0 | 0 |  | 12 | 32 | 48 | 22 | 0 | 39 | 9 | 4 | 0 | 0 | 0 | 280 | 260 | 110 | 8 | 0 | 39 | 0 | 0 | 51 | 0 | 26 | 8 | 17 | 11 | 26 | 20 | 168 | 17 | 0 | 16 | 1 | 43 | 30 | 50 | 49 | 112 | 0 | 50 | 73 | 0 | 126 | 0 | 0 | 10 | 335 | 16 | 8 | 0 | 47 | 95 | 0 | 69 | 25 | 17 | 2 | 38 | 17 | 5 | 327 | 18 | 35 | 63 | 2 | 70 | 17 | 20 | 34 | 9 | 25 | 390 | 72 | 8 | 35 | 17 | 0 | 17 | 16 | 76 | 17 | 227 | 18 | 0 | 0 | 14 |  | 912 | 0 | 130 | 0 | 37 | 192 | 0 | 0 | 0 | 20 | 0 | 82 | 27 | 32 | 0 | 0 | 0 | 0 | 5 | 6 | 14 | 0 | 27 | 0 | 0 | 15 | 0 | 8 | 63 | 0 | 230 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 348 | 54 | 40 | 35 | 50 | 34 | 0 | 1 | 35 | 0 | 105 | 0 | 17 | 2 | 47 | 36 | 219 | 0 | 371 | 4 | 260 | 759 | 61 | 0 |  | 7173 | 4582 | 11755 | 4121 | 912 | 2253 | 160 | 1641 | 1683 | 50 | 411 | 198 | 168 | 144 | 14 | 1905.225 | 73.16
17:00 | 0 | 0 | 100 | 160 | 0 | 0 | 0 | 396 | 322 |  | 0 | 450 | 305 | 75 | 90 | 30 | 314 | 0 | 189 | 75 | 82 | 16 | 60 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 20 | 23 | 33 | 28 | 8 | 0 | 25 | 25 | 80 | 0 | 16 | 220 | 0 | 0 | 0 |  | 12 | 40 | 51 | 23 | 0 | 39 | 9 | 4 | 0 | 0 | 0 | 280 | 260 | 114 | 8 | 0 | 37 | 0 | 0 | 51 | 0 | 26 | 8 | 20 | 11 | 32 | 20 | 166 | 19 | 0 | 16 | 0 | 43 | 30 | 50 | 49 | 112 | 0 | 50 | 73 | 0 | 126 | 0 | 0 | 10 | 335 | 16 | 8 | 0 | 47 | 0 | 0 | 68 | 0 | 17 | 0 | 30 | 17 | 7 | 352 | 18 | 52 | 68 | 1 | 70 | 17 | 17 | 34 | 9 | 25 | 390 | 72 | 11 | 35 | 17 | 0 | 17 | 8 | 75 | 27 | 228 | 18 | 0 | 0 | 12 |  | 911 | 0 | 135 | 0 | 55 | 180 | 0 | 0 | 0 | 20 | 8 | 82 | 24 | 32 | 0 | 0 | 0 | 0 | 28 | 0 | 14 | 0 | 21 | 0 | 0 | 16 | 0 | 8 | 62 | 0 | 230 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 361 | 54 | 0 | 35 | 50 | 48 | 0 | 1 | 35 | 0 | 101 | 0 | 17 | 1 | 15 | 36 | 170 | 0 | 370 | 6 | 260 | 754 | 26 | 0 |  | 7155 | 4470 | 11625 | 4172 | 911 | 2271 | 0 | 1728 | 1676 | 50 | 350 | 220 | 166 | 69 | 12 | 1695.125 | 73.15
18:00 | 0 | 0 | 100 | 160 | 0 | 0 | 0 | 379 | 281 |  | 0 | 400 | 288 | 72 | 90 | 30 | 320 | 0 | 181 | 75 | 91 | 16 | 64 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 20 | 0 | 33 | 28 | 9 | 0 | 25 | 25 | 85 | 0 | 16 | 223 | 0 | 0 | 0 |  | 12 | 40 | 51 | 23 | 0 | 39 | 9 | 3 | 0 | 0 | 0 | 280 | 260 | 117 | 8 | 0 | 37 | 0 | 0 | 51 | 0 | 27 | 8 | 20 | 11 | 30 | 20 | 158 | 29 | 0 | 18 | 0 | 43 | 30 | 50 | 49 | 112 | 0 | 50 | 73 | 0 | 126 | 0 | 0 | 10 | 340 | 16 | 8 | 0 | 50 | 0 | 0 | 67 | 0 | 35 | 1 | 30 | 17 | 13 | 338 | 18 | 52 | 68 | 0 | 120 | 17 | 23 | 34 | 55 | 38 | 340 | 92 | 4 | 35 | 20 | 0 | 17 | 3 | 75 | 35 | 228 | 18 | 0 | 0 | 15 |  | 912 | 0 | 135 | 0 | 74 | 145 | 0 | 0 | 0 | 40 | 8 | 110 | 21 | 32 | 0 | 0 | 0 | 0 | 28 | 0 | 14 | 25 | 28 | 0 | 35 | 16 | 0 | 8 | 65 | 0 | 230 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 320 | 54 | 0 | 35 | 85 | 56 | 0 | 1 | 40 | 0 | 98 | 0 | 17 | 0 | 7 | 40 | 150 | 0 | 377 | 3 | 260 | 760 | 12 | 0 |  | 7151 | 4547 | 11698 | 4117 | 912 | 2120 | 0 | 2025 | 1692 | 50 | 295 | 283 | 158 | 31 | 15 | 1338.91 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 100 | 160 | 0 | 0 | 0 | 366 | 327 |  | 0 | 450 | 300 | 73 | 92 | 15 | 310 | 0 | 180 | 75 | 91 | 115 | 66 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 20 | 0 | 33 | 30 | 24 | 0 | 25 | 25 | 90 | 0 | 25 | 214 | 0 | 0 | 0 |  | 12 | 32 | 51 | 23 | 0 | 46 | 9 | 13 | 0 | 0 | 0 | 325 | 260 | 115 | 8 | 0 | 37 | 0 | 0 | 51 | 0 | 30 | 34 | 20 | 11 | 33 | 20 | 174 | 31 | 0 | 19 | 0 | 43 | 30 | 50 | 46 | 112 | 0 | 50 | 73 | 0 | 126 | 0 | 0 | 10 | 280 | 22 | 8 | 0 | 135 | 115 | 0 | 87 | 26 | 135 | 0 | 38 | 17 | 47 | 273 | 85 | 88 | 68 | 0 | 292 | 17 | 34 | 34 | 95 | 38 | 372 | 92 | 0 | 86 | 68 | 0 | 17 | 0 | 75 | 35 | 231 | 18 | 0 | 0 | 11 |  | 902 | 0 | 135 | 0 | 92 | 170 | 0 | 0 | 0 | 61 | 32 | 117 | 30 | 48 | 0 | 0 | 0 | 0 | 28 | 46 | 14 | 34 | 28 | 15 | 35 | 16 | 0 | 8 | 66 | 0 | 230 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 365 | 54 | 0 | 35 | 85 | 56 | 0 | 0 | 55 | 0 | 106 | 0 | 150 | 0 | 0 | 109 | 224 | 0 | 377 | 0 | 260 | 752 | 0 | 0 |  | 8203 | 5042 | 13245 | 4124 | 902 | 2237 | 141 | 3083 | 1685 | 50 | 394 | 444 | 174 | 0 | 11 | 912.025 | 0
19:30 | 0 | 0 | 100 | 160 | 0 | 0 | 0 | 370 | 311 |  | 0 | 450 | 257 | 74 | 92 | 15 | 290 | 0 | 195 | 75 | 91 | 115 | 64 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 20 | 24 | 33 | 30 | 24 | 0 | 25 | 25 | 85 | 0 | 25 | 223 | 0 | 0 | 0 |  | 12 | 40 | 51 | 23 | 0 | 46 | 9 | 13 | 0 | 0 | 0 | 280 | 260 | 114 | 8 | 0 | 37 | 0 | 0 | 51 | 0 | 30 | 43 | 20 | 11 | 32 | 20 | 162 | 31 | 0 | 19 | 0 | 43 | 30 | 50 | 46 | 112 | 0 | 50 | 73 | 0 | 126 | 0 | 0 | 10 | 250 | 22 | 8 | 0 | 148 | 55 | 0 | 87 | 94 | 135 | 0 | 38 | 17 | 120 | 247 | 85 | 88 | 68 | 0 | 292 | 17 | 34 | 34 | 95 | 38 | 325 | 91 | 0 | 90 | 68 | 0 | 17 | 0 | 94 | 35 | 222 | 104 | 0 | 0 | 9 |  | 903 | 0 | 140 | 0 | 91 | 200 | 0 | 0 | 7 | 61 | 32 | 171 | 32 | 48 | 0 | 0 | 0 | 0 | 28 | 64 | 14 | 34 | 28 | 43 | 35 | 21 | 0 | 8 | 67 | 0 | 230 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 370 | 65 | 96 | 50 | 85 | 56 | 0 | 0 | 55 | 0 | 97 | 0 | 150 | 0 | 0 | 113 | 226 | 0 | 369 | 0 | 260 | 752 | 0 | 0 |  | 8216 | 5311 | 13527 | 4084 | 903 | 2151 | 245 | 3256 | 1678 | 50 | 426 | 563 | 162 | 0 | 9 | 1024.715 | 0
20:00 | 0 | 0 | 100 | 160 | 0 | 0 | 0 | 380 | 302 |  | 0 | 450 | 305 | 72 | 94 | 15 | 290 | 0 | 189 | 75 | 91 | 115 | 60 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 20 | 24 | 33 | 30 | 24 | 0 | 25 | 25 | 100 | 0 | 25 | 220 | 0 | 0 | 0 |  | 12 | 40 | 51 | 23 | 0 | 46 | 9 | 24 | 0 | 0 | 0 | 280 | 260 | 118 | 8 | 0 | 39 | 0 | 0 | 51 | 0 | 35 | 43 | 20 | 11 | 33 | 20 | 168 | 31 | 0 | 19 | 0 | 43 | 30 | 50 | 46 | 112 | 0 | 50 | 73 | 0 | 126 | 0 | 0 | 10 | 270 | 20 | 11 | 0 | 147 | 54 | 0 | 88 | 60 | 133 | 0 | 38 | 17 | 104 | 288 | 85 | 88 | 68 | 0 | 300 | 17 | 34 | 34 | 95 | 38 | 391 | 92 | 0 | 90 | 68 | 0 | 17 | 0 | 91 | 35 | 228 | 163 | 0 | 0 | 8 |  | 903 | 0 | 140 | 0 | 91 | 200 | 0 | 0 | 18 | 72 | 32 | 172 | 34 | 48 | 0 | 0 | 0 | 0 | 28 | 77 | 14 | 34 | 36 | 43 | 35 | 21 | 0 | 8 | 67 | 0 | 230 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 378 | 73 | 20 | 50 | 85 | 56 | 0 | 0 | 55 | 0 | 108 | 0 | 150 | 0 | 0 | 115 | 150 | 0 | 376 | 0 | 260 | 751 | 0 | 0 |  | 8441 | 5240 | 13681 | 4222 | 903 | 2242 | 134 | 3250 | 1684 | 50 | 350 | 670 | 168 | 0 | 8 | 1068.645 | 0
21:00 | 0 | 0 | 100 | 160 | 0 | 0 | 0 | 390 | 332 |  | 0 | 450 | 304 | 73 | 94 | 15 | 324 | 0 | 191 | 75 | 91 | 115 | 59 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 20 | 24 | 33 | 30 | 24 | 0 | 25 | 25 | 105 | 0 | 25 | 219 | 0 | 0 | 0 |  | 12 | 40 | 51 | 23 | 0 | 46 | 9 | 24 | 0 | 0 | 0 | 280 | 260 | 120 | 8 | 0 | 39 | 0 | 0 | 51 | 0 | 36 | 43 | 20 | 11 | 33 | 20 | 160 | 48 | 0 | 19 | 0 | 43 | 30 | 50 | 46 | 112 | 0 | 50 | 69 | 0 | 126 | 0 | 0 | 10 | 300 | 13 | 11 | 0 | 147 | 300 | 0 | 87 | 97 | 135 | 0 | 38 | 17 | 125 | 309 | 85 | 88 | 68 | 0 | 300 | 17 | 34 | 34 | 95 | 38 | 260 | 92 | 0 | 90 | 68 | 0 | 17 | 0 | 94 | 35 | 228 | 163 | 0 | 0 | 7 |  | 807 | 0 | 150 | 0 | 92 | 200 | 0 | 0 | 24 | 70 | 32 | 173 | 35 | 48 | 0 | 0 | 0 | 4 | 28 | 80 | 14 | 34 | 35 | 43 | 35 | 21 | 0 | 8 | 67 | 0 | 230 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 379 | 73 | 108 | 50 | 85 | 56 | 0 | 0 | 55 | 0 | 109 | 0 | 150 | 0 | 0 | 115 | 229 | 0 | 376 | 0 | 307 | 748 | 0 | 0 |  | 8748 | 5381 | 14129 | 4186 | 807 | 2300 | 505 | 3276 | 1728 | 50 | 429 | 681 | 160 | 0 | 7 | 831.805 | 0
22:00 | 0 | 0 | 100 | 160 | 0 | 0 | 0 | 400 | 321 |  | 0 | 450 | 306 | 59 | 94 | 0 | 324 | 0 | 195 | 75 | 82 | 115 | 55 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 20 | 24 | 33 | 30 | 24 | 0 | 25 | 0 | 105 | 0 | 25 | 224 | 0 | 0 | 0 |  | 12 | 40 | 51 | 23 | 0 | 46 | 9 | 35 | 0 | 0 | 0 | 280 | 260 | 116 | 8 | 0 | 40 | 0 | 0 | 51 | 0 | 36 | 30 | 20 | 11 | 32 | 20 | 160 | 49 | 0 | 19 | 0 | 43 | 30 | 50 | 49 | 112 | 0 | 50 | 69 | 0 | 126 | 0 | 0 | 10 | 305 | 13 | 11 | 0 | 147 | 305 | 0 | 88 | 98 | 135 | 0 | 38 | 17 | 135 | 351 | 82 | 88 | 68 | 0 | 123 | 17 | 34 | 34 | 95 | 38 | 260 | 91 | 0 | 90 | 68 | 0 | 17 | 0 | 76 | 35 | 230 | 108 | 0 | 0 | 11 |  | 787 | 0 | 150 | 0 | 93 | 203 | 0 | 0 | 24 | 60 | 32 | 170 | 36 | 48 | 0 | 0 | 0 | 21 | 28 | 80 | 14 | 34 | 35 | 43 | 35 | 21 | 0 | 8 | 67 | 0 | 230 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 356 | 72 | 190 | 50 | 85 | 49 | 0 | 0 | 55 | 0 | 110 | 0 | 150 | 0 | 0 | 115 | 230 | 0 | 376 | 0 | 307 | 750 | 0 | 0 |  | 8465 | 5426 | 13891 | 4244 | 787 | 2289 | 593 | 2986 | 1730 | 25 | 433 | 633 | 160 | 0 | 11 | 963.595 | 73.1
23:00 | 0 | 0 | 100 | 160 | 0 | 0 | 0 | 401 | 323 |  | 0 | 450 | 307 | 49 | 94 | 0 | 326 | 0 | 191 | 55 | 41 | 48 | 68 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 20 | 24 | 33 | 30 | 24 | 0 | 25 | 0 | 105 | 0 | 8 | 222 | 0 | 0 | 0 |  | 12 | 40 | 51 | 23 | 0 | 47 | 9 | 36 | 0 | 0 | 0 | 280 | 260 | 119 | 8 | 0 | 40 | 0 | 0 | 51 | 0 | 0 | 25 | 20 | 11 | 32 | 21 | 174 | 48 | 0 | 14 | 0 | 42 | 30 | 50 | 49 | 112 | 0 | 50 | 0 | 0 | 126 | 0 | 0 | 10 | 300 | 13 | 0 | 0 | 147 | 303 | 0 | 69 | 97 | 74 | 0 | 38 | 17 | 38 | 340 | 18 | 88 | 54 | 0 | 87 | 17 | 34 | 34 | 28 | 38 | 260 | 79 | 0 | 90 | 68 | 0 | 17 | 0 | 56 | 35 | 230 | 54 | 0 | 0 | 6 |  | 743 | 0 | 150 | 0 | 62 | 200 | 0 | 0 | 24 | 53 | 32 | 170 | 36 | 32 | 0 | 0 | 0 | 21 | 28 | 72 | 14 | 34 | 35 | 43 | 35 | 22 | 0 | 8 | 67 | 0 | 230 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 402 | 72 | 190 | 35 | 85 | 42 | 0 | 0 | 35 | 0 | 109 | 0 | 150 | 0 | 0 | 75 | 231 | 0 | 376 | 0 | 307 | 754 | 0 | 0 |  | 7747 | 5287 | 13034 | 4217 | 743 | 2265 | 590 | 2388 | 1734 | 25 | 431 | 461 | 174 | 0 | 6 | 1686.53 | 73.09
24:00 | 0 | 0 | 100 | 160 | 0 | 0 | 0 | 401 | 322 |  | 0 | 450 | 299 | 58 | 94 | 0 | 322 | 0 | 190 | 50 | 50 | 48 | 68 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 20 | 25 | 33 | 30 | 8 | 0 | 25 | 0 | 104 | 0 | 8 | 219 | 0 | 0 | 0 |  | 12 | 31 | 51 | 23 | 0 | 8 | 9 | 36 | 0 | 0 | 0 | 300 | 260 | 111 | 8 | 0 | 40 | 0 | 0 | 51 | 0 | 0 | 25 | 20 | 11 | 32 | 21 | 172 | 48 | 0 | 13 | 0 | 42 | 30 | 50 | 49 | 112 | 0 | 48 | 66 | 0 | 126 | 0 | 0 | 10 | 315 | 13 | 11 | 0 | 148 | 298 | 0 | 68 | 96 | 17 | 0 | 25 | 17 | 5 | 372 | 18 | 35 | 17 | 0 | 88 | 17 | 17 | 34 | 12 | 25 | 260 | 57 | 0 | 17 | 68 | 0 | 17 | 0 | 36 | 19 | 223 | 18 | 0 | 0 | 13 |  | 731 | 0 | 150 | 0 | 62 | 200 | 0 | 0 | 20 | 53 | 32 | 169 | 37 | 16 | 0 | 0 | 0 | 21 | 28 | 65 | 14 | 34 | 35 | 0 | 35 | 21 | 0 | 8 | 68 | 0 | 230 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 414 | 72 | 190 | 35 | 50 | 34 | 0 | 0 | 35 | 0 | 107 | 0 | 150 | 0 | 0 | 35 | 231 | 0 | 376 | 0 | 307 | 749 | 0 | 0 |  | 7329 | 5129 | 12458 | 4255 | 731 | 2347 | 584 | 1765 | 1730 | 25 | 431 | 405 | 172 | 0 | 13 | 1950.11 | 73.08
KWH | 0 | 0 | 2401406 | 4032000 | 0 | 0 | 0 | 9598970 | 7752000 |  | 0 | 9927500 | 7284393 | 1577280 | 2160764 | 213069 | 7672594 | 0 | 4755000 | 1599360 | 1592784 | 740640 | 1330020 | 0 | 0 | 0 | 260280 | 468709 | 465660 | 322488 | 480000 | 500580 | 811400 | 662900 | 287040 | 0 | 603000 | 556000 | 2300000 | 0 | 280171 | 5184438 | 0 | 0 | 0 |  | 297600 | 455232 | 1207260 | 512520 | 0 | 598560 | 214320 | 463680 | 0 | 0 | 0 | 7702500 | 6397000 | 2571000 | 200727 | 0 | 957528 | 0 | 0 | 1133612 | 0 | 242352 | 428578 | 453744 | 220140 | 299300 | 459910 | 3855360 | 737280 | 0 | 357732 | 10100 | 1017000 | 676920 | 1173000 | 1119456 | 2532927 | 0 | 1274016 | 1679040 | 0 | 3011380 | 0 | 0 | 239580 | 7719000 | 322224 | 188156 | 0 | 1763891 | 3437439 | 0 | 1708800 | 1376367 | 972864 | 88695 | 672000 | 427200 | 582109 | 8270000 | 698400 | 1119360 | 940909 | 14166 | 2461418 | 448759 | 527743 | 1565220 | 571200 | 603840 | 8575000 | 1642560 | 160200 | 956160 | 745200 | 0 | 400320 | 222532 | 1113600 | 550800 | 5494400 | 948436 | 0 | 0 | 296208 |  | 21262545 | 0 | 3862368 | 0 | 689280 | 4740077 | 0 | 0 | 298080 | 862464 | 239250 | 3191078 | 664009 | 698976 | 0 | 0 | 0 | 59344 | 196631 | 411072 | 328420 | 205540 | 719606 | 172291 | 275250 | 403200 | 0 | 189252 | 1515490 | 0 | 5573500 | 0 | 0 | 3581236 | 0 | 0 | 0 | 0 | 0 | 3808918 | 0 | 9261890 | 1226880 | 2280951 | 968352 | 1487520 | 813091 | 0 | 37859 | 810912 | 0 | 2549236 | 0 | 1209600 | 29160 | 712080 | 881664 | 5114782 | 0 | 8952727 | 207140 | 6654500 | 10303636 | 1020700 | 0 |  | 175904976 | 108470557 | 284375533 | 102554178 | 21262545 | 54103250 | 7094757 | 42276524 | 32999853 | 1159000 | 9854859 | 6416367 | 3855360 | 2502632 | 296208 | 0
Fuel Cost | 0 | 0 | 3506052.76 | 6007680 | 0 | 0 | 0 | 10078918.5 | 8372160 |  | 0 | 10820975 | 8085676.23 | 17633990.4 | 28630123 | 2823164.25 | 8593305.28 | 0 | 8321250 | 23382643.2 | 22410470.88 | 12005774.4 | 12262784.4 | 0 | 0 | 0 | 3310761.6 | 6327571.5 | 6244500.6 | 241866 | 360000 | 0 | 0 | 0 | 4882550.4 | 0 | 162810 | 150120 | 4347000 | 0 | 4580795.85 | 5391815.52 | 0 | 0 | 0 |  | 3883680 | 7593269.76 | 20547565.2 | 6924145.2 | 0 | 6925339.2 | 272186.4 | 1544054.4 | 0 | 0 | 0 | 8549775 | 6972730 | 2982360 | 258937.83 | 0 | 1082006.64 | 0 | 0 | 1893132.04 | 0 | 4185419.04 | 5764374.1 | 621629.28 | 165105 | 523775 | 344932.5 | 27681484.8 | 803635.2 | 0 | 486515.52 | 160994 | 1393290 | 893534.4 | 2041020 | 1936658.88 | 2912866.05 | 0 | 2471591.04 | 3828211.2 | 0 | 3041493.8 | 0 | 0 | 474368.4 | 7719000 | 241668 | 142998.56 | 0 | 24077112.15 | 72048721.44 | 0 | 23034624 | 28449505.89 | 13474166.4 | 1036844.55 | 6935040 | 5835552 | 7724586.43 | 7608400 | 8492544 | 16185945.6 | 11902498.85 | 0 | 28897047.32 | 4886985.51 | 5609908.09 | 21240035.4 | 7362768 | 7113235.2 | 7889000 | 21271152 | 2314890 | 12133670.4 | 8480376 | 0 | 5228179.2 | 2659257.4 | 16670592 | 7254036 | 0 | 0 | 0 | 0 | 0 |  | 63787635 | 0 | 4325852.16 | 0 | 7175404.8 | 78211270.5 | 0 | 0 | 5368420.8 | 15524352 | 3438022.5 | 3574007.36 | 1288177.46 | 7618838.4 | 0 | 0 | 0 | 995198.88 | 3439076.19 | 6429166.08 | 2528834 | 3403742.4 | 12168537.46 | 2348326.33 | 4643467.5 | 834624 | 0 | 143263.764 | 8804996.9 | 0 | 29483815 | 0 | 0 | 4154233.76 | 0 | 0 | 0 | 0 | 0 | 4418344.88 | 0 | 9169271.1 | 16489267.2 | 47831542.47 | 11455604.16 | 21494664 | 10326255.7 | 0 | 418341.95 | 9844471.68 | 0 | 2600220.72 | 0 | 8951040 | 329799.6 | 8352698.4 | 13515909.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 742015180.04 | 434886694.224 | 1176901874.264 | 109950216.324 | 63787635 | 63779353.31 | 148329769.8 | 538387329.42 | 38288811.9 | 312930 | 78211270.5 | 92900247.31 | 27681484.8 | 15272825.9 | 0 | 0
Yesterday Day Peak | 0 | 0 | 100 | 170 | 0 | 0 | 0 | 396 | 322 |  | 0 | 450 | 300 | 73 | 95 | 15 | 312 | 0 | 182 | 75 | 74 | 16 | 51 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 20 | 0 | 33 | 30 | 8 | 0 | 25 | 25 | 85 | 0 | 8 | 215 | 0 | 0 | 0 |  | 12 | 16 | 48 | 10 | 0 | 10 | 9 | 2 | 0 | 0 | 0 | 320 | 260 | 104 | 8 | 0 | 35 | 0 | 0 | 51 | 0 | 0 | 0 | 20 | 8 | 0 | 21 | 174 | 24 | 0 | 16 | 2 | 43 | 30 | 47 | 43 | 112 | 0 | 48 | 73 | 0 | 126 | 0 | 0 | 10 | 325 | 0 | 8 | 0 | 47 | 300 | 0 | 68 | 95 | 17 | 9 | 25 | 17 | 5 | 303 | 19 | 35 | 34 | 3 | 70 | 17 | 17 | 79 | 9 | 25 | 355 | 72 | 22 | 35 | 17 | 0 | 17 | 31 | 52 | 17 | 227 | 36 | 0 | 0 | 18 |  | 912 | 0 | 145 | 0 | 16 | 194 | 0 | 0 | 14 | 25 | 0 | 81 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 36 | 0 | 0 | 17 | 0 | 8 | 62 | 0 | 230 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 377 | 54 | 0 | 35 | 50 | 34 | 0 | 7 | 35 | 0 | 108 | 0 | 17 | 5 | 78 | 35 | 222 | 0 | 371 | 21 | 307 | 683 | 175 | 0 |  | 11976 | DayPeak
Yesterday Evening Peak | 0 | 0 | 100 | 160 | 0 | 0 | 0 | 390 | 332 | 0 | 0 | 450 | 304 | 73 | 94 | 15 | 324 | 0 | 191 | 75 | 91 | 115 | 59 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 20 | 24 | 33 | 30 | 24 | 0 | 25 | 25 | 105 | 0 | 25 | 219 | 0 | 0 | 0 | 0 | 12 | 40 | 51 | 23 | 0 | 46 | 9 | 24 | 0 | 0 | 0 | 280 | 260 | 120 | 8 | 0 | 39 | 0 | 0 | 51 | 0 | 36 | 43 | 20 | 11 | 33 | 20 | 160 | 48 | 0 | 19 | 0 | 43 | 30 | 50 | 46 | 112 | 0 | 50 | 69 | 0 | 126 | 0 | 0 | 10 | 300 | 13 | 11 | 0 | 147 | 300 | 0 | 87 | 97 | 135 | 0 | 38 | 17 | 125 | 309 | 85 | 88 | 68 | 0 | 300 | 17 | 34 | 34 | 95 | 38 | 260 | 92 | 0 | 90 | 68 | 0 | 17 | 0 | 94 | 35 | 228 | 163 | 0 | 0 | 7 |  | 807 | 0 | 150 | 0 | 92 | 200 | 0 | 0 | 24 | 70 | 32 | 173 | 35 | 48 | 0 | 0 | 0 | 4 | 28 | 80 | 14 | 34 | 35 | 43 | 35 | 21 | 0 | 8 | 67 | 0 | 230 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 379 | 73 | 108 | 50 | 85 | 56 | 0 | 0 | 55 | 0 | 109 | 0 | 150 | 0 | 0 | 115 | 229 | 0 | 376 | 0 | 307 | 748 | 0 | 0 |  | 14129 | EvPeak
Forecast for Evening | 0 | 0 | 100 | 160 | 0 | 0 | 0 | 400 | 330 | 0 | 0 | 450 | 305 | 93 | 97 | 30 | 320 | 0 | 190 | 92 | 92 | 115 | 59 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 20 | 24 | 33 | 30 | 50 | 0 | 30 | 25 | 110 | 0 | 25 | 225 |  | 0 | 0 | 0 | 12 | 40 | 51 | 33 | 0 | 50 | 9 | 25 | 0 | 0 | 0 | 300 | 280 | 120 | 8 | 0 | 40 | 0 | 0 | 51 | 0 | 40 | 43 | 20 | 11 | 33 | 20 | 152 | 50 | 0 | 19 | 0 | 43 | 30 | 50 | 45 | 112 | 0 | 60 | 76 | 0 | 125 | 0 | 0 | 10 | 320 | 13 | 11 | 0 | 145 | 300 | 0 | 86 | 100 | 149 | 0 | 50 | 17 | 150 | 0 | 85 | 105 | 105 | 0 | 285 | 17 | 34 | 114 | 115 | 50 | 400 | 92 | 0 | 90 | 68 | 0 | 17 |  | 97 | 35 | 230 | 163 |  | 0 | 10 |  | 918 | 0 | 185 |  | 92 | 200 | 0 | 0 | 25 | 72 | 40 | 170 | 35 | 48 | 0 | 0 | 0 | 25 | 35 | 80 | 28 | 34 | 35 | 43 | 35 | 22 | 0 | 8 | 70 | 0 | 230 | 16 | 0 | 165 |  | 0 | 0 | 0 | 0 | 150 | 0 | 414 | 73 | 200 | 95 | 85 | 71 | 0 | 0 | 95 | 0 | 110 |  | 150 |  |  | 115 | 330 |  | 376 |  | 200 | 748 |  | 0
Forecast for Day | 0 | 0 | 100 | 160 | 0 | 0 | 0 | 400 | 330 | 0 | 0 | 450 | 305 | 66 | 96 | 0 | 320 | 0 | 190 | 68 | 92 | 32 | 44 | 0 | 0 | 0 | 0 | 35 | 35 | 19 | 20 | 24 | 33 | 24 | 8 | 0 | 25 | 25 | 110 | 0 | 8 | 225 |  | 0 | 0 | 0 | 12 | 30 | 51 | 33 | 0 | 50 | 9 | 10 | 0 | 0 | 0 | 300 | 260 | 110 | 8 | 0 | 40 | 0 | 0 | 51 | 0 | 40 | 8 | 20 | 11 | 33 | 20 | 135 | 50 | 0 | 19 | 1.6 | 43 | 30 | 50 | 45 | 112 | 0 | 60 | 72 | 0 | 125 | 0 | 0 | 10 | 300 | 13 | 11 | 0 | 45 | 300 | 0 | 68 | 100 | 17 | 20 | 25 | 17 | 5 | 0 | 19 | 105 | 34 | 5 | 70 | 17 | 17 | 100 | 9 | 25 | 400 | 53 | 50 | 35 | 34 | 0 | 17 | 30 | 72 | 17 | 225 | 72 |  | 0 | 13 |  | 918 | 0 | 185 | 0 | 46 | 200 | 0 | 0 | 15 | 36 | 8 | 170 | 21 | 16 | 0 | 0 | 0 | 0 | 30 | 40 | 28 | 25 | 35 | 0 | 35 | 22 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 414 | 72 | 0 | 35 | 50 | 35 | 0 | 8 | 35 | 0 | 110 |  | 17 | 6 | 100 | 35 | 200 |  | 370 | 30 | 200 | 748 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 100 | 160 | 0 | 0 | 0 | 406 | 327 | 0 | 0 | 450 | 305 | 69 | 95 | 0 | 321 | 0 | 189 | 50 | 50 | 16 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 24 | 25 | 15 | 8 | 0 | 25 | 0 | 113 | 0 | 8 | 222 | 0 | 0 | 0 | 0 | 12 | 31 | 51 | 23 | 0 | 6 | 9 | 9 | 0 | 0 | 0 | 335 | 260 | 107 | 8 | 0 | 39 | 0 | 0 | 51 | 0 | 0 | 8 | 20 | 0 | 24 | 20 | 136 | 25 | 0 | 16 | 1 | 42 | 30 | 47 | 49 | 80 | 0 | 50 | 64 | 0 | 127 | 0 | 0 | 10 | 290 | 13 | 11 | 0 | 48 | 0 | 0 | 68 | 0 | 17 | 4 | 25 | 17 | 6 | 314 | 19 | 35 | 17 | 2 | 70 | 17 | 17 | 17 | 9 | 25 | 70 | 54 | 11 | 17 | 17 | 0 | 17 | 10 | 18 | 17 | 225 | 18 | 0 | 0 | 7 | 0 | 899 | 0 | 185 | 0 | 46 | 160 | 0 | 0 | 15 | 36 | 8 | 176 | 1 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 34 | 0 | 0 | 0 | 21 | 0 | 8 | 68 | 0 | 230 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 414 | 72 | 0 | 35 | 50 | 23 | 0 | 1 | 35 | 0 | 110 | 0 | 17 | 1 | 9 | 0 | 7 | 0 | 372 | 0 | 250 | 864 | 31 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
292.3904
| Minimum Generation |  | 10443 | 7:00
| Highest Generation |  | 14129 | 21:00
| Day Peak Generation |  | 11976 | 12:00
| Evening Peak Generation |  | 14129 | 21:00
| HVDC Max Flow |  | 913 | 10:00
| HVDC EvPeak Flow |  | 807 | 21:00
| Load factor L.F |  | 83.86% | [163 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-06-15
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-06-14 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 11976 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 10800
Evening Peak Generation : |  |  | 14129 | MW Hour : | 21:00 | Available Max Generation : |  | 14803
E.P. Demand (at gen end) : |  |  | 15000 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14800
Maximum Generation : |  |  | 14129 | MW Hour : | 21:00 | Reserve(Generation end) |  | 3
Total Gen. (MKWH) : |  |  | 284.3755 | System Load Factor : | 83.86% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 630 | MW at | 21:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-06-15
Actual : |  | 73.02 | Ft.(MSL) , | Rule curve : | 79.68 | Ft.( MSL )
Gas Consumed : |  | Total = | 1212.78 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 173729569.634
: |  |  | Coal : | 38288811.9 | Oil : | 857828617.03 | Total : | 1069846998.564
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 53 | 1272:00 | 5083.8668 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1400.0384 |  |  | 0 | 0%
Khulna Area |  | 250 | 6000:00 | 1962.1165 |  |  | 0 | 0%
Rajshahi Area |  | 87 | 2088:00 | 1706.2972 |  |  | 0 | 0%
Cumilla Area |  | 208 | 4992:00 | 1403.5387 |  |  | 0 | 0%
Mymensingh Area |  | 68 | 1632:00 | 1044.3414 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 584.8911 |  |  | 0 | 0%
Barisal Area |  | 47 | 1128:00 | 487.8885 |  |  | 0 | 0%
Rangpur Area |  | 119 | 2856:00 | 954.2139 |  |  | 0 | 0%
Total |  | 832 |  | 14627.1926 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,7
3) Bhula Nuton Biddut ST
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:18 | 15:48 | Madanganj-Shitalakhya 132kV ckt-1 Forced S/D from Shitalakhya 132/33kV end Due to by NLDC
08:18 | 15:47 | Madanganj 132/33kV S/S Madanganj -Shitalakhya 132 kv Ckt Scheduled S/D
08:49 | 19:37 | Shahmirpur 132/33kV S/S 406T LT Scheduled S/D Due to BREB 33KV GIS Extension Work.
08:50 | 19:25 | Shahmirpur 132/33kV S/S 406T HT Scheduled S/D Due to BREB 33KV GIS Extension Work.
09:07 |  | Bhola CCPP GT1 was shutdown
09:37 | 11:25 | Kaliakoir 400/230/132kV S/S 400/230kV TR1 LT Scheduled S/D Due to Transformer fire fighting system testing.
09:37 | 11:24 | Kaliakoir 400/230/132kV S/S 400/230kV TR1 HT Scheduled S/D Due to Transformer fire fighting system testing.
| 09:49 | Aminbazar-Mirpur 132kV Ckt-2 is restored.
| 09:49 | Aminbazar-Mirpur 132kV Ckt-2 is restored.
10:08 | 12:25 | Niamatpur 132/33kV S/S 417T LT Forced S/D Due to L.A change of deluabary 33 kv feeder. | [5 empty] | 7.0MW load interrup.
10:08 | 12:24 | Niamatpur 132/33kV S/S 417T HT Forced S/D Due to L.A change of deluabary 33 kv feeder. | [5 empty] | 7.0MW load interrup.
| 10:08 | Kallyanpur 132/33kV S/S GT-1 (132kV) HT is restored.
10:35 | 13:26 | Bagerhat-Bhandaria 132 kV Ckt-1 Scheduled S/D from Bagerhat 132/33kV end Due to Line Parameter Mesurement By
SPMD,Khulna
11:50 | 12:56 | Cumilla(N) 230/132/33kV S/S 132KV T-04 LT Scheduled S/D
11:51 | 12:55 | Cumilla(N) 230/132/33kV S/S 132KV T-04 HT Scheduled S/D Due to 33KV Summit Generation Feeder Bus Isolator (Yphase) Red
Hot Remove
12:00 |  | Day Peak Gen. 11292 MW
| 14:12 | Bogura-Natore 132 kV Ckt-1 is restored.
| 14:35 | Gopalganj 132/33kV S/S T1 HT is restored.
| 14:36 | Gopalganj 132/33kV S/S T1 LT is restored.
| 14:48 | Chapai 132/33kV S/S T-3 (425T) HT is restored.
| 17:10 | Khulna (S)-Satkhira 132kV Ckt-2 is restored.
17:18 | 18:08 | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-1 Tripped showing Distance Protection Relay (21) & Line Differential
Relay (87L) relays Due to Sudden trip
17:46 |  | Bhola CCPP GT1 was sync.
17:55 | 18:13 | Jhenaidah 132/33kV S/S Transformer T-2 HT Tripped showing over current relays Due to Due to rain | [5 empty] | 20.0MW load interrup.
17:55 | 18:13 | Jhenaidah 132/33kV S/S Transformer T-2 LT Tripped showing over current relays Due to Due to rain | [5 empty] | 20.0MW load interrup.
19:28 | 19:54 | Mongla 132/33kV S/S T-1 LT Tripped showing 50/51 relays Due to 33 kv BEZA feeder fault | [5 empty] | 11.0MW load interrup.
19:28 | 19:56 | Mongla 132/33kV S/S T-2 LT Tripped showing 50/51 relays Due to 33 kv BEZA feeder fault | [5 empty] | 11.0MW load interrup.
20:57 |  | Bibiyana South 400 MW ST tripped
21:00 |  | Evening Peak Generation = 14,129MW
22:22 | 23:49 | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) HT Forced S/D Due to 33kV Bus bar (Section-1) Red Hot Maintenance. | [5 empty] | 45.0MW load interrup.
22:46 | 22:49 | Shahjibazar 132/33kV S/S SPCL 86 MW Tripped showing N/A relays Due to Thunderstorm
22:46 | 22:55 | Shahjibazar-Sreemangal 132kV Ckt-2 Tripped from Shahjibazar 132/33kV end showing Distance relay relays Due
to Thunderstorm and from Sreemongol 132/33kV end showing Distance Realy relays Due to Stormy winds and lightning.
07:00 |  | Minimum Generation: 10323 MW
07:07 |  | Sholosohor 132/33kV S/S TRAFO-01 HT Scheduled S/D Due to seal the places at 33kV Gantry structures where Birds are
building nests frequently and causing fault regularly.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-06-14 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 100 | 2401406 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 160 | 4032000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 390 | 9598970 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 332 | 7752000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9927500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 73 | 1577280 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 304 | 7284393 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 94 | 2160764 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 213069 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 20 | 59 | 1330020
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 322488 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 191 | 4755000
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 75 | 1599360 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 324 | 7672594
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 91 | 1592784 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 260280 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 115 | 740640 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 468709
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 465660
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 44 | 980580 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 811400
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 30 | 662900
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 24 | 287040 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 147 | 1763891 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 300 | 3437439
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 97 | 1376367
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 135 | 972864 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1119360 | Fuel shortage
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 92 | 1642560 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 90 | 956160 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 222532
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 550800 | Fuel shortage
| Dhaka area Total |  |  |  | 5867 | 4052 | 78938810
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 105 | 2300000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 280171
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 88695
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 46 | 598560
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 50 | 1159000 | Low Water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 219 | 5184438
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 68 | 940909 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 40 | 455232 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 1207260 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 23 | 512520 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 38 | 672000 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 9 | 214320 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 24 | 463680
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 14166
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 300 | 2461418
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 448759 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 34 | 527743 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 38 | 603840 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 68 | 745200 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 163 | 948436
| SS Power I |  | SS Power | 0 | 0 | 0 | 0 | On test.
| Cox's Bazar Wind |  | IPP | 66 | 0 | 7 | 296208 | On test.
| Chattogram area Total |  |  |  | 2545 | 1325 | 20122555
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 120 | 2571000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7702500 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 260 | 6397000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 228 | 5494400 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 39 | 957528
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1133612
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 125 | 582109 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 242352 | Machine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 427200 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 453744
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 220140
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 160 | 3855360
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 299300
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 428578 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 459910 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 1565220 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 95 | 571200 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 400320 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 94 | 1113600 | Fuel shortage
| Cumilla Area Total |  |  |  | 3096 | 1691 | 35075800
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 48 | 737280 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 357732 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10100
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 87 | 1708800 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 85 | 698400 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 160200
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 297600 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 251 | 3970112
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1017000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 676920 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2532927 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1173000
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 46 | 1119456
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 188156 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 50 | 1274016
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 69 | 1679040
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 126 | 3011380 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 13 | 322224
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7719000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 309 | 8270000 | DP high
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 239580
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 260 | 8575000 | ST Tripped at 20:52
| Sylhet Area Total |  |  |  | 2427 | 1429 | 37797699
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 807 | 21262545
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 92 | 689280
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 24 | 298080 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 200 | 4740077
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 70 | 862464 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 150 | 3862368 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 32 | 239250 | Engine problem
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 73 | 1226880 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 85 | 1487520 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 712080
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 229 | 5114782 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 376 | 8952727 | Coal shortage.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 2901 | 2138 | 49448053
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 698976 | Fuel shortage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 35 | 664009 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 173 | 3191078 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 0 | 0 | Coal shortage.
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 109 | 2549236 | GT-1 Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1209600
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 307 | 6654500
| Barisal Area Total |  |  |  | 2265 | 822 | 14967399
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 4 | 59344 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 28 | 196631 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 28 | 14 | 328420
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 205540 | Fuel shortage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 719606 | Fuel shortage
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 167 | 3581236 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 144 | 3808918 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 379 | 9261890 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 275250 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 403200
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 189252 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 172291 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 80 | 411072 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 108 | 2280951
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 968352 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 55 | 810912 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 29160
| Adani Power Jharkhanda Ltd |  | Import | 748*1 | 748 | 748 | 10303636
| Rajshahi Area Total |  |  |  | 2905 | 1953 | 34005661
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 67 | 1515490
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 230 | 5573500
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 56 | 813091 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 37859
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 881664
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 207140
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 1020700
| Rangpur Area Total |  |  |  | 750 | 468 | 10049444
| Total |  |  |  | 23370 | 14129 | 284375533
| Eastern Grid Total |  |  |  | 14549 | 8748 | 175904976
| Western Grid Total |  |  |  | 8821 | 5381 | 108470557
| National Grid Total |  |  |  | 23370 | 14129 | 284375533
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-06-14
| (a) ENTIRE EASTERN GRID : |  | 9153.83 | MW | (b) ENTIRE WESTERN GRID : |  | 4394.8 | MW
| i) Dhaka area |  | 5369.33 | MW | i) Khulna area |  | 1628 | MW
| ii) Chittagong area |  | 1339.5 | MW | ii) Rajshahi area |  | 1461.8 | MW
| iii) Comilla area |  | 1224 | MW | iii) Barisal area |  | 458 | MW
| iv) Mymensingh area |  | 951 | MW | iv) Rangpur area |  | 847 | MW
| v) Sylhet area |  | 270 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 13548.63 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 25 | 00:00 | Kamrangirchar | 71.1 | 13:00 | Natore | 150 | 21:00 | Shitalakhya | 112.9 | 17:00
2 | AKSML | 9 | 22:00 | Chowmuhani | 195 | 21:00 | Kaptai | N/A | N/A | Nawabganj | 52.2 | 16:00 | Sholosohor | 36 | 20:00
3 | Aftabnagar | 60 | 19:00 | Chuadanga | 90 | 14:00 | Kazla | 97 | 16:00 | Netrakona | 90 | 18:30 | Shyampur | 178 | 13:00
4 | Agargaon | 112 | 15:00 | Coxsbazar | 113 | 20:00 | Keranigonj | 68 | 19:00 | New | 94.6 | 12:00 | Siddhirganj | 126 | 12:00
5 | Agrabad | 74 | 14:00 | Cumilla(N) | 159 | 21:00 | Khagrachori | 34 | 20:00 | Niamatpur | 97 | 22:00 | Sirajganj | 110 | 21:00
6 | Amnura | 61 | 22:00 | Cumilla(S) | 182 | 14:00 | Khulna | 106 | 19:00 | Noapara | 40 | 19:30 | Sonargaon | 68 | 15:00
7 | Ashuganj | 61 | 20:00 | Daudkandi | 117 | 21:00 | Khulshi | 192 | 20:00 | PHP | 8 | 19:00 | Sreemongol | 55 | 04:00
8 | BIPTC | N/A | N/A | Dhaka | 34 | 11:00 | Kishoreganj | 126 | 21:00 | Pabna | 105 | 07:00 | Sreepur | 67.08 | 12:00
9 | BSRM | 166 | 04:00 | Dhamrai | 130 | 19:30 | Kodda | 296 | 19:00 | Palashbari | 118 | 20:00 | Srinagar | 49.01 | 19:30
10 | Bagerhat | 81 | 18:30 | Dhanmondi | 162 | 13:00 | Kulaura | 42 | 01:00 | Panchagarh | 48 | 22:00 | Sunamganj | 38 | 00:00
11 | Bakulia | 118 | 20:00 | Dohazari | 106 | 21:00 | Kurigram | 62 | 21:00 | Patuakhali | 111 | 21:00 | Sylhet | 154 | 00:00
12 | Banani | 76 | 14:00 | Faridpur | 148 | 21:00 | Kushtia | 138 | 21:00 | Payra | 20 | 21:00 | TK | 25 | 23:00
13 | Bangabhaban | 20 | 10:00 | Fatullah | 63 | 12:00 | Lalbag | 95 | 13:00 | Postogola | 63 | 23:00 | Tangail | 250 | 21:00
14 | Barapukuria | 62 | 21:00 | Fenchuganj | 34 | 05:00 | Lalmonirhat | 46 | 21:00 | Purbachal | 23 | 22:00 | Thakurgaon | 87 | 21:00
15 | Barguna | 20 | 21:00 | Feni | 100 | 21:00 | Madanganj | 46 | 19:30 | Purbasadipur | 112 | 23:00 | Tongi | 114 | 15:00
16 | Barishal | 105 | 13:00 | GPH | 10 | 07:00 | Madaripur | 100 | 21:00 | Rahanpur_I | 0 | 00:00 | Ullon | 44 | 23:00
17 | Barishal-230 | 94 | 22:00 | Ghorashal | N/A | N/A | Madartek | 98.86 | 23:00 | Rahim | 40 | 14:00 | Uttara | 74 | 17:00
18 | Baroaulia | 70 | 11:00 | Goalpara | 40 | 21:00 | Madunaghat | 57 | 19:30 | Rajbari | 62 | 22:00 | UttaraNew | 61 | 15:00
19 | Baroirhat | 47 | 13:00 | Gollamari | 58 | 19:00 | Magura | 54 | 21:00 | Rajendrapur | 100 | 20:00 | Zigatola | 91 | 16:00
20 | Bashundhara | 189 | 19:00 | Gopalganj | 101.4 | 22:00 | Mahasthangarh | 66 | 23:00 | Rajshahi | 172 | 23:00
21 | BashundharaCement | 6 | 15:00 | Gulshan | 86 | 16:00 | Manikganj | 130 | 19:30 | Rajshahi-230 | 34 | 16:00
22 | Beanibazar | 56 | 00:00 | Halishahar | 88 | 09:00 | Maniknagar | 112 | 13:00 | Ramganj | 86 | 21:00
23 | Benapole | 54 | 20:00 | HaripurSBU | 166 | 09:00 | Matarbari | 44 | 21:00 | Rampur | 41 | 20:00
24 | Bhaluka | 126 | 10:00 | Hasnabad | 97 | 20:00 | Matuail | 69 | 15:00 | Rangamati | 18 | 20:00
25 | Bhandaria | 50 | 19:00 | Hathazari | 77 | 21:00 | Millgate | 114 | 16:00 | Rangpur | 139 | 19:00
26 | Bhangura | 42 | 22:00 | Ishurdi | 57 | 14:00 | Mirpur | 171 | 19:30 | Ruppur | 6 | 16:00
27 | Bheramara(GK) | 61 | 23:00 | Jaldhaka | 66 | 21:00 | Mirsorai | 5 | 19:30 | SSM | 4 | 03:00
28 | Bhulta | 279 | 23:00 | Jamalpur | 137 | 22:00 | Mithapukur | 38 | 21:00 | Saidpur | 99 | 21:00
29 | Bog-Sherpur | 68 | 21:00 | Jashore | 141 | 19:30 | Modern | 0 | 00:00 | Satkhira | 137 | 21:00
30 | Bogura | 156 | 21:00 | Jhenaidah | 121 | 21:00 | Mogbazar | 156.1 | 15:00 | Satmasjid | 97 | 19:00
31 | Borhanuddin | 60 | 21:00 | Joydebpur | 196 | 19:30 | Mongla | 30 | 15:00 | Savar | 193 | 21:00
32 | Brahmanbaria | 160 | 21:00 | Joypurhat | 62 | 22:00 | Motijheel | 49 | 17:00 | Shahjadpur | 122 | 21:00
33 | Cantonment | 156 | 13:00 | Juldah | 24 | 00:00 | Munshiganj | 113 | 20:00 | Shahjibazar | 103 | 19:00
34 | Chandpur | 62 | 21:00 | KSRM | 37.5 | 12:00 | Mymensingh | 214 | 20:00 | Shahmirpur | 44.5 | 22:00
35 | Chandraghona | 28 | 19:00 | Kabirpur | 273 | 21:00 | Naogaon | 130 | 20:00 | Shariatpur | 73 | 21:00
36 | Chapai | 73 | 20:00 | Kachua | 66 | 21:00 | Narail | 51 | 21:00 | Sherpur | 108 | 22:00
37 | Charsaidpur | 46 | 20:00 | Kallyanpur | 132 | 19:30 | Narinda | 84 | 13:00 | Shikalbaha | N/A | N/A
38 | Chauddagram | 57 | 21:00 | Kalurghat | 34 | 18:30 | Narshingdi | 174 | 00:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-06-14 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 401 | 01:00 | 389 | 11:00 | Kaliakoir | 373 | 03:00 | 363 | 12:00
| Ashuganj | N/A | N/A | N/A | N/A | Madunaghat_I | 413 | 19:00 | 394 | 10:00
| Bhulta | 394 | 00:00 | 382 | 11:00 | Payra | 415 | 19:30 | 406 | 11:00
| Bibiana | 402 | 19:30 | 390 | 16:00 | Rahanpur_I | 419 | 10:00 | 404 | 05:00
| BIPTC | 402 | 07:00 | 391 | 15:00 | Rampal | 411 | 19:30 | 402 | 08:00
| Gopalganj | 408 | 03:00 | 398 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 260 | 02:00 | 221 | 11:00 | Hasnabad | 232 | 00:00 | 222 | 11:00
| AKSML | 233 | 19:00 | 222 | 04:00 | Hathazari | 237 | 19:00 | 225 | 12:00
| Aminbazar | 234 | 00:00 | 225 | 10:00 | Ishurdi | 233 | 00:00 | 225 | 12:00
| Ashuganj | 235 | 00:00 | 227 | 12:00 | Jhenaidah | 229 | 00:00 | 221 | 12:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 239 | 08:00 | 223 | 11:00
| Baghabari | 230 | 00:00 | 224 | 12:00 | Keranigonj | 231 | 03:00 | 221 | 11:00
| Barapukuria | 219 | 18:30 | 211 | 21:00 | Khulna(S) | 237 | 18:00 | 231 | 12:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | 236 | 19:30 | 224 | 10:00
| Barishal | 239 | 18:30 | 234 | 05:00 | Maniknagar | 230 | 03:00 | 221 | 12:00
| Bheramara | 232 | 00:00 | 223 | 12:00 | Meghnaghat | 237 | 01:00 | 229 | 16:00
| Bhulta | 233 | 00:00 | 225 | 10:00 | Mirsorai | 236 | 19:30 | 222 | 09:00
| Bibiana | 238 | 18:00 | 233 | 07:00 | Rajshahi | 234 | 01:00 | 223 | 14:00
| BIPTC | 233 | 00:00 | 222 | 12:00 | Rampal | 235 | 00:00 | 230 | 11:00
| Bogura | 222 | 09:00 | 213 | 21:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 250 | 17:00 | 236 | 00:00 | Rampura | 230 | 00:00 | 221 | 12:00
| BSRM | 239 | 19:30 | 222 | 04:00 | Shikalbaha | 236 | 19:30 | 224 | 10:00
| Cumilla(N) | 233 | 19:30 | 223 | 12:00 | Shyampur | 231 | 03:00 | 222 | 11:00
| Fenchuganj | 243 | 18:00 | 238 | 00:00 | Siddhirganj | 233 | 00:00 | 226 | 13:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 235 | 00:00 | 230 | 17:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 230 | 00:00 | 224 | 12:00
| GPH | 240 | 19:30 | 222 | 12:00 | Tongi | 227 | 00:00 | 217 | 12:00
| Haripur | 230 | 00:00 | 222 | 15:00
| 132 kV | KV |  | KV |  | Tongi | KV |  | KV
| Aftabnagar | 136 | 00:00 | 127 | 12:00 | Lalbag | 135 | 03:00 | 127 | 11:00
| Agargaon | 138 | 00:00 | 130 | 12:00 | Lalmonirhat | 130 | 18:30 | 120 | 00:00
| Agrabad | 137 | 19:30 | 127 | 14:00 | Madanganj | 135 | 00:00 | 130 | 12:00
| AKS | 133 | 19:00 | 126 | 12:00 | Madaripur | 130 | 00:00 | 126 | 13:00
| Aminbazar | 130 | 00:00 | 124 | 10:00 | Madartek | 136 | 03:00 | 128 | 11:00
| Amnura | 137 | 00:00 | 127 | 03:00 | Madunaghat | 140 | 19:30 | 129 | 10:00
| Ashuganj | 137 | 00:00 | 135 | 12:00 | Magura | 135 | 00:00 | 128 | 13:00
| Bagerhat | 138 | 19:30 | 130 | 13:00 | Mahasthangarh | 132 | 01:00 | 123 | 21:00
| Bakulia | 139 | 19:30 | 128 | 14:00 | Manikganj | 134 | 18:00 | 125 | 15:00
| Banani | 136 | 02:00 | 128 | 11:00 | Maniknagar | 134 | 03:00 | 125 | 12:00
| Bangabhaban | 133 | 03:00 | 125 | 12:00 | Matarbari | 136 | 19:30 | 117 | 20:00
| Barapukuria | 136 | 18:30 | 129 | 21:00 | Matuail | 134 | 03:00 | 130 | 11:00
| Barguna | 138 | 00:00 | 132 | 14:00 | Millgate | 133 | 00:00 | 125 | 11:00
| Barishal | 137 | 00:00 | 126 | 06:00 | Mirpur | 128 | 02:00 | 122 | 11:00
| Barishal-230 | 132 | 17:00 | 128 | 13:00 | Mithapukur | 130 | 18:30 | 122 | 21:00
| Baroaulia | 139 | 19:30 | 127 | 14:00 | Modern | 138 | 19:00 | 128 | 10:00
| Baroirhat | 134 | 00:00 | 125 | 08:00 | Mogbazar | 138 | 03:00 | 130 | 10:00
| Bashundhara | 136 | 01:00 | 124 | 12:00 | Mongla | 135 | 17:00 | 130 | 04:00
| BashundharaCement | 135 | 00:00 | 130 | 12:00 | Motijheel | 133 | 03:00 | 125 | 12:00
| Beanibazar | 138 | 10:00 | 128 | 00:00 | Munshiganj | 136 | 08:00 | 131 | 11:00
| Benapole | 134 | 18:00 | 126 | 14:00 | Mymensingh | 134 | 18:00 | 117 | 20:00
| Bhaluka | 127 | 02:00 | 120 | 21:00 | Naogaon | 131 | 01:00 | 116 | 21:00
| Bhandaria | 134 | 00:00 | 125 | 14:00 | Narail | 134 | 00:00 | 126 | 21:00
| Bhangura | 136 | 00:00 | 132 | 04:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 134 | 00:00 | 130 | 12:00 | Narshingdi | 131 | 22:00 | 123 | 09:00
| Bheramara(GK) | 136 | 00:00 | 130 | 15:00 | Natore | 134 | 01:00 | 127 | 12:00
| Bhulta | 123 | 00:00 | 119 | 12:00 | Nawabganj | 135 | 03:00 | 127 | 16:00
| Bog-Sherpur | 135 | 01:00 | 125 | 21:00 | Netrakona | 131 | 20:00 | 118 | 14:00
| Bogura | 134 | 00:00 | 126 | 21:00 | New | 132 | 05:00 | 126 | 11:00
| Bogura-230 | 133 | 09:00 | 126 | 21:00 | Niamatpur | 134 | 00:00 | 108 | 21:00
| Brahmanbaria | 133 | 07:00 | 130 | 19:00 | Noapara | 136 | 18:00 | 132 | 07:00
| Cantonment | 138 | 03:00 | 130 | 11:00 | Pabna | 134 | 01:00 | 128 | 07:00
| Chandpur | 133 | 19:00 | 120 | 09:00 | Palashbari | 129 | 01:00 | 119 | 21:00
| Chandraghona | 138 | 19:00 | 130 | 09:00 | Panchagarh | 139 | 18:30 | 119 | 00:00
| Chapai | 133 | 00:00 | 128 | 06:00 | Patuakhali | 140 | 00:00 | 133 | 14:00
| Charsaidpur | 136 | 03:00 | 131 | 12:00 | Payra | 140 | 00:00 | 136 | 12:00
| Chauddagram | 135 | 00:00 | 125 | 09:00 | PHP | 135 | 00:00 | 124 | 09:00
| Chhatak | 136 | 09:00 | 128 | 00:00 | Postogola | 137 | 02:00 | 132 | 11:00
| Chowmuhani | 133 | 19:00 | 116 | 22:00 | Purbachal | 136 | 00:00 | 124 | 11:00
| Chuadanga | 134 | 18:00 | 123 | 21:00 | Purbasadipur | 128 | 16:00 | 120 | 00:00
| Coxsbazar | 132 | 18:00 | 117 | 21:00 | Rahim | 135 | 00:00 | 131 | 11:00
| Cumilla(N) | 137 | 19:30 | 128 | 13:00 | Rajbari | 129 | 00:00 | 125 | 12:00
| Cumilla(S) | 135 | 00:00 | 122 | 14:00 | Rajendrapur | 135 | 20:00 | 126 | 15:00
| Daudkandi | 133 | 00:00 | 128 | 09:00 | Rajshahi | 133 | 00:00 | 126 | 12:00
| Dhaka | 136 | 02:00 | 128 | 12:00 | Rajshahi-230 | 133 | 01:00 | 126 | 12:00
| Dhamrai | 134 | 04:00 | 127 | 11:00 | Ramganj | 131 | 19:30 | 118 | 13:00
| Dhanmondi | 135 | 00:00 | 128 | 12:00 | Rampur | 136 | 18:30 | 127 | 10:00
| Dohazari | 135 | 18:00 | 125 | 21:00 | Rampura | 136 | 03:00 | 127 | 12:00
| Dummy | 130 | 00:00 | 126 | 12:00 | Rangamati | 138 | 19:30 | 129 | 12:00
| Faridpur | 134 | 00:00 | 127 | 11:00 | Rangpur | 129 | 18:30 | 121 | 21:00
| Fatullah | 139 | 10:00 | 134 | 00:00 | Ruppur | 135 | 00:00 | 130 | 13:00
| Fenchuganj | 136 | 19:30 | 125 | 07:00 | Saidpur | 132 | 18:30 | 120 | 00:00
| Feni | N/A | N/A | N/A | N/A | Satkhira | 134 | 19:30 | 122 | 12:00
| Ghorashal | 139 | 18:00 | 134 | 12:00 | Satmasjid | 138 | 03:00 | 130 | 11:00
| Goalpara | 136 | 00:00 | 131 | 13:00 | Savar | 129 | 05:00 | 122 | 10:00
| Gollamari | 135 | 19:30 | 129 | 14:00 | Shahjadpur | 140 | 03:00 | 135 | 07:00
| Gopalganj | 130 | 03:00 | 126 | 12:00 | Shahjibazar | 136 | 10:00 | 132 | 00:00
| Gopalganj-400 | 135 | 00:00 | 127 | 12:00 | Shahmirpur | 138 | 19:30 | 127 | 07:00
| Gulshan | 139 | 19:30 | 128 | 09:00 | Shariatpur | 129 | 18:30 | 124 | 13:00
| Halishahar | 135 | 00:00 | 131 | 11:00 | Sherpur | 134 | 18:30 | 115 | 23:00
| Haripur | 135 | 00:00 | 131 | 11:00 | Shikalbaha | N/A | N/A | N/A | N/A
| HaripurSBU | 136 | 06:00 | 133 | 16:00 | Shikalbaha-230 | 137 | 19:30 | 130 | 06:00
| Hasnabad | 138 | 18:30 | 131 | 07:00 | Shitalakhya | 136 | 00:00 | 131 | 11:00
| Hathazari | 135 | 01:00 | 130 | 12:00 | Sholosohor | 138 | 19:30 | 128 | 10:00
| Ishurdi | 130 | 18:30 | 119 | 21:00 | Shyampur | 132 | 00:00 | 127 | 10:00
| Jaldhaka | 136 | 18:30 | 116 | 23:00 | Shyampur-230 | 132 | 00:00 | 127 | 11:00
| Jamalpur | 133 | 00:00 | 127 | 14:00 | Siddhirganj | 135 | 19:30 | 131 | 11:00
| Jashore | 136 | 00:00 | 130 | 13:00 | Sirajganj | 134 | 01:00 | 126 | 20:00
| Jhenaidah | 137 | 00:00 | 123 | 22:00 | Sonargaon | 135 | 00:00 | 129 | 11:00
| Jhenaidah-230 | 138 | 00:00 | 129 | 12:00 | Sreemongol | 136 | 10:00 | 132 | 00:00
| Joydebpur | 132 | 00:00 | 114 | 21:00 | Sreepur | 129 | 08:00 | 125 | 12:00
| Joypurhat | 138 | 19:30 | 129 | 14:00 | Srinagar | 135 | 00:00 | 128 | 11:00
| Juldah | 136 | 18:00 | 123 | 10:00 | SSM | 142 | 19:30 | 130 | 14:00
| Kabirpur | 134 | 19:30 | 122 | 09:00 | Sunamganj | 135 | 19:30 | 126 | 00:00
| Kachua | 136 | 03:00 | 129 | 11:00 | Sylhet | 135 | 09:00 | 129 | 00:00
| Kaliakoir | 129 | 00:00 | 123 | 11:00 | Tangail | 132 | 18:00 | 124 | 12:00
| Kallyanpur | 138 | 19:30 | 129 | 12:00 | Thakurgaon | 138 | 18:30 | 119 | 00:00
| Kalurghat | 135 | 01:00 | 121 | 10:00 | TK | 140 | 19:30 | 129 | 08:00
| Kamrangirchar | N/A | N/A | N/A | N/A | Tongi | 135 | 00:00 | 128 | 12:00
| Kaptai | 133 | 00:00 | 125 | 12:00 | Ullon | 136 | 00:00 | 128 | 12:00
| Kazla | 136 | 03:00 | 128 | 11:00 | Uttara | 130 | 07:00 | 122 | 11:00
| Keranigonj | 138 | 19:30 | 129 | 12:00 | UttaraNew | 129 | 02:00 | 122 | 11:00
| Khagrachori | 137 | 18:00 | 133 | 07:00 | Zigatola | 135 | 00:00 | 127 | 17:00
| Khulna | 137 | 18:00 | 132 | 12:00
| Khulna(S) | 137 | 19:30 | 127 | 09:00
| Khulshi | 130 | 07:00 | 125 | 21:00
| Kishoreganj | 135 | 18:00 | 126 | 12:00
| Kodda | 138 | 19:30 | 128 | 10:00
| KSRM | 137 | 19:00 | 133 | 00:00
| Kulaura | 127 | 03:00 | 117 | 21:00
| Kurigram | 133 | 00:00 | 129 | 13:00

## L-Curve
Date | 2023-06-14
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1000 | 7329 | 5129 | 12458 |  |  |  | QF-LDC-11
0:30 | 1105 | 7369.5 | 4470 | 11839.5 | Date: | 2023-06-14
1:00 | 1210 | 7410 | 3811 | 11221
1:30 | 1195 | 7377 | 3805 | 11182
2:00 | 1180 | 7344 | 3799 | 11143
2:30 | 1170 | 7281.5 | 3854 | 11135.5 | [5 empty] | Gen. at Eve. Peak | 14129 | 14129 MW (21:00 )
3:00 | 1160 | 7219 | 3909 | 11128 | [6 empty] | 21:00
3:30 | 1035 | 7157 | 3915 | 11072 | [5 empty] | Gen. at Day Peak | 11976 | 11976 MW (12:00 )
4:00 | 910 | 7095 | 3921 | 11016 | [6 empty] | 12:00
4:30 | 905 | 7073 | 3908 | 10981 | [5 empty] | Highest Generation | 14129
5:00 | 900 | 7051 | 3895 | 10946 | [6 empty] | 21:00
5:30 | 945 | 6883.5 | 3822.5 | 10706
6:00 | 990 | 6716 | 3750 | 10466
6:30 | 1075 | 6694.5 | 3760 | 10454.5
7:00 | 1160 | 6673 | 3770 | 10443
7:30 | 1240 | 6671.5 | 3835.5 | 10507
8:00 | 1320 | 6670 | 3901 | 10571
8:30 | 1370 | 6671 | 3998.5 | 10669.5
9:00 | 1420 | 6672 | 4096 | 10768
9:30 | 1385 | 6682.5 | 4197 | 10879.5
10:00 | 1350 | 6693 | 4298 | 10991
10:30 | 1315 | 6702 | 4431.5 | 11133.5
11:00 | 1280 | 6711 | 4565 | 11276
11:30 | 1200 | 6975.5 | 4650.5 | 11626
12:00 | 1120 | 7240 | 4736 | 11976
12:30 | 1115 | 7287 | 4757.5 | 12044.5
13:00 | 1110 | 7334 | 4779 | 12113
13:30 | 1100 | 7376.5 | 4832 | 12208.5
14:00 | 1090 | 7419 | 4885 | 12304
14:30 | 1080 | 7372 | 4837.5 | 12209.5
15:00 | 1070 | 7325 | 4790 | 12115
15:30 | 1100 | 7249 | 4686 | 11935
16:00 | 1130 | 7173 | 4582 | 11755
16:30 | 1115 | 7164 | 4526 | 11690
17:00 | 1100 | 7155 | 4470 | 11625
17:30 | 1110 | 7153 | 4508.5 | 11661.5
18:00 | 1120 | 7151 | 4547 | 11698
18:30 | 1085 | 7677 | 4794.5 | 12471.5
19:00 | 1050 | 8203 | 5042 | 13245
19:30 | 990 | 8216 | 5311 | 13527
20:00 | 700 | 8441 | 5240 | 13681 |  |  |  | Executive Engineer
20:30 | 665 | 8594.5 | 5310.5 | 13905 |  |  |  | Network Operation Division
21:00 | 630 | 8748 | 5381 | 14129
21:30 | 635 | 8606.5 | 5403.5 | 14010
22:00 | 640 | 8465 | 5426 | 13891 |  |  |  |  | Page 6 of 7
22:30 | 690 | 8106 | 5356.5 | 13462.5
23:00 | 740 | 7747 | 5287 | 13034
23:30 | 870 | 7538 | 5208 | 12746
24:00 | 1000 | 7329 | 5129 | 12458
14129 MW (21:00 )
11976 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-06-14 |  | Energy |  | 284375533
[15 empty] | 43629 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 4255 | 731 | 2347 | 584 | 1765 | 1730 | 25 | 431 | 405 | 172 | 0 | 13 | 1950.11
0:30 | 4302.5 | 760 | 2345.5 | 545 | 1589 | 1299 | 37.5 | 437.5 | 339.5 | 169 | 0 | 15 | 1920.0275 |  |  | Date: | 43629
1:00 | 4350 | 789 | 2344 | 506 | 1413 | 868 | 50 | 444 | 274 | 166 | 0 | 17 | 1889.945
1:30 | 4361.5 | 789.5 | 2358 | 527 | 1347.5 | 871 | 50 | 442 | 252.5 | 166 | 0 | 17 | 1831.69 | [8 empty] | 284.3755 | 284.3755 |  | Total Energy Gen MKWHr Energy Not Served MKWHr Energy Requirement MKWHr | Total Energy Gen 284.376 MKWHr Energy Not Served 34.597 MKWHr Energy Requirement 318.973 MKWHr
2:00 | 4373 | 790 | 2372 | 548 | 1282 | 874 | 50 | 440 | 231 | 166 | 0 | 17 | 1773.435 | [8 empty] | 34.5973 | 34.5973
2:30 | 4357 | 850.5 | 2365 | 529.5 | 1264.5 | 871 | 50 | 439.5 | 228.5 | 164 | 0 | 16 | 1708.9725 | [8 empty] | 318.9728 | 318.9728
3:00 | 4341 | 911 | 2358 | 511 | 1247 | 868 | 50 | 439 | 226 | 162 | 0 | 15 | 1644.51
3:30 | 4346 | 911.5 | 2353.5 | 454 | 1256.5 | 871.5 | 50 | 438.5 | 212.5 | 163 | 0 | 15 | 1602.49
4:00 | 4351 | 912 | 2349 | 397 | 1266 | 875 | 50 | 438 | 199 | 164 | 0 | 15 | 1560.47
4:30 | 4352 | 912 | 2354.5 | 329.5 | 1243 | 928.5 | 50 | 437.5 | 199 | 162 | 0 | 13 | 1498.395
5:00 | 4353 | 912 | 2360 | 262 | 1220 | 982 | 50 | 437 | 199 | 160 | 0 | 11 | 1436.32
5:30 | 4304.5 | 912 | 2354.5 | 131 | 1179 | 981 | 50 | 435.5 | 196 | 151 | 2.5 | 9 | 1402.895
6:00 | 4256 | 912 | 2349 | 0 | 1138 | 980 | 50 | 434 | 193 | 142 | 5 | 7 | 1369.47
6:30 | 4236 | 912 | 2350.5 | 0 | 1127.5 | 989.5 | 50 | 431 | 192 | 142 | 19 | 5 | 1404.3275 | [7 empty] | Coal
7:00 | 4216 | 912 | 2352 | 0 | 1117 | 999 | 50 | 428 | 191 | 142 | 33 | 3 | 1439.185
7:30 | 4238.5 | 912 | 2328.5 | 0 | 1125 | 1025 | 50 | 427 | 183 | 150 | 60 | 8 | 1401.94 | [6 empty] | Oil
8:00 | 4261 | 912 | 2305 | 0 | 1133 | 1051 | 50 | 426 | 175 | 158 | 87 | 13 | 1364.695
8:30 | 4263.5 | 912 | 2306.5 | 0 | 1148 | 1092.5 | 50 | 428 | 171 | 158 | 126.5 | 13.5 | 1461.6275
9:00 | 4266 | 912 | 2308 | 0 | 1163 | 1134 | 50 | 430 | 167 | 158 | 166 | 14 | 1558.56
9:30 | 4213 | 912.5 | 2299.5 | 0 | 1225 | 1189 | 50 | 429.5 | 173.5 | 157 | 216.5 | 14 | 1547.5775
10:00 | 4160 | 913 | 2291 | 0 | 1287 | 1244 | 50 | 429 | 180 | 156 | 267 | 14 | 1536.595
10:30 | 4090 | 912 | 2281.5 | 0 | 1340 | 1350 | 50 | 427.5 | 186 | 163 | 318.5 | 15 | 1543.7575
11:00 | 4020 | 911 | 2272 | 0 | 1393 | 1456 | 50 | 426 | 192 | 170 | 370 | 16 | 1550.92
11:30 | 4032.5 | 911.5 | 2271 | 197.5 | 1446 | 1554.5 | 50 | 421 | 191.5 | 172 | 361.5 | 17 | 1407.67
12:00 | 4045 | 912 | 2270 | 395 | 1499 | 1653 | 50 | 416 | 191 | 174 | 353 | 18 | 1264.42
12:30 | 4050 | 912.5 | 2267 | 456 | 1529.5 | 1655 | 50 | 415 | 188 | 172 | 332.5 | 17 | 1298.8
13:00 | 4055 | 913 | 2264 | 517 | 1560 | 1657 | 50 | 414 | 185 | 170 | 312 | 16 | 1333.18
13:30 | 4055 | 913 | 2264 | 517 | 1560 | 1657 | 50 | 414 | 185 | 170 | 312 | 16 | 1333.18
14:00 | 4055 | 913 | 2264 | 517 | 1560 | 1657 | 50 | 414 | 185 | 170 | 312 | 16 | 1333.18
14:30 | 4088 | 913 | 2251 | 466 | 1590.5 | 1691.5 | 50 | 412.5 | 192 | 168 | 277.5 | 14 | 1495.0525
15:00 | 4121 | 913 | 2238 | 415 | 1621 | 1726 | 50 | 411 | 199 | 166 | 243 | 12 | 1656.925
15:30 | 4121 | 912.5 | 2245.5 | 287.5 | 1631 | 1704.5 | 50 | 411 | 198.5 | 167 | 193.5 | 13 | 1781.075
16:00 | 4121 | 912 | 2253 | 160 | 1641 | 1683 | 50 | 411 | 198 | 168 | 144 | 14 | 1905.225
16:30 | 4146.5 | 911.5 | 2262 | 80 | 1684.5 | 1679.5 | 50 | 380.5 | 209 | 167 | 106.5 | 13 | 1800.175
17:00 | 4172 | 911 | 2271 | 0 | 1728 | 1676 | 50 | 350 | 220 | 166 | 69 | 12 | 1695.125 | [10 empty] | 472
17:30 | 4144.5 | 911.5 | 2195.5 | 0 | 1876.5 | 1684 | 50 | 322.5 | 251.5 | 162 | 50 | 13.5 | 1517.0175 | [10 empty] | 100
18:00 | 4117 | 912 | 2120 | 0 | 2025 | 1692 | 50 | 295 | 283 | 158 | 31 | 15 | 1338.91 | [10 empty] | 20
18:30 | 4120.5 | 907 | 2178.5 | 70.5 | 2554 | 1688.5 | 50 | 344.5 | 363.5 | 166 | 15.5 | 13 | 1125.4675 | [10 empty] | 592
19:00 | 4124 | 902 | 2237 | 141 | 3083 | 1685 | 50 | 394 | 444 | 174 | 0 | 11 | 912.025
19:30 | 4084 | 903 | 2151 | 245 | 3256 | 1678 | 50 | 426 | 563 | 162 | 0 | 9 | 990.335
20:00 | 4222 | 903 | 2242 | 134 | 3250 | 1684 | 50 | 350 | 670 | 168 | 0 | 8 | 1068.645
20:30 | 4204 | 855 | 2271 | 319.5 | 3263 | 1706 | 50 | 389.5 | 675.5 | 164 | 0 | 7.5 | 950.225
21:00 | 4186 | 807 | 2300 | 505 | 3276 | 1728 | 50 | 429 | 681 | 160 | 0 | 7 | 831.805
21:30 | 4215 | 797 | 2294.5 | 549 | 3131 | 1729 | 37.5 | 431 | 657 | 160 | 0 | 9 | 897.7
22:00 | 4244 | 787 | 2289 | 593 | 2986 | 1730 | 25 | 433 | 633 | 160 | 0 | 11 | 963.595
22:30 | 4230.5 | 765 | 2277 | 591.5 | 2687 | 1732 | 25 | 432 | 547 | 167 | 0 | 8.5 | 1325.0625
23:00 | 4217 | 743 | 2265 | 590 | 2388 | 1734 | 25 | 431 | 461 | 174 | 0 | 6 | 1686.53
23:30 | 4236 | 737 | 2306 | 587 | 2076.5 | 1732 | 25 | 431 | 433 | 173 | 0 | 9.5 | 1818.32 |  |  | Max Temp. in Dhaka |  | 36.8° C
24:00 | 4255 | 731 | 2347 | 584 | 1765 | 1730 | 25 | 431 | 405 | 172 | 0 | 13 | 1950.11
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 284.376 MKWHr Energy Not Served 34.597 MKWHr Energy Requirement 318.973 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-06-14
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 603000
2 | Karnaphuli Hydro PP Unit-4 & 5 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 0 |  |  | 556000
3 | Chattogram TPP-1 | 110 | 110 | 100 | 102 | 110 | 110 | 107 | 110 | 111 | 110 | 100 | 85 | 90 | 90 | 90 | 85 | 80 | 85 |  | 90 | 85 | 100 | 105 | 105 | 105 | 104 | 2300000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 |  | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 280171
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 2 | 4 | 4 | 13 | 13 | 9 | 12 | 10 | 7 | 2 | 0 | 1 | [8 empty] | 88695
6 | Sikalbaha 225MW CCPP (Gas) | 218 | 221 | 222 | 222 | 221 | 220 | 220 | 218 | 220 | 219 | 219 | 215 | 214 | 219 | 217 | 218 | 220 | 223 |  | 214 | 223 | 220 | 219 | 224 | 222 | 219 | 5184438
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 48 | 48 | 48 | 51 | 48 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1207260
12 | Hathazari 100 MW peaking PP | 16 | 16 | 17 | 17 | 17 | 17 | 15 | 15 | 16 | 16 | 20 | 16 | 16 | 16 | 16 | 32 | 40 | 40 |  | 32 | 40 | 40 | 40 | 40 | 40 | 31 | 455232
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 21 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 34 | 47 | 68 | 63 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 54 | 17 | 940909
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [13 empty] | 14 | 31 | 26 | 26 | 27 |  | 30 | 30 | 35 | 36 | 36 |  | 0 | 242352
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 195 | 191 | 194 | 193 | 191 | 189 | 187 | 183 | 190 | 189 | 185 | 182 | 183 | 183 | 183 | 187 | 189 | 181 |  | 180 | 195 | 189 | 191 | 195 | 191 | 190 | 4755000
17 | Siddhirganj 335 MW CCPP | 330 | 325 | 330 | 333 | 328 | 326 | 325 | 320 | 325 | 320 | 316 | 312 | 312 | 309 | 306 | 310 | 314 | 320 |  | 310 | 290 | 290 | 324 | 324 | 326 | 322 | 7672594
18 | Kodda 300 MW PP Unit-2 (Summit) | 62 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 50 |  | 135 | 148 | 147 | 147 | 147 | 147 | 148 | 1763891
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 99 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2401406
23 | Ghorasal TPP Unit-5 | 170 | 170 | 170 | 170 | 170 | 170 | 180 | 180 | 180 | 180 | 170 | 170 | 160 | 160 | 160 | 160 | 160 | 160 |  | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 4032000
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 37 | 38 | 35 | 35 | 35 | 43 | 42 | 39 | 37 | 37 |  | 37 | 37 | 39 | 39 | 40 | 40 | 40 | 957528
33 | Ashuganj 225 MW CCPP | 104 | 98 | 100 | 102 | 99 | 93 | 90 | 93 | 107 | 86 | 90 | 104 | 113 | 103 | 108 | 110 | 114 | 117 |  | 115 | 114 | 118 | 120 | 116 | 119 | 111 | 2571000
34 | Ashuganj 450 MW CCPP(South) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 6397000
| Ashuganj 450 MW CCPP(North) | 285 | 335 | 285 | 300 | 325 | 340 | 335 | 335 | 280 | 280 | 280 | 320 | 310 | 280 | 300 | 280 | 280 | 280 |  | 325 | 280 | 280 | 280 | 280 | 280 | 300 | 7702500
| Ashuganj 420 MW CCPP(East) | 234 | 234 | 234 | 234 | 235 | 222 | 222 | 222 | 232 | 218 | 208 | 227 | 227 | 227 | 227 | 227 | 228 | 228 |  | 231 | 222 | 228 | 228 | 230 | 230 | 223 | 5494400
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 403 | 403 | 402 | 404 | 402 | 401 | 395 | 397 | 396 | 398 | 393 | 396 | 393 | 393 | 391 | 392 | 396 | 379 |  | 366 | 370 | 380 | 390 | 400 | 401 | 401 | 9598970
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 400 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 9927500
41 | Haripur 360MW CCPP(HPL) | 342 | 340 | 322 | 322 | 327 | 327 | 322 | 322 | 321 | 322 | 322 | 322 | 322 | 322 | 321 | 311 | 322 | 281 |  | 327 | 311 | 302 | 332 | 321 | 323 | 322 | 7752000
42 | RPCL 210MW CCPP | 47 | 47 | 47 | 47 | 47 | 47 | 30 | 30 | 27 | 25 | 24 | 24 | 12 | 12 | 15 | 17 | 19 | 29 |  | 31 | 31 | 31 | 48 | 49 | 48 | 48 | 737280
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 1 | 1 | 4 | 11 | 14 | 22 | 31 | 35 | 9 | 8 | 11 | 4 |  | 0 | [6 empty] | 160200
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 1017000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 676920
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 60 | 60 | 59 | 60 | 58 | 57 | 58 | 57 | 58 | 60 | 48 | 48 | 48 | 48 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 48 | 1274016
48 | Shahjibazar 86MW PP (Shahjibazar) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 73 | 72 | 73 | 73 | 73 | 73 | 73 |  | 73 | 73 | 73 | 69 | 69 |  | 66 | 1679040
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 125 | 124 | 124 | 124 | 125 | 125 | 125 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 |  | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 3011380
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 239580
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 11 | 11 | 11 |  | 11 | 188156
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1173000
56 | Shahjahanulla 25 MW PP | 16 | 16 | 24 | 24 |  |  | 16 | 16 | 16 | 0 |  |  |  | 16 | 16 | 16 | 16 | 16 |  | 22 | 22 | 20 | 13 | 13 | 13 | 13 | 322224
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 315 | 320 | 310 | 330 | 325 | 330 | 320 | 320 | 300 | 290 | 325 | 325 | 330 | 334 | 335 | 335 | 340 |  | 280 | 250 | 270 | 300 | 305 | 300 | 315 | 7719000
| Bibiyana South 400 MW | 390 | 382 | 390 | 383 | 375 | 349 | 345 | 345 | 351 | 351 | 351 | 355 | 360 | 370 | 391 | 390 | 390 | 340 |  | 372 | 325 | 391 | 260 | 260 | 260 | 260 | 8575000
58 | Nababganj 55 MW PP (Southern power ) | [11 empty] | 17 | 17 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 35 | 35 | 0 | 465660
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 297600
60 | Barabkunda 22 MW PP (Regent) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 214320
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | [6 empty] | 0 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 322488
62 | Tangail 22 MW PP (Doreen) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 18 |  | 19 | 19 | 19 | 19 | 19 | 14 | 13 | 357732
63 | Impoprt (Tripura) | 166 | 166 | 162 | 164 | 160 | 142 | 142 | 158 | 158 | 156 | 170 | 174 | 170 | 182 | 166 | 168 | 166 | 158 |  | 174 | 162 | 168 | 160 | 160 | 174 | 172 | 3855360
64 | Malancha, Ctg. EPZ (United) | 35 | 39 | 39 | 40 | 40 | 38 | 37 | 8 | 2 | 2 | 2 | 2 | 5 | 3 | 2 | 4 | 4 | 3 |  | 13 | 13 | 24 | 24 | 35 | 36 | 36 | 463680
65 | Feni 22MW PP (Doreen) | 20 | 20 | 20 | 17 | 17 | 17 | 17 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 453744
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 220140
67 | Jangalia 33MW PP (Summit) | [13 empty] | 17 | 17 | 26 | 32 | 30 |  | 33 | 32 | 33 | 33 | 32 | 32 | 32 | 299300
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 20 | 20 | 12 | 21 | 18 | 20 | 15 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 459910
69 | Summit Ashulia | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 480000
70 | Summit Madhabdi | 25 | 25 | 25 | 25 | 25 | 18 | 26 | 26 | 25 | 18 | 18 | 0 | 10 | 23 | 23 | 23 | 23 | 0 |  |  | 24 | 24 | 24 | 24 | 24 | 25 | 500580
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 811400
72 | Rupganj 33 MW PP(Summit) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 28 | 28 | 28 | 28 | 28 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 662900
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 114 | 114 | 114 | 114 | 114 | 44 | 17 | 17 | 17 | 80 | 98 | 79 | 98 | 98 | 98 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 1565220
| Chowmuhani 113 MW | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 55 |  | 95 | 95 | 95 | 95 | 95 | 28 | 12 | 571200
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 86 | 90 | 90 | 90 | 90 | 90 | 17 | 956160
77 | Siddhirganj 100 PP(Dutch Bangla) | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 70 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 55 | 50 | 1599360
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 |  | 24 | 24 | 24 | 24 | 24 | 24 | 8 | 287040
79 | Kodda 150 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 115 | 115 | 115 | 115 | 115 | 48 | 48 | 740640
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | [5 empty] | 1 | 8 | 8 | 8 |  | 34 | 43 | 43 | 43 | 30 | 25 | 25 | 428578
| Gazipur 100 MW PP | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 52 | 52 |  | 88 | 88 | 88 | 88 | 88 | 88 | 35 | 1119360
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 1 | 0 |  | 3 | 1 | 5 | 2 | 2 | 1 | [9 empty] | 14166
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 448759
| Karnaphuli Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 17 | 23 |  | 34 | 34 | 34 | 34 | 34 | 34 | 17 | 527743
82 | Madanganj 102 PP(Summit) | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 96 | 96 | 96 | 96 | 95 | 95 | 92 | 90 | 90 | 90 | 90 |  | 92 | 92 | 94 | 94 | 94 | 94 | 94 | 2160764
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 46 | 43 | 46 | 46 | 44 | 43 | 43 | 44 | 44 | 48 | 55 | 51 | 55 | 55 | 54 | 53 | 60 | 64 |  | 66 | 64 | 60 | 59 | 55 | 68 | 68 | 1330020
86 | Meghnaghat CCPP ( Summit) | 303 | 307 | 300 | 304 | 307 | 302 | 303 | 299 | 307 | 310 | 305 | 300 | 300 | 305 | 300 | 305 | 305 | 288 |  | 300 | 257 | 305 | 304 | 306 | 307 | 299 | 7284393
87 | Meghnaghat 100 MW(IEL) | 54 | 58 | 58 | 58 | 66 | 67 | 67 | 66 | 64 | 60 | 72 | 73 | 73 | 72 | 72 | 73 | 75 | 72 |  | 73 | 74 | 72 | 73 | 59 | 49 | 58 | 1577280
| Meghnaghat 104 MW PP (OPCL) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 70 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 92 |  | 92 | 91 | 92 | 92 | 91 | 79 | 57 | 1642560
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 10 | 22 | 22 | 22 | 22 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 512520
92 | Fenchuganj 44MW (Energyprima) | 45 | 45 | 45 | 45 | 42 | 45 | 45 | 45 | 46 | 46 | 43 | 43 | 46 | 50 | 46 | 49 | 49 | 49 |  | 46 | 46 | 46 | 46 | 49 | 49 | 49 | 1119456
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1133612
94 | Gagnagar 102 MW PP (Digital Power) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 82 | 91 |  | 91 | 91 | 91 | 91 | 82 | 41 | 50 | 1592784
95 | Patenga 50MW PP (Baraka) | 50 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 10 | 32 | 37 | 39 | 39 | 39 | 39 |  | 46 | 46 | 46 | 46 | 46 | 47 | 8 | 598560
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [10 empty] | 12 | 15 | 15 | 15 | 15 | 30 | 30 | 30 |  | 15 | 15 | 15 | 15 |  |  | 0 | 213069
100 | Manikganj 55 MW PP (Northern) | [10 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 35 | 35 | 0 | 468709
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 |  | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 2532927
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | 1 | 2 | 1 | 0 | 0 | [8 empty] | 10100
103 | Kamalaghat 54 MW PP(Banco Energy) | [15 empty] | 17 | 17 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 260280
104 | Keranigonj 300 MW PP (APR) | 277 | 290 | 226 | 113 | 68 | [6 empty] | 300 | 301 | 301 | 205 | 95 | 0 |  |  | 115 | 55 | 54 | 300 | 305 | 303 | 298 | 3437439
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 67 | 68 | 68 | 68 | 68 | 68 | 68 | 69 | 68 | 67 |  | 87 | 87 | 88 | 87 | 88 | 69 | 68 | 1708800
112 | Aurahati 100MW PP (Aggreko) | 96 | 97 | 95 | 94 | 94 | [5 empty] | 0 | 95 | 97 | 95 | 60 | 25 | 0 |  |  | 26 | 94 | 60 | 97 | 98 | 97 | 96 | 1376367
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 35 |  | 135 | 135 | 133 | 135 | 135 | 74 | 17 | 972864
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 38 | 30 | 30 |  | 38 | 38 | 38 | 38 | 38 | 38 | 25 | 672000
116 | Chandpur 200MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 427200
117 | Ashuganj 150MW PP (Midland) | 30 | 5 | 5 | 6 | 5 | 6 | 2 | 3 | 5 | 5 | 6 | 5 | 5 | 6 | 5 | 5 | 7 | 13 |  | 47 | 120 | 104 | 125 | 135 | 38 | 5 | 582109
118 | Bibiyana-III 400 MW CCPP | 402 | 395 | 396 | 377 | 377 | 378 | 378 | 378 | 378 | 352 | 314 | 303 | 314 | 300 | 324 | 327 | 352 | 338 |  | 273 | 247 | 288 | 309 | 351 | 340 | 372 | 8270000
| Jamalpur 115 MW PP (United) | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 |  | 85 | 85 | 85 | 85 | 82 | 18 | 18 | 698400
| Anwara 300 MW PP (United) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 120 |  | 292 | 292 | 300 | 300 | 123 | 87 | 88 | 2461418
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 12 | 12 | 12 | 12 | 12 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 38 |  | 38 | 38 | 38 | 38 | 38 | 38 | 25 | 603840
| Anlima Energy Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 745200
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 |  | 0 | 10 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 400320
| Spectra Solar Plant Ltd. | [5 empty] | 2 | 5 | 13 | 17 | 21 | 30 | 31 | 30 | 27 | 20 | 16 | 8 | 3 | [8 empty] | 222532
| Chandpur 115(Doreen) | 48 | 21 | 18 | 18 | 18 | 18 | 18 | 17 | 18 | 18 | 19 | 52 | 54 | 54 | 58 | 76 | 75 | 75 |  | 75 | 94 | 91 | 94 | 76 | 56 | 36 | 1113600
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 27 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 19 | 550800
| Mirsharai 150 MW (Oil) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 36 | 36 | 36 | 36 | 36 | 36 | 18 | 18 | 18 |  | 18 | 104 | 163 | 163 | 108 | 54 | 18 | 948436
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 17 | 17 | 15 | 15 | 11 | 7 | 3 | 13 | 14 | 14 | 16 | 18 | 16 | 17 | 12 | 14 | 12 | 15 |  | 11 | 9 | 8 | 7 | 11 | 6 | 13 | 296208
120 | Eastern Zone Total | 7410 | 7344 | 7219 | 7095 | 7051 | 6716 | 6673 | 6670 | 6672 | 6693 | 6711 | 7240 | 7334 | 7419 | 7325 | 7173 | 7155 | 7151 |  | 8203 | 8216 | 8441 | 8748 | 8465 | 7747 | 7329 | 175904976
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [11 empty] | 16 | 16 |  | 21 | 37 | 55 | 74 |  | 92 | 91 | 91 | 92 | 93 | 62 | 62 | 689280
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL) | 237 | 235 | 234 | 233 | 233 | 231 | 228 | 226 | 230 | 229 | 226 | 222 | 221 | 219 | 219 | 219 | 170 | 150 |  | 224 | 226 | 150 | 229 | 230 | 231 | 231 | 5114782
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 21 | 21 | 21 | 20 | 20 | 15 | 15 | 15 | 14 | 14 | 14 | 14 | 14 | [7 empty] | 7 | 18 | 24 | 24 | 24 | 20 | 298080
| Khulna 225 MW CCPP | 207 | 205 | 205 | 205 | 204 | 203 | 200 | 200 | 200 | 200 | 200 | 194 | 193 | 190 | 192 | 192 | 180 | 145 |  | 170 | 200 | 200 | 200 | 203 | 200 | 200 | 4740077
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 54 | 36 | 36 | 54 | 36 | 36 | 36 | 36 | 36 | 50 | 53 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 65 | 73 | 73 | 72 | 72 | 72 | 1226880
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 3 | 20 | 39 | 67 | 73 | 93 | 78 | 93 | 83 | 68 | 47 | 15 | 7 | [8 empty] | 712080
131 | Rampal 1320 MW (BIFPCL) | 370 | 377 | 370 | 377 | 377 | 377 | 377 | 377 | 372 | 371 | 371 | 371 | 371 | 371 | 371 | 371 | 370 | 377 |  | 377 | 369 | 376 | 376 | 376 | 376 | 376 | 8952727
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 1209600
133 | Bhola Nutan Biddut BD LTD (GAS) | 111 | 111 | 110 | 110 | 111 | 111 | 107 | 107 | 108 | 107 | 107 | 108 | 108 | 108 | 106 | 105 | 101 | 98 |  | 106 | 97 | 108 | 109 | 110 | 109 | 107 | 2549236
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 48 | 48 | 48 | 48 | 48 | 32 | 16 | 698976
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 200 | 200 | 200 | 200 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 260 | 260 | 260 |  | 260 | 260 | 260 | 307 | 307 | 307 | 307 | 6654500
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 173 | 170 | 170 | 168 | 167 | 165 | 163 | 163 | 92 | 85 | 81 | 81 | 81 | 82 | 82 | 82 | 82 | 110 |  | 117 | 171 | 172 | 173 | 170 | 170 | 169 | 3191078
140 | Bhola 33 MW PP (Venture) | 31 | 30 | 29 | 29 | 27 | 25 | 23 | 21 | 21 | 23 | 22 | 25 | 26 | 26 | 28 | 27 | 24 | 21 |  | 30 | 32 | 34 | 35 | 36 | 36 | 37 | 664009
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | 8 | 8 | 8 | [6 empty] | 8 |  |  | 0 | 8 | 8 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 239250
143 | Gopalganj 100 MW Peaking PP | 46 | 46 | 41 | 41 | 41 | 41 | 41 | 25 | 25 | 25 | 25 | 25 | 20 | 20 | 20 | 20 | 20 | 40 |  | 61 | 61 | 72 | 70 | 60 | 53 | 53 | 862464
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 50 | 1487520
146 | Bheramara HVDC | 789 | 790 | 911 | 912 | 912 | 912 | 912 | 912 | 912 | 913 | 911 | 912 | 913 | 913 | 913 | 912 | 911 | 912 |  | 902 | 903 | 903 | 807 | 787 | 743 | 731 | 21262545
147 | Bheramara 410 MW CCPP | 150 | 150 | 150 | 165 | 180 | 185 | 185 | 180 | 180 | 175 | 155 | 145 | 135 | 130 | 130 | 130 | 135 | 135 |  | 135 | 140 | 140 | 150 | 150 | 150 | 150 | 3862368
148 | Payra 1320 MW
149
150 | Barapukuria TPP Unit-1 | 69 | 67 | 68 | 68 | 68 | 66 | 63 | 65 | 66 | 67 | 62 | 62 | 62 | 60 | 62 | 63 | 62 | 65 |  | 66 | 67 | 67 | 67 | 67 | 67 | 68 | 1515490
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 229 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5573500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [22 empty] | 4 | 21 | 21 | 21 | 59344
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 0 | 0 | 3 | 3 | 5 | 4 | 4 | 3 | 2 | 1 | 0 | [8 empty] | 29160
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 107 | 108 | 108 | 108 | 107 | 65 | 28 | 72 | 176 | 181 | 170 | 168 | 167 | 166 | 166 | 166 | 165 | 165 |  | 164 | 166 | 166 | 167 | 167 | 167 | 168 | 3581236
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 147 | 150 | 152 | 154 | 155 | 159 | 164 | 166 | 160 | 153 | 148 | 143 | 140 | 138 | 137 | 138 | 139 | 141 |  | 143 | 144 | 144 | 144 | 145 | 146 | 147 | 3808918
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 414 | 418 | 417 | 414 | 414 | 414 | 414 | 414 | 414 | 414 | 377 | 365 | 347 | 338 | 348 | 361 | 320 |  | 365 | 370 | 378 | 379 | 356 | 402 | 414 | 9261890
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 28 | 28 | 28 | [12 empty] | 5 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 196631
162 | Bogra 22 MW PP (GBB) |  | 18 | 22 | 22 | 22 | 22 | 21 | 19 | 19 | 17 | 17 | 17 | 17 | 17 | 15 | 15 | 16 | 16 |  | 16 | 21 | 21 | 21 | 21 | 22 | 21 | 403200
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 189252
165 | Amnura 50 MW PP(Sinha) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 328420
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 25 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 205540
167 | Katakhali 50 MW Peaking PP | 35 | 35 | 34 | 36 | 36 | 35 | 35 | 35 | 27 | 22 | 30 | 36 | 35 | 35 | 29 | 27 | 21 | 28 |  | 28 | 28 | 36 | 35 | 35 | 35 | 35 | 719606
168 | Santahar 50 MW Peaking PP | 35 | [16 empty] | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 275250
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 15 | 43 | 43 | 43 | 43 | 43 | 0 | 172291
170 | Chapainawabganj 100 MW Peaking PP | 8 | [14 empty] | 6 | 0 |  |  | 46 | 64 | 77 | 80 | 80 | 72 | 65 | 411072
171 | Baghabari 200 MW PP (Paramount) | 133 | 161 | 190 | 190 | 100 | [6 empty] | 0 | 119 | 188 | 150 | 40 | 0 |  |  |  | 96 | 20 | 108 | 190 | 190 | 190 | 2280951
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 50 | 50 | 50 | 50 | 35 | 35 | 968352
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 |  |  |  |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 |  | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 810912
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 |  |  |  | 17 | 33 | 34 | 28 | 34 | 28 | 34 | 34 | 34 | 48 | 56 |  | 56 | 56 | 56 | 56 | 49 | 42 | 34 | 813091
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 2 | 5 | 7 | 7 | 5 | 5 | 5 | 1 | 1 | 1 | [8 empty] | 37859
178 | Energypac Power Venture Thakurgaon Ltd. | [10 empty] | 5 | 35 | 35 | 36 | 36 | 36 | 36 | 40 |  | 109 | 113 | 115 | 115 | 115 | 75 | 35 | 881664
| Intraco Solar 30 MW | [5 empty] | 0 | 3 | 14 | 22 | 28 | 30 | 21 | 26 | 26 | 19 | 4 | 6 | 3 |  | 0 | [6 empty] | 207140
| Adani Power Jharkhanda Ltd | [6 empty] | 22 | 72 | 159 | 269 | 486 | 683 | 687 | 750 | 756 | 759 | 754 | 760 |  | 752 | 752 | 751 | 748 | 750 | 754 | 749 | 10303636
178 | Teesta Solar Limited | [6 empty] | 1 | 13 | 49 | 112 | 179 | 175 | 108 | 155 | 108 | 61 | 26 | 12 | [8 empty] | 1020700