## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-07-05 | Wednesday
|  | Date (day): | 2023-07-05 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12585.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14891 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-07-04 | 2023-07-05 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 180 | 220 | 130 | 180
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180 |  | 190
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 12 | 12 | 96 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 402 | 405 | 400 | 400 |  |  | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 333 | 342 | 330 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 9 | 8 | 8 | 8 | 92 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 300 | 306 | 305 | 305 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 16 | 72 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 30 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 23 | 0 | 23
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  | 3 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 158 | 150 | 100 | 160 |  |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 9 | 70 | 16 | 40 | 60 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 317 | 320 | 280 | 320
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 102 | 48 | 102 | 0
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 0 | 35 |  |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 32 | 54 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 38 | 30 | 45 | 45 |  | 35 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 15 | 15 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 31 | 32 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 0 | 8 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 15 | 195 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
33 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
34 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 15 | 96 | 130 | 130 |  |  | Fuel shortage
35 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 105 | 17 | 105
36 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 53 | 72 | 70 | 72 | 32 |  | Fuel shortage
37 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 72 | 72 | 108 |  |  | Fuel shortage
38 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 34 | 0 | 30 | 0
39 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 34 | 17 | 35 | 20 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6163 | 5822 | 2705 | 3517 | 3652 | 4190 | 486 | 988
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 107 | 106 | 110 | 110 | 70 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
41 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 16 | 8 | 25
42 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 0 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 50 | 6 | 50
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 30 | 30 | 60 | 200 |  | Low Water Level
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 220 | 151 | 151 | 151
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 51 | 17 | 51 | 54 |  | Fuel shortage
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 32 | 73 | 32 | 72 | 26 |  | Fuel shortage
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 31 | 33 | 33 | 33 | 69 |  | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 58 | 80 | 58 | 80 | 20 |  | Fuel shortage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 50 | 100 | 50 | 100
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 8 | 13 | 13 | 13 | 9 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 20 | 42 | 15 | 30
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 88 | 245 | 88 | 300
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 34 | 17 | 34 | 76 |  | Fuel shortage
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 90 | 50 | 90 |  |  | Fuel shortage
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 34 | 51 | 34 | 51 | 65 |  | Fuel shortage
60 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 72 | 157 | 163 | 163 |  |  | On test.
| SS Power I |  | Coal | SS Power | 0 | 0 | 0 | 106 | 0 | 0 | 0 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 0 | 0 | 18 | 10
| Chattogram area Total |  |  |  |  | 2605 | 2545 | 993 | 1339 | 935 | 1440 | 734 | 330
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 205 | 198 | 200 | 200 | 21 |  | Gas shortage
62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 330 | 300 | 330 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint
64 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 322 | 273 | 220 | 270 | 130 |  | Gas shortage
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 41 | 46 | 46
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 123 | 158 | 150 | 150
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 10 | 43 |  | 8 | Engine problem
69 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 6 | 128 | 5 | 150
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 36 | 36 | 36 | 36
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
72 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 68 | 103 | 50 | 100 | 100 |  | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 20 | 20 | 20
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 140 | 152 | 129 | 152
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 31 | 32 | 32 | 32
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 40 | 43 | 43 | 43 | 9 |  | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Contract Expired
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 105 | 105 | 105
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 27 | 58 | 9 | 55 | 58
81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 75 | 94 | 55 | 115
| Cumilla Area Total |  |  |  |  | 3159 | 3096 | 1537 | 1861 | 1458 | 1895 | 318 | 573
83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 194 | 153 | 200 | 200
84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 13 | 20 | 20
85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 24 | 112 | 65 | 85 | 115 |  | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 38 | 56 | 38 | 85 | 30 |  | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 21 | 0 | 50 | 0
90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 12 | 12 | 10 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 296 | 346 | 386.6 | 402 | 0 | 0
91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 39 | 30 | 30 |  | 60 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint.
94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 47 | 50 | 50
96 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 41 | 47 | 50 | 50
97 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 61 | 60 | 60
99 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 85 | 86 | 86
100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 135 | 132 | 135 | 135 |  | 96 | ST Under maint
102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 18 | 17 | 17
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
103 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24 |  |  | Gas shortage
104 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 290 | 0 | 0 |  |  | Machine tripped at 09:02
105 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 366 | 406 | 400 | 400
106 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
107 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 350 | 378 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1503 | 1588 | 1316 | 1316 | 0 | 776
108 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 909 | 814 | 934 | 934
109 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 64 | 49 | 98 |  | 17 | Engine problem
110 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 32 | 20 | 32 |  | 22 | Engine problem
111 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 150 | 150 |  | 80
112 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 65 | 36 | 78 |  | 31 | Engine problem
113 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 350 | 400 | 350 | 400 | 10
114 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 16 | 24 | 16 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
115 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 5 | 17 | 17 | 17 | 88 |  | Fuel shortage
116 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 15 | 105
117 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 54 | 0 | 100 | 0
118 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 220 | 220 | 0 | 0 | 0 | 0 |  |  | On test.
119 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0 |  | 617 | Under maint
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3125 | 3121 | 1318 | 1415 | 1687 | 1838 | 130 | 767
120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 96 | 16 | 96 | 14 |  | Fuel shortage
121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 19 | 29 | 25 | 38
122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 67 | 65 | 65 |  | 129 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 460 | 622 | 622 | 622 |  | 622 | Unit-2 Under maint
124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 222 | 220 | 220
125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 17 | 150
126 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 150 | 150 | 130 | 130 | 177 |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 865 | 1203 | 1095 | 1321 | 191 | 751
127 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 60 | 60 | 65 | 65
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
128 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 28 | 30 | 30 |  | 22 | Engine problem
129 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 35 |  | 36 | Engine problem
130 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0 | 28 |  | Fuel shortage
131 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 8 | 0 | 34 | 16 |  | Fuel shortage
132 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 22 | 0 | 30 |  | 20 | Engine problem
133 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 183 | 171 | 150 | 180 | 30 |  | Gas shortage
134 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 163 | 185 | 160 | 185 | 35 |  | Gas shortage
136 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 422 | 415 | 414 | 414
137 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 35 | 35 |  | 15 | Engine problem
138 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 6 | 8 | 8 |  | 3 | Engine problem
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 52
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 82 | 40 | 82 |  | 22 | Engine problem
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 200
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 50 | 35 | 50 |  |  | Fuel shortage
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 113 | 55 | 113
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 748*1 | 748 | 748 | 613 | 622 | 611 | 611
| Rajshahi Area Total |  |  |  |  | 2927 | 2905 | 1524 | 1805 | 1639 | 2124 | 429 | 118
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 180 | 180 | 180 | 180
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 34 | 34 | 70 |  |  | Fuel shortage
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 114 | 35 | 115
153 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 7 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 53 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 310 | 328 | 417 | 365 | 125 | 85
| Total |  |  |  |  | 24263 | 23545 | 11051 | 13402 | 12585.6 | 14891 | 2413 | 4388
A. |  | 2023-07-04 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 13474 | MW at | 23:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 9961 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13440 | MW
3 | Day peak Generation : |  |  | 11051 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12847.25 | MW
4 | Evening peak Generation : |  |  | 13402 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 36 | MW
5 | Total Energy Generation : |  | 277.1939 | MKWHr | By Solar | 1.9482 | MKWHr
| By Gas : | 166.3714 | MKWHr |  | By Oil: | 46.1798 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 36.9427 | MKWHr |  | By Hydro: | 0.82218 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2413 | MW | Dhaka | 3843.35 | 3843.35 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 4388 | MW | Chittagong | 1349.9 | 1349.9 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 6801 | MW | Khulna | 1819 | 1819 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 1293.54 | MMCFD |  |  | Rajshahi | 1386 | 1386 |  | 0 |  | 20:00 |  | 16
8 | Fuel Cost : | i) Gas : | Taka | 186259976.548 | ii) Oil : | Taka | 577674465.3 | Comilla | 1410 | 1410 |  | 0 |  | 21:00 |  | 36
|  | iii) Coal : | Taka | 118568386 | Total | Taka | 882502827.848 | Mymensingh | 1101 | 1101 |  | 0 |  | 22:00 |  | 15.28
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 573 | 573 |  | 0 |  | 23:00 |  | 177.63
| ii) During Peak Demand : |  |  | 476 | MW (E to W) at | 21:00 | hrs | Barisal | 499 | 499 |  | 0 |  | 24:00 |  | 186.225
| iii) Maximum : |  |  | 430 | MW at | 22:00 | hrs | Rangpur | 866 | 830 |  | 36
10 | Maximum Temperature in Dhaka was |  |  |  | 36.0° C |  |  | Total | 12847.25 | 12811.25 |  | 36
B. |  | 2023-07-05 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 36.0° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 13900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14891 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 11700 | MW
4 | Reserve(Generation end) |  |  |  | 991 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 285.9578 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10481 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.5295 | MKWHr. | ii) HVDC Flow at Peak Time |  | 814 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.4002 | MKWHr. | iii) Maximum HVDC Flow : |  | 916 | MW at | 4:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 73.2 |  | (b) Today: | 73.21 |  | (c) Rule Curve: |  | 84.64
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-07-04 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 150 | 180 | 0 | 12 | 0 | 398 | 347 |  | 0 | 450 | 272 | 9 | 50 | 15 | 326 | 0 | 160 | 25 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 19 | 20 | 8 | 15 | 20 | 8 | 0 | 30 | 0 | 109 | 0 | 8 | 223 | 0 | 0 | 0 |  | 12 | 34 | 33 | 58 | 0 | 16 | 13 | 42 | 0 | 0 | 0 | 280 | 0 | 186 | 180 | 0 | 20 | 0 | 0 | 43 | 0 | 36 | 43 | 20 | 10 | 32 | 20 | 148 | 199 | 0 | 18 | 0 | 43 | 30 | 47 | 45 | 0 | 0 | 61 | 85 | 0 | 137 | 18 | 0 | 10 | 300 | 24 | 5 | 0 | 120 | 0 | 0 | 47 | 0 | 62 | 0 | 50 | 17 | 16 | 329 | 38 | 50 | 34 | 0 | 88 | 17 | 17 | 105 | 9 | 50 | 382 | 51 | 0 | 72 | 17 | 0 | 17 | 0 | 87 | 17 | 292 | 108 | 0 | 305 | 0 |  | 858 | 0 | 355 | 0 | 95 | 0 | 0 | 0 | 18 | 47 | 40 | 0 | 30 | 90 | 0 | 0 | 65 | 0 | 21 | 0 | 0 | 0 | 0 | 52 | 35 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 420 | 17 | 0 | 92 | 85 | 107 | 0 | 0 | 113 | 0 | 225 | 0 | 100 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 150 | 619 | 0 | 0 |  | 7628 | 4279 | 11907 | 4557 | 858 | 2508 | 0 | 2220 | 1254 | 30 | 0 | 332 | 148 | 0 | 0 | 179.54 | 73.2
2:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 397 | 337 |  | 0 | 450 | 274 | 8 | 50 | 15 | 327 | 0 | 120 | 9 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 8 | 15 | 20 | 8 | 0 | 30 | 0 | 107 | 0 | 8 | 227 | 0 | 0 | 0 |  | 12 | 34 | 33 | 58 | 0 | 6 | 13 | 42 | 0 | 0 | 0 | 280 | 0 | 183 | 182 | 0 | 20 | 0 | 0 | 43 | 0 | 36 | 43 | 20 | 10 | 32 | 20 | 146 | 202 | 0 | 18 | 0 | 43 | 30 | 47 | 45 | 0 | 0 | 61 | 85 | 0 | 137 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 120 | 0 | 0 | 47 | 0 | 92 | 0 | 50 | 17 | 6 | 331 | 38 | 70 | 34 | 0 | 88 | 17 | 17 | 105 | 9 | 50 | 382 | 19 | 0 | 72 | 17 | 0 | 17 | 0 | 36 | 17 | 293 | 108 | 0 | 303 | 0 |  | 858 | 0 | 350 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 29 | 96 | 0 | 0 | 65 | 0 | 28 | 0 | 0 | 0 | 0 | 52 | 35 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 359 | 17 | 0 | 110 | 85 | 107 | 0 | 0 | 113 | 0 | 225 | 0 | 100 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 150 | 619 | 0 | 0 |  | 7431 | 4140 | 11571 | 4489 | 858 | 2430 | 0 | 2092 | 1252 | 30 | 0 | 274 | 146 | 0 | 0 | 161.395 | 73.2
3:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 396 | 336 |  | 0 | 450 | 277 | 0 | 42 | 0 | 327 | 0 | 99 | 9 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 8 | 15 | 20 | 8 | 0 | 30 | 0 | 108 | 0 | 8 | 224 | 0 | 0 | 0 |  | 12 | 34 | 33 | 58 | 0 | 6 | 13 | 42 | 0 | 0 | 0 | 280 | 0 | 183 | 189 | 0 | 20 | 0 | 0 | 43 | 0 | 36 | 43 | 20 | 10 | 32 | 20 | 142 | 199 | 0 | 18 | 0 | 43 | 30 | 47 | 45 | 0 | 0 | 61 | 85 | 0 | 136 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 120 | 0 | 0 | 47 | 0 | 101 | 0 | 50 | 17 | 6 | 331 | 38 | 50 | 34 | 0 | 88 | 17 | 17 | 105 | 9 | 50 | 375 | 17 | 0 | 72 | 17 | 0 | 17 | 0 | 24 | 17 | 293 | 108 | 0 | 305 | 0 |  | 915 | 0 | 360 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 96 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 360 | 17 | 0 | 110 | 15 | 107 | 0 | 0 | 113 | 57 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 620 | 0 | 0 |  | 7337 | 3748 | 11085 | 4399 | 915 | 2429 | 0 | 1647 | 1312 | 30 | 0 | 211 | 142 | 0 | 0 | 153.755 | 73.2
4:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 397 | 342 |  | 0 | 450 | 269 | 0 | 7 | 0 | 329 | 0 | 99 | 9 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 8 | 15 | 20 | 0 | 0 | 30 | 0 | 108 | 0 | 8 | 226 | 0 | 0 | 0 |  | 12 | 34 | 33 | 58 | 0 | 6 | 13 | 36 | 0 | 0 | 0 | 280 | 0 | 183 | 189 | 0 | 21 | 0 | 0 | 43 | 0 | 36 | 43 | 20 | 10 | 32 | 20 | 142 | 201 | 0 | 18 | 0 | 43 | 30 | 47 | 45 | 0 | 0 | 61 | 85 | 0 | 135 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 120 | 0 | 0 | 47 | 0 | 80 | 0 | 50 | 17 | 5 | 331 | 38 | 35 | 34 | 0 | 88 | 17 | 17 | 105 | 9 | 50 | 365 | 17 | 0 | 72 | 17 | 0 | 17 | 0 | 18 | 17 | 292 | 108 | 0 | 303 | 0 |  | 916 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 48 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 358 | 17 | 0 | 110 | 0 | 107 | 0 | 0 | 113 | 120 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 613 | 0 | 0 |  | 7247 | 3719 | 10966 | 4390 | 916 | 2429 | 0 | 1482 | 1366 | 30 | 0 | 211 | 142 | 0 | 0 | 141.34 | 73.2
5:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 396 | 342 |  | 0 | 450 | 285 | 0 | 0 | 0 | 329 | 0 | 101 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 8 | 15 | 20 | 0 | 0 | 30 | 0 | 104 | 0 | 8 | 226 | 0 | 0 | 0 |  | 0 | 34 | 33 | 58 | 0 | 6 | 13 | 42 | 0 | 0 | 0 | 275 | 0 | 210 | 189 | 0 | 21 | 0 | 0 | 43 | 0 | 36 | 43 | 20 | 10 | 32 | 20 | 140 | 198 | 0 | 18 | 0 | 43 | 30 | 47 | 45 | 0 | 0 | 61 | 85 | 0 | 135 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 47 | 0 | 42 | 0 | 50 | 17 | 6 | 329 | 38 | 35 | 34 | 0 | 88 | 17 | 17 | 105 | 9 | 50 | 365 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 18 | 17 | 292 | 108 | 0 | 301 | 0 |  | 916 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 16 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 180 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 358 | 17 | 0 | 70 | 0 | 50 | 0 | 0 | 113 | 190 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 610 | 0 | 0 |  | 6973 | 3654 | 10627 | 4401 | 916 | 2451 | 0 | 1047 | 1431 | 30 | 0 | 211 | 140 | 0 | 0 | 101.23 | 73.2
6:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 377 | 308 |  | 0 | 400 | 273 | 0 | 0 | 0 | 300 | 0 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 8 | 15 | 20 | 0 | 0 | 30 | 0 | 105 | 0 | 8 | 225 | 0 | 0 | 0 |  | 0 | 34 | 33 | 58 | 0 | 6 | 13 | 42 | 0 | 0 | 0 | 275 | 0 | 210 | 148 | 0 | 21 | 0 | 0 | 43 | 0 | 36 | 43 | 20 | 10 | 32 | 20 | 124 | 198 | 0 | 18 | 0 | 43 | 30 | 47 | 45 | 0 | 0 | 60 | 85 | 0 | 135 | 18 | 0 | 10 | 285 | 24 | 8 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 2 | 50 | 17 | 0 | 331 | 38 | 0 | 34 | 0 | 88 | 17 | 17 | 105 | 9 | 50 | 365 | 17 | 1 | 0 | 17 | 0 | 17 | 2 | 17 | 0 | 292 | 36 | 0 | 304 | 0 |  | 916 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 180 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 353 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 230 | 225 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 150 | 611 | 0 | 0 |  | 6578 | 3458 | 10036 | 4353 | 916 | 2302 | 0 | 689 | 1475 | 30 | 0 | 139 | 124 | 8 | 0 | 93.59 | 73.2
7:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 342 | 307 |  | 0 | 400 | 272 | 0 | 0 | 0 | 280 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 8 | 15 | 20 | 0 | 0 | 30 | 0 | 109 | 0 | 8 | 223 | 0 | 0 | 0 |  | 0 | 34 | 33 | 58 | 0 | 6 | 13 | 42 | 0 | 0 | 0 | 350 | 0 | 210 | 108 | 0 | 21 | 0 | 0 | 10 | 0 | 36 | 43 | 20 | 10 | 32 | 20 | 126 | 198 | 0 | 16 | 0 | 43 | 30 | 11 | 45 | 0 | 0 | 40 | 85 | 0 | 135 | 17 | 0 | 10 | 295 | 24 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 8 | 50 | 17 | 0 | 337 | 38 | 0 | 34 | 2 | 88 | 17 | 17 | 105 | 9 | 50 | 365 | 17 | 8 | 0 | 17 | 0 | 17 | 6 | 18 | 0 | 292 | 0 | 0 | 303 | 0 |  | 916 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 358 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 240 | 225 | 0 | 0 | 1 | 29 | 0 | 0 | 0 | 0 | 0 | 150 | 611 | 6 | 0 |  | 6445 | 3516 | 9961 | 4372 | 916 | 2203 | 0 | 667 | 1484 | 30 | 0 | 103 | 126 | 60 | 0 | 84.995 | 73.2
8:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 342 | 307 |  | 0 | 400 | 282 | 8 | 0 | 0 | 280 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 8 | 15 | 20 | 0 | 0 | 30 | 0 | 110 | 0 | 8 | 223 | 0 | 0 | 0 |  | 0 | 34 | 33 | 58 | 0 | 6 | 13 | 24 | 0 | 0 | 0 | 310 | 0 | 210 | 108 | 0 | 23 | 0 | 0 | 10 | 0 | 36 | 43 | 20 | 10 | 32 | 20 | 124 | 198 | 0 | 16 | 0 | 43 | 30 | 44 | 45 | 0 | 0 | 60 | 85 | 0 | 135 | 17 | 0 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 7 | 50 | 17 | 0 | 331 | 38 | 2 | 34 | 2 | 88 | 17 | 17 | 105 | 9 | 50 | 361 | 17 | 16 | 0 | 17 | 0 | 17 | 18 | 18 | 0 | 292 | 0 | 0 | 308 | 0 |  | 916 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 358 | 0 | 0 | 0 | 0 | 34 | 0 | 1 | 0 | 260 | 224 | 0 | 0 | 2 | 54 | 0 | 0 | 0 | 0 | 1 | 150 | 611 | 14 | 0 |  | 6478 | 3565 | 10043 | 4339 | 916 | 2230 | 0 | 677 | 1509 | 30 | 0 | 103 | 124 | 115 | 0 | 20.055 | 73.2
9:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 342 | 307 |  | 0 | 400 | 285 | 8 | 0 | 0 | 280 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 8 | 15 | 20 | 0 | 0 | 30 | 0 | 108 | 0 | 8 | 221 | 0 | 0 | 0 |  | 0 | 34 | 33 | 58 | 0 | 6 | 13 | 21 | 0 | 0 | 0 | 310 | 0 | 208 | 108 | 0 | 42 | 0 | 0 | 10 | 0 | 36 | 43 | 20 | 10 | 32 | 20 | 118 | 196 | 0 | 17 | 1 | 43 | 30 | 44 | 45 | 0 | 0 | 60 | 85 | 0 | 135 | 17 | 0 | 10 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 15 | 50 | 17 | 0 | 331 | 38 | 17 | 34 | 1 | 88 | 17 | 17 | 105 | 9 | 50 | 365 | 31 | 29 | 0 | 17 | 0 | 17 | 25 | 18 | 0 | 292 | 0 | 0 | 305 | 0 |  | 916 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 358 | 0 | 0 | 0 | 0 | 34 | 0 | 1 | 0 | 350 | 220 | 0 | 0 | 2 | 78 | 0 | 0 | 0 | 0 | 2 | 150 | 610 | 67 | 0 |  | 6535 | 3716 | 10251 | 4345 | 916 | 2216 | 0 | 706 | 1596 | 30 | 0 | 103 | 118 | 221 | 0 | 20.055 | 73.2
10:00 | 0 | 0 | 150 | 180 | 0 | 12 | 0 | 349 | 338 |  | 0 | 400 | 286 | 9 | 0 | 0 | 280 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 8 | 15 | 20 | 0 | 0 | 30 | 0 | 110 | 0 | 8 | 221 | 0 | 0 | 0 |  | 0 | 34 | 33 | 58 | 0 | 6 | 13 | 21 | 0 | 0 | 0 | 305 | 0 | 206 | 108 | 0 | 33 | 0 | 0 | 10 | 0 | 36 | 43 | 20 | 10 | 31 | 20 | 132 | 195 | 0 | 17 | 2 | 43 | 30 | 44 | 42 | 0 | 0 | 59 | 85 | 0 | 135 | 17 | 0 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 50 | 29 | 0 | 374 | 38 | 17 | 34 | 2 | 88 | 17 | 17 | 34 | 9 | 50 | 350 | 49 | 30 | 0 | 17 | 0 | 17 | 31 | 18 | 0 | 385 | 0 | 0 | 305 | 0 |  | 916 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 359 | 0 | 0 | 0 | 0 | 34 | 0 | 1 | 0 | 370 | 220 | 0 | 0 | 1 | 92 | 0 | 0 | 0 | 0 | 2 | 150 | 610 | 7 | 0 |  | 6673 | 3694 | 10367 | 4482 | 916 | 2255 | 0 | 666 | 1615 | 30 | 0 | 103 | 132 | 168 | 0 | 79.265 | 73.2
11:00 | 0 | 0 | 150 | 180 | 0 | 12 | 0 | 403 | 336 |  | 0 | 400 | 265 | 8 | 0 | 0 | 280 | 0 | 101 | 4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 20 | 8 | 15 | 20 | 0 | 0 | 30 | 0 | 108 | 0 | 8 | 221 | 0 | 0 | 0 |  | 0 | 34 | 33 | 58 | 0 | 6 | 13 | 20 | 0 | 0 | 0 | 305 | 0 | 206 | 108 | 0 | 34 | 0 | 0 | 32 | 0 | 36 | 43 | 20 | 10 | 28 | 20 | 134 | 192 | 0 | 15 | 2 | 43 | 30 | 44 | 44 | 0 | 0 | 60 | 85 | 0 | 135 | 17 | 0 | 10 | 290 | 24 | 8 | 0 | 8 | 0 | 0 | 24 | 0 | 0 | 14 | 50 | 54 | 5 | 367 | 38 | 17 | 34 | 3 | 88 | 17 | 17 | 34 | 8 | 50 | 350 | 53 | 29 | 17 | 34 | 0 | 17 | 34 | 50 | 7 | 385 | 47 | 0 | 240 | 0 |  | 916 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 317 | 0 | 0 | 6 | 0 | 34 | 0 | 1 | 35 | 430 | 220 | 0 | 0 | 5 | 101 | 10 | 0 | 0 | 0 | 3 | 150 | 611 | 11 | 0 |  | 6838 | 3777 | 10615 | 4514 | 916 | 2203 | 0 | 854 | 1611 | 30 | 0 | 150 | 134 | 203 | 0 | 0 | 73.2
12:00 | 0 | 0 | 180 | 180 | 0 | 12 | 0 | 402 | 333 |  | 0 | 450 | 300 | 9 | 16 | 0 | 317 | 0 | 158 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 19 | 20 | 18 | 15 | 31 | 0 | 0 | 30 | 0 | 107 | 0 | 8 | 220 | 0 | 0 | 0 |  | 0 | 32 | 31 | 58 | 0 | 6 | 8 | 20 | 0 | 0 | 0 | 305 | 0 | 205 | 123 | 0 | 33 | 0 | 0 | 43 | 0 | 36 | 40 | 19 | 10 | 31 | 20 | 140 | 194 | 0 | 17 | 2 | 43 | 20 | 44 | 41 | 0 | 0 | 60 | 85 | 0 | 135 | 17 | 0 | 10 | 300 | 24 | 8 | 0 | 15 | 0 | 0 | 24 | 0 | 15 | 0 | 50 | 68 | 6 | 366 | 38 | 17 | 34 | 5 | 88 | 17 | 17 | 17 | 27 | 50 | 350 | 53 | 21 | 17 | 34 | 0 | 17 | 34 | 75 | 17 | 322 | 72 | 0 | 106 | 0 |  | 909 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 422 | 5 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 460 | 220 | 0 | 0 | 5 | 54 | 35 | 0 | 0 | 0 | 7 | 150 | 613 | 53 | 0 |  | 7034 | 4017 | 11051 | 4618 | 909 | 2422 | 0 | 1070 | 1509 | 30 | 0 | 171 | 140 | 182 | 0 | 0 | 73.2
13:00 | 0 | 0 | 220 | 180 | 0 | 12 | 0 | 400 | 327 |  | 0 | 450 | 303 | 9 | 17 | 0 | 315 | 0 | 185 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 19 | 20 | 18 | 15 | 31 | 0 | 0 | 30 | 0 | 106 | 0 | 8 | 215 | 0 | 0 | 0 |  | 0 | 30 | 31 | 69 | 0 | 6 | 13 | 20 | 0 | 0 | 0 | 325 | 0 | 202 | 147 | 0 | 33 | 0 | 0 | 43 | 0 | 36 | 34 | 19 | 10 | 31 | 20 | 146 | 193 | 0 | 17 | 1 | 43 | 20 | 47 | 41 | 0 | 0 | 59 | 85 | 0 | 135 | 17 | 0 | 10 | 305 | 24 | 8 | 0 | 15 | 0 | 0 | 8 | 0 | 15 | 12 | 75 | 68 | 10 | 400 | 38 | 34 | 34 | 5 | 88 | 17 | 17 | 17 | 27 | 76 | 350 | 53 | 10 | 17 | 34 | 0 | 17 | 34 | 75 | 17 | 338 | 106 | 0 | 0 | 0 |  | 909 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 419 | 12 | 0 | 35 | 0 | 34 | 0 | 2 | 35 | 530 | 217 | 0 | 0 | 5 | 102 | 35 | 0 | 0 | 0 | 8 | 150 | 614 | 45 | 0 |  | 7202 | 4204 | 11406 | 4816 | 909 | 2447 | 0 | 1157 | 1474 | 30 | 0 | 203 | 146 | 224 | 0 | 0 | 73.2
14:00 | 0 | 0 | 220 | 180 | 0 | 12 | 0 | 396 | 327 |  | 0 | 450 | 304 | 0 | 17 | 0 | 313 | 0 | 187 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 19 | 20 | 18 | 15 | 31 | 0 | 0 | 30 | 0 | 107 | 0 | 8 | 217 | 0 | 0 | 0 |  | 0 | 32 | 31 | 69 | 0 | 6 | 13 | 17 | 0 | 0 | 0 | 310 | 0 | 204 | 147 | 0 | 33 | 0 | 0 | 43 | 0 | 36 | 41 | 17 | 10 | 30 | 20 | 148 | 174 | 0 | 17 | 2 | 43 | 20 | 44 | 43 | 0 | 0 | 59 | 84 | 0 | 132 | 17 | 0 | 10 | 320 | 24 | 8 | 0 | 17 | 0 | 0 | 8 | 0 | 17 | 13 | 75 | 68 | 11 | 366 | 56 | 34 | 34 | 2 | 87 | 17 | 17 | 17 | 26 | 76 | 350 | 53 | 14 | 83 | 34 | 0 | 17 | 26 | 76 | 17 | 322 | 157 | 0 | 0 | 0 |  | 909 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 16 | 0 | 0 | 60 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 419 | 17 | 0 | 38 | 0 | 34 | 0 | 2 | 35 | 560 | 219 | 0 | 0 | 2 | 56 | 35 | 0 | 0 | 0 | 14 | 150 | 620 | 83 | 0 |  | 7276 | 4259 | 11535 | 4735 | 909 | 2458 | 0 | 1267 | 1510 | 30 | 0 | 264 | 148 | 214 | 0 | 0 | 73.2
15:00 | 0 | 0 | 220 | 180 | 0 | 12 | 0 | 403 | 321 |  | 0 | 450 | 305 | 0 | 17 | 0 | 318 | 0 | 152 | 9 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 20 | 18 | 15 | 31 | 0 | 0 | 30 | 0 | 106 | 0 | 8 | 218 | 0 | 0 | 0 |  | 0 | 32 | 31 | 69 | 0 | 6 | 13 | 17 | 0 | 0 | 0 | 320 | 0 | 202 | 147 | 0 | 40 | 0 | 0 | 43 | 0 | 36 | 41 | 17 | 10 | 29 | 20 | 154 | 161 | 0 | 17 | 1 | 43 | 22 | 22 | 43 | 0 | 0 | 59 | 84 | 0 | 132 | 17 | 0 | 10 | 290 | 24 | 8 | 0 | 86 | 0 | 0 | 8 | 0 | 17 | 11 | 75 | 68 | 13 | 378 | 56 | 34 | 34 | 2 | 87 | 17 | 17 | 17 | 28 | 63 | 359 | 53 | 28 | 103 | 34 | 0 | 17 | 17 | 66 | 17 | 300 | 157 | 0 | 0 | 0 |  | 909 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 21 | 48 | 0 | 0 | 60 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 180 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 420 | 17 | 0 | 50 | 0 | 34 | 0 | 2 | 35 | 600 | 218 | 0 | 0 | 2 | 57 | 35 | 0 | 0 | 0 | 17 | 150 | 620 | 64 | 0 |  | 7275 | 4362 | 11637 | 4727 | 909 | 2403 | 0 | 1399 | 1550 | 30 | 0 | 264 | 154 | 201 | 0 | 122.24 | 73.2
16:00 | 0 | 0 | 220 | 180 | 0 | 12 | 0 | 400 | 321 |  | 0 | 450 | 298 | 0 | 17 | 0 | 315 | 0 | 155 | 9 | 50 | 0 | 9 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 8 | 18 | 15 | 31 | 0 | 0 | 30 | 0 | 104 | 0 | 8 | 221 | 0 | 0 | 0 |  | 0 | 33 | 33 | 58 | 0 | 6 | 13 | 17 | 0 | 0 | 0 | 305 | 0 | 204 | 147 | 0 | 39 | 0 | 0 | 43 | 0 | 36 | 41 | 18 | 10 | 29 | 20 | 150 | 161 | 0 | 17 | 1 | 41 | 39 | 22 | 43 | 0 | 0 | 59 | 84 | 0 | 132 | 17 | 0 | 10 | 310 | 24 | 8 | 0 | 95 | 0 | 0 | 8 | 0 | 17 | 6 | 50 | 68 | 18 | 367 | 56 | 34 | 34 | 3 | 87 | 17 | 17 | 17 | 27 | 50 | 350 | 53 | 27 | 108 | 34 | 0 | 17 | 18 | 40 | 17 | 234 | 157 | 0 | 0 | 0 |  | 909 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 22 | 96 | 0 | 0 | 60 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 417 | 17 | 0 | 50 | 0 | 34 | 0 | 1 | 35 | 600 | 218 | 0 | 0 | 0 | 30 | 35 | 0 | 0 | 0 | 15 | 150 | 619 | 53 | 0 |  | 7137 | 4382 | 11519 | 4647 | 909 | 2414 | 0 | 1399 | 1549 | 30 | 0 | 267 | 150 | 154 | 0 | 125.105 | 73.2
17:00 | 0 | 0 | 170 | 180 | 0 | 12 | 0 | 403 | 302 |  | 0 | 380 | 292 | 0 | 17 | 0 | 270 | 0 | 99 | 9 | 24 | 0 | 14 | 0 | 0 | 0 | 0 | 55 | 35 | 0 | 8 | 18 | 15 | 31 | 0 | 0 | 30 | 0 | 103 | 0 | 8 | 220 | 0 | 0 | 0 |  | 0 | 33 | 33 | 58 | 0 | 6 | 13 | 21 | 0 | 0 | 0 | 310 | 0 | 183 | 148 | 0 | 39 | 0 | 0 | 43 | 0 | 32 | 41 | 19 | 10 | 30 | 20 | 138 | 165 | 0 | 13 | 1 | 41 | 39 | 44 | 43 | 0 | 0 | 59 | 85 | 0 | 132 | 17 | 0 | 10 | 280 | 24 | 8 | 0 | 45 | 0 | 0 | 8 | 0 | 17 | 2 | 50 | 68 | 18 | 367 | 56 | 34 | 37 | 0 | 87 | 17 | 17 | 17 | 28 | 50 | 350 | 58 | 14 | 72 | 34 | 0 | 17 | 9 | 39 | 22 | 237 | 140 | 0 | 0 | 0 |  | 908 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 66 | 17 | 64 | 0 | 0 | 60 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 376 | 17 | 0 | 35 | 0 | 34 | 0 | 1 | 55 | 600 | 219 | 0 | 0 | 1 | 19 | 35 | 0 | 0 | 0 | 10 | 150 | 622 | 49 | 0 |  | 6743 | 4231 | 10974 | 4422 | 908 | 2272 | 0 | 1298 | 1552 | 30 | 0 | 248 | 138 | 106 | 0 | 129.88 | 73.2
18:00 | 0 | 0 | 140 | 180 | 0 | 12 | 0 | 348 | 252 |  | 0 | 300 | 267 | 6 | 17 | 0 | 250 | 0 | 76 | 9 | 24 | 0 | 23 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 8 | 18 | 15 | 31 | 0 | 0 | 60 | 0 | 102 | 0 | 13 | 223 | 0 | 0 | 0 |  | 0 | 33 | 33 | 58 | 0 | 43 | 13 | 32 | 0 | 0 | 0 | 275 | 0 | 183 | 148 | 0 | 38 | 0 | 0 | 43 | 0 | 35 | 41 | 20 | 10 | 31 | 20 | 132 | 150 | 0 | 13 | 0 | 41 | 39 | 47 | 42 | 0 | 0 | 40 | 40 | 0 | 132 | 18 | 0 | 10 | 260 | 16 | 8 | 0 | 45 | 0 | 0 | 8 | 0 | 17 | 1 | 50 | 86 | 35 | 367 | 66 | 34 | 51 | 0 | 119 | 17 | 20 | 52 | 28 | 50 | 350 | 73 | 4 | 72 | 38 | 0 | 17 | 2 | 48 | 34 | 200 | 163 | 0 | 0 | 0 |  | 908 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 52 | 21 | 64 | 0 | 0 | 60 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 303 | 17 | 0 | 35 | 7 | 34 | 0 | 1 | 55 | 550 | 182 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 0 | 3 | 150 | 621 | 28 | 0 |  | 6629 | 3914 | 10543 | 4054 | 908 | 1959 | 0 | 1586 | 1501 | 60 | 0 | 287 | 132 | 56 | 0 | 0 | 73.2
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 160 | 180 | 0 | 12 | 0 | 311 | 300 |  | 0 | 420 | 298 | 8 | 17 | 8 | 250 | 0 | 159 | 12 | 24 | 16 | 23 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 8 | 18 | 15 | 31 | 8 | 0 | 60 | 0 | 109 | 0 | 16 | 145 | 0 | 0 | 0 |  | 5 | 33 | 33 | 72 | 0 | 48 | 13 | 26 | 0 | 0 | 0 | 330 | 0 | 195 | 148 | 0 | 41 | 0 | 0 | 43 | 0 | 35 | 42 | 20 | 10 | 32 | 20 | 150 | 144 | 0 | 13 | 0 | 43 | 39 | 22 | 42 | 0 | 0 | 40 | 70 | 0 | 132 | 18 | 0 | 10 | 270 | 24 | 8 | 0 | 69 | 0 | 0 | 22 | 0 | 21 | 0 | 88 | 105 | 68 | 350 | 57 | 52 | 51 | 0 | 170 | 17 | 34 | 105 | 57 | 50 | 367 | 73 | 0 | 72 | 51 | 0 | 17 | 0 | 81 | 34 | 262 | 161 | 0 | 0 | 0 |  | 909 | 0 | 300 | 0 | 18 | 0 | 0 | 0 | 26 | 35 | 8 | 65 | 26 | 64 | 0 | 0 | 60 | 0 | 0 | 70 | 0 | 0 | 28 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 137 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 333 | 17 | 0 | 35 | 15 | 34 | 0 | 0 | 100 | 530 | 220 | 0 | 17 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 150 | 620 | 1 | 0 |  | 7377 | 4224 | 11601 | 4202 | 909 | 2240 | 0 | 2087 | 1480 | 60 | 0 | 472 | 150 | 1 | 0 | 0 | 73.2
19:30 | 0 | 0 | 220 | 180 | 0 | 12 | 0 | 405 | 312 |  | 0 | 450 | 273 | 9 | 40 | 30 | 318 | 0 | 197 | 30 | 64 | 48 | 23 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 8 | 18 | 15 | 31 | 16 | 0 | 60 | 0 | 103 | 0 | 16 | 152 | 0 | 0 | 0 |  | 12 | 33 | 33 | 80 | 0 | 50 | 13 | 35 | 0 | 0 | 0 | 310 | 0 | 183 | 148 | 0 | 41 | 0 | 0 | 43 | 0 | 35 | 43 | 20 | 10 | 32 | 20 | 154 | 151 | 0 | 13 | 0 | 43 | 40 | 44 | 42 | 0 | 0 | 61 | 85 | 0 | 132 | 18 | 0 | 10 | 260 | 24 | 8 | 0 | 130 | 0 | 0 | 104 | 0 | 63 | 0 | 88 | 100 | 115 | 416 | 56 | 95 | 51 | 0 | 292 | 17 | 34 | 105 | 57 | 90 | 389 | 73 | 0 | 108 | 51 | 0 | 17 | 0 | 94 | 34 | 278 | 161 | 0 | 0 | 0 |  | 909 | 0 | 390 | 0 | 69 | 0 | 0 | 0 | 36 | 50 | 40 | 54 | 28 | 64 | 0 | 0 | 60 | 21 | 0 | 92 | 0 | 0 | 28 | 0 | 35 | 0 | 0 | 6 | 0 | 0 | 180 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 421 | 17 | 0 | 50 | 43 | 34 | 0 | 0 | 113 | 590 | 220 | 0 | 30 | 0 | 0 | 109 | 0 | 0 | 0 | 0 | 150 | 620 | 0 | 0 |  | 8438 | 4804 | 13242 | 4723 | 909 | 2383 | 0 | 2901 | 1540 | 60 | 0 | 572 | 154 | 0 | 0 | 0 | 0
20:00 | 0 | 0 | 220 | 180 | 0 | 12 | 0 | 398 | 301 |  | 0 | 450 | 265 | 9 | 43 | 30 | 280 | 0 | 120 | 42 | 102 | 48 | 22 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 8 | 18 | 15 | 32 | 25 | 0 | 60 | 0 | 105 | 0 | 16 | 152 | 0 | 0 | 0 |  | 12 | 50 | 33 | 80 | 0 | 50 | 13 | 38 | 0 | 0 | 0 | 310 | 0 | 183 | 148 | 0 | 41 | 0 | 0 | 43 | 0 | 35 | 43 | 20 | 10 | 32 | 20 | 152 | 153 | 0 | 13 | 0 | 43 | 40 | 47 | 40 | 0 | 0 | 61 | 85 | 0 | 132 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 149 | 0 | 0 | 112 | 0 | 63 | 0 | 100 | 106 | 110 | 415 | 56 | 105 | 51 | 0 | 240 | 17 | 34 | 105 | 56 | 90 | 312 | 72 | 0 | 108 | 51 | 0 | 17 | 0 | 95 | 34 | 278 | 157 | 0 | 0 | 0 |  | 909 | 0 | 395 | 0 | 98 | 0 | 0 | 0 | 37 | 60 | 40 | 50 | 28 | 96 | 0 | 0 | 60 | 21 | 0 | 92 | 0 | 0 | 30 | 8 | 35 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 383 | 17 | 0 | 50 | 50 | 34 | 0 | 0 | 113 | 600 | 220 | 0 | 54 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 150 | 620 | 0 | 0 |  | 8317 | 4891 | 13208 | 4526 | 909 | 2350 | 0 | 3063 | 1550 | 60 | 0 | 598 | 152 | 0 | 0 | 16 | 73.2
21:00 | 0 | 0 | 220 | 180 | 0 | 12 | 0 | 405 | 342 |  | 0 | 450 | 306 | 8 | 72 | 30 | 320 | 0 | 150 | 70 | 102 | 32 | 23 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 8 | 22 | 15 | 32 | 0 | 0 | 30 | 0 | 106 | 0 | 16 | 151 | 0 | 0 | 0 |  | 12 | 73 | 33 | 80 | 0 | 50 | 13 | 42 | 0 | 0 | 0 | 330 | 0 | 198 | 158 | 0 | 41 | 0 | 0 | 43 | 0 | 36 | 43 | 20 | 10 | 32 | 20 | 152 | 153 | 0 | 13 | 0 | 43 | 39 | 47 | 47 | 0 | 0 | 61 | 85 | 0 | 132 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 195 | 0 | 0 | 112 | 0 | 96 | 0 | 100 | 103 | 128 | 406 | 56 | 105 | 51 | 0 | 245 | 17 | 34 | 105 | 58 | 90 | 378 | 72 | 0 | 72 | 51 | 0 | 17 | 0 | 94 | 34 | 273 | 157 | 0 | 0 | 0 |  | 814 | 0 | 400 | 0 | 64 | 0 | 0 | 0 | 32 | 65 | 8 | 67 | 29 | 96 | 0 | 0 | 60 | 28 | 0 | 82 | 0 | 8 | 22 | 8 | 35 | 0 | 0 | 6 | 0 | 0 | 180 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 415 | 17 | 0 | 50 | 15 | 34 | 0 | 0 | 113 | 622 | 222 | 0 | 17 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 150 | 622 | 0 | 0 |  | 8651 | 4751 | 13402 | 4729 | 814 | 2498 | 0 | 3010 | 1574 | 30 | 0 | 595 | 152 | 0 | 0 | 36 | 73.2
22:00 | 0 | 0 | 220 | 180 | 0 | 12 | 0 | 406 | 332 |  | 0 | 450 | 275 | 8 | 65 | 30 | 330 | 0 | 157 | 80 | 102 | 32 | 23 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 8 | 22 | 15 | 32 | 0 | 0 | 30 | 0 | 102 | 0 | 16 | 152 | 0 | 0 | 0 |  | 12 | 72 | 33 | 80 | 0 | 50 | 13 | 29 | 0 | 0 | 0 | 310 | 0 | 182 | 177 | 0 | 42 | 0 | 0 | 43 | 0 | 36 | 43 | 19 | 10 | 32 | 20 | 162 | 176 | 0 | 17 | 0 | 43 | 40 | 47 | 47 | 0 | 0 | 61 | 85 | 0 | 132 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 195 | 0 | 0 | 112 | 0 | 96 | 0 | 100 | 105 | 145 | 412 | 56 | 105 | 51 | 0 | 245 | 17 | 34 | 105 | 57 | 90 | 390 | 72 | 0 | 72 | 51 | 0 | 17 | 0 | 88 | 34 | 282 | 157 | 0 | 0 | 0 |  | 813 | 0 | 400 | 0 | 64 | 0 | 0 | 0 | 29 | 61 | 8 | 68 | 30 | 96 | 0 | 0 | 60 | 28 | 0 | 82 | 0 | 8 | 22 | 8 | 35 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 420 | 17 | 0 | 50 | 15 | 56 | 0 | 0 | 113 | 622 | 220 | 0 | 17 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 150 | 621 | 0 | 0 |  | 8674 | 4775 | 13449 | 4770 | 813 | 2467 | 0 | 3047 | 1573 | 30 | 0 | 587 | 162 | 0 | 0 | 15.28 | 73.2
23:00 | 0 | 0 | 220 | 180 | 0 | 12 | 0 | 405 | 331 |  | 0 | 450 | 279 | 9 | 65 | 30 | 325 | 0 | 195 | 75 | 58 | 64 | 23 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 8 | 22 | 15 | 32 | 8 | 0 | 30 | 0 | 102 | 0 | 8 | 150 | 0 | 0 | 0 |  | 12 | 71 | 33 | 80 | 0 | 50 | 13 | 33 | 0 | 0 | 0 | 310 | 0 | 211 | 185 | 0 | 42 | 0 | 0 | 43 | 0 | 36 | 43 | 19 | 11 | 32 | 20 | 162 | 176 | 0 | 17 | 0 | 43 | 40 | 47 | 47 | 0 | 0 | 60 | 85 | 0 | 132 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 195 | 0 | 0 | 38 | 0 | 95 | 0 | 100 | 105 | 150 | 409 | 47 | 105 | 51 | 0 | 123 | 17 | 34 | 105 | 13 | 90 | 390 | 64 | 0 | 72 | 51 | 0 | 17 | 0 | 72 | 34 | 279 | 157 | 0 | 0 | 0 |  | 778 | 0 | 400 | 0 | 95 | 0 | 0 | 0 | 29 | 62 | 40 | 68 | 30 | 96 | 0 | 0 | 65 | 28 | 0 | 82 | 0 | 34 | 22 | 52 | 35 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 419 | 17 | 0 | 35 | 50 | 70 | 0 | 0 | 55 | 622 | 225 | 0 | 150 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 150 | 622 | 0 | 0 |  | 8466 | 5008 | 13474 | 4843 | 778 | 2496 | 0 | 2972 | 1574 | 30 | 0 | 619 | 162 | 0 | 0 | 177.63 | 73.21
24:00 | 0 | 0 | 221 | 180 | 0 | 12 | 0 | 405 | 335 |  | 0 | 450 | 291 | 9 | 95 | 55 | 326 | 0 | 193 | 75 | 50 | 110 | 0 | 0 | 0 | 0 | 0 | 55 | 35 | 19 | 8 | 22 | 15 | 32 | 8 | 0 | 30 | 0 | 103 | 0 | 8 | 151 | 0 | 0 | 0 |  | 12 | 48 | 33 | 58 | 0 | 13 | 13 | 36 | 0 | 0 | 0 | 310 | 0 | 211 | 187 | 0 | 43 | 0 | 0 | 43 | 0 | 36 | 43 | 20 | 11 | 32 | 20 | 158 | 179 | 0 | 17 | 0 | 43 | 40 | 47 | 47 | 0 | 0 | 60 | 85 | 0 | 132 | 18 | 0 | 10 | 285 | 24 | 8 | 0 | 286 | 0 | 0 | 37 | 0 | 108 | 0 | 50 | 46 | 150 | 410 | 47 | 105 | 51 | 0 | 123 | 17 | 24 | 105 | 9 | 50 | 370 | 55 | 0 | 72 | 51 | 0 | 17 | 0 | 72 | 17 | 279 | 157 | 0 | 0 | 0 |  | 780 | 0 | 400 | 0 | 95 | 0 | 0 | 0 | 21 | 62 | 40 | 68 | 30 | 96 | 0 | 0 | 65 | 28 | 0 | 54 | 0 | 34 | 22 | 52 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 424 | 17 | 0 | 35 | 105 | 70 | 0 | 0 | 55 | 622 | 222 | 0 | 150 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 150 | 622 | 0 | 0 |  | 8323 | 4982 | 13305 | 4817 | 780 | 2504 | 0 | 2871 | 1574 | 30 | 0 | 571 | 158 | 0 | 0 | 186.225 | 73.21
KWH | 0 | 0 | 3948000 | 4315500 | 0 | 299000 | 0 | 9355260 | 7730000 |  | 0 | 9806500 | 6896989 | 120000 | 564081 | 244022 | 7387185 | 0 | 3338000 | 445440 | 947808 | 242400 | 173933 | 0 | 0 | 0 | 196200 | 587998 | 539872 | 388620 | 351750 | 331380 | 391320 | 645900 | 63360 | 0 | 822180 | 0 | 2500000 | 0 | 248385 | 4946154 | 0 | 0 | 0 |  | 120720 | 911376 | 783129 | 1484520 | 0 | 407520 | 309648 | 745440 | 0 | 0 | 0 | 7684500 | 0 | 4824000 | 3663272 | 0 | 759600 | 0 | 0 | 865854 | 0 | 835904 | 1005326 | 464112 | 252180 | 754000 | 477130 | 3400230 | 4273920 | 0 | 366120 | 10550 | 1009000 | 705840 | 995400 | 1040256 | 0 | 0 | 1371456 | 1976640 | 0 | 3218490 | 396000 | 0 | 247680 | 7149000 | 564624 | 189408 | 0 | 2027345 | 25588 | 0 | 964800 | 0 | 994752 | 85860 | 1501440 | 1316640 | 946763 | 8746000 | 1082400 | 1107840 | 970181 | 28199 | 2857855 | 449048 | 524397 | 1812600 | 514080 | 1427520 | 8686700 | 1120320 | 248300 | 1248480 | 779073 | 0 | 441360 | 254814 | 1253760 | 452520 | 7071700 | 2402036 | 0 | 3518181 | 0 |  | 21529454 | 0 | 9073440 | 0 | 620160 | 0 | 0 | 0 | 177120 | 355840 | 176625 | 625000 | 582684 | 1229760 | 0 | 0 | 1480000 | 125360 | 36140 | 474400 | 0 | 59405 | 125329 | 207538 | 260230 | 0 | 0 | 134874 | 0 | 0 | 4349400 | 0 | 0 | 4297164 | 0 | 0 | 0 | 0 | 0 | 4346973 | 0 | 9098800 | 289920 | 0 | 1157952 | 465120 | 1246396 | 0 | 14952 | 1455840 | 10606000 | 5292927 | 0 | 513600 | 35460 | 719280 | 1060224 | 0 | 0 | 0 | 79537 | 3621800 | 14847273 | 471280 | 0 |  | 175950634 | 101243257 | 277193891 | 109980948 | 21529454 | 56390442 | 25588 | 39424899 | 36942654 | 822180 | 0 | 6729264 | 3400230 | 1948232 | 0 | 0
Fuel Cost | 0 | 0 | 5764080 | 6430095 | 0 | 397670 | 0 | 9823023 | 8348400 |  | 0 | 10689085 | 7655657.79 | 1341600 | 7474073.25 | 3233291.5 | 8273647.2 | 0 | 5841500 | 6512332.8 | 13335658.56 | 3929304 | 1603662.26 | 0 | 0 | 0 | 2495664 | 7937973 | 7239683.52 | 291465 | 263812.5 | 0 | 0 | 0 | 1077753.6 | 0 | 221988.6 | 0 | 4725000 | 0 | 4061094.75 | 5144000.16 | 0 | 0 | 0 |  | 1575396 | 15201751.68 | 13328855.58 | 20055865.2 | 0 | 4715006.4 | 393252.96 | 2482315.2 | 0 | 0 | 0 | 8529795 | 0 | 5595840 | 4725620.88 | 0 | 858348 | 0 | 0 | 1445976.18 | 0 | 14436062.08 | 13521634.7 | 635833.44 | 189135 | 1319500 | 357847.5 | 24413651.4 | 4658572.8 | 0 | 497923.2 | 168167 | 1382330 | 931708.8 | 1731996 | 1799642.88 | 0 | 0 | 2660624.64 | 4506739.2 | 0 | 3250674.9 | 851400 | 0 | 490406.4 | 7149000 | 423468 | 143950.08 | 0 | 27673259.25 | 536324.48 | 0 | 13005504 | 0 | 13777315.2 | 1003703.4 | 15494860.8 | 17985302.4 | 12563545.01 | 8046320 | 13161984 | 16019366.4 | 12272789.65 | 0 | 33551217.7 | 4890132.72 | 5574340.11 | 24596982 | 6626491.2 | 16816185.6 | 7991764 | 14508144 | 3587935 | 15843211.2 | 8865850.74 | 0 | 5764161.6 | 3045027.3 | 18768787.2 | 5959688.4 | 0 | 0 | 0 | 0 | 0 |  | 64588362 | 0 | 10162252.8 | 0 | 6455865.6 | 0 | 0 | 0 | 3189931.2 | 6405120 | 2538101.25 | 700000 | 1130406.96 | 13404384 | 0 | 0 | 3034000 | 2102287.2 | 632088.6 | 7419616 | 0 | 983746.8 | 2119313.39 | 2828742.94 | 4390080.1 | 0 | 0 | 102099.618 | 0 | 0 | 23008326 | 0 | 0 | 4984710.24 | 0 | 0 | 0 | 0 | 0 | 5042488.68 | 0 | 9007812 | 3896524.8 | 0 | 13698572.16 | 6720984 | 15829229.2 | 0 | 165219.6 | 17673897.6 | 95560060 | 5398785.54 | 0 | 3800640 | 401052.6 | 8437154.4 | 16253233.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 626469999.95 | 362065089.198 | 988535089.148 | 119300462.518 | 64588362 | 66959514.03 | 536324.48 | 503983730.99 | 118568386 | 221988.6 | 0 | 73154409.83 | 24413651.4 | 16808259.3 | 0 | 0
Yesterday Day Peak | 0 | 0 | 180 | 180 | 0 | 12 | 0 | 402 | 333 |  | 0 | 450 | 300 | 9 | 16 | 0 | 317 | 0 | 158 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 19 | 20 | 18 | 15 | 31 | 0 | 0 | 30 | 0 | 107 | 0 | 8 | 220 | 0 | 0 | 0 |  | 0 | 32 | 31 | 58 | 0 | 6 | 8 | 20 | 0 | 0 | 0 | 305 | 0 | 205 | 123 | 0 | 33 | 0 | 0 | 43 | 0 | 36 | 40 | 19 | 10 | 31 | 20 | 140 | 194 | 0 | 17 | 2 | 43 | 20 | 44 | 41 | 0 | 0 | 60 | 85 | 0 | 135 | 17 | 0 | 10 | 300 | 24 | 8 | 0 | 15 | 0 | 0 | 24 | 0 | 15 | 0 | 50 | 68 | 6 | 366 | 38 | 17 | 34 | 5 | 88 | 17 | 17 | 17 | 27 | 50 | 350 | 53 | 21 | 17 | 34 | 0 | 17 | 34 | 75 | 17 | 322 | 72 | 0 | 106 | 0 |  | 909 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 422 | 5 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 460 | 220 | 0 | 0 | 5 | 54 | 35 | 0 | 0 | 0 | 7 | 150 | 613 | 53 | 0 |  | 11051 | DayPeak
Yesterday Evening Peak | 0 | 0 | 220 | 180 | 0 | 12 | 0 | 405 | 342 | 0 | 0 | 450 | 306 | 8 | 72 | 30 | 320 | 0 | 150 | 70 | 102 | 32 | 23 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 8 | 22 | 15 | 32 | 0 | 0 | 30 | 0 | 106 | 0 | 16 | 151 | 0 | 0 | 0 | 0 | 12 | 73 | 33 | 80 | 0 | 50 | 13 | 42 | 0 | 0 | 0 | 330 | 0 | 198 | 158 | 0 | 41 | 0 | 0 | 43 | 0 | 36 | 43 | 20 | 10 | 32 | 20 | 152 | 153 | 0 | 13 | 0 | 43 | 39 | 47 | 47 | 0 | 0 | 61 | 85 | 0 | 132 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 195 | 0 | 0 | 112 | 0 | 96 | 0 | 100 | 103 | 128 | 406 | 56 | 105 | 51 | 0 | 245 | 17 | 34 | 105 | 58 | 90 | 378 | 72 | 0 | 72 | 51 | 0 | 17 | 0 | 94 | 34 | 273 | 157 | 0 | 0 | 0 |  | 814 | 0 | 400 | 0 | 64 | 0 | 0 | 0 | 32 | 65 | 8 | 67 | 29 | 96 | 0 | 0 | 60 | 28 | 0 | 82 | 0 | 8 | 22 | 8 | 35 | 0 | 0 | 6 | 0 | 0 | 180 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 415 | 17 | 0 | 50 | 15 | 34 | 0 | 0 | 113 | 622 | 222 | 0 | 17 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 150 | 622 | 0 | 0 |  | 13402 | EvPeak
Forecast for Evening | 0 | 0 | 180 | 180 | 0 | 12 | 0 | 400 | 330 | 0 | 0 | 450 | 305 | 8 | 100 | 55 | 320 | 0 | 160 | 40 | 102 | 150 | 23 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 20 | 25 | 33 | 33 | 50 | 0 | 60 | 0 | 110 | 0 | 25 | 151 |  | 0 | 0 | 0 | 12 | 72 | 33 | 80 | 0 | 50 | 13 | 30 | 0 | 0 | 0 | 330 | 0 | 200 | 150 | 0 | 46 | 0 | 0 | 43 | 0 | 36 | 43 | 20 | 11 | 32 | 20 | 152 | 200 | 0 | 20 | 0 | 43 | 30 | 50 | 50 | 0 | 0 | 60 | 86 | 0 | 135 | 17 | 0 | 10 | 0 | 24 | 11 | 0 | 300 | 300 | 0 | 85 | 0 | 130 | 0 | 100 | 100 | 150 | 400 | 85 | 105 | 51 | 0 | 300 | 17 | 34 | 105 | 55 | 90 | 400 | 72 | 0 | 108 | 51 | 0 | 17 |  | 115 | 35 | 270 | 163 |  | 0 | 10 |  | 934 | 0 | 400 |  | 98 | 150 | 0 | 0 | 32 | 78 | 24 | 65 | 38 | 96 | 0 | 0 | 65 | 30 | 35 | 82 | 0 | 34 | 30 | 52 | 35 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 180 |  | 0 | 0 | 0 | 0 | 185 | 0 | 414 | 17 | 200 | 50 | 105 | 70 | 0 | 0 | 113 | 622 | 220 |  | 150 |  |  | 115 | 0 |  | 0 |  | 130 | 611 |  | 0
Forecast for Day | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 400 | 330 | 0 | 0 | 450 | 305 | 8 | 100 | 55 | 280 | 0 | 100 | 16 | 48 | 54 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 19 | 20 | 25 | 33 | 33 | 8 | 0 | 30 | 0 | 110 | 0 | 8 | 151 |  | 0 | 0 | 0 | 12 | 32 | 33 | 58 | 0 | 6 | 13 | 15 | 0 | 0 | 0 | 300 | 0 | 200 | 150 | 0 | 46 | 0 | 0 | 10 | 0 | 36 | 43 | 20 | 11 | 32 | 20 | 129 | 200 | 0 | 20 | 1.6 | 43 | 30 | 50 | 50 | 0 | 0 | 60 | 86 | 0 | 135 | 17 | 0 | 10 | 0 | 24 | 11 | 0 | 300 | 300 | 0 | 65 | 0 | 130 | 20 | 50 | 50 | 5 | 400 | 38 | 17 | 17 | 5 | 88 | 17 | 17 | 105 | 9 | 50 | 400 | 70 | 50 | 72 | 34 | 0 | 17 | 30 | 55 | 17 | 220 | 163 |  | 0 | 18 |  | 934 | 0 | 350 | 0 | 49 | 150 | 0 | 0 | 20 | 36 | 16 | 65 | 25 | 16 | 0 | 0 | 65 | 30 | 30 | 40 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 414 | 17 | 0 | 35 | 15 | 34 | 0 | 8 | 55 | 622 | 220 |  | 17 | 6 | 100 | 35 | 0 |  | 0 | 30 | 130 | 611 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 392 | 302 | 0 | 0 | 400 | 285 | 8 | 17 | 0 | 280 | 0 | 121 | 21 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 21 | 15 | 32 | 0 | 0 | 30 | 0 | 103 | 0 | 8 | 151 | 0 | 0 | 0 | 0 | 0 | 41 | 33 | 58 | 0 | 6 | 13 | 16 | 0 | 0 | 0 | 280 | 0 | 213 | 150 | 0 | 45 | 0 | 0 | 43 | 0 | 36 | 43 | 20 | 11 | 32 | 20 | 124 | 182 | 0 | 16 | 0 | 43 | 35 | 47 | 47 | 0 | 0 | 61 | 86 | 0 | 92 | 17 | 0 | 10 | 270 | 10 | 8 | 0 | 15 | 0 | 0 | 28 | 0 | 17 | 1 | 50 | 17 | 5 | 367 | 58 | 17 | 34 | 3 | 88 | 17 | 17 | 105 | 9 | 50 | 375 | 17 | 16 | 17 | 17 | 0 | 17 | 10 | 17 | 17 | 200 | 160 | 0 | 0 | 0 | 0 | 913 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 16 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 363 | 17 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 600 | 224 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 13 | 150 | 620 | 87 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
292.3904
| Minimum Generation |  | 9961 | 7:00
| Highest Generation |  | 13474 | 23:00
| Day Peak Generation |  | 11051 | 12:00
| Evening Peak Generation |  | 13402 | 21:00
| HVDC Max Flow |  | 916 | 4:00
| HVDC EvPeak Flow |  | 814 | 21:00
| Load factor L.F |  | 85.72% | [163 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  |  | DAILY REPORT |  |  |  |  | Page -1
[7 empty] | Reporting Date : | 2023-07-05
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-07-04 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 11051 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 10481 | MW
Evening Peak Generation : |  |  | 13402 | MW Hour : | 21:00 | Available Max Generation : |  | 14891 | MW
E.P. Demand (at gen end) : |  |  | 13440 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13900 | MW
Maximum Generation : |  |  | 13474 | MW Hour : | 23:00 | Reserve(Generation end) |  | 991 | MW
Total Gen. (MKWH) : |  |  | 277.1939 | System Load Factor : | 85.72% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 430 | MW at | 22:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | - | MKWHR.
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-07-05
Actual : |  | 73.21 | Ft.(MSL) , | Rule curve : | 84.64 | Ft.( MSL )
Gas Consumed : |  | Total = | 1293.54 | MMCFD. | Oil Consumed (PDB) :
[7 empty] | HSD : |  | Liter
[7 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 186259976.548
: |  |  | Coal : | 118568386 | Oil : | 577674465.3 | Total : | 882502827.848
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4372.6492 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1200.296 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1681.0207 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1460.7805 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1202.1318 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 893.9104 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 501.2489 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 417.5625 |  |  | 0 | 0%
Rangpur Area |  | 36 | 864:00 | 816.683 |  |  | 0 | 0%
Total |  | 36 |  | 12546.2832 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,5,7
3) Shajibazar 330 MW
4) Baghabari-100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:23 | 09:48 | Satkhira 132/33kV S/S Transformer-2 (T-2) HT Forced S/D Due to Station auxiliary transformer fuse connection work
08:23 | 09:49 | Satkhira 132/33kV S/S Transformer-2 (T-2) LT Forced S/D Due to Station auxiliary transformer fuse connection work | [5 empty] | 40.0MW load interrup.
08:28 | 09:39 | Satkhira 132/33kV S/S 33 KV BUS Forced S/D Due to Station auxiliary transformer fuse connection work. | [5 empty] | 40.0MW load interrup.
08:50 | 10:16 | Goalpara 132/33kV S/S T-6 LT Forced S/D Due to Redhot | [5 empty] | 4.0MW load interrup.
08:52 | 10:15 | Goalpara 132/33kV S/S T-6 HT Forced S/D Due to Red hot | [5 empty] | 4.0MW load interrup.
| 10:07 | Noapara 132/33kV S/S T-2 HT is restored.
| 10:08 | Noapara 132/33kV S/S T-2 LT is restored.
10:35 | 12:58 | Shyampur-Shyampur(New) 132kV Ckt-2 Scheduled S/D from Shyampur 230/132kV end Due to Maintenance at 132kV Shyampur
old ss end
11:04 | 12:01 | Kabirpur 132/33kV S/S XFR, T-2 LT Scheduled S/D Due to PBS working | [5 empty] | 60.0MW load interrup.
11:04 | 12:01 | Kabirpur 132/33kV S/S XFR, T-2 HT Scheduled S/D Due to PBS working | [5 empty] | 60.0MW load interrup.
12:00 |  | Day peak Generation: 11051 MW
12:04 |  | SS Power Unit-2 was shutdown due to superheater overheating.
12:09 | 16:35 | Chowmuhani-Feni 132 kV Ckt-2 Forced S/D from Chowmuhani 132/33kV end Due to Red Hot Maintenance Of 01 No Tower R | [5 empty] | 48.0MW load interrup.
|  | phase in Feni Line-02 and from Feni 132/33kV end Due to Due to Red-hot maintenance(R-Phase, T-Connector) of Tower No. -01 | [5 empty] | Feni 132/33kV end.
12:55 | 21:28 | Chandraghona-Madunaghat 132 kV Ckt-1 Tripped from Madunaghat 132/33kV end showing REL 670 REC 650 relays.
13:09 | 13:29 | Keranigonj 230/132/33kV S/S ATR-1 HT Tripped showing 86.1 & 86.2 relays Due to PRV-2 tripped.
13:09 | 13:29 | Keranigonj 230/132/33kV S/S ATR-1 LT Tripped showing 86.1 & 86.2 relays Due to PRV-2 tripped.
13:30 | 17:01 | Keranigonj 230/132/33kV S/S ATR-1 HT Scheduled S/D Due to To do the maintenance of 230/132/33 kV ATR 01.
13:30 | 17:02 | Keranigonj 230/132/33kV S/S ATR-1 LT Scheduled S/D Due to To do the maintenance of 230/132/33 kV ATR 01.
14:02 |  | Bhola CCPP GT1 was sync.
| 14:33 | Madanganj 132/33kV S/S Madanganj -DPDC Char sayedpur 132k Ckt-1 is restored.
14:34 | 15:01 | Aminbazar 400/230/132kV S/S ATR-03 LT Scheduled S/D Due to For NIPS system inactive
15:29 |  | Ashuganj East CCPP 420 MW ST was shutdown
16:02 | 16:43 | Kulaura 132/33kV S/S TR-2 LT Scheduled S/D Due to Redhot maintenance. | [5 empty] | 14.0MW load interrup.
16:02 | 16:43 | Kulaura 132/33kV S/S TR-1 LT Scheduled S/D Due to Redhot maintenance. | [5 empty] | 14.0MW load interrup.
16:03 | 16:42 | Kulaura 132/33kV S/S TR-1 HT Scheduled S/D Due to Redhot maintenance. | [5 empty] | 14.0MW load interrup.
16:04 | 16:42 | Kulaura 132/33kV S/S TR-2 HT Scheduled S/D Due to Redhot maintenance. | [5 empty] | 14.0MW load interrup.
| 16:50 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) HT is restored.
| 17:15 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) LT is restored.
18:39 |  | Sikalbaha 225MW ST tripped at 18:39 hrs
21:00 |  | Evening Peak Generation =13,402MW
21:39 | 22:25 | Ramganj 132/33kV S/S Transformer -02 LT Tripped showing o/c relays Due to Overload
21:39 | 22:29 | Ramganj 132/33kV S/S Transformer-01 LT Tripped showing O/C relays Due to Overload
21:39 | 22:25 | Ramganj 132/33kV S/S Transformer -02 HT Tripped showing T2 differential relay relays Due to Overload
21:39 | 22:29 | Ramganj 132/33kV S/S Transformer-01 HT Tripped showing T2 differential relay relays Due to Overload | [5 empty] | 122.0MW load interrup.
01:50 |  | Bhola CCPP 225 MW GT-1 tripped due to a control system problem.
05:37 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) LT Scheduled S/D Due to GT-2 132/33kV X-Former oil
Centrifuging.
05:37 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) HT Scheduled S/D Due to GT-2 132/33kV X-Former oil
Centrifuging.
06:42 |  | Pabna 132/33kV S/S T-1 LT Forced S/D Due to Red hot maintenance work
06:45 |  | Pabna 132/33kV S/S T-1 HT Forced S/D Due to Red hot maintenance work
07:00 |  | Minimum generation: 9618 MW
07:04 |  | Daudkandi 132/33kV S/S Transformer-1 HT Forced S/D Due to Red Hot removing work at 33KV bus of T-1 by PBS-3 Cumilla. | [5 empty] | 30.0MW load interrup.
07:04 |  | Daudkandi 132/33kV S/S Transformer-1 LT Forced S/D Due to Red Hot removing work at 33KV bus of T-1 by PBS-3 Cumilla. | [5 empty] | 30.0MW load interrup.
07:42 |  | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) LT Forced S/D Due to For Red-Hot Maintenance. | [5 empty] | 10.0MW load interrup.
07:43 |  | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) HT Forced S/D Due to For Red-Hot Maintenance. | [5 empty] | 10.0MW load interrup.
07:58 |  | Khulna (S)-Satkhira 132kV Ckt-2 Scheduled S/D from Satkhira 132/33kV end Due to Maintenance work and from Khulna(S)
230/132kV end Due to Red Hot Removed Work
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-07-04 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 220 | 3948000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4315500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 299000 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 405 | 9355260
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 342 | 7730000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9806500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 8 | 120000 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 306 | 6896989 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 72 | 564081 | Low Demand
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 30 | 244022 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 23 | 173933 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 388620 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 150 | 3338000
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 70 | 445440 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 320 | 7387185
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 947808
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 196200 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 242400 | Low Demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 587998 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 539872
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 30 | 683130 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 15 | 391320 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 32 | 645900 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 0 | 63360 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 195 | 2027345 | Low Demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 25588 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 96 | 994752 | Low Demand
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1107840 | Low Demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 72 | 1120320 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 1248480 | Low Demand
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 254814
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 34 | 452520 | Line problem
| Dhaka area Total |  |  |  | 5822 | 3517 | 66542177
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 106 | 2500000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 16 | 248385
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 85860
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 407520
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 822180 | Low Water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 151 | 4946154
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 970181 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 73 | 911376 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 33 | 783129 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 80 | 1484520 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1501440
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 13 | 309648 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 745440
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 28199
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 245 | 2857855
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 449048 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 34 | 524397 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 90 | 1427520 | Reserve
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 51 | 779073 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 157 | 2402036 | Low Demand
| SS Power I |  | SS Power | 0 | 0 | 0 | 3518181 | On test.
| Cox's Bazar Wind |  | IPP | 66 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2545 | 1339 | 27702142
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 198 | 4824000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 330 | 7684500 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 273 | 7071700 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 41 | 759600 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 158 | 3663272 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 865854 | Engine problem
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 128 | 946763 | Low Demand
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 835904 | Machine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 103 | 1316640 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 464112
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 252180
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 152 | 3400230
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 32 | 754000
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 1005326 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 477130 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 105 | 1812600
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 58 | 514080 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 441360 | Fuel shortage
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 94 | 1253760
| Cumilla Area Total |  |  |  | 3096 | 1861 | 38343011
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 153 | 4273920 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 13 | 366120 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10550
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 112 | 964800 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 56 | 1082400 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 248300
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 120720 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 346 | 7066810
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1009000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 39 | 705840 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 995400
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 47 | 1040256
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 189408 | Machine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1371456
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1976640
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 132 | 3218490 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 396000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 564624
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7149000 | Gas shortage
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 406 | 8746000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 247680
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 378 | 8686700
| Sylhet Area Total |  |  |  | 2427 | 1588 | 36296494
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 814 | 21529454
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 64 | 620160 | Low Demand
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 32 | 177120 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 65 | 355840 | Low Demand
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 400 | 9073440 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 176625 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 289920 | Low Demand
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 465120 | Low Demand
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 719280
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 220 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | Coal shortage.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 3121 | 1415 | 33406959
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 96 | 1229760 | Low Demand
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 29 | 582684 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 67 | 625000 | Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 622 | 10606000 | Machine problem
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 222 | 5292927
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 513600 | Low Demand
| Barisal 307 MW |  | IPP | 307*1 | 307 | 150 | 3621800
| Barisal Area Total |  |  |  | 2265 | 1203 | 22471771
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 60 | 1480000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 28 | 125360 | Reserve
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 36140 | Reserve
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Fuel shortage
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 59405 | Fuel shortage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 125329 | Low Demand
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 171 | 4297164 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 185 | 4346973 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 415 | 9098800
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 260230 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 6 | 134874 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 207538
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 82 | 474400 | Low Demand
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Reserve
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 1157952 | Low Demand
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1455840
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 35460
| Adani Power Jharkhanda Ltd |  | Import | 748*1 | 748 | 622 | 14847273
| Rajshahi Area Total |  |  |  | 2905 | 1805 | 38142738
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 180 | 4349400
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 1246396 | Low Demand
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 14952
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 114 | 1060224
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 79537
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 471280
| Rangpur Area Total |  |  |  | 750 | 328 | 7221789
| Total |  |  |  | 23545 | 13402 | 277193891
| Eastern Grid Total |  |  |  | 14504 | 8651 | 175950634
| Western Grid Total |  |  |  | 9041 | 4751 | 101243257
| National Grid Total |  |  |  | 23545 | 13402 | 277193891
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-07-04
| (a) ENTIRE EASTERN GRID : |  | 8277.25 | MW | (b) ENTIRE WESTERN GRID : |  | 4534 | MW
| i) Dhaka area |  | 3843.35 | MW | i) Khulna area |  | 1819 | MW
| ii) Chittagong area |  | 1349.9 | MW | ii) Rajshahi area |  | 1386 | MW
| iii) Comilla area |  | 1410 | MW | iii) Barisal area |  | 499 | MW
| iv) Mymensingh area |  | 1101 | MW | iv) Rangpur area |  | 830 | MW
| v) Sylhet area |  | 573 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 12811.25 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 32 | 20:00 | Kamrangirchar | 40.5 | 23:00 | Natore | 150 | 23:00 | Shitalakhya | 77 | 21:00
2 | AKSML | 10 | 05:00 | Chowmuhani | 227 | 19:30 | Kaptai | N/A | N/A | Nawabganj | 50.7 | 23:00 | Sholosohor | 29 | 00:00
3 | Aftabnagar | 32 | 22:00 | Chuadanga | 119 | 23:00 | Kazla | 74 | 23:00 | Netrakona | 140 | 22:00 | Shyampur | 74 | 13:00
4 | Agargaon | 83 | 13:00 | Coxsbazar | 125 | 00:00 | Keranigonj | 66 | 23:00 | New | 52 | 13:00 | Siddhirganj | 90 | 23:00
5 | Agrabad | 66 | 09:00 | Cumilla(N) | 182 | 22:00 | Khagrachori | 34 | 19:30 | Niamatpur | 82 | 23:00 | Sirajganj | 108 | 20:00
6 | Amnura | 53 | 22:00 | Cumilla(S) | 162 | 22:00 | Khulna | 100 | 20:00 | Noapara | 51.5 | 19:30 | Sonargaon | 82 | 09:00
7 | Ashuganj | 63 | 21:00 | Daudkandi | 151 | 22:00 | Khulshi | 169 | 12:00 | PHP | 10 | 05:00 | Sreemongol | 67 | 22:00
8 | BIPTC | N/A | N/A | Dhaka | 22 | 12:00 | Kishoreganj | 158 | 21:00 | Pabna | 126 | 23:00 | Sreepur | 48.78 | 22:00
9 | BSRM | 162 | 04:00 | Dhamrai | 90 | 20:00 | Kodda | 179 | 21:00 | Palashbari | 126 | 23:00 | Srinagar | 49.15 | 23:00
10 | Bagerhat | 98 | 00:00 | Dhanmondi | 99 | 13:00 | Kulaura | 56 | 19:00 | Panchagarh | 53 | 00:00 | Sunamganj | 57 | 22:00
11 | Bakulia | 106 | 16:00 | Dohazari | 90 | 00:00 | Kurigram | 64 | 19:30 | Patuakhali | 123 | 23:00 | Sylhet | 147 | 20:00
12 | Banani | 46 | 13:00 | Faridpur | 163 | 21:00 | Kushtia | 146 | 20:00 | Payra | 24 | 00:00 | TK | 32.4 | 21:00
13 | Bangabhaban | 20 | 10:00 | Fatullah | 39 | 23:00 | Lalbag | 37 | 13:00 | Postogola | 47 | 23:00 | Tangail | 226 | 21:00
14 | Barapukuria | 58 | 21:00 | Fenchuganj | 49 | 19:30 | Lalmonirhat | 48 | 19:30 | Purbachal | 18 | 23:00 | Thakurgaon | 94 | 00:00
15 | Barguna | 26 | 00:00 | Feni | 126 | 22:00 | Madanganj | 14 | 21:00 | Purbasadipur | 117 | 23:00 | Tongi | 85 | 19:30
16 | Barishal | 114 | 11:00 | GPH | 89 | 11:00 | Madaripur | 121 | 00:00 | Rahanpur_I | 0 | 00:00 | Ullon | 38 | 23:00
17 | Barishal-230 | 116 | 23:00 | Ghorashal | N/A | N/A | Madartek | 80.72 | 23:00 | Rahim | 0 | 00:00 | Uttara | 61 | 15:00
18 | Baroaulia | 62 | 19:30 | Goalpara | 38 | 23:00 | Madunaghat | 55 | 19:30 | Rajbari | 72 | 20:00 | UttaraNew | 48 | 23:00
19 | Baroirhat | 65 | 22:00 | Gollamari | 55 | 00:00 | Magura | 68 | 23:00 | Rajendrapur | 78 | 22:00 | Zigatola | 69 | 13:00
20 | Bashundhara | 131 | 13:00 | Gopalganj | 114.2 | 23:00 | Mahasthangarh | 70 | 21:00 | Rajshahi | 155 | 21:00
21 | BashundharaCement | 7 | 15:00 | Gulshan | 116 | 12:00 | Manikganj | 100 | 23:00 | Rajshahi-230 | 36 | 23:00
22 | Beanibazar | 72 | 19:30 | Halishahar | 67 | 20:00 | Maniknagar | 84 | 13:00 | Ramganj | 124 | 20:00
23 | Benapole | 66 | 23:00 | HaripurSBU | 106 | 21:00 | Matarbari | 48 | 22:00 | Rampur | 29 | 00:00
24 | Bhaluka | 112 | 19:30 | Hasnabad | 79 | 23:00 | Matuail | 40 | 23:00 | Rangamati | 16 | 19:30
25 | Bhandaria | 58 | 23:00 | Hathazari | 80 | 21:00 | Millgate | 66 | 22:00 | Rangpur | 136 | 19:30
26 | Bhangura | 46 | 20:00 | Ishurdi | 56 | 21:00 | Mirpur | 113.5 | 23:00 | Ruppur | 5.8 | 17:00
27 | Bheramara(GK) | 66 | 21:00 | Jaldhaka | 70 | 00:00 | Mirsorai | 5.7 | 22:00 | SSM | 0 | 00:00
28 | Bhulta | 148 | 14:00 | Jamalpur | 164 | 22:00 | Mithapukur | 46 | 19:30 | Saidpur | 102 | 23:00
29 | Bog-Sherpur | 58 | 21:00 | Jashore | 142 | 23:00 | Modern | 0 | 00:00 | Satkhira | 143 | 00:00
30 | Bogura | 163 | 22:00 | Jhenaidah | 133 | 23:00 | Mogbazar | 112.9 | 13:00 | Satmasjid | 94 | 19:30
31 | Borhanuddin | 82 | 22:00 | Joydebpur | 119 | 22:00 | Mongla | 32 | 11:00 | Savar | 131 | 00:00
32 | Brahmanbaria | 188 | 21:00 | Joypurhat | 57 | 23:00 | Motijheel | 33 | 13:00 | Shahjadpur | 96 | 19:30
33 | Cantonment | 116 | 14:00 | Juldah | 18 | 20:00 | Munshiganj | 118 | 00:00 | Shahjibazar | 130 | 22:00
34 | Chandpur | 79 | 22:00 | KSRM | 31.5 | 00:00 | Mymensingh | 230 | 22:00 | Shahmirpur | 46 | 00:00
35 | Chandraghona | 35 | 19:30 | Kabirpur | 180 | 21:00 | Naogaon | 124 | 22:00 | Shariatpur | 94 | 23:00
36 | Chapai | 69 | 23:00 | Kachua | 97 | 22:00 | Narail | 62 | 23:00 | Sherpur | 128 | 20:00
37 | Charsaidpur | 29 | 18:30 | Kallyanpur | 87 | 23:00 | Narinda | 58 | 15:00 | Shikalbaha | N/A | N/A
38 | Chauddagram | 71 | 22:00 | Kalurghat | 12 | 00:00 | Narshingdi | 156 | 23:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-07-04 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 412 | 18:30 | 396 | 13:00 | Gopalganj | 416 | 18:30 | 400 | 13:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 400 | 18:30 | 392 | 14:00
| Bhulta | 404 | 18:00 | 394 | 13:00 | Madunaghat_I | 417 | 18:00 | 390 | 04:00
| Bibiana | 410 | 02:00 | 400 | 14:00 | Payra | 419 | 18:30 | 410 | 15:00
| BIPTC | 396 | 07:00 | 387 | 15:00 | Rahanpur_I | 420 | 18:00 | 409 | 23:00
| Bogura | N/A | N/A | N/A | N/A | Rampal | 415 | 18:00 | 396 | 13:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 241 | 18:30 | 232 | 10:00 | Hasnabad | 241 | 18:30 | 230 | 13:00
| AKSML | 236 | 20:00 | 210 | 00:00 | Hathazari | 235 | 22:00 | 223 | 15:00
| Aminbazar | 241 | 20:00 | 234 | 12:00 | Ishurdi | 236 | 18:30 | 226 | 21:00
| Ashuganj | 239 | 18:30 | 232 | 13:00 | Jhenaidah | 228 | 18:30 | 213 | 22:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 238 | 18:00 | 232 | 14:00
| Baghabari | 230 | 18:00 | 223 | 19:30 | Keranigonj | 240 | 18:30 | 230 | 13:00
| Barapukuria | 218 | 18:00 | 207 | 20:00 | Khulna(S) | 235 | 18:30 | 220 | 14:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | 238 | 18:00 | 224 | 01:00
| Barishal | 248 | 18:30 | 238 | 05:00 | Maniknagar | 238 | 18:00 | 231 | 15:00
| Bheramara | 233 | 18:00 | 224 | 19:30 | Meghnaghat | 242 | 15:00 | 236 | 11:00
| Bhulta | 240 | 18:30 | 233 | 13:00 | Mirsorai | 239 | 18:30 | 224 | 12:00
| Bibiana | 243 | 18:30 | 235 | 15:00 | Rajshahi | 233 | 18:30 | 223 | 22:00
| BIPTC | 235 | 18:00 | 223 | 22:00 | Rampal | 237 | 18:30 | 221 | 22:00
| Bogura | 222 | 18:30 | 212 | 23:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 245 | 02:00 | 237 | 00:00 | Rampura | 237 | 01:00 | 231 | 13:00
| BSRM | 240 | 18:30 | 225 | 13:00 | Shikalbaha | 236 | 22:00 | 221 | 15:00
| Cumilla(N) | 239 | 18:30 | 227 | 13:00 | Shyampur | 239 | 18:30 | 231 | 13:00
| Fenchuganj | 244 | 18:00 | 238 | 13:00 | Siddhirganj | 240 | 18:00 | 234 | 13:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 235 | 02:00 | 233 | 00:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 233 | 18:30 | 227 | 14:00
| GPH | 237 | 22:00 | 22 | 05:00 | Tongi | 237 | 04:00 | 227 | 09:00
| Haripur | 238 | 18:00 | 231 | 13:00
| 132 kV | KV |  | KV |  | Tongi | KV |  | KV
| Aftabnagar | 134 | 00:00 | 128 | 13:00 | Lalbag | 137 | 18:30 | 128 | 14:00
| Agargaon | 139 | 18:30 | 33 | 13:00 | Lalmonirhat | 128 | 11:00 | 118 | 23:00
| Agrabad | 137 | 18:30 | 127 | 15:00 | Madanganj | 140 | 20:00 | 132 | 13:00
| AKS | 132 | 19:30 | 126 | 01:00 | Madaripur | 133 | 18:30 | 128 | 02:00
| Aminbazar | 139 | 00:00 | 135 | 09:00 | Madartek | 134 | 04:00 | 128 | 13:00
| Amnura | 135 | 18:30 | 124 | 21:00 | Madunaghat | 139 | 18:30 | 127 | 13:00
| Ashuganj | 140 | 03:00 | 137 | 13:00 | Magura | 137 | 18:00 | 126 | 21:00
| Bagerhat | 136 | 18:30 | 122 | 22:00 | Mahasthangarh | 132 | 18:00 | 122 | 23:00
| Bakulia | 136 | 22:00 | 125 | 15:00 | Manikganj | 135 | 17:00 | 128 | 00:00
| Banani | 134 | 02:00 | 128 | 13:00 | Maniknagar | 135 | 00:00 | 130 | 15:00
| Bangabhaban | 135 | 06:00 | 130 | 15:00 | Matarbari | 126 | 18:00 | 108 | 01:00
| Barapukuria | 135 | 18:00 | 127 | 19:30 | Matuail | 139 | 18:30 | 134 | 12:00
| Barguna | 138 | 18:30 | 128 | 22:00 | Millgate | 137 | 01:00 | 131 | 13:00
| Barishal | 136 | 18:30 | 126 | 22:00 | Mirpur | 140 | 18:00 | 133 | 10:00
| Barishal-230 | 137 | 18:30 | 130 | 05:00 | Mithapukur | 131 | 18:00 | 120 | 20:00
| Baroaulia | 137 | 22:00 | 127 | 14:00 | Modern | 135 | 18:00 | 126 | 15:00
| Baroirhat | 136 | 18:30 | 121 | 14:00 | Mogbazar | 135 | 01:00 | 128 | 13:00
| Bashundhara | 137 | 18:30 | 128 | 13:00 | Mongla | 135 | 18:00 | 123 | 22:00
| BashundharaCement | 140 | 20:00 | 132 | 10:00 | Motijheel | 135 | 06:00 | 130 | 15:00
| Beanibazar | 131 | 05:00 | 126 | 19:00 | Munshiganj | 140 | 20:00 | 132 | 10:00
| Benapole | 133 | 18:30 | 122 | 22:00 | Mymensingh | 133 | 11:00 | 118 | 23:00
| Bhaluka | 131 | 18:30 | 123 | 15:00 | Naogaon | 130 | 18:30 | 117 | 22:00
| Bhandaria | 136 | 18:00 | 121 | 21:00 | Narail | 138 | 18:30 | 125 | 22:00
| Bhangura | 137 | 18:00 | 131 | 19:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 136 | 18:00 | 131 | 22:00 | Narshingdi | 137 | 18:30 | 129 | 13:00
| Bheramara(GK) | 137 | 00:00 | 131 | 21:00 | Natore | 133 | 18:00 | 126 | 19:30
| Bhulta | 131 | 18:00 | 126 | 10:00 | Nawabganj | 136 | 18:00 | 126 | 13:00
| Bog-Sherpur | 134 | 18:00 | 126 | 22:00 | Netrakona | 133 | 11:00 | 118 | 19:00
| Bogura | 134 | 18:00 | 127 | 19:30 | New | 137 | 18:00 | 131 | 13:00
| Bogura-230 | 134 | 18:30 | 125 | 23:00 | Niamatpur | 129 | 18:00 | 113 | 22:00
| Brahmanbaria | 135 | 18:30 | 131 | 21:00 | Noapara | 139 | 18:30 | 127 | 14:00
| Cantonment | 138 | 18:30 | 131 | 15:00 | Pabna | 135 | 18:00 | 128 | 21:00
| Chandpur | 140 | 18:30 | 118 | 14:00 | Palashbari | 129 | 18:00 | 117 | 23:00
| Chandraghona | 139 | 22:00 | 126 | 13:00 | Panchagarh | 136 | 19:00 | 118 | 03:00
| Chapai | 133 | 18:00 | 126 | 21:00 | Patuakhali | 139 | 18:30 | 132 | 21:00
| Charsaidpur | 141 | 20:00 | 133 | 10:00 | Payra | 141 | 18:30 | 136 | 21:00
| Chauddagram | 137 | 18:30 | 122 | 14:00 | PHP | 136 | 18:30 | 121 | 13:00
| Chhatak | 133 | 06:00 | 126 | 20:00 | Postogola | 140 | 19:30 | 134 | 13:00
| Chowmuhani | 135 | 18:30 | 115 | 15:00 | Purbachal | 137 | 00:00 | 128 | 14:00
| Chuadanga | 133 | 18:30 | 117 | 22:00 | Purbasadipur | 131 | 17:00 | 120 | 04:00
| Coxsbazar | 125 | 18:30 | 108 | 00:00 | Rahim | 138 | 18:00 | 134 | 13:00
| Cumilla(N) | 139 | 18:30 | 128 | 13:00 | Rajbari | 131 | 18:00 | 125 | 13:00
| Cumilla(S) | 138 | 22:00 | 125 | 13:00 | Rajendrapur | 136 | 03:00 | 129 | 11:00
| Daudkandi | 138 | 18:30 | 128 | 13:00 | Rajshahi | 132 | 18:00 | 125 | 13:00
| Dhaka | 134 | 01:00 | 129 | 13:00 | Rajshahi-230 | 133 | 18:00 | 125 | 13:00
| Dhamrai | 135 | 02:00 | 130 | 13:00 | Ramganj | 137 | 18:30 | 112 | 14:00
| Dhanmondi | 139 | 18:30 | 133 | 14:00 | Rampur | 137 | 18:30 | 126 | 13:00
| Dohazari | 137 | 18:30 | 123 | 00:00 | Rampura | 134 | 02:00 | 128 | 12:00
| Faridpur | 132 | 18:30 | 126 | 13:00 | Rangamati | 137 | 18:30 | 126 | 15:00
| Fatullah | 136 | 18:30 | 131 | 13:00 | Rangpur | 129 | 17:00 | 118 | 19:30
| Fenchuganj | 137 | 02:00 | 134 | 13:00 | Ruppur | 135 | 06:00 | 131 | 13:00
| Feni | 136 | 18:30 | 122 | 13:00 | Saidpur | 132 | 18:30 | 122 | 19:30
| Ghorashal | N/A | N/A | N/A | N/A | Satkhira | 136 | 18:30 | 121 | 22:00
| Goalpara | 141 | 18:30 | 126 | 02:00 | Satmasjid | 138 | 02:00 | 132 | 13:00
| Gollamari | 140 | 18:30 | 129 | 13:00 | Savar | 140 | 18:00 | 132 | 10:00
| Gopalganj | 136 | 18:30 | 127 | 13:00 | Shahjadpur | 140 | 04:00 | 135 | 19:30
| Gopalganj-400 | 133 | 18:30 | 126 | 10:00 | Shahjibazar | 135 | 06:00 | 133 | 00:00
| Gulshan | 133 | 00:00 | 128 | 13:00 | Shahmirpur | 138 | 22:00 | 128 | 13:00
| Halishahar | 138 | 19:00 | 126 | 15:00 | Shariatpur | 133 | 18:30 | 126 | 04:00
| Haripur | 138 | 18:00 | 134 | 13:00 | Sherpur | 125 | 06:00 | 112 | 19:00
| HaripurSBU | 138 | 18:00 | 134 | 13:00 | Shikalbaha | N/A | N/A | N/A | N/A
| Hasnabad | 140 | 20:00 | 135 | 13:00 | Shikalbaha-230 | 136 | 18:30 | 127 | 15:00
| Hathazari | 138 | 22:00 | 130 | 13:00 | Shitalakhya | 140.4 | 20:00 | 133.2 | 13:00
| Ishurdi | 137 | 18:30 | 130 | 21:00 | Sholosohor | 137 | 22:00 | 126 | 13:00
| Jaldhaka | 130 | 17:00 | 120 | 01:00 | Shyampur | 136 | 18:30 | 130 | 13:00
| Jamalpur | 129 | 11:00 | 115 | 00:00 | Shyampur-230 | 136 | 18:30 | 131 | 13:00
| Jashore | 135 | 18:00 | 123 | 21:00 | Siddhirganj | 139 | 18:00 | 134 | 13:00
| Jhenaidah | 139 | 18:30 | 127 | 22:00 | Sirajganj | 135 | 18:30 | 126 | 22:00
| Jhenaidah-230 | 139 | 18:30 | 128 | 22:00 | Sonargaon | 135 | 00:00 | 132 | 10:00
| Joydebpur | 142 | 20:00 | 134 | 10:00 | Sreemongol | 135 | 04:00 | 132 | 14:00
| Joypurhat | 130 | 18:30 | 115 | 23:00 | Sreepur | 130 | 18:00 | 126 | 15:00
| Juldah | 138 | 18:30 | 129 | 10:00 | Srinagar | 135 | 18:00 | 126 | 13:00
| Kabirpur | 136 | 18:30 | 129 | 14:00 | SSM | 138 | 18:00 | 130 | 01:00
| Kachua | 137 | 18:30 | 121 | 08:00 | Sunamganj | 131 | 09:00 | 122 | 22:00
| Kaliakoir | 137 | 18:00 | 133 | 14:00 | Sylhet | 133 | 05:00 | 130 | 15:00
| Kallyanpur | 134 | 03:00 | 129 | 13:00 | Tangail | 132 | 18:30 | 124 | 19:00
| Kalurghat | 138 | 18:30 | 127 | 13:00 | Thakurgaon | 135 | 19:00 | 116 | 03:00
| Kamrangirchar | 137 | 18:30 | 127 | 13:00 | TK | 138 | 22:00 | 0.8 | 06:00
| Kaptai | N/A | N/A | N/A | N/A | Tongi | 138 | 03:00 | 133 | 16:00
| Kazla | 135 | 00:00 | 130 | 14:00 | Ullon | 134 | 02:00 | 128 | 13:00
| Keranigonj | 137 | 18:30 | 127 | 14:00 | Uttara | 141 | 18:00 | 133 | 13:00
| Khagrachori | 138 | 22:00 | 124 | 15:00 | UttaraNew | 140 | 18:30 | 133 | 11:00
| Khulna | 138 | 18:30 | 127 | 22:00 | Zigatola | 137 | 18:30 | 126 | 14:00
| Khulna(S) | 140 | 18:30 | 130 | 13:00
| Khulshi | 138 | 22:00 | 125 | 13:00
| Kishoreganj | 132 | 18:00 | 124 | 21:00
| Kodda | 140 | 19:30 | 128 | 15:00
| KSRM | 137 | 19:30 | 127 | 13:00
| Kulaura | 135 | 10:00 | 132 | 19:00
| Kurigram | 131 | 18:00 | 117 | 22:00
| Kushtia | 136 | 18:00 | 128 | 22:00

## L-Curve
Date | 2023-07-04
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 470 | 8323 | 4982 | 13305 |  |  |  | QF-LDC-11
0:30 | 485 | 7975.5 | 4630.5 | 12606 | Date: | 2023-07-04
1:00 | 500 | 7628 | 4279 | 11907
1:30 | 515 | 7529.5 | 4209.5 | 11739
2:00 | 530 | 7431 | 4140 | 11571
2:30 | 525 | 7384 | 3944 | 11328 | [5 empty] | Gen. at Eve. Peak | 13402 | 13402 MW (21:00 )
3:00 | 520 | 7337 | 3748 | 11085 | [6 empty] | 21:00
3:30 | 525 | 7292 | 3733.5 | 11025.5 | [5 empty] | Gen. at Day Peak | 11051 | 11051 MW (12:00 )
4:00 | 530 | 7247 | 3719 | 10966 | [6 empty] | 12:00
4:30 | 545 | 7110 | 3686.5 | 10796.5 | [5 empty] | Highest Generation | 13474
5:00 | 560 | 6973 | 3654 | 10627 | [6 empty] | 23:00
5:30 | 555 | 6775.5 | 3556 | 10331.5
6:00 | 550 | 6578 | 3458 | 10036
6:30 | 587 | 6511.5 | 3487 | 9998.5
7:00 | 624 | 6445 | 3516 | 9961
7:30 | 622 | 6461.5 | 3540.5 | 10002
8:00 | 620 | 6478 | 3565 | 10043
8:30 | 710 | 6506.5 | 3640.5 | 10147
9:00 | 800 | 6535 | 3716 | 10251
9:30 | 797 | 6604 | 3705 | 10309
10:00 | 794 | 6673 | 3694 | 10367
10:30 | 802 | 6755.5 | 3735.5 | 10491
11:00 | 810 | 6838 | 3777 | 10615
11:30 | 840 | 6936 | 3897 | 10833
12:00 | 870 | 7034 | 4017 | 11051
12:30 | 865 | 7118 | 4110.5 | 11228.5
13:00 | 860 | 7202 | 4204 | 11406
13:30 | 865 | 7239 | 4231.5 | 11470.5
14:00 | 870 | 7276 | 4259 | 11535
14:30 | 970 | 7275.5 | 4310.5 | 11586
15:00 | 1070 | 7275 | 4362 | 11637
15:30 | 1073 | 7206 | 4372 | 11578
16:00 | 1076 | 7137 | 4382 | 11519
16:30 | 1048 | 6940 | 4306.5 | 11246.5
17:00 | 1020 | 6743 | 4231 | 10974
17:30 | 915 | 6686 | 4072.5 | 10758.5
18:00 | 810 | 6629 | 3914 | 10543
18:30 | 780 | 7003 | 4069 | 11072
19:00 | 750 | 7377 | 4224 | 11601
19:30 | 640 | 8438 | 4804 | 13242
20:00 | 530 | 8317 | 4891 | 13208 |  |  |  | Executive Engineer
20:30 | 503 | 8484 | 4821 | 13305 |  |  |  | Network Operation Division
21:00 | 476 | 8651 | 4751 | 13402
21:30 | 453 | 8662.5 | 4763 | 13425.5
22:00 | 430 | 8674 | 4775 | 13449 |  |  |  |  | Page 6 of 7
22:30 | 450 | 8570 | 4891.5 | 13461.5
23:00 | 470 | 8466 | 5008 | 13474
23:30 | 470 | 8394.5 | 4995 | 13389.5
24:00 | 470 | 8323 | 4982 | 13305
13402 MW (21:00 )
11051 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-07-04 |  | Energy |  | 279463511
[15 empty] | 43649 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 4817 | 780 | 2504 | 0 | 2871 | 1574 | 30 | 0 | 571 | 158 | 0 | 0 | 186.225
0:30 | 4687 | 819 | 2506 | 0 | 2545.5 | 1414 | 30 | 0 | 451.5 | 153 | 0 | 0 | 182.8825 |  |  | Date: | 43649
1:00 | 4557 | 858 | 2508 | 0 | 2220 | 1254 | 30 | 0 | 332 | 148 | 0 | 0 | 179.54
1:30 | 4523 | 858 | 2469 | 0 | 2156 | 1253 | 30 | 0 | 303 | 147 | 0 | 0 | 170.4675 | [9 empty] | Total Energy | 277.1939 | Total Energy Gen 277.194 MKWHr Energy Not Served 1.859 MKWHr Energy Requirement 279.053 MKWHr
2:00 | 4489 | 858 | 2430 | 0 | 2092 | 1252 | 30 | 0 | 274 | 146 | 0 | 0 | 161.395 | [9 empty] | Energy not Served | 1.8592
2:30 | 4444 | 886.5 | 2429.5 | 0 | 1869.5 | 1282 | 30 | 0 | 242.5 | 144 | 0 | 0 | 157.575 | [9 empty] | Energy Requirement | 279.0531
3:00 | 4399 | 915 | 2429 | 0 | 1647 | 1312 | 30 | 0 | 211 | 142 | 0 | 0 | 153.755
3:30 | 4394.5 | 915.5 | 2429 | 0 | 1564.5 | 1339 | 30 | 0 | 211 | 142 | 0 | 0 | 147.5475 | [8 empty] | Shortage
4:00 | 4390 | 916 | 2429 | 0 | 1482 | 1366 | 30 | 0 | 211 | 142 | 0 | 0 | 141.34
4:30 | 4395.5 | 916 | 2440 | 0 | 1264.5 | 1398.5 | 30 | 0 | 211 | 141 | 0 | 0 | 121.285
5:00 | 4401 | 916 | 2451 | 0 | 1047 | 1431 | 30 | 0 | 211 | 140 | 0 | 0 | 101.23
5:30 | 4377 | 916 | 2376.5 | 0 | 868 | 1453 | 30 | 0 | 175 | 132 | 4 | 0 | 97.41
6:00 | 4353 | 916 | 2302 | 0 | 689 | 1475 | 30 | 0 | 139 | 124 | 8 | 0 | 93.59
6:30 | 4362.5 | 916 | 2252.5 | 0 | 678 | 1479.5 | 30 | 0 | 121 | 125 | 34 | 0 | 89.2925 | [7 empty] | Coal
7:00 | 4372 | 916 | 2203 | 0 | 667 | 1484 | 30 | 0 | 103 | 126 | 60 | 0 | 84.995
7:30 | 4355.5 | 916 | 2216.5 | 0 | 672 | 1496.5 | 30 | 0 | 103 | 125 | 87.5 | 0 | 52.525 | [6 empty] | Oil
8:00 | 4339 | 916 | 2230 | 0 | 677 | 1509 | 30 | 0 | 103 | 124 | 115 | 0 | 20.055
8:30 | 4342 | 916 | 2223 | 0 | 691.5 | 1552.5 | 30 | 0 | 103 | 121 | 168 | 0 | 20.055
9:00 | 4345 | 916 | 2216 | 0 | 706 | 1596 | 30 | 0 | 103 | 118 | 221 | 0 | 20.055
9:30 | 4413.5 | 916 | 2235.5 | 0 | 686 | 1605.5 | 30 | 0 | 103 | 125 | 194.5 | 0 | 49.66
10:00 | 4482 | 916 | 2255 | 0 | 666 | 1615 | 30 | 0 | 103 | 132 | 168 | 0 | 79.265
10:30 | 4498 | 916 | 2229 | 0 | 760 | 1613 | 30 | 0 | 126.5 | 133 | 185.5 | 0 | 39.6325
11:00 | 4514 | 916 | 2203 | 0 | 854 | 1611 | 30 | 0 | 150 | 134 | 203 | 0 | 0
11:30 | 4566 | 912.5 | 2312.5 | 0 | 962 | 1560 | 30 | 0 | 160.5 | 137 | 192.5 | 0 | 0
12:00 | 4618 | 909 | 2422 | 0 | 1070 | 1509 | 30 | 0 | 171 | 140 | 182 | 0 | 0
12:30 | 4717 | 909 | 2434.5 | 0 | 1113.5 | 1491.5 | 30 | 0 | 187 | 143 | 203 | 0 | 0
13:00 | 4816 | 909 | 2447 | 0 | 1157 | 1474 | 30 | 0 | 203 | 146 | 224 | 0 | 0
13:30 | 4816 | 909 | 2447 | 0 | 1157 | 1474 | 30 | 0 | 203 | 146 | 224 | 0 | 0
14:00 | 4816 | 909 | 2447 | 0 | 1157 | 1474 | 30 | 0 | 203 | 146 | 224 | 0 | 0
14:30 | 4771.5 | 909 | 2425 | 0 | 1278 | 1512 | 30 | 0 | 233.5 | 150 | 212.5 | 0 | 61.12
15:00 | 4727 | 909 | 2403 | 0 | 1399 | 1550 | 30 | 0 | 264 | 154 | 201 | 0 | 122.24
15:30 | 4687 | 909 | 2408.5 | 0 | 1399 | 1549.5 | 30 | 0 | 265.5 | 152 | 177.5 | 0 | 123.6725
16:00 | 4647 | 909 | 2414 | 0 | 1399 | 1549 | 30 | 0 | 267 | 150 | 154 | 0 | 125.105
16:30 | 4534.5 | 908.5 | 2343 | 0 | 1348.5 | 1550.5 | 30 | 0 | 257.5 | 144 | 130 | 0 | 127.4925
17:00 | 4422 | 908 | 2272 | 0 | 1298 | 1552 | 30 | 0 | 248 | 138 | 106 | 0 | 129.88
17:30 | 4238 | 908 | 2115.5 | 0 | 1442 | 1526.5 | 45 | 0 | 267.5 | 135 | 81 | 0 | 64.94
18:00 | 4054 | 908 | 1959 | 0 | 1586 | 1501 | 60 | 0 | 287 | 132 | 56 | 0 | 0
18:30 | 4128 | 908.5 | 2099.5 | 0 | 1836.5 | 1490.5 | 60 | 0 | 379.5 | 141 | 28.5 | 0 | 0
19:00 | 4202 | 909 | 2240 | 0 | 2087 | 1480 | 60 | 0 | 472 | 150 | 1 | 0 | 0
19:30 | 4723 | 909 | 2383 | 0 | 2901 | 1540 | 60 | 0 | 572 | 154 | 0 | 0 | 8
20:00 | 4526 | 909 | 2350 | 0 | 3063 | 1550 | 60 | 0 | 598 | 152 | 0 | 0 | 16
20:30 | 4627.5 | 861.5 | 2424 | 0 | 3036.5 | 1562 | 45 | 0 | 596.5 | 152 | 0 | 0 | 26
21:00 | 4729 | 814 | 2498 | 0 | 3010 | 1574 | 30 | 0 | 595 | 152 | 0 | 0 | 36
21:30 | 4749.5 | 813.5 | 2482.5 | 0 | 3028.5 | 1573.5 | 30 | 0 | 591 | 157 | 0 | 0 | 25.64
22:00 | 4770 | 813 | 2467 | 0 | 3047 | 1573 | 30 | 0 | 587 | 162 | 0 | 0 | 15.28
22:30 | 4806.5 | 795.5 | 2481.5 | 0 | 3009.5 | 1573.5 | 30 | 0 | 603 | 162 | 0 | 0 | 96.455
23:00 | 4843 | 778 | 2496 | 0 | 2972 | 1574 | 30 | 0 | 619 | 162 | 0 | 0 | 177.63
23:30 | 4830 | 779 | 2500 | 0 | 2921.5 | 1574 | 30 | 0 | 595 | 160 | 0 | 0 | 181.9275 |  |  | Max Temp. in Dhaka |  | 36.0° C
24:00 | 4817 | 780 | 2504 | 0 | 2871 | 1574 | 30 | 0 | 571 | 158 | 0 | 0 | 186.225
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 277.194 MKWHr Energy Not Served 1.859 MKWHr Energy Requirement 279.053 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-07-04
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 60 |  | 60 | 60 | 60 | 30 | 30 | 30 | 30 | 822180
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 109 | 107 | 108 | 108 | 104 | 105 | 109 | 110 | 108 | 110 | 108 | 107 | 106 | 107 | 106 | 104 | 103 | 102 |  | 109 | 103 | 105 | 106 | 102 | 102 | 103 | 2500000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 13 |  | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 248385
| Teknaf 20MW PP (Solartech) | [5 empty] | 2 | 8 | 7 | 15 |  | 14 |  | 12 | 13 | 11 | 6 | 2 | 1 | [8 empty] | 85860
6 | Sikalbaha 225MW CCPP (Gas) | 223 | 227 | 224 | 226 | 226 | 225 | 223 | 223 | 221 | 221 | 221 | 220 | 215 | 217 | 218 | 221 | 220 | 223 |  | 145 | 152 | 152 | 151 | 152 | 150 | 151 | 4946154
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 31 | 31 | 31 | 31 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 783129
12 | Hathazari 100 MW peaking PP | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 32 | 30 | 32 | 32 | 33 | 33 | 33 |  | 33 | 33 | 50 | 73 | 72 | 71 | 48 | 911376
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 37 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 970181
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 32 | 35 |  | 35 | 35 | 35 | 36 | 36 | 36 | 36 | 835904
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 160 | 120 | 99 | 99 | 101 | 101 | 102 | 100 | 103 | 103 | 101 | 158 | 185 | 187 | 152 | 155 | 99 | 76 |  | 159 | 197 | 120 | 150 | 157 | 195 | 193 | 3338000
17 | Siddhirganj 335 MW CCPP | 326 | 327 | 327 | 329 | 329 | 300 | 280 | 280 | 280 | 280 | 280 | 317 | 315 | 313 | 318 | 315 | 270 | 250 |  | 250 | 318 | 280 | 320 | 330 | 325 | 326 | 7387185
18 | Kodda 300 MW PP Unit-2 (Summit) | 120 | 120 | 120 | 120 | [6 empty] | 8 | 15 | 15 | 17 | 86 | 95 | 45 | 45 |  | 69 | 130 | 149 | 195 | 195 | 195 | 286 | 2027345
19 | Ashuganj 195 MW PP (APSCL-United) | 180 | 182 | 189 | 189 | 189 | 148 | 108 | 108 | 108 | 108 | 108 | 123 | 147 | 147 | 147 | 147 | 148 | 148 |  | 148 | 148 | 148 | 158 | 177 | 185 | 187 | 3663272
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 150 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 150 | 150 | 180 | 220 | 220 | 220 | 220 | 170 | 140 |  | 160 | 220 | 220 | 220 | 220 | 220 | 221 | 3948000
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4315500
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 305 | 303 | 305 | 303 | 301 | 304 | 303 | 308 | 305 | 305 | 240 | 106 | [13 empty] | 0 | 3518181
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 23 | 42 | 33 | 34 | 33 | 33 | 33 | 40 | 39 | 39 | 38 |  | 41 | 41 | 41 | 41 | 42 | 42 | 43 | 759600
33 | Ashuganj 225 MW CCPP | 186 | 183 | 183 | 183 | 210 | 210 | 210 | 210 | 208 | 206 | 206 | 205 | 202 | 204 | 202 | 204 | 183 | 183 |  | 195 | 183 | 183 | 198 | 182 | 211 | 211 | 4824000
34 | Ashuganj 450 MW CCPP(South) | [25 empty] | 0 | 0
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 275 | 275 | 350 | 310 | 310 | 305 | 305 | 305 | 325 | 310 | 320 | 305 | 310 | 275 |  | 330 | 310 | 310 | 330 | 310 | 310 | 310 | 7684500
| Ashuganj 420 MW CCPP(East) | 292 | 293 | 293 | 292 | 292 | 292 | 292 | 292 | 292 | 385 | 385 | 322 | 338 | 322 | 300 | 234 | 237 | 200 |  | 262 | 278 | 278 | 273 | 282 | 279 | 279 | 7071700
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 398 | 397 | 396 | 397 | 396 | 377 | 342 | 342 | 342 | 349 | 403 | 402 | 400 | 396 | 403 | 400 | 403 | 348 |  | 311 | 405 | 398 | 405 | 406 | 405 | 405 | 9355260
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 400 | 400 | 400 | 400 | 400 | 400 | 450 | 450 | 450 | 450 | 450 | 380 | 300 |  | 420 | 450 | 450 | 450 | 450 | 450 | 450 | 9806500
41 | Haripur 360 MW CCPP(HPL) | 347 | 337 | 336 | 342 | 342 | 308 | 307 | 307 | 307 | 338 | 336 | 333 | 327 | 327 | 321 | 321 | 302 | 252 |  | 300 | 312 | 301 | 342 | 332 | 331 | 335 | 7730000
42 | RPCL 210MW CCPP | 199 | 202 | 199 | 201 | 198 | 198 | 198 | 198 | 196 | 195 | 192 | 194 | 193 | 174 | 161 | 161 | 165 | 150 |  | 144 | 151 | 153 | 153 | 176 | 176 | 179 | 4273920
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 8 | 16 | 29 | 30 | 29 | 21 | 10 | 14 | 28 | 27 | 14 | 4 |  | 0 | [6 empty] | 248300
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 41 | 41 | 41 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1009000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 20 | 20 | 20 | 22 | 39 | 39 | 39 |  | 39 | 40 | 40 | 39 | 40 | 40 | 40 | 705840
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 61 | 61 | 61 | 61 | 61 | 60 | 40 | 60 | 60 | 59 | 60 | 60 | 59 | 59 | 59 | 59 | 59 | 40 |  | 40 | 61 | 61 | 61 | 61 | 60 | 60 | 1371456
48 | Shahjibazar 86 MW PP (Shahjibazar) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 84 | 84 | 84 | 85 | 40 |  | 70 | 85 | 85 | 85 | 85 | 85 | 85 | 1976640
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 137 | 137 | 136 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 132 | 132 | 132 | 132 | 132 |  | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 3218490
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 396000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 247680
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 189408
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 47 | 47 | 11 | 44 | 44 | 44 | 44 | 44 | 47 | 44 | 22 | 22 | 44 | 47 |  | 22 | 44 | 47 | 47 | 47 | 47 | 47 | 995400
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 564624
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 290 | 280 | 290 | 290 | 285 | 295 | 300 | 290 | 300 | 290 | 300 | 305 | 320 | 290 | 310 | 280 | 260 |  | 270 | 260 | 280 | 290 | 290 | 300 | 285 | 7149000
| Bibiyana South 400 MW | 382 | 382 | 375 | 365 | 365 | 365 | 365 | 361 | 365 | 350 | 350 | 350 | 350 | 350 | 359 | 350 | 350 | 350 |  | 367 | 389 | 312 | 378 | 390 | 390 | 370 | 8686700
58 | Nababganj 55 MW PP (Southern power ) | [10 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 55 |  | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 539872
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | [15 empty] | 5 | 12 | 12 | 12 | 12 | 12 | 12 | 120720
60 | Barabkunda 22 MW PP (Regent) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 8 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 309648
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  |  |  | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 388620
62 | Tangail 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 16 | 16 | 17 | 17 | 15 | 17 | 17 | 17 | 17 | 17 | 13 | 13 |  | 13 | 13 | 13 | 13 | 17 | 17 | 17 | 366120
63 | Impoprt (Tripura) | 148 | 146 | 142 | 142 | 140 | 124 | 126 | 124 | 118 | 132 | 134 | 140 | 146 | 148 | 154 | 150 | 138 | 132 |  | 150 | 154 | 152 | 152 | 162 | 162 | 158 | 3400230
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 36 | 42 | 42 | 42 | 24 | 21 | 21 | 20 | 20 | 20 | 17 | 17 | 17 | 21 | 32 |  | 26 | 35 | 38 | 42 | 29 | 33 | 36 | 745440
65 | Feni 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 19 | 17 | 17 | 18 | 19 | 20 |  | 20 | 20 | 20 | 20 | 19 | 19 | 20 | 464112
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 252180
67 | Jangalia 33 MW PP (Summit) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 31 | 28 | 31 | 31 | 30 | 29 | 29 | 30 | 31 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 754000
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 477130
69 | Summit Ashulia | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 351750
70 | Summit Madhabdi | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 22 | 22 | 22 | 22 | 331380
71 | Maona 33 MW PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 391320
72 | Rupganj 33 MW PP(Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 31 | 31 | 31 | 31 | 31 | 31 | 31 |  | 31 | 31 | 32 | 32 | 32 | 32 | 32 | 645900
73 | Ghorashal 108 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 299000
| Feni Lanka Power | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 34 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 52 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1812600
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 27 | 27 | 26 | 28 | 27 | 28 | 28 |  | 57 | 57 | 56 | 58 | 57 | 13 | 9 | 514080
| Manikgonj 162MW PP(MPGL) | 72 | 72 | 72 | 72 | 17 | [5 empty] | 17 | 17 | 17 | 83 | 103 | 108 | 72 | 72 |  | 72 | 108 | 108 | 72 | 72 | 72 | 72 | 1248480
77 | Siddhirganj 100 PP(Dutch Bangla) | 25 | 9 | 9 | 9 | [6 empty] | 4 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 12 | 30 | 42 | 70 | 80 | 75 | 75 | 445440
78 | Gazipur 52 MW PP | 8 | 8 | 8 | [16 empty] | 8 | 16 | 25 |  |  | 8 | 8 | 63360
79 | Kodda 150 MW PP | [19 empty] | 16 | 48 | 48 | 32 | 32 | 64 | 110 | 242400
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 40 | 34 | 41 | 41 | 41 | 41 | 41 |  | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 1005326
| Gazipur 100 MW PP | 50 | 70 | 50 | 35 | 35 |  |  | 2 | 17 | 17 | 17 | 17 | 34 | 34 | 34 | 34 | 34 | 34 |  | 52 | 95 | 105 | 105 | 105 | 105 | 105 | 1107840
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 2 | 2 | 1 | 2 | 3 | 5 | 5 | 2 | 2 | 3 | 0 | [9 empty] | 28199
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 449048
| Karnaphuli Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 |  | 34 | 34 | 34 | 34 | 34 | 34 | 24 | 524397
82 | Madanganj 102 PP(Summit) | 50 | 50 | 42 | 7 | [7 empty] | 16 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 40 | 43 | 72 | 65 | 65 | 95 | 564081
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [15 empty] | 9 | 14 | 23 |  | 23 | 23 | 22 | 23 | 23 | 23 | 0 | 173933
86 | Meghnaghat CCPP ( Summit) | 272 | 274 | 277 | 269 | 285 | 273 | 272 | 282 | 285 | 286 | 265 | 300 | 303 | 304 | 305 | 298 | 292 | 267 |  | 298 | 273 | 265 | 306 | 275 | 279 | 291 | 6896989
87 | Meghnaghat 100 MW(IEL) | 9 | 8 |  |  |  |  | 0 | 8 | 8 | 9 | 8 | 9 | 9 |  |  |  |  | 6 |  | 8 | 9 | 9 | 8 | 8 | 9 | 9 | 120000
| Meghnaghat 104 MW PP (OPCL) | 51 | 19 | 17 | 17 | 17 | 17 | 17 | 17 | 31 | 49 | 53 | 53 | 53 | 53 | 53 | 53 | 58 | 73 |  | 73 | 73 | 72 | 72 | 72 | 64 | 55 | 1120320
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 69 | 69 | 69 | 58 | 58 | 58 |  | 72 | 80 | 80 | 80 | 80 | 80 | 58 | 1484520
92 | Fenchuganj 44 MW (Energyprima) | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 42 | 44 | 41 | 41 | 43 | 43 | 43 | 43 | 42 |  | 42 | 42 | 40 | 47 | 47 | 47 | 47 | 1040256
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 10 | 10 | 10 | 10 | 32 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 865854
94 | Gagnagar 102 MW PP (Digital Power) | 74 | 74 | 74 | 74 | 8 | [5 empty] | 3 | 16 | 16 | 32 | 50 | 50 | 24 | 24 |  | 24 | 64 | 102 | 102 | 102 | 58 | 50 | 947808
95 | Patenga 50MW PP (Baraka) | 16 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 43 |  | 48 | 50 | 50 | 50 | 50 | 50 | 13 | 407520
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | [17 empty] | 8 | 30 | 30 | 30 | 30 | 30 | 55 | 244022
100 | Manikganj 55 MW PP (Northern) | 55 | [10 empty] | 17 | 35 | 35 | 35 | 35 | 55 | 55 |  | 55 | 55 | 55 | 35 | 35 | 55 | 55 | 587998
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 1 | 2 | 1 | 1 | 1 | 0 | [8 empty] | 10550
103 | Kamalaghat 54 MW PP(Banco Energy) | [17 empty] | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 0 | 196200
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0 | 25588
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 47 | 47 | 47 | 47 | 47 | 47 | 24 | 24 | 24 | 24 | 24 | 24 | 8 | 8 | 8 | 8 | 8 | 8 |  | 22 | 104 | 112 | 112 | 112 | 38 | 37 | 964800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 62 | 92 | 101 | 80 | 42 | [6 empty] | 15 | 15 | 17 | 17 | 17 | 17 | 17 |  | 21 | 63 | 63 | 96 | 96 | 95 | 108 | 994752
115 | Juldah 100 MW PP Unit-3 (Acorn) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 75 | 75 | 75 | 50 | 50 | 50 |  | 88 | 88 | 100 | 100 | 100 | 100 | 50 | 1501440
116 | Chandpur 200 MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 29 | 54 | 68 | 68 | 68 | 68 | 68 | 68 | 86 |  | 105 | 100 | 106 | 103 | 105 | 105 | 46 | 1316640
117 | Ashuganj 150 MW PP (Midland) | 16 | 6 | 6 | 5 | 6 | [5 empty] | 5 | 6 | 10 | 11 | 13 | 18 | 18 | 35 |  | 68 | 115 | 110 | 128 | 145 | 150 | 150 | 946763
118 | Bibiyana-III 400 MW CCPP | 329 | 331 | 331 | 331 | 329 | 331 | 337 | 331 | 331 | 374 | 367 | 366 | 400 | 366 | 378 | 367 | 367 | 367 |  | 350 | 416 | 415 | 406 | 412 | 409 | 410 | 8746000
| Jamalpur 115 MW PP (United) | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 56 | 56 | 56 | 56 | 66 |  | 57 | 56 | 56 | 56 | 56 | 47 | 47 | 1082400
| Anwara 300 MW PP (United) | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 87 | 87 | 87 | 87 | 119 |  | 170 | 292 | 240 | 245 | 245 | 123 | 123 | 2857855
| Juldah unit-2 (Acorn) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 76 | 76 | 63 | 50 | 50 | 50 |  | 50 | 90 | 90 | 90 | 90 | 90 | 50 | 1427520
| Anlima Energy Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 38 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 779073
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 441360
| Spectra Solar Plant Ltd. | [5 empty] | 2 | 6 | 18 | 25 | 31 | 34 | 34 | 34 | 26 | 17 | 18 | 9 | 2 | [8 empty] | 254814
| Chandpur 115(Doreen) | 87 | 36 | 24 | 18 | 18 | 17 | 18 | 18 | 18 | 18 | 50 | 75 | 75 | 76 | 66 | 40 | 39 | 48 |  | 81 | 94 | 95 | 94 | 88 | 72 | 72 | 1253760
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | [5 empty] | 7 | 17 | 17 | 17 | 17 | 17 | 22 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 17 | 452520
| Mirsharai 150 MW (Oil) | 108 | 108 | 108 | 108 | 108 | 36 |  |  |  |  | 47 | 72 | 106 | 157 | 157 | 157 | 140 | 163 |  | 161 | 161 | 157 | 157 | 157 | 157 | 157 | 2402036
Mirsharai 150 MW (Gas)
Cox's Bazar Wind
120 | Eastern Zone Total | 7628 | 7431 | 7337 | 7247 | 6973 | 6578 | 6445 | 6478 | 6535 | 6673 | 6838 | 7034 | 7202 | 7276 | 7275 | 7137 | 6743 | 6629 |  | 7377 | 8438 | 8317 | 8651 | 8674 | 8466 | 8323 | 175950634
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 95 | 95 | 16 | [16 empty] | 18 | 69 | 98 | 64 | 64 | 95 | 95 | 620160
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 18 | [15 empty] | 2 | 15 |  | 26 | 36 | 37 | 32 | 29 | 29 | 21 | 177120
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | 17 | 17 | 17 | [6 empty] | 5 | 12 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 289920
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 3 | 29 | 54 | 78 | 92 | 101 | 54 | 102 | 56 | 57 | 30 | 19 | 17 | [8 empty] | 719280
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | 100 | 100 | [17 empty] | 17 | 30 | 54 | 17 | 17 | 150 | 150 | 513600
133 | Bhola Nutan Biddut BD LTD (GAS) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 224 | 220 | 220 | 220 | 220 | 217 | 219 | 218 | 218 | 219 | 182 |  | 220 | 220 | 220 | 222 | 220 | 225 | 222 | 5292927
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 90 | 96 | 96 | 48 | 16 | [6 empty] | 16 | 16 | 16 | 48 | 96 | 64 | 64 |  | 64 | 64 | 96 | 96 | 96 | 96 | 96 | 1229760
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3621800
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | [14 empty] | 65 | 67 | 66 | 52 |  | 65 | 54 | 50 | 67 | 68 | 68 | 68 | 625000
140 | Bhola 33 MW PP (Venture) | 30 | 29 | 28 | 28 | 28 | 26 | 23 | 21 | 21 | 20 | 20 | 19 | 21 | 19 | 21 | 22 | 17 | 21 |  | 26 | 28 | 28 | 29 | 30 | 30 | 30 | 582684
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 16 | [17 empty] | 8 | 40 | 40 | 8 | 8 | 40 | 40 | 176625
143 | Gopalganj 100 MW Peaking PP | 47 | [18 empty] | 35 | 50 | 60 | 65 | 61 | 62 | 62 | 355840
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 85 | 85 | 15 | [14 empty] | 7 |  | 15 | 43 | 50 | 15 | 15 | 50 | 105 | 465120
146 | Bheramara HVDC | 858 | 858 | 915 | 916 | 916 | 916 | 916 | 916 | 916 | 916 | 916 | 909 | 909 | 909 | 909 | 909 | 908 | 908 |  | 909 | 909 | 909 | 814 | 813 | 778 | 780 | 21529454
147 | Bheramara 410 MW CCPP | 355 | 350 | 360 | 355 | 355 | 355 | 360 | 355 | 355 | 350 | 350 | 350 | 395 | 395 | 395 | 395 | 350 | 280 |  | 300 | 390 | 395 | 400 | 400 | 400 | 400 | 9073440
148 | Payra 1320 MW |  |  | 57 | 120 | 190 | 230 | 240 | 260 | 350 | 370 | 430 | 460 | 530 | 560 | 600 | 600 | 600 | 550 |  | 530 | 590 | 600 | 622 | 622 | 622 | 622 | 10606000
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 181 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4349400
153 | Baghabari 71 MW GTPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 65 | 65 | 1480000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [20 empty] | 21 | 21 | 28 | 28 | 28 | 28 | 125360
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 2 | 2 | 1 | 5 | 5 | 5 | 2 | 2 | 0 | 1 | 0 | [8 empty] | 35460
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 195 | 214 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 153 | 152 | 183 | 186 | 187 | 163 | 171 | 164 | 150 |  | 137 | 181 | 176 | 171 | 176 | 179 | 177 | 4297164
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 187 | 157 | 156 | 156 | 157 | 156 | 160 | 161 | 156 | 164 | 157 | 163 | 186 | 201 | 186 | 192 | 181 | 130 |  | 134 | 164 | 172 | 185 | 184 | 196 | 184 | 4346973
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 420 | 359 | 360 | 358 | 358 | 353 | 358 | 358 | 358 | 359 | 317 | 422 | 419 | 419 | 420 | 417 | 376 | 303 |  | 333 | 421 | 383 | 415 | 420 | 419 | 424 | 9098800
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 21 | 28 | [24 empty] | 36140
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 4 | 4 | 8 | 8 |  |  | 8 | 8 | 8 | 0 | 6 | 8 | 8 | 8 |  | 0 | 6 | 0 | 6 | 8 | 8 | 8 | 134874
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern) | [22 empty] | 8 | 8 | 34 | 34 | 59405
167 | Katakhali 50 MW Peaking PP | [19 empty] | 28 | 28 | 30 | 22 | 22 | 22 | 22 | 125329
168 | Santahar 50 MW Peaking PP | 35 | 35 | [17 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 0 | 260230
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | [19 empty] | 8 | 8 | 8 | 52 | 52 | 207538
170 | Chapainawabganj 100 MW Peaking PP | [13 empty] | 8 | 8 | 8 | 8 | 8 |  | 70 | 92 | 92 | 82 | 82 | 82 | 54 | 474400
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 92 | 110 | 110 | 110 | 70 | [5 empty] | 6 | 35 | 35 | 38 | 50 | 50 | 35 | 35 |  | 35 | 50 | 50 | 50 | 50 | 35 | 35 | 1157952
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | [5 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 55 |  | 100 | 113 | 113 | 113 | 113 | 55 | 55 | 1455840
173 | Rangpur 20 MW GTPP | [25 empty] | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 107 | 107 | 107 | 107 | 50 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 56 | 70 | 70 | 1246396
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 1 | [8 empty] | 14952
178 | Energypac Power Venture Thakurgaon Ltd. | 75 | 72 | [8 empty] | 10 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 57 | 109 | 113 | 114 | 114 | 114 | 114 | 1060224
| Intraco Solar 30 MW | [5 empty] | 0 | 0 | 1 | 2 | 2 | 3 | 7 | 8 | 14 | 17 | 15 | 10 | 3 |  | 0 | [6 empty] | 79537
| Adani Power Jharkhanda Ltd | 619 | 619 | 620 | 613 | 610 | 611 | 611 | 611 | 610 | 610 | 611 | 613 | 614 | 620 | 620 | 619 | 622 | 621 |  | 620 | 620 | 620 | 622 | 621 | 622 | 622 | 14847273
178 | Teesta Solar Limited | [6 empty] | 6 | 14 | 67 | 7 | 11 | 53 | 45 | 83 | 64 | 53 | 49 | 28 |  | 1 | [6 empty] | 471280
|  | 4279 | 4140 | 3748 | 3719 | 3654 | 3458 | 3516 | 3565 | 3716 | 3694 | 3777 | 4017 | 4204 | 4259 | 4362 | 4382 | 4231 | 3914 |  | 4224 | 4804 | 4891 | 4751 | 4775 | 5008 | 4982 | 101243257
|  | 11907 | 11571 | 11085 | 10966 | 10627 | 10036 | 9961 | 10043 | 10251 | 10367 | 10615 | 11051 | 11406 | 11535 | 11637 | 11519 | 10974 | 10543 | 0 | 11601 | 13242 | 13208 | 13402 | 13449 | 13474 | 13305 | 277193891