## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-07-12 | Wednesday
|  | Date (day): | 2023-07-12 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13386.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15429 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-07-11 | 2023-07-12 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 120 | 120 | 120 |  |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 170 | 170 | 170 | 170
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 401 | 401 | 380 | 380 | 32 |  | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 330 | 301 | 280 | 280 | 80 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 400 | 370 | 370
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 41 | 74 | 50 | 74 | 26 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 299 | 291 | 300 | 300 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 80 | 80 | 80 | 80 |  | 22 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 11 | 22 | 22 | 22 |  |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  | 3 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 50 | 58 | 58 | 75 | 25 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 331 | 315 | 230 | 230 | 105 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 48 | 101 | 33 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 54 | 0
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 82 | 132 | 82 | 130 | 19 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 40 | 38 | 42 | 42 |  | 38 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 18 | 18 | 24 | 24 |  |  | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 25 | 8 | 25 | 27 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 265 | 292 | 115 | 293 |  | 7 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 245 | 295 | 300 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
33 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
34 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 132 | 132 | 149 | 149
35 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 88 | 88 | 88 |  | 17 | Engine problem
36 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 53 | 72 | 54 | 72 | 32 |  | Fuel shortage
37 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 162 | 72 | 162
38 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 28 | 0 | 30 | 0
39 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 34 | 17 | 35 | 20 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6163 | 5822 | 3537 | 3884 | 3260 | 3786 | 840 | 855
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 105 | 108 | 110 | 110 | 70 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
41 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 17 | 8 | 17 |  | 8 | Engine problem
42 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 15 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 50 | 6 | 50
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 60 | 60 | 60 | 60 | 170 |  | Low Water Level
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 225 | 225 | 225
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 68 | 68 | 51 | 68 | 37 |  | Fuel shortage
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 32 | 48 | 32 | 70 | 28 |  | Fuel shortage
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 32 | 34 | 34 | 34 | 68 |  | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 58 | 70 | 58 | 80 | 20 |  | Fuel shortage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 50 | 87 | 50 | 88 | 12 |  | Fuel shortage
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 10 | 10 | 11 | 11 | 11 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 28 | 2 | 25
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 10 | 30 | 12 | 30 | 78 |  | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 88 | 280 | 88 | 280
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 35 | 17 | 17 | 37 |  | Fuel shortage
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 51 | 51 | 51 | 51 | 59 |  | Fuel shortage
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 76 | 50 | 75 | 25 |  | Fuel shortage
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 34 | 107 | 34 | 107 | 9 |  | Fuel shortage
60 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 53 | 160 | 54 | 163
| SS Power I |  | Coal | SS Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 0 | 11 | 15 | 10 |  |  | On test.
| Chattogram area Total |  |  |  |  | 2605 | 2545 | 971 | 1555 | 993 | 1571 | 624 | 338
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 206 | 211 | 200 | 200 | 21 |  | Gas shortage
62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 310 | 310 | 320 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint
64 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 325 | 317 | 350 | 350 | 50
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 43 | 45 | 45 | 45
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 55 | 8 | 8 | 8 | 187 |  | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
69 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 5 | 135 | 5 | 150
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 30 | 45 | 44 | 45 |  | 7 | Machine problem
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
72 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 51 | 104 | 50 | 120 | 80 |  | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 20 | 20 | 20
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 148 | 154 | 129 | 160
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 34 | 43 | 43 | 43 | 9 |  | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 20 | 20 | 20 |  | 5 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Contract Expired
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 106 | 52 | 106
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 66 | 9 | 76 | 37 |  | Fuel shortage
81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 57 | 115 | 55 | 115 | 0
| Cumilla Area Total |  |  |  |  | 3159 | 3096 | 1435 | 1802 | 1443 | 1881 | 384 | 580
83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 10 | 30 | 25 | 30 | 172 |  | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 19 | 18 | 18 |  | 4 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 69 | 108 | 78 | 105 | 95 |  | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 85 | 20 | 85 | 30 |  | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 13 | 0 | 50 | 0
90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 | 10 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 142 | 254 | 204.6 | 250 | 172 | 4
91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 39 | 39 | 39 | 39 |  | 51 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 112 | 112 |  | 51 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 42 | 45 | 45 | 45
96 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 47 | 47 | 44 | 44
97 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5
98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 60 | 60 | 60
99 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 84 | 86 | 86
100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 204 | 207 | 204 | 204 |  | 27 | Machine problem
102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 17 | 18
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
103 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 24 | 24
104 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 300 | 300 | 300 |  |  | FGMO
105 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 80 | 366 | 400 | 400 |  |  | FGMO
106 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
107 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 350 | 364 | 376 | 380
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1420 | 1723 | 1765 | 1770 | 0 | 586
108 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 910 | 814 | 930 | 930
109 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 31 | 95 | 80 | 95 |  | 20 | Engine problem
110 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 10 | 25 | 20 | 33 |  | 21 | Engine problem
111 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 205 | 150 | 225
112 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 30 | 60 | 36 | 70 |  | 39 | Engine problem
113 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 100 | 130 | 240 | 240 | 170 |  | Gas shortage
114 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 24 | 8 | 40
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
115 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 36 | 36 | 35 | 35 | 70 |  | Fuel shortage
116 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 15 | 67 | 15 | 68 | 37 |  | Fuel shortage
117 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 44 | 0 | 100 | 0
118 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 220 | 220 | 180 | 200 | 200 | 200 |  |  | On test.
119 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 365 | 374 | 370 | 370 |  | 247 | Unit-2 Under maint
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3125 | 3121 | 1721 | 2030 | 2184 | 2306 | 293 | 327
120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 83 | 98 | 100 | 100 | 10
121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 23 | 32 | 25 | 27 |  | 13
122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 136 | 136 | 135 | 135 |  | 59 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 622 | 622 | 622 | 622 |  | 622 | Unit-2 Under maint
124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 226 | 220 | 220 | 220
125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 150 | 17 | 150
126 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 | 307 |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1107 | 1258 | 1119 | 1254 | 317 | 694
127 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
128 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 35 | 0 | 35 | 17 |  | Fuel shortage
129 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 0 |  | 71 | Engine problem
130 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 28 | 21 | 28 | 28
131 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 50 | 42 | 50
132 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 21 | 26 | 22 | 27 |  | 23 | Engine problem
133 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Under maint
134 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 121 | 0 | 0 | 0 | 220 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 118 | 166 | 170 | 170 | 50 |  | Gas shortage
136 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 241 | 416 | 380 | 400 | 14 |  | Gas shortage
137 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 25 | 35 | 35 | 35 | 15 |  | Fuel shortage
138 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 0 | 8 | 8 |  | 3 | Engine problem
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 8 | 44 |  | Fuel shortage
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 92 | 0 | 90 | 14 |  | Fuel shortage
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 200 | 200 | 150 | 200
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 50 | 35 | 50 | 63 |  | Fuel shortage
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 55 | 35 | 55 | 58 |  | Fuel shortage
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 748*1 | 748 | 748 | 618 | 627 | 1050 | 1050
| Rajshahi Area Total |  |  |  |  | 2927 | 2905 | 1487 | 1781 | 1961 | 2206 | 666 | 307
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 220 | 220 | 220 | 220
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 27 | 70 | 34 | 70 | 43 |  | Fuel shortage
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 36 | 114 | 35 | 115
153 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 6 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 64 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 358 | 404 | 457 | 405 | 168 | 85
| Total |  |  |  |  | 24263 | 23545 | 12178 | 14691 | 13386.6 | 15429 | 3464 | 3776
A. |  | 2023-07-11 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 14691 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 11487 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14921 | MW
3 | Day peak Generation : |  |  | 12178 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14322.15 | MW
4 | Evening peak Generation : |  |  | 14691 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 220 | MW
5 | Total Energy Generation : |  | 301.3611 | MKWHr | By Solar | 1.4543 | MKWHr
| By Gas : | 148.6509 | MKWHr |  | By Oil: | 79.8452 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 44.8577 | MKWHr |  | By Hydro: | 1.4104 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.13056 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3464 | MW | Dhaka | 4899.35 | 4887.35 |  | 12 |  | 18:00 |  | 915.845
|  |  | For Plants S/D or M/C prob = |  |  | 3776 | MW | Chittagong | 1439 | 1439 |  | 0 |  | 19:00 |  | 774.505
|  |  | Total = |  |  | 7240 | MW | Khulna | 1839 | 1839 |  | 0 |  | 19:30 |  | 659.905
7 | Total Gas Supplied : |  |  | 1071.79 | MMCFD |  |  | Rajshahi | 1554.2 | 1554.2 |  | 0 |  | 20:00 |  | 253.075
8 | Fuel Cost : | i) Gas : | Taka | 162169710.26 | ii) Oil : | Taka | 1043787068.48 | Comilla | 1403 | 1403 |  | 0 |  | 21:00 |  | 220
|  | iii) Coal : | Taka | 169677212 | Total | Taka | 1375633990.74 | Mymensingh | 1192 | 1095 |  | 97 |  | 22:00 |  | 311.33
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 586 | 586 |  | 0 |  | 23:00 |  | 822.255
| ii) During Peak Demand : |  |  | 270 | MW (E to W) at | 21:00 | hrs | Barisal | 462.6 | 462.6 |  | 0 |  | 24:00 |  | 1313.125
| iii) Maximum : |  |  | 46 | MW at | 7:00 | hrs | Rangpur | 947 | 836 |  | 111
10 | Maximum Temperature in Dhaka was |  |  |  | 33.4° C |  |  | Total | 14322.15 | 14102.15 |  | 220
B. |  | 2023-07-12 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 33.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 15000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15429 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 13200 | MW
4 | Reserve(Generation end) |  |  |  | 429 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 307.6997 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11475 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.6596 | MKWHr. | ii) HVDC Flow at Peak Time |  | 814 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.3523 | MKWHr. | iii) Maximum HVDC Flow : |  | 910 | MW at | 6:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 75.31 |  | (b) Today: | 75.32 |  | (c) Rule Curve: |  | 85.6
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-07-11 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 401 | 327 |  | 0 | 420 | 314 | 33 | 74 | 55 | 326 | 0 | 32 | 42 | 32 | 82 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 14 | 25 | 21 | 8 | 0 | 60 | 0 | 105 | 0 | 8 | 223 | 0 | 0 | 0 |  | 12 | 66 | 34 | 58 | 0 | 6 | 11 | 34 | 0 | 0 | 0 | 285 | 0 | 209 | 55 | 0 | 45 | 0 | 0 | 43 | 0 | 36 | 43 | 20 | 8 | 33 | 20 | 134 | 32 | 0 | 18 | 0 | 43 | 39 | 45 | 47 | 112 | 0 | 55 | 86 | 0 | 207 | 17 | 0 | 10 | 320 | 24 | 5 | 0 | 275 | 259 | 0 | 68 | 0 | 117 | 0 | 50 | 18 | 5 | 280 | 19 | 88 | 57 | 0 | 86 | 17 | 51 | 70 | 9 | 50 | 354 | 36 | 0 | 17 | 17 | 0 | 17 | 0 | 95 | 17 | 293 | 17 | 0 | 0 | 13 |  | 908 | 0 | 105 | 0 | 16 | 150 | 0 | 0 | 15 | 45 | 8 | 138 | 35 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 26 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 125 | 0 | 314 | 36 | 200 | 35 | 15 | 34 | 0 | 0 | 35 | 622 | 226 | 0 | 17 | 0 | 0 | 70 | 200 | 0 | 374 | 0 | 0 | 619 | 0 | 0 |  | 7540 | 4865 | 12405 | 3965 | 908 | 2388 | 459 | 1972 | 1835 | 60 | 350 | 321 | 134 | 0 | 13 | 1236.725 | 75.3
2:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 400 | 346 |  | 0 | 410 | 313 | 42 | 80 | 55 | 327 | 0 | 32 | 42 | 32 | 82 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 22 | 25 | 21 | 8 | 0 | 60 | 0 | 106 | 0 | 8 | 224 | 0 | 0 | 0 |  | 12 | 33 | 34 | 58 | 0 | 6 | 11 | 34 | 0 | 0 | 0 | 280 | 0 | 210 | 55 | 0 | 45 | 0 | 0 | 43 | 0 | 38 | 43 | 20 | 8 | 33 | 20 | 136 | 32 | 0 | 18 | 0 | 43 | 39 | 45 | 47 | 112 | 0 | 55 | 86 | 0 | 207 | 17 | 0 | 10 | 310 | 24 | 5 | 0 | 288 | 242 | 0 | 68 | 0 | 125 | 0 | 50 | 17 | 6 | 280 | 19 | 88 | 55 | 0 | 87 | 17 | 51 | 17 | 9 | 50 | 360 | 36 | 0 | 17 | 17 | 0 | 17 | 0 | 94 | 17 | 292 | 17 | 0 | 0 | 4 |  | 909 | 0 | 105 | 0 | 16 | 150 | 0 | 0 | 11 | 45 | 8 | 138 | 34 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 21 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 126 | 0 | 0 | 0 | 125 | 0 | 319 | 36 | 173 | 35 | 15 | 34 | 0 | 0 | 35 | 622 | 226 | 0 | 17 | 0 | 0 | 0 | 200 | 0 | 371 | 0 | 0 | 621 | 0 | 0 |  | 7474 | 4764 | 12238 | 3977 | 909 | 2390 | 415 | 1882 | 1834 | 60 | 350 | 281 | 136 | 0 | 4 | 1205.21 | 75.3
3:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 401 | 343 |  | 0 | 400 | 312 | 42 | 80 | 55 | 327 | 0 | 30 | 42 | 32 | 82 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 22 | 25 | 21 | 8 | 0 | 60 | 0 | 107 | 0 | 8 | 225 | 0 | 0 | 0 |  | 12 | 33 | 34 | 58 | 0 | 6 | 11 | 34 | 0 | 0 | 0 | 280 | 0 | 210 | 55 | 0 | 46 | 0 | 0 | 43 | 0 | 38 | 43 | 20 | 8 | 33 | 20 | 140 | 32 | 0 | 18 | 0 | 43 | 39 | 45 | 47 | 112 | 0 | 59 | 86 | 0 | 207 | 17 | 0 | 10 | 305 | 24 | 5 | 0 | 293 | 200 | 0 | 68 | 0 | 132 | 0 | 50 | 17 | 6 | 280 | 19 | 88 | 51 | 0 | 87 | 17 | 51 | 17 | 9 | 50 | 360 | 50 | 0 | 17 | 17 | 0 | 17 | 0 | 54 | 17 | 292 | 17 | 0 | 0 | 4 |  | 909 | 0 | 105 | 0 | 16 | 150 | 0 | 0 | 11 | 45 | 0 | 138 | 33 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 21 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 124 | 0 | 0 | 0 | 125 | 0 | 321 | 36 | 150 | 35 | 15 | 34 | 0 | 0 | 35 | 622 | 226 | 0 | 17 | 0 | 0 | 0 | 200 | 0 | 374 | 0 | 0 | 621 | 0 | 0 |  | 7405 | 4735 | 12140 | 3981 | 909 | 2372 | 350 | 1856 | 1837 | 60 | 350 | 281 | 140 | 0 | 4 | 1155.55 | 75.3
4:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 400 | 332 |  | 0 | 410 | 313 | 42 | 80 | 55 | 327 | 0 | 30 | 42 | 32 | 82 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 22 | 25 | 22 | 8 | 0 | 60 | 0 | 105 | 0 | 8 | 226 | 0 | 0 | 0 |  | 12 | 33 | 34 | 58 | 0 | 6 | 11 | 35 | 0 | 0 | 0 | 280 | 0 | 210 | 55 | 0 | 46 | 0 | 0 | 43 | 0 | 38 | 43 | 20 | 8 | 33 | 20 | 144 | 31 | 0 | 18 | 0 | 43 | 39 | 45 | 47 | 112 | 0 | 59 | 86 | 0 | 207 | 17 | 0 | 10 | 300 | 24 | 5 | 0 | 296 | 150 | 0 | 68 | 0 | 133 | 0 | 50 | 17 | 5 | 280 | 19 | 88 | 51 | 0 | 88 | 17 | 51 | 17 | 9 | 50 | 360 | 54 | 0 | 17 | 17 | 0 | 17 | 0 | 35 | 17 | 292 | 17 | 0 | 0 | 11 |  | 909 | 0 | 105 | 0 | 16 | 145 | 0 | 0 | 11 | 45 | 0 | 138 | 31 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 21 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | 126 | 0 | 327 | 36 | 128 | 35 | 15 | 34 | 0 | 0 | 35 | 622 | 226 | 0 | 17 | 0 | 0 | 0 | 200 | 0 | 378 | 0 | 0 | 622 | 0 | 0 |  | 7350 | 4717 | 12067 | 3979 | 909 | 2372 | 278 | 1846 | 1842 | 60 | 345 | 281 | 144 | 0 | 11 | 1034.265 | 75.31
5:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 401 | 332 |  | 0 | 410 | 314 | 42 | 80 | 55 | 328 | 0 | 29 | 42 | 32 | 82 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 22 | 25 | 22 | 8 | 0 | 60 | 0 | 105 | 0 | 8 | 226 | 0 | 0 | 0 |  | 12 | 33 | 34 | 58 | 0 | 6 | 11 | 36 | 0 | 0 | 0 | 280 | 0 | 210 | 55 | 0 | 46 | 0 | 0 | 43 | 0 | 38 | 43 | 20 | 8 | 33 | 20 | 142 | 31 | 0 | 18 | 0 | 43 | 39 | 45 | 47 | 112 | 0 | 59 | 86 | 0 | 206 | 17 | 0 | 10 | 305 | 24 | 5 | 0 | 293 | 150 | 0 | 68 | 0 | 133 | 0 | 50 | 17 | 6 | 240 | 19 | 88 | 51 | 0 | 88 | 17 | 51 | 17 | 9 | 50 | 360 | 54 | 0 | 17 | 17 | 0 | 17 | 0 | 33 | 17 | 293 | 17 | 0 | 0 | 0 |  | 908 | 0 | 110 | 0 | 16 | 145 | 0 | 0 | 11 | 45 | 0 | 138 | 31 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 21 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | 126 | 0 | 327 | 36 | 100 | 35 | 15 | 34 | 0 | 0 | 35 | 622 | 226 | 0 | 17 | 0 | 0 | 0 | 200 | 0 | 376 | 0 | 0 | 622 | 0 | 0 |  | 7301 | 4691 | 11992 | 3945 | 908 | 2379 | 250 | 1842 | 1840 | 60 | 345 | 281 | 142 | 0 | 0 | 914.89 | 75.31
6:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 400 | 332 |  | 0 | 410 | 315 | 43 | 80 | 55 | 327 | 0 | 29 | 42 | 32 | 82 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 22 | 25 | 22 | 8 | 0 | 60 | 0 | 108 | 0 | 8 | 228 | 0 | 0 | 0 |  | 12 | 33 | 34 | 58 | 0 | 6 | 11 | 36 | 0 | 0 | 0 | 280 | 0 | 210 | 55 | 0 | 46 | 0 | 0 | 43 | 0 | 38 | 43 | 20 | 8 | 33 | 20 | 134 | 31 | 0 | 18 | 0 | 43 | 39 | 45 | 47 | 112 | 0 | 61 | 86 | 0 | 206 | 17 | 0 | 10 | 290 | 24 | 5 | 0 | 296 | 105 | 0 | 68 | 0 | 133 | 1 | 50 | 17 | 6 | 80 | 19 | 88 | 51 | 0 | 88 | 17 | 51 | 17 | 9 | 50 | 351 | 36 | 1 | 17 | 17 | 0 | 17 | 2 | 36 | 17 | 292 | 17 | 0 | 0 | 0 |  | 910 | 0 | 110 | 0 | 16 | 145 | 0 | 0 | 11 | 45 | 0 | 138 | 28 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 21 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 211 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | 126 | 0 | 328 | 36 | 100 | 35 | 15 | 34 | 0 | 0 | 35 | 622 | 226 | 0 | 17 | 0 | 4 | 0 | 200 | 0 | 376 | 0 | 0 | 626 | 2 | 0 |  | 7062 | 4692 | 11754 | 3780 | 910 | 2363 | 205 | 1831 | 1835 | 60 | 345 | 281 | 134 | 10 | 0 | 521.43 | 75.31
7:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 400 | 332 |  | 0 | 420 | 305 | 42 | 80 | 45 | 324 | 0 | 34 | 42 | 32 | 82 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 21 | 25 | 18 | 8 | 0 | 60 | 0 | 109 | 0 | 8 | 226 | 0 | 0 | 0 |  | 12 | 33 | 34 | 58 | 0 | 6 | 10 | 32 | 0 | 0 | 0 | 310 | 0 | 211 | 55 | 0 | 43 | 0 | 0 | 43 | 0 | 38 | 43 | 20 | 8 | 33 | 20 | 128 | 31 | 0 | 18 | 0 | 43 | 39 | 45 | 47 | 112 | 0 | 60 | 86 | 0 | 206 | 17 | 0 | 10 | 300 | 24 | 5 | 0 | 293 | 105 | 0 | 68 | 0 | 133 | 2 | 50 | 17 | 5 | 80 | 19 | 88 | 51 | 1 | 88 | 17 | 51 | 17 | 9 | 50 | 355 | 36 | 12 | 17 | 17 | 0 | 17 | 6 | 36 | 17 | 322 | 17 | 0 | 0 | 6 |  | 909 | 0 | 110 | 0 | 16 | 10 | 0 | 0 | 11 | 20 | 0 | 138 | 25 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 21 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | 126 | 0 | 315 | 36 | 106 | 35 | 15 | 34 | 0 | 0 | 35 | 622 | 226 | 0 | 17 | 0 | 14 | 0 | 200 | 0 | 374 | 2 | 0 | 625 | 32 | 0 |  | 7126 | 4549 | 11675 | 3836 | 909 | 2353 | 211 | 1816 | 1821 | 60 | 210 | 256 | 128 | 69 | 6 | 201.505 | 75.32
8:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 401 | 327 |  | 0 | 420 | 307 | 42 | 80 | 55 | 321 | 0 | 36 | 50 | 32 | 82 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 18 | 25 | 18 | 8 | 0 | 60 | 0 | 107 | 0 | 8 | 226 | 0 | 0 | 0 |  | 12 | 32 | 34 | 58 | 0 | 6 | 10 | 8 | 0 | 0 | 0 | 320 | 0 | 212 | 55 | 0 | 45 | 0 | 0 | 43 | 0 | 38 | 43 | 20 | 8 | 33 | 20 | 128 | 12 | 0 | 18 | 0 | 43 | 39 | 45 | 47 | 112 | 0 | 60 | 86 | 0 | 207 | 17 | 0 | 10 | 300 | 24 | 5 | 0 | 293 | 108 | 0 | 68 | 0 | 133 | 10 | 50 | 17 | 6 | 80 | 19 | 88 | 51 | 2 | 88 | 17 | 51 | 17 | 9 | 50 | 355 | 50 | 20 | 17 | 17 | 0 | 17 | 3 | 36 | 17 | 331 | 17 | 0 | 0 | 6 |  | 909 | 0 | 105 | 0 | 16 | 0 | 0 | 0 | 11 | 20 | 0 | 134 | 23 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 21 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 124 | 0 | 0 | 0 | 124 | 0 | 304 | 36 | 150 | 35 | 15 | 34 | 0 | 0 | 35 | 622 | 226 | 0 | 17 | 1 | 17 | 0 | 200 | 0 | 380 | 6 | 0 | 607 | 30 | 0 |  | 7147 | 4554 | 11701 | 3825 | 909 | 2313 | 258 | 1849 | 1809 | 60 | 200 | 255 | 128 | 89 | 6 | 212.01 | 75.32
9:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 401 | 321 |  | 0 | 420 | 308 | 42 | 80 | 55 | 322 | 0 | 35 | 50 | 32 | 82 | 23 | 0 | 0 | 0 | 0 | 17 | 17 | 19 | 20 | 20 | 25 | 18 | 8 | 0 | 60 | 0 | 107 | 0 | 8 | 223 | 0 | 0 | 0 |  | 12 | 32 | 34 | 58 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 330 | 0 | 207 | 55 | 0 | 44 | 0 | 0 | 43 | 0 | 37 | 43 | 20 | 8 | 29 | 20 | 120 | 10 | 0 | 18 | 1 | 43 | 39 | 45 | 47 | 112 | 0 | 60 | 86 | 0 | 207 | 17 | 0 | 10 | 310 | 24 | 5 | 0 | 293 | 0 | 0 | 68 | 0 | 133 | 5 | 50 | 17 | 5 | 80 | 19 | 88 | 51 | 4 | 88 | 17 | 51 | 17 | 9 | 50 | 358 | 54 | 30 | 17 | 17 | 0 | 17 | 17 | 46 | 17 | 369 | 17 | 0 | 0 | 8 |  | 910 | 0 | 105 | 0 | 16 | 0 | 0 | 0 | 11 | 20 | 0 | 134 | 20 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 21 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 121 | 0 | 280 | 36 | 0 | 35 | 15 | 34 | 0 | 1 | 35 | 622 | 226 | 0 | 17 | 1 | 37 | 0 | 75 | 0 | 375 | 7 | 0 | 615 | 76 | 0 |  | 7149 | 4338 | 11487 | 3857 | 910 | 2285 | 0 | 1907 | 1832 | 60 | 75 | 254 | 120 | 179 | 8 | 871.915 | 75.32
10:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 402 | 322 |  | 0 | 420 | 305 | 39 | 80 | 55 | 322 | 0 | 29 | 50 | 32 | 82 | 22 | 0 | 0 | 0 | 0 | 35 | 35 | 19 | 20 | 20 | 25 | 18 | 8 | 0 | 60 | 0 | 110 | 0 | 8 | 221 | 0 | 0 | 0 |  | 12 | 32 | 34 | 58 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 335 | 0 | 207 | 55 | 0 | 44 | 0 | 0 | 43 | 0 | 37 | 43 | 18 | 10 | 23 | 20 | 130 | 8 | 0 | 18 | 1 | 43 | 39 | 42 | 44 | 112 | 0 | 59 | 84 | 0 | 204 | 17 | 0 | 10 | 310 | 16 | 5 | 0 | 291 | 20 | 0 | 68 | 0 | 133 | 10 | 50 | 37 | 5 | 80 | 19 | 88 | 51 | 4 | 88 | 17 | 51 | 17 | 9 | 50 | 348 | 53 | 20 | 17 | 20 | 0 | 17 | 32 | 57 | 17 | 373 | 23 | 0 | 0 | 4 |  | 909 | 0 | 100 | 0 | 16 | 0 | 0 | 0 | 11 | 20 | 0 | 132 | 21 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 21 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 120 | 0 | 258 | 36 | 0 | 35 | 15 | 34 | 0 | 2 | 35 | 600 | 226 | 0 | 17 | 2 | 75 | 0 | 200 | 0 | 374 | 27 | 0 | 621 | 74 | 0 |  | 7219 | 4475 | 11694 | 3825 | 909 | 2254 | 20 | 1970 | 1815 | 60 | 200 | 260 | 130 | 247 | 4 | 1056.23 | 75.32
11:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 402 | 333 |  | 0 | 430 | 305 | 41 | 80 | 55 | 327 | 0 | 0 | 50 | 48 | 82 | 22 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 20 | 20 | 25 | 18 | 8 | 0 | 60 | 0 | 105 | 0 | 8 | 223 | 0 | 0 | 0 |  | 12 | 32 | 32 | 58 | 10 | 6 | 10 | 2 | 0 | 0 | 0 | 305 | 0 | 209 | 55 | 0 | 42 | 0 | 0 | 43 | 0 | 36 | 43 | 18 | 10 | 29 | 20 | 136 | 10 | 0 | 18 | 1 | 43 | 38 | 42 | 47 | 112 | 0 | 60 | 86 | 0 | 204 | 17 | 0 | 9 | 305 | 16 | 5 | 0 | 260 | 53 | 0 | 68 | 0 | 133 | 12 | 50 | 51 | 6 | 80 | 19 | 88 | 68 | 3 | 88 | 17 | 51 | 17 | 9 | 50 | 366 | 53 | 23 | 35 | 34 | 0 | 17 | 36 | 57 | 17 | 322 | 53 | 0 | 0 | 3 |  | 909 | 0 | 100 | 0 | 32 | 0 | 0 | 0 | 11 | 20 | 0 | 132 | 21 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 21 | 0 | 25 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 118 | 0 | 253 | 36 | 67 | 35 | 15 | 34 | 0 | 2 | 35 | 600 | 226 | 0 | 17 | 2 | 38 | 36 | 180 | 0 | 371 | 11 | 0 | 615 | 134 | 0 |  | 7308 | 4589 | 11897 | 3740 | 909 | 2269 | 120 | 2100 | 1806 | 60 | 180 | 312 | 136 | 262 | 3 | 1196.615 | 75.32
12:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 401 | 330 |  | 0 | 450 | 299 | 41 | 80 | 55 | 331 | 0 | 0 | 50 | 48 | 82 | 11 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 20 | 20 | 25 | 18 | 8 | 0 | 60 | 0 | 105 | 0 | 8 | 219 | 0 | 0 | 0 |  | 12 | 32 | 32 | 58 | 10 | 6 | 10 | 2 | 0 | 0 | 0 | 320 | 0 | 206 | 55 | 0 | 43 | 0 | 0 | 43 | 0 | 30 | 34 | 18 | 10 | 33 | 14 | 148 | 10 | 0 | 18 | 1 | 43 | 39 | 42 | 47 | 112 | 0 | 59 | 86 | 0 | 204 | 17 | 0 | 10 | 310 | 16 | 5 | 0 | 265 | 245 | 0 | 69 | 0 | 132 | 15 | 50 | 51 | 5 | 80 | 19 | 88 | 68 | 3 | 88 | 17 | 51 | 17 | 9 | 50 | 350 | 53 | 13 | 54 | 34 | 0 | 17 | 28 | 57 | 17 | 325 | 53 | 0 | 0 | 0 |  | 910 | 0 | 100 | 0 | 31 | 0 | 0 | 0 | 10 | 30 | 0 | 136 | 23 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 21 | 0 | 25 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 118 | 0 | 241 | 36 | 200 | 35 | 15 | 27 | 0 | 5 | 35 | 622 | 226 | 0 | 17 | 3 | 44 | 36 | 180 | 0 | 365 | 6 | 0 | 618 | 64 | 0 |  | 7505 | 4673 | 12178 | 3741 | 910 | 2276 | 445 | 2096 | 1825 | 60 | 180 | 315 | 148 | 182 | 0 | 1167.01 | 75.32
13:00 | 0 | 0 | 105 | 170 | 0 | 0 | 0 | 409 | 331 |  | 0 | 450 | 312 | 43 | 80 | 55 | 335 | 0 | 0 | 50 | 48 | 82 | 11 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 20 | 20 | 25 | 18 | 8 | 0 | 30 | 30 | 100 | 0 | 8 | 220 | 0 | 0 | 0 |  | 12 | 32 | 32 | 58 | 13 | 6 | 10 | 6 | 0 | 0 | 0 | 305 | 0 | 207 | 55 | 0 | 41 | 0 | 0 | 43 | 0 | 26 | 43 | 18 | 10 | 32 | 14 | 152 | 10 | 0 | 18 | 1 | 43 | 38 | 42 | 47 | 112 | 0 | 60 | 86 | 0 | 204 | 17 | 0 | 10 | 310 | 16 | 5 | 0 | 273 | 214 | 0 | 87 | 0 | 132 | 20 | 50 | 51 | 5 | 80 | 19 | 88 | 68 | 3 | 88 | 17 | 51 | 17 | 9 | 50 | 355 | 53 | 19 | 54 | 34 | 0 | 17 | 7 | 57 | 17 | 321 | 53 | 0 | 0 | 3 |  | 910 | 0 | 95 | 0 | 31 | 0 | 0 | 0 | 11 | 32 | 0 | 136 | 24 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 21 | 0 | 30 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 117 | 0 | 222 | 36 | 200 | 35 | 15 | 27 | 0 | 4 | 35 | 622 | 226 | 0 | 17 | 5 | 21 | 36 | 180 | 0 | 374 | 5 | 0 | 615 | 63 | 0 |  | 7493 | 4638 | 12131 | 3702 | 910 | 2276 | 414 | 2136 | 1831 | 60 | 180 | 319 | 152 | 148 | 3 | 1116.395 | 75.32
14:00 | 0 | 0 | 120 | 170 | 0 | 0 | 0 | 410 | 330 |  | 0 | 450 | 306 | 49 | 80 | 55 | 322 | 0 | 0 | 50 | 48 | 82 | 11 | 0 | 0 | 0 | 17 | 35 | 35 | 17 | 20 | 20 | 25 | 18 | 8 | 0 | 30 | 30 | 105 | 0 | 8 | 220 | 0 | 0 | 0 |  | 12 | 32 | 30 | 58 | 15 | 7 | 10 | 4 | 0 | 0 | 0 | 305 | 0 | 203 | 55 | 0 | 41 | 0 | 0 | 43 | 0 | 24 | 43 | 20 | 10 | 32 | 14 | 132 | 10 | 0 | 19 | 1 | 43 | 39 | 42 | 47 | 112 | 0 | 60 | 86 | 0 | 204 | 17 | 0 | 10 | 295 | 16 | 5 | 0 | 278 | 55 | 0 | 88 | 0 | 132 | 18 | 50 | 51 | 6 | 115 | 19 | 88 | 68 | 2 | 88 | 17 | 51 | 17 | 9 | 50 | 350 | 53 | 1 | 54 | 43 | 0 | 17 | 17 | 57 | 17 | 322 | 53 | 0 | 0 | 11 |  | 909 | 0 | 90 | 0 | 32 | 10 | 0 | 0 | 11 | 22 | 0 | 136 | 24 | 83 | 0 | 0 | 0 | 35 | 0 | 0 | 28 | 34 | 21 | 0 | 35 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 119 | 0 | 0 | 0 | 115 | 0 | 220 | 36 | 180 | 35 | 15 | 34 | 0 | 5 | 35 | 622 | 222 | 0 | 17 | 1 | 37 | 36 | 180 | 0 | 374 | 10 | 0 | 616 | 1 | 0 |  | 7364 | 4608 | 11972 | 3750 | 909 | 2246 | 235 | 2169 | 1832 | 60 | 190 | 345 | 132 | 93 | 11 | 1172.74 | 75.32
15:00 | 0 | 0 | 120 | 170 | 0 | 0 | 0 | 403 | 322 |  | 0 | 450 | 283 | 50 | 80 | 55 | 319 | 0 | 0 | 50 | 48 | 82 | 11 | 0 | 0 | 0 | 17 | 35 | 35 | 17 | 20 | 20 | 25 | 18 | 8 | 0 | 30 | 30 | 102 | 0 | 8 | 220 | 0 | 0 | 0 |  | 12 | 16 | 32 | 58 | 9 | 28 | 10 | 2 | 0 | 0 | 0 | 315 | 0 | 157 | 55 | 0 | 42 | 0 | 0 | 43 | 0 | 35 | 43 | 20 | 10 | 32 | 20 | 146 | 10 | 0 | 19 | 1 | 43 | 39 | 42 | 47 | 112 | 0 | 60 | 86 | 0 | 204 | 17 | 0 | 10 | 310 | 24 | 5 | 0 | 275 | 208 | 0 | 88 | 0 | 132 | 6 | 50 | 51 | 5 | 244 | 19 | 88 | 68 | 2 | 88 | 17 | 51 | 17 | 9 | 50 | 350 | 53 | 8 | 54 | 51 | 0 | 17 | 26 | 61 | 17 | 295 | 53 | 0 | 0 | 5 |  | 910 | 0 | 80 | 0 | 32 | 20 | 0 | 0 | 11 | 22 | 0 | 133 | 25 | 83 | 0 | 0 | 0 | 35 | 0 | 0 | 28 | 34 | 21 | 0 | 35 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 119 | 0 | 0 | 0 | 117 | 0 | 219 | 36 | 180 | 35 | 15 | 34 | 0 | 4 | 35 | 622 | 223 | 0 | 17 | 1 | 36 | 36 | 180 | 0 | 374 | 10 | 0 | 612 | 3 | 0 |  | 7600 | 4605 | 12205 | 3807 | 910 | 2229 | 388 | 2193 | 1828 | 60 | 200 | 342 | 146 | 97 | 5 | 1284.475 | 75.32
16:00 | 0 | 0 | 120 | 170 | 0 | 0 | 0 | 403 | 322 |  | 0 | 430 | 281 | 65 | 80 | 55 | 320 | 0 | 0 | 50 | 48 | 82 | 12 | 0 | 0 | 0 | 35 | 35 | 55 | 17 | 20 | 20 | 25 | 18 | 8 | 0 | 30 | 30 | 102 | 0 | 8 | 220 | 0 | 0 | 0 |  | 12 | 16 | 32 | 58 | 9 | 33 | 10 | 2 | 0 | 0 | 0 | 305 | 0 | 154 | 6 | 0 | 42 | 0 | 0 | 43 | 0 | 35 | 43 | 20 | 10 | 32 | 20 | 128 | 12 | 0 | 19 | 1 | 43 | 39 | 42 | 47 | 112 | 0 | 60 | 86 | 0 | 204 | 16 | 0 | 10 | 305 | 24 | 5 | 0 | 292 | 0 | 0 | 78 | 0 | 131 | 8 | 50 | 51 | 5 | 312 | 19 | 88 | 68 | 2 | 102 | 17 | 51 | 17 | 8 | 50 | 350 | 53 | 2 | 72 | 51 | 0 | 17 | 17 | 75 | 17 | 292 | 36 | 0 | 0 | 8 |  | 909 | 0 | 80 | 0 | 32 | 20 | 0 | 0 | 12 | 23 | 0 | 130 | 24 | 83 | 0 | 0 | 0 | 35 | 0 | 0 | 21 | 34 | 24 | 0 | 35 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 117 | 0 | 221 | 36 | 0 | 50 | 15 | 34 | 0 | 4 | 55 | 622 | 220 | 0 | 17 | 0 | 47 | 36 | 180 | 0 | 374 | 0 | 0 | 618 | 8 | 0 |  | 7435 | 4464 | 11899 | 3859 | 909 | 2151 | 0 | 2331 | 1834 | 60 | 200 | 330 | 128 | 89 | 8 | 1433.455 | 75.32
17:00 | 0 | 0 | 120 | 170 | 0 | 0 | 0 | 403 | 302 |  | 0 | 400 | 272 | 67 | 80 | 55 | 322 | 0 | 0 | 50 | 48 | 82 | 22 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 20 | 20 | 25 | 18 | 8 | 0 | 30 | 30 | 105 | 0 | 13 | 222 | 0 | 0 | 0 |  | 12 | 20 | 32 | 46 | 11 | 42 | 10 | 13 | 0 | 0 | 0 | 280 | 0 | 184 | 6 | 0 | 42 | 0 | 0 | 43 | 0 | 35 | 43 | 20 | 10 | 32 | 20 | 138 | 18 | 0 | 19 | 0 | 43 | 39 | 42 | 47 | 80 | 0 | 60 | 84 | 0 | 204 | 17 | 0 | 10 | 290 | 24 | 5 | 0 | 292 | 0 | 0 | 78 | 0 | 131 | 3 | 50 | 51 | 5 | 349 | 19 | 88 | 68 | 1 | 88 | 17 | 51 | 17 | 9 | 50 | 350 | 53 | 1 | 72 | 51 | 0 | 17 | 10 | 76 | 29 | 292 | 53 | 0 | 0 | 8 |  | 910 | 0 | 80 | 0 | 32 | 40 | 0 | 0 | 18 | 23 | 0 | 130 | 22 | 94 | 0 | 0 | 0 | 35 | 0 | 0 | 28 | 34 | 24 | 0 | 35 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | 120 | 0 | 268 | 36 | 0 | 50 | 15 | 69 | 0 | 2 | 55 | 622 | 220 | 0 | 17 | 0 | 23 | 36 | 80 | 0 | 375 | 1 | 0 | 609 | 6 | 0 |  | 7428 | 4460 | 11888 | 3923 | 910 | 2099 | 0 | 2400 | 1826 | 60 | 120 | 357 | 138 | 47 | 8 | 1252.96 | 75.32
18:00 | 0 | 0 | 120 | 170 | 0 | 0 | 0 | 341 | 282 |  | 0 | 400 | 255 | 74 | 80 | 55 | 260 | 0 | 0 | 50 | 48 | 115 | 22 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 16 | 20 | 25 | 18 | 25 | 0 | 30 | 30 | 108 | 0 | 17 | 220 | 0 | 0 | 0 |  | 12 | 24 | 32 | 70 | 14 | 50 | 10 | 11 | 0 | 0 | 0 | 280 | 0 | 209 | 8 | 0 | 42 | 0 | 0 | 43 | 0 | 37 | 43 | 20 | 10 | 33 | 20 | 136 | 21 | 0 | 19 | 0 | 43 | 39 | 42 | 47 | 80 | 0 | 60 | 84 | 0 | 203 | 17 | 0 | 10 | 270 | 24 | 5 | 0 | 291 | 0 | 0 | 78 | 0 | 132 | 1 | 50 | 51 | 10 | 306 | 19 | 88 | 68 | 0 | 120 | 17 | 51 | 17 | 37 | 50 | 360 | 56 | 1 | 72 | 55 | 0 | 17 | 3 | 94 | 34 | 254 | 159 | 0 | 0 | 10 |  | 910 | 0 | 80 | 0 | 32 | 100 | 0 | 0 | 28 | 36 | 0 | 80 | 22 | 96 | 0 | 0 | 0 | 35 | 0 | 0 | 28 | 34 | 25 | 0 | 35 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 122 | 0 | 279 | 36 | 0 | 50 | 67 | 70 | 0 | 1 | 55 | 622 | 163 | 0 | 17 | 0 | 9 | 36 | 80 | 0 | 376 | 0 | 0 | 621 | 9 | 0 |  | 7494 | 4497 | 11991 | 3678 | 910 | 1996 | 0 | 2632 | 1839 | 60 | 180 | 526 | 136 | 24 | 10 | 915.845 | 75.32
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 120 | 170 | 0 | 0 | 0 | 327 | 330 |  | 0 | 340 | 300 | 72 | 60 | 55 | 260 | 0 | 0 | 58 | 92 | 132 | 21 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 16 | 20 | 25 | 18 | 25 | 0 | 30 | 30 | 108 | 0 | 17 | 225 | 0 | 0 | 0 |  | 12 | 32 | 34 | 70 | 22 | 50 | 10 | 20 | 0 | 0 | 0 | 300 | 0 | 208 | 8 | 0 | 43 | 0 | 0 | 43 | 0 | 37 | 43 | 20 | 10 | 33 | 20 | 164 | 23 | 0 | 19 | 0 | 43 | 39 | 44 | 47 | 80 | 0 | 61 | 84 | 0 | 204 | 17 | 0 | 10 | 270 | 24 | 5 | 0 | 292 | 24 | 0 | 96 | 0 | 132 | 0 | 60 | 78 | 60 | 316 | 75 | 88 | 68 | 0 | 274 | 17 | 51 | 52 | 65 | 76 | 354 | 70 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 34 | 298 | 160 | 0 | 0 | 12 |  | 910 | 0 | 105 | 0 | 89 | 150 | 0 | 0 | 29 | 64 | 16 | 135 | 29 | 98 | 0 | 0 | 0 | 35 | 0 | 61 | 28 | 42 | 21 | 8 | 35 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 0 | 371 | 36 | 2 | 50 | 67 | 70 | 0 | 0 | 55 | 622 | 220 | 0 | 150 | 0 | 0 | 97 | 80 | 0 | 375 | 0 | 0 | 625 | 0 | 0 |  | 8316 | 5023 | 13339 | 3723 | 910 | 2196 | 26 | 3536 | 1842 | 60 | 230 | 640 | 164 | 0 | 12 | 774.505 | 75.32
19:30 | 0 | 0 | 120 | 170 | 0 | 0 | 0 | 400 | 331 |  | 0 | 400 | 265 | 75 | 63 | 55 | 322 | 0 | 0 | 58 | 101 | 132 | 21 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 16 | 20 | 25 | 18 | 25 | 0 | 30 | 30 | 107 | 0 | 17 | 225 | 0 | 0 | 0 |  | 12 | 32 | 34 | 70 | 26 | 50 | 10 | 22 | 0 | 0 | 0 | 305 | 0 | 211 | 8 | 0 | 44 | 0 | 0 | 43 | 0 | 45 | 43 | 20 | 10 | 33 | 20 | 144 | 23 | 0 | 19 | 0 | 43 | 39 | 44 | 47 | 80 | 0 | 61 | 84 | 0 | 204 | 17 | 0 | 10 | 260 | 24 | 5 | 0 | 292 | 21 | 0 | 96 | 0 | 132 | 0 | 87 | 100 | 120 | 366 | 85 | 88 | 68 | 0 | 274 | 17 | 51 | 88 | 65 | 76 | 345 | 72 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 34 | 317 | 160 | 0 | 0 | 13 |  | 909 | 0 | 115 | 0 | 96 | 170 | 0 | 0 | 33 | 67 | 16 | 135 | 32 | 98 | 0 | 0 | 0 | 35 | 0 | 92 | 28 | 42 | 26 | 8 | 35 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 392 | 36 | 20 | 50 | 67 | 70 | 0 | 0 | 55 | 622 | 220 | 0 | 150 | 0 | 0 | 97 | 115 | 0 | 374 | 0 | 0 | 623 | 0 | 0 |  | 8719 | 5190 | 13909 | 3950 | 909 | 2238 | 41 | 3739 | 1839 | 60 | 285 | 691 | 144 | 0 | 13 | 659.905 | 0
20:00 | 0 | 0 | 120 | 170 | 0 | 0 | 0 | 397 | 333 |  | 0 | 400 | 308 | 73 | 66 | 55 | 327 | 0 | 0 | 58 | 101 | 132 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 16 | 22 | 25 | 18 | 25 | 0 | 30 | 30 | 108 | 0 | 17 | 217 | 0 | 0 | 0 |  | 12 | 36 | 34 | 70 | 27 | 50 | 10 | 25 | 0 | 0 | 0 | 335 | 0 | 209 | 8 | 0 | 45 | 0 | 0 | 43 | 0 | 44 | 43 | 20 | 10 | 33 | 20 | 152 | 23 | 0 | 19 | 0 | 43 | 39 | 45 | 47 | 112 | 0 | 60 | 84 | 0 | 207 | 17 | 0 | 10 | 290 | 24 | 5 | 0 | 292 | 125 | 0 | 98 | 0 | 132 | 0 | 87 | 103 | 115 | 408 | 85 | 88 | 68 | 0 | 280 | 22 | 51 | 88 | 66 | 76 | 354 | 72 | 0 | 144 | 107 | 0 | 17 | 0 | 115 | 34 | 330 | 160 | 0 | 0 | 14 |  | 815 | 0 | 125 | 0 | 95 | 205 | 0 | 0 | 27 | 68 | 24 | 135 | 32 | 98 | 0 | 0 | 0 | 35 | 0 | 92 | 28 | 50 | 26 | 8 | 35 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 400 | 36 | 22 | 50 | 67 | 70 | 0 | 0 | 55 | 622 | 220 | 0 | 150 | 0 | 0 | 114 | 200 | 0 | 374 | 0 | 0 | 622 | 0 | 0 |  | 9035 | 5257 | 14292 | 4047 | 815 | 2357 | 147 | 3768 | 1838 | 60 | 405 | 689 | 152 | 0 | 14 | 253.075 | 75.32
21:00 | 0 | 0 | 120 | 170 | 0 | 0 | 0 | 401 | 301 |  | 0 | 400 | 291 | 74 | 80 | 55 | 315 | 0 | 0 | 58 | 101 | 132 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 16 | 22 | 25 | 18 | 25 | 0 | 30 | 30 | 108 | 0 | 17 | 225 | 0 | 0 | 0 |  | 12 | 48 | 34 | 70 | 30 | 50 | 10 | 28 | 0 | 0 | 0 | 310 | 0 | 211 | 8 | 0 | 45 | 0 | 0 | 43 | 0 | 45 | 43 | 20 | 10 | 33 | 20 | 154 | 30 | 0 | 19 | 0 | 43 | 39 | 45 | 47 | 112 | 0 | 60 | 84 | 0 | 207 | 17 | 0 | 10 | 300 | 24 | 5 | 0 | 292 | 295 | 0 | 108 | 0 | 132 | 0 | 87 | 104 | 135 | 366 | 85 | 88 | 68 | 0 | 280 | 35 | 51 | 106 | 66 | 76 | 364 | 72 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 34 | 317 | 160 | 0 | 0 | 11 |  | 814 | 0 | 130 | 0 | 95 | 205 | 0 | 0 | 25 | 60 | 24 | 136 | 32 | 98 | 0 | 0 | 0 | 35 | 0 | 92 | 21 | 50 | 26 | 8 | 35 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 416 | 36 | 200 | 50 | 67 | 70 | 0 | 0 | 55 | 622 | 220 | 0 | 150 | 0 | 0 | 114 | 200 | 0 | 374 | 0 | 0 | 627 | 0 | 0 |  | 9218 | 5473 | 14691 | 4021 | 814 | 2337 | 495 | 3859 | 1843 | 60 | 405 | 692 | 154 | 0 | 11 | 220 | 75.32
22:00 | 0 | 0 | 120 | 170 | 0 | 0 | 0 | 400 | 272 |  | 0 | 400 | 283 | 70 | 80 | 55 | 277 | 0 | 0 | 50 | 101 | 132 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 16 | 22 | 25 | 21 | 25 | 0 | 30 | 30 | 105 | 0 | 17 | 225 | 0 | 0 | 0 |  | 12 | 48 | 34 | 70 | 30 | 50 | 8 | 29 | 0 | 0 | 0 | 305 | 0 | 211 | 8 | 0 | 45 | 0 | 0 | 43 | 0 | 44 | 43 | 20 | 10 | 33 | 20 | 166 | 34 | 0 | 19 | 0 | 43 | 39 | 46 | 47 | 112 | 0 | 61 | 84 | 0 | 207 | 17 | 0 | 10 | 290 | 24 | 5 | 0 | 288 | 300 | 0 | 98 | 0 | 132 | 0 | 87 | 104 | 132 | 366 | 85 | 88 | 68 | 0 | 280 | 35 | 51 | 106 | 68 | 76 | 355 | 72 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 34 | 317 | 160 | 0 | 0 | 9 |  | 798 | 0 | 170 | 0 | 95 | 206 | 0 | 0 | 25 | 60 | 24 | 136 | 34 | 98 | 0 | 0 | 0 | 35 | 0 | 92 | 21 | 42 | 26 | 8 | 35 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 416 | 36 | 200 | 50 | 67 | 70 | 0 | 0 | 55 | 610 | 220 | 0 | 150 | 0 | 0 | 92 | 200 | 0 | 375 | 0 | 0 | 623 | 0 | 0 |  | 9110 | 5464 | 14574 | 4020 | 798 | 2294 | 500 | 3802 | 1828 | 60 | 406 | 691 | 166 | 0 | 9 | 311.33 | 75.32
23:00 | 0 | 0 | 120 | 170 | 0 | 0 | 0 | 400 | 272 |  | 0 | 380 | 294 | 50 | 81 | 55 | 257 | 0 | 0 | 36 | 101 | 132 | 21 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 16 | 22 | 25 | 21 | 25 | 0 | 30 | 30 | 105 | 0 | 8 | 225 | 0 | 0 | 0 |  | 9 | 47 | 34 | 70 | 0 | 50 | 8 | 32 | 0 | 0 | 0 | 305 | 0 | 203 | 8 | 0 | 45 | 0 | 0 | 43 | 0 | 44 | 43 | 20 | 10 | 33 | 20 | 166 | 34 | 0 | 19 | 0 | 43 | 39 | 46 | 47 | 112 | 0 | 61 | 84 | 0 | 207 | 17 | 0 | 10 | 300 | 24 | 5 | 0 | 293 | 248 | 0 | 69 | 0 | 134 | 0 | 88 | 104 | 25 | 366 | 19 | 88 | 68 | 0 | 123 | 35 | 51 | 106 | 25 | 76 | 355 | 68 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 34 | 317 | 160 | 0 | 0 | 4 |  | 797 | 0 | 175 | 0 | 82 | 220 | 0 | 0 | 25 | 60 | 0 | 134 | 35 | 98 | 0 | 0 | 0 | 35 | 0 | 92 | 21 | 42 | 26 | 0 | 35 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 414 | 36 | 200 | 50 | 67 | 70 | 0 | 0 | 55 | 600 | 225 | 0 | 150 | 0 | 0 | 55 | 75 | 0 | 375 | 0 | 0 | 628 | 0 | 0 |  | 8554 | 5285 | 13839 | 4008 | 797 | 2302 | 448 | 3246 | 1823 | 60 | 295 | 690 | 166 | 0 | 4 | 822.255 | 75.32
24:00 | 0 | 0 | 120 | 170 | 0 | 0 | 0 | 401 | 266 |  | 0 | 380 | 304 | 50 | 81 | 41 | 246 | 0 | 0 | 34 | 25 | 132 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 20 | 22 | 25 | 21 | 8 | 0 | 30 | 30 | 105 | 0 | 8 | 222 | 0 | 0 | 0 |  | 12 | 47 | 34 | 58 | 0 | 50 | 8 | 25 | 0 | 0 | 0 | 340 | 0 | 188 | 8 | 0 | 45 | 0 | 0 | 43 | 0 | 44 | 43 | 20 | 10 | 33 | 20 | 160 | 34 | 0 | 19 | 0 | 43 | 39 | 46 | 47 | 112 | 0 | 60 | 84 | 0 | 207 | 17 | 0 | 10 | 310 | 24 | 5 | 0 | 288 | 187 | 0 | 68 | 0 | 148 | 0 | 50 | 63 | 5 | 415 | 19 | 88 | 68 | 0 | 124 | 36 | 60 | 106 | 12 | 50 | 355 | 54 | 0 | 54 | 107 | 0 | 17 | 0 | 58 | 17 | 376 | 90 | 0 | 0 | 4 |  | 797 | 0 | 180 | 0 | 32 | 222 | 0 | 0 | 16 | 50 | 0 | 136 | 34 | 98 | 0 | 0 | 0 | 35 | 0 | 0 | 21 | 42 | 26 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 414 | 35 | 200 | 50 | 67 | 34 | 0 | 0 | 55 | 600 | 224 | 0 | 150 | 0 | 0 | 55 | 75 | 0 | 375 | 0 | 0 | 631 | 0 | 0 |  | 8110 | 5065 | 13175 | 4136 | 797 | 2307 | 387 | 2727 | 1826 | 60 | 297 | 474 | 160 | 0 | 4 | 1313.125 | 75.29
KWH | 0 | 0 | 2716594 | 4126500 | 0 | 0 | 0 | 9644030 | 7662000 |  | 0 | 9124000 | 7269004 | 1218240 | 1789962 | 1323533 | 7543167 | 0 | 384000 | 1110720 | 1236672 | 2242560 | 401576 | 0 | 0 | 0 | 521640 | 657648 | 663461 | 400428 | 480000 | 478800 | 595500 | 479400 | 288960 | 0 | 1066380 | 344000 | 2500000 | 0 | 250846 | 5415497 | 0 | 0 | 0 |  | 295440 | 802704 | 788558 | 1368000 | 211200 | 549600 | 242016 | 484320 | 0 | 0 | 0 | 7802600 | 0 | 4869000 | 936727 | 0 | 1041120 | 0 | 0 | 983318 | 0 | 901040 | 1006642 | 464212 | 226440 | 791700 | 462920 | 3352320 | 493440 | 0 | 425988 | 9400 | 1024000 | 901680 | 1050000 | 1135296 | 2559272 | 0 | 1429056 | 2043840 | 0 | 5141840 | 390000 | 0 | 246420 | 7358000 | 534720 | 120960 | 0 | 6877418 | 3370597 | 0 | 1855200 | 0 | 3195216 | 105840 | 1421760 | 1174560 | 580436 | 5458000 | 684000 | 2118720 | 1513818 | 24238 | 2950691 | 528769 | 1287994 | 950760 | 466200 | 1319040 | 8479900 | 1301760 | 174060 | 1562400 | 1195582 | 0 | 441000 | 186430 | 1687680 | 554400 | 7630300 | 1557309 | 0 | 0 | 130560 |  | 21659636 | 0 | 2721888 | 0 | 882240 | 2323379 | 0 | 0 | 344640 | 890624 | 92250 | 3120000 | 662930 | 2091648 | 0 | 0 | 0 | 358400 | 0 | 435272 | 621940 | 837709 | 520600 | 34099 | 391911 | 0 | 0 | 143370 | 0 | 0 | 5258500 | 0 | 0 | 0 | 0 | 2386145 | 0 | 0 | 0 | 3392382 | 0 | 7378400 | 847200 | 2945589 | 1086816 | 757584 | 1064140 | 0 | 28904 | 1094208 | 15744700 | 5299827 | 0 | 1212000 | 23340 | 385200 | 852864 | 3935760 | 0 | 8952727 | 78515 | 0 | 14901818 | 438360 | 0 |  | 185163545 | 116197515 | 301361060 | 94457593 | 21659636 | 54193354 | 6316186 | 58036242 | 44857745 | 1410380 | 6259139 | 9233618 | 3352320 | 1454287 | 130560 | 0
Fuel Cost | 0 | 0 | 3966227.24 | 6148485 | 0 | 0 | 0 | 10126231.5 | 8274960 |  | 0 | 9945160 | 8068594.44 | 13619923.2 | 23716996.5 | 17536812.25 | 8448347.04 | 0 | 672000 | 16238726.4 | 17399975.04 | 36351897.6 | 3702530.72 | 0 | 0 | 0 | 6635260.8 | 8878248 | 8897012.01 | 300321 | 360000 | 0 | 0 | 0 | 4915209.6 | 0 | 287922.6 | 92880 | 4725000 | 0 | 4101332.1 | 5632116.88 | 0 | 0 | 0 |  | 3855492 | 13389102.72 | 13421257.16 | 18481680 | 2678016 | 6358872 | 307360.32 | 1612785.6 | 0 | 0 | 0 | 8660886 | 0 | 5648040 | 1208377.83 | 0 | 1176465.6 | 0 | 0 | 1642141.06 | 0 | 15560960.8 | 13539334.9 | 635970.44 | 169830 | 1385475 | 347190 | 24069657.6 | 537849.6 | 0 | 579343.68 | 149836 | 1402880 | 1190217.6 | 1827000 | 1964062.08 | 2943162.8 | 0 | 2772368.64 | 4659955.2 | 0 | 5193258.4 | 838500 | 0 | 487911.6 | 7358000 | 401040 | 91929.6 | 0 | 93876755.7 | 70647713.12 | 0 | 25008096 | 0 | 44253741.6 | 1237269.6 | 14672563.2 | 16044489.6 | 7702385.72 | 5021360 | 8317440 | 30636691.2 | 19149797.7 | 0 | 34641112.34 | 5758294.41 | 13691376.22 | 12901813.2 | 6009318 | 15538291.2 | 7801508 | 16857792 | 2515167 | 19826856 | 13605723.16 | 0 | 5759460 | 2227838.5 | 25264569.6 | 7301448 | 0 | 0 | 0 | 0 | 0 |  | 64978908 | 0 | 3048514.56 | 0 | 9184118.4 | 38335753.5 | 0 | 0 | 6206966.4 | 16031232 | 1325632.5 | 3494400 | 1286084.2 | 22798963.2 | 0 | 0 | 0 | 6010368 | 0 | 6807654.08 | 4788938 | 13872461.04 | 8803346 | 464769.37 | 6611538.57 | 0 | 0 | 108531.09 | 0 | 0 | 27817465 | 0 | 0 | 0 | 0 | 3054265.6 | 0 | 0 | 0 | 3935163.12 | 0 | 7304616 | 11386368 | 61769001.33 | 12857033.28 | 10947088.8 | 13514578 | 0 | 319389.2 | 13283685.12 | 141859747 | 5405823.54 | 0 | 8968800 | 263975.4 | 4518396 | 13074405.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 921857251.22 | 554437979.42 | 1476295230.64 | 98181075.91 | 64978908 | 63988634.35 | 132416714.45 | 743840277.2 | 169677212 | 380802.6 | 38335753.5 | 129194323.33 | 24069657.6 | 11231871.7 | 0 | 0
Yesterday Day Peak | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 401 | 330 |  | 0 | 450 | 299 | 41 | 80 | 55 | 331 | 0 | 0 | 50 | 48 | 82 | 11 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 20 | 20 | 25 | 18 | 8 | 0 | 60 | 0 | 105 | 0 | 8 | 219 | 0 | 0 | 0 |  | 12 | 32 | 32 | 58 | 10 | 6 | 10 | 2 | 0 | 0 | 0 | 320 | 0 | 206 | 55 | 0 | 43 | 0 | 0 | 43 | 0 | 30 | 34 | 18 | 10 | 33 | 14 | 148 | 10 | 0 | 18 | 1 | 43 | 39 | 42 | 47 | 112 | 0 | 59 | 86 | 0 | 204 | 17 | 0 | 10 | 310 | 16 | 5 | 0 | 265 | 245 | 0 | 69 | 0 | 132 | 15 | 50 | 51 | 5 | 80 | 19 | 88 | 68 | 3 | 88 | 17 | 51 | 17 | 9 | 50 | 350 | 53 | 13 | 54 | 34 | 0 | 17 | 28 | 57 | 17 | 325 | 53 | 0 | 0 | 0 |  | 910 | 0 | 100 | 0 | 31 | 0 | 0 | 0 | 10 | 30 | 0 | 136 | 23 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 21 | 0 | 25 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 118 | 0 | 241 | 36 | 200 | 35 | 15 | 27 | 0 | 5 | 35 | 622 | 226 | 0 | 17 | 3 | 44 | 36 | 180 | 0 | 365 | 6 | 0 | 618 | 64 | 0 |  | 12178 | DayPeak
Yesterday Evening Peak | 0 | 0 | 120 | 170 | 0 | 0 | 0 | 401 | 301 | 0 | 0 | 400 | 291 | 74 | 80 | 55 | 315 | 0 | 0 | 58 | 101 | 132 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 16 | 22 | 25 | 18 | 25 | 0 | 30 | 30 | 108 | 0 | 17 | 225 | 0 | 0 | 0 | 0 | 12 | 48 | 34 | 70 | 30 | 50 | 10 | 28 | 0 | 0 | 0 | 310 | 0 | 211 | 8 | 0 | 45 | 0 | 0 | 43 | 0 | 45 | 43 | 20 | 10 | 33 | 20 | 154 | 30 | 0 | 19 | 0 | 43 | 39 | 45 | 47 | 112 | 0 | 60 | 84 | 0 | 207 | 17 | 0 | 10 | 300 | 24 | 5 | 0 | 292 | 295 | 0 | 108 | 0 | 132 | 0 | 87 | 104 | 135 | 366 | 85 | 88 | 68 | 0 | 280 | 35 | 51 | 106 | 66 | 76 | 364 | 72 | 0 | 162 | 107 | 0 | 17 | 0 | 115 | 34 | 317 | 160 | 0 | 0 | 11 |  | 814 | 0 | 130 | 0 | 95 | 205 | 0 | 0 | 25 | 60 | 24 | 136 | 32 | 98 | 0 | 0 | 0 | 35 | 0 | 92 | 21 | 50 | 26 | 8 | 35 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 416 | 36 | 200 | 50 | 67 | 70 | 0 | 0 | 55 | 622 | 220 | 0 | 150 | 0 | 0 | 114 | 200 | 0 | 374 | 0 | 0 | 627 | 0 | 0 |  | 14691 | EvPeak
Forecast for Evening | 0 | 0 | 120 | 170 | 0 | 0 | 0 | 380 | 280 | 0 | 0 | 370 | 300 | 74 | 80 | 55 | 230 | 0 | 0 | 75 | 102 | 130 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 20 | 22 | 25 | 24 | 25 | 0 | 30 | 30 | 110 | 0 | 17 | 225 |  | 0 | 0 | 0 | 12 | 70 | 34 | 80 | 30 | 50 | 11 | 25 | 0 | 0 | 0 | 320 | 0 | 200 | 8 | 0 | 45 | 0 | 0 | 43 | 0 | 45 | 43 | 20 | 10 | 33 | 20 | 160 | 30 | 0 | 18 | 0 | 43 | 39 | 45 | 44 | 112 | 0 | 60 | 86 | 0 | 204 | 18 | 0 | 10 | 300 | 24 | 5 | 0 | 293 | 300 | 0 | 105 | 0 | 149 | 0 | 88 | 120 | 150 | 400 | 85 | 88 | 68 | 0 | 280 | 17 | 51 | 106 | 76 | 75 | 380 | 72 | 0 | 162 | 107 | 0 | 17 |  | 115 | 35 | 350 | 163 |  | 0 | 10 |  | 930 | 0 | 240 |  | 95 | 225 | 0 | 0 | 33 | 70 | 40 | 135 | 27 | 100 | 0 | 0 | 0 | 35 | 0 | 90 | 28 | 50 | 27 | 8 | 35 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 170 | 0 | 400 | 35 | 200 | 50 | 68 | 70 | 0 | 0 | 55 | 622 | 220 |  | 150 |  |  | 115 | 200 |  | 370 |  | 0 | 1050 |  | 0
Forecast for Day | 0 | 0 | 120 | 170 | 0 | 0 | 0 | 380 | 280 | 0 | 0 | 370 | 300 | 50 | 80 | 55 | 230 | 0 | 0 | 58 | 33 | 82 | 22 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 20 | 22 | 25 | 24 | 8 | 0 | 30 | 30 | 110 | 0 | 8 | 225 |  | 0 | 0 | 0 | 12 | 32 | 34 | 58 | 12 | 6 | 11 | 2 | 0 | 0 | 0 | 310 | 0 | 200 | 8 | 0 | 45 | 0 | 0 | 43 | 0 | 44 | 43 | 20 | 10 | 33 | 20 | 129 | 25 | 0 | 18 | 1.6 | 43 | 39 | 45 | 44 | 112 | 0 | 60 | 86 | 0 | 204 | 17 | 0 | 10 | 300 | 24 | 5 | 0 | 115 | 300 | 0 | 78 | 0 | 149 | 20 | 50 | 50 | 5 | 400 | 20 | 88 | 51 | 5 | 88 | 17 | 51 | 52 | 9 | 50 | 376 | 54 | 50 | 72 | 34 | 0 | 17 | 30 | 55 | 17 | 350 | 54 |  | 0 | 15 |  | 930 | 0 | 240 | 0 | 80 | 150 | 0 | 0 | 20 | 36 | 8 | 135 | 25 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 42 | 22 | 0 | 35 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 380 | 35 | 150 | 35 | 15 | 34 | 0 | 8 | 35 | 622 | 220 |  | 17 | 6 | 100 | 35 | 200 |  | 370 | 30 | 0 | 1050 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 120 | 170 | 0 | 0 | 0 | 401 | 262 | 0 | 0 | 370 | 282 | 50 | 80 | 55 | 234 | 0 | 0 | 34 | 33 | 82 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 16 | 22 | 17 | 22 | 8 | 0 | 30 | 30 | 108 | 0 | 8 | 227 | 0 | 0 | 0 | 0 | 12 | 32 | 34 | 58 | 0 | 6 | 8 | 8 | 0 | 0 | 0 | 305 | 0 | 211 | 8 | 0 | 45 | 0 | 0 | 43 | 0 | 44 | 43 | 20 | 8 | 33 | 20 | 138 | 21 | 0 | 19 | 0 | 43 | 39 | 44 | 45 | 80 | 0 | 60 | 81 | 0 | 206 | 17 | 0 | 10 | 290 | 24 | 5 | 0 | 113 | 0 | 0 | 77 | 0 | 149 | 3 | 50 | 17 | 5 | 367 | 19 | 88 | 51 | 1 | 88 | 17 | 51 | 17 | 8 | 50 | 352 | 36 | 7 | 35 | 34 | 0 | 0 | 14 | 36 | 17 | 293 | 17 | 0 | 0 | 6 | 0 | 913 | 0 | 250 | 0 | 32 | 120 | 0 | 0 | 11 | 37 | 0 | 137 | 22 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 14 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 359 | 36 | 0 | 35 | 15 | 34 | 0 | 1 | 35 | 622 | 222 | 0 | 17 | 1 | 34 | 0 | 75 | 0 | 370 | 4 | 0 | 888 | 16 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
292.3904
| Minimum Generation |  | 11487 | 9:00
| Highest Generation |  | 14691 | 21:00
| Day Peak Generation |  | 12178 | 12:00
| Evening Peak Generation |  | 14691 | 21:00
| HVDC Max Flow |  | 910 | 6:00
| HVDC EvPeak Flow |  | 814 | 21:00
| Load factor L.F |  | 85.47% | [163 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-07-12
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-07-11 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 12178 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 11475
Evening Peak Generation : |  |  | 14691 | MW Hour : | 21:00 | Available Max Generation : |  | 15429
E.P. Demand (at gen end) : |  |  | 14921 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 15000
Maximum Generation : |  |  | 14691 | MW Hour : | 21:00 | Reserve(Generation end) |  | 429
Total Gen. (MKWH) : |  |  | 301.3611 | System Load Factor : | 85.47% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 46 | MW at | 7:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-07-12
Actual : |  | 75.32 | Ft.(MSL) , | Rule curve : | 85.6 | Ft.( MSL )
Gas Consumed : |  | Total = | 1071.79 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 162169710.26
: |  |  | Coal : | 169677212 | Oil : | 1043787068.48 | Total : | 1375633990.74
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 12 | 288:00 | 4404.9773 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1209.3752 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1693.7978 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1471.9403 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1211.2867 |  |  | 0 | 0%
Mymensingh Area |  | 97 | 2328:00 | 900.7482 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 505.0509 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 420.7592 |  |  | 0 | 0%
Rangpur Area |  | 111 | 2664:00 | 822.9344 |  |  | 0 | 0%
Total |  | 220 |  | 12640.8699 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:07 | 16:45 | Ashuganj-Brahmanbaria 132kV Ckt-2 Scheduled S/D from Brahmanbaria 132/33kV end Due to Sag adjust and conductor armering.
08:29 | 12:37 | Chandraghona 132/33kV S/S TR-01(406T) LT Scheduled S/D Due to High temperature maintenance.
08:30 | 12:37 | Chandraghona 132/33kV S/S TR-01(406T) HT Scheduled S/D Due to High temperature maintenance.
| 09:02 | Natore 132/33kV S/S TR-1 (405 T) HT is restored.
| 09:05 | Natore 132/33kV S/S TR-1 (405 T) LT is restored.
09:09 | 10:59 | Mongla 132/33kV S/S T-1 LT Forced S/D Due to Shutdown due to Mongla WZPDCL substation 33kv ds3 bus coupler red phase | [5 empty] | 4 MW load interrup.
jumper out.
09:10 | 10:58 | Mongla 132/33kV S/S T-1 HT Forced S/D Due to Shutdown due to Mongla WZPDCL substation 33kv ds3 bus coupler red phase
jumper out.
10:18 | 11:33 | Ashuganj 230/132/33kV S/S T-4 Kalabagan HT Forced S/D Due to "B" Phase CB connection point Temperature rise.
10:19 | 11:35 | Ashuganj 230/132/33kV S/S T-4 Kalabagan LT Forced S/D Due to "B" Phase CB connection point Temperature rise.
10:23 |  | Siddhirganj GT-2 was shutdown due to gas shortage. | [5 empty] | 30 MW generation interrup.
11:29 | 14:23 | Sherpur 132/33kV S/S Transformer- 01 LT Scheduled S/D Due to Roumari 33 Kv Feeder C.T & D/S Loop Change.
| 13:22 | Khulna 225MW GT was sync.
| 13:32 | Bibiyana-3 400MW ST was sync.
| 16:46 | Khulna 225MW ST was sync.
17:49 | 17:54 | Chowmuhani 132/33kV S/S TR1-415T LT Tripped showing INST. Earth -Fault. relays Due to INST. Earth -Fault 33KV LPBS | [5 empty] | 60 MW load interrup.
Feeder fault.
18:31 |  | Sirajgonj Gas 225MW Unit-2 was shutdown due to gas shortage.
| 19:10 | Madanganj 132/33kV S/S GT-2 HT is restored.
| 20:16 | Adani (Godda)- Bogura west 400 KV ckt-1 Syn .
20:33 |  | Chhatak 132/33kV S/S T-2 HT Forced S/D Due to T-2 33kV incoming R phase Red hot.
03:32 | 03:47 | Barishal 132/33kV S/S T-2 (415T) LT Tripped showing Insta O/C, Def O/C. relays Due to For 33kV Polashpur feeder fault. | [5 empty] | 33 MW load interrup.
03:32 | 03:47 | Barishal 132/33kV S/S T-1 (405T) LT Tripped showing Inst. O/C ,Def O/C relays Due to For WZPDCL 33kV Polashpur Fedder fault. | [5 empty] | 52 MW load interrup.
05:49 | 06:12 | Jashore 132/33kV S/S T-3 HT Tripped showing Lock out relay (Both side) relays Due to T3 both side triped by lockout | [5 empty] | 26 MW load interrup.
relay due to earth fault of 33 kv PBS Hasimpur feeder fault.
05:49 | 06:12 | Jashore 132/33kV S/S T-3 LT Tripped showing Lock out relay (Both side) relays Due to T3 both side triped by lockout
relay due to earth fault of 33 kv PBS Hasimpur feeder fault.
| 06:06 | Adani Power Jharkhand Ltd. unit-2 was sync.
fault.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-07-11 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 120 | 2716594 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 170 | 4126500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 401 | 9644030
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 301 | 7662000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 9124000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 74 | 1218240 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 291 | 7269004 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 80 | 1789962 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1323533
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 22 | 401576 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 400428 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 384000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 58 | 1110720 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 315 | 7543167
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 101 | 1236672
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 521640
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 2242560 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 657648
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 663461
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 38 | 958800 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 595500 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 18 | 479400 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 288960 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 292 | 6877418 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 295 | 3370597 | Engine problem
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 3195216 | Machine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 2118720
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 72 | 1301760 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1562400
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 186430
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 34 | 554400 | Line problem
| Dhaka area Total |  |  |  | 5822 | 3884 | 81525336
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 108 | 2500000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 250846 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 105840
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 549600
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 60 | 1410380 | Low Water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 225 | 5415497
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 68 | 1513818 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 48 | 802704 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 788558 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 70 | 1368000 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 87 | 1421760
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 10 | 242016 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 28 | 484320
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 30 | 211200 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 24238
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 280 | 2950691 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 528769 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 51 | 1287994 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 76 | 1319040 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 1195582 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 160 | 1557309
| SS Power I |  | SS Power | 0 | 0 | 0 | 0 | On test.
| Cox's Bazar Wind |  | IPP | 66 | 0 | 11 | 130560 | On test.
| Chattogram area Total |  |  |  | 2545 | 1555 | 26058722
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 211 | 4869000 | 0
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7802600
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 317 | 7630300 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 45 | 1041120
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 936727 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 983318
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 135 | 580436
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 45 | 901040 | Machine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 104 | 1174560 | Engine problem
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 464212
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 226440
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 154 | 3352320
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 791700
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 1006642 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 462920 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 106 | 950760 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 66 | 466200 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 441000 | Fuel shortage
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1687680
| Cumilla Area Total |  |  |  | 3096 | 1802 | 35768975
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 30 | 493440 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 425988 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9400
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 108 | 1855200 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 85 | 684000 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 174060
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 295440 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 254 | 3937528
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1024000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 39 | 901680 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2559272 | ST under maint
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 45 | 1050000
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 47 | 1135296
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 120960 | Machine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1429056
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 2043840
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 207 | 5141840
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 390000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 534720
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7358000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 366 | 5458000 | Gas shortage
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 246420
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 364 | 8479900 | Gas shortage
| Sylhet Area Total |  |  |  | 2427 | 1723 | 37872984
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 814 | 21659636
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 95 | 882240 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 25 | 344640 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 205 | 2323379
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 60 | 890624 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 130 | 2721888 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 24 | 92250 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 36 | 847200 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 67 | 757584
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 385200
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 220 | 200 | 3935760 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 374 | 8952727 | Coal shortage.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 3121 | 2030 | 43793128
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 98 | 2091648 | Fuel shortage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 32 | 662930 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 136 | 3120000 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 622 | 15744700 | Machine problem
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5299827
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1212000
| Barisal 307 MW |  | IPP | 307*1 | 307 | 0 | 0 | Coal shortage.
| Barisal Area Total |  |  |  | 2265 | 1258 | 28131105
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 35 | 358400 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 21 | 621940
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 837709
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 26 | 520600 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 2386145
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 166 | 3392382 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 416 | 7378400
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 391911 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 0 | 143370 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 34099 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 435272 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 200 | 2945589
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 1086816 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 55 | 1094208 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 23340
| Adani Power Jharkhanda Ltd |  | Import | 748*1 | 748 | 627 | 14901818
| Rajshahi Area Total |  |  |  | 2905 | 1781 | 36551999
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 220 | 5258500
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 1064140 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 28904
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 114 | 852864
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 78515
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 438360
| Rangpur Area Total |  |  |  | 750 | 404 | 7721283
| Total |  |  |  | 23545 | 14691 | 301361060
| Eastern Grid Total |  |  |  | 14504 | 9218 | 185163545
| Western Grid Total |  |  |  | 9041 | 5473 | 116197515
| National Grid Total |  |  |  | 23545 | 14691 | 301361060
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-07-11
| (a) ENTIRE EASTERN GRID : |  | 9410.35 | MW | (b) ENTIRE WESTERN GRID : |  | 4691.8 | MW
| i) Dhaka area |  | 4887.35 | MW | i) Khulna area |  | 1839 | MW
| ii) Chittagong area |  | 1439 | MW | ii) Rajshahi area |  | 1554.2 | MW
| iii) Comilla area |  | 1403 | MW | iii) Barisal area |  | 462.6 | MW
| iv) Mymensingh area |  | 1095 | MW | iv) Rangpur area |  | 836 | MW
| v) Sylhet area |  | 586 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 14102.15 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 22 | 20:00 | Kamrangirchar | 48.6 | 13:00 | Natore | 161 | 21:00 | Shitalakhya | 105.9 | 15:00
2 | AKSML | 11.9 | 15:00 | Chowmuhani | 242 | 21:00 | Kaptai | N/A | N/A | Nawabganj | 48.2 | 22:00 | Sholosohor | 35 | 19:00
3 | Aftabnagar | 36 | 21:00 | Chuadanga | 120 | 21:00 | Kazla | 87 | 18:30 | Netrakona | 104 | 21:00 | Shyampur | 128 | 00:00
4 | Agargaon | 95 | 15:00 | Coxsbazar | 115 | 21:00 | Keranigonj | 64 | 00:00 | New | 88.6 | 12:00 | Siddhirganj | 114 | 14:00
5 | Agrabad | 72 | 19:00 | Cumilla(N) | 157 | 23:00 | Khagrachori | 30 | 19:00 | Niamatpur | 74 | 20:00 | Sirajganj | 106 | 19:30
6 | Amnura | 62 | 21:00 | Cumilla(S) | 173 | 19:00 | Khulna | 95 | 19:30 | Noapara | 50 | 19:30 | Sonargaon | 106 | 21:00
7 | Ashuganj | 60 | 21:00 | Daudkandi | 160 | 21:00 | Khulshi | 164 | 23:00 | PHP | 7 | 10:00 | Sreemongol | 65 | 21:00
8 | BIPTC | N/A | N/A | Dhaka | 30 | 11:00 | Kishoreganj | 156 | 19:30 | Pabna | 129 | 21:00 | Sreepur | 70 | 19:00
9 | BSRM | 135 | 10:00 | Dhamrai | 126 | 21:00 | Kodda | 293 | 19:30 | Palashbari | 109 | 19:00 | Srinagar | 45.7 | 22:00
10 | Bagerhat | 97 | 20:00 | Dhanmondi | 140 | 13:00 | Kulaura | 54 | 20:00 | Panchagarh | 49 | 18:00 | Sunamganj | 50 | 21:00
11 | Bakulia | 101 | 19:30 | Dohazari | 104 | 19:00 | Kurigram | 58 | 07:00 | Patuakhali | 115.5 | 22:00 | Sylhet | 149 | 20:00
12 | Banani | 52 | 13:00 | Faridpur | 168 | 21:00 | Kushtia | 156 | 21:00 | Payra | 21.6 | 23:00 | TK | 31.5 | 22:00
13 | Bangabhaban | 20 | 10:00 | Fatullah | 60 | 10:00 | Lalbag | 79 | 13:00 | Postogola | 55 | 00:00 | Tangail | 207 | 21:00
14 | Barapukuria | 57 | 21:00 | Fenchuganj | 47 | 21:00 | Lalmonirhat | 52 | 20:00 | Purbachal | 21 | 15:00 | Thakurgaon | 102 | 20:00
15 | Barguna | 22 | 23:00 | Feni | 114 | 22:00 | Madanganj | 12 | 00:00 | Purbasadipur | 139 | 20:00 | Tongi | 112 | 16:00
16 | Barishal | 102 | 19:30 | GPH | 18 | 19:30 | Madaripur | 114 | 21:00 | Rahanpur_I | N/A | N/A | Ullon | 42 | 19:00
17 | Barishal-230 | 104 | 21:00 | Ghorashal | 70 | 22:00 | Madartek | 86.39 | 00:00 | Rahim | 48 | 06:00 | Uttara | 78 | 12:00
18 | Baroaulia | 72 | 01:00 | Goalpara | 36 | 04:00 | Madunaghat | 54 | 19:00 | Rajbari | 74 | 20:00 | UttaraNew | 50 | 15:00
19 | Baroirhat | 68 | 19:00 | Gollamari | 57 | 21:00 | Magura | 69 | 19:30 | Rajendrapur | 94 | 00:00 | Zigatola | 94 | 15:00
20 | Bashundhara | 165 | 15:00 | Gopalganj | 107.2 | 21:00 | Mahasthangarh | 74 | 21:00 | Rajshahi | 172 | 21:00
21 | BashundharaCement | 0 | 00:00 | Gulshan | 130 | 12:00 | Manikganj | 110 | 00:00 | Rajshahi-230 | 40 | 21:00
22 | Beanibazar | 68 | 22:00 | Halishahar | 80 | 09:00 | Maniknagar | 102 | 13:00 | Ramganj | 122 | 22:00
23 | Benapole | 58 | 19:30 | HaripurSBU | 157 | 20:00 | Matarbari | 47 | 19:00 | Rampur | 28 | 19:30
24 | Bhaluka | 164 | 19:30 | Hasnabad | 86 | 15:00 | Matuail | 62 | 12:00 | Rangamati | 18 | 19:00
25 | Bhandaria | 54 | 21:00 | Hathazari | 74 | 18:30 | Millgate | 100 | 12:00 | Rangpur | 145 | 19:00
26 | Bhangura | 45 | 20:00 | Ishurdi | 57 | 13:00 | Mirpur | 136 | 15:00 | Ruppur | 6 | 17:00
27 | Bheramara(GK) | 67 | 22:00 | Jaldhaka | 74 | 20:00 | Mirsorai | 6 | 15:00 | SSM | 0 | 00:00
28 | Bhulta | 238 | 22:00 | Jamalpur | 141 | 21:00 | Mithapukur | 36 | 19:00 | Saidpur | 96 | 18:00
29 | Bog-Sherpur | 66 | 21:00 | Jashore | 141 | 21:00 | Modern | 0 | 00:00 | Satkhira | 140 | 22:00
30 | Bogura | 169 | 21:00 | Jhenaidah | 139 | 21:00 | Mogbazar | 143.5 | 15:00 | Satmasjid | 96 | 14:00
31 | Borhanuddin | 61 | 23:00 | Joydebpur | 171 | 19:30 | Mongla | 30 | 21:00 | Savar | 188 | 17:00
32 | Brahmanbaria | 181 | 22:00 | Joypurhat | 59 | 21:00 | Motijheel | 40 | 15:00 | Shahjadpur | 104 | 21:00
33 | Cantonment | 138 | 14:00 | Juldah | 25 | 00:00 | Munshiganj | 110 | 00:00 | Shahjibazar | 122 | 22:00
34 | Chandpur | 74 | 21:00 | KSRM | 31 | 05:00 | Mymensingh | 230 | 01:00 | Shahmirpur | 45.8 | 15:00
35 | Chandraghona | 31 | 00:00 | Kabirpur | 297 | 20:00 | Naogaon | 130 | 20:00 | Shariatpur | 86 | 22:00
36 | Chapai | 83 | 22:00 | Kachua | 86 | 20:00 | Narail | 60 | 19:30 | Sherpur | 110 | 20:00
37 | Charsaidpur | 30 | 01:00 | Kallyanpur | 99 | 00:00 | Narinda | 69 | 13:00 | Shikalbaha | N/A | N/A
38 | Chauddagram | 63 | 20:00 | Kalurghat | 34 | 15:00 | Narshingdi | 168 | 19:30 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-07-11 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 406 | 18:30 | 397 | 12:00 | Gopalganj | 410 | 18:00 | 403 | 12:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 402 | 18:30 | 392 | 21:00
| Bhulta | 401 | 18:30 | 395 | 00:00 | Madunaghat_I | 411 | 18:30 | 395 | 10:00
| Bibiana | 413 | 19:00 | 405 | 02:00 | Payra | 414 | 18:00 | 410 | 01:00
| BIPTC | 397 | 06:00 | 387 | 01:00 | Rahanpur_I | N/A | N/A | N/A | N/A
| Bogura | N/A | N/A | N/A | N/A | Rampal | 411 | 18:30 | 403 | 00:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 237 | 06:00 | 232 | 10:00 | Hasnabad | 236 | 18:30 | 232 | 12:00
| AKSML | 236 | 21:00 | 212 | 08:00 | Hathazari | 236 | 19:00 | 226 | 09:00
| Aminbazar | 238 | 18:30 | 234 | 13:00 | Ishurdi | 233 | 18:00 | 226 | 20:00
| Ashuganj | 235 | 18:30 | 230 | 20:00 | Jhenaidah | 226 | 18:30 | 218 | 20:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 237 | 18:30 | 233 | 14:00
| Baghabari | 231 | 14:00 | 224 | 20:00 | Keranigonj | 236 | 18:30 | 231 | 10:00
| Barapukuria | 222 | 11:00 | 206 | 03:00 | Khulna(S) | 234 | 18:30 | 228 | 07:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | 235 | 18:30 | 225 | 08:00
| Barishal | 238 | 18:00 | 230 | 19:30 | Maniknagar | 235 | 04:00 | 231 | 12:00
| Bheramara | 231 | 18:00 | 224 | 20:00 | Meghnaghat | 241 | 00:00 | 238 | 12:00
| Bhulta | 237 | 06:00 | 233 | 12:00 | Mirsorai | 238 | 19:00 | 225 | 10:00
| Bibiana | 237 | 22:00 | 233 | 16:00 | Rajshahi | 230 | 18:30 | 221 | 20:00
| BIPTC | 233 | 18:30 | 224 | 20:00 | Rampal | 233 | 18:00 | 227 | 07:00
| Bogura | 225 | 11:00 | 215 | 20:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 238 | 08:00 | 235 | 19:30 | Rampura | 235 | 04:00 | 231 | 12:00
| BSRM | 238 | 18:00 | 226 | 08:00 | Shikalbaha | 234 | 00:00 | 225 | 04:00
| Cumilla(N) | 235 | 18:30 | 229 | 02:00 | Shyampur | 235 | 06:00 | 230 | 09:00
| Fenchuganj | 243 | 17:00 | 234 | 15:00 | Siddhirganj | 237 | 09:00 | 233 | 12:00
| Ghorashal | 240 | 00:00 | 235 | 11:00 | Sirajgonj | 236 | 11:00 | 230 | 20:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 230 | 09:00 | 218 | 01:00
| GPH | 236 | 19:00 | 225 | 04:00 | Tongi | 234 | 07:00 | 230 | 01:00
| Haripur | 235 | 22:00 | 231 | 16:00
| 132 kV | KV |  | KV |  | Tongi | KV |  | KV
| Aftabnagar | 134 | 22:00 | 129 | 09:00 | Lalbag | 133 | 06:00 | 128 | 12:00
| Agargaon | 137 | 06:00 | 133 | 10:00 | Lalmonirhat | 132 | 11:00 | 119 | 22:00
| Agrabad | 136 | 18:30 | 130 | 10:00 | Madanganj | 137 | 18:30 | 133 | 00:00
| AKS | 0 | 00:00 | N/A | N/A | Madaripur | 132 | 18:30 | 126 | 05:00
| Aminbazar | 137 | 18:00 | 134 | 07:00 | Madartek | 133 | 06:00 | 128 | 09:00
| Amnura | 140 | 23:00 | 128 | 07:00 | Madunaghat | 138 | 00:00 | 132 | 02:00
| Ashuganj | 140 | 18:00 | 136 | 00:00 | Magura | 135 | 18:30 | 128 | 20:00
| Bagerhat | 137 | 18:30 | 131 | 08:00 | Mahasthangarh | 133 | 11:00 | 123 | 00:00
| Bakulia | 138 | 18:00 | 131 | 23:00 | Manikganj | 137 | 11:00 | 129 | 20:00
| Banani | 133 | 18:30 | 126 | 09:00 | Maniknagar | 134 | 04:00 | 128 | 12:00
| Bangabhaban | 134 | 06:00 | 128 | 15:00 | Matarbari | 126 | 04:00 | 116 | 21:00
| Barapukuria | 138 | 11:00 | 125 | 02:00 | Matuail | 136 | 18:30 | 133 | 12:00
| Barguna | 138 | 18:30 | 131 | 03:00 | Millgate | 133 | 01:00 | 128 | 12:00
| Barishal | 138 | 18:30 | 130 | 00:00 | Mirpur | 137 | 18:30 | 132 | 08:00
| Barishal-230 | 139 | 18:00 | 132 | 00:00 | Mithapukur | 134 | 11:00 | 120 | 02:00
| Baroaulia | 137 | 03:00 | 130 | 07:00 | Modern | 137 | 19:00 | 132 | 05:00
| Baroirhat | 134 | 18:00 | 122 | 03:00 | Mogbazar | 134 | 05:00 | 130 | 09:00
| Bashundhara | 134 | 22:00 | 128 | 09:00 | Mongla | 136 | 14:00 | 130 | 20:00
| BashundharaCement | 137 | 18:30 | 133 | 00:00 | Motijheel | 134 | 06:00 | 128 | 12:00
| Beanibazar | 131 | 08:00 | 126 | 21:00 | Munshiganj | 138 | 18:30 | 133 | 00:00
| Benapole | 135 | 23:00 | 128 | 00:00 | Mymensingh | 130 | 16:00 | 115 | 23:00
| Bhaluka | 128 | 06:00 | 121 | 20:00 | Naogaon | 130 | 17:00 | 118 | 00:00
| Bhandaria | 134 | 18:30 | 125 | 02:00 | Narail | 136 | 23:00 | 127 | 20:00
| Bhangura | 136 | 15:00 | 131 | 20:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 134 | 18:30 | 130 | 20:00 | Narshingdi | 132 | 19:00 | 126 | 00:00
| Bheramara(GK) | 134 | 10:00 | 131 | 20:00 | Natore | 134 | 18:30 | 127 | 00:00
| Bhulta | 127 | 18:30 | 123 | 00:00 | Nawabganj | 132 | 04:00 | 129 | 11:00
| Bog-Sherpur | 134 | 17:00 | 126 | 20:00 | Netrakona | 129 | 16:00 | 117 | 23:00
| Bogura | 135 | 17:00 | 126 | 20:00 | New | 134 | 06:00 | 129 | 12:00
| Bogura-230 | 135 | 17:00 | 126 | 20:00 | Niamatpur | 131 | 17:00 | 114 | 20:00
| Brahmanbaria | 134 | 07:00 | 129 | 21:00 | Noapara | 138 | 18:30 | 132 | 07:00
| Cantonment | 136 | 04:00 | 132 | 10:00 | Pabna | 133 | 11:00 | 127 | 20:00
| Chandpur | 136 | 18:30 | 116 | 04:00 | Palashbari | 129 | 11:00 | 119 | 00:00
| Chandraghona | 138 | 18:00 | 131 | 03:00 | Panchagarh | 133 | 11:00 | 114 | 02:00
| Chapai | 134 | 11:00 | 129 | 20:00 | Patuakhali | 139 | 19:00 | 134 | 05:00
| Charsaidpur | 138 | 18:30 | 134 | 00:00 | Payra | 141 | 18:30 | 137 | 01:00
| Chauddagram | 134 | 18:00 | 122 | 03:00 | PHP | 135 | 18:00 | 121 | 03:00
| Chhatak | 132 | 09:00 | 126 | 20:00 | Postogola | 139 | 22:00 | 135 | 09:00
| Chowmuhani | 130 | 19:30 | 119 | 04:00 | Purbachal | 134 | 06:00 | 127 | 12:00
| Chuadanga | 130 | 18:30 | 120 | 20:00 | Purbasadipur | 131 | 11:00 | 120 | 02:00
| Coxsbazar | 125 | 18:00 | 112 | 23:00 | Rahim | 136 | 07:00 | 134 | 00:00
| Cumilla(N) | 137 | 18:30 | 129 | 03:00 | Rajbari | 130 | 18:00 | 124 | 20:00
| Cumilla(S) | 137 | 18:00 | 123 | 19:00 | Rajendrapur | 137 | 19:00 | 132 | 18:00
| Daudkandi | 136 | 18:30 | 129 | 00:00 | Rajshahi | 135 | 17:00 | 130 | 00:00
| Dhaka | 133 | 05:00 | 129 | 12:00 | Rajshahi-230 | 136 | 18:30 | 131 | 20:00
| Dhamrai | 133 | 03:00 | 129 | 00:00 | Ramganj | 129 | 18:00 | 112 | 04:00
| Dhanmondi | 136 | 05:00 | 132 | 12:00 | Rampur | 136 | 00:00 | 131 | 03:00
| Dohazari | 138 | 18:00 | 128 | 19:30 | Rampura | 133 | 22:00 | 128 | 09:00
| Faridpur | 130 | 18:00 | 126 | 02:00 | Rangamati | 136 | 18:00 | 130 | 10:00
| Fatullah | 133 | 18:30 | 130 | 10:00 | Rangpur | 130 | 17:00 | 117 | 02:00
| Fenchuganj | 138 | 18:30 | 134 | 21:00 | Ruppur | 135 | 17:00 | 131 | 19:30
| Feni | 134 | 18:30 | 124 | 07:00 | Saidpur | 132 | 11:00 | 115 | 02:00
| Ghorashal | 140 | 01:00 | 137 | 12:00 | Satkhira | 137 | 18:30 | 129 | 07:00
| Goalpara | 141 | 18:30 | 135 | 07:00 | Satmasjid | 136 | 04:00 | 132 | 12:00
| Gollamari | 139 | 18:30 | 134 | 08:00 | Savar | 138 | 18:30 | 131 | 08:00
| Gopalganj | 137 | 18:30 | 130 | 07:00 | Shahjadpur | 140 | 18:00 | 134 | 20:00
| Gopalganj-400 | 132 | 18:00 | 128 | 00:00 | Shahjibazar | 135 | 18:00 | 130 | 21:00
| Gulshan | 132 | 05:00 | 128 | 09:00 | Shahmirpur | 138 | 19:00 | 131 | 08:00
| Halishahar | 137 | 18:00 | 131 | 04:00 | Shariatpur | 131 | 18:00 | 126 | 00:00
| Haripur | 136 | 05:00 | 134 | 00:00 | Sherpur | 128 | 22:00 | 114 | 23:00
| HaripurSBU | 136 | 07:00 | 134 | 00:00 | Shikalbaha | N/A | N/A | N/A | N/A
| Hasnabad | 138 | 02:00 | 136 | 00:00 | Shikalbaha-230 | 138 | 00:00 | 133 | 03:00
| Hathazari | 138 | 18:00 | 133 | 04:00 | Shitalakhya | 138.4 | 19:00 | 134.3 | 15:00
| Ishurdi | 135 | 18:00 | 131 | 00:00 | Sholosohor | 136 | 18:00 | 131 | 03:00
| Jaldhaka | 132 | 11:00 | 117 | 00:00 | Shyampur | 133 | 19:30 | 129 | 12:00
| Jamalpur | 132 | 22:00 | 118 | 23:00 | Shyampur-230 | 135 | 22:00 | 122 | 03:00
| Jashore | 135 | 18:30 | 130 | 00:00 | Siddhirganj | 137 | 18:00 | 134 | 00:00
| Jhenaidah | 137 | 18:30 | 130 | 20:00 | Sirajganj | 135 | 18:30 | 126 | 20:00
| Jhenaidah-230 | 137 | 18:00 | 131 | 20:00 | Sonargaon | 137 | 19:00 | 131 | 09:00
| Joydebpur | 139 | 04:00 | 133 | 12:00 | Sreemongol | 134 | 16:00 | 130 | 22:00
| Joypurhat | 131 | 16:00 | 117 | 21:00 | Sreepur | 129 | 09:00 | 125 | 00:00
| Juldah | 138 | 19:00 | 133 | 12:00 | Srinagar | 133 | 06:00 | 129 | 12:00
| Kabirpur | 137 | 07:00 | 125 | 12:00 | SSM | 140 | 00:00 | 132 | 07:00
| Kachua | 135 | 18:00 | 120 | 04:00 | Sunamganj | 130 | 16:00 | 123 | 20:00
| Kaliakoir | 139 | 18:30 | 131 | 17:00 | Sylhet | 132 | 01:00 | 130 | 20:00
| Kallyanpur | 131 | 06:00 | 123 | 18:00 | Tangail | 133 | 16:00 | 124 | 21:00
| Kalurghat | 136 | 18:00 | 131 | 04:00 | Thakurgaon | 132 | 11:00 | 111 | 02:00
| Kamrangirchar | 133 | 07:00 | 127 | 00:00 | TK | 137 | 18:30 | 132 | 08:00
| Kaptai | N/A | N/A | N/A | N/A | Tongi | 135 | 07:00 | 131 | 12:00
| Kazla | 133 | 06:00 | 128 | 12:00 | Ullon | 133 | 06:00 | 128 | 12:00
| Keranigonj | 133 | 04:00 | 129 | 12:00 | Uttara | 137 | 18:30 | 132 | 08:00
| Khagrachori | 136 | 00:00 | 130 | 03:00 | UttaraNew | 137 | 18:30 | 132 | 08:00
| Khulna | 140 | 18:30 | 133 | 07:00 | Zigatola | 133 | 00:00 | 121 | 11:00
| Khulna(S) | 140 | 18:30 | 135 | 07:00
| Khulshi | 135 | 17:00 | 130 | 02:00
| Kishoreganj | 132 | 18:00 | 123 | 00:00
| Kodda | 138 | 11:00 | 131 | 17:00
| KSRM | 136 | 14:00 | 131 | 02:00
| Kulaura | 135 | 01:00 | 132 | 20:00
| Kurigram | 132 | 11:00 | 116 | 02:00
| Kushtia | 133 | 11:00 | 128 | 20:00

## L-Curve
Date | 2023-07-11
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 430 | 8110 | 5065 | 13175 |  |  |  | QF-LDC-11
0:30 | 415 | 7825 | 4965 | 12790 | Date: | 2023-07-11
1:00 | 400 | 7540 | 4865 | 12405
1:30 | 370 | 7507 | 4814.5 | 12321.5
2:00 | 340 | 7474 | 4764 | 12238
2:30 | 245 | 7439.5 | 4749.5 | 12189 | [5 empty] | Gen. at Eve. Peak | 14691 | 14691 MW (21:00 )
3:00 | 150 | 7405 | 4735 | 12140 | [6 empty] | 21:00
3:30 | 134 | 7377.5 | 4726 | 12103.5 | [5 empty] | Gen. at Day Peak | 12178 | 12178 MW (12:00 )
4:00 | 118 | 7350 | 4717 | 12067 | [6 empty] | 12:00
4:30 | 99 | 7325.5 | 4704 | 12029.5 | [5 empty] | Highest Generation | 14691
5:00 | 80 | 7301 | 4691 | 11992 | [6 empty] | 21:00
5:30 | 85 | 7181.5 | 4691.5 | 11873
6:00 | 90 | 7062 | 4692 | 11754
6:30 | 68 | 7094 | 4620.5 | 11714.5
7:00 | 46 | 7126 | 4549 | 11675
7:30 | 188 | 7136.5 | 4551.5 | 11688
8:00 | 330 | 7147 | 4554 | 11701
8:30 | 357 | 7148 | 4446 | 11594
9:00 | 384 | 7149 | 4338 | 11487
9:30 | 472 | 7184 | 4406.5 | 11590.5
10:00 | 560 | 7219 | 4475 | 11694
10:30 | 670 | 7263.5 | 4532 | 11795.5
11:00 | 780 | 7308 | 4589 | 11897
11:30 | 750 | 7406.5 | 4631 | 12037.5
12:00 | 720 | 7505 | 4673 | 12178
12:30 | 690 | 7499 | 4655.5 | 12154.5
13:00 | 660 | 7493 | 4638 | 12131
13:30 | 730 | 7428.5 | 4623 | 12051.5
14:00 | 800 | 7364 | 4608 | 11972
14:30 | 716 | 7482 | 4606.5 | 12088.5
15:00 | 632 | 7600 | 4605 | 12205
15:30 | 606 | 7517.5 | 4534.5 | 12052
16:00 | 580 | 7435 | 4464 | 11899
16:30 | 658 | 7431.5 | 4462 | 11893.5
17:00 | 736 | 7428 | 4460 | 11888
17:30 | 686 | 7461 | 4478.5 | 11939.5
18:00 | 636 | 7494 | 4497 | 11991
18:30 | 668 | 7905 | 4760 | 12665
19:00 | 700 | 8316 | 5023 | 13339
19:30 | 642 | 8719 | 5190 | 13909
20:00 | 290 | 9035 | 5257 | 14292 |  |  |  | Executive Engineer
20:30 | 280 | 9126.5 | 5365 | 14491.5 |  |  |  | Network Operation Division
21:00 | 270 | 9218 | 5473 | 14691
21:30 | 245 | 9164 | 5468.5 | 14632.5
22:00 | 220 | 9110 | 5464 | 14574 |  |  |  |  | Page 6 of 7
22:30 | 270 | 8832 | 5374.5 | 14206.5
23:00 | 320 | 8554 | 5285 | 13839
23:30 | 375 | 8332 | 5175 | 13507
24:00 | 430 | 8110 | 5065 | 13175
14691 MW (21:00 )
12178 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-07-11 |  | Energy |  | 301361060
QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 4136 | 797 | 2307 | 387 | 2727 | 1826 | 60 | 297 | 474 | 160 | 0 | 4 | 1313.125
0:30 | 4050.5 | 852.5 | 2347.5 | 423 | 2349.5 | 1830.5 | 60 | 323.5 | 397.5 | 147 | 0 | 8.5 | 1274.925 |  | Date: | 43656
1:00 | 3965 | 908 | 2388 | 459 | 1972 | 1835 | 60 | 350 | 321 | 134 | 0 | 13 | 1236.725
1:30 | 3971 | 908.5 | 2389 | 437 | 1927 | 1834.5 | 60 | 350 | 301 | 135 | 0 | 8.5 | 1220.9675 | [8 empty] | Total Energy | 301.3611 | 301.3611 | Total Energy Gen 301.361 MKWHr Energy Not Served 21.462 MKWHr Energy Requirement 322.823 MKWHr
2:00 | 3977 | 909 | 2390 | 415 | 1882 | 1834 | 60 | 350 | 281 | 136 | 0 | 4 | 1205.21 | [8 empty] | Energy not Served | 21.4622 | 21.4622
2:30 | 3979 | 909 | 2381 | 382.5 | 1869 | 1835.5 | 60 | 350 | 281 | 138 | 0 | 4 | 1180.38 | [8 empty] | Energy Requirement | 322.8232 | 322.8232
3:00 | 3981 | 909 | 2372 | 350 | 1856 | 1837 | 60 | 350 | 281 | 140 | 0 | 4 | 1155.55
3:30 | 3980 | 909 | 2372 | 314 | 1851 | 1839.5 | 60 | 347.5 | 281 | 142 | 0 | 7.5 | 1094.9075 | [7 empty] | Shortage
4:00 | 3979 | 909 | 2372 | 278 | 1846 | 1842 | 60 | 345 | 281 | 144 | 0 | 11 | 1034.265
4:30 | 3962 | 908.5 | 2375.5 | 264 | 1844 | 1841 | 60 | 345 | 281 | 143 | 0 | 5.5 | 974.5775
5:00 | 3945 | 908 | 2379 | 250 | 1842 | 1840 | 60 | 345 | 281 | 142 | 0 | 0 | 914.89
5:30 | 3862.5 | 909 | 2371 | 227.5 | 1836.5 | 1837.5 | 60 | 345 | 281 | 138 | 5 | 0 | 718.16
6:00 | 3780 | 910 | 2363 | 205 | 1831 | 1835 | 60 | 345 | 281 | 134 | 10 | 0 | 521.43
6:30 | 3808 | 909.5 | 2358 | 208 | 1823.5 | 1828 | 60 | 277.5 | 268.5 | 131 | 39.5 | 3 | 361.4675 | [6 empty] | Coal
7:00 | 3836 | 909 | 2353 | 211 | 1816 | 1821 | 60 | 210 | 256 | 128 | 69 | 6 | 201.505
7:30 | 3830.5 | 909 | 2333 | 234.5 | 1832.5 | 1815 | 60 | 205 | 255.5 | 128 | 79 | 6 | 206.7575 | [5 empty] | Oil
8:00 | 3825 | 909 | 2313 | 258 | 1849 | 1809 | 60 | 200 | 255 | 128 | 89 | 6 | 212.01
8:30 | 3841 | 909.5 | 2299 | 129 | 1878 | 1820.5 | 60 | 137.5 | 254.5 | 124 | 134 | 7 | 541.9625
9:00 | 3857 | 910 | 2285 | 0 | 1907 | 1832 | 60 | 75 | 254 | 120 | 179 | 8 | 871.915
9:30 | 3841 | 909.5 | 2269.5 | 10 | 1938.5 | 1823.5 | 60 | 137.5 | 257 | 125 | 213 | 6 | 964.0725
10:00 | 3825 | 909 | 2254 | 20 | 1970 | 1815 | 60 | 200 | 260 | 130 | 247 | 4 | 1056.23
10:30 | 3782.5 | 909 | 2261.5 | 70 | 2035 | 1810.5 | 60 | 190 | 286 | 133 | 254.5 | 3.5 | 1126.4225
11:00 | 3740 | 909 | 2269 | 120 | 2100 | 1806 | 60 | 180 | 312 | 136 | 262 | 3 | 1196.615
11:30 | 3740.5 | 909.5 | 2272.5 | 282.5 | 2098 | 1815.5 | 60 | 180 | 313.5 | 142 | 222 | 1.5 | 1181.8125
12:00 | 3741 | 910 | 2276 | 445 | 2096 | 1825 | 60 | 180 | 315 | 148 | 182 | 0 | 1167.01
12:30 | 3721.5 | 910 | 2276 | 429.5 | 2116 | 1828 | 60 | 180 | 317 | 150 | 165 | 1.5 | 1169.875
13:00 | 3702 | 910 | 2276 | 414 | 2136 | 1831 | 60 | 180 | 319 | 152 | 148 | 3 | 1172.74
13:30 | 3702 | 910 | 2276 | 414 | 2136 | 1831 | 60 | 180 | 319 | 152 | 148 | 3 | 1172.74
14:00 | 3702 | 910 | 2276 | 414 | 2136 | 1831 | 60 | 180 | 319 | 152 | 148 | 3 | 1172.74
14:30 | 3754.5 | 910 | 2252.5 | 401 | 2164.5 | 1829.5 | 60 | 190 | 330.5 | 149 | 122.5 | 4 | 1228.6075
15:00 | 3807 | 910 | 2229 | 388 | 2193 | 1828 | 60 | 200 | 342 | 146 | 97 | 5 | 1284.475
15:30 | 3833 | 909.5 | 2190 | 194 | 2262 | 1831 | 60 | 200 | 336 | 137 | 93 | 6.5 | 1358.965
16:00 | 3859 | 909 | 2151 | 0 | 2331 | 1834 | 60 | 200 | 330 | 128 | 89 | 8 | 1433.455
16:30 | 3891 | 909.5 | 2125 | 0 | 2365.5 | 1830 | 60 | 160 | 343.5 | 133 | 68 | 8 | 1343.2075
17:00 | 3923 | 910 | 2099 | 0 | 2400 | 1826 | 60 | 120 | 357 | 138 | 47 | 8 | 1252.96
17:30 | 3800.5 | 910 | 2047.5 | 0 | 2516 | 1832.5 | 60 | 150 | 441.5 | 137 | 35.5 | 9 | 1084.4025
18:00 | 3678 | 910 | 1996 | 0 | 2632 | 1839 | 60 | 180 | 526 | 136 | 24 | 10 | 915.845
18:30 | 3700.5 | 910 | 2096 | 13 | 3084 | 1840.5 | 60 | 205 | 583 | 150 | 12 | 11 | 845.175
19:00 | 3723 | 910 | 2196 | 26 | 3536 | 1842 | 60 | 230 | 640 | 164 | 0 | 12 | 774.505
19:30 | 3950 | 909 | 2238 | 41 | 3739 | 1839 | 60 | 285 | 691 | 144 | 0 | 13 | 513.79
20:00 | 4047 | 815 | 2357 | 147 | 3768 | 1838 | 60 | 405 | 689 | 152 | 0 | 14 | 253.075
20:30 | 4034 | 814.5 | 2347 | 321 | 3813.5 | 1840.5 | 60 | 405 | 690.5 | 153 | 0 | 12.5 | 236.5375
21:00 | 4021 | 814 | 2337 | 495 | 3859 | 1843 | 60 | 405 | 692 | 154 | 0 | 11 | 220
21:30 | 4020.5 | 806 | 2315.5 | 497.5 | 3830.5 | 1835.5 | 60 | 405.5 | 691.5 | 160 | 0 | 10 | 265.665
22:00 | 4020 | 798 | 2294 | 500 | 3802 | 1828 | 60 | 406 | 691 | 166 | 0 | 9 | 311.33
22:30 | 4014 | 797.5 | 2298 | 474 | 3524 | 1825.5 | 60 | 350.5 | 690.5 | 166 | 0 | 6.5 | 566.7925
23:00 | 4008 | 797 | 2302 | 448 | 3246 | 1823 | 60 | 295 | 690 | 166 | 0 | 4 | 822.255
23:30 | 4072 | 797 | 2304.5 | 417.5 | 2986.5 | 1824.5 | 60 | 296 | 582 | 163 | 0 | 4 | 1067.69 |  | Max Temp. in Dhaka |  | 33.4° C
24:00 | 4136 | 797 | 2307 | 387 | 2727 | 1826 | 60 | 297 | 474 | 160 | 0 | 4 | 1313.125
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 301.361 MKWHr Energy Not Served 21.462 MKWHr Energy Requirement 322.823 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-07-11
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 1066380
2 | Karnaphuli Hydro PP Unit-4 & 5 | [12 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 344000
3 | Chattogram TPP-1 | 105 | 106 | 107 | 105 | 105 | 108 | 109 | 107 | 107 | 110 | 105 | 105 | 100 | 105 | 102 | 102 | 105 | 108 |  | 108 | 107 | 108 | 108 | 105 | 105 | 105 | 2500000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 13 | 17 |  | 17 | 17 | 17 | 17 | 17 | 8 | 8 | 250846
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 2 | 10 | 5 | 10 | 12 | 15 | 20 | 18 | 6 | 8 | 3 | 1 | [8 empty] | 105840
6 | Sikalbaha 225MW CCPP (Gas) | 223 | 224 | 225 | 226 | 226 | 228 | 226 | 226 | 223 | 221 | 223 | 219 | 220 | 220 | 220 | 220 | 222 | 220 |  | 225 | 225 | 217 | 225 | 225 | 225 | 222 | 5415497
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 32 | 32 | 32 | 30 | 32 | 32 | 32 | 32 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 788558
12 | Hathazari 100 MW peaking PP | 66 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 20 | 24 |  | 32 | 32 | 36 | 48 | 48 | 47 | 47 | 802704
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 57 | 55 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1513818
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 36 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 37 | 37 | 36 | 30 | 26 | 24 | 35 | 35 | 35 | 37 |  | 37 | 45 | 44 | 45 | 44 | 44 | 44 | 901040
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 32 | 32 | 30 | 30 | 29 | 29 | 34 | 36 | 35 | 29 | 0 | [14 empty] | 0 | 384000
17 | Siddhirganj 335 MW CCPP | 326 | 327 | 327 | 327 | 328 | 327 | 324 | 321 | 322 | 322 | 327 | 331 | 335 | 322 | 319 | 320 | 322 | 260 |  | 260 | 322 | 327 | 315 | 277 | 257 | 246 | 7543167
18 | Kodda 300 MW PP Unit-2 (Summit) | 275 | 288 | 293 | 296 | 293 | 296 | 293 | 293 | 293 | 291 | 260 | 265 | 273 | 278 | 275 | 292 | 292 | 291 |  | 292 | 292 | 292 | 292 | 288 | 293 | 288 | 6877418
19 | Ashuganj 195 MW PP (APSCL-United) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 6 | 6 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 936727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 105 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2716594
23 | Ghorasal TPP Unit-5 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4126500
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 45 | 45 | 46 | 46 | 46 | 46 | 43 | 45 | 44 | 44 | 42 | 43 | 41 | 41 | 42 | 42 | 42 | 42 |  | 43 | 44 | 45 | 45 | 45 | 45 | 45 | 1041120
33 | Ashuganj 225 MW CCPP | 209 | 210 | 210 | 210 | 210 | 210 | 211 | 212 | 207 | 207 | 209 | 206 | 207 | 203 | 157 | 154 | 184 | 209 |  | 208 | 211 | 209 | 211 | 211 | 203 | 188 | 4869000
34 | Ashuganj 450 MW CCPP(South) | [25 empty] | 0 | 0
| Ashuganj 450 MW CCPP(North) | 285 | 280 | 280 | 280 | 280 | 280 | 310 | 320 | 330 | 335 | 305 | 320 | 305 | 305 | 315 | 305 | 280 | 280 |  | 300 | 305 | 335 | 310 | 305 | 305 | 340 | 7802600
| Ashuganj 420 MW CCPP(East) | 293 | 292 | 292 | 292 | 293 | 292 | 322 | 331 | 369 | 373 | 322 | 325 | 321 | 322 | 295 | 292 | 292 | 254 |  | 298 | 317 | 330 | 317 | 317 | 317 | 376 | 7630300
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 401 | 400 | 401 | 400 | 401 | 400 | 400 | 401 | 401 | 402 | 402 | 401 | 409 | 410 | 403 | 403 | 403 | 341 |  | 327 | 400 | 397 | 401 | 400 | 400 | 401 | 9644030
40 | Meghnaghat 450 MW CCPP(MPL) | 420 | 410 | 400 | 410 | 410 | 410 | 420 | 420 | 420 | 420 | 430 | 450 | 450 | 450 | 450 | 430 | 400 | 400 |  | 340 | 400 | 400 | 400 | 400 | 380 | 380 | 9124000
41 | Haripur 360 MW CCPP(HPL) | 327 | 346 | 343 | 332 | 332 | 332 | 332 | 327 | 321 | 322 | 333 | 330 | 331 | 330 | 322 | 322 | 302 | 282 |  | 330 | 331 | 333 | 301 | 272 | 272 | 266 | 7662000
42 | RPCL 210MW CCPP | 32 | 32 | 32 | 31 | 31 | 31 | 31 | 12 | 10 | 8 | 10 | 10 | 10 | 10 | 10 | 12 | 18 | 21 |  | 23 | 23 | 23 | 30 | 34 | 34 | 34 | 493440
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 12 | 20 | 30 | 20 | 23 | 13 | 19 | 1 | 8 | 2 | 1 | 1 | [8 empty] | 174060
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1024000
45 | Fenchugonj CCPP Phase-2 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 38 | 39 | 38 | 39 | 39 | 39 | 39 | 39 |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 901680
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 55 | 55 | 59 | 59 | 59 | 61 | 60 | 60 | 60 | 59 | 60 | 59 | 60 | 60 | 60 | 60 | 60 | 60 |  | 61 | 61 | 60 | 60 | 61 | 61 | 60 | 1429056
48 | Shahjibazar 86 MW PP (Shahjibazar) | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 84 | 86 | 86 | 86 | 86 | 86 | 86 | 84 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 2043840
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 207 | 207 | 207 | 207 | 206 | 206 | 206 | 207 | 207 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 203 |  | 204 | 204 | 207 | 207 | 207 | 207 | 207 | 5141840
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 390000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 246420
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120960
55 | Fenchugonj 51 MW PP (Barakatullah) | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 44 | 44 | 45 | 45 | 46 | 46 | 46 | 1050000
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 16 | 16 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 534720
57 | Bibiana-II 341 MW CCPP (Summit) | 320 | 310 | 305 | 300 | 305 | 290 | 300 | 300 | 310 | 310 | 305 | 310 | 310 | 295 | 310 | 305 | 290 | 270 |  | 270 | 260 | 290 | 300 | 290 | 300 | 310 | 7358000
| Bibiyana South 400 MW | 354 | 360 | 360 | 360 | 360 | 351 | 355 | 355 | 358 | 348 | 366 | 350 | 355 | 350 | 350 | 350 | 350 | 360 |  | 354 | 345 | 354 | 364 | 355 | 355 | 355 | 8479900
58 | Nababganj 55 MW PP (Southern power ) | [8 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 55 | 35 |  | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 663461
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 9 | 12 | 295440
60 | Barabkunda 22 MW PP (Regent) | 11 | 11 | 11 | 11 | 11 | 11 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 8 | 8 | 8 | 242016
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 17 | 17 | 17 | 19 | 0 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 400428
62 | Tangail 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 425988
63 | Impoprt (Tripura) | 134 | 136 | 140 | 144 | 142 | 134 | 128 | 128 | 120 | 130 | 136 | 148 | 152 | 132 | 146 | 128 | 138 | 136 |  | 164 | 144 | 152 | 154 | 166 | 166 | 160 | 3352320
64 | Malancha, Ctg. EPZ (United) | 34 | 34 | 34 | 35 | 36 | 36 | 32 | 8 | 2 | 2 | 2 | 2 | 6 | 4 | 2 | 2 | 13 | 11 |  | 20 | 22 | 25 | 28 | 29 | 32 | 25 | 484320
65 | Feni 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 464212
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 226440
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 29 | 23 | 29 | 33 | 32 | 32 | 32 | 32 | 32 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 791700
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 14 | 14 | 14 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 462920
69 | Summit Ashulia | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 480000
70 | Summit Madhabdi | 14 | 22 | 22 | 22 | 22 | 22 | 21 | 18 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 478800
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 595500
72 | Rupganj 33 MW PP(Summit) | 21 | 21 | 21 | 22 | 22 | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 21 | 21 | 21 | 479400
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 70 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 52 | 88 | 88 | 106 | 106 | 106 | 106 | 950760
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 9 | 37 |  | 65 | 65 | 66 | 66 | 68 | 25 | 12 | 466200
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 54 | 54 | 54 | 54 | 72 | 72 | 72 |  | 162 | 162 | 144 | 162 | 162 | 162 | 54 | 1562400
77 | Siddhirganj 100 PP(Dutch Bangla) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 58 | 58 | 58 | 58 | 50 | 36 | 34 | 1110720
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 288960
79 | Kodda 150 MW PP | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 115 |  | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 2242560
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 34 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1006642
| Gazipur 100 MW PP | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 2118720
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 4 | 4 | 3 | 3 | 3 | 2 | 2 | 2 | 1 | [9 empty] | 24238
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 22 | 35 | 35 | 35 | 36 | 528769
| Karnaphuli Power Ltd. | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 60 | 1287994
82 | Madanganj 102 PP(Summit) | 74 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 60 | 63 | 66 | 80 | 80 | 81 | 81 | 1789962
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 12 | 11 | 11 | 12 | 12 | 12 | 12 | 12 | 23 | 22 | 22 | 11 | 11 | 11 | 11 | 12 | 22 | 22 |  | 21 | 21 | 22 | 22 | 22 | 21 | 22 | 401576
86 | Meghnaghat CCPP ( Summit) | 314 | 313 | 312 | 313 | 314 | 315 | 305 | 307 | 308 | 305 | 305 | 299 | 312 | 306 | 283 | 281 | 272 | 255 |  | 300 | 265 | 308 | 291 | 283 | 294 | 304 | 7269004
87 | Meghnaghat 100 MW(IEL) | 33 | 42 | 42 | 42 | 42 | 43 | 42 | 42 | 42 | 39 | 41 | 41 | 43 | 49 | 50 | 65 | 67 | 74 |  | 72 | 75 | 73 | 74 | 70 | 50 | 50 | 1218240
| Meghnaghat 104 MW PP (OPCL) | 36 | 36 | 50 | 54 | 54 | 36 | 36 | 50 | 54 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 56 |  | 70 | 72 | 72 | 72 | 72 | 68 | 54 | 1301760
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 46 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 58 | 1368000
92 | Fenchuganj 44 MW (Energyprima) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 1135296
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 983318
94 | Gagnagar 102 MW PP (Digital Power) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 |  | 92 | 101 | 101 | 101 | 101 | 101 | 25 | 1236672
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 28 | 33 | 42 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 549600
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 10 | 10 | 13 | 15 | 9 | 9 | 11 | 14 |  | 22 | 26 | 27 | 30 | 30 | 0 | 0 | 211200
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 41 | 1323533
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 657648
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 80 | 80 |  | 80 | 80 | 112 | 112 | 112 | 112 | 112 | 2559272
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | [8 empty] | 9400
103 | Kamalaghat 54 MW PP(Banco Energy) | [10 empty] | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 521640
104 | Keranigonj 300 MW PP (APR) | 259 | 242 | 200 | 150 | 150 | 105 | 105 | 108 |  | 20 | 53 | 245 | 214 | 55 | 208 |  |  |  |  | 24 | 21 | 125 | 295 | 300 | 248 | 187 | 3370597
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 69 | 87 | 88 | 88 | 78 | 78 | 78 |  | 96 | 96 | 98 | 108 | 98 | 69 | 68 | 1855200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 117 | 125 | 132 | 133 | 133 | 133 | 133 | 133 | 133 | 133 | 133 | 132 | 132 | 132 | 132 | 131 | 131 | 132 |  | 132 | 132 | 132 | 132 | 132 | 134 | 148 | 3195216
115 | Juldah 100 MW PP Unit-3 (Acorn) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 60 | 87 | 87 | 87 | 87 | 88 | 50 | 1421760
116 | Chandpur 200 MW (Desh energy) | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 37 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 78 | 100 | 103 | 104 | 104 | 104 | 63 | 1174560
117 | Ashuganj 150 MW PP (Midland) | 5 | 6 | 6 | 5 | 6 | 6 | 5 | 6 | 5 | 5 | 6 | 5 | 5 | 6 | 5 | 5 | 5 | 10 |  | 60 | 120 | 115 | 135 | 132 | 25 | 5 | 580436
118 | Bibiyana-III 400 MW CCPP | 280 | 280 | 280 | 280 | 240 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 115 | 244 | 312 | 349 | 306 |  | 316 | 366 | 408 | 366 | 366 | 366 | 415 | 5458000
| Jamalpur 115 MW PP (United) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 75 | 85 | 85 | 85 | 85 | 19 | 19 | 684000
| Anwara 300 MW PP (United) | 86 | 87 | 87 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 102 | 88 | 120 |  | 274 | 274 | 280 | 280 | 280 | 123 | 124 | 2950691
| Juldah unit-2 (Acorn) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 76 | 76 | 76 | 76 | 76 | 76 | 50 | 1319040
| Anlima Energy Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 34 | 34 | 34 | 43 | 51 | 51 | 51 | 55 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 1195582
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 441000
| Spectra Solar Plant Ltd. | [5 empty] | 2 | 6 | 3 | 17 | 32 | 36 | 28 | 7 | 17 | 26 | 17 | 10 | 3 | [8 empty] | 186430
| Chandpur 115(Doreen) | 95 | 94 | 54 | 35 | 33 | 36 | 36 | 36 | 46 | 57 | 57 | 57 | 57 | 57 | 61 | 75 | 76 | 94 |  | 115 | 115 | 115 | 115 | 115 | 115 | 58 | 1687680
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 29 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 17 | 554400
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 23 | 53 | 53 | 53 | 53 | 53 | 36 | 53 | 159 |  | 160 | 160 | 160 | 160 | 160 | 160 | 90 | 1557309
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 13 | 4 | 4 | 11 | 0 | 0 | 6 | 6 | 8 | 4 | 3 | 0 | 3 | 11 | 5 | 8 | 8 | 10 |  | 12 | 13 | 14 | 11 | 9 | 4 | 4 | 130560
120 | Eastern Zone Total | 7540 | 7474 | 7405 | 7350 | 7301 | 7062 | 7126 | 7147 | 7149 | 7219 | 7308 | 7505 | 7493 | 7364 | 7600 | 7435 | 7428 | 7494 |  | 8316 | 8719 | 9035 | 9218 | 9110 | 8554 | 8110 | 185163545
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 31 | 31 | 32 | 32 | 32 | 32 | 32 |  | 89 | 96 | 95 | 95 | 95 | 82 | 32 | 882240
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL) | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 75 | 200 | 180 | 180 | 180 | 180 | 180 | 180 | 80 | 80 |  | 80 | 115 | 200 | 200 | 200 | 75 | 75 | 3935760
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 15 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 10 | 11 | 11 | 11 | 12 | 18 | 28 |  | 29 | 33 | 27 | 25 | 25 | 25 | 16 | 344640
| Khulna 225 MW CCPP | 150 | 150 | 150 | 145 | 145 | 145 | 10 | 0 | [5 empty] | 10 | 20 | 20 | 40 | 100 |  | 150 | 170 | 205 | 205 | 206 | 220 | 222 | 2323379
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 35 | 847200
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 4 | 14 | 17 | 37 | 75 | 38 | 44 | 21 | 37 | 36 | 47 | 23 | 9 | [7 empty] | 0 | 385200
131 | Rampal 1320 MW (BIFPCL) | 374 | 371 | 374 | 378 | 376 | 376 | 374 | 380 | 375 | 374 | 371 | 365 | 374 | 374 | 374 | 374 | 375 | 376 |  | 375 | 374 | 374 | 374 | 375 | 375 | 375 | 8952727
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 1212000
133 | Bhola Nutan Biddut BD LTD (GAS) | 226 | 226 | 226 | 226 | 226 | 226 | 226 | 226 | 226 | 226 | 226 | 226 | 226 | 222 | 223 | 220 | 220 | 163 |  | 220 | 220 | 220 | 220 | 220 | 225 | 224 | 5299827
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 83 | 83 | 83 | 83 | 83 | 94 | 96 |  | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 2091648
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 134 | 134 | 132 | 132 | 136 | 136 | 136 | 133 | 130 | 130 | 80 |  | 135 | 135 | 135 | 136 | 136 | 134 | 136 | 3120000
140 | Bhola 33 MW PP (Venture) | 35 | 34 | 33 | 31 | 31 | 28 | 25 | 23 | 20 | 21 | 21 | 23 | 24 | 24 | 25 | 24 | 22 | 22 |  | 29 | 32 | 32 | 32 | 34 | 35 | 34 | 662930
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | [17 empty] | 16 | 16 | 24 | 24 | 24 | 0 | 0 | 92250
143 | Gopalganj 100 MW Peaking PP | 45 | 45 | 45 | 45 | 45 | 45 | 20 | 20 | 20 | 20 | 20 | 30 | 32 | 22 | 22 | 23 | 23 | 36 |  | 64 | 67 | 68 | 60 | 60 | 60 | 50 | 890624
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 67 |  | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 757584
146 | Bheramara HVDC | 908 | 909 | 909 | 909 | 908 | 910 | 909 | 909 | 910 | 909 | 909 | 910 | 910 | 909 | 910 | 909 | 910 | 910 |  | 910 | 909 | 815 | 814 | 798 | 797 | 797 | 21659636
147 | Bheramara 410 MW CCPP | 105 | 105 | 105 | 105 | 110 | 110 | 110 | 105 | 105 | 100 | 100 | 100 | 95 | 90 | 80 | 80 | 80 | 80 |  | 105 | 115 | 125 | 130 | 170 | 175 | 180 | 2721888
148 | Payra 1320 MW | 622 | 622 | 622 | 622 | 622 | 622 | 622 | 622 | 622 | 600 | 600 | 622 | 622 | 622 | 622 | 622 | 622 | 622 |  | 622 | 622 | 622 | 622 | 610 | 600 | 600 | 15744700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 220 | 220 | 220 | 220 | 220 | 211 | 200 | 200 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5258500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [13 empty] | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 358400
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 3 | 5 | 1 | 1 | 0 | 0 | 0 | [8 empty] | 23340
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 125 | 126 | 124 | 123 | 123 | 123 | 123 | 124 | 121 | 122 | 121 | 121 | 120 | 119 | 119 | 120 | 123 | 115 |  | 0 | [5 empty] | 0 | 2386145
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 125 | 125 | 125 | 126 | 126 | 126 | 126 | 124 | 121 | 120 | 118 | 118 | 117 | 115 | 117 | 117 | 120 | 122 |  | 128 | 134 | 137 | 166 | 175 | 180 | 183 | 3392382
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 314 | 319 | 321 | 327 | 327 | 328 | 315 | 304 | 280 | 258 | 253 | 241 | 222 | 220 | 219 | 221 | 268 | 279 |  | 371 | 392 | 400 | 416 | 416 | 414 | 414 | 7378400
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 0 | 8 |  |  |  | 8 | 8 | 143370
165 | Amnura 50 MW PP(Sinha) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 21 | 28 | 28 |  | 28 | 28 | 28 | 21 | 21 | 21 | 21 | 621940
166 | Katakhali 50 MW PP (Northern) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 42 | 42 | 50 | 50 | 42 | 42 | 42 | 837709
167 | Katakhali 50 MW Peaking PP | 26 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 24 | 24 | 25 |  | 21 | 26 | 26 | 26 | 26 | 26 | 26 | 520600
168 | Santahar 50 MW Peaking PP | [10 empty] | 25 | 25 | 30 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 0 | 391911
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 34099
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 61 | 92 | 92 | 92 | 92 | 92 | 0 | 435272
171 | Baghabari 200 MW PP (Paramount) | 200 | 173 | 150 | 128 | 100 | 100 | 106 | 150 |  | 0 | 67 | 200 | 200 | 180 | 180 |  |  |  |  | 2 | 20 | 22 | 200 | 200 | 200 | 200 | 2945589
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1086816
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1094208
173 | Rangpur 20 MW GTPP | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 27 | 27 | 34 | 34 | 34 | 69 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 34 | 1064140
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 0 | 1 | 2 | 2 | 5 | 4 | 5 | 4 | 4 | 2 | 1 | [8 empty] | 28904
178 | Energypac Power Venture Thakurgaon Ltd. | 70 | [9 empty] | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 97 | 97 | 114 | 114 | 92 | 55 | 55 | 852864
| Intraco Solar 30 MW | [6 empty] | 2 | 6 | 7 | 27 | 11 | 6 | 5 | 10 | 10 | 0 | 1 | 0 |  | 0 | [6 empty] | 78515
| Adani Power Jharkhanda Ltd | 619 | 621 | 621 | 622 | 622 | 626 | 625 | 607 | 615 | 621 | 615 | 618 | 615 | 616 | 612 | 618 | 609 | 621 |  | 625 | 623 | 622 | 627 | 623 | 628 | 631 | 14901818
178 | Teesta Solar Limited | [5 empty] | 2 | 32 | 30 | 76 | 74 | 134 | 64 | 63 | 1 | 3 | 8 | 6 | 9 | [8 empty] | 438360