## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-07-16 | Sunday
|  | Date (day): | 2023-07-16 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13419.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15540 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-07-15 | 2023-07-16 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 160 | 160 | 160 | 160
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 406 | 400 | 400 | 412
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 332 | 326 | 330 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 27 | 68 | 50 | 70 | 30 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 306 | 286 | 280 | 290 | 45 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 75 | 80 | 80 | 80 |  | 22 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 11 | 11 | 22 | 53 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  | 3 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 96 | 194 | 150 | 200 | 10 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 50 | 75 | 58 | 75 | 25 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 330 | 300 | 330
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 83 | 48 | 83 |  | 19 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 64 | 130 | 82 | 130 | 19 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 34 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 40 | 40 | 40 | 41 |  | 39 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 22 | 22 | 22 | 22 |  | 11 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 25 | 8 | 25 | 27 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 107 | 183 | 112 | 145 | 155 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
33 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
34 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 23 | 149 | 34 | 149
35 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 88 | 88 | 88 |  | 17 | Engine problem
36 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 105 | 36 | 54 | 55 | 49 |  | Fuel shortage
37 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 72 | 144 | 72 | 144 |  | 18 | Engine problem
38 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 36 | 0 | 30 | 0
39 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 30 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6163 | 5822 | 3119 | 3720 | 3541 | 4061 | 745 | 897
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
41 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 17 | 8 | 17 |  | 8 | Engine problem
42 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 15 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 46 | 6 | 50
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 60 | 60 | 30 | 60 | 200 |  | Low Water Level
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 222 | 226 | 225 | 225
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 17 | 34 | 71 |  | Fuel shortage
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 16 | 66 | 32 | 66 | 32 |  | Fuel shortage
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 32 | 34 | 33 | 34 | 68 |  | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 25 | 58 | 35 | 58 | 42 |  | Fuel shortage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 37 | 50 | 38 | 50 | 50 |  | Fuel shortage
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 10 | 10 | 10 | 10 | 12 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 6 | 20 | 10 | 20
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 25 | 12 | 25 | 83 |  | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 87 | 279 | 88 | 280 |  | 20 | Engine problem
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 36 | 17 | 36 | 18 |  | Fuel shortage
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 34 | 34 | 34 | 34 | 76 |  | Fuel shortage
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 38 | 50 | 38 | 50 | 50 |  | Fuel shortage
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 34 | 87 | 34 | 87 | 29 |  | Fuel shortage
60 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 53 | 163 | 54 | 163
| SS Power I |  | Coal | SS Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 0 | 0 | 15 | 10 |  |  | On test.
| Chattogram area Total |  |  |  |  | 2605 | 2545 | 820 | 1378 | 861 | 1409 | 811 | 358
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 208 | 205 | 200 | 210
62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 270 | 270 | 270 | 90 |  | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 230 | 230 | 230 | 230 | 130 |  | Gas shortage
64 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 230 | 230 | 230 | 230 | 170 |  | Gas shortage
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 15 | 20 | 5 | 20 | 25 |  | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
69 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 5 | 118 | 5 | 150
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 29 | 35 | 35 | 35 |  | 17 | Machine problem
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
72 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 51 | 100 | 50 | 100 | 100 |  | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 20 | 20 | 20
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 156 | 164 | 146 | 169
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 30 | 34 | 34 | 34 | 18 |  | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Contract Expired
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 88 | 106 | 52 | 114
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 97 | 9 | 95 | 18 |  | Fuel shortage
81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 54 | 115 | 55 | 115
| Cumilla Area Total |  |  |  |  | 3159 | 3096 | 1482 | 1865 | 1472 | 1923 | 746 | 222
83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 30 | 92 | 60 | 90 | 112 |  | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 19 | 18 | 19 |  | 3 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 68 | 88 | 85 | 88 | 112 |  | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 85 | 20 | 85 | 30 |  | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 17 | 0 | 50 | 0
90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 | 10 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 166 | 296 | 246.6 | 294 | 112 | 3
91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 29 | 30 | 30 | 30 |  | 60 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 112 | 112 |  | 51 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 47 | 45 | 47
96 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 47 | 48 | 44 | 48
97 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 58 | 60 | 60
99 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 84 | 86 | 86
100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 204 | 204 | 200 | 204 |  | 27 | Machine problem
102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 17 | 17
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
103 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 20 | 20 | 24
104 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 285 | 290 | 300 | 300 |  |  | FGMO
105 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 368 | 367 | 400 | 400 |  |  | FGMO
106 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 8 | 10
107 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 392 | 260 | 250 | 260 |  | 123 | ST Under maint.
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1725 | 1601 | 1626 | 1652 | 0 | 718
108 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 909 | 766 | 920 | 920
109 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 98 | 80 | 98 |  | 17 | Engine problem
110 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 23 | 20 | 30 |  | 24 | Engine problem
111 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 222 | 150 | 225
112 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 |  | 109 | Engine problem
113 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 310 | 235 | 200 | 200 | 210 |  | Gas shortage
114 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 24 | 8 | 24 | 16 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
115 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 36 | 35 | 36 | 69 |  | Fuel shortage
116 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 105 | 50 | 105
117 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 60 | 0 | 100 | 0
118 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 220 | 220 | 0 | 0 | 200 | 200
119 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 308 | 316 | 300 | 310 |  | 307 | Turbine leakage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3125 | 3121 | 1742 | 1825 | 2063 | 2148 | 311 | 457
120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 50 | 16 | 50 | 78 |  | Fuel shortage
121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 20 | 31 | 25 | 31 |  | 9 | Engine problem
122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 130 | 137 | 135 | 137 |  | 57 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1140 | 1244 | 1244 | 1244
124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 225 | 222 | 220 | 225
125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 150 | 17 | 150
126 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 | 307 |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1532 | 1834 | 1657 | 1837 | 385 | 66
127 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
128 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 35 | 0 | 35 | 17 |  | Fuel shortage
129 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 28 | 0 | 28 |  | 43 | Engine problem
130 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 28 | 28 | 28
131 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 42 | 42 | 42 |  | 8 | Engine problem
132 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 29 | 22 | 29 |  | 21 | Engine problem
133 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Under maint
134 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 170 | 183 | 170 | 180 | 40 |  | Gas shortage
136 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 417 | 427 | 400 | 414
137 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 27 | 0 | 30 | 20 |  | Fuel shortage
138 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 50 | 52
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 93 | 0 | 93 | 11 |  | Fuel shortage
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 150 | 200
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 50 | 35 | 50 | 63 |  | Fuel shortage
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 57 | 35 | 55 | 58 |  | Fuel shortage
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 748*1 | 748 | 748 | 616 | 607 | 600 | 610
| Rajshahi Area Total |  |  |  |  | 2927 | 2905 | 1283 | 1666 | 1546 | 1854 | 600 | 285
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 77 | 34 | 77 | 36 |  | Fuel shortage
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 36 | 113 | 35 | 115
153 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 35 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 69 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 350 | 360 | 407 | 362 | 161 | 85
| Total |  |  |  |  | 24263 | 23545 | 12219 | 14545 | 13419.6 | 15540 | 3871 | 3091
A. |  | 2023-07-15 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 14545 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 10930 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14545 | MW
3 | Day peak Generation : |  |  | 12219 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14027.54 | MW
4 | Evening peak Generation : |  |  | 14545 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 298.5272 | MKWHr | By Solar | 2.3906 | MKWHr
| By Gas : | 157.7051 | MKWHr |  | By Oil: | 56.4672 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 55.7153 | MKWHr |  | By Hydro: | 1.446 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3871 | MW | Dhaka | 4917.54 | 4917.54 |  | 0 |  | 18:00 |  | 128
|  |  | For Plants S/D or M/C prob = |  |  | 3091 | MW | Chittagong | 1373.4 | 1373.4 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 6962 | MW | Khulna | 1761 | 1761 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 1227.39 | MMCFD |  |  | Rajshahi | 1495.4 | 1495.4 |  | 0 |  | 20:00 |  | 30
8 | Fuel Cost : | i) Gas : | Taka | 174287679.4 | ii) Oil : | Taka | 741206268.45 | Comilla | 1364 | 1364 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 286437537 | Total | Taka | 1201931484.85 | Mymensingh | 1128 | 1128 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 598 | 598 |  | 0 |  | 23:00 |  | 414
| ii) During Peak Demand : |  |  | 310 | MW (E to W) at | 21:00 | hrs | Barisal | 424.2 | 424.2 |  | 0 |  | 24:00 |  | 787
| iii) Maximum : |  |  | 300 | MW at | 20:00 | hrs | Rangpur | 966 | 966 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 32.7° C |  |  | Total | 14027.54 | 14027.54 |  | 0
B. |  | 2023-07-16 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 32.7° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 15200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15540 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 13000 | MW
4 | Reserve(Generation end) |  |  |  | 340 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 311.9706 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11227 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.296 | MKWHr. | ii) HVDC Flow at Peak Time |  | 766 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.5069 | MKWHr. | iii) Maximum HVDC Flow : |  | 911 | MW at | 7:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 75.2 |  | (b) Today: | 75.12 |  | (c) Rule Curve: |  | 86.24
.

## YesterdayGen
2023-07-15 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 400 | 332 |  | 0 | 450 | 292 | 74 | 82 | 55 | 335 | 0 | 99 | 75 | 99 | 82 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 21 | 25 | 24 | 8 | 0 | 30 | 30 | 94 | 0 | 8 | 228 | 0 | 0 | 0 |  | 12 | 32 | 33 | 26 | 0 | 46 | 10 | 37 | 0 | 0 | 0 | 280 | 260 | 196 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 32 | 34 | 18 | 0 | 33 | 20 | 150 | 43 | 0 | 19 | 0 | 43 | 39 | 47 | 48 | 112 | 0 | 61 | 84 | 0 | 205 | 17 | 0 | 7 | 260 | 24 | 11 | 0 | 112 | 0 | 0 | 68 | 0 | 33 | 0 | 25 | 17 | 6 | 367 | 19 | 35 | 17 | 0 | 88 | 17 | 34 | 106 | 9 | 25 | 380 | 46 | 0 | 17 | 34 | 0 | 17 | 0 | 94 | 17 | 230 | 17 | 0 | 0 | 0 |  | 909 | 0 | 300 | 0 | 65 | 226 | 0 | 0 | 11 | 0 | 8 | 120 | 32 | 32 | 0 | 0 | 0 | 0 | 21 | 0 | 21 | 34 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 430 | 35 | 0 | 35 | 105 | 34 | 0 | 0 | 35 | 1222 | 223 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 620 | 0 | 0 |  | 7369 | 5363 | 12732 | 4494 | 909 | 2405 | 0 | 1940 | 2320 | 60 | 226 | 228 | 150 | 0 | 0 | 542.44 | 75.21
2:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 400 | 333 |  | 0 | 450 | 283 | 73 | 82 | 55 | 336 | 0 | 100 | 50 | 99 | 82 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 21 | 25 | 24 | 8 | 0 | 30 | 30 | 97 | 0 | 8 | 228 | 0 | 0 | 0 |  | 12 | 0 | 33 | 26 | 0 | 46 | 10 | 37 | 0 | 0 | 0 | 280 | 260 | 197 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 36 | 34 | 20 | 0 | 33 | 20 | 144 | 43 | 0 | 19 | 0 | 43 | 39 | 47 | 48 | 112 | 0 | 61 | 84 | 0 | 205 | 17 | 0 | 7 | 260 | 24 | 11 | 0 | 112 | 0 | 0 | 68 | 0 | 34 | 0 | 25 | 17 | 5 | 367 | 19 | 35 | 17 | 0 | 88 | 17 | 34 | 52 | 9 | 25 | 385 | 54 | 0 | 17 | 34 | 0 | 17 | 0 | 86 | 17 | 230 | 17 | 0 | 0 | 0 |  | 909 | 0 | 300 | 0 | 64 | 162 | 0 | 0 | 0 | 0 | 8 | 120 | 31 | 32 | 0 | 0 | 0 | 0 | 21 | 0 | 21 | 34 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 427 | 35 | 0 | 35 | 105 | 34 | 0 | 0 | 35 | 1122 | 225 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 612 | 0 | 0 |  | 7259 | 5176 | 12435 | 4506 | 909 | 2395 | 0 | 1858 | 2212 | 60 | 162 | 189 | 144 | 0 | 0 | 348.575 | 75.21
3:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 400 | 332 |  | 0 | 450 | 282 | 74 | 82 | 55 | 335 | 0 | 100 | 42 | 74 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 21 | 25 | 24 | 8 | 0 | 30 | 30 | 99 | 0 | 8 | 228 | 0 | 0 | 0 |  | 12 | 2 | 33 | 26 | 0 | 46 | 10 | 37 | 0 | 0 | 0 | 280 | 260 | 200 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 36 | 34 | 20 | 0 | 33 | 20 | 140 | 43 | 0 | 19 | 0 | 43 | 39 | 47 | 48 | 112 | 0 | 62 | 84 | 0 | 205 | 17 | 0 | 7 | 265 | 24 | 11 | 0 | 112 | 0 | 0 | 68 | 0 | 34 | 0 | 25 | 17 | 6 | 367 | 19 | 35 | 17 | 0 | 88 | 17 | 34 | 34 | 9 | 25 | 385 | 44 | 0 | 17 | 34 | 0 | 17 | 0 | 38 | 17 | 230 | 17 | 0 | 0 | 0 |  | 909 | 0 | 305 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 110 | 30 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 419 | 35 | 0 | 35 | 67 | 34 | 0 | 0 | 35 | 1122 | 225 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 613 | 0 | 0 |  | 7136 | 4912 | 12048 | 4505 | 909 | 2389 | 0 | 1543 | 2212 | 60 | 120 | 170 | 140 | 0 | 0 | 527.16 | 75.21
4:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 399 | 332 |  | 0 | 450 | 280 | 45 | 82 | 55 | 336 | 0 | 59 | 42 | 24 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 21 | 25 | 24 | 8 | 0 | 30 | 30 | 101 | 0 | 8 | 228 | 0 | 0 | 0 |  | 12 | 16 | 33 | 25 | 0 | 46 | 10 | 42 | 0 | 0 | 0 | 280 | 260 | 202 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 36 | 34 | 20 | 0 | 33 | 20 | 140 | 43 | 0 | 19 | 0 | 43 | 39 | 47 | 48 | 112 | 0 | 62 | 84 | 0 | 206 | 17 | 0 | 7 | 270 | 24 | 11 | 0 | 45 | 0 | 0 | 68 | 0 | 34 | 0 | 25 | 17 | 5 | 367 | 19 | 35 | 17 | 0 | 88 | 17 | 34 | 17 | 9 | 25 | 385 | 47 | 0 | 17 | 34 | 0 | 17 | 0 | 36 | 17 | 230 | 17 | 0 | 0 | 0 |  | 909 | 0 | 310 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 136 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 405 | 35 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 1162 | 225 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 613 | 0 | 0 |  | 6958 | 4808 | 11766 | 4501 | 909 | 2382 | 0 | 1218 | 2252 | 60 | 120 | 184 | 140 | 0 | 0 | 509.97 | 75.2
5:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 400 | 332 |  | 0 | 400 | 311 | 42 | 28 | 15 | 300 | 0 | 61 | 19 | 24 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 21 | 25 | 24 | 8 | 0 | 30 | 30 | 99 | 0 | 8 | 227 | 0 | 0 | 0 |  | 12 | 16 | 33 | 25 | 0 | 13 | 10 | 42 | 0 | 0 | 0 | 280 | 260 | 209 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 36 | 34 | 20 | 0 | 33 | 20 | 140 | 43 | 0 | 19 | 0 | 43 | 29 | 47 | 48 | 80 | 0 | 62 | 84 | 0 | 208 | 17 | 0 | 7 | 295 | 24 | 11 | 0 | 45 | 0 | 0 | 68 | 0 | 34 | 0 | 25 | 17 | 6 | 367 | 19 | 35 | 17 | 0 | 88 | 17 | 34 | 17 | 9 | 25 | 385 | 35 | 0 | 17 | 34 | 0 | 17 | 0 | 36 | 17 | 230 | 17 | 0 | 0 | 0 |  | 910 | 0 | 315 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 136 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 407 | 35 | 0 | 35 | 0 | 25 | 0 | 0 | 35 | 1122 | 225 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 614 | 0 | 0 |  | 6731 | 4680 | 11411 | 4439 | 910 | 2357 | 0 | 987 | 2214 | 60 | 120 | 184 | 140 | 0 | 0 | 514.745 | 75.2
6:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 400 | 303 |  | 0 | 400 | 285 | 41 | 17 | 15 | 300 | 0 | 59 | 8 | 24 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 21 | 25 | 24 | 8 | 0 | 30 | 30 | 98 | 0 | 8 | 227 | 0 | 0 | 0 |  | 12 | 16 | 33 | 25 | 0 | 6 | 10 | 42 | 0 | 0 | 0 | 280 | 260 | 208 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 36 | 34 | 20 | 0 | 33 | 18 | 138 | 43 | 0 | 19 | 0 | 43 | 29 | 47 | 48 | 80 | 0 | 62 | 84 | 0 | 207 | 17 | 0 | 7 | 270 | 24 | 11 | 0 | 27 | 0 | 0 | 68 | 0 | 34 | 1 | 25 | 17 | 5 | 367 | 19 | 35 | 17 | 0 | 88 | 17 | 34 | 17 | 9 | 25 | 385 | 36 | 1 | 17 | 34 | 0 | 17 | 1 | 36 | 17 | 230 | 17 | 0 | 0 | 0 |  | 910 | 0 | 325 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 136 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 376 | 35 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 950 | 225 | 0 | 17 | 0 | 3 | 0 | 0 | 0 | 310 | 1 | 0 | 614 | 7 | 0 |  | 6579 | 4506 | 11085 | 4442 | 910 | 2243 | 0 | 948 | 2044 | 60 | 120 | 166 | 138 | 14 | 0 | 491.825 | 75.2
7:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 360 | 274 |  | 0 | 370 | 313 | 41 | 17 | 15 | 270 | 0 | 62 | 9 | 24 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 8 | 25 | 24 | 8 | 0 | 30 | 30 | 100 | 0 | 8 | 226 | 0 | 0 | 0 |  | 12 | 16 | 33 | 25 | 0 | 6 | 10 | 38 | 0 | 0 | 0 | 280 | 260 | 209 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 37 | 34 | 20 | 0 | 33 | 20 | 130 | 43 | 0 | 19 | 0 | 43 | 29 | 47 | 48 | 80 | 0 | 61 | 84 | 0 | 206 | 17 | 0 | 7 | 300 | 24 | 11 | 0 | 15 | 0 | 0 | 68 | 0 | 34 | 4 | 25 | 17 | 6 | 367 | 19 | 35 | 17 | 1 | 88 | 17 | 34 | 17 | 8 | 25 | 350 | 59 | 3 | 17 | 34 | 0 | 17 | 3 | 35 | 17 | 230 | 17 | 0 | 0 | 0 |  | 911 | 0 | 330 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 136 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 377 | 35 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 900 | 225 | 0 | 17 | 1 | 9 | 0 | 0 | 0 | 309 | 4 | 0 | 615 | 29 | 0 |  | 6473 | 4492 | 10965 | 4334 | 911 | 2236 | 0 | 959 | 1994 | 60 | 120 | 167 | 130 | 54 | 0 | 415.425 | 75.19
8:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 355 | 273 |  | 0 | 370 | 310 | 40 | 17 | 15 | 270 | 0 | 62 | 9 | 24 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 8 | 25 | 22 | 8 | 0 | 30 | 30 | 100 | 0 | 8 | 226 | 0 | 0 | 0 |  | 12 | 16 | 33 | 25 | 0 | 6 | 10 | 6 | 0 | 0 | 0 | 300 | 260 | 194 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 37 | 34 | 20 | 0 | 33 | 20 | 124 | 31 | 0 | 18 | 1 | 43 | 29 | 47 | 48 | 80 | 0 | 60 | 84 | 0 | 206 | 17 | 0 | 7 | 285 | 24 | 11 | 0 | 15 | 0 | 0 | 68 | 0 | 34 | 1 | 25 | 17 | 5 | 389 | 19 | 35 | 17 | 3 | 88 | 17 | 34 | 17 | 9 | 25 | 350 | 82 | 6 | 17 | 34 | 0 | 17 | 3 | 36 | 26 | 230 | 17 | 0 | 0 | 0 |  | 910 | 0 | 330 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 136 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 376 | 35 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 900 | 175 | 0 | 17 | 1 | 10 | 0 | 0 | 0 | 309 | 7 | 0 | 618 | 56 | 0 |  | 6457 | 4473 | 10930 | 4340 | 910 | 2132 | 0 | 991 | 1997 | 60 | 120 | 167 | 124 | 89 | 0 | 448.85 | 75.19
9:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 358 | 272 |  | 0 | 370 | 288 | 41 | 22 | 18 | 270 | 0 | 97 | 9 | 24 | 64 | 0 | 0 | 0 | 0 | 0 | 17 | 10 | 19 | 19 | 8 | 25 | 22 | 8 | 0 | 30 | 30 | 100 | 0 | 8 | 228 | 0 | 0 | 0 |  | 12 | 16 | 33 | 25 | 0 | 6 | 10 | 5 | 0 | 0 | 0 | 280 | 230 | 207 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 37 | 34 | 20 | 0 | 0 | 20 | 128 | 31 | 0 | 18 | 2 | 43 | 29 | 47 | 45 | 80 | 0 | 60 | 81 | 0 | 206 | 17 | 0 | 7 | 280 | 24 | 11 | 0 | 34 | 0 | 0 | 67 | 0 | 35 | 11 | 25 | 17 | 6 | 367 | 19 | 35 | 17 | 2 | 88 | 17 | 34 | 17 | 9 | 25 | 350 | 105 | 21 | 35 | 34 | 0 | 17 | 14 | 36 | 34 | 230 | 17 | 0 | 0 | 0 |  | 909 | 0 | 325 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 136 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 324 | 35 | 0 | 35 | 0 | 34 | 0 | 5 | 35 | 1050 | 225 | 0 | 17 | 1 | 30 | 0 | 0 | 0 | 307 | 18 | 0 | 617 | 93 | 0 |  | 6515 | 4693 | 11208 | 4293 | 909 | 2094 | 0 | 1096 | 2144 | 60 | 120 | 167 | 128 | 197 | 0 | 422.11 | 75.19
10:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 374 | 303 |  | 0 | 370 | 302 | 40 | 51 | 30 | 270 | 0 | 39 | 9 | 24 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 19 | 19 | 21 | 25 | 22 | 8 | 0 | 30 | 30 | 100 | 0 | 8 | 222 | 0 | 0 | 0 |  | 12 | 16 | 32 | 25 | 0 | 6 | 10 | 5 | 0 | 0 | 0 | 280 | 230 | 212 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 37 | 34 | 20 | 0 | 0 | 20 | 134 | 31 | 0 | 18 | 2 | 43 | 29 | 47 | 47 | 80 | 0 | 60 | 81 | 0 | 207 | 17 | 0 | 0 | 280 | 24 | 11 | 0 | 45 | 0 | 0 | 68 | 0 | 35 | 11 | 25 | 31 | 5 | 367 | 19 | 35 | 17 | 2 | 88 | 17 | 34 | 88 | 9 | 25 | 387 | 105 | 30 | 35 | 34 | 0 | 17 | 9 | 42 | 34 | 230 | 53 | 0 | 0 | 0 |  | 910 | 0 | 325 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 136 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 324 | 35 | 0 | 35 | 0 | 34 | 0 | 5 | 35 | 1100 | 225 | 0 | 17 | 4 | 42 | 0 | 0 | 0 | 308 | 14 | 0 | 617 | 77 | 0 |  | 6793 | 4710 | 11503 | 4271 | 910 | 2134 | 0 | 1281 | 2195 | 60 | 120 | 202 | 134 | 196 | 0 | 125.105 | 75.18
11:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 402 | 345 |  | 0 | 370 | 307 | 30 | 53 | 32 | 333 | 0 | 39 | 9 | 24 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 19 | 19 | 21 | 25 | 22 | 8 | 0 | 30 | 30 | 100 | 0 | 8 | 221 | 0 | 0 | 0 |  | 12 | 16 | 32 | 25 | 0 | 6 | 10 | 5 | 0 | 0 | 0 | 280 | 230 | 208 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 28 | 34 | 19 | 0 | 0 | 20 | 138 | 31 | 0 | 18 | 2 | 43 | 29 | 47 | 46 | 80 | 0 | 60 | 81 | 0 | 207 | 17 | 0 | 0 | 280 | 24 | 11 | 0 | 47 | 0 | 0 | 68 | 0 | 32 | 4 | 30 | 51 | 5 | 368 | 19 | 35 | 17 | 5 | 87 | 17 | 34 | 88 | 9 | 38 | 384 | 105 | 51 | 72 | 34 | 0 | 17 | 33 | 54 | 34 | 230 | 53 | 0 | 0 | 0 |  | 909 | 0 | 325 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 136 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 324 | 17 | 0 | 35 | 0 | 34 | 0 | 5 | 35 | 1120 | 225 | 0 | 17 | 1 | 50 | 20 | 0 | 0 | 308 | 15 | 0 | 618 | 110 | 0 |  | 7037 | 4772 | 11809 | 4354 | 909 | 2181 | 0 | 1362 | 2216 | 60 | 120 | 193 | 138 | 276 | 0 | 116.51 | 75.18
12:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 406 | 332 |  | 0 | 420 | 306 | 27 | 75 | 40 | 330 | 0 | 96 | 50 | 24 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 19 | 21 | 25 | 22 | 8 | 0 | 30 | 30 | 100 | 0 | 8 | 222 | 0 | 0 | 0 |  | 12 | 16 | 32 | 25 | 0 | 6 | 10 | 6 | 0 | 0 | 0 | 270 | 230 | 208 | 0 | 0 | 15 | 0 | 0 | 51 | 0 | 29 | 30 | 19 | 0 | 0 | 20 | 156 | 30 | 0 | 18 | 2 | 43 | 29 | 44 | 47 | 112 | 0 | 58 | 81 | 0 | 204 | 17 | 0 | 10 | 285 | 24 | 11 | 0 | 107 | 0 | 0 | 68 | 0 | 23 | 15 | 37 | 51 | 5 | 368 | 19 | 35 | 17 | 3 | 87 | 17 | 34 | 88 | 9 | 38 | 392 | 105 | 17 | 72 | 34 | 0 | 17 | 36 | 54 | 30 | 230 | 53 | 0 | 0 | 0 |  | 909 | 0 | 310 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 130 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 417 | 35 | 0 | 35 | 0 | 34 | 0 | 6 | 35 | 1140 | 225 | 0 | 17 | 2 | 60 | 36 | 0 | 0 | 308 | 35 | 0 | 616 | 69 | 0 |  | 7312 | 4907 | 12219 | 4414 | 909 | 2356 | 0 | 1531 | 2234 | 60 | 120 | 194 | 156 | 245 | 0 | 114.6 | 75.18
13:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 401 | 331 |  | 0 | 450 | 285 | 39 | 78 | 45 | 331 | 0 | 99 | 66 | 64 | 64 | 12 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 19 | 21 | 25 | 22 | 8 | 0 | 30 | 30 | 100 | 0 | 8 | 224 | 0 | 0 | 0 |  | 12 | 16 | 32 | 25 | 0 | 6 | 10 | 9 | 0 | 0 | 0 | 270 | 230 | 210 | 0 | 0 | 15 | 0 | 0 | 51 | 0 | 29 | 26 | 19 | 0 | 0 | 20 | 148 | 31 | 0 | 18 | 2 | 43 | 29 | 47 | 47 | 112 | 0 | 58 | 81 | 0 | 203 | 17 | 0 | 10 | 305 | 24 | 11 | 0 | 112 | 55 | 0 | 69 | 0 | 35 | 5 | 37 | 51 | 5 | 366 | 19 | 35 | 17 | 5 | 87 | 17 | 34 | 88 | 9 | 38 | 160 | 105 | 49 | 72 | 34 | 0 | 17 | 10 | 54 | 17 | 230 | 53 | 0 | 0 | 0 |  | 909 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 103 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 25 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 417 | 35 | 1 | 35 | 0 | 30 | 0 | 5 | 35 | 1180 | 225 | 0 | 17 | 1 | 106 | 36 | 0 | 0 | 310 | 36 | 0 | 617 | 72 | 0 |  | 7249 | 5026 | 12275 | 4164 | 909 | 2390 | 56 | 1666 | 2277 | 60 | 120 | 194 | 148 | 291 | 0 | 148.025 | 75.17
14:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 406 | 301 |  | 0 | 450 | 305 | 42 | 80 | 55 | 331 | 0 | 40 | 66 | 91 | 64 | 21 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 19 | 21 | 25 | 22 | 8 | 0 | 60 | 0 | 95 | 0 | 8 | 224 | 0 | 0 | 0 |  | 12 | 16 | 32 | 25 | 10 | 38 | 10 | 9 | 0 | 0 | 0 | 270 | 230 | 204 | 0 | 0 | 15 | 0 | 0 | 51 | 0 | 28 | 30 | 19 | 0 | 0 | 20 | 156 | 31 | 0 | 15 | 2 | 43 | 29 | 47 | 46 | 112 | 0 | 60 | 84 | 0 | 203 | 17 | 0 | 0 | 260 | 0 | 11 | 0 | 115 | 0 | 0 | 69 | 0 | 35 | 8 | 37 | 51 | 5 | 368 | 19 | 35 | 17 | 5 | 85 | 17 | 34 | 88 | 9 | 38 | 120 | 105 | 40 | 72 | 34 | 0 | 17 | 14 | 53 | 0 | 230 | 53 | 0 | 0 | 0 |  | 909 | 0 | 260 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 134 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 0 | 52 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 382 | 35 | 0 | 35 | 0 | 34 | 0 | 5 | 35 | 1212 | 224 | 0 | 17 | 2 | 94 | 36 | 0 | 0 | 310 | 35 | 0 | 621 | 186 | 0 |  | 7088 | 5182 | 12270 | 4021 | 909 | 2293 | 0 | 1814 | 2313 | 60 | 120 | 193 | 156 | 391 | 0 | 191 | 75.18
15:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 403 | 341 |  | 0 | 450 | 308 | 48 | 80 | 55 | 328 | 0 | 96 | 74 | 91 | 64 | 21 | 0 | 0 | 0 | 17 | 35 | 45 | 19 | 19 | 21 | 25 | 22 | 8 | 0 | 60 | 0 | 100 | 0 | 8 | 221 | 0 | 0 | 0 |  | 12 | 20 | 34 | 25 | 11 | 42 | 10 | 5 | 0 | 0 | 0 | 270 | 230 | 205 | 0 | 0 | 15 | 0 | 0 | 51 | 0 | 34 | 34 | 20 | 0 | 0 | 20 | 149 | 31 | 0 | 15 | 0 | 43 | 29 | 44 | 46 | 112 | 0 | 57 | 84 | 0 | 205 | 17 | 0 | 10 | 315 | 16 | 11 | 0 | 112 | 0 | 0 | 68 | 0 | 35 | 8 | 37 | 51 | 5 | 368 | 19 | 35 | 17 | 4 | 87 | 17 | 34 | 88 | 9 | 38 | 255 | 105 | 12 | 90 | 34 | 0 | 17 | 29 | 51 | 0 | 230 | 53 | 0 | 0 | 0 |  | 909 | 0 | 245 | 0 | 4 | 150 | 0 | 0 | 0 | 0 | 0 | 132 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 25 | 0 | 52 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 414 | 35 | 0 | 35 | 39 | 34 | 0 | 1 | 55 | 1222 | 223 | 0 | 17 | 2 | 85 | 36 | 0 | 0 | 308 | 19 | 0 | 559 | 157 | 0 |  | 7429 | 5154 | 12583 | 4194 | 909 | 2425 | 0 | 1915 | 2259 | 60 | 150 | 205 | 149 | 317 | 0 | 254.985 | 75.17
16:00 | 0 | 0 | 155 | 180 | 0 | 0 | 0 | 406 | 326 |  | 0 | 450 | 265 | 51 | 80 | 55 | 321 | 0 | 98 | 74 | 91 | 64 | 22 | 0 | 0 | 0 | 17 | 35 | 55 | 19 | 19 | 13 | 25 | 22 | 8 | 0 | 60 | 0 | 100 | 0 | 8 | 224 | 0 | 0 | 0 |  | 12 | 20 | 33 | 25 | 12 | 46 | 10 | 7 | 0 | 0 | 0 | 270 | 230 | 201 | 0 | 0 | 15 | 0 | 0 | 51 | 0 | 35 | 34 | 20 | 0 | 0 | 20 | 156 | 32 | 0 | 15 | 1 | 43 | 28 | 42 | 46 | 112 | 0 | 58 | 84 | 0 | 205 | 17 | 0 | 10 | 290 | 16 | 11 | 0 | 115 | 0 | 0 | 68 | 0 | 35 | 5 | 37 | 51 | 2 | 367 | 19 | 35 | 17 | 3 | 87 | 17 | 34 | 34 | 9 | 38 | 250 | 74 | 18 | 90 | 34 | 0 | 17 | 8 | 61 | 0 | 230 | 53 | 0 | 0 | 0 |  | 910 | 0 | 250 | 0 | 39 | 170 | 0 | 0 | 5 | 0 | 0 | 104 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 0 | 52 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 414 | 35 | 0 | 35 | 93 | 34 | 0 | 2 | 57 | 1244 | 223 | 0 | 17 | 1 | 39 | 36 | 0 | 0 | 311 | 15 | 0 | 619 | 113 | 0 |  | 7258 | 5260 | 12518 | 4147 | 910 | 2341 | 0 | 1975 | 2344 | 60 | 170 | 210 | 156 | 205 | 0 | 269.31 | 75.16
17:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 368 | 308 |  | 0 | 450 | 265 | 61 | 77 | 40 | 300 | 0 | 39 | 68 | 48 | 64 | 22 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 19 | 13 | 25 | 22 | 8 | 0 | 60 | 0 | 100 | 0 | 8 | 225 | 0 | 0 | 0 |  | 12 | 50 | 32 | 25 | 12 | 46 | 10 | 12 | 0 | 0 | 0 | 270 | 230 | 197 | 0 | 0 | 15 | 0 | 0 | 51 | 0 | 35 | 33 | 20 | 0 | 0 | 20 | 152 | 31 | 0 | 15 | 1 | 43 | 28 | 44 | 46 | 80 | 0 | 60 | 84 | 0 | 205 | 17 | 0 | 10 | 275 | 24 | 11 | 0 | 112 | 0 | 0 | 68 | 0 | 35 | 2 | 37 | 51 | 5 | 318 | 19 | 35 | 17 | 1 | 87 | 17 | 34 | 34 | 11 | 38 | 255 | 54 | 5 | 72 | 34 | 0 | 17 | 10 | 83 | 9 | 230 | 53 | 0 | 0 | 0 |  | 911 | 0 | 250 | 0 | 48 | 120 | 0 | 0 | 12 | 0 | 0 | 126 | 19 | 16 | 0 | 0 | 0 | 0 | 5 | 0 | 14 | 8 | 14 | 8 | 27 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 353 | 35 | 0 | 35 | 50 | 34 | 0 | 3 | 37 | 1244 | 191 | 0 | 17 | 1 | 36 | 36 | 0 | 0 | 311 | 4 | 0 | 619 | 61 | 0 |  | 6993 | 4997 | 11990 | 4027 | 911 | 2188 | 0 | 1772 | 2344 | 60 | 120 | 292 | 152 | 124 | 0 | 248.3 | 75.16
18:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 355 | 307 |  | 0 | 350 | 286 | 53 | 51 | 40 | 270 | 0 | 40 | 32 | 48 | 72 | 0 | 0 | 0 | 0 | 35 | 17 | 35 | 19 | 19 | 7 | 0 | 22 | 16 | 0 | 60 | 0 | 110 | 0 | 9 | 223 | 0 | 0 | 0 |  | 12 | 65 | 32 | 12 | 19 | 46 | 10 | 10 | 0 | 0 | 0 | 270 | 230 | 205 | 0 | 0 | 15 | 0 | 0 | 10 | 0 | 35 | 33 | 20 | 0 | 0 | 20 | 150 | 31 | 0 | 16 | 0 | 43 | 29 | 14 | 10 | 80 | 0 | 40 | 84 | 0 | 205 | 17 | 0 | 10 | 280 | 24 | 11 | 0 | 60 | 0 | 0 | 68 | 0 | 41 | 1 | 37 | 58 | 6 | 318 | 19 | 35 | 17 | 0 | 120 | 17 | 34 | 34 | 54 | 12 | 225 | 54 | 3 | 72 | 46 | 0 | 17 | 2 | 97 | 17 | 230 | 53 | 0 | 0 | 0 |  | 910 | 0 | 250 | 0 | 47 | 120 | 0 | 0 | 27 | 0 | 0 | 131 | 18 | 16 | 0 | 0 | 0 | 0 | 28 | 0 | 14 | 8 | 14 | 8 | 27 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 353 | 17 | 0 | 35 | 32 | 34 | 0 | 1 | 37 | 1080 | 167 | 0 | 17 | 0 | 3 | 36 | 0 | 0 | 312 | 4 | 0 | 619 | 13 | 0 |  | 6651 | 4735 | 11386 | 3932 | 910 | 1979 | 0 | 1674 | 2181 | 60 | 120 | 353 | 150 | 27 | 0 | 128 | 75.16
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 165 | 180 | 0 | 0 | 0 | 355 | 306 |  | 0 | 350 | 270 | 39 | 65 | 42 | 270 | 0 | 98 | 37 | 48 | 130 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 19 | 8 | 25 | 22 | 25 | 0 | 60 | 0 | 105 | 0 | 17 | 224 | 0 | 0 | 0 |  | 12 | 60 | 33 | 42 | 24 | 46 | 10 | 20 | 0 | 0 | 0 | 270 | 230 | 205 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 35 | 33 | 20 | 0 | 9 | 20 | 166 | 48 | 0 | 18 | 0 | 43 | 29 | 20 | 20 | 112 | 0 | 60 | 84 | 0 | 204 | 17 | 0 | 10 | 290 | 24 | 11 | 0 | 65 | 0 | 0 | 87 | 0 | 136 | 0 | 50 | 76 | 47 | 330 | 85 | 88 | 17 | 0 | 205 | 17 | 34 | 47 | 72 | 50 | 225 | 54 | 0 | 109 | 53 | 0 | 17 | 0 | 105 | 17 | 230 | 104 | 0 | 0 | 0 |  | 909 | 0 | 240 | 0 | 67 | 120 | 0 | 0 | 34 | 0 | 24 | 131 | 27 | 16 | 0 | 0 | 0 | 0 | 28 | 33 | 21 | 25 | 28 | 34 | 27 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 354 | 21 | 0 | 35 | 62 | 74 | 0 | 0 | 55 | 1090 | 167 | 0 | 150 | 0 | 0 | 40 | 0 | 0 | 315 | 0 | 0 | 621 | 0 | 0 |  | 7559 | 5077 | 12636 | 4039 | 909 | 2045 | 0 | 2590 | 2195 | 60 | 120 | 512 | 166 | 0 | 0 | 0 | 75.15
19:30 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 400 | 345 |  | 0 | 450 | 310 | 58 | 75 | 55 | 333 | 0 | 98 | 75 | 48 | 130 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 19 | 8 | 25 | 22 | 25 | 0 | 60 | 0 | 110 | 0 | 17 | 224 | 0 | 0 | 0 |  | 12 | 60 | 33 | 58 | 25 | 46 | 10 | 20 | 0 | 0 | 0 | 270 | 230 | 206 | 0 | 0 | 20 | 0 | 0 | 51 | 0 | 35 | 33 | 20 | 0 | 10 | 20 | 166 | 65 | 0 | 18 | 0 | 43 | 30 | 45 | 47 | 112 | 0 | 61 | 84 | 0 | 204 | 17 | 0 | 10 | 280 | 24 | 11 | 0 | 114 | 12 | 0 | 87 | 0 | 149 | 0 | 50 | 100 | 90 | 368 | 85 | 88 | 17 | 0 | 256 | 17 | 34 | 106 | 97 | 50 | 260 | 54 | 0 | 144 | 87 | 0 | 17 | 0 | 115 | 17 | 230 | 163 | 0 | 0 | 0 |  | 909 | 0 | 240 | 0 | 93 | 150 | 0 | 0 | 26 | 0 | 24 | 131 | 30 | 23 | 0 | 0 | 0 | 7 | 28 | 93 | 28 | 42 | 28 | 52 | 27 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 414 | 25 | 6 | 50 | 105 | 76 | 0 | 0 | 55 | 1230 | 222 | 0 | 150 | 0 | 0 | 111 | 0 | 0 | 307 | 0 | 0 | 621 | 0 | 0 |  | 8554 | 5652 | 14206 | 4265 | 909 | 2420 | 18 | 3260 | 2328 | 60 | 150 | 630 | 166 | 0 | 0 | 0 | 75.15
20:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 394 | 347 |  | 0 | 450 | 263 | 56 | 80 | 55 | 332 | 0 | 197 | 75 | 58 | 130 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 19 | 8 | 25 | 22 | 25 | 0 | 60 | 0 | 109 | 0 | 17 | 227 | 0 | 0 | 0 |  | 12 | 60 | 34 | 58 | 25 | 46 | 10 | 14 | 0 | 0 | 0 | 270 | 230 | 205 | 0 | 0 | 20 | 0 | 0 | 51 | 0 | 35 | 34 | 20 | 0 | 25 | 20 | 166 | 92 | 0 | 18 | 0 | 43 | 30 | 45 | 48 | 112 | 0 | 61 | 84 | 0 | 203 | 17 | 0 | 10 | 300 | 16 | 11 | 0 | 102 | 60 | 0 | 88 | 0 | 149 | 0 | 50 | 103 | 95 | 367 | 85 | 88 | 17 | 0 | 273 | 21 | 34 | 106 | 96 | 50 | 260 | 54 | 0 | 144 | 87 | 0 | 17 | 0 | 115 | 17 | 230 | 162 | 0 | 0 | 0 |  | 767 | 0 | 240 | 0 | 96 | 190 | 0 | 0 | 28 | 0 | 24 | 136 | 30 | 50 | 0 | 0 | 0 | 35 | 28 | 93 | 28 | 42 | 30 | 52 | 27 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 420 | 26 | 10 | 50 | 105 | 77 | 0 | 0 | 57 | 1232 | 222 | 0 | 150 | 0 | 0 | 113 | 0 | 0 | 311 | 0 | 0 | 618 | 0 | 0 |  | 8728 | 5639 | 14367 | 4398 | 767 | 2396 | 70 | 3327 | 2331 | 60 | 190 | 662 | 166 | 0 | 0 | 30 | 75.15
21:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 400 | 326 |  | 0 | 450 | 286 | 68 | 80 | 55 | 330 | 0 | 194 | 75 | 83 | 130 | 11 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 19 | 21 | 25 | 22 | 25 | 0 | 60 | 0 | 100 | 0 | 17 | 226 | 0 | 0 | 0 |  | 12 | 66 | 34 | 58 | 25 | 46 | 10 | 20 | 0 | 0 | 0 | 270 | 230 | 205 | 0 | 0 | 20 | 0 | 0 | 51 | 0 | 35 | 34 | 20 | 0 | 33 | 20 | 164 | 92 | 0 | 19 | 0 | 43 | 30 | 47 | 48 | 112 | 0 | 58 | 84 | 0 | 204 | 17 | 0 | 10 | 290 | 20 | 11 | 0 | 183 | 0 | 0 | 88 | 0 | 149 | 0 | 50 | 100 | 118 | 367 | 85 | 88 | 17 | 0 | 279 | 36 | 34 | 106 | 97 | 50 | 260 | 36 | 0 | 144 | 87 | 0 | 17 | 0 | 115 | 17 | 230 | 163 | 0 | 0 | 0 |  | 766 | 0 | 235 | 0 | 98 | 222 | 0 | 0 | 23 | 0 | 24 | 137 | 31 | 50 | 0 | 0 | 0 | 35 | 28 | 93 | 28 | 42 | 29 | 52 | 27 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 427 | 36 | 0 | 50 | 105 | 77 | 0 | 0 | 57 | 1244 | 222 | 0 | 150 | 0 | 0 | 113 | 0 | 0 | 316 | 0 | 0 | 607 | 0 | 0 |  | 8860 | 5685 | 14545 | 4418 | 766 | 2404 | 0 | 3511 | 2337 | 60 | 222 | 663 | 164 | 0 | 0 | 0 | 75.15
22:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 399 | 337 |  | 0 | 450 | 307 | 77 | 80 | 55 | 331 | 0 | 81 | 75 | 82 | 130 | 11 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 19 | 21 | 25 | 22 | 25 | 0 | 60 | 0 | 102 | 0 | 17 | 224 | 0 | 0 | 0 |  | 12 | 66 | 34 | 58 | 15 | 46 | 10 | 31 | 0 | 0 | 0 | 270 | 230 | 208 | 0 | 0 | 20 | 0 | 0 | 51 | 0 | 35 | 34 | 20 | 0 | 33 | 20 | 162 | 91 | 0 | 19 | 0 | 43 | 29 | 47 | 48 | 80 | 0 | 59 | 84 | 0 | 204 | 17 | 0 | 10 | 280 | 20 | 11 | 0 | 196 | 0 | 0 | 88 | 0 | 149 | 0 | 50 | 103 | 143 | 367 | 85 | 88 | 17 | 0 | 279 | 36 | 34 | 106 | 96 | 50 | 230 | 36 | 0 | 144 | 87 | 0 | 17 | 0 | 115 | 17 | 230 | 163 | 0 | 0 | 0 |  | 766 | 0 | 230 | 0 | 98 | 190 | 0 | 0 | 23 | 0 | 24 | 137 | 32 | 50 | 0 | 0 | 0 | 35 | 28 | 93 | 28 | 42 | 29 | 52 | 27 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 419 | 36 | 0 | 50 | 105 | 76 | 0 | 0 | 57 | 1244 | 222 | 0 | 150 | 0 | 0 | 114 | 0 | 0 | 305 | 0 | 0 | 619 | 0 | 0 |  | 8756 | 5640 | 14396 | 4270 | 766 | 2398 | 0 | 3549 | 2338 | 60 | 190 | 663 | 162 | 0 | 0 | 0 | 75.14
23:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 401 | 331 |  | 0 | 450 | 272 | 69 | 80 | 55 | 335 | 0 | 199 | 75 | 24 | 113 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 19 | 21 | 25 | 22 | 25 | 0 | 60 | 0 | 100 | 0 | 8 | 228 | 0 | 0 | 0 |  | 12 | 66 | 34 | 58 | 0 | 46 | 10 | 33 | 0 | 0 | 0 | 270 | 230 | 209 | 0 | 0 | 20 | 0 | 0 | 51 | 0 | 35 | 34 | 20 | 0 | 33 | 20 | 166 | 92 | 0 | 19 | 0 | 43 | 30 | 47 | 48 | 112 | 0 | 59 | 84 | 0 | 204 | 18 | 0 | 10 | 305 | 20 | 11 | 0 | 196 | 71 | 0 | 69 | 0 | 93 | 0 | 50 | 103 | 33 | 367 | 19 | 88 | 17 | 0 | 123 | 36 | 34 | 106 | 36 | 50 | 250 | 36 | 0 | 144 | 87 | 0 | 17 | 0 | 115 | 17 | 230 | 163 | 0 | 0 | 0 |  | 776 | 0 | 235 | 0 | 96 | 200 | 0 | 0 | 23 | 0 | 24 | 106 | 33 | 50 | 0 | 0 | 0 | 35 | 28 | 63 | 28 | 42 | 29 | 52 | 27 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 419 | 36 | 0 | 50 | 105 | 77 | 0 | 0 | 57 | 1244 | 222 | 0 | 150 | 0 | 0 | 114 | 0 | 0 | 306 | 0 | 0 | 628 | 0 | 0 |  | 8434 | 5612 | 14046 | 4392 | 776 | 2417 | 71 | 3000 | 2348 | 60 | 200 | 616 | 166 | 0 | 0 | 414 | 75.14
24:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 398 | 335 |  | 0 | 450 | 302 | 56 | 80 | 55 | 335 | 0 | 137 | 75 | 24 | 113 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 19 | 21 | 25 | 23 | 8 | 0 | 60 | 0 | 100 | 0 | 8 | 226 | 0 | 0 | 0 |  | 12 | 66 | 34 | 58 | 0 | 46 | 10 | 34 | 0 | 0 | 0 | 270 | 230 | 207 | 0 | 0 | 20 | 0 | 0 | 51 | 0 | 37 | 34 | 20 | 0 | 33 | 20 | 168 | 82 | 0 | 19 | 0 | 43 | 30 | 47 | 48 | 80 | 0 | 61 | 84 | 0 | 203 | 18 | 0 | 10 | 265 | 20 | 11 | 0 | 195 | 23 | 0 | 68 | 0 | 35 | 0 | 25 | 39 | 5 | 367 | 19 | 35 | 17 | 0 | 122 | 36 | 34 | 106 | 9 | 50 | 258 | 36 | 0 | 144 | 87 | 0 | 25 | 0 | 107 | 17 | 230 | 90 | 0 | 0 | 0 |  | 776 | 0 | 230 | 0 | 96 | 226 | 0 | 0 | 14 | 0 | 24 | 138 | 33 | 50 | 0 | 0 | 0 | 35 | 28 | 26 | 28 | 42 | 29 | 52 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 390 | 35 | 0 | 50 | 105 | 77 | 0 | 0 | 57 | 1160 | 221 | 0 | 150 | 0 | 0 | 52 | 0 | 0 | 306 | 0 | 0 | 620 | 0 | 0 |  | 7923 | 5403 | 13326 | 4346 | 776 | 2350 | 23 | 2649 | 2256 | 60 | 226 | 472 | 168 | 0 | 0 | 787 | 75.14
KWH | 0 | 0 | 2805875 | 4315500 | 0 | 0 | 0 | 9476090 | 7676000 |  | 0 | 9857500 | 7034822 | 1215360 | 1367789 | 1054547 | 7527694 | 0 | 2302000 | 1080000 | 1280448 | 1991520 | 181774 | 0 | 0 | 0 | 456120 | 599455 | 625192 | 453996 | 456000 | 394380 | 524520 | 548100 | 290400 | 0 | 1026000 | 420000 | 2300000 | 0 | 242269 | 5266330 | 0 | 0 | 0 |  | 299280 | 730752 | 787894 | 687360 | 156480 | 723840 | 226656 | 545280 | 0 | 0 | 0 | 7005000 | 5919000 | 4957000 | 0 | 0 | 277920 | 0 | 0 | 1098538 | 0 | 837872 | 803496 | 467388 | 4320 | 423500 | 489260 | 3506880 | 1053120 | 0 | 403056 | 13200 | 1023000 | 735000 | 1069200 | 1093536 | 2331572 | 0 | 1413504 | 1980480 | 0 | 4139490 | 397000 | 0 | 196920 | 6953500 | 537768 | 264000 | 0 | 2406218 | 315126 | 0 | 1716000 | 0 | 1347696 | 79380 | 819840 | 1141440 | 540290 | 8759000 | 706800 | 1090560 | 429890 | 34801 | 2872909 | 529955 | 851410 | 1512780 | 620760 | 811200 | 7296800 | 1597440 | 258810 | 1660320 | 1145400 | 0 | 448920 | 162192 | 1671360 | 464040 | 5670900 | 1445236 | 0 | 0 | 0 |  | 21296000 | 0 | 6933888 | 0 | 812160 | 3635467 | 0 | 0 | 173280 | 0 | 142875 | 3085000 | 593497 | 381792 | 0 | 0 | 0 | 150752 | 150980 | 389088 | 337910 | 397078 | 185700 | 473549 | 184095 | 0 | 0 | 161550 | 0 | 0 | 4119000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4640382 | 0 | 9400727 | 780960 | 54698 | 1026432 | 1148112 | 1021334 | 0 | 41148 | 1046688 | 29372700 | 5219536 | 0 | 1582800 | 28200 | 521280 | 834048 | 0 | 0 | 7403636 | 201574 | 0 | 14820000 | 1050030 | 0 |  | 174729216 | 123797946 | 298527162 | 102653987 | 21296000 | 55051108 | 369824 | 45434776 | 55715336 | 1446000 | 3635467 | 7027169 | 3506880 | 2390615 | 0 | 0
Fuel Cost | 0 | 0 | 4096577.5 | 6430095 | 0 | 0 | 0 | 9949894.5 | 8290080 |  | 0 | 10744675 | 7808652.42 | 13587724.8 | 18123204.25 | 13972747.75 | 8431017.28 | 0 | 4028500 | 15789600 | 18015903.36 | 32282539.2 | 1675956.28 | 0 | 0 | 0 | 5801846.4 | 8092642.5 | 8383824.72 | 340497 | 342000 | 0 | 0 | 0 | 4939704 | 0 | 277020 | 113400 | 4347000 | 0 | 3961098.15 | 5476983.2 | 0 | 0 | 0 |  | 3905604 | 12188943.36 | 13409955.88 | 9286233.6 | 1984166.4 | 8374828.8 | 287853.12 | 1815782.4 | 0 | 0 | 0 | 7775550 | 6451710 | 5750120 | 0 | 0 | 314049.6 | 0 | 0 | 1834558.46 | 0 | 14470049.44 | 10807021.2 | 640321.56 | 3240 | 741125 | 366945 | 25179398.4 | 1147900.8 | 0 | 548156.16 | 210408 | 1401510 | 970200 | 1860408 | 1891817.28 | 2681307.8 | 0 | 2742197.76 | 4515494.4 | 0 | 4180884.9 | 853550 | 0 | 389901.6 | 6953500 | 403326 | 200640 | 0 | 32844875.7 | 6605040.96 | 0 | 23131680 | 0 | 18665589.6 | 927952.2 | 8460748.8 | 15592070.4 | 7169648.3 | 8058280 | 8594688 | 15769497.6 | 5438108.5 | 0 | 33727951.66 | 5771209.95 | 9050488.3 | 20528424.6 | 8001596.4 | 9555936 | 6713056 | 20686848 | 3739804.5 | 21069460.8 | 13034652 | 0 | 5862895.2 | 1938194.4 | 25020259.2 | 6111406.8 | 0 | 0 | 0 | 0 | 0 |  | 63888000 | 0 | 7765954.56 | 0 | 8454585.6 | 59985205.5 | 0 | 0 | 3120772.8 | 0 | 2053113.75 | 3455200 | 1151384.18 | 4161532.8 | 0 | 0 | 0 | 2528111.04 | 2640640.2 | 6085336.32 | 2601907 | 6575611.68 | 3140187 | 6454472.87 | 3105682.65 | 0 | 0 | 122293.35 | 0 | 0 | 21789510 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5382843.12 | 0 | 9306719.73 | 10496102.4 | 1147017.06 | 12142690.56 | 16590218.4 | 12970941.8 | 0 | 454685.4 | 12706792.32 | 264648027 | 5323926.72 | 0 | 11712720 | 318942 | 6114614.4 | 12785955.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 713912206.1 | 591181698.05 | 1305093904.15 | 109719471.41 | 63888000 | 64568207.99 | 7752058.02 | 580496787.04 | 286437537 | 390420 | 59985205.5 | 92972217.89 | 25179398.4 | 13704600.9 | 0 | 0
Yesterday Day Peak | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 406 | 332 |  | 0 | 420 | 306 | 27 | 75 | 40 | 330 | 0 | 96 | 50 | 24 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 19 | 21 | 25 | 22 | 8 | 0 | 30 | 30 | 100 | 0 | 8 | 222 | 0 | 0 | 0 |  | 12 | 16 | 32 | 25 | 0 | 6 | 10 | 6 | 0 | 0 | 0 | 270 | 230 | 208 | 0 | 0 | 15 | 0 | 0 | 51 | 0 | 29 | 30 | 19 | 0 | 0 | 20 | 156 | 30 | 0 | 18 | 2 | 43 | 29 | 44 | 47 | 112 | 0 | 58 | 81 | 0 | 204 | 17 | 0 | 10 | 285 | 24 | 11 | 0 | 107 | 0 | 0 | 68 | 0 | 23 | 15 | 37 | 51 | 5 | 368 | 19 | 35 | 17 | 3 | 87 | 17 | 34 | 88 | 9 | 38 | 392 | 105 | 17 | 72 | 34 | 0 | 17 | 36 | 54 | 30 | 230 | 53 | 0 | 0 | 0 |  | 909 | 0 | 310 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 130 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 417 | 35 | 0 | 35 | 0 | 34 | 0 | 6 | 35 | 1140 | 225 | 0 | 17 | 2 | 60 | 36 | 0 | 0 | 308 | 35 | 0 | 616 | 69 | 0 |  | 12219 | DayPeak
Yesterday Evening Peak | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 400 | 326 | 0 | 0 | 450 | 286 | 68 | 80 | 55 | 330 | 0 | 194 | 75 | 83 | 130 | 11 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 19 | 21 | 25 | 22 | 25 | 0 | 60 | 0 | 100 | 0 | 17 | 226 | 0 | 0 | 0 | 0 | 12 | 66 | 34 | 58 | 25 | 46 | 10 | 20 | 0 | 0 | 0 | 270 | 230 | 205 | 0 | 0 | 20 | 0 | 0 | 51 | 0 | 35 | 34 | 20 | 0 | 33 | 20 | 164 | 92 | 0 | 19 | 0 | 43 | 30 | 47 | 48 | 112 | 0 | 58 | 84 | 0 | 204 | 17 | 0 | 10 | 290 | 20 | 11 | 0 | 183 | 0 | 0 | 88 | 0 | 149 | 0 | 50 | 100 | 118 | 367 | 85 | 88 | 17 | 0 | 279 | 36 | 34 | 106 | 97 | 50 | 260 | 36 | 0 | 144 | 87 | 0 | 17 | 0 | 115 | 17 | 230 | 163 | 0 | 0 | 0 |  | 766 | 0 | 235 | 0 | 98 | 222 | 0 | 0 | 23 | 0 | 24 | 137 | 31 | 50 | 0 | 0 | 0 | 35 | 28 | 93 | 28 | 42 | 29 | 52 | 27 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 427 | 36 | 0 | 50 | 105 | 77 | 0 | 0 | 57 | 1244 | 222 | 0 | 150 | 0 | 0 | 113 | 0 | 0 | 316 | 0 | 0 | 607 | 0 | 0 |  | 14545 | EvPeak
Forecast for Evening | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 412 | 330 | 0 | 0 | 450 | 290 | 70 | 80 | 55 | 330 | 0 | 200 | 75 | 83 | 130 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 20 | 21 | 25 | 22 | 25 | 0 | 60 | 0 | 100 | 0 | 17 | 225 |  | 0 | 0 | 0 | 12 | 66 | 34 | 58 | 25 | 50 | 10 | 20 | 0 | 0 | 0 | 270 | 230 | 210 | 0 | 0 | 20 | 0 | 0 | 51 | 0 | 35 | 34 | 20 | 10 | 33 | 20 | 169 | 90 | 0 | 19 | 0 | 43 | 30 | 47 | 48 | 112 | 0 | 60 | 86 | 0 | 204 | 17 | 0 | 10 | 300 | 24 | 11 | 0 | 145 | 300 | 0 | 88 | 0 | 149 | 0 | 50 | 100 | 150 | 400 | 85 | 88 | 34 | 0 | 280 | 36 | 34 | 114 | 95 | 50 | 260 | 55 | 0 | 144 | 87 | 0 | 17 |  | 115 | 17 | 230 | 163 |  | 0 | 10 |  | 920 | 0 | 200 |  | 98 | 225 | 0 | 0 | 30 | 0 | 24 | 137 | 31 | 50 | 0 | 0 | 0 | 35 | 28 | 93 | 28 | 42 | 29 | 52 | 30 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 180 | 0 | 414 | 36 | 200 | 50 | 105 | 77 | 0 | 0 | 55 | 1244 | 225 |  | 150 |  |  | 115 | 200 |  | 310 |  | 0 | 610 |  | 0
Forecast for Day | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 400 | 330 | 0 | 0 | 450 | 280 | 50 | 80 | 55 | 300 | 0 | 150 | 58 | 48 | 82 | 11 | 0 | 0 | 0 | 17 | 34 | 35 | 19 | 20 | 20 | 25 | 22 | 8 | 0 | 30 | 0 | 100 | 0 | 8 | 225 |  | 0 | 0 | 0 | 12 | 32 | 33 | 35 | 12 | 6 | 10 | 10 | 0 | 0 | 0 | 270 | 230 | 200 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 35 | 34 | 20 | 10 | 33 | 20 | 146 | 60 | 0 | 18 | 1.6 | 43 | 30 | 45 | 44 | 112 | 0 | 60 | 86 | 0 | 200 | 17 | 0 | 8 | 300 | 20 | 11 | 0 | 112 | 300 | 0 | 85 | 0 | 34 | 20 | 38 | 50 | 5 | 400 | 20 | 88 | 17 | 5 | 88 | 17 | 34 | 52 | 9 | 38 | 250 | 54 | 50 | 72 | 34 | 0 | 17 | 30 | 55 | 17 | 230 | 54 |  | 0 | 15 |  | 920 | 0 | 200 | 0 | 80 | 150 | 0 | 0 | 20 | 0 | 8 | 135 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 42 | 22 | 50 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 400 | 35 | 150 | 35 | 50 | 34 | 0 | 8 | 35 | 1244 | 220 |  | 17 | 6 | 100 | 35 | 200 |  | 300 | 30 | 0 | 600 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 398 | 336 | 0 | 0 | 450 | 294 | 42 | 17 | 15 | 335 | 0 | 139 | 16 | 8 | 32 | 11 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 19 | 21 | 25 | 23 | 8 | 0 | 60 | 0 | 100 | 0 | 8 | 227 | 0 | 0 | 0 | 0 | 12 | 33 | 34 | 25 | 0 | 6 | 10 | 4 | 0 | 0 | 0 | 270 | 230 | 213 | 0 | 0 | 20 | 0 | 0 | 51 | 0 | 37 | 34 | 20 | 0 | 0 | 20 | 132 | 31 | 0 | 19 | 1 | 43 | 0 | 47 | 48 | 80 | 0 | 60 | 84 | 0 | 204 | 17 | 0 | 10 | 280 | 20 | 11 | 0 | 15 | 0 | 0 | 77 | 0 | 34 | 10 | 25 | 17 | 5 | 365 | 19 | 35 | 17 | 1 | 88 | 17 | 34 | 17 | 9 | 25 | 260 | 35 | 19 | 17 | 34 | 0 | 17 | 2 | 35 | 17 | 230 | 17 | 0 | 0 | 0 | 0 | 909 | 0 | 225 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 130 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 8 | 0 | 16 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 382 | 36 | 0 | 35 | 15 | 34 | 0 | 1 | 35 | 1000 | 225 | 0 | 17 | 0 | 9 | 0 | 0 | 0 | 315 | 16 | 0 | 615 | 99 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
292.3904
| Minimum Generation |  | 10930 | 8:00
| Highest Generation |  | 14545 | 21:00 |  | 340 | 180 |  | 19:00 |  | 165
| Day Peak Generation |  | 12219 | 12:00 |  |  |  | 340 hh
| Evening Peak Generation |  | 14545 | 21:00 |  |  |  |  | Rampal: 315 MW, Payra:1090 MW, Barapukuria: 169 MW at 19:00 hrs on 15/07/23
| HVDC Max Flow |  | 911 | 7:00
| HVDC EvPeak Flow |  | 766 | 21:00
| Load factor L.F |  | 85.52% | [163 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-07-16
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-07-15 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 12219 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 11227
Evening Peak Generation : |  |  | 14545 | MW Hour : | 21:00 | Available Max Generation : |  | 15540
E.P. Demand (at gen end) : |  |  | 14545 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 15200
Maximum Generation : |  |  | 14545 | MW Hour : | 21:00 | Reserve(Generation end) |  | 340
Total Gen. (MKWH) : |  |  | 298.5272 | System Load Factor : | 85.52% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 300 | MW at | 20:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-07-16
Actual : |  | 75.12 | Ft.(MSL) , | Rule curve : | 86.24 | Ft.( MSL )
Gas Consumed : |  | Total = | 1227.39 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 174287679.4
: |  |  | Coal : | 286437537 | Oil : | 741206268.45 | Total : | 1201931484.85
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4954.5545 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1363.7216 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1911.0082 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1661.6578 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1366.9193 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 1016.9903 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 569.6834 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 475.102 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 929.2083 |  |  | 0 | 0%
Total |  | 0 |  | 14248.8454 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
09:04 |  | Ishurdi 230/132kV S/S 230/132 kV T-03 LT Scheduled S/D Due to Oil Leakage Maintanance work 15-7-23 to 19-07-23
09:04 |  | Ishurdi 230/132kV S/S 230/132 kV T-03 HT Scheduled S/D Due to Oil Leakage Maintanance work 15-7-23 to 19-07-23
| 09:22 | Chattak-Sylhet 132 kV Ckt-2 is restored.
| 09:55 | Chowmuhani 132/33kV S/S TR1-415T LT is restored.
| 10:26 | Bhulta 132/33kV S/S GT2 HT is restored.
10:26 | 16:31 | Rampura-Ullon-2 132kV Ckt-1 Project Work S/D from Rampura 230/132kV end Due to Shutdown for transformar replace
10:26 | 16:31 | Rampura-Ullon-2 132kV Ckt-2 Project Work S/D from Rampura 230/132kV end Due to Shutdown for transformar replace
10:31 | 11:26 | Khulna (S)-Rampal Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end Due to Distance Relay Update Rampal End.
from Rampal 400/230kV end Due to Distances protection relay software updated.
10:35 |  | Chowmuhani 132/33kV S/S TR1-415T LT Tripped showing O/C (T) relays Due to T-1 VCB 33kv incoming tripping O/C (T) | [5 empty] | 30 MW load interrup.
for CHO.33/11 T-4 Feeder .
11:28 | 13:53 | Khulna (S)-Rampal Ckt-2 Scheduled S/D from Khulna(S) 230/132kV end Due to Distance Relay Update Rampal End. and
from Rampal 400/230kV end Due to Distances protection relay software updated.
12:53 |  | At magura SS, 33 kv Bus Section-3 is Restored
13:04 |  | Bibiyana South 400 MW ST was shutdown at due to damper leakage. | [5 empty] | 135 MW generation interrup.
13:20 |  | New battery charger -1 replace for outgoing feeder in Shajadpur S/S. 50 MW L/S .
13:38 |  | Day peak generation: 12220 MW.
13:52 |  | New battery charger -1(Pulser) replacement work complete for outgoing feeder in Shajadpur S/S.
13:54 |  | Rampal-Khulna South CKT -2 is Restored
14:28 |  | Adani GSUT -1 (24/400 kv, 330*3 MVA) was switched on.
19:33 |  | Siddhirganj GT- 2 was sync.
21:00 |  | Evening Peak Gen. 14546 MW
04:22 | 04:37 | Kishoreganj 132/33kV S/S Tr-1 (404T) LT Tripped showing Over Current (B,C Phase) relays Due to Over Current (B,C Phase) | [5 empty] | 45 MW load interrup.
04:22 | 04:37 | Kishoreganj 132/33kV S/S Tr-2 (414T) LT Tripped showing Over Current (B Phase) relays Due to Over Current (B Phase)
| 04:37 | Kishoreganj 132/33kV S/S Tr-1 (404T) LT is restored.
06:00 |  | Minimum generation 11302 MW
06:30 |  | Faridpur 132/33kV S/S Transformer-1 LT Scheduled S/D Due to রেড হট সমস্যা সমাধান ।
06:31 |  | Faridpur 132/33kV S/S Transformer-1 HT Scheduled S/D Due to রেড হট সমস্যা সমাধান।
07:28 |  | Noapara 132/33kV S/S T-4 LT Scheduled S/D Due to REB-5 Feeder D/S Point Maintenance. | [5 empty] | 22 MW load interrup.
07:30 |  | Noapara 132/33kV S/S T-4 HT Scheduled S/D Due to REB-5 Feeder D/S Point Maintenance.
showing 21 relays Due to 132kV Mymensingh-Jamalpur ckt-2 GCB(213B) Trip due Z1,Dist.-(A-phase), Aided Trip.
15:55 | 16:00 | 132kV Mymensingh-Jamalpur ckt-2 GCB(213B) Trip due Z1,Dist.-(A-phase), Aided Trip.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-07-15 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 160 | 2805875
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4315500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 400 | 9476090
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 326 | 7676000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9857500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 68 | 1215360 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 286 | 7034822 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 80 | 1367789 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1054547
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 11 | 181774 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 453996 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 194 | 2302000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 75 | 1080000 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 7527694
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 83 | 1280448 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 456120
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 130 | 1991520 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 599455
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 625192 | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 40 | 850380 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 524520 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 22 | 548100 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 290400 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 183 | 2406218 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 315126 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1347696
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1090560 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 36 | 1597440 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1660320 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 162192
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 464040 | Line problem
| Dhaka area Total |  |  |  | 5822 | 3720 | 72558674
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2300000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 242269 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 79380
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 46 | 723840 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 60 | 1446000 | Low Water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 226 | 5266330
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 429890 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 66 | 730752 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 787894 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 58 | 687360 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 819840 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 10 | 226656 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 20 | 545280
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 25 | 156480 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 34801
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 279 | 2872909 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 529955 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 34 | 851410 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 811200 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 87 | 1145400 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 163 | 1445236 | Fuel shortage
| SS Power I |  | SS Power | 0 | 0 | 0 | 0 | On test.
| Cox's Bazar Wind |  | IPP | 66 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2545 | 1378 | 22132882
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 205 | 4957000 | 0
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 270 | 7005000
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 230 | 5919000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 230 | 5670900 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 20 | 277920 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1098538
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 118 | 540290 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 35 | 837872 | Machine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 100 | 1141440 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 467388
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 4320
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 164 | 3506880
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 423500
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 34 | 803496 | Low demand
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 489260 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 106 | 1512780 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 97 | 620760 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 448920 | Fuel shortage
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1671360
| Cumilla Area Total |  |  |  | 3096 | 1865 | 37396624
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 92 | 1053120 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 403056 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13200
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 88 | 1716000 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 85 | 706800 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 258810
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 299280 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 296 | 4450266
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1023000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 735000 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2331572 | ST under maint
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 1069200
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 48 | 1093536
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000 | Machine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 58 | 1413504
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1980480
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 204 | 4139490 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 397000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 20 | 537768 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 6953500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 367 | 8759000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 196920
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 260 | 7296800 | ST under maint
| Sylhet Area Total |  |  |  | 2427 | 1601 | 38190770
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 766 | 21296000 | Load restriction.
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 98 | 812160 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 23 | 173280 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 222 | 3635467
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 235 | 6933888 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 24 | 142875 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 36 | 780960 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 1148112
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 521280
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 220 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 316 | 7403636 | Coal shortage.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 3121 | 1825 | 42847658
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 50 | 381792 | Fuel shortage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 31 | 593497 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 137 | 3085000 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 29372700
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 222 | 5219536
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1582800
| Barisal 307 MW |  | IPP | 307*1 | 307 | 0 | 0 | Coal shortage.
| Barisal Area Total |  |  |  | 2265 | 1834 | 40235325
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 35 | 150752 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 28 | 150980
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 28 | 337910 | Fuel shortage
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 397078 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 29 | 185700 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 183 | 4640382 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 427 | 9400727
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 27 | 184095 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 161550 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 473549 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 93 | 389088 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 54698 | Reserve
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 1026432 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 57 | 1046688 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 28200
| Adani Power Jharkhanda Ltd |  | Import | 748*1 | 748 | 607 | 14820000
| Rajshahi Area Total |  |  |  | 2905 | 1666 | 33447829
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4119000
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 77 | 1021334 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 41148
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 113 | 834048
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 201574
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 1050030
| Rangpur Area Total |  |  |  | 750 | 360 | 7267134
| Total |  |  |  | 23545 | 14545 | 298527162
| Eastern Grid Total |  |  |  | 14504 | 8860 | 174729216
| Western Grid Total |  |  |  | 9041 | 5685 | 123797946
| National Grid Total |  |  |  | 23545 | 14545 | 298527162
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-07-15
| (a) ENTIRE EASTERN GRID : |  | 9380.94 | MW | (b) ENTIRE WESTERN GRID : |  | 4646.6 | MW
| i) Dhaka area |  | 4917.54 | MW | i) Khulna area |  | 1761 | MW
| ii) Chittagong area |  | 1373.4 | MW | ii) Rajshahi area |  | 1495.4 | MW
| iii) Comilla area |  | 1364 | MW | iii) Barisal area |  | 424.2 | MW
| iv) Mymensingh area |  | 1128 | MW | iv) Rangpur area |  | 966 | MW
| v) Sylhet area |  | 598 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 14027.54 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 32 | 00:00 | Kamrangirchar | 43 | 00:00 | Natore | 147 | 22:00 | Shitalakhya | 103.1 | 16:00
2 | AKSML | 99.3 | 13:00 | Chowmuhani | 222 | 21:00 | Kaptai | N/A | N/A | Nawabganj | 46.1 | 00:00 | Sholosohor | 34 | 16:00
3 | Aftabnagar | 36 | 00:00 | Chuadanga | 117 | 21:00 | Kazla | 90 | 13:00 | Netrakona | 125 | 21:00 | Shyampur | 156 | 12:00
4 | Agargaon | 84 | 13:00 | Coxsbazar | 119 | 20:00 | Keranigonj | 62 | 00:00 | New | 86 | 12:00 | Siddhirganj | 120 | 09:00
5 | Agrabad | 64 | 14:00 | Cumilla(N) | 181 | 21:00 | Khagrachori | 32 | 21:00 | Niamatpur | 86 | 21:00 | Sirajganj | 107 | 20:00
6 | Amnura | 63 | 20:00 | Cumilla(S) | 166 | 19:00 | Khulna | 91 | 00:00 | Noapara | 47 | 21:00 | Sonargaon | 110 | 23:00
7 | Ashuganj | 77 | 00:00 | Daudkandi | 157 | 21:00 | Khulshi | 171 | 16:00 | PHP | 9 | 18:30 | Sreemongol | 66 | 19:00
8 | BIPTC | N/A | N/A | Dhaka | 17 | 18:00 | Kishoreganj | 144 | 21:00 | Pabna | 120 | 20:00 | Sreepur | 68 | 16:00
9 | BSRM | 164 | 10:00 | Dhamrai | 126 | 21:00 | Kodda | 295 | 19:00 | Palashbari | 134 | 20:00 | Srinagar | 44.73 | 00:00
10 | Bagerhat | 93 | 21:00 | Dhanmondi | 120 | 17:00 | Kulaura | 54 | 22:00 | Panchagarh | 59 | 22:00 | Sunamganj | 56 | 21:00
11 | Bakulia | 96 | 19:30 | Dohazari | 82 | 20:00 | Kurigram | 68 | 19:30 | Patuakhali | 105 | 00:00 | Sylhet | 160 | 19:00
12 | Banani | 40.2 | 12:00 | Faridpur | 161 | 23:00 | Kushtia | 146 | 00:00 | Payra | 19.2 | 21:00 | TK | 29 | 20:00
13 | Bangabhaban | 9 | 10:00 | Fatullah | 65 | 16:00 | Lalbag | 84 | 13:00 | Postogola | 56 | 13:00 | Tangail | 219 | 19:30
14 | Barapukuria | 62 | 21:00 | Fenchuganj | 50 | 22:00 | Lalmonirhat | 53 | 20:00 | Purbachal | 20 | 21:00 | Thakurgaon | 99 | 20:00
15 | Barguna | 20 | 00:00 | Feni | 97 | 23:00 | Madanganj | 29 | 23:00 | Purbasadipur | 134 | 22:00 | Tongi | 104 | 23:00
16 | Barishal | 96 | 13:00 | GPH | 85 | 05:00 | Madaripur | 110 | 00:00 | Rahanpur_I | N/A | N/A | Ullon | 42 | 00:00
17 | Barishal-230 | 92 | 00:00 | Ghorashal | 72 | 21:00 | Madartek | 80.65 | 23:00 | Rahim | 37 | 09:00 | Uttara | 69 | 12:00
18 | Baroaulia | 70 | 12:00 | Goalpara | 38 | 23:00 | Madunaghat | 51 | 19:30 | Rajbari | 70 | 20:00 | UttaraNew | 50 | 00:00
19 | Baroirhat | 65 | 19:30 | Gollamari | 57 | 19:30 | Magura | 64 | 20:00 | Rajendrapur | 94 | 19:30 | Zigatola | 97 | 13:00
20 | Bashundhara | 152 | 13:00 | Gopalganj | 103.4 | 00:00 | Mahasthangarh | 80 | 23:00 | Rajshahi | 164 | 21:00
21 | BashundharaCement | 0 | 00:00 | Gulshan | 104 | 12:00 | Manikganj | 111 | 19:30 | Rajshahi-230 | 39 | 23:00
22 | Beanibazar | 74 | 21:00 | Halishahar | 80.5 | 15:00 | Maniknagar | 98 | 13:00 | Ramganj | 104 | 19:30
23 | Benapole | 64 | 00:00 | HaripurSBU | 168 | 10:00 | Matarbari | 43 | 19:30 | Rampur | 27 | 20:00
24 | Bhaluka | 164 | 19:30 | Hasnabad | 100 | 23:00 | Matuail | 68 | 12:00 | Rangamati | 18 | 19:30
25 | Bhandaria | 52 | 00:00 | Hathazari | 72 | 20:00 | Millgate | 100 | 16:00 | Rangpur | 143 | 19:30
26 | Bhangura | 34 | 00:00 | Ishurdi | 71 | 20:00 | Mirpur | 129 | 19:00 | Ruppur | 3.8 | 10:00
27 | Bheramara(GK) | 64 | 21:00 | Jaldhaka | 81 | 19:30 | Mirsorai | 6 | 19:30 | SSM | 14 | 15:00
28 | Bhulta | 261 | 12:00 | Jamalpur | 146 | 20:00 | Mithapukur | 42 | 20:00 | Saidpur | 117 | 19:30
29 | Bog-Sherpur | 62 | 20:00 | Jashore | 139 | 20:00 | Modern | 0 | 00:00 | Satkhira | 128 | 00:00
30 | Bogura | 172 | 21:00 | Jhenaidah | 136 | 00:00 | Mogbazar | 114.2 | 10:00 | Satmasjid | 91 | 00:00
31 | Borhanuddin | 59 | 23:00 | Joydebpur | 180 | 19:30 | Mongla | 30 | 16:00 | Savar | 188 | 12:00
32 | Brahmanbaria | 173 | 22:00 | Joypurhat | 60 | 22:00 | Motijheel | 44 | 13:00 | Shahjadpur | 102 | 21:00
33 | Cantonment | 132 | 13:00 | Juldah | 26 | 14:00 | Munshiganj | 108 | 23:00 | Shahjibazar | 124 | 21:00
34 | Chandpur | 72 | 21:00 | KSRM | 27 | 19:30 | Mymensingh | 241 | 23:00 | Shahmirpur | 42.4 | 00:00
35 | Chandraghona | 30 | 21:00 | Kabirpur | 302 | 19:30 | Naogaon | 136 | 22:00 | Shariatpur | 81 | 00:00
36 | Chapai | 74 | 22:00 | Kachua | 77 | 20:00 | Narail | 57 | 19:30 | Sherpur | 132 | 21:00
37 | Charsaidpur | 44 | 15:00 | Kallyanpur | 102 | 00:00 | Narinda | 100 | 13:00 | Shikalbaha | N/A | N/A
38 | Chauddagram | 64 | 20:00 | Kalurghat | 32 | 16:00 | Narshingdi | 176 | 00:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-07-15 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 399 | 06:00 | 391 | 15:00 | Gopalganj | 406 | 18:30 | 398 | 15:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 395 | 18:30 | 287 | 10:00
| Bhulta | 398 | 03:00 | 391 | 11:00 | Madunaghat_I | 408 | 20:00 | 386 | 12:00
| Bibiana | 411 | 18:00 | 402 | 12:00 | Payra | 412 | 06:00 | 407 | 15:00
| BIPTC | 399 | 06:00 | 392 | 16:00 | Rahanpur_I | N/A | N/A | N/A | N/A
| Bogura | N/A | N/A | N/A | N/A | Rampal | 406 | 18:00 | 398 | 14:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 234 | 04:00 | 228 | 12:00 | Hasnabad | 234 | 20:00 | 227 | 11:00
| AKSML | 236 | 20:00 | 208 | 02:00 | Hathazari | 234 | 20:00 | 221 | 15:00
| Aminbazar | 236 | 19:00 | 231 | 15:00 | Ishurdi | 238 | 15:00 | 226 | 02:00
| Ashuganj | 235 | 18:30 | 230 | 16:00 | Jhenaidah | 226 | 23:00 | 218 | 19:30
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 232 | 03:00 | 226 | 11:00
| Baghabari | 229 | 18:30 | 223 | 02:00 | Keranigonj | 232 | 00:00 | 226 | 12:00
| Barapukuria | 219 | 19:00 | 206 | 21:00 | Khulna(S) | 232 | 18:00 | 226 | 12:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | 236 | 20:00 | 221 | 12:00
| Barishal | 235 | 17:00 | 229 | 04:00 | Maniknagar | 234 | 02:00 | 228 | 11:00
| Bheramara | 232 | 23:00 | 228 | 09:00 | Meghnaghat | 240 | 02:00 | 232 | 11:00
| Bhulta | 236 | 04:00 | 230 | 12:00 | Mirsorai | 237 | 21:00 | 220 | 02:00
| Bibiana | 236 | 20:00 | 230 | 12:00 | Rajshahi | 229 | 23:00 | 220 | 05:00
| BIPTC | 233 | 18:30 | 223 | 02:00 | Rampal | 231 | 18:00 | 226 | 05:00
| Bogura | 224 | 19:00 | 214 | 21:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 239 | 20:00 | 235 | 14:00 | Rampura | 233 | 00:00 | 228 | 12:00
| BSRM | 236 | 20:00 | 220 | 12:00 | Shikalbaha | 235 | 21:00 | 221 | 10:00
| Cumilla(N) | 233 | 20:00 | 226 | 11:00 | Shyampur | 232 | 00:00 | 227 | 11:00
| Fenchuganj | 240 | 00:00 | 235 | 01:00 | Siddhirganj | 235 | 01:00 | 231 | 10:00
| Ghorashal | 240 | 07:00 | 232 | 10:00 | Sirajgonj | 234 | 18:30 | 230 | 02:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 230 | 06:00 | 226 | 01:00
| GPH | 235 | 22:00 | 220 | 15:00 | Tongi | 232 | 01:00 | 220 | 09:00
| Haripur | 233 | 00:00 | 228 | 11:00
| 132 kV | KV |  | KV |  | Tongi | KV |  | KV
| Aftabnagar | 136 | 03:00 | 130 | 12:00 | Lalbag | 131 | 00:00 | 126 | 12:00
| Agargaon | 135 | 03:00 | 130 | 12:00 | Lalmonirhat | 129 | 16:00 | 115 | 20:00
| Agrabad | 136 | 19:30 | 128 | 11:00 | Madanganj | 137 | 20:00 | 131 | 10:00
| AKS | 134 | 21:00 | 126 | 11:00 | Madaripur | 130 | 06:00 | 127 | 00:00
| Aminbazar | 137 | 23:00 | 133 | 07:00 | Madartek | 136 | 04:00 | 130 | 11:00
| Amnura | 140 | 19:00 | 126 | 20:00 | Madunaghat | 137 | 21:00 | 129 | 15:00
| Ashuganj | 139 | 07:00 | 136 | 00:00 | Magura | 136 | 18:30 | 128 | 19:30
| Bagerhat | 136 | 09:00 | 132 | 00:00 | Mahasthangarh | 131 | 17:00 | 121 | 02:00
| Bakulia | 137 | 20:00 | 129 | 12:00 | Manikganj | 134 | 18:00 | 124 | 08:00
| Banani | 136 | 00:00 | 130 | 12:00 | Maniknagar | 132 | 00:00 | 125 | 13:00
| Bangabhaban | 132 | 06:00 | 126 | 12:00 | Matarbari | 128 | 19:00 | 115 | 23:00
| Barapukuria | 135 | 16:00 | 124 | 21:00 | Matuail | 135.1 | 20:00 | 131 | 11:00
| Barguna | 137 | 09:00 | 133 | 04:00 | Millgate | 135 | 02:00 | 129 | 11:00
| Barishal | 136 | 18:30 | 129 | 12:00 | Mirpur | 136 | 21:00 | 131 | 11:00
| Barishal-230 | 134 | 17:00 | 130 | 15:00 | Mithapukur | 131 | 17:00 | 118 | 02:00
| Baroaulia | 138 | 21:00 | 129 | 12:00 | Modern | 136 | 19:30 | 128 | 12:00
| Baroirhat | 133 | 21:00 | 124 | 15:00 | Mogbazar | 135 | 00:00 | 131 | 12:00
| Bashundhara | 136 | 00:00 | 129 | 11:00 | Mongla | 137 | 09:00 | 132 | 19:30
| BashundharaCement | 137 | 07:00 | 132 | 08:00 | Motijheel | 132 | 06:00 | 126 | 12:00
| Beanibazar | 131 | 20:00 | 126 | 00:00 | Munshiganj | 136 | 20:00 | 132 | 07:00
| Benapole | 134 | 18:00 | 128 | 01:00 | Mymensingh | 135 | 18:30 | 116 | 22:00
| Bhaluka | 127 | 07:00 | 120 | 21:00 | Naogaon | 129 | 18:00 | 114 | 21:00
| Bhandaria | 134 | 09:00 | 128 | 00:00 | Narail | 134 | 09:00 | 126 | 21:00
| Bhangura | 136 | 18:30 | 130 | 02:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 134 | 18:00 | 131 | 01:00 | Narshingdi | 130 | 06:00 | 123 | 11:00
| Bheramara(GK) | 136 | 18:30 | 131 | 19:30 | Natore | 135 | 19:00 | 127 | 04:00
| Bhulta | 125 | 03:00 | 120 | 12:00 | Nawabganj | 131 | 02:00 | 127 | 11:00
| Bog-Sherpur | 133 | 18:30 | 124 | 21:00 | Netrakona | 134 | 18:30 | 114 | 22:00
| Bogura | 134 | 19:00 | 125 | 04:00 | New | 136 | 07:00 | 130 | 11:00
| Bogura-230 | 134 | 19:00 | 125 | 21:00 | Niamatpur | 128 | 18:00 | 110 | 21:00
| Brahmanbaria | 133 | 05:00 | 130 | 00:00 | Noapara | 138 | 19:00 | 133 | 04:00
| Cantonment | 134 | 03:00 | 129 | 12:00 | Pabna | 133 | 18:00 | 128 | 02:00
| Chandpur | 135 | 18:30 | 117 | 02:00 | Palashbari | 129 | 17:00 | 115 | 21:00
| Chandraghona | 138 | 21:00 | 128 | 15:00 | Panchagarh | 134 | 19:00 | 113 | 02:00
| Chapai | 135 | 18:30 | 127 | 22:00 | Patuakhali | 139 | 02:00 | 135 | 15:00
| Charsaidpur | 136 | 02:00 | 132 | 11:00 | Payra | 139 | 00:00 | 137 | 05:00
| Chauddagram | 134 | 18:30 | 123 | 02:00 | PHP | 132 | 21:00 | 121 | 02:00
| Chhatak | 131 | 06:00 | 126 | 22:00 | Postogola | 137 | 00:00 | 133 | 11:00
| Chowmuhani | 130 | 18:30 | 116 | 03:00 | Purbachal | 136 | 02:00 | 128 | 11:00
| Chuadanga | 132 | 09:00 | 121 | 21:00 | Purbasadipur | 130 | 18:00 | 115 | 21:00
| Coxsbazar | 125 | 05:00 | 115 | 23:00 | Rahim | 135 | 18:30 | 132 | 11:00
| Cumilla(N) | 135 | 18:00 | 129 | 15:00 | Rajbari | 129 | 18:00 | 124 | 19:30
| Cumilla(S) | 135 | 18:30 | 125 | 14:00 | Rajendrapur | 135 | 19:00 | 125 | 13:00
| Daudkandi | 133 | 18:30 | 127 | 15:00 | Rajshahi | 136 | 23:00 | 129 | 03:00
| Dhaka | 136 | 03:00 | 131 | 11:00 | Rajshahi-230 | 137 | 23:00 | 128 | 13:00
| Dhamrai | 131 | 04:00 | 126 | 11:00 | Ramganj | 131 | 18:30 | 114 | 03:00
| Dhanmondi | 135.2 | 03:00 | 130 | 11:00 | Rampur | 137 | 21:00 | 127 | 15:00
| Dohazari | 135 | 20:00 | 125 | 05:00 | Rampura | 136 | 04:00 | 130 | 12:00
| Faridpur | 130 | 18:00 | 125 | 02:00 | Rangamati | 136 | 22:00 | 128 | 15:00
| Fatullah | 131 | 06:00 | 126 | 12:00 | Rangpur | 130 | 16:00 | 117 | 22:00
| Fenchuganj | 135 | 06:00 | 133 | 01:00 | Ruppur | 135 | 18:30 | 131 | 12:00
| Feni | 134 | 20:00 | 121 | 02:00 | Saidpur | 130 | 19:00 | 115 | 21:00
| Ghorashal | 140 | 20:00 | 136 | 11:00 | Satkhira | 137 | 18:00 | 130 | 00:00
| Goalpara | 141 | 23:00 | 137 | 04:00 | Satmasjid | 134 | 00:00 | 130 | 12:00
| Gollamari | 139 | 23:00 | 135 | 04:00 | Savar | 137 | 20:00 | 130 | 08:00
| Gopalganj | 134 | 16:00 | 129 | 04:00 | Shahjadpur | 139 | 04:00 | 135 | 22:00
| Gopalganj-400 | 130 | 18:00 | 127 | 06:00 | Shahjibazar | 136 | 05:00 | 131 | 00:00
| Gulshan | 134 | 00:00 | 130 | 11:00 | Shahmirpur | 137 | 20:00 | 129 | 11:00
| Halishahar | 137 | 20:00 | 128 | 11:00 | Shariatpur | 129 | 18:30 | 124 | 00:00
| Haripur | 135 | 18:30 | 132 | 11:00 | Sherpur | 132 | 18:30 | 112 | 22:00
| HaripurSBU | 135 | 18:30 | 123 | 09:00 | Shikalbaha | N/A | N/A | N/A | N/A
| Hasnabad | 136 | 00:00 | 133 | 11:00 | Shikalbaha-230 | 138 | 21:00 | 129 | 12:00
| Hathazari | 138 | 19:30 | 130 | 15:00 | Shitalakhya | 137 | 00:00 | 132 | 11:00
| Ishurdi | 135 | 18:30 | 130 | 02:00 | Sholosohor | 136 | 20:00 | 128 | 12:00
| Jaldhaka | 129 | 16:00 | 114 | 22:00 | Shyampur | 130 | 00:00 | 124 | 12:00
| Jamalpur | 136 | 18:30 | 115 | 02:00 | Shyampur-230 | 130 | 00:00 | 126 | 12:00
| Jashore | 135 | 18:00 | 129 | 19:30 | Siddhirganj | 136 | 20:00 | 132 | 11:00
| Jhenaidah | 137 | 08:00 | 131 | 19:00 | Sirajganj | 134 | 18:30 | 126 | 21:00
| Jhenaidah-230 | 138 | 18:30 | 132 | 01:00 | Sonargaon | 134 | 00:00 | 130 | 03:00
| Joydebpur | 138 | 06:00 | 132 | 11:00 | Sreemongol | 133 | 07:00 | 130 | 00:00
| Joypurhat | 129 | 18:30 | 113 | 21:00 | Sreepur | 130 | 07:00 | 126 | 00:00
| Juldah | 138 | 20:00 | 129 | 12:00 | Srinagar | 131 | 04:00 | 127 | 11:00
| Kabirpur | 137 | 18:30 | 127 | 09:00 | SSM | 140 | 19:00 | 131 | 12:00
| Kachua | 134 | 18:00 | 117 | 02:00 | Sunamganj | 129 | 07:00 | 122 | 21:00
| Kaliakoir | 137 | 18:30 | 129 | 12:00 | Sylhet | 132 | 05:00 | 130 | 00:00
| Kallyanpur | 130 | 05:00 | 127 | 11:00 | Tangail | 132 | 18:30 | 121 | 22:00
| Kalurghat | 137 | 20:00 | 129 | 11:00 | Thakurgaon | 134 | 19:00 | 110 | 04:00
| Kamrangirchar | 131 | 00:00 | 125 | 12:00 | TK | 138 | 21:00 | 129 | 12:00
| Kaptai | N/A | N/A | N/A | N/A | Tongi | 136 | 01:00 | 131 | 11:00
| Kazla | 132 | 04:00 | 125 | 13:00 | Ullon | 137 | 04:00 | 130 | 11:00
| Keranigonj | 131 | 00:00 | 127 | 12:00 | Uttara | 135 | 00:00 | 131 | 11:00
| Khagrachori | 135 | 22:00 | 128 | 12:00 | UttaraNew | 136 | 19:30 | 131 | 14:00
| Khulna | 140 | 23:00 | 136 | 12:00 | Zigatola | 131 | 00:00 | 126 | 13:00
| Khulna(S) | 139 | 18:00 | 136 | 00:00
| Khulshi | 136 | 20:00 | 127 | 11:00
| Kishoreganj | 131 | 06:00 | 124 | 22:00
| Kodda | 137 | 18:30 | 125 | 12:00
| KSRM | 137 | 20:00 | 127 | 12:00
| Kulaura | 134 | 02:00 | 132 | 22:00
| Kurigram | 129 | 16:00 | 114 | 20:00
| Kushtia | 135 | 18:00 | 130 | 19:30

## L-Curve
Date | 2023-07-15
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 580 | 7923 | 5403 | 13326 |  |  |  | QF-LDC-11
0:30 | 582 | 7646 | 5383 | 13029 | Date: | 2023-07-15
1:00 | 584 | 7369 | 5363 | 12732
1:30 | 562 | 7314 | 5269.5 | 12583.5
2:00 | 540 | 7259 | 5176 | 12435
2:30 | 535 | 7197.5 | 5044 | 12241.5 | [5 empty] | Gen. at Eve. Peak | 14545 | 14545 MW (21:00 )
3:00 | 530 | 7136 | 4912 | 12048 | [6 empty] | 21:00
3:30 | 545 | 7047 | 4860 | 11907 | [5 empty] | Gen. at Day Peak | 12219 | 12219 MW (12:00 )
4:00 | 560 | 6958 | 4808 | 11766 | [6 empty] | 12:00
4:30 | 555 | 6844.5 | 4744 | 11588.5 | [5 empty] | Highest Generation | 14545
5:00 | 550 | 6731 | 4680 | 11411 | [6 empty] | 21:00
5:30 | 565 | 6655 | 4593 | 11248
6:00 | 580 | 6579 | 4506 | 11085
6:30 | 600 | 6526 | 4499 | 11025
7:00 | 620 | 6473 | 4492 | 10965
7:30 | 730 | 6465 | 4482.5 | 10947.5
8:00 | 840 | 6457 | 4473 | 10930
8:30 | 885 | 6486 | 4583 | 11069
9:00 | 930 | 6515 | 4693 | 11208
9:30 | 945 | 6654 | 4701.5 | 11355.5
10:00 | 960 | 6793 | 4710 | 11503
10:30 | 955 | 6915 | 4741 | 11656
11:00 | 950 | 7037 | 4772 | 11809
11:30 | 960 | 7174.5 | 4839.5 | 12014
12:00 | 970 | 7312 | 4907 | 12219
12:30 | 960 | 7280.5 | 4966.5 | 12247
13:00 | 950 | 7249 | 5026 | 12275
13:30 | 995 | 7168.5 | 5104 | 12272.5
14:00 | 1040 | 7088 | 5182 | 12270
14:30 | 1055 | 7258.5 | 5168 | 12426.5
15:00 | 1070 | 7429 | 5154 | 12583
15:30 | 1060 | 7343.5 | 5207 | 12550.5
16:00 | 1050 | 7258 | 5260 | 12518
16:30 | 1070 | 7125.5 | 5128.5 | 12254
17:00 | 1090 | 6993 | 4997 | 11990
17:30 | 1075 | 6822 | 4866 | 11688
18:00 | 1060 | 6651 | 4735 | 11386
18:30 | 985 | 7105 | 4906 | 12011
19:00 | 910 | 7559 | 5077 | 12636
19:30 | 750 | 8554 | 5652 | 14206
20:00 | 300 | 8728 | 5639 | 14367 |  |  |  | Executive Engineer
20:30 | 305 | 8794 | 5662 | 14456 |  |  |  | Network Operation Division
21:00 | 310 | 8860 | 5685 | 14545
21:30 | 315 | 8808 | 5662.5 | 14470.5
22:00 | 320 | 8756 | 5640 | 14396 |  |  |  |  | Page 6 of 7
22:30 | 440 | 8595 | 5626 | 14221
23:00 | 560 | 8434 | 5612 | 14046
23:30 | 570 | 8178.5 | 5507.5 | 13686
24:00 | 580 | 7923 | 5403 | 13326
14545 MW (21:00 )
12219 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-07-15 |  | Energy |  | 298527162
QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 4346 | 776 | 2350 | 23 | 2649 | 2256 | 60 | 226 | 472 | 168 | 0 | 0 | 787
0:30 | 4420 | 842.5 | 2377.5 | 11.5 | 2294.5 | 2288 | 60 | 226 | 350 | 159 | 0 | 0 | 664.72 |  | Date: | 43660
1:00 | 4494 | 909 | 2405 | 0 | 1940 | 2320 | 60 | 226 | 228 | 150 | 0 | 0 | 542.44
1:30 | 4500 | 909 | 2400 | 0 | 1899 | 2266 | 60 | 194 | 208.5 | 147 | 0 | 0 | 445.5075 | [8 empty] | Total Energy | 298.5272 | 298.5272 | Total Energy Gen 298.527 MKWHr Energy Not Served 7.185 MKWHr Energy Requirement 305.712 MKWHr
2:00 | 4506 | 909 | 2395 | 0 | 1858 | 2212 | 60 | 162 | 189 | 144 | 0 | 0 | 348.575 | [8 empty] | Energy not Served | 7.185 | 7.185
2:30 | 4505.5 | 909 | 2392 | 0 | 1700.5 | 2212 | 60 | 141 | 179.5 | 142 | 0 | 0 | 437.8675 | [8 empty] | Energy Requirement | 305.7122 | 305.7122
3:00 | 4505 | 909 | 2389 | 0 | 1543 | 2212 | 60 | 120 | 170 | 140 | 0 | 0 | 527.16
3:30 | 4503 | 909 | 2385.5 | 0 | 1380.5 | 2232 | 60 | 120 | 177 | 140 | 0 | 0 | 518.565 | [7 empty] | Shortage
4:00 | 4501 | 909 | 2382 | 0 | 1218 | 2252 | 60 | 120 | 184 | 140 | 0 | 0 | 509.97
4:30 | 4470 | 909.5 | 2369.5 | 0 | 1102.5 | 2233 | 60 | 120 | 184 | 140 | 0 | 0 | 512.3575
5:00 | 4439 | 910 | 2357 | 0 | 987 | 2214 | 60 | 120 | 184 | 140 | 0 | 0 | 514.745
5:30 | 4440.5 | 910 | 2300 | 0 | 967.5 | 2129 | 60 | 120 | 175 | 139 | 7 | 0 | 503.285
6:00 | 4442 | 910 | 2243 | 0 | 948 | 2044 | 60 | 120 | 166 | 138 | 14 | 0 | 491.825
6:30 | 4388 | 910.5 | 2239.5 | 0 | 953.5 | 2019 | 60 | 120 | 166.5 | 134 | 34 | 0 | 453.625 | [6 empty] | Coal
7:00 | 4334 | 911 | 2236 | 0 | 959 | 1994 | 60 | 120 | 167 | 130 | 54 | 0 | 415.425
7:30 | 4337 | 910.5 | 2184 | 0 | 975 | 1995.5 | 60 | 120 | 167 | 127 | 71.5 | 0 | 432.1375 | [5 empty] | Oil
8:00 | 4340 | 910 | 2132 | 0 | 991 | 1997 | 60 | 120 | 167 | 124 | 89 | 0 | 448.85
8:30 | 4316.5 | 909.5 | 2113 | 0 | 1043.5 | 2070.5 | 60 | 120 | 167 | 126 | 143 | 0 | 435.48
9:00 | 4293 | 909 | 2094 | 0 | 1096 | 2144 | 60 | 120 | 167 | 128 | 197 | 0 | 422.11
9:30 | 4282 | 909.5 | 2114 | 0 | 1188.5 | 2169.5 | 60 | 120 | 184.5 | 131 | 196.5 | 0 | 273.6075
10:00 | 4271 | 910 | 2134 | 0 | 1281 | 2195 | 60 | 120 | 202 | 134 | 196 | 0 | 125.105
10:30 | 4312.5 | 909.5 | 2157.5 | 0 | 1321.5 | 2205.5 | 60 | 120 | 197.5 | 136 | 236 | 0 | 120.8075
11:00 | 4354 | 909 | 2181 | 0 | 1362 | 2216 | 60 | 120 | 193 | 138 | 276 | 0 | 116.51
11:30 | 4384 | 909 | 2268.5 | 0 | 1446.5 | 2225 | 60 | 120 | 193.5 | 147 | 260.5 | 0 | 115.555
12:00 | 4414 | 909 | 2356 | 0 | 1531 | 2234 | 60 | 120 | 194 | 156 | 245 | 0 | 114.6
12:30 | 4289 | 909 | 2373 | 28 | 1598.5 | 2255.5 | 60 | 120 | 194 | 152 | 268 | 0 | 152.8
13:00 | 4164 | 909 | 2390 | 56 | 1666 | 2277 | 60 | 120 | 194 | 148 | 291 | 0 | 191
13:30 | 4164 | 909 | 2390 | 56 | 1666 | 2277 | 60 | 120 | 194 | 148 | 291 | 0 | 191
14:00 | 4164 | 909 | 2390 | 56 | 1666 | 2277 | 60 | 120 | 194 | 148 | 291 | 0 | 191
14:30 | 4179 | 909 | 2407.5 | 28 | 1790.5 | 2268 | 60 | 135 | 199.5 | 148.5 | 304 | 0 | 222.9925
15:00 | 4194 | 909 | 2425 | 0 | 1915 | 2259 | 60 | 150 | 205 | 149 | 317 | 0 | 254.985
15:30 | 4170.5 | 909.5 | 2383 | 0 | 1945 | 2301.5 | 60 | 160 | 207.5 | 152.5 | 261 | 0 | 262.1475
16:00 | 4147 | 910 | 2341 | 0 | 1975 | 2344 | 60 | 170 | 210 | 156 | 205 | 0 | 269.31
16:30 | 4087 | 910.5 | 2264.5 | 0 | 1873.5 | 2344 | 60 | 145 | 251 | 154 | 164.5 | 0 | 258.805
17:00 | 4027 | 911 | 2188 | 0 | 1772 | 2344 | 60 | 120 | 292 | 152 | 124 | 0 | 248.3
17:30 | 3979.5 | 910.5 | 2083.5 | 0 | 1723 | 2262.5 | 60 | 120 | 322.5 | 151 | 75.5 | 0 | 188.15
18:00 | 3932 | 910 | 1979 | 0 | 1674 | 2181 | 60 | 120 | 353 | 150 | 27 | 0 | 128
18:30 | 3985.5 | 909.5 | 2012 | 0 | 2132 | 2188 | 60 | 120 | 432.5 | 158 | 13.5 | 0 | 64
19:00 | 4039 | 909 | 2045 | 0 | 2590 | 2195 | 60 | 120 | 512 | 166 | 0 | 0 | 0
19:30 | 4265 | 909 | 2420 | 18 | 3260 | 2328 | 60 | 150 | 630 | 166 | 0 | 0 | 15
20:00 | 4398 | 767 | 2396 | 70 | 3327 | 2331 | 60 | 190 | 662 | 166 | 0 | 0 | 30
20:30 | 4408 | 766.5 | 2400 | 35 | 3419 | 2334 | 60 | 206 | 662.5 | 165 | 0 | 0 | 15
21:00 | 4418 | 766 | 2404 | 0 | 3511 | 2337 | 60 | 222 | 663 | 164 | 0 | 0 | 0
21:30 | 4344 | 766 | 2401 | 0 | 3530 | 2337.5 | 60 | 206 | 663 | 163 | 0 | 0 | 0
22:00 | 4270 | 766 | 2398 | 0 | 3549 | 2338 | 60 | 190 | 663 | 162 | 0 | 0 | 0
22:30 | 4331 | 771 | 2407.5 | 35.5 | 3274.5 | 2343 | 60 | 195 | 639.5 | 164 | 0 | 0 | 207
23:00 | 4392 | 776 | 2417 | 71 | 3000 | 2348 | 60 | 200 | 616 | 166 | 0 | 0 | 414
23:30 | 4369 | 776 | 2383.5 | 47 | 2824.5 | 2302 | 60 | 213 | 544 | 167 | 0 | 0 | 600.5 |  | Max Temp. in Dhaka |  | 32.7° C
24:00 | 4346 | 776 | 2350 | 23 | 2649 | 2256 | 60 | 226 | 472 | 168 | 0 | 0 | 787
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 298.527 MKWHr Energy Not Served 7.185 MKWHr Energy Requirement 305.712 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-07-15
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1026000
2 | Karnaphuli Hydro PP Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 |  |  |  | 0 | [8 empty] | 420000
3 | Chattogram TPP-1 | 94 | 97 | 99 | 101 | 99 | 98 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 95 | 100 | 100 | 100 | 110 |  | 105 | 110 | 109 | 100 | 102 | 100 | 100 | 2300000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 |  | 17 | 17 | 17 | 17 | 17 | 8 | 8 | 242269
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 4 | 1 | 11 | 11 | 4 | 15 | 5 | 8 | 8 | 5 | 2 | 1 | [8 empty] | 79380
6 | Sikalbaha 225MW CCPP (Gas) | 228 | 228 | 228 | 228 | 227 | 227 | 226 | 226 | 228 | 222 | 221 | 222 | 224 | 224 | 221 | 224 | 225 | 223 |  | 224 | 224 | 227 | 226 | 224 | 228 | 226 | 5266330
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 32 | 32 | 32 | 32 | 34 | 33 | 32 | 32 |  | 33 | 33 | 34 | 34 | 34 | 34 | 34 | 787894
12 | Hathazari 100 MW peaking PP | 32 |  | 2 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 20 | 50 | 65 |  | 60 | 60 | 60 | 66 | 66 | 66 | 66 | 730752
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 429890
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 32 | 36 | 36 | 36 | 36 | 36 | 37 | 37 | 37 | 37 | 28 | 29 | 29 | 28 | 34 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 37 | 837872
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 99 | 100 | 100 | 59 | 61 | 59 | 62 | 62 | 97 | 39 | 39 | 96 | 99 | 40 | 96 | 98 | 39 | 40 |  | 98 | 98 | 197 | 194 | 81 | 199 | 137 | 2302000
17 | Siddhirganj 335 MW CCPP | 335 | 336 | 335 | 336 | 300 | 300 | 270 | 270 | 270 | 270 | 333 | 330 | 331 | 331 | 328 | 321 | 300 | 270 |  | 270 | 333 | 332 | 330 | 331 | 335 | 335 | 7527694
18 | Kodda 300 MW PP Unit-2 (Summit) | 112 | 112 | 112 | 45 | 45 | 27 | 15 | 15 | 34 | 45 | 47 | 107 | 112 | 115 | 112 | 115 | 112 | 60 |  | 65 | 114 | 102 | 183 | 196 | 196 | 195 | 2406218
19 | Ashuganj 195 MW PP (APSCL-United)
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 155 | 160 | 160 |  | 165 | 160 | 160 | 160 | 160 | 160 | 160 | 2805875
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4315500
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 20 | 20 | 20 | 20 | 20 | 20 | 277920
33 | Ashuganj 225 MW CCPP | 196 | 197 | 200 | 202 | 209 | 208 | 209 | 194 | 207 | 212 | 208 | 208 | 210 | 204 | 205 | 201 | 197 | 205 |  | 205 | 206 | 205 | 205 | 208 | 209 | 207 | 4957000
34 | Ashuganj 450 MW CCPP(South) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5919000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 300 | 280 | 280 | 280 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 7005000
| Ashuganj 420 MW CCPP(East) | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5670900
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 400 | 400 | 400 | 399 | 400 | 400 | 360 | 355 | 358 | 374 | 402 | 406 | 401 | 406 | 403 | 406 | 368 | 355 |  | 355 | 400 | 394 | 400 | 399 | 401 | 398 | 9476090
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 400 | 400 | 370 | 370 | 370 | 370 | 370 | 420 | 450 | 450 | 450 | 450 | 450 | 350 |  | 350 | 450 | 450 | 450 | 450 | 450 | 450 | 9857500
41 | Haripur 360 MW CCPP(HPL) | 332 | 333 | 332 | 332 | 332 | 303 | 274 | 273 | 272 | 303 | 345 | 332 | 331 | 301 | 341 | 326 | 308 | 307 |  | 306 | 345 | 347 | 326 | 337 | 331 | 335 | 7676000
42 | RPCL 210MW CCPP | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 31 | 31 | 31 | 31 | 30 | 31 | 31 | 31 | 32 | 31 | 31 |  | 48 | 65 | 92 | 92 | 91 | 92 | 82 | 1053120
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 3 | 6 | 21 | 30 | 51 | 17 | 49 | 40 | 12 | 18 | 5 | 3 |  | 0 | [6 empty] | 258810
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1023000
45 | Fenchugonj CCPP Phase-2 | 39 | 39 | 39 | 39 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 28 | 28 | 29 |  | 29 | 30 | 30 | 30 | 29 | 30 | 30 | 735000
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 61 | 61 | 62 | 62 | 62 | 62 | 61 | 60 | 60 | 60 | 60 | 58 | 58 | 60 | 57 | 58 | 60 | 40 |  | 60 | 61 | 61 | 58 | 59 | 59 | 61 | 1413504
48 | Shahjibazar 86 MW PP (Shahjibazar) | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 81 | 81 | 81 | 81 | 81 | 84 | 84 | 84 | 84 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1980480
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 205 | 205 | 205 | 206 | 208 | 207 | 206 | 206 | 206 | 207 | 207 | 204 | 203 | 203 | 205 | 205 | 205 | 205 |  | 204 | 204 | 203 | 204 | 204 | 204 | 203 | 4139490
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 18 | 18 | 397000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 0 |  | 10 | 10 |  | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 196920
54 | Hobiganj 11 MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 47 | 47 | 44 | 42 | 44 | 14 |  | 20 | 45 | 45 | 47 | 47 | 47 | 47 | 1069200
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 16 | 16 | 24 | 24 |  | 24 | 24 | 16 | 20 | 20 | 20 | 20 | 537768
57 | Bibiana-II 341 MW CCPP (Summit) | 260 | 260 | 265 | 270 | 295 | 270 | 300 | 285 | 280 | 280 | 280 | 285 | 305 | 260 | 315 | 290 | 275 | 280 |  | 290 | 280 | 300 | 290 | 280 | 305 | 265 | 6953500
| Bibiyana South 400 MW | 380 | 385 | 385 | 385 | 385 | 385 | 350 | 350 | 350 | 387 | 384 | 392 | 160 | 120 | 255 | 250 | 255 | 225 |  | 225 | 260 | 260 | 260 | 230 | 250 | 258 | 7296800
58 | Nababganj 55 MW PP (Southern power ) | [8 empty] | 10 | 35 | 35 | 35 | 35 | 35 | 45 | 55 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 55 | 55 | 625192
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 299280
60 | Barabkunda 22 MW PP (Regent) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 226656
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 453996
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 15 | 15 | 15 | 15 | 16 |  | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 403056
63 | Impoprt (Tripura) | 150 | 144 | 140 | 140 | 140 | 138 | 130 | 124 | 128 | 134 | 138 | 156 | 148 | 156 | 149 | 156 | 152 | 150 |  | 166 | 166 | 166 | 164 | 162 | 166 | 168 | 3506880
64 | Malancha, Ctg. EPZ (United) | 37 | 37 | 37 | 42 | 42 | 42 | 38 | 6 | 5 | 5 | 5 | 6 | 9 | 9 | 5 | 7 | 12 | 10 |  | 20 | 20 | 14 | 20 | 31 | 33 | 34 | 545280
65 | Feni 22 MW PP (Doreen) | 18 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 19 | 19 | 19 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 467388
66 | Feni 11 MW PP (Doreen) | [25 empty] | 0 | 4320
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | [11 empty] | 9 | 10 | 25 | 33 | 33 | 33 | 33 | 423500
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 18 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 489260
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456000
70 | Summit Madhabdi | 21 | 21 | 21 | 21 | 21 | 21 | 8 | 8 | 8 | 21 | 21 | 21 | 21 | 21 | 21 | 13 | 13 | 7 |  | 8 | 8 | 8 | 21 | 21 | 21 | 21 | 394380
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 524520
72 | Rupganj 33 MW PP(Summit) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 23 | 548100
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 106 | 52 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 88 | 88 | 88 | 88 | 88 | 88 | 34 | 34 | 34 |  | 47 | 106 | 106 | 106 | 106 | 106 | 106 | 1512780
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 11 | 54 |  | 72 | 97 | 96 | 97 | 96 | 36 | 9 | 620760
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 72 | 72 | 72 | 72 | 90 | 90 | 72 | 72 |  | 109 | 144 | 144 | 144 | 144 | 144 | 144 | 1660320
77 | Siddhirganj 100 PP(Dutch Bangla) | 75 | 50 | 42 | 42 | 19 | 8 | 9 | 9 | 9 | 9 | 9 | 50 | 66 | 66 | 74 | 74 | 68 | 32 |  | 37 | 75 | 75 | 75 | 75 | 75 | 75 | 1080000
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 |  | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 290400
79 | Kodda 150 MW PP | 82 | 82 | 82 | 82 | 82 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 72 |  | 130 | 130 | 130 | 130 | 130 | 113 | 113 | 1991520
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 30 | 26 | 30 | 34 | 34 | 33 | 33 |  | 33 | 33 | 34 | 34 | 34 | 34 | 34 | 803496
| Gazipur 100 MW PP | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 88 | 88 | 88 | 88 | 88 | 88 | 35 | 1090560
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 3 | 2 | 2 | 5 | 3 | 5 | 5 | 4 | 3 | 1 | [9 empty] | 34801
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 21 | 36 | 36 | 36 | 36 | 529955
| Karnaphuli Power Ltd. | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 851410
82 | Madanganj 102 PP(Summit) | 82 | 82 | 82 | 82 | 28 | 17 | 17 | 17 | 22 | 51 | 53 | 75 | 78 | 80 | 80 | 80 | 77 | 51 |  | 65 | 75 | 80 | 80 | 80 | 80 | 80 | 1367789
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 23 | 22 | [10 empty] | 12 | 21 | 21 | 22 | 22 | [5 empty] | 11 | 11 |  | 0 | 181774
86 | Meghnaghat CCPP ( Summit) | 292 | 283 | 282 | 280 | 311 | 285 | 313 | 310 | 288 | 302 | 307 | 306 | 285 | 305 | 308 | 265 | 265 | 286 |  | 270 | 310 | 263 | 286 | 307 | 272 | 302 | 7034822
87 | Meghnaghat 100 MW(IEL) | 74 | 73 | 74 | 45 | 42 | 41 | 41 | 40 | 41 | 40 | 30 | 27 | 39 | 42 | 48 | 51 | 61 | 53 |  | 39 | 58 | 56 | 68 | 77 | 69 | 56 | 1215360
| Meghnaghat 104 MW PP (OPCL) | 46 | 54 | 44 | 47 | 35 | 36 | 59 | 82 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 74 | 54 | 54 |  | 54 | 54 | 54 | 36 | 36 | 36 | 36 | 1597440
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 26 | 26 | 26 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 12 |  | 42 | 58 | 58 | 58 | 58 | 58 | 58 | 687360
92 | Fenchuganj 44 MW (Energyprima) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 45 | 47 | 46 | 47 | 47 | 46 | 46 | 46 | 46 | 10 |  | 20 | 47 | 48 | 48 | 48 | 48 | 48 | 1093536
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 10 |  | 15 | 51 | 51 | 51 | 51 | 51 | 51 | 1098538
94 | Gagnagar 102 MW PP (Digital Power) | 99 | 99 | 74 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 64 | 91 | 91 | 91 | 48 | 48 |  | 48 | 48 | 58 | 83 | 82 | 24 | 24 | 1280448
95 | Patenga 50MW PP (Baraka) | 46 | 46 | 46 | 46 | 13 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 38 | 42 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 723840
96 | Chattogram 108 MW PP (ECPV) | [13 empty] | 10 | 11 | 12 | 12 | 19 |  | 24 | 25 | 25 | 25 | 15 |  | 0 | 156480
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 15 | 15 | 15 | 15 | 18 | 30 | 32 | 40 | 45 | 55 | 55 | 55 | 40 | 40 |  | 42 | 55 | 55 | 55 | 55 | 55 | 55 | 1054547
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 |  | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 599455
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 112 | 112 | 112 | 112 | 112 | 80 | 80 |  | 112 | 112 | 112 | 112 | 80 | 112 | 80 | 2331572
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 1 | 1 | 0 | [8 empty] | 13200
103 | Kamalaghat 54 MW PP(Banco Energy) | [11 empty] | 17 | 17 | 17 | 17 | 17 | 35 | 35 |  | 35 | 35 | 35 | 54 | 54 | 54 | 54 | 456120
104 | Keranigonj 300 MW PP (APR) | [12 empty] | 55 | [7 empty] | 12 | 60 |  |  | 71 | 23 | 315126
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 67 | 68 | 68 | 68 | 69 | 69 | 68 | 68 | 68 | 68 |  | 87 | 87 | 88 | 88 | 88 | 69 | 68 | 1716000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 33 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 35 | 35 | 32 | 23 | 35 | 35 | 35 | 35 | 35 | 41 |  | 136 | 149 | 149 | 149 | 149 | 93 | 35 | 1347696
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 30 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 819840
116 | Chandpur 200 MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 31 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 58 |  | 76 | 100 | 103 | 100 | 103 | 103 | 39 | 1141440
117 | Ashuganj 150 MW PP (Midland) | 6 | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 5 | 6 |  | 47 | 90 | 95 | 118 | 143 | 33 | 5 | 540290
118 | Bibiyana-III 400 MW CCPP | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 389 | 367 | 367 | 368 | 368 | 366 | 368 | 368 | 367 | 318 | 318 |  | 330 | 368 | 367 | 367 | 367 | 367 | 367 | 8759000
| Jamalpur 115 MW PP (United) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 85 | 85 | 85 | 85 | 85 | 19 | 19 | 706800
| Anwara 300 MW PP (United) | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 87 | 87 | 87 | 85 | 87 | 87 | 87 | 120 |  | 205 | 256 | 273 | 279 | 279 | 123 | 122 | 2872909
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 12 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 811200
| Anlima Energy Ltd. | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 46 |  | 53 | 87 | 87 | 87 | 87 | 87 | 87 | 1145400
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 448920
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 3 | 3 | 14 | 9 | 33 | 36 | 10 | 14 | 29 | 8 | 10 | 2 | [8 empty] | 162192
| Chandpur 115(Doreen) | 94 | 86 | 38 | 36 | 36 | 36 | 35 | 36 | 36 | 42 | 54 | 54 | 54 | 53 | 51 | 61 | 83 | 97 |  | 105 | 115 | 115 | 115 | 115 | 115 | 107 | 1671360
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 26 | 34 | 34 | 34 | 30 | 17 |  |  |  | 9 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 464040
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 104 | 163 | 162 | 163 | 163 | 163 | 90 | 1445236
Mirsharai 150 MW (Gas)
Cox's Bazar Wind
120 | Eastern Zone Total | 7369 | 7259 | 7136 | 6958 | 6731 | 6579 | 6473 | 6457 | 6515 | 6793 | 7037 | 7312 | 7249 | 7088 | 7429 | 7258 | 6993 | 6651 |  | 7559 | 8554 | 8728 | 8860 | 8756 | 8434 | 7923 | 174729216
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 65 | 64 | 16 | [11 empty] | 4 | 39 | 48 | 47 |  | 67 | 93 | 96 | 98 | 98 | 96 | 96 | 812160
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 11 | [14 empty] | 5 | 12 | 27 |  | 34 | 26 | 28 | 23 | 23 | 23 | 14 | 173280
| Khulna 225 MW CCPP | 226 | 162 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 150 | 170 | 120 | 120 |  | 120 | 150 | 190 | 222 | 190 | 200 | 226 | 3635467
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 17 |  | 21 | 25 | 26 | 36 | 36 | 36 | 35 | 780960
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 3 | 9 | 10 | 30 | 42 | 50 | 60 | 106 | 94 | 85 | 39 | 36 | 3 | [8 empty] | 521280
131 | Rampal 1320 MW (BIFPCL) | 308 | 308 | 307 | 307 | 308 | 310 | 309 | 309 | 307 | 308 | 308 | 308 | 310 | 310 | 308 | 311 | 311 | 312 |  | 315 | 307 | 311 | 316 | 305 | 306 | 306 | 7403636
132 | United Payra Power Ltd. | 150 | 150 | 100 | 54 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 1582800
133 | Bhola Nutan Biddut BD LTD (GAS) | 223 | 225 | 225 | 225 | 225 | 225 | 225 | 175 | 225 | 225 | 225 | 225 | 225 | 224 | 223 | 223 | 191 | 167 |  | 167 | 222 | 222 | 222 | 222 | 222 | 221 | 5219536
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 32 | [12 empty] | 16 | 16 | 16 |  | 16 | 23 | 50 | 50 | 50 | 50 | 50 | 381792
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 120 | 120 | 110 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 130 | 103 | 134 | 132 | 104 | 126 | 131 |  | 131 | 131 | 136 | 137 | 137 | 106 | 138 | 3085000
140 | Bhola 33 MW PP (Venture) | 32 | 31 | 30 | 29 | 28 | 25 | 22 | 20 | 19 | 19 | 20 | 20 | 20 | 22 | 22 | 21 | 19 | 18 |  | 27 | 30 | 30 | 31 | 32 | 33 | 33 | 593497
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | [17 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 142875
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 67 | [11 empty] | 39 | 93 | 50 | 32 |  | 62 | 105 | 105 | 105 | 105 | 105 | 105 | 1148112
146 | Bheramara HVDC | 909 | 909 | 909 | 909 | 910 | 910 | 911 | 910 | 909 | 910 | 909 | 909 | 909 | 909 | 909 | 910 | 911 | 910 |  | 909 | 909 | 767 | 766 | 766 | 776 | 776 | 21296000
147 | Bheramara 410 MW CCPP | 300 | 300 | 305 | 310 | 315 | 325 | 330 | 330 | 325 | 325 | 325 | 310 | 300 | 260 | 245 | 250 | 250 | 250 |  | 240 | 240 | 240 | 235 | 230 | 235 | 230 | 6933888
148 | Payra 1320 MW | 1222 | 1122 | 1122 | 1162 | 1122 | 950 | 900 | 900 | 1050 | 1100 | 1120 | 1140 | 1180 | 1212 | 1222 | 1244 | 1244 | 1080 |  | 1090 | 1230 | 1232 | 1244 | 1244 | 1244 | 1160 | 29372700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 169 | 170 | 170 | 170 | 170 | 170 | 170 | 4119000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [20 empty] | 7 | 35 | 35 | 35 | 35 | 35 | 150752
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 1 | 1 | 4 | 1 | 2 | 1 | 2 | 2 | 1 | 1 | 0 | [8 empty] | 28200
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 201 | 200 | 199 | 200 | 170 | 170 | 170 | 170 | 180 | 150 | 150 | 170 | 188 | 182 | 168 | 165 | 174 | 187 |  | 160 | 179 | 182 | 183 | 181 | 179 | 175 | 4640382
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 430 | 427 | 419 | 405 | 407 | 376 | 377 | 376 | 324 | 324 | 324 | 417 | 417 | 382 | 414 | 414 | 353 | 353 |  | 354 | 414 | 420 | 427 | 419 | 419 | 390 | 9400727
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 21 | 21 | [14 empty] | 5 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 150980
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 |  | 0 |  |  | 8 | 8 | 8 | 8 | 161550
165 | Amnura 50 MW PP(Sinha) | 21 | 21 | 21 | 21 | [9 empty] | 28 | 28 | 28 | 14 | 14 |  | 21 | 28 | 28 | 28 | 28 | 28 | 28 | 337910
166 | Katakhali 50 MW PP (Northern) | 34 | 34 | [10 empty] | 25 | 34 | 25 | 34 | 8 | 8 |  | 25 | 42 | 42 | 42 | 42 | 42 | 42 | 397078
167 | Katakhali 50 MW Peaking PP | [16 empty] | 14 | 14 |  | 28 | 28 | 30 | 29 | 29 | 29 | 29 | 185700
168 | Santahar 50 MW Peaking PP | [16 empty] | 27 | 27 |  | 27 | 27 | 27 | 27 | 27 | 27 | 0 | 184095
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | [10 empty] | 25 | 52 | 52 | 52 | 8 | 8 |  | 34 | 52 | 52 | 52 | 52 | 52 | 52 | 473549
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 33 | 93 | 93 | 93 | 93 | 63 | 26 | 389088
171 | Baghabari 200 MW PP (Paramount) | [12 empty] | 1 | [7 empty] | 6 | 10 |  |  |  | 0 | 54698
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 50 | 50 | 50 | 50 | 50 | 50 | 1026432
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 57 | 37 | 37 |  | 55 | 55 | 57 | 57 | 57 | 57 | 57 | 1046688
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 | 25 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 30 | 34 | 34 | 34 | 34 | 34 |  | 74 | 76 | 77 | 77 | 76 | 77 | 77 | 1021334
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 5 | 5 | 5 | 6 | 5 | 5 | 1 | 2 | 3 | 1 | [8 empty] | 41148
178 | Energypac Power Venture Thakurgaon Ltd. | [10 empty] | 20 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 40 | 111 | 113 | 113 | 114 | 114 | 52 | 834048
| Intraco Solar 30 MW | [5 empty] | 1 | 4 | 7 | 18 | 14 | 15 | 35 | 36 | 35 | 19 | 15 | 4 | 4 |  | 0 | [6 empty] | 201574
| Adani Power Jharkhanda Ltd | 620 | 612 | 613 | 613 | 614 | 614 | 615 | 618 | 617 | 617 | 618 | 616 | 617 | 621 | 559 | 619 | 619 | 619 |  | 621 | 621 | 618 | 607 | 619 | 628 | 620 | 14820000
178 | Teesta Solar Limited | [5 empty] | 7 | 29 | 56 | 93 | 77 | 110 | 69 | 72 | 186 | 157 | 113 | 61 | 13 | [8 empty] | 1050030