## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2019-04-22 | Monday
|  | Date (day): | 2019-04-22 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12503 | MW |  |  | (b) At Evening Peak Hour : |  | 13068 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-04-21 | 2019-04-22 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 36 | 36 | 36 | 36 |  | 49 | Unit-1 under maint.
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 93 | 94 | 94 | 94 |  |  | On test.
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 170 | 81 | 170 | 170 |  |  | On test.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 120 | 120 | 120 | 120
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 250 | 225 | 250 | 250
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  |  | Under maint.
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 63 | 110 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 252 | 265 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 320 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 76 | 55 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 245 | 210 | 335 | 335
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 60 | 64 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 34 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 57 | 39 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 84 | 0 | 97 | 97 | 113 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract expired
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 73 | 20 | 100 | 100
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 75 | 0 | 0 | 217 |  | On test.
0 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
21 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 74 | 102 | 102 | 102
22 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 50
23 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
24 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 149 | 149 | 149 | 149
25 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 56 | 55 | 55
26 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
27 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 46 | 52 | 54 | 54 |  | 54 | Engine problem
28 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 43 | 57 | 57 |  | 23 | Engine problem
29 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
30 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
31 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 50 | 11 | 51 | 51
32 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
33 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 105 | 271 | 300 | 300
34 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
35 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
36 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
37 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
| Gazipur 100 MW |  | HFO | RPCL | 100 MW | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 6034 | 5798 | 2888 | 2796 | 4091 | 4141 | 776 | 126
38 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 110 | 110 | 110 | 70 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
39 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
40 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 14.66 | 0 | 20 | 0
41 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 40 | 39 | 39 | 39
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 98 | 105 | 110 | 110 |  | 120 | Low water lavel
43 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
44 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  |  | Under maint. |  | 23/04/2019
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 130 | 130 | 130
46 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 33 | 41 | 41 | 41 |  | 10 | Engine problem
47 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 38 | 61 | 70 | 70
48 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 68 | 84 | 85 | 85
49 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 68 | 102 | 100 | 100
50 | Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 100 | 100 | 89 | 100 | 100 | 100
51 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 26 | 40 | 40
52 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 96 | 105 | 98 | 98 |  |  | Engine problem
| Chattogram area Total |  |  |  |  | 1761 | 1681 | 821.66 | 1067 | 1110 | 1090 | 130 | 170
53 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 80 | 80 |  | 54 | Gas shortage
54 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 222 | 183 | 220 | 220
55 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 330 | 260 | 360 | 360
56 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 250 | 360 | 360
57 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 14 | 17 | 40 | 40
58 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 10 | 10 | 10 | 10
59 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage
60 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 110 | 82 | 110 | 110
61 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 45 | 45 | 45 | 45 |  | 6 | Engine problem
62 | Midland 150MW |  | HFO | IPP | 23*7.015 | 150 | 150 | 100 | 100 | 150 | 150
63 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
64 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 0 | 50
65 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 90 | 50 | 50
66 | Chandpur Desh 200MW |  | HFO | IPP | 0 | 200 | 200 | 200 | 165 | 200 | 200
67 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
68 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 152 | 176 | 131 | 169
69 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
70 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 43 | 52 | 52
71 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 21 | 21
72 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 200 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1787 | 1632 | 2100 | 2188 | 312 | 60
73 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 90 | 90 | 160 | 160 |  |  | Gas shortage
74 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
75 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 78 | 85 | 85 | 85 |  | 10 | Engine problem
76 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 2.5 | 0 | 2 | 0
77 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 80 | 137 | 200 | 200
78 | United Jamalpur PPL |  | HFO | IPP | 115 MW | 115 | 115 | 68 | 68 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 338.5 | 400 | 582 | 580 | 0 | 10
79 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 57 | 60 | 60 | 60
80 | Fenchugonj CCPP-2 |  | Gas | PDB | !F71 | 104 | 90 | 50 | 67 | 66 | 66
81 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 100 | 163 | 163
82 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 130 | 121 | 140 | 140 |  |  | FGMO, GT-2 under maint.
83 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 31 | 50 | 50 | 50
84 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 33 | 50 | 50
85 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
86 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 46 | 66 | 66 |  |  | FGMO
87 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 79 | 85 | 85
88 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 22 | 45 | 46 | 46 |  | 4 | Engine problem
89 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 79 | 45 | 120 | 120
90 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 0 | 20
91 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 34 | 41 | 45 | 45
92 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 25 | 25
93 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 240 | 341 | 341 |  |  | FGMO
| Bibiyana-3 285 MW |  | Gas | PDB | 285 MW | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
94 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1054 | 990 | 1278 | 1298 | 0 | 4
95 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 46
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 851 | 948 | 862 | 960
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
96 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 99 | 99 | 115 | 115
97 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 40 | 40 | 40
98 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 |  |  | Reserve
99 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 6 | 60 | 50 | 80
100 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint.
101 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
0 | Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
102 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 100 | 100
103 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 90 | 105 | 105 | 105
| Madhumati Power Plant |  | HFO | IPP | 100 MW | 0 | 0 | 108 | 109 | 108 | 108
| Khulna Area Total |  |  |  |  | 2223 | 2209 | 1194 | 1401 | 1420 | 1594 | 0 | 410
104 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 48 | 110 | 110 | 110
105 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 12 | 0 | 26
106 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 36 | 33 | 33
107 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 145 | 135 | 145 | 145
108 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 93 | 80 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 304 | 373 | 383 | 409 | 0 | 0
109 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 |  |  | Gas shortage
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Gas shortage
110 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 50 | 50 | 0 | 50
111 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 51 | 0 | 55
112 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 6 | 12 | 6 | 35 |  | 15 | Engine problem
113 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 43 | 33 | 35 | 50
114 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 44 | 0 | 44
115 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 190 | 167 | 200 | 200 |  |  | FGMO
116 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 188 | 140 | 225 | 225 |  |  | FGMO
117 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 168 | 148 | 200 | 200 |  |  | FGMO
118 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282 | 282 | 282 | 322 | 230 | 282 | 282 |  |  | ON test
119 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 0 | 36
120 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
121 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 14 | 16 | 17 | 17
122 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
123 | Rajlanka 52 MW |  | HFO | IPP | 52 | 52 | 52 | 34 | 34 | 43 | 43 |  | 9 | Engine problem
124 | Chapainawabganj-100 MW |  | HFO | PDB | 104 | 104 | 104 | 93 | 93 | 100 | 100
125 | Paramount Baghabari |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Reserve
126 | Confidence CPBL-2 |  | HFO | IPP | 113 MW | 113 | 113 | 70 | 72 | 113 | 113 |  |  | On test
| Rajshahi Area Total |  |  |  |  | 1948 | 1938 | 1211 | 1156 | 1254 | 1483 | 0 | 24
127 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under overhauling
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 65 | 69 | 65 | 65
128 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 280 | 265 | 185 | 185 | 89
129 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 17 | 17
130 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 18 | 18 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 345 | 369 | 285 | 285 | 89 | 85
| Total |  |  |  |  | 18192 | 17649 | 9943.16 | 10184 | 12503 | 13068 | 1307 | 889
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9534.0689 | 9765 | 11988.5895 | 12530.3437
A. |  | 2019-04-21 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 10436 | MW at | 15:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 8060.9 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10184 | MW
3 | Day peak Generation : |  |  | 9943.16 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9765 | MW
4 | Evening peak Generation : |  |  | 10184 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 222.5171 | MKWHr | By Solar | 0.15329 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 127.858 | MKWHr |  | By Oil: | 62.6018 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 7.0967 | MKWHr |  | By Hydro: | 1.9821 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1307 | MW | Dhaka | 3605 | 3605 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 889 | MW | Chittagong | 1044 | 1044 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2196 | MW | Khulna | 1052 | 1052 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1130.79 | MMCFD |  |  | Rajshahi | 858 | 858 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 86992429.548 | ii) Oil : | Taka | 466604084.2 | Comilla | 1017 | 1017 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 30964121.78 | Total | Taka | 584560635.528 | Mymensingh | 858 | 858 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.8775 | MKWHr. | Sylhet | 413 | 413 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 240 | MW (E to W) at | 19:00 | hrs | Barisal | 277 | 277 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -320 | MW at | 1:00 | hrs | Rangpur | 641 | 641 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 35.6° C |  |  | Total | 9765 | 9765 |  | 0
B. |  | 2019-04-22 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 37.0° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13068 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7500 | MW
4 | Reserve(Generation end) |  |  |  | 3068 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 213.2206 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6146.7 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.3549 | MKWHr. | ii) HVDC Flow at Peak Time |  | 948 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.4704 | MKWHr. | iii) Maximum HVDC Flow : |  | 948 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 80.6 |  | (b) Today: | 80.22 |  | (c) Rule Curve: |  | 83.8
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-04-21
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285 MW | United Jamalpur PPL | Gazipur 100 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | Paramount Baghabari | Confidence CPBL-2 | Madhumati Power Plant | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 36 | 94 | 165 | 120 | 250 | 0 | 0 | 0 | 356 | 13 | 0 | 450 | 235 | 100 | 60 | 30 | 0 | 0 | 92 | 0 | 7 | 102 | 98 | 10 | 57 | 0 | 0 | 17 | 56 | 55 | 19 | 25 | 25 | 33 | 33 | 51 | 0 | 76 | 0 | 100 | 120 | 25 | 0 | 0 | 0 | 0 | 0 | 41 | 40 | 85 | 90 | 105 | 46 | 19 | 30 | 0 | 0 | 80 | 300 | 250 | 227 | 110 | 100 | 14 | 10 | 5 | 45 | 0 | 0 | 52 | 19 | 8 | 25 | 20 | 124 | 108 | 84 | 20 | 0 | 58 | 38 | 53 | 50 | 163 | 131 | 53 | 78 | 46 | 85 | 0 | 39 | 10 | 250 | 16 | 11 | 50 | 97 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 200 | 142 | 0 | 111 | 0 |  | 523 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 31 | 10 | 40 | 139 | 31 | 80 | 0 | 0 | 0 | 50 | 0 | 93 | 6 | 50 | 39 | 34 | 35 | 22 | 16 | 11 | 0 | 67 | 184 | 17 | 16 | 161 | 0 | 168 | 0 | 95 | 20 | 165 | 0 | 331 | 105 | 0 | 90 | 108 |  | 7097 | 2820 | 9917 | 3338 | 523 | 2190 | 2901 | 251 | 76 | 514 | 124 | 0 | 0 | 80.75
2:00 | 36 | 93 | 170 | 120 | 250 | 0 | 0 | 0 | 357 | 13 | 0 | 450 | 280 | 100 | 15 | 15 | 0 | 0 | 97 | 0 | 7 | 64 | 64 | 10 | 58 | 0 | 0 | 17 | 55 | 55 | 19 | 25 | 25 | 33 | 33 | 51 | 0 | 76 | 0 | 100 | 120 | 25 | 0 | 0 | 0 | 0 | 0 | 41 | 40 | 85 | 90 | 105 | 46 | 19 | 31 | 0 | 0 | 80 | 300 | 300 | 226 | 110 | 50 | 14 | 10 | 5 | 45 | 0 | 0 | 52 | 19 | 8 | 25 | 20 | 120 | 107 | 84 | 20 | 0 | 58 | 38 | 53 | 50 | 163 | 131 | 66 | 78 | 46 | 85 | 0 | 39 | 10 | 240 | 16 | 11 | 50 | 15 | 0 | 0 | 150 | 0 | 100 | 0 | 100 | 200 | 142 | 0 | 111 | 0 |  | 389 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 31 | 5 | 40 | 141 | 28 | 64 | 0 | 0 | 0 | 0 | 0 | 93 | 6 | 50 | 39 | 34 | 0 | 22 | 15 | 11 | 0 | 67 | 184 | 0 | 0 | 172 | 0 | 167 | 0 | 95 | 0 | 165 | 0 | 350 | 105 | 0 | 70 | 108 |  | 6837 | 2534 | 9371 | 3370 | 389 | 2197 | 2611 | 251 | 76 | 357 | 120 | 0 | 0 | 80.72
3:00 | 36 | 94 | 170 | 120 | 250 | 0 | 0 | 0 | 356 | 0 | 0 | 450 | 250 | 58 | 15 | 0 | 0 | 0 | 97 | 0 | 7 | 7 | 16 | 10 | 58 | 0 | 0 | 17 | 37 | 17 | 19 | 25 | 23 | 33 | 33 | 25 | 0 | 76 | 0 | 100 | 120 | 25 | 0 | 0 | 0 | 0 | 0 | 41 | 40 | 85 | 90 | 105 | 41 | 19 | 31 | 0 | 0 | 80 | 300 | 300 | 226 | 110 | 50 | 14 | 10 | 5 | 45 | 0 | 0 | 43 | 19 | 8 | 25 | 20 | 120 | 108 | 81 | 20 | 0 | 58 | 38 | 53 | 50 | 163 | 128 | 66 | 78 | 46 | 85 | 0 | 39 | 10 | 255 | 16 | 11 | 50 | 0 | 0 | 0 | 100 | 0 | 15 | 0 | 100 | 200 | 142 | 0 | 111 | 0 |  | 703 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 5 | 8 | 143 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 93 | 6 | 50 | 39 | 34 | 0 | 22 | 16 | 11 | 0 | 67 | 184 | 0 | 0 | 173 | 0 | 173 | 0 | 95 | 0 | 165 | 0 | 371 | 94 | 0 | 53 | 108 |  | 6394 | 2672 | 9066 | 3376 | 703 | 2232 | 2030 | 251 | 76 | 278 | 120 | 0 | 0 | 80.69
4:00 | 36 | 95 | 169 | 120 | 250 | 0 | 0 | 0 | 361 | 0 | 0 | 450 | 260 | 25 | 15 | 0 | 0 | 0 | 97 | 0 | 7 | 0 | 0 | 10 | 58 | 0 | 0 | 54 | 18 | 17 | 19 | 25 | 23 | 33 | 33 | 25 | 0 | 76 | 0 | 100 | 120 | 25 | 0 | 0 | 0 | 0 | 0 | 41 | 40 | 85 | 90 | 105 | 45 | 19 | 31 | 0 | 0 | 80 | 300 | 300 | 226 | 110 | 50 | 14 | 10 | 5 | 45 | 0 | 0 | 16 | 19 | 8 | 25 | 20 | 116 | 108 | 0 | 20 | 0 | 58 | 38 | 31 | 50 | 163 | 129 | 50 | 78 | 46 | 85 | 0 | 40 | 10 | 250 | 16 | 11 | 50 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 100 | 200 | 64 | 0 | 0 | 0 |  | 703 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 5 | 8 | 140 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 93 | 6 | 43 | 39 | 34 | 0 | 22 | 16 | 11 | 0 | 66 | 184 | 0 | 0 | 175 | 0 | 179 | 0 | 95 | 0 | 173 | 0 | 372 | 70 | 0 | 53 | 108 |  | 5933 | 2654 | 8587 | 3374 | 703 | 2212 | 1594 | 250 | 76 | 262 | 116 | 0 | 0 | 80.66
5:00 | 36 | 94 | 170 | 120 | 250 | 0 | 0 | 0 | 362 | 0 | 0 | 450 | 240 | 24 | 15 | 0 | 0 | 0 | 92 | 0 | 7 | 0 | 0 | 10 | 58 | 0 | 0 | 54 | 18 | 17 | 19 | 25 | 23 | 33 | 33 | 25 | 0 | 76 | 0 | 100 | 120 | 25 | 0 | 0 | 0 | 0 | 0 | 41 | 40 | 85 | 90 | 101 | 45 | 19 | 25 | 0 | 0 | 80 | 300 | 300 | 225 | 110 | 50 | 14 | 10 | 5 | 45 | 0 | 0 | 16 | 19 | 8 | 25 | 20 | 112 | 108 | 10 | 20 | 0 | 58 | 38 | 31 | 50 | 163 | 127 | 60 | 78 | 46 | 85 | 0 | 40 | 10 | 250 | 16 | 11 | 50 | 0 | 0 | 0 | 16 | 0 | 15 | 0 | 100 | 200 | 64 | 0 | 28 | 0 |  | 703 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 5 | 8 | 138 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 93 | 6 | 43 | 0 | 34 | 0 | 22 | 16 | 11 | 0 | 67 | 184 | 0 | 0 | 174 | 0 | 179 | 0 | 95 | 0 | 174 | 0 | 372 | 65 | 0 | 53 | 109 |  | 5955 | 2610 | 8565 | 3374 | 703 | 2207 | 1619 | 251 | 76 | 223 | 112 | 0 | 0 | 80.63
6:00 | 36 | 94 | 170 | 120 | 250 | 0 | 0 | 0 | 303 | 0 | 0 | 370 | 270 | 7 | 0 | 0 | 0 | 0 | 89 | 0 | 7 | 0 | 0 | 10 | 24 | 0 | 0 | 54 | 18 | 17 | 19 | 25 | 23 | 33 | 33 | 25 | 0 | 76 | 0 | 100 | 120 | 25 | 0 | 0 | 0 | 0 | 0 | 41 | 40 | 85 | 90 | 98 | 44 | 19 | 34 | 0 | 0 | 80 | 270 | 270 | 227 | 110 | 50 | 14 | 10 | 5 | 45 | 0 | 0 | 16 | 19 | 8 | 25 | 20 | 102 | 108 | 40 | 20 | 0 | 58 | 38 | 31 | 50 | 130 | 129 | 45 | 78 | 46 | 85 | 0 | 40 | 10 | 240 | 24 | 11 | 50 | 0 | 0 | 0 | 16 | 0 | 15 | 0.9 | 100 | 105 | 12 | 0 | 68 | 0 |  | 704 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 5 | 8 | 143 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 93 | 6 | 8 | 0 | 34 | 0 | 22 | 16 | 11 | 0 | 68 | 184 | 0 | 0 | 172 | 0 | 179 | 0 | 96 | 0 | 172 | 0 | 330 | 35 | 0 | 35 | 94 |  | 5589.9 | 2471 | 8060.9 | 3309 | 704 | 1990 | 1404 | 252 | 76 | 223 | 102 | 0.9 | 0 | 80.6
7:00 | 36 | 94 | 171 | 120 | 250 | 0 | 0 | 0 | 303 | 0 | 0 | 370 | 260 | 7 | 0 | 0 | 0 | 0 | 97 | 0 | 7 | 0 | 0 | 10 | 24 | 0 | 0 | 54 | 18 | 17 | 19 | 25 | 22 | 33 | 33 | 25 | 0 | 78 | 0 | 100 | 120 | 25 | 0 | 0 | 0 | 0 | 0 | 41 | 38 | 68 | 90 | 98 | 42 | 19 | 28 | 0 | 0 | 80 | 270 | 270 | 228 | 110 | 50 | 14 | 10 | 5 | 45 | 0 | 0 | 16 | 19 | 8 | 25 | 16 | 100 | 107 | 48 | 20 | 0.5 | 58 | 38 | 31 | 50 | 100 | 131 | 45 | 78 | 46 | 85 | 0 | 40 | 10 | 250 | 24 | 11 | 50 | 0 | 0 | 0 | 16 | 0 | 15 | 5 | 100 | 105 | 12 | 0 | 68 | 0 |  | 852 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 5 | 8 | 145 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 93 | 6 | 8 | 0 | 34 | 0 | 22 | 16 | 11 | 0 | 65 | 185 | 0 | 0 | 171 | 0 | 179 | 0 | 95 | 0 | 174 | 0 | 280 | 35 | 0 | 35 | 72 |  | 5551.5 | 2544 | 8095.5 | 3318 | 852 | 1910 | 1378 | 250 | 78 | 204 | 100 | 5.5 | 0 | 80.57
8:00 | 36 | 94 | 170 | 120 | 250 | 0 | 0 | 0 | 303 | 0 | 0 | 370 | 285 | 11 | 0 | 0 | 0 | 0 | 97 | 0 | 7 | 4 | 0 | 10 | 44 | 0 | 0 | 54 | 36 | 17 | 19 | 25 | 24 | 35 | 33 | 26 | 0 | 80 | 0 | 100 | 120 | 25 | 0 | 0 | 0 | 0 | 0 | 41 | 38 | 68 | 90 | 98 | 39 | 17 | 12 | 0 | 0 | 80 | 270 | 270 | 226 | 110 | 50 | 14 | 10 | 5 | 45 | 0 | 0 | 17 | 19 | 8 | 25 | 15 | 100 | 105 | 48 | 20 | 1 | 58 | 58 | 31 | 50 | 100 | 131 | 65 | 78 | 46 | 105 | 0 | 38 | 10 | 280 | 24 | 8 | 0 | 0 | 0 | 0 | 16 | 0 | 15 | 9.07 | 100 | 105 | 32 | 0 | 68 | 0 |  | 851 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 5 | 40 | 145 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 93 | 6 | 35 | 0 | 33 | 0 | 18 | 15 | 11 | 0 | 65 | 185 | 0 | 0 | 197 | 0 | 182 | 0 | 95 | 0 | 180 | 0 | 280 | 53 | 0 | 36 | 72 |  | 5663.07 | 2665 | 8328.07 | 3406 | 851 | 1916 | 1511 | 250 | 80 | 204 | 100 | 10.07 | 0 | 80.56
9:00 | 36 | 94 | 170 | 120 | 250 | 0 | 0 | 0 | 304 | 0 | 0 | 400 | 275 | 47 | 0 | 0 | 0 | 0 | 97 | 0 | 24 | 16 | 32 | 10 | 50 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 24 | 33 | 33 | 48 | 0 | 80 | 0 | 100 | 120 | 25 | 0 | 0 | 0 | 0 | 0 | 41 | 38 | 68 | 90 | 98 | 40 | 19 | 4 | 0 | 0 | 80 | 300 | 300 | 222 | 110 | 50 | 14 | 10 | 5 | 45 | 0 | 0 | 49 | 19 | 8 | 25 | 15 | 126 | 104 | 50 | 20 | 1.6 | 58 | 38 | 31 | 50 | 130 | 128 | 65 | 78 | 45 | 90 | 0 | 39 | 10 | 270 | 24 | 8 | 0 | 13 | 0 | 0 | 16 | 0 | 32 | 14.58 | 100 | 125 | 90 | 0 | 68 | 0 |  | 852 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 5 | 40 | 145 | 13 | 16 | 0 | 0 | 0 | 0 | 0 | 94 | 6 | 43 | 0 | 34 | 0 | 22 | 15 | 11 | 0 | 65 | 185 | 0 | 0 | 196 | 0 | 185 | 0 | 96 | 0 | 180 | 0 | 280 | 70 | 0 | 36 | 108 |  | 6050.18 | 2763 | 8813.18 | 3425 | 852 | 1957 | 1870 | 250 | 80 | 237 | 126 | 16.18 | 0 | 80.55
10:00 | 36 | 93 | 170 | 120 | 250 | 0 | 0 | 0 | 253 | 40 | 0 | 400 | 275 | 50 | 0 | 0 | 0 | 0 | 97 | 0 | 50 | 45 | 90 | 10 | 49 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 24 | 33 | 33 | 50 | 0 | 78 | 0 | 110 | 120 | 25 | 0 | 0 | 0 | 0 | 0 | 41 | 38 | 68 | 78 | 98 | 40 | 19 | 3 | 0 | 0 | 80 | 330 | 330 | 224 | 110 | 40 | 14 | 10 | 5 | 48 | 0 | 0 | 52 | 19 | 8 | 25 | 15 | 132 | 103 | 70 | 20 | 2 | 60 | 38 | 31 | 50 | 163 | 128 | 63 | 75 | 45 | 80 | 0 | 37 | 10 | 280 | 24 | 8 | 0 | 44 | 75 | 0 | 33 | 0 | 75 | 18.67 | 100 | 185 | 100 | 0 | 68 | 0 |  | 852 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 5 | 40 | 145 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 94 | 6 | 43 | 0 | 34 | 0 | 22 | 15 | 11 | 0 | 67 | 194 | 0 | 0 | 199 | 0 | 185 | 0 | 97 | 0 | 177 | 0 | 322 | 70 | 0 | 35 | 108 |  | 6521.67 | 2850 | 9371.67 | 3475 | 852 | 1993 | 2265 | 261 | 78 | 295 | 132 | 20.67 | 0 | 80.54
11:00 | 36 | 94 | 170 | 120 | 250 | 0 | 0 | 0 | 253 | 40 | 0 | 400 | 250 | 73 | 5 | 8 | 0 | 0 | 92 | 0 | 68 | 68 | 98 | 50 | 48 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 24 | 33 | 33 | 46 | 0 | 68 | 0 | 110 | 120 | 25 | 0 | 0 | 0 | 0 | 0 | 41 | 38 | 68 | 78 | 98 | 40 | 19 | 4 | 0 | 0 | 80 | 330 | 300 | 223 | 110 | 98 | 14 | 10 | 5 | 45 | 0 | 0 | 52 | 19 | 8 | 25 | 15 | 144 | 103 | 78 | 20 | 2 | 58 | 50 | 31 | 50 | 130 | 130 | 58 | 78 | 45 | 78 | 0 | 37 | 10 | 270 | 24 | 8 | 0 | 70 | 0 | 0 | 67 | 0 | 125 | 17 | 89 | 200 | 100 | 0 | 68 | 0 |  | 851 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 4 | 40 | 145 | 15 | 48 | 0 | 0 | 0 | 10 | 0 | 94 | 6 | 43 | 0 | 34 | 0 | 22 | 14 | 11 | 0 | 66 | 230 | 0 | 0 | 201 | 0 | 185 | 0 | 95 | 0 | 172 | 0 | 322 | 90 | 0 | 52 | 108 |  | 6650 | 2957 | 9607 | 3500 | 851 | 1946 | 2471 | 296 | 68 | 312 | 144 | 19 | 0 | 80.53
12:00 | 36 | 93 | 170 | 120 | 250 | 0 | 0 | 0 | 252 | 63 | 0 | 400 | 245 | 76 | 60 | 34 | 0 | 0 | 84 | 0 | 73 | 74 | 149 | 57 | 46 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 33 | 33 | 50 | 0 | 68 | 30 | 110 | 120 | 25 | 0 | 0 | 0 | 0 | 0 | 33 | 38 | 68 | 68 | 96 | 40 | 19 | 3 | 0 | 0 | 80 | 330 | 300 | 222 | 110 | 100 | 14 | 10 | 5 | 45 | 0 | 0 | 52 | 19 | 8 | 25 | 15 | 152 | 90 | 78 | 20 | 2.5 | 57 | 50 | 31 | 50 | 130 | 130 | 58 | 78 | 22 | 79 | 0 | 34 | 10 | 290 | 24 | 11 | 0 | 105 | 0 | 0 | 80 | 0 | 149 | 14.66 | 89 | 200 | 100 | 0 | 68 | 0 |  | 851 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 6 | 40 | 145 | 18 | 48 | 0 | 0 | 0 | 50 | 0 | 93 | 6 | 43 | 0 | 34 | 0 | 22 | 14 | 11 | 0 | 65 | 280 | 0 | 0 | 190 | 0 | 188 | 0 | 93 | 0 | 168 | 0 | 322 | 90 | 0 | 70 | 108 |  | 6889.16 | 3054 | 9943.16 | 3474 | 851 | 1939 | 2663 | 345 | 98 | 404 | 152 | 17.16 | 0 | 80.52
13:00 | 36 | 93 | 162 | 120 | 250 | 0 | 0 | 0 | 263 | 96 | 0 | 420 | 215 | 84 | 80 | 50 | 0 | 0 | 0 | 0 | 87 | 102 | 149 | 64 | 52 | 0 | 0 | 54 | 56 | 55 | 19 | 25 | 23 | 33 | 33 | 50 | 0 | 65 | 30 | 0 | 120 | 25 | 0 | 0 | 0 | 0 | 0 | 33 | 38 | 68 | 68 | 96 | 39 | 19 | 6 | 0 | 0 | 80 | 360 | 360 | 212 | 110 | 98 | 14 | 10 | 5 | 45 | 0 | 0 | 52 | 19 | 8 | 25 | 15 | 156 | 91 | 85 | 20 | 2 | 56 | 50 | 45 | 50 | 163 | 135 | 40 | 80 | 22 | 74 | 0 | 39 | 10 | 280 | 25 | 11 | 0 | 162 | 75 | 0 | 93 | 42 | 149 | 14 | 89 | 200 | 100 | 0 | 68 | 0 |  | 851 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 10 | 40 | 135 | 17 | 80 | 0 | 0 | 0 | 50 | 0 | 93 | 6 | 43 | 0 | 34 | 0 | 22 | 14 | 11 | 0 | 67 | 283 | 0 | 0 | 181 | 0 | 186 | 0 | 94 | 0 | 166 | 0 | 332 | 105 | 0 | 70 | 108 |  | 7117 | 3097 | 10214 | 3305 | 851 | 2027 | 3006 | 350 | 95 | 408 | 156 | 16 | 0 | 80.51
14:00 | 36 | 94 | 170 | 120 | 250 | 0 | 0 | 0 | 338 | 96 | 0 | 330 | 255 | 90 | 84 | 55 | 0 | 0 | 0 | 0 | 82 | 102 | 149 | 73 | 52 | 0 | 0 | 54 | 56 | 55 | 19 | 25 | 23 | 33 | 33 | 50 | 0 | 65 | 30 | 110 | 120 | 24 | 0 | 0 | 0 | 0 | 0 | 33 | 38 | 77 | 68 | 100 | 39 | 19 | 6 | 0 | 0 | 80 | 330 | 340 | 192 | 80 | 100 | 14 | 10 | 5 | 45 | 0 | 0 | 52 | 19 | 8 | 25 | 18 | 158 | 86 | 85 | 20 | 1 | 58 | 50 | 50 | 50 | 100 | 129 | 48 | 78 | 25 | 74 | 0 | 39 | 10 | 270 | 24 | 11 | 0 | 214 | 0 | 0 | 100 | 0 | 149 | 16 | 89 | 200 | 100 | 0 | 68 | 0 |  | 852 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 12 | 40 | 145 | 20 | 80 | 0 | 0 | 0 | 50 | 0 | 93 | 6 | 50 | 0 | 34 | 0 | 22 | 14 | 11 | 0 | 65 | 270 | 0 | 0 | 176 | 0 | 152 | 0 | 95 | 0 | 148 | 0 | 280 | 105 | 0 | 70 | 108 |  | 7073 | 2997 | 10070 | 3310 | 852 | 1867 | 3017 | 335 | 95 | 419 | 158 | 17 | 0 | 80.5
15:00 | 36 | 94 | 171 | 120 | 250 | 0 | 0 | 0 | 337 | 110 | 0 | 380 | 280 | 97 | 97 | 55 | 0 | 0 | 0 | 0 | 91 | 102 | 149 | 73 | 51 | 0 | 0 | 54 | 56 | 55 | 19 | 25 | 24 | 33 | 8 | 50 | 0 | 62 | 30 | 110 | 120 | 24 | 0 | 0 | 65 | 0 | 0 | 33 | 38 | 84 | 68 | 104 | 40 | 19 | 2 | 0 | 0 | 80 | 330 | 338 | 216 | 82 | 80 | 14 | 10 | 5 | 45 | 0 | 0 | 52 | 19 | 8 | 25 | 18 | 164 | 86 | 85 | 20 | 1 | 57 | 61 | 50 | 50 | 130 | 122 | 52 | 78 | 25 | 74 | 0 | 37 | 10 | 295 | 24 | 11 | 0 | 260 | 0 | 0 | 100 | 0 | 148 | 13 | 100 | 200 | 100 | 15 | 68 | 0 |  | 851 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 12 | 40 | 145 | 22 | 110 | 0 | 0 | 0 | 50 | 0 | 93 | 6 | 50 | 0 | 33 | 0 | 22 | 14 | 11 | 0 | 67 | 265 | 0 | 0 | 192 | 0 | 163 | 0 | 95 | 0 | 152 | 0 | 300 | 90 | 0 | 72 | 108 |  | 7374 | 3062 | 10436 | 3407 | 851 | 1989 | 3161 | 332 | 92 | 426 | 164 | 14 | 0 | 80.49
16:00 | 36 | 93 | 170 | 120 | 250 | 0 | 0 | 0 | 323 | 110 | 0 | 380 | 250 | 80 | 97 | 55 | 0 | 0 | 0 | 0 | 70 | 48 | 149 | 75 | 51 | 0 | 0 | 54 | 56 | 55 | 19 | 25 | 24 | 33 | 33 | 50 | 0 | 60 | 30 | 110 | 120 | 24 | 0 | 0 | 145 | 0 | 0 | 33 | 38 | 84 | 68 | 103 | 34 | 19 | 3 | 0 | 0 | 80 | 330 | 300 | 217 | 82 | 90 | 14 | 10 | 5 | 45 | 0 | 0 | 52 | 19 | 8 | 25 | 18 | 168 | 86 | 85 | 20 | 0 | 57 | 67 | 50 | 50 | 130 | 122 | 49 | 74 | 25 | 74 | 0 | 37 | 10 | 265 | 24 | 11 | 0 | 270 | 0 | 0 | 50 | 0 | 148 | 7 | 100 | 200 | 100 | 15 | 68 | 0 |  | 851 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 15 | 40 | 145 | 18 | 110 | 0 | 0 | 0 | 50 | 0 | 93 | 6 | 8 | 0 | 8 | 0 | 22 | 14 | 11 | 0 | 67 | 265 | 0 | 0 | 178 | 0 | 162 | 0 | 98 | 0 | 153 | 0 | 300 | 90 | 0 | 72 | 108 |  | 7234 | 2970 | 10204 | 3472 | 851 | 1941 | 2914 | 332 | 90 | 429 | 168 | 7 | 0 | 80.48
17:00 | 36 | 94 | 100 | 120 | 250 | 0 | 0 | 0 | 293 | 110 | 0 | 350 | 242 | 35 | 97 | 55 | 0 | 0 | 0 | 0 | 15 | 24 | 149 | 30 | 52 | 0 | 0 | 54 | 56 | 55 | 19 | 25 | 24 | 33 | 17 | 50 | 0 | 60 | 30 | 110 | 120 | 24 | 0 | 0 | 130 | 0 | 0 | 33 | 38 | 84 | 78 | 104 | 39 | 19 | 7 | 0 | 0 | 80 | 300 | 300 | 184 | 82 | 90 | 14 | 10 | 5 | 45 | 0 | 0 | 52 | 21 | 8 | 25 | 20 | 154 | 86 | 85 | 20 | 0 | 57 | 67 | 11 | 10 | 130 | 122 | 40 | 40 | 25 | 67 | 0 | 39 | 10 | 260 | 24 | 11 | 0 | 275 | 0 | 0 | 50 | 0 | 149 | 2 | 100 | 200 | 100 | 20 | 58 | 0 |  | 851 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 33 | 8 | 135 | 19 | 110 | 0 | 0 | 0 | 50 | 0 | 93 | 6 | 8 | 0 | 8 | 0 | 21 | 16 | 11 | 0 | 67 | 265 | 0 | 0 | 176 | 0 | 167 | 0 | 44 | 0 | 153 | 0 | 300 | 105 | 0 | 72 | 108 |  | 6709 | 2909 | 9618 | 3295 | 851 | 1717 | 2730 | 332 | 90 | 447 | 154 | 2 | 0 | 80.47
18:00 | 36 | 94 | 90 | 120 | 250 | 0 | 0 | 0 | 273 | 110 | 0 | 320 | 235 | 24 | 97 | 55 | 20 | 0 | 0 | 0 | 15 | 24 | 149 | 10 | 52 | 0 | 0 | 54 | 56 | 55 | 19 | 25 | 24 | 33 | 33 | 50 | 0 | 60 | 30 | 110 | 120 | 24 | 0 | 0 | 130 | 0 | 0 | 33 | 42 | 84 | 78 | 98 | 40 | 0 | 10 | 0 | 0 | 80 | 270 | 250 | 184 | 82 | 90 | 14 | 10 | 5 | 45 | 0 | 0 | 40 | 21 | 8 | 25 | 21 | 148 | 86 | 70 | 20 | 0 | 60 | 67 | 11 | 10 | 100 | 122 | 43 | 10 | 25 | 65 | 0 | 40 | 10 | 245 | 24 | 11 | 0 | 278 | 0 | 0 | 50 | 0 | 142 | 0 | 100 | 140 | 100 | 0 | 58 | 0 |  | 849 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 35 | 37 | 8 | 135 | 26 | 110 | 0 | 0 | 0 | 50 | 10 | 93 | 6 | 8 | 12 | 8 | 0 | 20 | 16 | 11 | 0 | 68 | 265 | 0 | 0 | 172 | 0 | 147 | 0 | 24 | 0 | 149 | 0 | 230 | 53 | 0 | 72 | 108 |  | 6362 | 2821 | 9183 | 3179 | 849 | 1512 | 2560 | 333 | 90 | 512 | 148 | 0 | 0 | 80.46
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 36 | 94 | 81 | 120 | 225 | 0 | 0 | 0 | 265 | 110 | 0 | 320 | 210 | 55 | 64 | 55 | 75 | 0 | 0 | 0 | 20 | 102 | 149 | 39 | 52 | 0 | 0 | 54 | 56 | 55 | 19 | 25 | 18 | 33 | 33 | 11 | 0 | 75 | 30 | 110 | 120 | 25 | 0 | 0 | 130 | 0 | 0 | 41 | 61 | 84 | 102 | 105 | 39 | 19 | 26 | 0 | 0 | 80 | 260 | 250 | 183 | 82 | 90 | 17 | 10 | 5 | 45 | 0 | 50 | 43 | 22 | 8 | 25 | 21 | 176 | 90 | 85 | 20 | 0 | 60 | 67 | 50 | 33 | 100 | 121 | 46 | 79 | 45 | 45 | 18 | 41 | 10 | 240 | 24 | 11 | 0 | 271 | 0 | 0 | 137 | 0 | 149 | 0 | 100 | 165 | 100 | 0 | 68 | 0 |  | 948 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 40 | 60 | 40 | 135 | 36 | 110 | 12 | 0 | 0 | 50 | 51 | 93 | 12 | 33 | 44 | 34 | 33 | 22 | 16 | 11 | 0 | 69 | 265 | 17 | 18 | 167 | 0 | 140 | 0 | 80 | 0 | 148 | 0 | 230 | 105 | 0 | 72 | 109 |  | 6885 | 3299 | 10184 | 3197 | 948 | 1735 | 2927 | 334 | 105 | 762 | 176 | 0 | 0 | 80.45
19:30 | 36 | 93 | 90 | 120 | 225 | 0 | 0 | 0 | 263 | 27 | 0 | 280 | 250 | 7 | 30 | 30 | 75 | 0 | 0 | 0 | 30 | 50 | 149 | 60 | 53 | 0 | 43 | 54 | 56 | 55 | 19 | 25 | 18 | 25 | 33 | 43 | 0 | 77 | 30 | 110 | 120 | 25 | 0 | 0 | 130 | 0 | 0 | 41 | 61 | 84 | 102 | 105 | 39 | 19 | 33 | 0 | 0 | 80 | 260 | 250 | 183 | 82 | 86 | 17 | 10 | 5 | 45 | 0 | 0 | 52 | 22 | 8 | 25 | 0 | 170 | 90 | 85 | 20 | 0 | 60 | 67 | 53 | 50 | 100 | 124 | 52 | 79 | 45 | 70 | 18 | 40 | 10 | 255 | 24 | 11 | 0 | 140 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 200 | 100 | 0 | 68 | 0 |  | 948 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 40 | 50 | 40 | 139 | 36 | 110 | 0 | 0 | 0 | 50 | 53 | 63 | 12 | 8 | 48 | 25 | 35 | 22 | 17 | 11 | 0 | 70 | 250 | 17 | 17 | 155 | 0 | 137 | 0 | 96 | 0 | 146 | 0 | 230 | 105 | 0 | 72 | 108 |  | 6720 | 3176 | 9896 | 3193 | 948 | 1751 | 2740 | 320 | 107 | 667 | 170 | 0 | 0 | 0
20:00 | 36 | 94 | 90 | 120 | 250 | 0 | 0 | 0 | 263 | 0 | 0 | 280 | 250 | 30 | 0 | 15 | 75 | 0 | 0 | 0 | 0 | 32 | 149 | 0 | 54 | 0 | 32 | 54 | 56 | 35 | 19 | 25 | 18 | 33 | 33 | 43 | 0 | 80 | 30 | 110 | 120 | 25 | 0 | 0 | 130 | 0 | 0 | 41 | 30 | 84 | 101 | 105 | 39 | 19 | 37 | 0 | 0 | 80 | 260 | 250 | 183 | 82 | 90 | 17 | 10 | 5 | 45 | 0 | 0 | 52 | 22 | 11 | 25 | 0 | 174 | 90 | 85 | 20 | 0 | 58 | 67 | 53 | 50 | 100 | 123 | 53 | 79 | 45 | 70 | 18 | 41 | 10 | 240 | 24 | 0 | 0 | 160 | 0 | 0 | 200 | 0 | 118 | 0 | 100 | 200 | 100 | 0 | 68 | 0 |  | 948 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 40 | 51 | 8 | 139 | 32 | 96 | 0 | 0 | 0 | 50 | 23 | 63 | 12 | 8 | 0 | 8 | 35 | 22 | 16 | 0 | 0 | 69 | 250 | 17 | 16 | 155 | 0 | 144 | 0 | 96 | 0 | 146 | 0 | 230 | 70 | 0 | 72 | 108 |  | 6515 | 2969 | 9484 | 3217 | 948 | 1736 | 2422 | 319 | 110 | 558 | 174 | 0 | 0 | 80.44
21:00 | 36 | 94 | 90 | 120 | 250 | 0 | 0 | 0 | 260 | 0 | 0 | 280 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 115 | 0 | 54 | 0 | 43 | 54 | 36 | 35 | 19 | 25 | 18 | 33 | 33 | 50 | 0 | 80 | 30 | 110 | 120 | 25 | 0 | 0 | 131 | 0 | 0 | 41 | 30 | 51 | 102 | 105 | 40 | 19 | 38 | 0 | 0 | 80 | 260 | 250 | 184 | 82 | 90 | 17 | 10 | 5 | 45 | 0 | 0 | 25 | 22 | 11 | 25 | 5 | 176 | 91 | 84 | 20 | 0 | 58 | 67 | 53 | 50 | 100 | 124 | 64 | 80 | 45 | 62 | 19 | 41 | 10 | 275 | 24 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 92 | 0 | 100 | 200 | 70 | 0 | 68 | 0 |  | 948 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 136 | 35 | 80 | 0 | 0 | 0 | 0 | 0 | 40 | 12 | 8 | 0 | 8 | 30 | 14 | 17 | 0 | 0 | 69 | 250 | 17 | 16 | 158 | 0 | 158 | 0 | 66 | 0 | 148 | 0 | 230 | 70 | 0 | 72 | 108 |  | 6118 | 2714 | 8832 | 3182 | 948 | 1736 | 2062 | 319 | 110 | 299 | 176 | 0 | 0 | 80.43
22:00 | 36 | 94 | 87 | 120 | 230 | 0 | 0 | 0 | 270 | 0 | 0 | 300 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 10 | 0 | 42 | 54 | 18 | 17 | 19 | 25 | 11 | 33 | 25 | 25 | 0 | 80 | 30 | 110 | 120 | 25 | 0 | 0 | 131 | 0 | 0 | 41 | 30 | 51 | 30 | 105 | 40 | 19 | 39 | 0 | 0 | 80 | 260 | 250 | 183 | 82 | 90 | 17 | 10 | 5 | 45 | 0 | 0 | 16 | 22 | 11 | 25 | 21 | 172 | 91 | 84 | 20 | 0 | 58 | 67 | 53 | 50 | 100 | 125 | 40 | 79 | 45 | 70 | 19 | 40 | 10 | 240 | 25 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 59 | 0 | 100 | 144 | 0 | 0 | 68 | 0 |  | 948 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 36 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 18 | 16 | 0 | 0 | 69 | 250 | 17 | 16 | 157 | 0 | 159 | 0 | 41 | 0 | 151 | 0 | 200 | 70 | 0 | 17 | 63 |  | 5508 | 2412 | 7920 | 3148 | 948 | 1679 | 1366 | 319 | 110 | 178 | 172 | 0 | 0 | 80.42
23:00 | 36 | 94 | 50 | 110 | 240 | 0 | 0 | 0 | 300 | 0 | 0 | 360 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 38 | 35 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 8 | 0 | 80 | 30 | 110 | 120 | 25 | 0 | 0 | 135 | 0 | 0 | 41 | 0 | 0 | 10 | 105 | 40 | 19 | 40 | 0 | 0 | 80 | 240 | 250 | 204 | 82 | 90 | 17 | 10 | 5 | 45 | 0 | 0 | 0 | 22 | 11 | 0 | 15 | 168 | 103 | 40 | 20 | 0 | 58 | 67 | 53 | 50 | 100 | 128 | 63 | 79 | 45 | 85 | 19 | 8 | 10 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 140 | 0 | 0 | 48 | 0 |  | 851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 8 | 0 | 67 | 226 | 0 | 0 | 168 | 0 | 147 | 0 | 42 | 0 | 148 | 0 | 250 | 0 | 0 | 17 | 35 |  | 5120 | 2167 | 7287 | 3053 | 851 | 1821 | 975 | 293 | 110 | 16 | 168 | 0 | 0 | 80.41
24:00 | 36 | 94 | 50 | 110 | 250 | 0 | 0 | 0 | 320 | 0 | 0 | 360 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 18 | 17 | 0 | 25 | 0 | 0 | 29 | 8 | 0 | 80 | 30 | 110 | 120 | 25 | 0 | 0 | 131 | 0 | 0 | 41 | 0 | 0 | 10 | 103 | 40 | 19 | 41 | 0 | 0 | 80 | 300 | 300 | 193 | 82 | 90 | 17 | 10 | 5 | 45 | 0 | 0 | 0 | 22 | 11 | 0 | 21 | 158 | 104 | 0 | 20 | 0 | 58 | 67 | 53 | 50 | 130 | 128 | 63 | 79 | 45 | 73 | 19 | 8 | 10 | 295 | 25 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 140 | 0 | 0 | 48 | 0 |  | 850 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 16 | 8 | 0 | 66 | 184 | 0 | 0 | 197 | 0 | 192 | 0 | 93 | 0 | 175 | 0 | 350 | 0 | 0 | 17 | 17 |  | 5267 | 2357 | 7624 | 3294 | 850 | 2038 | 924 | 250 | 110 | 0 | 158 | 0 | 0 | 80.4
KWH | 718000 | 2414400 | 3471000 | 2835000 | 5890036 | 0 | 0 | 0 | 7322000 | 849700 | 0 | 8947875 | 6398516 | 1123200 | 885312 | 529530 | 174800 | 0 | 1199000 | 0 | 753600 | 1029888 | 1977600 | 669257 | 1094400 | 0 | 192576 | 1152360 | 996327 | 959820 | 405072 | 600000 | 479160 | 695700 | 734400 | 950496 | 0 | 1602060 | 380000 | 2400000 | 2900000 | 594124 | 0 | 0 | 1119342 | 0 | 0 | 939840 | 902112 | 1694231 | 1814640 | 2440320 | 976320 | 432576 | 490560 | 0 | 0 | 1923456 | 7475000 | 7036500 | 5104000 | 2392000 | 1723050 | 312408 | 248640 | 120000 | 1004344 | 0 | 48488 | 923534 | 469296 | 205740 | 545200 | 406080 | 3470400 | 2266840 | 1637760 | 456804 | 16000 | 1392000 | 1241040 | 978000 | 1103000 | 3538271 | 2829000 | 1332576 | 1758720 | 905400 | 1970100 | 98000 | 877960 | 243180 | 6691450 | 526680 | 223968 | 397440 | 2295820 | 93042 | 0 | 2109600 | 19958 | 2105280 | 137295 | 2359680 | 4224000 | 1957090 | 57100 | 1647600 | 0 |  | 19354909 | 0 | 0 | 0 | 1391960 | 0 | 0 | 0 | 172320 | 315904 | 550125 | 3440280 | 581007 | 1341216 | 10815 | 0 | 0 | 539734 | 72074 | 1777886 | 170870 | 715339 | 249046 | 623040 | 127427 | 479760 | 368136 | 231624 | 0 | 1615854 | 5480800 | 80600 | 82000 | 4537009 | 0 | 4275536 | 0 | 2023767 | 55680 | 4110300 | 0 | 7125818 | 1796160 | 0 | 1446720 | 2339400 |  | 155033940 | 67483116 | 222517056 | 80658073 | 19354909 | 47199888 | 54551540 | 7096654 | 1982060 | 8050237 | 3470400 | 153295 | 0
Fuel Cost | 617480 | 2076384 | 2985060 | 2438100 | 3769623.04 | 0 | 0 | 0 | 4466420 | 8165617 | 0 | 5995076.25 | 97193458.04 | 7053696 | 5913884.16 | 3235428.3 | 113620 | 0 | 1330890 | 0 | 4710000 | 6786961.92 | 19123392 | 4263167.09 | 6555456 | 0 | 1284481.92 | 8216326.8 | 6227043.75 | 6018071.4 | 303804 | 450000 | 0 | 0 | 0 | 8991692.16 | 0 | 0 | 0 | 2640000 | 3190000 | 5626354.28 | 0 | 0 | 1287243.3 | 0 | 0 | 8261193.6 | 9715746.24 | 16484867.63 | 11232621.6 | 15764467.2 | 6385132.8 | 367689.6 | 0 | 0 | 0 | 1750344.96 | 4634500 | 4855185 | 3572800 | 1650480 | 1654128 | 209313.36 | 213830.4 | 110400 | 823562.08 | 0 | 525609.92 | 6852622.28 | 361357.92 | 154305 | 419804 | 304560 | 23737536 | 1700130 | 15051014.4 | 351739.08 | 0 | 1447680 | 1290681.6 | 938880 | 992700 | 2759851.38 | 1980300 | 1519136.64 | 1881830.4 | 995940 | 2245914 | 125440 | 816502.8 | 226157.4 | 4282528 | 395010 | 170215.68 | 6887635.2 | 16667653.2 | 1612417.86 | 0 | 15083640 | 340283.9 | 0 | 0 | 0 | 39452160 | 18279220.6 | 49677 | 0 | 0 |  | 98710035.9 | 0 | 0 | 0 | 11539348.4 | 0 | 0 | 0 | 1940323.2 | 3721349.12 | 4334985 | 2373793.2 | 575196.93 | 9924998.4 | 364249.2 | 0 | 0 | 6179954.3 | 772633.28 | 15929858.56 | 1478025.5 | 6366517.1 | 2652339.9 | 6180556.8 | 1499815.79 | 527736 | 346047.84 | 175339.368 | 0 | 9808233.78 | 21155888 | 2597738 | 2195140 | 3085166.12 | 0 | 2992875.2 | 0 | 0 | 964934.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 488615128.14 | 218393079.288 | 707008207.428 | 59389290.068 | 98710035.9 | 27603139.48 | 382901067.06 | 30964121.78 | 0 | 83703017.14 | 23737536 | 0 | 0
Yesterday Day Peak | 36 | 93 | 170 | 120 | 250 | 0 | 0 | 0 | 252 | 63 | 0 | 400 | 245 | 76 | 60 | 34 | 0 | 0 | 84 | 0 | 73 | 74 | 149 | 57 | 46 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 33 | 33 | 50 | 0 | 68 | 30 | 110 | 120 | 25 | 0 | 0 | 0 | 0 | 0 | 33 | 38 | 68 | 68 | 96 | 40 | 19 | 3 | 0 | 0 | 80 | 330 | 300 | 222 | 110 | 100 | 14 | 10 | 5 | 45 | 0 | 0 | 52 | 19 | 8 | 25 | 15 | 152 | 90 | 78 | 20 | 2.5 | 57 | 50 | 31 | 50 | 130 | 130 | 58 | 78 | 22 | 79 | 0 | 34 | 10 | 290 | 24 | 11 | 0 | 105 | 0 | 0 | 80 | 0 | 149 | 14.66 | 89 | 200 | 100 | 0 | 68 | 0 |  | 851 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 6 | 40 | 145 | 18 | 48 | 0 | 0 | 0 | 50 | 0 | 93 | 6 | 43 | 0 | 34 | 0 | 22 | 14 | 11 | 0 | 65 | 280 | 0 | 0 | 190 | 0 | 188 | 0 | 93 | 0 | 168 | 0 | 322 | 90 | 0 | 70 | 108 |  | 9943.16 | DayPeak
Yesterday Evening Peak | 36 | 94 | 81 | 120 | 225 | 0 | 0 | 0 | 265 | 110 | 0 | 320 | 210 | 55 | 64 | 55 | 75 | 0 | 0 | 0 | 20 | 102 | 149 | 39 | 52 | 0 | 0 | 54 | 56 | 55 | 19 | 25 | 18 | 33 | 33 | 11 | 0 | 75 | 30 | 110 | 120 | 25 | 0 | 0 | 130 | 0 | 0 | 41 | 61 | 84 | 102 | 105 | 39 | 19 | 26 | 0 | 0 | 80 | 260 | 250 | 183 | 82 | 90 | 17 | 10 | 5 | 45 | 0 | 50 | 43 | 22 | 8 | 25 | 21 | 176 | 90 | 85 | 20 | 0 | 60 | 67 | 50 | 33 | 100 | 121 | 46 | 79 | 45 | 45 | 18 | 41 | 10 | 240 | 24 | 11 | 0 | 271 | 0 | 0 | 137 | 0 | 149 | 0 | 100 | 165 | 100 | 0 | 68 | 0 |  | 948 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 40 | 60 | 40 | 135 | 36 | 110 | 12 | 0 | 0 | 50 | 51 | 93 | 12 | 33 | 44 | 34 | 33 | 22 | 16 | 11 | 0 | 69 | 265 | 17 | 18 | 167 | 0 | 140 | 0 | 80 | 0 | 148 | 0 | 230 | 105 | 0 | 72 | 109 |  | 10184 | EvPeak
Forecast for Evening | 36 | 94 | 170 | 120 | 250 | 0 | 0 | 0 | 360 | 110 | 0 | 450 | 335 | 100 | 100 | 55 | 0 | 0 | 97 | 0 | 100 | 102 | 149 | 100 | 54 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 80 | 30 | 110 | 120 | 25 | 0 | 0 | 130 | 0 | 0 | 41 | 70 | 85 | 100 | 98 | 39 | 22 | 40 | 0 | 0 | 80 | 360 | 360 | 220 | 110 | 50 | 40 | 10 | 5 | 45 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 169 | 160 | 85 | 20 | 0 | 60 | 66 | 50 | 50 | 163 | 140 | 66 | 85 | 46 | 120 | 20 | 45 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 |  |  | 960 | 46 | 0 | 0 | 115 | 0 | 0 | 0 | 40 | 80 | 40 | 145 | 33 | 110 | 26 | 0 | 0 | 50 | 55 | 100 | 35 | 50 | 44 | 43 | 36 | 22 | 17 | 11 | 0 | 65 | 185 | 17 | 18 | 200 | 0 | 225 | 0 | 95 | 100 | 200 | 0 | 282 | 105 | 0 | 113 | 108
Forecast for Day | 36 | 94 | 170 | 120 | 250 | 0 | 0 | 0 | 360 | 110 | 0 | 450 | 335 | 100 | 100 | 55 | 0 | 0 | 97 | 0 | 100 | 102 | 149 | 100 | 54 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 80 | 30 | 110 | 120 | 25 | 0 | 0 | 130 | 0 | 0 | 41 | 70 | 85 | 100 | 98 | 39 | 22 | 40 | 0 | 0 | 80 | 360 | 360 | 220 | 110 | 50 | 40 | 10 | 5 | 45 | 0 | 0 | 52 | 22 | 11 | 33 | 21 | 131 | 160 | 85 | 20 | 2 | 60 | 66 | 50 | 50 | 163 | 140 | 66 | 85 | 46 | 120 | 0 | 45 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 20 | 100 | 200 | 150 | 0 | 115 |  |  | 862 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 40 | 50 | 40 | 145 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 6 | 35 |  | 43 | 0 | 22 | 17 | 11 | 0 | 65 | 185 | 17 | 18 | 200 | 0 | 225 | 0 | 95 | 100 | 200 | 0 | 282 | 105 | 0 | 113 | 108
Generation at 08:00(Today) | 36 | 96 | 50 | 110 | 250 | 0 | 0 | 0 | 290 | 0 | 0 | 330 | 275 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 0 | 25 | 14 | 28 | 29 | 0 | 0 | 80 | 0 | 110 | 120 | 0 | 0 | 0 | 131 | 0 | 0 | 41 | 0 | 0 | 10 | 0 | 6 | 19 | 42 | 0 | 0 | 80 | 250 | 250 | 191 | 45 | 50 | 16 | 5 | 5 | 5 | 0 | 0 | 0 | 22 | 11 | 0 | 15 | 98 | 159 | 0 | 0 | 0.8 | 30 | 67 | 11 | 10 | 100 | 123 | 55 | 10 | 10 | 80 | 0 | 5 | 0 | 285 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 11 | 0 | 66 | 185 | 0 | 0 | 170 | 0 | 169 | 0 | 12 | 0 | 164 | 0 | 280 | 0 | 0 | 17 | 0 | 0
199
| Minimum Generation |  | 8060.9 | 6:00
| Highest Generation |  | 10436 | 15:00
| Day Peak Generation |  | 9943.16 | 12:00
| Evening Peak Generation |  | 10184 | 19:00
| HVDC Max Flow |  | 948 | 19:00
| HVDC EvPeak Flow |  | 948 | 19:00
| Load factor L.F |  | 88.84%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-04-22
Till now the maximum generation is : - |  |  | 11623 MW | 19:30 | Hrs on | 2018-09-19
The Summary of Yesterday's |  | 2019-04-21 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9943.16 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 6146.7 | MW
Evening Peak Generation : |  | 10184 | MW Hour : | 19:00 | Available Max Generation : |  | 13068 | MW
E.P. Demand (at gen end) : |  | 10184 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 10000 | MW
Maximum Generation : |  | 10436 | MW Hour : | 15:00 | Reserve(Generation end) |  | 3068 | MW
Total Gen. (MKWH) : |  | 222.5171 | System Load Factor : | 88.84% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -320 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-04-22
Actual : | 80.22 | Ft.(MSL) , | Rule curve : | 83.8 | Ft.( MSL )
Gas Consumed : | Total = | 1130.79 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 86992429.548
|  | Coal : | 30964121.78 | Oil : | 466604084.2 | Total : | 584560635.528
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3574.7697 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1212.914 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1086.2487 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 981.3461 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 886.9227 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 715.7084 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 403.6705 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 184.3678 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 551.9732 |  |  | 0 | 0%
Total | 0 |  | 9597.9212 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1 |  | 7) Ghorashal Unit-1
|  |  |  | 2) Khulna ST 110 MW |  | 8) Haripur SBU-1,2
|  |  |  | 3) Sikalbaha ST 60 MW |  | 9) Haripur 412 MW
|  |  |  | 4) Bheramara 410 MW. |  | 10) Ghorasal Max
|  |  |  | 5) Siddhirganj ST |  | 11) Ghorasal Unit-7 ST
|  |  |  | 6) Ashuganj #3,4 |  | 12) Sikalbaha 225 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Hathazari-Baroierhat 132 kV Ckt-2 was under shut down from 08:12 to 17:43 for C/M.
b) Chowmuhoni 132/33 kV T1 transformer was under shut down from 07:55 to 10:55 for C/M.
c) Naogaon 132/33 kV T2 transformer was under shut down from 08:20 to 09:20 due to red hot at 33 kV
Y-phase bushing.
d) Dohazari 132/33 kV T1 transformer was under shut down from 11:02 to 12:58 due to red hot at 33 kV
R-phase clamp of incoming breaker.
e) After maintenance Sreemongal-Fenchuganj 132 kV Ckt-2 switched on at 11:40.
f) Raozan unit-1 tripped at 12:03 due to tripping of boiler and was synchronized at 13:21.
g) Siddirganj GT-1 was shut down at 12:26 for gas shortage.
h) Modunaghat 132/33 kV T1 transformer was under shut down from 20:32 to 21:59 due to red hot maintenance
at R-phase DS.
i) Siddirganj GT-2 was synchronized at 00:10(22/04/2019).
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-04-21 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 36 | 718000 | Unit-1 under maint.
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 94 | 2414400 | On test
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 81 | 3471000 | On test
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 120 | 2835000
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 225 | 5890036
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 110 | 849700
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 265 | 7322000 | Gas shortage
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 320 | 8947875 | Frequency control
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 55 | 1123200 | Low demand
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 210 | 6398516 | FGMO
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 64 | 885312 | Low demand
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 529530
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 39 | 669257 | Low demand
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 405072 | Engine problem
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 0 | 1199000 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 0 | Contract Expired
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 20 | 753600 | Low demand
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 75 | 174800
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 102 | 1029888
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 0 | 192576 | Engine problem
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 1152360
25 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 1977600
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 56 | 996327
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 959820
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 52 | 1094400 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 43 | 1079160 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 695700
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 734400
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 11 | 950496 | Low demand
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
34 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 271 | 2295820 | Engine problem
35 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 0 | 93042 | Reserve
36 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
37 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 19958 | Reserve
38 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 149 | 2105280
| Gazipur 100 MW |  | RPCL | 100 MW | 0 | 0 | 0 | on test
| Dhaka area Total |  |  |  | 5798 | 2796 | 59963125
39 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 110 | 2400000 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage
40 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 594124
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 137295
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 39 | 976320 | Engine problem
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 105 | 1982060 | Low water level
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Gas shortage
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 130 | 1119342
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 41 | 939840 | Engine problem
47 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 61 | 902112
48 | Dohazari Peaking |  | PDB | 6*17 | 102 | 84 | 1694231
49 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 102 | 1814640
| Juldah 100 MW Unit-3 |  | IPP | 0 | 100 | 100 | 2359680
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 432576
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 490560
51 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 105 | 2440320
| Chattogram area Total |  |  |  | 1681 | 1067 | 21183100
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1923456 | Gas shortage
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 183 | 5104000
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 7475000 | Frequency control
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 250 | 7036500 | Frequency control
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 17 | 312408 | Gas shortage
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 10 | 248640 | Gas shortage
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 82 | 2392000 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 45 | 1004344 | Engine problem
| Midland 150MW |  | IPP | 23*7.015 | 150 | 100 | 1957090 | Engine problem
61 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
62 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 50 | 48488
63 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 1723050 | Gas shortage
| Chandpur Desh 200MW |  | IPP | 0 | 200 | 165 | 4224000
64 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 469296
65 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 205740 | Engine problem
** | Tripura |  | Imported power | 0 | 160 | 176 | 3470400
66 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 25 | 545200 | Gas shortage
67 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 43 | 923534 | Engine problem
68 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 406080 | Engine problem
69 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 397440 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1632 | 39986666
70 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 90 | 2266840 | Gas shortage
71 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 20 | 456804
72 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 85 | 1637760 | Engine problem
73 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 16000
74 | United Mymensingh PPL |  | IPP | 200 | 200 | 137 | 2109600 | Low demand
| United Jamalpur PPL |  | IPP | 115 MW | 115 | 68 | 1647600 | Low demand
| Mymensingh Area Total |  |  |  | 637 | 400 | 8134604
75 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1392000
76 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 67 | 1241040
77 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 100 | 3538271 | Frequency control
78 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 121 | 2829000
79 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 50 | 978000
80 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 33 | 1103000
81 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 223968
82 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 46 | 1332576 | FGMO
83 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 79 | 1758720
84 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 45 | 905400
85 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 45 | 1970100 | FGMO
86 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 18 | 98000
87 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 41 | 877960 | Engine problem
88 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 24 | 526680
89 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 240 | 6691450 | FGMO
| Bibiyana-3 285 MW |  | PDB | 285 MW | 0 | 0 | 57100 | On test
90 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 243180
| Sylhet Area Total |  |  |  | 1549 | 990 | 25766445
91 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 948 | 19354909
92 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
93 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 1391960
94 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 40 | 172320
95 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
96 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 60 | 315904 | Low demand
97 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
98 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 550125
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
99 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 0 | 55680 | Reserve
| Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 105 | 1796160
| Madhumati Power Plant |  | IPP | 100 MW | 0 | 109 | 2339400 | on test.
| Khulna Area Total |  |  |  | 2209 | 1401 | 25976458
100 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 110 | 1341216
101 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 12 | 10815 | Low demand
102 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 36 | 581007
103 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 135 | 3440280
104 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 80 | 2023767
| Barisal Area Total |  |  |  | 462 | 373 | 7397085
105 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
106 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 50 | 539734
107 | Bera Peaking |  | PDB | 9*8.29 | 71 | 51 | 72074
108 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 12 | 170870 | Engine problem
109 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 33 | 715339
110 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 44 | 249046
111 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 167 | 4537009 | FGMO
112 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 140 | 4275536 | FGMO
113 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 148 | 4110300 | FGMO
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282 | 282 | 230 | 7125818 | Gas shortage
114 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 33 | 127427
115 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 479760
116 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 16 | 368136
117 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 231624
118 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 34 | 623040 | Engine problem
119 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 93 | 1777886
| Paramount Baghabari |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
| Confidence CPBL-2 |  | IPP | 113 MW | 113 | 72 | 1446720 | Low demand
| Rajshahi Area Total |  |  |  | 1938 | 1156 | 26850319
120 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 69 | 1615854
121 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 265 | 5480800
122 | Rangpur GT |  | PDB | 1*20 | 20 | 17 | 80600
123 | Saidpur GT |  | PDB | 1*20 | 20 | 18 | 82000
| Rangpur Area Total |  |  |  | 484 | 369 | 7259254
| Total |  |  |  | 17649 | 10184 | 222517056
| Eastern Grid Total |  |  |  | 12556 | 6885 | 155033940
| Western Grid Total |  |  |  | 5093 | 3299 | 67483116
| National Grid Total |  |  |  | 17649 | 10184 | 222517056
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2019-04-21 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 6937 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2828 | MW
i) Dhaka area |  |  | 3605 | MW | i) Khulna area |  |  | 1052 | MW
ii) Chittagong area |  |  | 1044 | MW | ii) Rajshahi area |  |  | 858 | MW
iii) Comilla area |  |  | 1017 | MW | iii) Barisal area |  |  | 277 | MW
iv) Mymensingh area |  |  | 858 | MW | iv) Rangpur area |  |  | 641 | MW
v) Sylhet area |  |  | 413 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 9765 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 118 | 1200 | Netrokona | 93 | 1930 | Central s/s | 87 | 1900
Munsiganj | 108 | 1900 | Jamalpur | 124 | 1900 | Noapara | 89 | 1900
Sonargaon | 57 | 2000 | Sherpur | 92 | 1930 | Jessore | 130 | 1300
Shyampur | 200 | 900 | Srimongal | 32 | 1900 | Jhenida | 78 | 100
Bhulta | 179 | 1200 | Shahjibazar | 110 | 1900 | Bottail | 100 | 100
Madanganj | 57 | 100 | Fenchuganj | 38 | 2200 | G.K Project | 40 | 100
Shitalakhya | 115 | 1500 | Kulawara | 40 | 2000 | Faridpur | 150 | 1900
Rahim steel | 22 | 700 | Sylhet | 120 | 1900 | Madaripur | 127 | 1930
Matuail | 94 | 1000 | Chatak | 27 | 2100 | Gopalganj | 80 | 2000
Ghorasal | 74 | 1900 | Sunamganj | 31 | 1930 | Bagerhat | 79 | 1900
Narsingdi | 119 | 100 | Biani Bazar | 41 | 2200 | Mongla | 40 | 900
Haripur (SBU) | 104 | 1200 | Comilla (S) | 176 | 2100 | Satkhira | 93 | 1900
Ullon | 86 | 1830 | Comilla(N) | 115 | 2200 | Gallamari | 49 | 1300
Hasnabad | 190 | 2000 | Chandpur | 96 | 1900 | Magura | 59 | 1900
Magbazar | 122 | 1300 | Feni | 126 | 1900 | Chuadanga | 68 | 100
Maniknagar | 120 | 1300 | Chowmuhani | 174 | 2100 | Barisal | 114 | 1900
Bangabhaban | 32 | 1300 | Ashuganj | 53 | 2000 | Patuakhali | 91 | 2100
Narinda | 82 | 1300 | Daudkandi | 124 | 1900 | Bhandaria | 50 | 1930
Dhanmondi | 151 | 1300 | B.Baria | 133 | 2100 | Ishurdi | 59 | 100
Lalbag | 83 | 1300 | Ramganj | 72 | 1900 | Ruppur Paromanobik | 1 | 100
Madartek | 51 | 2000 | Madunaghat | 58 | 1830 | Natore | 97 | 1500
Mirpur | 102 | 1500 | Hathazari | 91 | 2000 | Bogra | 217 | 2000
Kalyanpur | 102 | 1800 | Khulshi | 206 | 1400 | Noagaon | 118 | 2000
Gulshan | 138 | 1500 | Halishahar | 143 | 1500 | Rajshahi | 117 | 1200
Uttara | 66 | 1900 | Baraulia | 149 | 1000 | C.Nawabganj | 68 | 1200
Uttara(New) | 14 | 1100 | Sikalbaha | 34 | 1200 | Amnura | 31 | 200
Kamrangirchar | 78 | 1200 | Dohazari | 92 | 2100 | Pabna | 75 | 1500
Savar | 148 | 1200 | Cox'sbazar | 91 | 1900 | Shahjadpur | 85 | 1200
Bhasantec | 165 | 1500 | Chandraghona | 29 | 1900 | Serajganj | 85 | 1100
Agargaon | 59 | 1300 | Kaptai | 0 | 0 | Niyamatpur | 112 | 1900
Satmosjid | 95 | 1700 | A. Khaer Stl. | 4 | 2100 | Joypurhat | 50 | 1900
Tongi | 124 | 1800 | Bakulia | 106 | 1500 | Mohastangor | 14 | 1930
Kabirpur | 214 | 1500 | Julda | 21 | 1700 | Rangpur | 117 | 1900
Basundhara | 140 | 1400 | TK chemical | 4 | 1300 | Lalmonirhat | 90 | 1830
Manikganj | 91 | 1900 | Modern Steel | 16 | 1100 | Saidpur | 101 | 1900
Joydevpur | 218 | 1600 | Shahmirpur | 33 | 100 | Purbasadipur | 85 | 2000
New Tongi | 114 | 1200 | Khagrachhari | 18 | 1830 | Thakurgaon | 71 | 1930
Kodda | 234 | 1500 | Matarbari | 27 | 2000 | Palashbari | 106 | 2000
Dhamrai | 52 | 1930 | Baroiar Hat | 24 | 1930 | Barapukuria | 46 | 1900
Valuka | 68 | 1500 | Rangamati | 12 | 1900 | Panchagar | 34 | 1930
Tangail | 175 | 1900 | Abul Khair 230 | 18 | 700 | Joldhaka | 16 | 1900
Mymensing | 228 | 2000 | BSRM | 149 | 1300
Kishorganj | 114 | 1930 | Goalpara | 26 | 1900
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-04-21
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 397 | 6:00 | 387 | 13:00 | Kaliakoir | 383 | 22:00 | 366 | 9:00
Bheramara | 400 | 1:00 | 392 | 12:00 | Bhulta | 403 | 1:00 | 391 | 10:00
Ashuganj(N) | 405 | 1:00 | 396 | 10:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 221 | 1:00 | 216 | 13:00
Ishurdi | 238 | 18:00 | 226 | 4:00 | Megnaghat | 233 | 22:00 | 225 | 11:00
Ashuganj | 243 | 19:00 | 239 | 15:00 | Fenchuganj | 239 | 1:00 | 234 | 17:00
Serajganj | 235 | 1:00 | 233 | 8:00 | Siddhirganj | 228 | 1:00 | 221 | 10:00
Baghabari | 231 | 4:00 | 225 | 24:00 | Maniknagar | 227 | 1:00 | 219 | 15:00
Barapukuria | 227 | 3:00 | 218 | 19:00 | Old Airport | 227 | 1:00 | 219 | 10:00
Bogra | 230 | 4:00 | 221 | 13:00 | Barisal | 242 | 8:00 | 226 | 24:00
Khulna South | 235 | 19:30 | 210 | 24:00 | AKSML | 222 | 19:00 | 214 | 15:00
Rampura | 228 | 4:00 | 220 | 11:00 | BSRM | 223 | 6:00 | 214 | 13:00
Haripur | 228 | 19:00 | 220 | 10:00 | Bibiyana | 235 | 7:00 | 230 | 12:00
Hasnabad | 230 | 19:00 | 220 | 9:00 | Bhulta | 230 | 2:00 | 222 | 10:00
Aminbazar | 229 | 22:00 | 220 | 10:00 | Ashuganj (S) | 240 | 19:00 | 236 | 7:00
Tongi | 227 | 18:00 | 219 | 10:00 | Kaliakoir | 231 | 1:00 | 221 | 10:00
Comilla (N) | 234 | 19:00 | 230 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 1900 | 127 | 1000 | Madanhat | 135 | 500 | 128 | 1100
Munsiganj | 137 | 2200 | 126 | 1000 | Hathazari | 131 | 400 | 127 | 1300
Megnaghat | 134 | 1900 | 128 | 1200 | Khulshi | 129 | 1930 | 123 | 1300
Shyampur | 136 | 2200 | 128 | 1000 | Halishahar | 135 | 600 | 126 | 1000
Bhulta | 131 | 1900 | 123 | 1000 | Baraulia | 131 | 300 | 125 | 1200
Madanganj | 135 | 300 | 126 | 1000 | Sikalbaha | 135 | 600 | 125 | 1200
Shitalakhya | 138 | 1900 | 127 | 1000 | Dohazari | 132 | 600 | 124 | 1400
Rahim steal | 135 | 1900 | 127 | 1000 | Cox'sbazar | 127 | 600 | 115 | 1400
Matuail | 133 | 1830 | 126 | 1200 | Chandraghona | 136 | 700 | 127 | 1400
Ghorasal | 138 | 1300 | 136 | 100 | Kaptai | 0 | 0 | 0 | 0
Narsingdi | 136 | 2300 | 122 | 1500 | A. Khaer Stl. | 130 | 400 | 125 | 1300
Haripur (SBU) | 134 | 1900 | 128 | 1000 | Bakulia | 133 | 700 | 120 | 1300
Ullon | 134 | 600 | 128 | 1100 | Julda | 132 | 600 | 125 | 1400
Hasnabad | 135 | 100 | 128 | 900 | TK Chemical | 135 | 500 | 125 | 800
Magbazar | 135 | 600 | 128 | 1200 | Modern Steel | 133 | 2100 | 124 | 1100
Maniknagar | 134 | 600 | 130 | 1200 | Shahmirpur | 135 | 600 | 126 | 1500
Bangabhaban | 135 | 1930 | 124 | 900 | Khagrachhari | 133 | 700 | 125 | 1300
Narinda | 134 | 600 | 128 | 900 | Matarbari | 127 | 400 | 118 | 1400
Dhanmondi | 134 | 600 | 128 | 1100 | Baroiar Hat | 133 | 700 | 126 | 1400
Lalbag | 135 | 1930 | 124 | 900 | Rangamati | 133 | 600 | 126 | 1000
Madartek | 134 | 600 | 128 | 900 | Goalpara | 138 | 100 | 125 | 2300
Mirpur | 131 | 600 | 127 | 1100 | Central s/s | 138 | 1900 | 124 | 2300
Kalyanpur | 133 | 100 | 129 | 1200 | Noapara | 137 | 1930 | 122 | 2300
Gulshan | 134 | 100 | 127 | 1000 | Jessore | 135 | 2000 | 120 | 1300
Uttara | 130 | 500 | 125 | 1100 | Jhenida | 137 | 1930 | 119 | 100
Uttara New | 131 | 100 | 125 | 1200 | Bottail | 138 | 1930 | 125 | 600
Kamrangirchar | 134 | 1830 | 126 | 800 | G.K.Project | 141 | 1930 | 130 | 300
Savar | 131 | 100 | 126 | 1200 | Faridpur | 134 | 2100 | 120 | 2300
Bhasantec | 135 | 100 | 129 | 1200 | Madaripur | 135 | 700 | 126 | 1830
Agargaon | 136 | 100 | 130 | 1000 | Gopalganj | 140 | 800 | 129 | 2300
Satmosjid | 136 | 100 | 130 | 1200 | Bagerhat | 131 | 1300 | 121 | 2300
Tongi | 140 | 2200 | 133 | 900 | Mongla | 134 | 1100 | 121 | 2300
Kabirpur | 139 | 2200 | 130 | 1600 | Satkhira | 138 | 1930 | 122 | 2300
Basundhara | 135 | 2200 | 124 | 1000 | Gallamari | 139 | 1930 | 125 | 2300
Manikganj | 142 | 2200 | 131 | 800 | Magura | 140 | 2000 | 117 | 300
Joydevpur | 143 | 2100 | 134 | 1200 | Chuadanga | 137 | 2000 | 113 | 300
New Tongi | 140 | 2200 | 130 | 800 | Barisal | 140 | 800 | 131 | 2400
Kodda | 140 | 1900 | 125 | 700 | Patuakhali | 137 | 1800 | 125 | 2200
Dhamrai | 138 | 2300 | 129 | 2200 | Bhandaria | 137 | 1800 | 125 | 2300
Valuka | 130 | 100 | 123 | 900 | Ishurdi | 140 | 1930 | 130 | 700
Tangail | 140 | 2200 | 126 | 900 | Ruppur Paromanobik | 139 | 1800 | 132 | 500
Mymensing | 135 | 2300 | 120 | 1500 | Natore | 139 | 1930 | 121 | 700
Kishorganj | 135 | 2300 | 120 | 1900 | Bogra | 139 | 100 | 131 | 800
Netrokona | 135 | 2400 | 120 | 1900 | Noagaon | 133 | 100 | 122 | 1300
Jamalpur | 138 | 2200 | 127 | 900 | Rajshahi | 137 | 1900 | 125 | 500
Sherpur | 134 | 200 | 125 | 800 | C.Nawabganj | 135 | 1930 | 116 | 700
Srimongal | 138 | 600 | 133 | 1830 | Amnura | 139 | 1930 | 118 | 700
Shahjibazar | 137 | 600 | 130 | 1930 | Pabna | 137 | 2000 | 126 | 600
Fenchuganj | 137 | 500 | 132 | 1930 | Shahjadpur | 145 | 2000 | 136 | 1300
Khulawara | 136 | 100 | 132 | 1830 | Serajganj | 136 | 200 | 130 | 1500
Sylhet | 136 | 300 | 131 | 1100 | Niyamatpur | 131 | 2000 | 117 | 1300
Chatak | 135 | 300 | 130 | 1830 | Joypurhat | 131 | 100 | 120 | 1300
Sunamganj | 135 | 300 | 129 | 1930 | Mohastangor | 136 | 2000 | 128 | 1500
Biani Bazar | 136 | 400 | 129 | 1830 | Rangpur | 123 | 400 | 109 | 1900
Comilla(s) | 127 | 700 | 119 | 1830 | Lalmonirhat | 120 | 400 | 100 | 1900
Comilla(n) | 139 | 700 | 133 | 300 | Saidpur | 125 | 500 | 110 | 1500
Chandpur | 139 | 900 | 130 | 2300 | Purbasadipur | 125 | 400 | 108 | 1900
Feni | 132 | 700 | 125 | 2200 | Thakurgaon | 119 | 500 | 98 | 1930
Chowmuhani | 128 | 700 | 123 | 1900 | Palashbari | 134 | 100 | 121 | 1500
Ashuganj | 140 | 2400 | 134 | 1400 | Barapukuria | 127 | 300 | 118 | 1900
Daudkandi | 134 | 700 | 127 | 2000 | Panchagar | 117 | 500 | 94 | 1930
B.Baria | 137 | 2300 | 127 | 1500 | Joldhaka | 125 | 600 | 107 | 1930

## L-Curve
Date | 2019-04-21
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 70 | 5267 | 2357 | 7624 |  |  |  | QF-LDC-12
0:30 | 195 | 6182 | 2588.5 | 8770.5 | Date: | 2019-04-21
1:00 | 320 | 7097 | 2820 | 9917
1:30 | 290 | 6967 | 2677 | 9644
2:00 | 260 | 6837 | 2534 | 9371
2:30 | 210 | 6615.5 | 2603 | 9218.5 | [5 empty] | Gen. at Eve. Peak | 10184 | 10184 MW (19:00 )
3:00 | 160 | 6394 | 2672 | 9066 | [6 empty] | 19:00
3:30 | 105 | 6163.5 | 2663 | 8826.5 | [5 empty] | Gen. at Day Peak | 9943.16 | 9943.16 MW (12:00 )
4:00 | 50 | 5933 | 2654 | 8587 | [6 empty] | 12:00
4:30 | 45 | 5944 | 2632 | 8576 | [5 empty] | Highest Generation | 10436
5:00 | 40 | 5955 | 2610 | 8565 | [6 empty] | 15:00
5:30 | 40 | 5772.45 | 2540.5 | 8312.95
6:00 | 40 | 5589.9 | 2471 | 8060.9
6:30 | 70 | 5570.7 | 2507.5 | 8078.2
7:00 | 100 | 5551.5 | 2544 | 8095.5
7:30 | 110 | 5607.285 | 2604.5 | 8211.785
8:00 | 120 | 5663.07 | 2665 | 8328.07
8:30 | 160 | 5856.625 | 2714 | 8570.625
9:00 | 200 | 6050.18 | 2763 | 8813.18
9:30 | 215 | 6285.925 | 2806.5 | 9092.425
10:00 | 230 | 6521.67 | 2850 | 9371.67
10:30 | 270 | 6585.835 | 2903.5 | 9489.335
11:00 | 310 | 6650 | 2957 | 9607
11:30 | 280 | 6769.58 | 3005.5 | 9775.08
12:00 | 250 | 6889.16 | 3054 | 9943.16
12:30 | 215 | 7003.08 | 3075.5 | 10078.58
13:00 | 180 | 7117 | 3097 | 10214
13:30 | 160 | 7095 | 3047 | 10142
14:00 | 140 | 7073 | 2997 | 10070
14:30 | 125 | 7223.5 | 3029.5 | 10253
15:00 | 110 | 7374 | 3062 | 10436
15:30 | 140 | 7304 | 3016 | 10320
16:00 | 170 | 7234 | 2970 | 10204
16:30 | 205 | 6971.5 | 2939.5 | 9911
17:00 | 240 | 6709 | 2909 | 9618
17:30 | 275 | 6535.5 | 2865 | 9400.5
18:00 | 310 | 6362 | 2821 | 9183
18:30 | 275 | 6623.5 | 3060 | 9683.5
19:00 | 240 | 6885 | 3299 | 10184
19:30 | 490 | 6720 | 3176 | 9896
20:00 | 520 | 6515 | 2969 | 9484 |  |  |  | Executive Engineer
20:30 | 545 | 6316.5 | 2841.5 | 9158 |  |  |  | Network Operation Division
21:00 | 570 | 6118 | 2714 | 8832
21:30 | 380 | 5813 | 2563 | 8376
22:00 | 190 | 5508 | 2412 | 7920 |  |  |  |  | Page 6 of 7
22:30 | 155 | 5314 | 2289.5 | 7603.5
23:00 | 120 | 5120 | 2167 | 7287
23:30 | 95 | 5193.5 | 2262 | 7455.5
24:00 | 70 | 5267 | 2357 | 7624
10184 MW (19:00 )
9943.16 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-04-21 |  | Energy | 222517056
[10 empty] | 2019-04-21 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3294 | 850 | 2038 | 924 | 250 | 110 | 0 | 0 | 158
0:30 | 3316 | 686.5 | 2114 | 1912.5 | 250.5 | 93 | 257 | 0 | 141 | Date: | 2019-04-21
1:00 | 3338 | 523 | 2190 | 2901 | 251 | 76 | 514 | 0 | 124
1:30 | 3354 | 456 | 2193.5 | 2756 | 251 | 76 | 435.5 | 0 | 122 | [7 empty] | Total Energy | 222.5171 | Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
2:00 | 3370 | 389 | 2197 | 2611 | 251 | 76 | 357 | 0 | 120 | [7 empty] | Energy not Served | 0
2:30 | 3373 | 546 | 2214.5 | 2320.5 | 251 | 76 | 317.5 | 0 | 120 | [7 empty] | Energy Requirement | 222.5171
3:00 | 3376 | 703 | 2232 | 2030 | 251 | 76 | 278 | 0 | 120
3:30 | 3375 | 703 | 2222 | 1812 | 250.5 | 76 | 270 | 0 | 118 | [6 empty] | Shortage
4:00 | 3374 | 703 | 2212 | 1594 | 250 | 76 | 262 | 0 | 116
4:30 | 3374 | 703 | 2209.5 | 1606.5 | 250.5 | 76 | 242.5 | 0 | 114
5:00 | 3374 | 703 | 2207 | 1619 | 251 | 76 | 223 | 0 | 112
5:30 | 3341.5 | 703.5 | 2098.5 | 1511.5 | 251.5 | 76 | 223 | 0 | 107
6:00 | 3309 | 704 | 1990 | 1404 | 252 | 76 | 223 | 0 | 102
6:30 | 3313.5 | 778 | 1950 | 1391 | 251 | 77 | 213.5 | 0 | 101 |  |  |  |  | Coal
7:00 | 3318 | 852 | 1910 | 1378 | 250 | 78 | 204 | 0 | 100
7:30 | 3362 | 851.5 | 1913 | 1444.5 | 250 | 79 | 204 | 0 | 100 |  |  |  | Oil |  |  |  | ,
8:00 | 3406 | 851 | 1916 | 1511 | 250 | 80 | 204 | 0 | 100
8:30 | 3415.5 | 851.5 | 1936.5 | 1690.5 | 250 | 80 | 220.5 | 0 | 113
9:00 | 3425 | 852 | 1957 | 1870 | 250 | 80 | 237 | 0 | 126
9:30 | 3450 | 852 | 1975 | 2067.5 | 255.5 | 79 | 266 | 0 | 129
10:00 | 3475 | 852 | 1993 | 2265 | 261 | 78 | 295 | 0 | 132
10:30 | 3487.5 | 851.5 | 1969.5 | 2368 | 278.5 | 73 | 303.5 | 0 | 138
11:00 | 3500 | 851 | 1946 | 2471 | 296 | 68 | 312 | 0 | 144
11:30 | 3487 | 851 | 1942.5 | 2567 | 320.5 | 83 | 358 | 0 | 148
12:00 | 3474 | 851 | 1939 | 2663 | 345 | 98 | 404 | 0 | 152
12:30 | 3389.5 | 851 | 1983 | 2834.5 | 347.5 | 96.5 | 406 | 0 | 154
13:00 | 3305 | 851 | 2027 | 3006 | 350 | 95 | 408 | 0 | 156
13:30 | 3305 | 851 | 2027 | 3006 | 350 | 95 | 408 | 0 | 156
14:00 | 3305 | 851 | 2027 | 3006 | 350 | 95 | 408 | 0 | 156
14:30 | 3356 | 851 | 2008 | 3083.5 | 341 | 93.5 | 417 | 0 | 160
15:00 | 3407 | 851 | 1989 | 3161 | 332 | 92 | 426 | 0 | 164
15:30 | 3439.5 | 851 | 1965 | 3037.5 | 332 | 91 | 427.5 | 0 | 166
16:00 | 3472 | 851 | 1941 | 2914 | 332 | 90 | 429 | 0 | 168
16:30 | 3383.5 | 851 | 1829 | 2822 | 332 | 90 | 438 | 0 | 161
17:00 | 3295 | 851 | 1717 | 2730 | 332 | 90 | 447 | 0 | 154
17:30 | 3237 | 850 | 1614.5 | 2645 | 332.5 | 90 | 479.5 | 0 | 151
18:00 | 3179 | 849 | 1512 | 2560 | 333 | 90 | 512 | 0 | 148
18:30 | 3188 | 898.5 | 1623.5 | 2743.5 | 333.5 | 97.5 | 637 | 0 | 162
19:00 | 3197 | 948 | 1735 | 2927 | 334 | 105 | 762 | 0 | 176
19:30 | 3193 | 948 | 1751 | 2740 | 320 | 107 | 667 | 0 | 170
20:00 | 3217 | 948 | 1736 | 2422 | 319 | 110 | 558 | 0 | 174
20:30 | 3199.5 | 948 | 1736 | 2242 | 319 | 110 | 428.5 | 0 | 175
21:00 | 3182 | 948 | 1736 | 2062 | 319 | 110 | 299 | 0 | 176
21:30 | 3165 | 948 | 1707.5 | 1714 | 319 | 110 | 238.5 | 0 | 174
22:00 | 3148 | 948 | 1679 | 1366 | 319 | 110 | 178 | 0 | 172
22:30 | 3100.5 | 899.5 | 1750 | 1170.5 | 306 | 110 | 97 | 0 | 170
23:00 | 3053 | 851 | 1821 | 975 | 293 | 110 | 16 | 0 | 168
23:30 | 3173.5 | 850.5 | 1929.5 | 949.5 | 271.5 | 110 | 8 | 0 | 163 | Max Temp. in Dhaka |  | 35.6° C
24:00 | 3294 | 850 | 2038 | 924 | 250 | 110 | 0 | 0 | 158
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
Note on W13: Author:

## Generation
2019-04-21
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 76 | 76 | 76 | 76 | 76 | 76 | 78 | 80 | 80 | 78 | 68 | 68 | 65 | 65 | 62 | 60 | 60 | 60 |  | 75 | 77 | 80 | 80 | 80 | 80 | 80 | 1602060
2 | Kaptai Unit-4 & 5 | [11 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 380000
3 | Chattogram ST-1 (Raozan) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 110 | 110 | 110 | 0 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2400000
4 | Chittgong ST-2 (Raozan) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
5 | Raozan 25 MW (RPCL) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 24 | 24 | 24 | 24 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 594124
| Teknaf Solartech 20MW |  |  |  |  | 0 | 0.9 | 5 | 9.07 | 14.58 | 18.67 | 17 | 14.66 | 14 | 16 | 13 | 7 | 2 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 137295
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas) | [13 empty] | 0 | 65 | 145 | 130 | 130 |  | 130 | 130 | 130 | 131 | 131 | 135 | 131 | 1119342
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | 85 | 85 | 85 | 85 | 85 | 85 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 77 | 84 | 84 | 84 | 84 |  | 84 | 84 | 84 | 51 | 51 | 0 |  | 1694231
12 | Hathazari peaking | 40 | 40 | 40 | 40 | 40 | 40 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 42 |  | 61 | 61 | 30 | 30 | 30 | 0 |  | 902112
| Daudkandi bangla trak | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 0 | [18 empty] | 397440
14 | Daudkandi Peaking 52MW | [19 empty] | 50 | 0 | [5 empty] | 48488
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 92 | 97 | 97 | 97 | 92 | 89 | 97 | 97 | 97 | 97 | 92 | 84 | 0 | [13 empty] | 1199000
17 | Siddhirganj CCPP-335 MW | [17 empty] | 20 |  | 75 | 75 | 75 | 0 | 0 |  |  | 174800
18 | Summit Gazipur -2 | 97 | 15 | 0 |  |  |  |  | 0 | 13 | 44 | 70 | 105 | 162 | 214 | 260 | 270 | 275 | 278 |  | 271 | 140 | 160 | 0 |  |  |  | 2295820
19 | Ashuganj 195MW Modular | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 80 | 82 | 82 | 82 | 82 |  | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 2392000
20 | Ghorasal ST: Unit-1,2 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 718000
21 | Ghorasal GT: Unit-3 | 94 | 93 | 94 | 95 | 94 | 94 | 94 | 94 | 94 | 93 | 94 | 93 | 93 | 94 | 94 | 93 | 94 | 94 |  | 94 | 93 | 94 | 94 | 94 | 94 | 94 | 2414400
22 | Ghorasal GT: Unit-4 | 165 | 170 | 170 | 169 | 170 | 170 | 171 | 170 | 170 | 170 | 170 | 170 | 162 | 170 | 171 | 170 | 100 | 90 |  | 81 | 90 | 90 | 90 | 87 | 50 | 50 | 3471000
23 | Ghorasal ST: Unit-5 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 110 | 110 | 2835000
24
25 | Ghorasal ST: Unit-7 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 225 | 225 | 250 | 250 | 230 | 240 | 250 | 5890036
26
28 | Ashuganj ST: Unit- 3
29 | Ashuganj ST: Unit- 4
30 | Ashuganj ST: Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1923456
32 | Ashuganj Engines TSK | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 312408
33 | Ashuganj CCPP 225 MW | 227 | 226 | 226 | 226 | 225 | 227 | 228 | 226 | 222 | 224 | 223 | 222 | 212 | 192 | 216 | 217 | 184 | 184 |  | 183 | 183 | 183 | 184 | 183 | 204 | 193 | 5104000
34 | Ashuganj CCPP(South) | 250 | 300 | 300 | 300 | 300 | 270 | 270 | 270 | 300 | 330 | 300 | 300 | 360 | 340 | 338 | 300 | 300 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 300 | 7036500
| Ashuganj CCPP(North) | 300 | 300 | 300 | 300 | 300 | 270 | 270 | 270 | 300 | 330 | 330 | 330 | 360 | 330 | 330 | 330 | 300 | 270 |  | 260 | 260 | 260 | 260 | 260 | 240 | 300 | 7475000
35 | Ashuganj (Precision) 55MW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 248640
36 | Chandpur CCPP | 100 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 40 | 98 | 100 | 98 | 100 | 80 | 90 | 90 | 90 |  | 90 | 86 | 90 | 90 | 90 | 90 | 90 | 1723050
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP
40 | Meghnaghat CCPP 450MW | 450 | 450 | 450 | 450 | 450 | 370 | 370 | 370 | 400 | 400 | 400 | 400 | 420 | 330 | 380 | 380 | 350 | 320 |  | 320 | 280 | 280 | 280 | 300 | 360 | 360 | 8947875
41 | Haripur Power CCPP 360MW | 356 | 357 | 356 | 361 | 362 | 303 | 303 | 303 | 304 | 253 | 253 | 252 | 263 | 338 | 337 | 323 | 293 | 273 |  | 265 | 263 | 263 | 260 | 270 | 300 | 320 | 7322000
42 | Mymensingh RPCL 210MW | 108 | 107 | 108 | 108 | 108 | 108 | 107 | 105 | 104 | 103 | 103 | 90 | 91 | 86 | 86 | 86 | 86 | 86 |  | 90 | 90 | 90 | 91 | 91 | 103 | 104 | 2266840
43 | Haripur NEPC 110MW | 13 | 13 | 0 | [6 empty] | 40 | 40 | 63 | 96 | 96 | 110 | 110 | 110 | 110 |  | 110 | 27 | 0 |  |  |  |  | 849700
44 | Fenchugonj CCPP-1 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 60 | 58 | 57 | 56 | 58 | 57 | 57 | 57 | 60 |  | 60 | 60 | 58 | 58 | 58 | 58 | 58 | 1392000
45 | Fenchugonj CCPP-2 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 58 | 38 | 38 | 50 | 50 | 50 | 50 | 61 | 67 | 67 | 67 |  | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 1241040
46 | Shajibazar 330 MW | 131 | 131 | 128 | 129 | 127 | 129 | 131 | 131 | 128 | 128 | 130 | 130 | 135 | 129 | 122 | 122 | 122 | 122 |  | 121 | 124 | 123 | 124 | 125 | 128 | 128 | 2829000
47 | Shahjibazar GT: Unit- 8, 9 | 53 | 66 | 66 | 50 | 60 | 45 | 45 | 65 | 65 | 63 | 58 | 58 | 40 | 48 | 52 | 49 | 40 | 43 |  | 46 | 52 | 53 | 64 | 40 | 63 | 63 | 1332576
48 | Shahjibazar 86MW | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 75 | 78 | 78 | 80 | 78 | 78 | 74 | 40 | 10 |  | 79 | 79 | 79 | 80 | 79 | 79 | 79 | 1758720
49 | Shahjibazar (EPL) 50MW | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 45 | 45 | 45 | 22 | 22 | 25 | 25 | 25 | 25 | 25 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 905400
50 | Sylhet GT 150 MW | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 105 | 90 | 80 | 78 | 79 | 74 | 74 | 74 | 74 | 67 | 65 |  | 45 | 70 | 70 | 62 | 70 | 85 | 73 | 1970100
51 | Sylhet GT 20 MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 98000
52 | Sylhet (EPL) 50MW | 39 | 39 | 39 | 40 | 40 | 40 | 40 | 38 | 39 | 37 | 37 | 34 | 39 | 39 | 37 | 37 | 39 | 40 |  | 41 | 40 | 41 | 41 | 40 | 8 | 8 | 877960
53 | Sylhet (Desh) 10MW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 243180
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 0 | 11 | 11 | 11 | 11 | 223968
55 | Fenchugonj (Barakatullah) 51MW | 53 | 53 | 53 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 45 | 50 | 50 | 50 | 11 | 11 |  | 50 | 53 | 53 | 53 | 53 | 53 | 53 | 978000
56 | Shahjahanulla 25 MW | 16 | 16 | 16 | 16 | 16 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 25 | 24 | 25 | 526680
57 | Summit Bibiana- 2 | 250 | 240 | 255 | 250 | 250 | 240 | 250 | 280 | 270 | 280 | 270 | 290 | 280 | 270 | 295 | 265 | 260 | 245 |  | 240 | 255 | 240 | 275 | 240 | 270 | 295 | 6691450
58 | Southern 55MW | 55 | 55 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 35 | 35 | 17 | 0 | 17 | 959820
59 | Sikalbaha (Energis) | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 939840
60 | Barabkunda (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 17 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 432576
61 | Narshingdi (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 0 | 0 | 405072
62 | Tangail (Doreen) 22MW | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 456804
63 | Tripura | 124 | 120 | 120 | 116 | 112 | 102 | 100 | 100 | 126 | 132 | 144 | 152 | 156 | 158 | 164 | 168 | 154 | 148 |  | 176 | 170 | 174 | 176 | 172 | 168 | 158 | 3470400
64 | Malancha, Ctg. EPZ (United) | 30 | 31 | 31 | 31 | 25 | 34 | 28 | 12 | 4 | 3 | 4 | 3 | 6 | 6 | 2 | 3 | 7 | 10 |  | 26 | 33 | 37 | 38 | 39 | 40 | 41 | 490560
65 | Feni (Doreen) 22MW | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 21 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 469296
66 | Feni, Mohipal (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 205740
67 | Jangalia (Summit) 33MW | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 0 | 0 | 545200
68 | Summit Cumilla 25MW | 20 | 20 | 20 | 20 | 20 | 20 | 16 | 15 | 15 | 15 | 15 | 15 | 15 | 18 | 18 | 18 | 20 | 21 |  | 21 | 0 | 0 | 5 | 21 | 15 | 21 | 406080
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 25 | 25 | 23 | 23 | 23 | 23 | 22 | 24 | 24 | 24 | 24 | 28 | 23 | 23 | 24 | 24 | 24 | 24 |  | 18 | 18 | 18 | 18 | 11 | 0 | 0 | 479160
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 35 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 25 | 33 | 33 | 33 | 0 | 0 | 695700
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 8 | 33 | 17 | 33 |  | 33 | 33 | 33 | 33 | 25 | 0 | 29 | 734400
73 | Ghorashal (Regent)
76 | Siddhirganj (Desh)
77 | Siddhirganj (Dutch Bangla) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 24 | 50 | 68 | 73 | 87 | 82 | 91 | 70 | 15 | 15 |  | 20 | 30 | 0 | 0 | 0 |  |  | 753600
78 | Gazipur (RPCL) | 51 | 51 | 25 | 25 | 25 | 25 | 25 | 26 | 48 | 50 | 46 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 11 | 43 | 43 | 50 | 25 | 8 | 8 | 950496
79 | Kodda 149MW | 98 | 64 | 16 | 0 | 0 | 0 |  | 0 | 32 | 90 | 98 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 115 | 64 | 16 | 0 | 1977600
80 | Jamalpur 95MW | 84 | 84 | 81 | 0 | 10 | 40 | 48 | 48 | 50 | 70 | 78 | 78 | 85 | 85 | 85 | 85 | 85 | 70 |  | 85 | 85 | 85 | 84 | 84 | 40 | 0 | 1637760
81 | Lakdhanvi 52 MW | 52 | 52 | 43 | 16 | 16 | 16 | 16 | 17 | 49 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 40 |  | 43 | 52 | 52 | 25 | 16 | 0 |  | 923534
Gazipur 100 MW
82 | Madanganj 102MW | 60 | 15 | 15 | 15 | 15 | 0 |  |  |  |  | 5 | 60 | 80 | 84 | 97 | 97 | 97 | 97 |  | 64 | 30 | 0 |  |  |  |  | 885312
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj (Powerpac) 100MW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 50 | 57 | 64 | 73 | 73 | 75 | 30 | 10 |  | 39 | 60 | 0 | 0 | 0 |  |  | 669257
86 | Meghnaghat CCPP(Summit) | 235 | 280 | 250 | 260 | 240 | 270 | 260 | 285 | 275 | 275 | 250 | 245 | 215 | 255 | 280 | 250 | 242 | 235 |  | 210 | 250 | 250 | 240 | 210 | 285 | 270 | 6398516
87 | Meghnaghat (IEL) | 100 | 100 | 58 | 25 | 24 | 7 | 7 | 11 | 47 | 50 | 73 | 76 | 84 | 90 | 97 | 80 | 35 | 24 |  | 55 | 7 | 30 | 0 | 0 |  |  | 1123200
88 | Ghorashal 78MW (MAX)
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 78 | 78 | 68 | 68 | 68 | 68 | 68 | 78 | 78 |  | 102 | 102 | 101 | 102 | 30 | 10 | 10 | 1814640
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 10 | 10 |  | 33 | 50 | 50 | 50 | 50 | 50 | 50 | 1103000
93 | Ashuganj (Midland) 51MW | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 48 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 1004344
94 | Gagnagar (Orion) | 102 | 64 | 7 | 0 |  |  |  | 4 | 16 | 45 | 68 | 74 | 102 | 102 | 102 | 48 | 24 | 24 |  | 102 | 50 | 32 | 16 | 0 |  |  | 1029888
95 | Patenga 50MW | 46 | 46 | 41 | 45 | 45 | 44 | 42 | 39 | 40 | 40 | 40 | 40 | 39 | 39 | 40 | 34 | 39 | 40 |  | 39 | 39 | 39 | 40 | 40 | 40 | 40 | 976320
96 | Chattogram ECPV 108 MW | 105 | 105 | 105 | 105 | 101 | 98 | 98 | 98 | 98 | 98 | 98 | 96 | 96 | 100 | 104 | 103 | 104 | 98 |  | 105 | 105 | 105 | 105 | 105 | 105 | 103 | 2440320
97 | Katpotti 51 MW | [20 empty] | 43 | 32 | 43 | 42 | 38 | 35 | 192576
98 | Bosila 108MW | 57 | 58 | 58 | 58 | 58 | 24 | 24 | 44 | 50 | 49 | 48 | 46 | 52 | 52 | 51 | 51 | 52 | 52 |  | 52 | 53 | 54 | 54 | 10 | 8 | 0 | 1094400
99 | Madanganj-55 MW | 30 | 15 | 0 | [6 empty] | 0 | 8 | 34 | 50 | 55 | 55 | 55 | 55 | 55 |  | 55 | 30 | 15 | 0 |  |  |  | 529530
100 | Northern 55 MW | 56 | 55 | 37 | 18 | 18 | 18 | 18 | 36 | 55 | 55 | 55 | 55 | 56 | 56 | 56 | 56 | 56 | 56 |  | 56 | 56 | 56 | 36 | 18 | 0 | 18 | 996327
101 | Kushiara 163 MW CCPP GT | 163 | 163 | 163 | 163 | 163 | 130 | 100 | 100 | 130 | 163 | 130 | 130 | 163 | 100 | 130 | 130 | 130 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 3538271
102 | Sarishabari (Solar) | [5 empty] | 0 | 0.5 | 1 | 1.6 | 2 | 2 | 2.5 | 2 | 1 | 1 | 0 | 0 | 0 |  | 0 | [6 empty] | 16000
103 | Banco Energy 54MW | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 1152360
104 | APR Energy , Keranigonj | [8 empty] | 0 | 75 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 93042
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 200 | 150 | 100 | 0 | 16 | 16 | 16 | 16 | 16 | 33 | 67 | 80 | 93 | 100 | 100 | 50 | 50 | 50 |  | 137 | 200 | 200 | 200 | 80 | 0 |  | 2109600
112 | Aggreko Aurahati 100MW | [12 empty] | 42 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 19958
114 | Summit Gazipur-1 150MW | 149 | 100 | 15 | 15 | 15 | 15 | 15 | 15 | 32 | 75 | 125 | 149 | 149 | 149 | 148 | 148 | 149 | 142 |  | 149 | 149 | 118 | 92 | 59 | 0 |  | 2105280
115 | Juldah 100 MW Unit-3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 89 | 89 | 89 | 89 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2359680
116 | Chandpur Desh 200MW | 200 | 200 | 200 | 200 | 200 | 105 | 105 | 105 | 125 | 185 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 140 |  | 165 | 200 | 200 | 200 | 144 | 140 | 140 | 4224000
117 | Midland 150MW | 142 | 142 | 142 | 64 | 64 | 12 | 12 | 32 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 70 | 0 |  |  | 1957090
118 | Bibiyana-3 285 MW | [14 empty] | 15 | 15 | 20 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 57100
| United Jamalpur PPL | 111 | 111 | 111 | 0 | 28 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 58 | 58 |  | 68 | 68 | 68 | 68 | 68 | 48 | 48 | 1647600
120 | Eastern Zone Total | 7097 | 6837 | 6394 | 5933 | 5955 | 5589.9 | 5551.5 | 5663.07 | 6050.18 | 6521.67 | 6650 | 6889.16 | 7117 | 7073 | 7374 | 7234 | 6709 | 6362 |  | 6885 | 6720 | 6515 | 6118 | 5508 | 5120 | 5267 | 155033940
121
122 | o
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | 83 | 83 | 16 | 16 | 16 | 16 | 16 | 32 | 66 | 96 | 99 | 99 | 99 | 99 | 99 | 86 | 83 | 99 |  | 99 | 66 | 45 | 16 | 16 | 0 |  | 1391960
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | 31 | 31 | 0 | [14 empty] | 35 |  | 40 | 40 | 40 | 0 |  |  |  | 172320
Khulna CCPP 225MW
129 | Labon Chora 105 MW | 105 | 105 | 94 | 70 | 65 | 35 | 35 | 53 | 70 | 70 | 90 | 90 | 105 | 105 | 90 | 90 | 105 | 53 |  | 105 | 105 | 70 | 70 | 70 | 0 |  | 1796160
130
131
132
133
| Summit Barisal 110 MW | 80 | 64 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 48 | 48 | 80 | 80 | 110 | 110 | 110 | 110 |  | 110 | 110 | 96 | 80 | 16 | 0 |  | 1341216
136 | Barisal GT: Unit-1, 2 | [19 empty] | 12 | 0 | [5 empty] | 10815
137 | Bhola Aggreko 95MW | 95 | 95 | 95 | 95 | 95 | 96 | 95 | 95 | 96 | 97 | 95 | 93 | 94 | 95 | 95 | 98 | 44 | 24 |  | 80 | 96 | 96 | 66 | 41 | 42 | 93 | 2023767
| Bhola CCPP 194MW | 139 | 141 | 143 | 140 | 138 | 143 | 145 | 145 | 145 | 145 | 145 | 145 | 135 | 145 | 145 | 145 | 135 | 135 |  | 135 | 139 | 139 | 136 | 136 | 136 | 146 | 3440280
140 | Bhola (Venture) 33MW | 31 | 28 | 27 | 27 | 27 | 24 | 21 | 20 | 13 | 17 | 15 | 18 | 17 | 20 | 22 | 18 | 19 | 26 |  | 36 | 36 | 32 | 35 | 36 | 33 | 24 | 581007
141 | Bangla Trak Noapara | 20 | 0 | [24 empty] | 55680
142 | Noapara (KZA) 40MW | 40 | 40 | 8 | 8 | 8 | 8 | 8 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 8 | 8 |  | 40 | 40 | 8 | 8 | 0 |  |  | 550125
143 | Gopalganj Peaking | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 6 | 10 | 12 | 12 | 15 | 33 | 37 |  | 60 | 50 | 51 | 0 |  |  |  | 315904
144 | Bheramara GT-1,2,3
145 | Madhumati Power Plant | 108 | 108 | 108 | 108 | 109 | 94 | 72 | 72 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 |  | 109 | 108 | 108 | 108 | 63 | 35 | 17 | 2339400
146 | Bheramara HVDC | 523 | 389 | 703 | 703 | 703 | 704 | 852 | 851 | 852 | 852 | 851 | 851 | 851 | 852 | 851 | 851 | 851 | 849 |  | 948 | 948 | 948 | 948 | 948 | 851 | 850 | 19354909
147 | Bheramara 360 MW
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2 | 67 | 67 | 67 | 66 | 67 | 68 | 65 | 65 | 65 | 67 | 66 | 65 | 67 | 65 | 67 | 67 | 67 | 68 |  | 69 | 70 | 69 | 69 | 69 | 67 | 66 | 1615854
152 | Barapukuria Unit-3 | 184 | 184 | 184 | 184 | 184 | 184 | 185 | 185 | 185 | 194 | 230 | 280 | 283 | 270 | 265 | 265 | 265 | 265 |  | 265 | 250 | 250 | 250 | 250 | 226 | 184 | 5480800
153 | Baghabari GT 71MW
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | 50 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 10 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 0 | 0 |  |  | 539734
157 | Sirajgonj Unit-1 225MW (Gas) | 161 | 172 | 173 | 175 | 174 | 172 | 171 | 197 | 196 | 199 | 201 | 190 | 181 | 176 | 192 | 178 | 176 | 172 |  | 167 | 155 | 155 | 158 | 157 | 168 | 197 | 4537009
158 | Sirajgonj Unit-1 225MW (Oil)
| Sirajgonj Unit-2 225MW (Gas) | 168 | 167 | 173 | 179 | 179 | 179 | 179 | 182 | 185 | 185 | 185 | 188 | 186 | 152 | 163 | 162 | 167 | 147 |  | 140 | 137 | 144 | 158 | 159 | 147 | 192 | 4275536
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas) | 165 | 165 | 165 | 173 | 174 | 172 | 174 | 180 | 180 | 177 | 172 | 168 | 166 | 148 | 152 | 153 | 153 | 149 |  | 148 | 146 | 146 | 148 | 151 | 148 | 175 | 4110300
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas) | 331 | 350 | 371 | 372 | 372 | 330 | 280 | 280 | 280 | 322 | 322 | 322 | 332 | 280 | 300 | 300 | 300 | 230 |  | 230 | 230 | 230 | 230 | 200 | 250 | 350 | 7125818
161 | Bera Peaking | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 10 |  | 51 | 53 | 23 | 0 | 0 |  |  | 72074
162 | Bogra (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 |  | 22 | 22 | 22 | 14 | 18 | 22 | 22 | 479760
163 | Bogra (EPL) | 16 | 15 | 16 | 16 | 16 | 16 | 16 | 15 | 15 | 15 | 14 | 14 | 14 | 14 | 14 | 14 | 16 | 16 |  | 16 | 17 | 16 | 17 | 16 | 17 | 16 | 368136
164 | Ullapara (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 0 | 0 | 0 | 8 | 8 | 231624
165 | Amnura 50MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 12 | 12 | 12 | 12 | 0 |  |  | 170870
166 | Katakhali (Northern) | 50 | 50 | 50 | 43 | 43 | 8 | 8 | 35 | 43 | 43 | 43 | 43 | 43 | 50 | 50 | 8 | 8 | 8 |  | 33 | 8 | 8 | 8 | 8 | 0 |  | 715339
167 | Katakhali Peaking | 39 | 39 | 39 | 39 | 0 | 0 | [11 empty] | 12 |  | 44 | 48 | 0 | 0 | 0 |  |  | 249046
168 | Santahar Peaking | 35 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 33 | 35 | 35 | 30 | 0 |  |  | 127427
169 | Rajlanka 52 MW | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 33 | 34 | 34 | 34 | 34 | 34 | 34 | 33 | 8 | 8 | 8 |  | 34 | 25 | 8 | 8 | 8 | 0 |  | 623040
170 | Chapainawabganj-100 MW | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 94 | 94 | 94 | 93 | 93 | 93 | 93 | 93 | 93 | 93 |  | 93 | 63 | 63 | 40 | 0 |  |  | 1777886
171 | Paramount Baghabari
172 | Confidence CPBL-2 | 90 | 70 | 53 | 53 | 53 | 35 | 35 | 36 | 36 | 35 | 52 | 70 | 70 | 70 | 72 | 72 | 72 | 72 |  | 72 | 72 | 72 | 72 | 17 | 17 | 17 | 1446720
173 | Rangpur GT | 17 | 0 | [17 empty] | 17 | 17 | 17 | 17 | 17 |  |  | 80600
175 | Saidpur GT | 16 | 0 | [17 empty] | 18 | 17 | 16 | 16 | 16 |  |  | 82000
176
177
178
178 | Western Zone Total | 2820 | 2534 | 2672 | 2654 | 2610 | 2471 | 2544 | 2665 | 2763 | 2850 | 2957 | 3054 | 3097 | 2997 | 3062 | 2970 | 2909 | 2821 |  | 3299 | 3176 | 2969 | 2714 | 2412 | 2167 | 2357 | 67483116