## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-07-20 | Thursday
|  | Date (day): | 2023-07-20 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13295.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15338 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-07-19 | 2023-07-20 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 160 | 160 | 180 | 180
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 401 | 403 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 327 | 343 | 330 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 58 | 58 | 58 | 64 | 36 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 294 | 274 | 300 | 300 | 35 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 95 | 96 | 96 | 96 |  | 6 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 15 | 15 | 30
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 36 | 31 | 45 | 45 | 30 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  | 3 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 191 | 195 | 185 | 195 | 15 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 50 | 72 | 58 | 70 | 30 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 324 | 323 | 330 | 330
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 50 | 102 | 50 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 17 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 96 | 130 | 64 | 130 | 19 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 17 | 17 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 40 | 40 | 40 | 41 |  | 39 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 23 | 22 | 22 | 22 |  | 11 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 25 | 8 | 25 | 27 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 145 | 97 | 115 | 115 | 185 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 260 | 296 | 300 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
33 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
34 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 89 | 151 | 34 | 149
35 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 88 | 35 | 88 |  | 17 | Engine problem
36 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 54 | 59 | 54 | 72 | 32 |  | Fuel shortage
37 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 108 | 17 | 126 | 36 |  | Fuel shortage
38 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 16 | 0 | 30 | 0
39 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6063 | 5722 | 3544 | 3886 | 3526 | 4046 | 796 | 844
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
41 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 16 | 8 | 17 | 8 |  | Fuel shortage
42 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 12 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 32 | 39 | 26 | 46
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 60 | 60 | 60 | 60 | 170 |  | Low Water Level
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 220 | 224 | 225 | 225
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 74 | 96 | 105 | 105 | 0
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 24 | 66 | 32 | 66 | 32 |  | Fuel shortage
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 32 | 33 | 50 | 50 | 52 |  | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 35 | 46 | 35 | 46 | 54 |  | Fuel shortage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 37 | 37 | 25 | 50 | 50 |  | Fuel shortage
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 11 | 11 | 11 | 11 | 11 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 34 | 5 | 20
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 18 | 12 | 18 | 90 |  | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 87 | 276 | 88 | 300
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 36 | 17 | 36 | 18 |  | Fuel shortage
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 54 | 74 | 74 | 74 | 36 |  | Fuel shortage
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 38 | 44 | 25 | 38 | 62 |  | Fuel shortage
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 51 | 100 | 51 | 107 | 9 |  | Fuel shortage
60 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 53 | 163 | 17 | 163
| SS Power I |  | Coal | SS Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 6 | 2 | 15 | 10 |  |  | On test.
| Chattogram area Total |  |  |  |  | 2605 | 2545 | 858 | 1375 | 906 | 1442 | 592 | 510
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 179 | 205 | 200 | 200 | 21 |  | Gas shortage
62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 275 | 280 | 300 | 60 |  | Gas shortage
63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 240 | 240 | 240 | 120 |  | Gas shortage
64 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 240 | 240 | 240 | 240 | 160 |  | Gas shortage
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 5 | 5 | 5 | 40 |  | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43
69 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 5 | 125 | 6 | 150
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 36 | 42 | 43 | 43 |  | 9 | Machine problem
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
72 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 34 | 51 | 34 | 51 | 149 |  | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 20 | 20 | 20
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 160 | 120 | 146 | 169
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 32 | 33 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 42 | 43 | 43 |  | 9 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Contract Expired
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 52 | 103 | 52 | 88 |  | 26 | Engine problem
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 97 | 9 | 95 | 18 |  | Fuel shortage
81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 93 | 99 | 98 | 98 | 17 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 3159 | 3096 | 1558 | 1788 | 1540 | 1866 | 780 | 249
83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 30 | 53 | 30 | 50 | 152 |  | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  | 3 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 67 | 87 | 68 | 88 | 112 |  | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 84 | 20 | 85 | 30 |  | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 48 | 0 | 50 | 0
90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 | 10 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 197 | 255 | 200.6 | 254 | 152 | 3
91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 40 | 40 | 40 |  | 50 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 80 | 112 | 112 | 112 |  | 51 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 44 | 45 | 45
96 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 46 | 46 | 44 | 44
97 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 60 | 60 | 60
99 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 81 | 86 | 86
100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 204 | 201 | 203 | 204 |  | 27 | Machine problem
102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 17 | 17
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
103 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
104 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 290 | 300 | 300 |  |  | FGMO
105 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 368 | 407 | 400 | 400 |  |  | FGMO
106 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
107 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 50 | 347 | 340 | 385
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1351 | 1730 | 1735 | 1781 | 0 | 585
108 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 904 | 764 | 924 | 924
109 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 86 | 80 | 98 |  | 17 | Engine problem
110 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 11 | 21 | 20 | 30 |  | 24 | Engine problem
111 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 218 | 208 | 210 | 225
112 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 25 | 54 | 26 | 60 |  | 49 | Engine problem
113 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 145 | 160 | 150 | 150 | 260 |  | Gas shortage
114 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 16 | 40 | 8 | 40
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
115 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 36 | 36 | 35 | 35 | 70 |  | Fuel shortage
116 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 32 | 105 | 50 | 105
117 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 107 | 0 | 100 | 0
118 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 220 | 220 | 0 | 233 | 200 | 233
119 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0 |  | 617 | Machine problem
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3125 | 3121 | 1510 | 1707 | 1803 | 1900 | 346 | 707
120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 32 | 16 | 32
121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 22 | 34 | 21 | 34 |  | 6 | Engine problem
122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 124 | 132 | 135 | 135 |  | 59 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1222 | 1222 | 1244 | 1244
124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 221 | 220 | 220 | 220
125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 0 | 17 | 150
126 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 | 307 |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1622 | 1640 | 1653 | 1815 | 307 | 65
127 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
128 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 35 | 0 | 35 | 17 |  | Fuel shortage
129 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 28 |  | 43 | Engine problem
130 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 21 | 21 | 21 | 21
131 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 42 | 25 | 34 | 42 |  | 8 | Engine problem
132 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 29 | 0 | 29 |  | 21 | Engine problem
133 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Under maint
134 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 150 | 155 | 148 | 155 | 65 |  | Gas shortage
136 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 414 | 380 | 380 |  |  | Gas shortage
137 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 0 | 35 | 15 |  | Fuel shortage
138 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 0 | 8 | 8 |  | 3 | Engine problem
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 0 | 93 | 11 |  | Fuel shortage
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 150 | 200
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 70 | 35 | 70 | 43 |  | Fuel shortage
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 75 | 35 | 75 | 38 |  | Fuel shortage
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 748*2 | 1496 | 1496 | 716 | 716 | 700 | 700
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 1434 | 1673 | 1525 | 1879 | 580 | 285
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 235 | 170 | 170
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 84 | 34 | 70 | 43 |  | Fuel shortage
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 75 | 75 | 35 | 115
153 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 19 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 207 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 512 | 394 | 407 | 355 | 168 | 85
| Total |  |  |  |  | 24911 | 24171 | 12586 | 14448 | 13295.6 | 15338 | 3721 | 3333
A. |  | 2023-07-19 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 14448 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 11652 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 15600 | MW
3 | Day peak Generation : |  |  | 12586 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14903.44 | MW
4 | Evening peak Generation : |  |  | 14448 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 1100 | MW
5 | Total Energy Generation : |  | 303.4361 | MKWHr | By Solar | 3.2895 | MKWHr
| By Gas : | 153.3855 | MKWHr |  | By Oil: | 67.4496 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 53.1032 | MKWHr |  | By Hydro: | 1.4598 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.21504 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3721 | MW | Dhaka | 5295.54 | 5157.54 |  | 138 |  | 18:00 |  | 1625
|  |  | For Plants S/D or M/C prob = |  |  | 3333 | MW | Chittagong | 1440 | 1440 |  | 0 |  | 19:00 |  | 1276.835
|  |  | Total = |  |  | 7054 | MW | Khulna | 1891.6 | 1719.6 |  | 172 |  | 19:30 |  | 1260.6
7 | Total Gas Supplied : |  |  | 1196.89 | MMCFD |  |  | Rajshahi | 1631.8 | 1531.8 |  | 100 |  | 20:00 |  | 1343.685
8 | Fuel Cost : | i) Gas : | Taka | 169292110.8 | ii) Oil : | Taka | 889328321.7 | Comilla | 1303 | 1123 |  | 180 |  | 21:00 |  | 1100.16
|  | iii) Coal : | Taka | 306905782 | Total | Taka | 1365526214.5 | Mymensingh | 1239 | 1039 |  | 200 |  | 22:00 |  | 1125.945
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 632 | 542 |  | 90 |  | 23:00 |  | 1414.355
| ii) During Peak Demand : |  |  | 310 | MW (E to W) at | 21:00 | hrs | Barisal | 479.5 | 439.5 |  | 40 |  | 24:00 |  | 1677.935
| iii) Maximum : |  |  | 310 | MW at | 21:00 | hrs | Rangpur | 991 | 811 |  | 180
10 | Maximum Temperature in Dhaka was |  |  |  | 35.4° C |  |  | Total | 14903.44 | 13803.44 |  | 1100
B. |  | 2023-07-20 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 35.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 15800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 426 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15338 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 14400 | MW
4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 331.8307 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11991 | MW at | 8:00 | 120 | 55 | 50 | 50 | 45 | 36 | 20 | 15 | 35
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.0679 | MKWHr. | ii) HVDC Flow at Peak Time |  | 764 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.4656 | MKWHr. | iii) Maximum HVDC Flow : |  | 909 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 74.99 |  | (b) Today: | 75.54 |  | (c) Rule Curve: |  | 87.04
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-07-19 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 401 | 327 |  | 0 | 450 | 310 | 34 | 96 | 15 | 332 | 0 | 195 | 34 | 24 | 82 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 19 | 21 | 25 | 23 | 8 | 0 | 30 | 30 | 0 | 0 | 8 | 226 | 0 | 0 | 0 |  | 12 | 32 | 50 | 25 | 0 | 40 | 11 | 35 | 0 | 0 | 0 | 280 | 240 | 195 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 43 | 43 | 20 | 11 | 33 | 20 | 164 | 84 | 0 | 18 | 0 | 43 | 30 | 42 | 30 | 112 | 0 | 58 | 81 | 0 | 203 | 17 | 0 | 10 | 300 | 24 | 5 | 0 | 102 | 218 | 0 | 68 | 0 | 35 | 0 | 25 | 17 | 5 | 367 | 19 | 35 | 48 | 0 | 88 | 17 | 74 | 34 | 9 | 25 | 260 | 54 | 0 | 0 | 42 | 0 | 17 | 0 | 58 | 17 | 290 | 17 | 0 | 0 | 3 |  | 908 | 0 | 150 | 0 | 49 | 224 | 0 | 0 | 10 | 53 | 8 | 134 | 34 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 21 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 414 | 36 | 0 | 35 | 37 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 17 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 718 | 0 | 0 |  | 7417 | 5065 | 12482 | 4260 | 908 | 2408 | 218 | 1563 | 2132 | 60 | 458 | 308 | 164 | 0 | 3 | 1927.19 | 74.99
2:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 403 | 342 |  | 0 | 450 | 310 | 33 | 96 | 15 | 329 | 0 | 193 | 34 | 24 | 64 | 44 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 21 | 25 | 23 | 8 | 0 | 30 | 30 | 0 | 0 | 8 | 227 | 0 | 0 | 0 |  | 12 | 32 | 50 | 25 | 0 | 40 | 11 | 36 | 0 | 0 | 0 | 280 | 240 | 200 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 43 | 43 | 20 | 11 | 33 | 20 | 164 | 84 | 0 | 18 | 0 | 43 | 30 | 42 | 46 | 112 | 0 | 58 | 81 | 0 | 203 | 17 | 0 | 10 | 310 | 24 | 5 | 0 | 115 | 156 | 0 | 68 | 0 | 35 | 0 | 25 | 17 | 5 | 390 | 19 | 35 | 48 | 0 | 88 | 17 | 74 | 34 | 9 | 25 | 260 | 54 | 0 | 0 | 34 | 0 | 17 | 0 | 57 | 17 | 290 | 17 | 0 | 0 | 9 |  | 909 | 0 | 150 | 0 | 49 | 223 | 0 | 0 | 10 | 53 | 8 | 134 | 34 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 21 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 414 | 36 | 0 | 35 | 32 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 17 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 721 | 0 | 0 |  | 7391 | 5065 | 12456 | 4268 | 909 | 2450 | 156 | 1557 | 2135 | 60 | 458 | 290 | 164 | 0 | 9 | 1808.77 | 74.99
3:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 402 | 342 |  | 0 | 450 | 308 | 34 | 96 | 15 | 327 | 0 | 189 | 34 | 24 | 48 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 21 | 25 | 23 | 8 | 0 | 30 | 30 | 0 | 0 | 8 | 225 | 0 | 0 | 0 |  | 12 | 32 | 50 | 25 | 0 | 36 | 10 | 32 | 0 | 0 | 0 | 280 | 240 | 206 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 43 | 43 | 20 | 11 | 33 | 20 | 144 | 84 | 0 | 18 | 0 | 43 | 30 | 42 | 46 | 112 | 0 | 58 | 81 | 0 | 204 | 17 | 0 | 10 | 320 | 24 | 5 | 0 | 112 | 157 | 0 | 68 | 0 | 35 | 0 | 25 | 17 | 5 | 409 | 19 | 35 | 48 | 0 | 88 | 17 | 74 | 34 | 9 | 25 | 145 | 35 | 0 | 0 | 34 | 0 | 34 | 0 | 58 | 17 | 290 | 17 | 0 | 0 | 6 |  | 909 | 0 | 150 | 0 | 49 | 221 | 0 | 0 | 10 | 53 | 8 | 135 | 32 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 414 | 36 | 0 | 35 | 32 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 17 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 722 | 0 | 0 |  | 7254 | 5042 | 12296 | 4190 | 909 | 2452 | 157 | 1534 | 2136 | 60 | 455 | 253 | 144 | 0 | 6 | 1722.82 | 74.99
4:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 402 | 340 |  | 0 | 450 | 308 | 35 | 96 | 15 | 324 | 0 | 187 | 34 | 24 | 48 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 21 | 25 | 23 | 8 | 0 | 30 | 30 | 0 | 0 | 8 | 224 | 0 | 0 | 0 |  | 12 | 32 | 50 | 25 | 0 | 25 | 10 | 32 | 0 | 0 | 0 | 280 | 240 | 206 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 43 | 43 | 20 | 11 | 33 | 20 | 152 | 85 | 0 | 18 | 0 | 43 | 30 | 42 | 46 | 112 | 0 | 58 | 81 | 0 | 204 | 18 | 0 | 10 | 320 | 24 | 5 | 0 | 115 | 250 | 0 | 68 | 0 | 35 | 0 | 25 | 17 | 5 | 404 | 19 | 35 | 48 | 0 | 88 | 17 | 74 | 34 | 9 | 25 | 15 | 35 | 0 | 0 | 34 | 0 | 35 | 0 | 58 | 17 | 290 | 17 | 0 | 0 | 5 |  | 909 | 0 | 160 | 0 | 49 | 221 | 0 | 0 | 11 | 53 | 8 | 132 | 31 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 409 | 36 | 0 | 35 | 32 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 17 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 719 | 0 | 0 |  | 7207 | 5028 | 12235 | 4061 | 909 | 2444 | 250 | 1512 | 2133 | 60 | 455 | 254 | 152 | 0 | 5 | 1637.825 | 74.99
5:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 402 | 343 |  | 0 | 450 | 305 | 58 | 96 | 15 | 331 | 0 | 194 | 34 | 24 | 48 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 21 | 25 | 23 | 8 | 0 | 30 | 30 | 0 | 0 | 8 | 228 | 0 | 0 | 0 |  | 12 | 32 | 50 | 25 | 0 | 19 | 10 | 39 | 0 | 0 | 0 | 280 | 230 | 208 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 42 | 43 | 20 | 11 | 33 | 20 | 158 | 84 | 0 | 18 | 0 | 43 | 30 | 42 | 46 | 112 | 0 | 60 | 81 | 0 | 203 | 18 | 0 | 10 | 310 | 24 | 5 | 0 | 112 | 168 | 0 | 68 | 0 | 35 | 0 | 25 | 17 | 6 | 403 | 19 | 35 | 48 | 0 | 88 | 17 | 74 | 34 | 9 | 25 | 35 | 50 | 0 | 0 | 34 | 0 | 20 | 0 | 58 | 17 | 230 | 17 | 0 | 0 | 7 |  | 906 | 0 | 160 | 0 | 49 | 224 | 0 | 0 | 11 | 53 | 8 | 134 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 414 | 36 | 0 | 35 | 32 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 17 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 714 | 0 | 0 |  | 7113 | 5014 | 12127 | 4034 | 906 | 2443 | 168 | 1511 | 2128 | 60 | 459 | 253 | 158 | 0 | 7 | 1502.215 | 74.99
6:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 403 | 342 |  | 0 | 450 | 307 | 58 | 96 | 15 | 327 | 0 | 191 | 34 | 24 | 48 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 21 | 25 | 23 | 8 | 0 | 30 | 30 | 0 | 0 | 8 | 226 | 0 | 0 | 0 |  | 12 | 32 | 50 | 25 | 0 | 19 | 10 | 39 | 0 | 0 | 0 | 350 | 250 | 206 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 43 | 43 | 20 | 11 | 33 | 20 | 140 | 86 | 0 | 18 | 0 | 43 | 30 | 42 | 46 | 112 | 0 | 60 | 81 | 0 | 203 | 18 | 0 | 10 | 310 | 24 | 5 | 0 | 112 | 0 | 0 | 68 | 0 | 35 | 1 | 25 | 17 | 5 | 403 | 19 | 35 | 48 | 0 | 88 | 17 | 64 | 34 | 9 | 25 | 30 | 54 | 2 | 0 | 34 | 0 | 17 | 2 | 58 | 17 | 230 | 17 | 0 | 0 | 13 |  | 905 | 0 | 170 | 0 | 49 | 222 | 0 | 0 | 11 | 53 | 8 | 136 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 414 | 36 | 0 | 35 | 32 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 17 | 0 | 7 | 0 | 25 | 0 | 0 | 1 | 0 | 738 | 11 | 0 |  | 7003 | 4856 | 11859 | 4124 | 905 | 2443 | 0 | 1497 | 2152 | 60 | 247 | 254 | 140 | 24 | 13 | 1328.405 | 74.99
7:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 404 | 337 |  | 0 | 450 | 295 | 59 | 96 | 15 | 332 | 0 | 197 | 34 | 24 | 48 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 21 | 25 | 23 | 8 | 0 | 30 | 30 | 0 | 0 | 8 | 228 | 0 | 0 | 0 |  | 12 | 24 | 50 | 25 | 0 | 20 | 10 | 34 | 0 | 0 | 0 | 320 | 320 | 182 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 40 | 43 | 20 | 11 | 33 | 20 | 140 | 30 | 0 | 18 | 0 | 43 | 30 | 42 | 46 | 112 | 0 | 60 | 78 | 0 | 203 | 17 | 0 | 10 | 300 | 24 | 5 | 0 | 112 | 0 | 0 | 68 | 0 | 35 | 6 | 25 | 17 | 5 | 402 | 19 | 35 | 48 | 1 | 88 | 17 | 74 | 34 | 8 | 25 | 50 | 54 | 13 | 0 | 34 | 0 | 17 | 6 | 57 | 17 | 250 | 17 | 0 | 0 | 6 |  | 905 | 0 | 170 | 0 | 49 | 224 | 0 | 0 | 11 | 53 | 8 | 122 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 414 | 36 | 0 | 24 | 32 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 17 | 1 | 26 | 0 | 0 | 0 | 0 | 6 | 0 | 725 | 35 | 0 |  | 6996 | 4840 | 11836 | 4121 | 905 | 2405 | 0 | 1499 | 2139 | 60 | 224 | 243 | 140 | 94 | 6 | 1207.12 | 74.99
8:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 403 | 341 |  | 0 | 450 | 310 | 58 | 96 | 15 | 300 | 0 | 193 | 34 | 24 | 48 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 21 | 25 | 16 | 8 | 0 | 30 | 30 | 0 | 0 | 8 | 223 | 0 | 0 | 0 |  | 12 | 24 | 49 | 25 | 0 | 26 | 10 | 4 | 0 | 0 | 0 | 280 | 280 | 182 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 44 | 43 | 20 | 11 | 33 | 20 | 138 | 30 | 0 | 18 | 1 | 43 | 30 | 42 | 47 | 80 | 0 | 60 | 78 | 0 | 204 | 17 | 0 | 10 | 295 | 24 | 8 | 0 | 112 | 0 | 0 | 68 | 0 | 36 | 11 | 25 | 17 | 3 | 317 | 19 | 35 | 48 | 3 | 88 | 17 | 74 | 34 | 9 | 25 | 50 | 35 | 29 | 0 | 34 | 0 | 17 | 17 | 58 | 17 | 250 | 17 | 0 | 0 | 9 |  | 906 | 0 | 160 | 0 | 48 | 223 | 0 | 0 | 11 | 26 | 8 | 132 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 390 | 36 | 0 | 35 | 32 | 34 | 0 | 3 | 35 | 1244 | 220 | 0 | 17 | 2 | 59 | 0 | 0 | 0 | 0 | 12 | 0 | 717 | 91 | 0 |  | 6766 | 4886 | 11652 | 3910 | 906 | 2331 | 0 | 1497 | 2131 | 60 | 223 | 219 | 138 | 228 | 9 | 1430.59 | 75
9:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 402 | 327 |  | 0 | 450 | 280 | 58 | 96 | 15 | 328 | 0 | 197 | 40 | 24 | 48 | 43 | 0 | 0 | 0 | 0 | 5 | 0 | 19 | 19 | 21 | 25 | 16 | 8 | 0 | 30 | 30 | 0 | 0 | 8 | 222 | 0 | 0 | 0 |  | 12 | 24 | 40 | 25 | 0 | 26 | 10 | 2 | 0 | 0 | 0 | 280 | 280 | 193 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 44 | 34 | 20 | 11 | 33 | 20 | 142 | 30 | 0 | 18 | 2 | 43 | 30 | 42 | 47 | 112 | 0 | 60 | 78 | 0 | 204 | 17 | 0 | 10 | 300 | 24 | 8 | 0 | 112 | 0 | 0 | 68 | 0 | 35 | 5 | 25 | 17 | 5 | 368 | 19 | 35 | 48 | 4 | 88 | 17 | 74 | 34 | 9 | 25 | 50 | 35 | 40 | 0 | 34 | 0 | 17 | 18 | 58 | 17 | 250 | 17 | 0 | 0 | 8 |  | 906 | 0 | 160 | 0 | 33 | 221 | 0 | 0 | 11 | 26 | 16 | 126 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 1 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 380 | 36 | 0 | 35 | 32 | 34 | 0 | 5 | 35 | 1232 | 220 | 0 | 17 | 2 | 66 | 0 | 0 | 0 | 0 | 23 | 0 | 717 | 148 | 0 |  | 6852 | 4915 | 11767 | 3993 | 906 | 2311 | 0 | 1484 | 2119 | 60 | 221 | 210 | 142 | 313 | 8 | 1607.265 | 75.02
10:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 403 | 327 |  | 0 | 450 | 292 | 59 | 96 | 15 | 327 | 0 | 195 | 50 | 24 | 82 | 31 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 19 | 7 | 25 | 23 | 8 | 0 | 30 | 30 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 12 | 24 | 32 | 25 | 0 | 26 | 11 | 2 | 0 | 0 | 0 | 280 | 280 | 196 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 43 | 34 | 17 | 0 | 33 | 20 | 148 | 30 | 0 | 18 | 2 | 43 | 30 | 42 | 47 | 112 | 0 | 60 | 78 | 0 | 204 | 17 | 0 | 10 | 290 | 24 | 8 | 0 | 112 | 0 | 0 | 69 | 0 | 35 | 20 | 25 | 26 | 5 | 367 | 19 | 35 | 48 | 3 | 88 | 17 | 74 | 52 | 9 | 25 | 50 | 35 | 36 | 17 | 41 | 0 | 17 | 30 | 65 | 17 | 250 | 17 | 0 | 0 | 9 |  | 905 | 0 | 155 | 0 | 32 | 222 | 0 | 0 | 11 | 23 | 16 | 124 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 414 | 36 | 0 | 35 | 32 | 34 | 0 | 6 | 35 | 1232 | 221 | 0 | 17 | 5 | 83 | 5 | 0 | 0 | 0 | 16 | 0 | 720 | 185 | 0 |  | 6950 | 5005 | 11955 | 3964 | 905 | 2350 | 0 | 1557 | 2122 | 60 | 222 | 232 | 148 | 386 | 9 | 1523.225 | 75.04
11:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 404 | 327 |  | 0 | 450 | 300 | 58 | 95 | 15 | 331 | 0 | 195 | 50 | 50 | 82 | 37 | 0 | 0 | 0 | 0 | 17 | 5 | 19 | 19 | 21 | 25 | 23 | 8 | 0 | 30 | 30 | 0 | 0 | 8 | 222 | 0 | 0 | 0 |  | 12 | 24 | 32 | 25 | 0 | 32 | 11 | 2 | 0 | 0 | 0 | 280 | 280 | 190 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 43 | 43 | 17 | 11 | 33 | 20 | 140 | 30 | 0 | 18 | 2 | 43 | 30 | 44 | 46 | 80 | 0 | 60 | 78 | 0 | 202 | 17 | 0 | 10 | 290 | 24 | 8 | 0 | 115 | 0 | 0 | 68 | 0 | 68 | 17 | 25 | 35 | 5 | 368 | 19 | 52 | 48 | 5 | 87 | 17 | 54 | 52 | 9 | 25 | 50 | 45 | 23 | 17 | 51 | 0 | 17 | 32 | 89 | 17 | 240 | 53 | 0 | 0 | 14 |  | 906 | 0 | 150 | 0 | 32 | 220 | 0 | 0 | 11 | 24 | 16 | 124 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 350 | 36 | 0 | 35 | 32 | 34 | 0 | 7 | 35 | 1222 | 221 | 0 | 17 | 5 | 98 | 35 | 0 | 0 | 0 | 34 | 0 | 719 | 179 | 0 |  | 7103 | 4974 | 12077 | 3970 | 906 | 2256 | 0 | 1729 | 2111 | 60 | 220 | 269 | 140 | 402 | 14 | 1549.965 | 75.06
12:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 401 | 327 |  | 0 | 450 | 294 | 58 | 95 | 15 | 324 | 0 | 191 | 50 | 50 | 96 | 36 | 0 | 0 | 0 | 0 | 17 | 35 | 19 | 19 | 21 | 25 | 23 | 8 | 0 | 30 | 30 | 0 | 0 | 8 | 220 | 0 | 0 | 0 |  | 12 | 24 | 32 | 35 | 0 | 32 | 11 | 2 | 0 | 0 | 0 | 280 | 280 | 179 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 36 | 43 | 19 | 11 | 32 | 20 | 160 | 30 | 0 | 19 | 2 | 43 | 30 | 44 | 46 | 80 | 0 | 60 | 77 | 0 | 204 | 17 | 0 | 10 | 290 | 24 | 8 | 0 | 145 | 260 | 0 | 67 | 0 | 89 | 12 | 37 | 34 | 5 | 368 | 19 | 52 | 74 | 5 | 87 | 17 | 54 | 52 | 9 | 38 | 50 | 54 | 48 | 17 | 51 | 0 | 17 | 16 | 93 | 17 | 240 | 53 | 0 | 0 | 6 |  | 904 | 0 | 145 | 0 | 16 | 218 | 0 | 0 | 11 | 25 | 16 | 124 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 414 | 36 | 0 | 35 | 32 | 34 | 0 | 7 | 35 | 1222 | 221 | 0 | 17 | 5 | 107 | 75 | 0 | 0 | 0 | 19 | 0 | 716 | 207 | 0 |  | 7508 | 5078 | 12586 | 3940 | 904 | 2320 | 260 | 1905 | 2108 | 60 | 218 | 277 | 160 | 428 | 6 | 1541.37 | 75.09
13:00 | 0 | 0 | 156 | 180 | 0 | 0 | 0 | 397 | 322 |  | 0 | 450 | 300 | 59 | 92 | 15 | 321 | 0 | 193 | 50 | 50 | 96 | 45 | 0 | 0 | 0 | 0 | 17 | 35 | 19 | 19 | 21 | 25 | 23 | 8 | 0 | 30 | 30 | 0 | 0 | 8 | 217 | 0 | 0 | 0 |  | 12 | 24 | 31 | 35 | 6 | 32 | 11 | 8 | 0 | 0 | 0 | 280 | 280 | 172 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 36 | 43 | 20 | 11 | 30 | 20 | 160 | 30 | 0 | 19 | 2 | 43 | 30 | 44 | 43 | 80 | 0 | 59 | 80 | 0 | 199 | 17 | 0 | 10 | 305 | 24 | 8 | 0 | 148 | 282 | 0 | 67 | 0 | 89 | 13 | 37 | 36 | 3 | 369 | 19 | 52 | 80 | 5 | 88 | 17 | 54 | 52 | 9 | 25 | 79 | 54 | 43 | 17 | 51 | 0 | 17 | 34 | 93 | 17 | 240 | 53 | 0 | 0 | 12 |  | 906 | 0 | 140 | 0 | 16 | 218 | 0 | 0 | 11 | 30 | 16 | 132 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 380 | 37 | 0 | 35 | 32 | 34 | 0 | 7 | 35 | 1222 | 221 | 0 | 0 | 5 | 99 | 75 | 0 | 0 | 0 | 32 | 0 | 712 | 206 | 0 |  | 7585 | 5037 | 12622 | 3945 | 906 | 2309 | 282 | 1899 | 2104 | 60 | 218 | 281 | 160 | 446 | 12 | 1506.99 | 75.12
14:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 398 | 322 |  | 0 | 450 | 299 | 58 | 92 | 15 | 318 | 0 | 187 | 58 | 50 | 96 | 45 | 0 | 0 | 0 | 0 | 17 | 35 | 19 | 19 | 21 | 25 | 23 | 8 | 0 | 30 | 30 | 0 | 0 | 8 | 216 | 0 | 0 | 0 |  | 12 | 16 | 31 | 35 | 12 | 32 | 11 | 3 | 0 | 0 | 0 | 280 | 280 | 173 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 36 | 33 | 20 | 11 | 30 | 20 | 154 | 30 | 0 | 19 | 2 | 43 | 30 | 44 | 43 | 80 | 0 | 59 | 80 | 0 | 199 | 17 | 0 | 10 | 300 | 24 | 8 | 0 | 148 | 250 | 0 | 67 | 0 | 89 | 5 | 37 | 36 | 2 | 390 | 19 | 52 | 90 | 2 | 88 | 17 | 74 | 52 | 9 | 38 | 100 | 54 | 50 | 17 | 51 | 0 | 17 | 26 | 96 | 17 | 240 | 53 | 0 | 0 | 14 |  | 905 | 0 | 140 | 0 | 15 | 203 | 0 | 0 | 11 | 25 | 16 | 128 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 380 | 41 | 0 | 35 | 32 | 34 | 0 | 7 | 35 | 1232 | 221 | 0 | 0 | 4 | 29 | 75 | 0 | 0 | 0 | 32 | 0 | 718 | 190 | 0 |  | 7604 | 4944 | 12548 | 3978 | 905 | 2299 | 250 | 1950 | 2120 | 60 | 203 | 268 | 154 | 347 | 14 | 1529.91 | 75.06
15:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 393 | 312 |  | 0 | 450 | 297 | 45 | 90 | 15 | 316 | 0 | 187 | 56 | 66 | 96 | 42 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 19 | 21 | 25 | 14 | 8 | 0 | 30 | 30 | 0 | 0 | 8 | 213 | 0 | 0 | 0 |  | 12 | 17 | 31 | 35 | 11 | 32 | 11 | 3 | 0 | 0 | 0 | 280 | 280 | 173 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 35 | 32 | 20 | 11 | 30 | 20 | 144 | 32 | 0 | 19 | 2 | 43 | 30 | 44 | 45 | 80 | 0 | 59 | 79 | 0 | 196 | 17 | 0 | 10 | 320 | 24 | 8 | 0 | 120 | 301 | 0 | 68 | 0 | 65 | 17 | 25 | 36 | 5 | 368 | 19 | 52 | 96 | 4 | 88 | 17 | 74 | 52 | 8 | 25 | 113 | 55 | 19 | 17 | 51 | 0 | 17 | 26 | 65 | 17 | 240 | 53 | 0 | 0 | 21 |  | 907 | 0 | 140 | 0 | 0 | 204 | 0 | 0 | 11 | 22 | 16 | 128 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 362 | 53 | 0 | 37 | 32 | 34 | 0 | 6 | 35 | 1244 | 221 | 0 | 0 | 3 | 48 | 75 | 0 | 0 | 0 | 23 | 0 | 713 | 117 | 0 |  | 7528 | 4867 | 12395 | 3948 | 907 | 2291 | 301 | 1862 | 2127 | 60 | 204 | 265 | 144 | 265 | 21 | 1723.775 | 75.18
16:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 395 | 312 |  | 0 | 450 | 289 | 42 | 90 | 15 | 316 | 0 | 186 | 55 | 66 | 96 | 36 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 19 | 21 | 25 | 22 | 8 | 0 | 30 | 30 | 0 | 0 | 8 | 221 | 0 | 0 | 0 |  | 12 | 41 | 31 | 25 | 11 | 26 | 11 | 3 | 0 | 0 | 0 | 265 | 280 | 165 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 35 | 32 | 20 | 11 | 30 | 20 | 140 | 31 | 0 | 19 | 1 | 43 | 30 | 44 | 43 | 112 | 0 | 59 | 80 | 0 | 197 | 16 | 0 | 10 | 310 | 16 | 8 | 0 | 97 | 160 | 0 | 67 | 0 | 34 | 7 | 25 | 34 | 3 | 368 | 19 | 52 | 96 | 1 | 88 | 17 | 74 | 52 | 15 | 25 | 124 | 55 | 21 | 17 | 51 | 0 | 17 | 18 | 56 | 17 | 240 | 53 | 0 | 0 | 12 |  | 906 | 0 | 140 | 0 | 16 | 202 | 0 | 0 | 5 | 22 | 16 | 130 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 25 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 414 | 43 | 0 | 50 | 32 | 24 | 0 | 4 | 55 | 1244 | 221 | 0 | 0 | 2 | 54 | 75 | 0 | 0 | 0 | 19 | 0 | 718 | 107 | 0 |  | 7300 | 4919 | 12219 | 3947 | 906 | 2356 | 160 | 1787 | 2132 | 60 | 202 | 283 | 140 | 234 | 12 | 1796.355 | 75.21
17:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 393 | 312 |  | 0 | 450 | 302 | 41 | 92 | 15 | 316 | 0 | 191 | 56 | 66 | 96 | 45 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 19 | 21 | 25 | 15 | 8 | 0 | 30 | 30 | 0 | 0 | 8 | 220 | 0 | 0 | 0 |  | 12 | 56 | 31 | 35 | 11 | 26 | 11 | 14 | 0 | 0 | 0 | 270 | 240 | 168 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 40 | 34 | 20 | 11 | 30 | 20 | 148 | 31 | 0 | 19 | 1 | 43 | 20 | 44 | 45 | 112 | 0 | 59 | 80 | 0 | 199 | 17 | 0 | 10 | 305 | 24 | 8 | 0 | 97 | 30 | 0 | 67 | 0 | 35 | 5 | 25 | 34 | 5 | 368 | 19 | 52 | 96 | 2 | 88 | 17 | 74 | 50 | 27 | 28 | 138 | 55 | 9 | 17 | 51 | 0 | 17 | 0 | 52 | 17 | 240 | 53 | 0 | 0 | 12 |  | 907 | 0 | 140 | 0 | 16 | 202 | 0 | 0 | 11 | 22 | 16 | 132 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 25 | 0 | 8 | 35 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 414 | 35 | 0 | 50 | 32 | 60 | 0 | 3 | 55 | 1244 | 221 | 0 | 0 | 1 | 38 | 36 | 50 | 0 | 0 | 10 | 0 | 719 | 46 | 0 |  | 7201 | 4916 | 12117 | 3928 | 907 | 2377 | 30 | 1811 | 2133 | 60 | 252 | 344 | 148 | 115 | 12 | 1621.59 | 75.24
18:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 383 | 315 |  | 0 | 450 | 288 | 51 | 93 | 15 | 280 | 0 | 154 | 56 | 65 | 96 | 45 | 0 | 0 | 0 | 35 | 17 | 55 | 19 | 19 | 21 | 25 | 22 | 16 | 0 | 30 | 30 | 0 | 0 | 12 | 222 | 0 | 0 | 0 |  | 12 | 56 | 31 | 46 | 12 | 39 | 11 | 15 | 0 | 0 | 0 | 265 | 240 | 186 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 40 | 41 | 20 | 11 | 32 | 20 | 146 | 42 | 0 | 19 | 0 | 43 | 20 | 44 | 43 | 80 | 0 | 60 | 80 | 0 | 202 | 17 | 0 | 10 | 270 | 16 | 8 | 0 | 97 | 0 | 0 | 67 | 0 | 54 | 1 | 25 | 42 | 5 | 319 | 19 | 52 | 96 | 0 | 104 | 17 | 74 | 50 | 36 | 29 | 229 | 54 | 5 | 54 | 53 | 0 | 17 | 2 | 54 | 17 | 240 | 53 | 0 | 0 | 8 |  | 907 | 0 | 145 | 0 | 16 | 205 | 0 | 0 | 25 | 30 | 16 | 124 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 20 | 21 | 34 | 28 | 8 | 35 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 370 | 35 | 0 | 50 | 105 | 70 | 0 | 1 | 55 | 1220 | 221 | 0 | 0 | 0 | 16 | 36 | 50 | 0 | 0 | 2 | 0 | 721 | 14 | 0 |  | 7252 | 4946 | 12198 | 3916 | 907 | 2252 | 0 | 2088 | 2111 | 60 | 255 | 414 | 146 | 41 | 8 | 1625 | 75.27
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 352 | 307 |  | 0 | 450 | 297 | 58 | 93 | 15 | 323 | 0 | 169 | 65 | 102 | 130 | 40 | 0 | 0 | 0 | 35 | 17 | 55 | 19 | 19 | 21 | 25 | 22 | 25 | 0 | 30 | 30 | 0 | 0 | 16 | 216 | 0 | 0 | 0 |  | 12 | 56 | 33 | 46 | 16 | 40 | 11 | 26 | 0 | 0 | 0 | 305 | 240 | 204 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 40 | 41 | 20 | 11 | 32 | 20 | 138 | 82 | 0 | 19 | 0 | 43 | 20 | 42 | 46 | 80 | 0 | 40 | 80 | 0 | 204 | 17 | 0 | 10 | 255 | 24 | 8 | 0 | 97 | 0 | 0 | 87 | 0 | 143 | 0 | 37 | 51 | 36 | 349 | 84 | 88 | 96 | 0 | 221 | 17 | 74 | 50 | 66 | 42 | 300 | 58 | 0 | 54 | 76 | 0 | 17 | 0 | 61 | 17 | 240 | 163 | 0 | 0 | 13 |  | 906 | 0 | 150 | 0 | 47 | 221 | 0 | 0 | 26 | 50 | 32 | 132 | 30 | 32 | 0 | 0 | 0 | 35 | 0 | 63 | 21 | 34 | 29 | 8 | 35 | 0 | 0 | 8 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 330 | 35 | 0 | 55 | 105 | 70 | 0 | 0 | 55 | 1222 | 221 | 0 | 0 | 0 | 0 | 36 | 50 | 0 | 0 | 0 | 0 | 725 | 0 | 0 |  | 8117 | 5146 | 13263 | 4143 | 906 | 2217 | 0 | 2678 | 2177 | 60 | 271 | 660 | 138 | 0 | 13 | 1276.835 | 75.35
19:30 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 403 | 332 |  | 0 | 450 | 304 | 59 | 94 | 15 | 325 | 0 | 196 | 72 | 102 | 130 | 45 | 0 | 0 | 0 | 35 | 17 | 55 | 19 | 19 | 21 | 25 | 22 | 25 | 0 | 30 | 30 | 0 | 0 | 16 | 222 | 0 | 0 | 0 |  | 12 | 63 | 33 | 46 | 17 | 39 | 11 | 26 | 0 | 0 | 0 | 270 | 240 | 201 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 40 | 42 | 20 | 11 | 32 | 20 | 130 | 82 | 0 | 19 | 0 | 43 | 27 | 42 | 46 | 112 | 0 | 61 | 80 | 0 | 201 | 17 | 0 | 10 | 270 | 24 | 8 | 0 | 97 | 30 | 0 | 87 | 0 | 134 | 0 | 37 | 51 | 100 | 367 | 84 | 88 | 96 | 0 | 236 | 18 | 74 | 54 | 95 | 42 | 360 | 72 | 0 | 108 | 87 | 0 | 17 | 0 | 96 | 20 | 240 | 163 | 0 | 0 | 10 |  | 907 | 0 | 155 | 0 | 56 | 207 | 0 | 0 | 32 | 55 | 32 | 132 | 32 | 32 | 0 | 0 | 0 | 35 | 0 | 92 | 21 | 34 | 30 | 8 | 35 | 0 | 0 | 8 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 414 | 35 | 0 | 60 | 105 | 80 | 0 | 0 | 75 | 1222 | 221 | 0 | 0 | 0 | 0 | 72 | 232 | 0 | 0 | 0 | 0 | 715 | 0 | 0 |  | 8609 | 5521 | 14130 | 4303 | 907 | 2382 | 30 | 2994 | 2167 | 60 | 439 | 708 | 130 | 0 | 10 | 1260.6 | 0
20:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 398 | 338 |  | 0 | 450 | 275 | 59 | 96 | 15 | 323 | 0 | 186 | 72 | 102 | 130 | 42 | 0 | 0 | 0 | 35 | 17 | 55 | 19 | 19 | 21 | 25 | 22 | 25 | 0 | 30 | 30 | 0 | 0 | 16 | 202 | 0 | 0 | 0 |  | 12 | 63 | 33 | 46 | 17 | 39 | 11 | 30 | 0 | 0 | 0 | 270 | 240 | 204 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 40 | 42 | 20 | 11 | 33 | 20 | 122 | 83 | 0 | 19 | 0 | 43 | 40 | 44 | 46 | 112 | 0 | 61 | 81 | 0 | 202 | 17 | 0 | 10 | 280 | 24 | 8 | 0 | 97 | 10 | 0 | 87 | 0 | 135 | 0 | 37 | 51 | 93 | 414 | 84 | 88 | 96 | 0 | 272 | 25 | 74 | 103 | 94 | 43 | 385 | 71 | 0 | 108 | 87 | 0 | 17 | 0 | 94 | 32 | 240 | 163 | 0 | 0 | 12 |  | 766 | 0 | 155 | 0 | 81 | 207 | 0 | 0 | 21 | 60 | 40 | 132 | 32 | 32 | 0 | 0 | 0 | 35 | 0 | 90 | 21 | 34 | 30 | 8 | 35 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 414 | 36 | 0 | 70 | 105 | 84 | 0 | 0 | 75 | 1222 | 220 | 0 | 0 | 0 | 0 | 75 | 232 | 0 | 0 | 0 | 0 | 715 | 0 | 0 |  | 8725 | 5418 | 14143 | 4348 | 766 | 2375 | 10 | 3139 | 2172 | 60 | 439 | 700 | 122 | 0 | 12 | 1343.685 | 75.33
21:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 403 | 343 |  | 0 | 450 | 274 | 58 | 96 | 15 | 323 | 0 | 195 | 72 | 102 | 130 | 31 | 0 | 0 | 0 | 35 | 17 | 55 | 19 | 19 | 21 | 25 | 22 | 25 | 0 | 30 | 30 | 0 | 0 | 16 | 224 | 0 | 0 | 0 |  | 12 | 66 | 33 | 46 | 18 | 39 | 11 | 34 | 0 | 0 | 0 | 275 | 240 | 205 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 42 | 42 | 20 | 11 | 33 | 20 | 120 | 53 | 0 | 19 | 0 | 43 | 40 | 44 | 46 | 112 | 0 | 60 | 81 | 0 | 201 | 17 | 0 | 10 | 290 | 24 | 8 | 0 | 97 | 296 | 0 | 87 | 0 | 151 | 0 | 37 | 51 | 125 | 407 | 84 | 88 | 96 | 0 | 276 | 36 | 74 | 103 | 97 | 44 | 347 | 59 | 0 | 108 | 100 | 0 | 17 | 0 | 99 | 17 | 240 | 163 | 0 | 0 | 2 |  | 764 | 0 | 160 | 0 | 86 | 208 | 0 | 0 | 21 | 54 | 40 | 132 | 34 | 32 | 0 | 0 | 0 | 35 | 0 | 90 | 21 | 25 | 29 | 8 | 35 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 414 | 36 | 0 | 70 | 105 | 84 | 0 | 0 | 75 | 1222 | 220 | 0 | 0 | 0 | 0 | 75 | 233 | 0 | 0 | 0 | 0 | 716 | 0 | 0 |  | 9034 | 5414 | 14448 | 4317 | 764 | 2395 | 296 | 3182 | 2173 | 60 | 441 | 698 | 120 | 0 | 2 | 1100.16 | 75.35
22:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 400 | 344 |  | 0 | 450 | 289 | 58 | 96 | 15 | 327 | 0 | 195 | 72 | 102 | 130 | 34 | 0 | 0 | 0 | 35 | 17 | 55 | 19 | 19 | 21 | 25 | 22 | 25 | 0 | 30 | 30 | 0 | 0 | 16 | 209 | 0 | 0 | 0 |  | 12 | 65 | 50 | 46 | 18 | 40 | 11 | 35 | 0 | 0 | 0 | 275 | 240 | 204 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 43 | 43 | 20 | 11 | 33 | 20 | 110 | 53 | 0 | 19 | 0 | 43 | 40 | 44 | 46 | 112 | 0 | 58 | 81 | 0 | 203 | 17 | 0 | 10 | 280 | 24 | 8 | 0 | 100 | 150 | 0 | 88 | 0 | 149 | 0 | 37 | 51 | 130 | 409 | 84 | 88 | 96 | 0 | 283 | 36 | 74 | 103 | 97 | 45 | 340 | 70 | 0 | 108 | 107 | 0 | 17 | 0 | 93 | 17 | 240 | 163 | 0 | 0 | 12 |  | 764 | 0 | 160 | 0 | 97 | 207 | 0 | 0 | 16 | 54 | 40 | 132 | 35 | 32 | 0 | 0 | 0 | 35 | 0 | 90 | 21 | 25 | 29 | 8 | 35 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 380 | 35 | 0 | 70 | 105 | 84 | 0 | 0 | 75 | 1232 | 220 | 0 | 0 | 0 | 0 | 75 | 233 | 0 | 0 | 0 | 0 | 720 | 0 | 0 |  | 8924 | 5397 | 14321 | 4295 | 764 | 2369 | 150 | 3224 | 2187 | 60 | 440 | 710 | 110 | 0 | 12 | 1125.945 | 75.39
23:00 | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 394 | 342 |  | 0 | 450 | 281 | 45 | 96 | 15 | 330 | 0 | 195 | 38 | 102 | 130 | 34 | 0 | 0 | 0 | 35 | 17 | 35 | 19 | 19 | 21 | 25 | 23 | 25 | 0 | 30 | 30 | 0 | 0 | 10 | 226 | 0 | 0 | 0 |  | 9 | 66 | 50 | 46 | 0 | 40 | 11 | 39 | 0 | 0 | 0 | 275 | 240 | 185 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 44 | 43 | 20 | 11 | 33 | 20 | 136 | 71 | 0 | 18 | 0 | 43 | 40 | 45 | 46 | 112 | 0 | 58 | 81 | 0 | 203 | 17 | 0 | 10 | 300 | 24 | 8 | 0 | 100 | 301 | 0 | 68 | 0 | 78 | 0 | 37 | 51 | 55 | 404 | 18 | 88 | 96 | 0 | 124 | 36 | 74 | 103 | 57 | 46 | 340 | 71 | 0 | 108 | 107 | 0 | 17 | 0 | 86 | 17 | 240 | 163 | 0 | 0 | 5 |  | 764 | 0 | 145 | 0 | 32 | 208 | 0 | 0 | 16 | 51 | 32 | 130 | 35 | 32 | 0 | 0 | 0 | 35 | 0 | 90 | 21 | 34 | 27 | 8 | 35 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 414 | 35 | 0 | 70 | 105 | 84 | 0 | 0 | 75 | 1244 | 220 | 0 | 19 | 0 | 0 | 75 | 234 | 0 | 0 | 0 | 0 | 722 | 0 | 0 |  | 8589 | 5380 | 13969 | 4286 | 764 | 2418 | 301 | 2649 | 2201 | 60 | 442 | 707 | 136 | 0 | 5 | 1414.355 | 75.42
24:00 | 0 | 0 | 180 | 180 | 0 | 0 | 0 | 402 | 339 |  | 0 | 450 | 302 | 42 | 96 | 15 | 322 | 0 | 187 | 33 | 40 | 130 | 33 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 19 | 21 | 25 | 23 | 8 | 0 | 30 | 30 | 0 | 0 | 8 | 222 | 0 | 0 | 0 |  | 12 | 66 | 50 | 25 | 0 | 40 | 11 | 37 | 0 | 0 | 0 | 330 | 240 | 161 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 44 | 43 | 20 | 11 | 33 | 20 | 120 | 71 | 0 | 18 | 0 | 43 | 40 | 45 | 46 | 112 | 0 | 58 | 81 | 0 | 203 | 17 | 0 | 10 | 310 | 24 | 8 | 0 | 100 | 300 | 0 | 68 | 0 | 35 | 0 | 25 | 21 | 6 | 390 | 18 | 34 | 96 | 0 | 124 | 36 | 71 | 103 | 9 | 47 | 348 | 71 | 0 | 103 | 107 | 0 | 17 | 0 | 57 | 17 | 240 | 72 | 0 | 0 | 3 |  | 781 | 0 | 150 | 0 | 32 | 205 | 0 | 0 | 10 | 51 | 32 | 130 | 35 | 32 | 0 | 0 | 0 | 35 | 0 | 90 | 21 | 34 | 27 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 414 | 36 | 0 | 35 | 105 | 34 | 0 | 0 | 57 | 1244 | 220 | 0 | 150 | 0 | 0 | 0 | 231 | 0 | 0 | 0 | 0 | 717 | 0 | 0 |  | 8140 | 5303 | 13443 | 4323 | 781 | 2444 | 300 | 2205 | 2196 | 60 | 436 | 575 | 120 | 0 | 3 | 1677.935 | 75.45
KWH | 0 | 0 | 3838000 | 4347000 | 0 | 0 | 0 | 9664510 | 7800000 |  | 0 | 10223500 | 7169309 | 1206720 | 2191487 | 370302 | 7753931 | 0 | 4674000 | 1111680 | 1222416 | 2066400 | 1023702 | 0 | 0 | 0 | 272160 | 318910 | 537753 | 418212 | 456000 | 462780 | 589300 | 515000 | 302400 | 0 | 727806 | 732000 | 0 | 0 | 234696 | 5232023 | 0 | 0 | 0 |  | 294720 | 882000 | 964124 | 713040 | 140160 | 766560 | 253536 | 514080 | 0 | 0 | 0 | 7231300 | 6350000 | 4605000 | 0 | 0 | 134136 | 0 | 0 | 955692 | 0 | 985680 | 963086 | 467532 | 239400 | 786700 | 492830 | 3465600 | 1240320 | 0 | 414828 | 14850 | 1020000 | 684720 | 1029600 | 1054440 | 2403081 | 0 | 1404096 | 1845120 | 0 | 4082110 | 387000 | 0 | 244620 | 7325000 | 553104 | 171552 | 0 | 2692255 | 3320335 | 0 | 1718400 | 0 | 1588608 | 117180 | 696960 | 764640 | 531927 | 9233000 | 711600 | 1265280 | 1758036 | 32879 | 2918073 | 528669 | 1734610 | 1309860 | 638400 | 740160 | 3849300 | 1262400 | 354410 | 768960 | 1372473 | 0 | 471240 | 236363 | 1682880 | 447840 | 6093500 | 1453600 | 0 | 0 | 215040 |  | 21067887 | 0 | 2510496 | 0 | 948480 | 5192237 | 0 | 0 | 285600 | 907904 | 421500 | 3107000 | 648144 | 622560 | 0 | 0 | 0 | 215024 | 0 | 508544 | 494720 | 843208 | 215077 | 200150 | 241060 | 0 | 0 | 133400 | 0 | 0 | 4461900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3933918 | 0 | 9555454 | 880320 | 0 | 1136352 | 1339632 | 1115990 | 0 | 56487 | 1172448 | 31443100 | 5287909 | 0 | 404400 | 38580 | 712800 | 855360 | 2503821 | 0 | 0 | 226130 | 0 | 17198182 | 1499830 | 0 |  | 181050492 | 122385604 | 303436096 | 97329534 | 21067887 | 56055949 | 3320335 | 47708183 | 53103182 | 1459806 | 7696058 | 8725013 | 3465600 | 3289509 | 215040 | 0
Fuel Cost | 0 | 0 | 5603480 | 6477030 | 0 | 0 | 0 | 10147735.5 | 8424000 |  | 0 | 11143615 | 7957932.99 | 13491129.6 | 29037202.75 | 4906501.5 | 8684402.72 | 0 | 8179500 | 16252761.6 | 17199393.12 | 33496344 | 9438532.44 | 0 | 0 | 0 | 3461875.2 | 4305285 | 7211267.73 | 313659 | 342000 | 0 | 0 | 0 | 5143824 | 0 | 196507.62 | 197640 | 0 | 0 | 3837279.6 | 5441303.92 | 0 | 0 | 0 |  | 3846096 | 14711760 | 16409390.48 | 9633170.4 | 1777228.8 | 8869099.2 | 321990.72 | 1711886.4 | 0 | 0 | 0 | 8026743 | 6921500 | 5341800 | 0 | 0 | 151573.68 | 0 | 0 | 1596005.64 | 0 | 17022693.6 | 12953506.7 | 640518.84 | 179550 | 1376725 | 369622.5 | 24883008 | 1351948.8 | 0 | 564166.08 | 236709 | 1397400 | 903830.4 | 1791504 | 1824181.2 | 2763543.15 | 0 | 2723946.24 | 4206873.6 | 0 | 4122931.1 | 832050 | 0 | 484347.6 | 7325000 | 414828 | 130379.52 | 0 | 36749280.75 | 69594221.6 | 0 | 23164032 | 0 | 22002220.8 | 1369834.2 | 7192627.2 | 10444982.4 | 7058671.29 | 8494360 | 8653056 | 18295948.8 | 22239155.4 | 0 | 34258177.02 | 5757205.41 | 18438904.3 | 17774800.2 | 8228976 | 8719084.8 | 3541356 | 16348080 | 5121224.5 | 9758102.4 | 15618742.74 | 0 | 6154394.4 | 2824537.85 | 25192713.6 | 5898052.8 | 0 | 0 | 0 | 0 | 0 |  | 63203661 | 0 | 2811755.52 | 0 | 9873676.8 | 85671910.5 | 0 | 0 | 5143656 | 16342272 | 6056955 | 3479840 | 1257399.36 | 6785904 | 0 | 0 | 0 | 3605952.48 | 0 | 7953628.16 | 3809344 | 13963524.48 | 3636952.07 | 2728044.5 | 4066682.2 | 0 | 0 | 100983.8 | 0 | 0 | 23603451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4563344.88 | 0 | 9459899.46 | 11831500.8 | 0 | 13443044.16 | 19357682.4 | 14173073 | 0 | 624181.35 | 14233518.72 | 283302331 | 5393667.18 | 0 | 2992560 | 436339.8 | 8361144 | 13112668.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 807600453.4 | 665380548.42 | 1472981001.82 | 103952255.22 | 63203661 | 65339855.58 | 69594221.6 | 611672858.61 | 306905782 | 394147.62 | 85671910.5 | 122389330.99 | 24883008 | 18973970.7 | 0 | 0
Yesterday Day Peak | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 401 | 327 |  | 0 | 450 | 294 | 58 | 95 | 15 | 324 | 0 | 191 | 50 | 50 | 96 | 36 | 0 | 0 | 0 | 0 | 17 | 35 | 19 | 19 | 21 | 25 | 23 | 8 | 0 | 30 | 30 | 0 | 0 | 8 | 220 | 0 | 0 | 0 |  | 12 | 24 | 32 | 35 | 0 | 32 | 11 | 2 | 0 | 0 | 0 | 280 | 280 | 179 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 36 | 43 | 19 | 11 | 32 | 20 | 160 | 30 | 0 | 19 | 2 | 43 | 30 | 44 | 46 | 80 | 0 | 60 | 77 | 0 | 204 | 17 | 0 | 10 | 290 | 24 | 8 | 0 | 145 | 260 | 0 | 67 | 0 | 89 | 12 | 37 | 34 | 5 | 368 | 19 | 52 | 74 | 5 | 87 | 17 | 54 | 52 | 9 | 38 | 50 | 54 | 48 | 17 | 51 | 0 | 17 | 16 | 93 | 17 | 240 | 53 | 0 | 0 | 6 |  | 904 | 0 | 145 | 0 | 16 | 218 | 0 | 0 | 11 | 25 | 16 | 124 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 414 | 36 | 0 | 35 | 32 | 34 | 0 | 7 | 35 | 1222 | 221 | 0 | 17 | 5 | 107 | 75 | 0 | 0 | 0 | 19 | 0 | 716 | 207 | 0 |  | 12586 | DayPeak
Yesterday Evening Peak | 0 | 0 | 160 | 180 | 0 | 0 | 0 | 403 | 343 | 0 | 0 | 450 | 274 | 58 | 96 | 15 | 323 | 0 | 195 | 72 | 102 | 130 | 31 | 0 | 0 | 0 | 35 | 17 | 55 | 19 | 19 | 21 | 25 | 22 | 25 | 0 | 30 | 30 | 0 | 0 | 16 | 224 | 0 | 0 | 0 | 0 | 12 | 66 | 33 | 46 | 18 | 39 | 11 | 34 | 0 | 0 | 0 | 275 | 240 | 205 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 42 | 42 | 20 | 11 | 33 | 20 | 120 | 53 | 0 | 19 | 0 | 43 | 40 | 44 | 46 | 112 | 0 | 60 | 81 | 0 | 201 | 17 | 0 | 10 | 290 | 24 | 8 | 0 | 97 | 296 | 0 | 87 | 0 | 151 | 0 | 37 | 51 | 125 | 407 | 84 | 88 | 96 | 0 | 276 | 36 | 74 | 103 | 97 | 44 | 347 | 59 | 0 | 108 | 100 | 0 | 17 | 0 | 99 | 17 | 240 | 163 | 0 | 0 | 2 |  | 764 | 0 | 160 | 0 | 86 | 208 | 0 | 0 | 21 | 54 | 40 | 132 | 34 | 32 | 0 | 0 | 0 | 35 | 0 | 90 | 21 | 25 | 29 | 8 | 35 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 414 | 36 | 0 | 70 | 105 | 84 | 0 | 0 | 75 | 1222 | 220 | 0 | 0 | 0 | 0 | 75 | 233 | 0 | 0 | 0 | 0 | 716 | 0 | 0 |  | 14448 | EvPeak
Forecast for Evening | 0 | 0 | 180 | 180 | 0 | 0 | 0 | 400 | 330 | 0 | 0 | 450 | 300 | 64 | 96 | 30 | 330 | 0 | 195 | 70 | 102 | 130 | 45 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 20 | 21 | 25 | 22 | 25 | 0 | 30 | 30 | 0 | 0 | 17 | 225 |  | 0 | 0 | 0 | 12 | 66 | 50 | 46 | 18 | 46 | 11 | 20 | 0 | 0 | 0 | 300 | 240 | 200 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 43 | 43 | 20 | 11 | 33 | 20 | 169 | 50 | 0 | 19 | 0 | 43 | 40 | 45 | 44 | 112 | 0 | 60 | 86 | 0 | 204 | 17 | 0 | 10 | 300 | 24 | 11 | 0 | 115 | 300 | 0 | 88 | 0 | 149 | 0 | 50 | 51 | 150 | 400 | 85 | 88 | 105 | 0 | 300 | 36 | 74 | 88 | 95 | 38 | 385 | 72 | 0 | 126 | 107 | 0 | 17 |  | 98 | 17 | 240 | 163 |  | 0 | 10 |  | 924 | 0 | 150 |  | 98 | 225 | 0 | 0 | 30 | 60 | 40 | 135 | 34 | 32 | 0 | 0 | 0 | 35 | 28 | 93 | 21 | 42 | 29 | 8 | 35 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 155 | 0 | 380 | 35 | 200 | 70 | 105 | 70 | 0 | 0 | 75 | 1244 | 220 |  | 150 |  |  | 115 | 233 |  | 0 |  | 0 | 700 |  | 0
Forecast for Day | 0 | 0 | 180 | 180 | 0 | 0 | 0 | 400 | 330 | 0 | 0 | 450 | 300 | 58 | 96 | 15 | 330 | 0 | 185 | 58 | 50 | 64 | 45 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 20 | 20 | 25 | 22 | 8 | 0 | 30 | 30 | 0 | 0 | 8 | 225 |  | 0 | 0 | 0 | 12 | 32 | 50 | 35 | 12 | 26 | 11 | 5 | 0 | 0 | 0 | 280 | 240 | 200 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 43 | 43 | 20 | 11 | 33 | 20 | 146 | 30 | 0 | 19 | 1.6 | 43 | 40 | 45 | 44 | 112 | 0 | 60 | 86 | 0 | 203 | 17 | 0 | 10 | 300 | 24 | 11 | 0 | 115 | 300 | 0 | 68 | 0 | 34 | 20 | 25 | 34 | 6 | 400 | 20 | 35 | 105 | 5 | 88 | 17 | 74 | 52 | 9 | 25 | 340 | 54 | 50 | 17 | 51 | 0 | 17 | 30 | 98 | 17 | 240 | 17 |  | 0 | 15 |  | 924 | 0 | 150 | 0 | 80 | 210 | 0 | 0 | 20 | 26 | 8 | 135 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 34 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 380 | 35 | 150 | 35 | 50 | 34 | 0 | 8 | 35 | 1244 | 220 |  | 17 | 6 | 100 | 35 | 200 |  | 0 | 30 | 0 | 700 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 200 | 180 | 0 | 0 | 0 | 399 | 337 | 0 | 0 | 450 | 299 | 50 | 96 | 15 | 321 | 0 | 184 | 34 | 24 | 48 | 34 | 0 | 0 | 0 | 0 | 17 | 0 | 16 | 19 | 21 | 25 | 23 | 0 | 0 | 30 | 30 | 0 | 0 | 8 | 216 | 0 | 0 | 0 | 0 | 12 | 0 | 50 | 25 | 0 | 19 | 11 | 12 | 0 | 0 | 0 | 330 | 240 | 152 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 43 | 43 | 20 | 11 | 33 | 20 | 124 | 46 | 0 | 19 | 1 | 43 | 40 | 45 | 46 | 112 | 0 | 59 | 81 | 0 | 201 | 17 | 0 | 10 | 320 | 24 | 8 | 0 | 98 | 0 | 0 | 67 | 0 | 36 | 3 | 25 | 17 | 6 | 404 | 19 | 35 | 105 | 3 | 88 | 17 | 68 | 32 | 9 | 12 | 342 | 49 | 20 | 0 | 34 | 0 | 17 | 15 | 54 | 17 | 240 | 18 | 0 | 0 | 1 | 0 | 905 | 0 | 150 | 0 | 16 | 203 | 0 | 0 | 6 | 20 | 8 | 130 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 34 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 384 | 35 | 0 | 35 | 50 | 34 | 0 | 1 | 35 | 1244 | 220 | 0 | 17 | 1 | 48 | 0 | 0 | 0 | 0 | 15 | 0 | 718 | 106 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
292.3904
| Minimum Generation |  | 11652 | 8:00
| Highest Generation |  | 14448 | 21:00 |  | 340 | 180 |  | 19:00 |  | 160
| Day Peak Generation |  | 12586 | 12:00 |  |  |  | 340 hh
| Evening Peak Generation |  | 14448 | 21:00 |  |  |  |  | Rampal: 0 MW, Payra:1222 MW, Barapukuria: 230 MW at 19:00 hrs on 19/07/23
| HVDC Max Flow |  | 909 | 2:00
| HVDC EvPeak Flow |  | 764 | 21:00
| Load factor L.F |  | 87.51% | [163 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-07-20
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-07-19 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 12586 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 11991
Evening Peak Generation : |  |  | 14448 | MW Hour : | 21:00 | Available Max Generation : |  | 15338
E.P. Demand (at gen end) : |  |  | 15600 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 15800
Maximum Generation : |  |  | 14448 | MW Hour : | 21:00 | Reserve(Generation end) |  | -
Total Gen. (MKWH) : |  |  | 303.4361 | System Load Factor : | 87.51% | Load Shed : |  | 426
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 310 | MW at | 21:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-07-20
Actual : |  | 75.54 | Ft.(MSL) , | Rule curve : | 87.04 | Ft.( MSL )
Gas Consumed : |  | Total = | 1196.89 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 169292110.8
: |  |  | Coal : | 306905782 | Oil : | 889328321.7 | Total : | 1365526214.5
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 138 | 3312:00 | 5180.851 |  |  | 120 | 2.316%
Chittagong Area |  | 0 | 0:00 | 1427.276 |  |  | 55 | 3.853%
Khulna Area |  | 172 | 4128:00 | 2000.4478 |  |  | 50 | 2.499%
Rajshahi Area |  | 100 | 2400:00 | 1739.7767 |  |  | 50 | 2.874%
Cumilla Area |  | 180 | 4320:00 | 1431.0033 |  |  | 45 | 3.145%
Mymensingh Area |  | 200 | 4800:00 | 1064.8547 |  |  | 36 | 3.381%
Sylhet Area |  | 90 | 2160:00 | 596.2968 |  |  | 20 | 3.354%
Barisal Area |  | 40 | 960:00 | 497.4784 |  |  | 15 | 3.015%
Rangpur Area |  | 180 | 4320:00 | 972.9682 |  |  | 35 | 3.597%
Total |  | 1100 |  | 14910.953 |  |  | 426
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
| 08:18 | Barguna 132/33kV S/S Transformer-2 LT is restored.
| 08:18 | Barguna 132/33kV S/S Transformer-2 HT is restored.
09:03 |  | Meghnaghat 230/132kV S/S Meghnaghat-Aminbazar-02 Project Work S/D Due to Project Wortk Shoutdown.
09:57 | 13:06 | Savar 132/33kV S/S Bus-A Scheduled S/D Due to Red hot maintenance
11:13 |  | Meghnaghat 400/230kV T1 was S/D due project work
12:00 |  | Day Peak Gen. 12586 MW
12:04 |  | Bibiyana South 400 MW ST was sync.
14:21 | 14:39 | Ashuganj-Kishoreganj 132kV Ckt-2 Forced S/D from Kishoreganj 132/33kV end Due to emergency ROW
17:20 | 18:16 | Bhaluka-Mymensingh 132 kV Ckt-1 Tripped from Bhaluka 132/33kV end showing O/C RYB Phase, O/C PU Only E, 86.1 | [5 empty] | 80.0MW load interrup.
|  | operated, 86.2 operated. relays Due to O/C RYB Phase, O/C PU Only E.(PT operated at ckt1 sreepur s/s) | [5 empty] | Bhaluka 132/33kV end
17:20 | 18:15 | Sreepur 230/132/33kV S/S Sreepur-Valuka Ckt-2 Tripped showing 7SJ85 relays Due to Over Current
17:20 | 17:58 | Bhaluka-Mymensingh 132 kV Ckt-2 Tripped from Bhaluka 132/33kV end showing O/C. relays Due to Sreepur ckt 2
tripped at sreepur s/s not Bhaluka s/s by O/C.
17:21 | 17:56 | Sreepur 230/132/33kV S/S Sreepur-Valuka Ckt-1 Tripped showing 7SD522 relays Due to PD operate
| 18:04 | Baghabari-Ishurdi 230 kV Ckt-1 is restored.
18:07 |  | Meghnaghat 400/230kV T1 switched on
| 19:11 | Baghabari-Ishurdi 230 kV Ckt-2 is restored.
21:00 |  | Evening Peak Generation = 14,448MW
05:43 |  | Maniknagar-Siddhirganj 230kV Ckt-2 Scheduled S/D from Siddhirganj 230/132kV end Due to Order of NLDC and from
Maniknagar 230/132kV end Due to Tower Erection
07:00 |  | Minimum Generation :12040 MW
07:04 |  | Baghabari-Ishurdi 230 kV Ckt-1 Project Work S/D from Baghabari 230/132kV end Due to Project development work at
Ishurdi SS end. and from Ishurdi 230/132kVend.
07:06 |  | Baghabari-Ishurdi 230 kV Ckt-2 Project Work S/D from Baghabari 230/132kV end Due to Project development work at
Ishurdi SS end. and from Ishurdi 230/132kVend.
07:09 |  | Gopalganj(N)-Madaripur 132kV Ckt-3 Scheduled S/D from Gopalganj 400/132kV end. and from Madaripur 132/33kV end
Due to TCS Relay Installation and Maintenance Works
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-07-19 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 160 | 3838000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 403 | 9664510
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 343 | 7800000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10223500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 58 | 1206720 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 274 | 7169309 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 96 | 2191487 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 370302 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 31 | 1023702 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 418212 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 195 | 4674000
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 72 | 1111680 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 323 | 7753931
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1222416
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 272160 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 130 | 2066400 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 318910 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 537753
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 40 | 918780 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 589300 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 22 | 515000 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 302400 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 97 | 2692255 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 296 | 3320335
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 151 | 1588608
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1265280 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 59 | 1262400 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 768960 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 236363
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 447840 | Line problem
| Dhaka area Total |  |  |  | 5722 | 3886 | 80117513
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 16 | 234696 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 117180
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 39 | 766560 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 60 | 1459806 | Low Water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 224 | 5232023
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 96 | 1758036 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 66 | 882000 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 33 | 964124 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 46 | 713040 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 37 | 696960 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 11 | 253536 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 34 | 514080
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 18 | 140160 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 32879
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 276 | 2918073 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 528669 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 74 | 1734610 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 44 | 740160 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 100 | 1372473 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 163 | 1453600
| SS Power I |  | SS Power | 0 | 0 | 0 | 0 | On test.
| Cox's Bazar Wind |  | IPP | 66 | 0 | 2 | 215040 | On test.
| Chattogram area Total |  |  |  | 2545 | 1375 | 22727705
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 205 | 4605000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 275 | 7231300 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 240 | 6350000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 240 | 6093500 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 134136 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 955692 | Engine problem
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 125 | 531927 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 42 | 985680 | Machine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 51 | 764640 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 467532
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 239400
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 120 | 3465600
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 786700
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 42 | 963086 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 492830 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 103 | 1309860
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 97 | 638400 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 471240 | Fuel shortage
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 99 | 1682880 | Fuel shortage
| Cumilla Area Total |  |  |  | 3096 | 1788 | 38169403
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 53 | 1240320 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 414828 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14850
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 87 | 1718400 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 84 | 711600 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 354410
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 294720 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 255 | 4749128
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1020000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 684720 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2403081 | ST under maint
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 44 | 1029600
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 46 | 1054440
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 171552 | Machine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1404096
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1845120
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 201 | 4082110 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 387000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 553104
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7325000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 407 | 9233000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 244620
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 347 | 3849300
| Sylhet Area Total |  |  |  | 2427 | 1730 | 35286743
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 764 | 21067887
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 86 | 948480 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 21 | 285600 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 208 | 5192237
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 54 | 907904 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 160 | 2510496 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 40 | 421500
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 36 | 880320 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 1339632
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 712800
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 220 | 233 | 2503821
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | Under maint.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 3121 | 1707 | 36770677
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 622560 | Fuel shortage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 34 | 648144 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 132 | 3107000 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1222 | 31443100
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5287909
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 404400 | Fuel shortage
| Barisal 307 MW |  | IPP | 307*1 | 307 | 0 | 0 | Coal shortage.
| Barisal Area Total |  |  |  | 2265 | 1640 | 41513113
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 35 | 215024 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Fuel shortage
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 21 | 494720 | Engine problem
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 25 | 843208 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 29 | 215077 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 155 | 3933918 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 9555454
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 241060 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 0 | 133400 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 200150 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 508544 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 1136352 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 75 | 1172448 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 38580
| Adani Power Jharkhanda Ltd |  | Import | 748*2 | 1496 | 716 | 17198182
| Rajshahi Area Total |  |  |  | 3631 | 1673 | 35886117
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 235 | 4461900
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 84 | 1115990 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 56487
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 75 | 855360 | Fuel shortage
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 226130
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 1499830
| Rangpur Area Total |  |  |  | 750 | 394 | 8215697
| Total |  |  |  | 24171 | 14448 | 303436096
| Eastern Grid Total |  |  |  | 14404 | 9034 | 181050492
| Western Grid Total |  |  |  | 9767 | 5414 | 122385604
| National Grid Total |  |  |  | 24171 | 14448 | 303436096
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-07-19
| (a) ENTIRE EASTERN GRID : |  | 9301.54 | MW | (b) ENTIRE WESTERN GRID : |  | 4501.9 | MW
| i) Dhaka area |  | 5157.54 | MW | i) Khulna area |  | 1719.6 | MW
| ii) Chittagong area |  | 1440 | MW | ii) Rajshahi area |  | 1531.8 | MW
| iii) Comilla area |  | 1123 | MW | iii) Barisal area |  | 439.5 | MW
| iv) Mymensingh area |  | 1039 | MW | iv) Rangpur area |  | 811 | MW
| v) Sylhet area |  | 542 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 13803.44 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 27 | 21:00 | Kamrangirchar | 53.1 | 12:00 | Natore | 159 | 20:00 | Shitalakhya | 108.7 | 16:00
2 | AKSML | 105 | 10:00 | Chowmuhani | 166 | 22:00 | Kaptai | N/A | N/A | Nawabganj | 64 | 22:00 | Sholosohor | 38 | 19:00
3 | Aftabnagar | 40 | 23:00 | Chuadanga | 104 | 21:00 | Kazla | 99 | 18:30 | Netrakona | 102 | 21:00 | Shyampur | 168 | 12:00
4 | Agargaon | 99 | 11:00 | Coxsbazar | 128 | 19:00 | Keranigonj | 74 | 20:00 | New | 90.4 | 12:00 | Siddhirganj | 126 | 12:00
5 | Agrabad | 74 | 18:30 | Cumilla(N) | 155 | 22:00 | Khagrachori | 36 | 19:00 | Niamatpur | 99 | 22:00 | Sirajganj | 124 | 20:00
6 | Amnura | 70 | 07:00 | Cumilla(S) | 167 | 00:00 | Khulna | 106 | 20:00 | Noapara | 49 | 21:00 | Sonargaon | 97 | 22:00
7 | Ashuganj | 82 | 04:00 | Daudkandi | 110 | 21:00 | Khulshi | 188 | 18:30 | PHP | 8 | 00:00 | Sreemongol | 60 | 20:00
8 | BIPTC | N/A | N/A | Dhaka | 28 | 12:00 | Kishoreganj | 124 | 22:00 | Pabna | 121 | 22:00 | Sreepur | 59.4 | 23:00
9 | BSRM | 169 | 02:00 | Dhamrai | 126 | 21:00 | Kodda | 289 | 21:00 | Palashbari | 140 | 22:00 | Srinagar | 59.95 | 23:00
10 | Bagerhat | 90 | 20:00 | Dhanmondi | 150 | 13:00 | Kulaura | 44 | 19:00 | Panchagarh | 49 | 19:00 | Sunamganj | 48 | 22:00
11 | Bakulia | 106 | 20:00 | Dohazari | 114 | 19:30 | Kurigram | 60 | 19:30 | Patuakhali | 116 | 23:00 | Sylhet | 149 | 23:00
12 | Banani | 54 | 15:00 | Faridpur | 161 | 22:00 | Kushtia | 134 | 21:00 | Payra | 20 | 23:00 | TK | 27.6 | 01:00
13 | Bangabhaban | 21 | 10:00 | Fatullah | 64 | 16:00 | Lalbag | 92 | 19:30 | Postogola | 61 | 23:00 | Tangail | 219 | 20:00
14 | Barapukuria | 59 | 22:00 | Fenchuganj | 41 | 23:00 | Lalmonirhat | 44 | 00:00 | Purbachal | 21 | 00:00 | Thakurgaon | 81 | 20:00
15 | Barguna | 20 | 22:00 | Feni | 107 | 20:00 | Madanganj | 38 | 21:00 | Purbasadipur | 117 | 08:00 | Tongi | 107 | 14:00
16 | Barishal | 110 | 21:00 | GPH | 92 | 13:00 | Madaripur | 103 | 21:00 | Rahanpur_I | N/A | N/A | Ullon | 44 | 00:00
17 | Barishal-230 | 84 | 21:00 | Ghorashal | 59 | 00:00 | Madartek | 94.86 | 23:00 | Rahim | 43 | 09:00 | Uttara | 81 | 15:00
18 | Baroaulia | 74 | 00:00 | Goalpara | 38 | 12:00 | Madunaghat | 59 | 19:00 | Rajbari | 66 | 23:00 | UttaraNew | 57 | 23:00
19 | Baroirhat | 56 | 00:00 | Gollamari | 56 | 22:00 | Magura | 56 | 21:00 | Rajendrapur | 96 | 21:00 | Zigatola | 100 | 19:30
20 | Bashundhara | 164 | 15:00 | Gopalganj | 110 | 20:00 | Mahasthangarh | 70 | 22:00 | Rajshahi | 172 | 23:00
21 | BashundharaCement | 1 | 10:00 | Gulshan | 140 | 14:00 | Manikganj | 110 | 22:00 | Rajshahi-230 | 42 | 23:00
22 | Beanibazar | 62 | 23:00 | Halishahar | 87.5 | 15:00 | Maniknagar | 106 | 13:00 | Ramganj | 94 | 22:00
23 | Benapole | 62 | 00:00 | HaripurSBU | 151 | 21:00 | Matarbari | 51 | 21:00 | Rampur | 31 | 19:00
24 | Bhaluka | 122 | 19:30 | Hasnabad | 98 | 00:00 | Matuail | 68 | 12:00 | Rangamati | 14 | 10:00
25 | Bhandaria | 50 | 23:00 | Hathazari | 82 | 20:00 | Millgate | 110 | 16:00 | Rangpur | 130 | 19:30
26 | Bhangura | 38 | 20:00 | Ishurdi | 84 | 21:00 | Mirpur | 145 | 19:30 | Ruppur | 6.2 | 11:00
27 | Bheramara(GK) | 61 | 22:00 | Jaldhaka | 64 | 00:00 | Mirsorai | 6 | 19:30 | SSM | 0 | 00:00
28 | Bhulta | 249 | 20:00 | Jamalpur | 150 | 19:30 | Mithapukur | 38 | 19:00 | Saidpur | 96 | 19:00
29 | Bog-Sherpur | 64 | 21:00 | Jashore | 148 | 22:00 | Modern | 0 | 00:00 | Satkhira | 135 | 20:00
30 | Bogura | 156 | 23:00 | Jhenaidah | 130 | 22:00 | Mogbazar | 150.8 | 15:00 | Satmasjid | 103 | 19:30
31 | Borhanuddin | 64 | 21:00 | Joydebpur | 147 | 22:00 | Mongla | 30 | 09:00 | Savar | 192 | 21:00
32 | Brahmanbaria | 145 | 21:00 | Joypurhat | 63 | 21:00 | Motijheel | 43 | 16:00 | Shahjadpur | 103 | 20:00
33 | Cantonment | 150 | 15:00 | Juldah | 21 | 23:00 | Munshiganj | 113 | 23:00 | Shahjibazar | 134 | 22:00
34 | Chandpur | 64 | 20:00 | KSRM | 34 | 08:00 | Mymensingh | 233 | 22:00 | Shahmirpur | 48 | 00:00
35 | Chandraghona | 34 | 19:00 | Kabirpur | 300 | 18:30 | Naogaon | 144 | 21:00 | Shariatpur | 72 | 22:00
36 | Chapai | 72 | 22:00 | Kachua | 58 | 21:00 | Narail | 53 | 22:00 | Sherpur | 140 | 19:30
37 | Charsaidpur | 49.5 | 15:00 | Kallyanpur | 111 | 00:00 | Narinda | 82 | 13:00 | Shikalbaha | 36 | 19:30
38 | Chauddagram | 71 | 21:00 | Kalurghat | 40 | 15:00 | Narshingdi | 160 | 04:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-07-19 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 400 | 07:00 | 390 | 16:00 | Gopalganj | 407 | 18:30 | 398 | 16:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 393 | 05:00 | 293 | 00:00
| Bhulta | 399 | 07:00 | 392 | 14:00 | Madunaghat_I | 420 | 20:00 | 388 | 07:00
| Bibiana | 410 | 05:00 | 404 | 12:00 | Payra | 412 | 18:30 | 407 | 14:00
| BIPTC | 398 | 19:30 | 386 | 15:00 | Rahanpur_I | N/A | N/A | N/A | N/A
| Bogura | N/A | N/A | N/A | N/A | Rampal | 408 | 05:00 | 400 | 15:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 234 | 07:00 | 227 | 16:00 | Hasnabad | 233 | 20:00 | 228 | 15:00
| AKSML | 236 | 21:00 | 222 | 04:00 | Hathazari | 239 | 21:00 | 223 | 09:00
| Aminbazar | 235 | 07:00 | 229 | 13:00 | Ishurdi | 234 | 00:00 | 226 | 03:00
| Ashuganj | 236 | 20:00 | 232 | 01:00 | Jhenaidah | 227 | 00:00 | 221 | 12:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 232 | 01:00 | 229 | 10:00
| Baghabari | 228 | 00:00 | 223 | 07:00 | Keranigonj | 232 | 05:00 | 226 | 16:00
| Barapukuria | 221 | 15:00 | 208 | 03:00 | Khulna(S) | 235 | 00:00 | 230 | 12:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | 240 | 20:00 | 222 | 09:00
| Barishal | 235 | 18:30 | 231 | 19:30 | Maniknagar | 233 | 02:00 | 228 | 14:00
| Bheramara | 231 | 00:00 | 223 | 03:00 | Meghnaghat | 239 | 00:00 | 235 | 11:00
| Bhulta | 236 | 05:00 | 230 | 16:00 | Mirsorai | 239 | 20:00 | 222 | 02:00
| Bibiana | 237 | 18:00 | 232 | 07:00 | Rajshahi | 230 | 00:00 | 220 | 14:00
| BIPTC | 234 | 00:00 | 224 | 02:00 | Rampal | 234 | 04:00 | 228 | 16:00
| Bogura | 224 | 15:00 | 217 | 07:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 240 | 00:00 | 236 | 05:00 | Rampura | 234 | 05:00 | 228 | 16:00
| BSRM | 240 | 21:00 | 224 | 02:00 | Shikalbaha | 236 | 19:30 | 223 | 09:00
| Cumilla(N) | 235 | 20:00 | 228 | 00:00 | Shyampur | 232 | 00:00 | 227 | 16:00
| Fenchuganj | 240 | 17:00 | 236 | 03:00 | Siddhirganj | 234 | 00:00 | 231 | 14:00
| Ghorashal | 238 | 00:00 | 235 | 01:00 | Sirajgonj | 234 | 00:00 | 229 | 07:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 230 | 18:00 | 225 | 02:00
| GPH | 237 | 21:00 | 222 | 04:00 | Tongi | 228 | 00:00 | 224 | 17:00
| Haripur | 234 | 20:00 | 229 | 14:00
| 132 kV | KV |  | KV |  | Tongi | KV |  | KV
| Aftabnagar | 137 | 07:00 | 130 | 14:00 | Lalbag | 132 | 04:00 | 128 | 10:00
| Agargaon | 134 | 05:00 | 129 | 12:00 | Lalmonirhat | 132 | 15:00 | 117 | 04:00
| Agrabad | 138 | 21:00 | 129 | 00:00 | Madanganj | 135 | 05:00 | 132 | 10:00
| AKS | 134 | 19:30 | 128 | 07:00 | Madaripur | 131 | 05:00 | 129 | 03:00
| Aminbazar | 135 | 19:30 | 130 | 13:00 | Madartek | 136 | 05:00 | 130 | 12:00
| Amnura | 139 | 20:00 | 123 | 04:00 | Madunaghat | 137 | 20:00 | 128 | 00:00
| Ashuganj | 139 | 18:30 | 136 | 00:00 | Magura | 136 | 00:00 | 131 | 06:00
| Bagerhat | 137 | 05:00 | 132 | 22:00 | Mahasthangarh | 131 | 16:00 | 123 | 04:00
| Bakulia | 138 | 20:00 | 130 | 00:00 | Manikganj | 133 | 13:00 | 126 | 05:00
| Banani | 136 | 05:00 | 129 | 16:00 | Maniknagar | 132 | 02:00 | 125 | 13:00
| Bangabhaban | 132 | 06:00 | 125 | 12:00 | Matarbari | 127 | 09:00 | 113 | 00:00
| Barapukuria | 139 | 12:00 | 126 | 05:00 | Matuail | 135.2 | 19:30 | 132 | 12:00
| Barguna | 136 | 00:00 | 131 | 19:00 | Millgate | 135 | 05:00 | 129 | 15:00
| Barishal | 135 | 00:00 | 129 | 19:30 | Mirpur | 134 | 01:00 | 128 | 16:00
| Barishal-230 | 136 | 18:30 | 133 | 00:00 | Mithapukur | 130 | 10:00 | 120 | 02:00
| Baroaulia | 138 | 22:00 | 130 | 00:00 | Modern | 137 | 20:00 | 129 | 09:00
| Baroirhat | 138 | 20:00 | 123 | 02:00 | Mogbazar | 137 | 02:00 | 130 | 16:00
| Bashundhara | 137 | 07:00 | 128 | 16:00 | Mongla | 136 | 07:00 | 132 | 19:30
| BashundharaCement | 135 | 04:00 | 132 | 10:00 | Motijheel | 132 | 06:00 | 125 | 12:00
| Beanibazar | 131 | 10:00 | 128 | 19:00 | Munshiganj | 136 | 20:00 | 132 | 08:00
| Benapole | 135 | 09:00 | 130 | 21:00 | Mymensingh | 130 | 18:30 | 117 | 21:00
| Bhaluka | 130 | 18:00 | 122 | 03:00 | Naogaon | 127 | 17:00 | 115 | 22:00
| Bhandaria | 133 | 09:00 | 123 | 23:00 | Narail | 133 | 00:00 | 130 | 12:00
| Bhangura | 134 | 00:00 | 131 | 02:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 133 | 00:00 | 130 | 04:00 | Narshingdi | 131 | 19:00 | 124 | 03:00
| Bheramara(GK) | 134 | 00:00 | 131 | 22:00 | Natore | 132 | 10:00 | 128 | 04:00
| Bhulta | 126 | 19:30 | 120 | 12:00 | Nawabganj | 133 | 07:00 | 129 | 10:00
| Bog-Sherpur | 132 | 15:00 | 127 | 00:00 | Netrakona | 133 | 18:30 | 116 | 21:00
| Bogura | 133 | 15:00 | 126 | 06:00 | New | 136 | 05:00 | 130 | 15:00
| Bogura-230 | 133 | 15:00 | 127 | 07:00 | Niamatpur | 125 | 17:00 | 107 | 22:00
| Brahmanbaria | 134 | 09:00 | 131 | 04:00 | Noapara | 138 | 00:00 | 135 | 06:00
| Cantonment | 158 | 03:00 | 128 | 15:00 | Pabna | 133 | 00:00 | 128 | 04:00
| Chandpur | 138 | 19:30 | 120 | 00:00 | Palashbari | 130 | 15:00 | 118 | 06:00
| Chandraghona | 138 | 21:00 | 131 | 08:00 | Panchagarh | 137 | 15:00 | 111 | 04:00
| Chapai | 130 | 18:00 | 125 | 06:00 | Patuakhali | 138 | 00:00 | 133 | 15:00
| Charsaidpur | 136 | 19:30 | 132 | 10:00 | Payra | 139 | 00:00 | 137 | 01:00
| Chauddagram | 136 | 21:00 | 122 | 00:00 | PHP | 136 | 20:00 | 121 | 00:00
| Chhatak | 132 | 09:00 | 128 | 01:00 | Postogola | 133 | 00:00 | 133 | 00:00
| Chowmuhani | 135 | 19:30 | 120 | 01:00 | Purbachal | 136 | 05:00 | 129 | 16:00
| Chuadanga | 138 | 23:00 | 125 | 21:00 | Purbasadipur | 135 | 15:00 | 111 | 02:00
| Coxsbazar | 125 | 01:00 | 114 | 00:00 | Rahim | 135 | 19:00 | 132 | 12:00
| Cumilla(N) | 138 | 20:00 | 129 | 00:00 | Rajbari | 129 | 09:00 | 125 | 22:00
| Cumilla(S) | 138 | 19:30 | 124 | 12:00 | Rajendrapur | 137 | 18:30 | 127 | 03:00
| Daudkandi | 134 | 20:00 | 129 | 00:00 | Rajshahi | 134 | 00:00 | 129 | 14:00
| Dhaka | 137 | 07:00 | 130 | 16:00 | Rajshahi-230 | 136 | 00:00 | 125 | 07:00
| Dhamrai | 131 | 00:00 | 126 | 21:00 | Ramganj | 135 | 20:00 | 117 | 00:00
| Dhanmondi | 135 | 05:00 | 130 | 12:00 | Rampur | 136 | 20:00 | 126 | 00:00
| Dohazari | 132 | 15:00 | 124 | 00:00 | Rampura | 136 | 05:00 | 130 | 13:00
| Faridpur | 130 | 09:00 | 126 | 11:00 | Rangamati | 136 | 20:00 | 130 | 00:00
| Fatullah | 131 | 20:00 | 127 | 10:00 | Rangpur | 134 | 15:00 | 120 | 00:00
| Fenchuganj | 137 | 20:00 | 134 | 00:00 | Ruppur | 134 | 00:00 | 131 | 13:00
| Feni | 138 | 20:00 | 120 | 00:00 | Saidpur | 134 | 15:00 | 118 | 00:00
| Ghorashal | 139 | 00:00 | 136 | 16:00 | Satkhira | 135 | 01:00 | 130 | 21:00
| Goalpara | 140 | 01:00 | 136 | 06:00 | Satmasjid | 134 | 07:00 | 128 | 15:00
| Gollamari | 138 | 00:00 | 135 | 12:00 | Savar | 135 | 18:30 | 128 | 15:00
| Gopalganj | 136 | 18:30 | 131 | 12:00 | Shahjadpur | 140 | 05:00 | 135 | 07:00
| Gopalganj-400 | 131 | 18:30 | 127 | 16:00 | Shahjibazar | 134 | 18:00 | 130 | 00:00
| Gulshan | 135 | 00:00 | 129 | 16:00 | Shahmirpur | 138 | 20:00 | 129 | 00:00
| Halishahar | 138 | 20:00 | 128 | 00:00 | Shariatpur | 132 | 18:30 | 127 | 12:00
| Haripur | 135 | 19:00 | 132 | 12:00 | Sherpur | 131 | 18:30 | 112 | 23:00
| HaripurSBU | 135 | 19:00 | 132 | 12:00 | Shikalbaha | 126 | 20:00 | 119 | 09:00
| Hasnabad | 137 | 21:00 | 134 | 03:00 | Shikalbaha-230 | 137 | 19:30 | 131 | 09:00
| Hathazari | 139 | 21:00 | 132 | 00:00 | Shitalakhya | 136.2 | 20:00 | 131.6 | 13:00
| Ishurdi | 135 | 00:00 | 130 | 06:00 | Sholosohor | 136 | 20:00 | 129 | 04:00
| Jaldhaka | 134 | 15:00 | 116 | 03:00 | Shyampur | 131 | 20:00 | 126 | 16:00
| Jamalpur | 134 | 18:30 | 114 | 21:00 | Shyampur-230 | 130 | 00:00 | 127 | 10:00
| Jashore | 136 | 09:00 | 132 | 14:00 | Siddhirganj | 136 | 19:30 | 133 | 10:00
| Jhenaidah | 137 | 00:00 | 133 | 05:00 | Sirajganj | 132 | 18:00 | 127 | 07:00
| Jhenaidah-230 | 138 | 00:00 | 134 | 12:00 | Sonargaon | 135 | 22:00 | 129 | 15:00
| Joydebpur | 140 | 18:00 | 133 | 10:00 | Sreemongol | 133 | 06:00 | 131 | 02:00
| Joypurhat | 125 | 18:00 | 112 | 22:00 | Sreepur | 130 | 18:00 | 125 | 02:00
| Juldah | 138 | 19:30 | 129 | 07:00 | Srinagar | 133 | 07:00 | 129 | 15:00
| Kabirpur | 136 | 18:30 | 127 | 15:00 | SSM | 140 | 20:00 | 132 | 00:00
| Kachua | 138 | 21:00 | 122 | 00:00 | Sunamganj | 130 | 06:00 | 125 | 21:00
| Kaliakoir | 136 | 13:00 | 130 | 10:00 | Sylhet | 133 | 09:00 | 130 | 00:00
| Kallyanpur | 129 | 03:00 | 125 | 11:00 | Tangail | 131 | 18:30 | 122 | 21:00
| Kalurghat | 137 | 20:00 | 130 | 00:00 | Thakurgaon | 132 | 13:00 | 108 | 04:00
| Kamrangirchar | 132 | 04:00 | 124 | 16:00 | TK | 138 | 01:00 | 130 | 09:00
| Kaptai | N/A | N/A | N/A | N/A | Tongi | 136 | 07:00 | 133 | 13:00
| Kazla | 131 | 04:00 | 125 | 13:00 | Ullon | 137 | 07:00 | 129 | 16:00
| Keranigonj | 133 | 05:00 | 128 | 16:00 | Uttara | 134 | 04:00 | 127 | 15:00
| Khagrachori | 136 | 21:00 | 128 | 00:00 | UttaraNew | 133 | 01:00 | 128 | 15:00
| Khulna | 139 | 00:00 | 136 | 06:00 | Zigatola | 133 | 06:00 | 128 | 16:00
| Khulna(S) | 139 | 05:00 | 135 | 12:00
| Khulshi | 136 | 20:00 | 128 | 00:00
| Kishoreganj | 132 | 18:00 | 127 | 02:00
| Kodda | 138 | 19:30 | 127 | 04:00
| KSRM | 138 | 19:30 | 129 | 08:00
| Kulaura | 135 | 09:00 | 133 | 00:00
| Kurigram | 134 | 15:00 | 117 | 02:00
| Kushtia | 134 | 09:00 | 131 | 05:00

## L-Curve
Date | 2023-07-19
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 680 | 8140 | 5303 | 13443 |  |  |  | QF-LDC-11
0:30 | 710 | 7778.5 | 5184 | 12962.5 | Date: | 2023-07-19
1:00 | 740 | 7417 | 5065 | 12482
1:30 | 748 | 7404 | 5065 | 12469
2:00 | 756 | 7391 | 5065 | 12456
2:30 | 713 | 7322.5 | 5053.5 | 12376 | [5 empty] | Gen. at Eve. Peak | 14448 | 14448 MW (21:00 )
3:00 | 670 | 7254 | 5042 | 12296 | [6 empty] | 21:00
3:30 | 665 | 7230.5 | 5035 | 12265.5 | [5 empty] | Gen. at Day Peak | 12586 | 12586 MW (12:00 )
4:00 | 660 | 7207 | 5028 | 12235 | [6 empty] | 12:00
4:30 | 675 | 7160 | 5021 | 12181 | [5 empty] | Highest Generation | 14448
5:00 | 690 | 7113 | 5014 | 12127 | [6 empty] | 21:00
5:30 | 705 | 7058 | 4935 | 11993
6:00 | 720 | 7003 | 4856 | 11859
6:30 | 690 | 6999.5 | 4848 | 11847.5
7:00 | 660 | 6996 | 4840 | 11836
7:30 | 715 | 6881 | 4863 | 11744
8:00 | 770 | 6766 | 4886 | 11652
8:30 | 855 | 6809 | 4900.5 | 11709.5
9:00 | 940 | 6852 | 4915 | 11767
9:30 | 985 | 6901 | 4960 | 11861
10:00 | 1030 | 6950 | 5005 | 11955
10:30 | 1060 | 7026.5 | 4989.5 | 12016
11:00 | 1090 | 7103 | 4974 | 12077
11:30 | 1080 | 7305.5 | 5026 | 12331.5
12:00 | 1070 | 7508 | 5078 | 12586
12:30 | 965 | 7546.5 | 5057.5 | 12604
13:00 | 860 | 7585 | 5037 | 12622
13:30 | 920 | 7594.5 | 4990.5 | 12585
14:00 | 980 | 7604 | 4944 | 12548
14:30 | 945 | 7566 | 4905.5 | 12471.5
15:00 | 910 | 7528 | 4867 | 12395
15:30 | 855 | 7414 | 4893 | 12307
16:00 | 800 | 7300 | 4919 | 12219
16:30 | 805 | 7250.5 | 4917.5 | 12168
17:00 | 810 | 7201 | 4916 | 12117
17:30 | 760 | 7226.5 | 4931 | 12157.5
18:00 | 710 | 7252 | 4946 | 12198
18:30 | 685 | 7684.5 | 5046 | 12730.5
19:00 | 660 | 8117 | 5146 | 13263
19:30 | 400 | 8609 | 5521 | 14130
20:00 | 400 | 8725 | 5418 | 14143 |  |  |  | Executive Engineer
20:30 | 355 | 8879.5 | 5416 | 14295.5 |  |  |  | Network Operation Division
21:00 | 310 | 9034 | 5414 | 14448
21:30 | 325 | 8979 | 5405.5 | 14384.5
22:00 | 340 | 8924 | 5397 | 14321 |  |  |  |  | Page 6 of 7
22:30 | 455 | 8756.5 | 5388.5 | 14145
23:00 | 570 | 8589 | 5380 | 13969
23:30 | 625 | 8364.5 | 5341.5 | 13706
24:00 | 680 | 8140 | 5303 | 13443
14448 MW (21:00 )
12586 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-07-19 |  | Energy |  | 303436096
[14 empty] | Date: | 2023-07-19 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 4323 | 781 | 2444 | 300 | 2205 | 2196 | 60 | 436 | 575 | 120 | 0 | 3 | 1677.935
0:30 | 4291.5 | 844.5 | 2426 | 259 | 1884 | 2164 | 60 | 447 | 441.5 | 142 | 0 | 3 | 1802.5625 |  |  | Date: | 43664
1:00 | 4260 | 908 | 2408 | 218 | 1563 | 2132 | 60 | 458 | 308 | 164 | 0 | 3 | 1927.19
1:30 | 4264 | 908.5 | 2429 | 187 | 1560 | 2133.5 | 60 | 458 | 299 | 164 | 0 | 6 | 1867.98 | [9 empty] | Total Energy | 303.4361 | 303.4361 | Total Energy Gen 303.436 MKWHr Energy Not Served 35.896 MKWHr Energy Requirement 339.332 MKWHr
2:00 | 4268 | 909 | 2450 | 156 | 1557 | 2135 | 60 | 458 | 290 | 164 | 0 | 9 | 1808.77 | [9 empty] | Energy not Served | 35.8955 | 35.8955
2:30 | 4229 | 909 | 2451 | 156.5 | 1545.5 | 2135.5 | 60 | 456.5 | 271.5 | 154 | 0 | 7.5 | 1765.795 | [9 empty] | Energy Requirement | 339.3316 | 339.3316
3:00 | 4190 | 909 | 2452 | 157 | 1534 | 2136 | 60 | 455 | 253 | 144 | 0 | 6 | 1722.82
3:30 | 4125.5 | 909 | 2448 | 203.5 | 1523 | 2134.5 | 60 | 455 | 253.5 | 148 | 0 | 5.5 | 1680.3225 | [8 empty] | Shortage
4:00 | 4061 | 909 | 2444 | 250 | 1512 | 2133 | 60 | 455 | 254 | 152 | 0 | 5 | 1637.825
4:30 | 4047.5 | 907.5 | 2443.5 | 209 | 1511.5 | 2130.5 | 60 | 457 | 253.5 | 155 | 0 | 6 | 1570.02
5:00 | 4034 | 906 | 2443 | 168 | 1511 | 2128 | 60 | 459 | 253 | 158 | 0 | 7 | 1502.215
5:30 | 4079 | 905.5 | 2443 | 84 | 1504 | 2140 | 60 | 353 | 253.5 | 149 | 12 | 10 | 1415.31
6:00 | 4124 | 905 | 2443 | 0 | 1497 | 2152 | 60 | 247 | 254 | 140 | 24 | 13 | 1328.405
6:30 | 4122.5 | 905 | 2424 | 0 | 1498 | 2145.5 | 60 | 235.5 | 248.5 | 140 | 59 | 9.5 | 1267.7625 | [7 empty] | Coal
7:00 | 4121 | 905 | 2405 | 0 | 1499 | 2139 | 60 | 224 | 243 | 140 | 94 | 6 | 1207.12
7:30 | 4015.5 | 905.5 | 2368 | 0 | 1498 | 2135 | 60 | 223.5 | 231 | 139 | 161 | 7.5 | 1318.855 | [6 empty] | Oil
8:00 | 3910 | 906 | 2331 | 0 | 1497 | 2131 | 60 | 223 | 219 | 138 | 228 | 9 | 1430.59
8:30 | 3951.5 | 906 | 2321 | 0 | 1490.5 | 2125 | 60 | 222 | 214.5 | 140 | 270.5 | 8.5 | 1518.9275
9:00 | 3993 | 906 | 2311 | 0 | 1484 | 2119 | 60 | 221 | 210 | 142 | 313 | 8 | 1607.265
9:30 | 3978.5 | 905.5 | 2330.5 | 0 | 1520.5 | 2120.5 | 60 | 221.5 | 221 | 145 | 349.5 | 8.5 | 1565.245
10:00 | 3964 | 905 | 2350 | 0 | 1557 | 2122 | 60 | 222 | 232 | 148 | 386 | 9 | 1523.225
10:30 | 3967 | 905.5 | 2303 | 0 | 1643 | 2116.5 | 60 | 221 | 250.5 | 144 | 394 | 11.5 | 1536.595
11:00 | 3970 | 906 | 2256 | 0 | 1729 | 2111 | 60 | 220 | 269 | 140 | 402 | 14 | 1549.965
11:30 | 3955 | 905 | 2288 | 130 | 1817 | 2109.5 | 60 | 219 | 273 | 150 | 415 | 10 | 1545.6675
12:00 | 3940 | 904 | 2320 | 260 | 1905 | 2108 | 60 | 218 | 277 | 160 | 428 | 6 | 1541.37
12:30 | 3942.5 | 905 | 2314.5 | 271 | 1902 | 2106 | 60 | 218 | 279 | 160 | 437 | 9 | 1535.64
13:00 | 3945 | 906 | 2309 | 282 | 1899 | 2104 | 60 | 218 | 281 | 160 | 446 | 12 | 1529.91
13:30 | 3945 | 906 | 2309 | 282 | 1899 | 2104 | 60 | 218 | 281 | 160 | 446 | 12 | 1529.91
14:00 | 3945 | 906 | 2309 | 282 | 1899 | 2104 | 60 | 218 | 281 | 160 | 446 | 12 | 1529.91
14:30 | 3946.5 | 906.5 | 2300 | 291.5 | 1880.5 | 2115.5 | 60 | 211 | 273 | 152 | 355.5 | 16.5 | 1626.8425
15:00 | 3948 | 907 | 2291 | 301 | 1862 | 2127 | 60 | 204 | 265 | 144 | 265 | 21 | 1723.775
15:30 | 3947.5 | 906.5 | 2323.5 | 230.5 | 1824.5 | 2129.5 | 60 | 203 | 274 | 142 | 249.5 | 16.5 | 1760.065
16:00 | 3947 | 906 | 2356 | 160 | 1787 | 2132 | 60 | 202 | 283 | 140 | 234 | 12 | 1796.355
16:30 | 3937.5 | 906.5 | 2366.5 | 95 | 1799 | 2132.5 | 60 | 227 | 313.5 | 144 | 174.5 | 12 | 1708.9725
17:00 | 3928 | 907 | 2377 | 30 | 1811 | 2133 | 60 | 252 | 344 | 148 | 115 | 12 | 1621.59
17:30 | 3922 | 907 | 2314.5 | 15 | 1949.5 | 2122 | 60 | 253.5 | 379 | 147 | 78 | 10 | 1623.295
18:00 | 3916 | 907 | 2252 | 0 | 2088 | 2111 | 60 | 255 | 414 | 146 | 41 | 8 | 1625
18:30 | 4029.5 | 906.5 | 2234.5 | 0 | 2383 | 2144 | 60 | 263 | 537 | 142 | 20.5 | 10.5 | 1450.9175
19:00 | 4143 | 906 | 2217 | 0 | 2678 | 2177 | 60 | 271 | 660 | 138 | 0 | 13 | 1276.835
19:30 | 4303 | 907 | 2382 | 30 | 2994 | 2167 | 60 | 439 | 708 | 130 | 0 | 10 | 1310.26
20:00 | 4348 | 766 | 2375 | 10 | 3139 | 2172 | 60 | 439 | 700 | 122 | 0 | 12 | 1343.685
20:30 | 4332.5 | 765 | 2385 | 153 | 3160.5 | 2172.5 | 60 | 440 | 699 | 121 | 0 | 7 | 1221.9225
21:00 | 4317 | 764 | 2395 | 296 | 3182 | 2173 | 60 | 441 | 698 | 120 | 0 | 2 | 1100.16
21:30 | 4306 | 764 | 2382 | 223 | 3203 | 2180 | 60 | 440.5 | 704 | 115 | 0 | 7 | 1113.0525
22:00 | 4295 | 764 | 2369 | 150 | 3224 | 2187 | 60 | 440 | 710 | 110 | 0 | 12 | 1125.945
22:30 | 4290.5 | 764 | 2393.5 | 225.5 | 2936.5 | 2194 | 60 | 441 | 708.5 | 123 | 0 | 8.5 | 1270.15
23:00 | 4286 | 764 | 2418 | 301 | 2649 | 2201 | 60 | 442 | 707 | 136 | 0 | 5 | 1414.355
23:30 | 4304.5 | 772.5 | 2431 | 300.5 | 2427 | 2198.5 | 60 | 439 | 641 | 128 | 0 | 4 | 1546.145 |  |  | Max Temp. in Dhaka |  | 35.4° C
24:00 | 4323 | 781 | 2444 | 300 | 2205 | 2196 | 60 | 436 | 575 | 120 | 0 | 3 | 1677.935
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 303.436 MKWHr Energy Not Served 35.896 MKWHr Energy Requirement 339.332 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-07-19
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 727806
2 | Karnaphuli Hydro PP Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 732000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 12 |  | 16 | 16 | 16 | 16 | 16 | 10 | 8 | 234696
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 6 | 11 | 5 | 20 | 17 | 12 | 13 | 5 | 17 | 7 | 5 | 1 | [8 empty] | 117180
6 | Sikalbaha 225MW CCPP (Gas) | 226 | 227 | 225 | 224 | 228 | 226 | 228 | 223 | 222 | 222 | 222 | 220 | 217 | 216 | 213 | 221 | 220 | 222 |  | 216 | 222 | 202 | 224 | 209 | 226 | 222 | 5232023
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 49 | 40 | 32 | 32 | 32 | 31 | 31 | 31 | 31 | 31 | 31 |  | 33 | 33 | 33 | 33 | 50 | 50 | 50 | 964124
12 | Hathazari 100 MW peaking PP | 32 | 32 | 32 | 32 | 32 | 32 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 17 | 41 | 56 | 56 |  | 56 | 63 | 63 | 66 | 65 | 66 | 66 | 882000
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 74 | 80 | 90 | 96 | 96 | 96 | 96 |  | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 1758036
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 43 | 43 | 43 | 43 | 42 | 43 | 40 | 44 | 44 | 43 | 43 | 36 | 36 | 36 | 35 | 35 | 40 | 40 |  | 40 | 40 | 40 | 42 | 43 | 44 | 44 | 985680
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 195 | 193 | 189 | 187 | 194 | 191 | 197 | 193 | 197 | 195 | 195 | 191 | 193 | 187 | 187 | 186 | 191 | 154 |  | 169 | 196 | 186 | 195 | 195 | 195 | 187 | 4674000
17 | Siddhirganj 335 MW CCPP | 332 | 329 | 327 | 324 | 331 | 327 | 332 | 300 | 328 | 327 | 331 | 324 | 321 | 318 | 316 | 316 | 316 | 280 |  | 323 | 325 | 323 | 323 | 327 | 330 | 322 | 7753931
18 | Kodda 300 MW PP Unit-2 (Summit) | 102 | 115 | 112 | 115 | 112 | 112 | 112 | 112 | 112 | 112 | 115 | 145 | 148 | 148 | 120 | 97 | 97 | 97 |  | 97 | 97 | 97 | 97 | 100 | 100 | 100 | 2692255
19 | Ashuganj 195 MW PP (APSCL-United) | [25 empty] | 0 | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 156 | 160 | 160 | 160 | 160 | 160 |  | 160 | 160 | 160 | 160 | 160 | 160 | 180 | 3838000
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 134136
33 | Ashuganj 225 MW CCPP | 195 | 200 | 206 | 206 | 208 | 206 | 182 | 182 | 193 | 196 | 190 | 179 | 172 | 173 | 173 | 165 | 168 | 186 |  | 204 | 201 | 204 | 205 | 204 | 185 | 161 | 4605000
34 | Ashuganj 450 MW CCPP(South) | 240 | 240 | 240 | 240 | 230 | 250 | 320 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 6350000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 350 | 320 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 265 | 270 | 265 |  | 305 | 270 | 270 | 275 | 275 | 275 | 330 | 7231300
| Ashuganj 420 MW CCPP(East) | 290 | 290 | 290 | 290 | 230 | 230 | 250 | 250 | 250 | 250 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 6093500
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 401 | 403 | 402 | 402 | 402 | 403 | 404 | 403 | 402 | 403 | 404 | 401 | 397 | 398 | 393 | 395 | 393 | 383 |  | 352 | 403 | 398 | 403 | 400 | 394 | 402 | 9664510
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 10223500
41 | Haripur 360 MW CCPP(HPL) | 327 | 342 | 342 | 340 | 343 | 342 | 337 | 341 | 327 | 327 | 327 | 327 | 322 | 322 | 312 | 312 | 312 | 315 |  | 307 | 332 | 338 | 343 | 344 | 342 | 339 | 7800000
42 | RPCL 210MW CCPP | 84 | 84 | 84 | 85 | 84 | 86 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 32 | 31 | 31 | 42 |  | 82 | 82 | 83 | 53 | 53 | 71 | 71 | 1240320
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 13 | 29 | 40 | 36 | 23 | 48 | 43 | 50 | 19 | 21 | 9 | 5 |  | 0 | [6 empty] | 354410
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1020000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 20 | 20 |  | 20 | 27 | 40 | 40 | 40 | 40 | 40 | 684720
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 58 | 58 | 58 | 58 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 59 | 59 | 59 | 59 | 59 | 60 |  | 40 | 61 | 61 | 60 | 58 | 58 | 58 | 1404096
48 | Shahjibazar 86 MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 78 | 78 | 78 | 78 | 78 | 77 | 80 | 80 | 79 | 80 | 80 | 80 |  | 80 | 80 | 81 | 81 | 81 | 81 | 81 | 1845120
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 203 | 203 | 204 | 204 | 203 | 203 | 203 | 204 | 204 | 204 | 202 | 204 | 199 | 199 | 196 | 197 | 199 | 202 |  | 204 | 201 | 202 | 201 | 203 | 203 | 203 | 4082110
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 387000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 244620
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 171552
55 | Fenchugonj 51 MW PP (Barakatullah) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 |  | 42 | 42 | 44 | 44 | 44 | 45 | 45 | 1029600
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 24 | 16 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 553104
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 310 | 320 | 320 | 310 | 310 | 300 | 295 | 300 | 290 | 290 | 290 | 305 | 300 | 320 | 310 | 305 | 270 |  | 255 | 270 | 280 | 290 | 280 | 300 | 310 | 7325000
| Bibiyana South 400 MW | 260 | 260 | 145 | 15 | 35 | 30 | 50 | 50 | 50 | 50 | 50 | 50 | 79 | 100 | 113 | 124 | 138 | 229 |  | 300 | 360 | 385 | 347 | 340 | 340 | 348 | 3849300
58 | Nababganj 55 MW PP (Southern power ) | [10 empty] | 5 | 35 | 35 | 35 | 35 | 35 | 35 | 55 |  | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 537753
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 9 | 12 | 294720
60 | Barabkunda 22 MW PP (Regent) | 11 | 11 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 253536
61 | Narshingdi 22 MW PP (Doreen) | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 418212
62 | Tangail 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 414828
63 | Impoprt (Tripura) | 164 | 164 | 144 | 152 | 158 | 140 | 140 | 138 | 142 | 148 | 140 | 160 | 160 | 154 | 144 | 140 | 148 | 146 |  | 138 | 130 | 122 | 120 | 110 | 136 | 120 | 3465600
64 | Malancha, Ctg. EPZ (United) | 35 | 36 | 32 | 32 | 39 | 39 | 34 | 4 | 2 | 2 | 2 | 2 | 8 | 3 | 3 | 3 | 14 | 15 |  | 26 | 26 | 30 | 34 | 35 | 39 | 37 | 514080
65 | Feni 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 19 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 467532
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 239400
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 30 | 30 | 30 | 30 | 30 | 32 |  | 32 | 32 | 33 | 33 | 33 | 33 | 33 | 786700
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 492830
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456000
70 | Summit Madhabdi | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 7 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 462780
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 589300
72 | Rupganj 33 MW PP(Summit) | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 16 | 16 | 23 | 23 | 23 | 23 | 23 | 14 | 22 | 15 | 22 |  | 22 | 22 | 22 | 22 | 22 | 23 | 23 | 515000
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 50 | 50 |  | 50 | 54 | 103 | 103 | 103 | 103 | 103 | 1309860
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 15 | 27 | 36 |  | 66 | 95 | 94 | 97 | 97 | 57 | 9 | 638400
| Manikgonj 162MW PP(MPGL) | [9 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 |  | 54 | 108 | 108 | 108 | 108 | 108 | 103 | 768960
77 | Siddhirganj 100 PP(Dutch Bangla) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 40 | 50 | 50 | 50 | 50 | 58 | 56 | 55 | 56 | 56 |  | 65 | 72 | 72 | 72 | 72 | 38 | 33 | 1111680
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 |  | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 302400
79 | Kodda 150 MW PP | 82 | 64 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 82 | 82 | 96 | 96 | 96 | 96 | 96 | 96 | 96 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 2066400
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 34 | 34 | 43 | 43 | 43 | 33 | 32 | 32 | 34 | 41 |  | 41 | 42 | 42 | 42 | 43 | 43 | 43 | 963086
| Gazipur 100 MW PP | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 88 | 88 | 88 | 88 | 88 | 88 | 34 | 1265280
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 4 | 3 | 5 | 5 | 5 | 2 | 4 | 1 | 2 | [9 empty] | 32879
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 18 | 25 | 36 | 36 | 36 | 36 | 528669
| Karnaphuli Power Ltd. | 74 | 74 | 74 | 74 | 74 | 64 | 74 | 74 | 74 | 74 | 54 | 54 | 54 | 74 | 74 | 74 | 74 | 74 |  | 74 | 74 | 74 | 74 | 74 | 74 | 71 | 1734610
82 | Madanganj 102 PP(Summit) | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 95 | 95 | 92 | 92 | 90 | 90 | 92 | 93 |  | 93 | 94 | 96 | 96 | 96 | 96 | 96 | 2191487
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 48 | 44 | 45 | 45 | 45 | 41 | 44 | 45 | 43 | 31 | 37 | 36 | 45 | 45 | 42 | 36 | 45 | 45 |  | 40 | 45 | 42 | 31 | 34 | 34 | 33 | 1023702
86 | Meghnaghat CCPP ( Summit) | 310 | 310 | 308 | 308 | 305 | 307 | 295 | 310 | 280 | 292 | 300 | 294 | 300 | 299 | 297 | 289 | 302 | 288 |  | 297 | 304 | 275 | 274 | 289 | 281 | 302 | 7169309
87 | Meghnaghat 100 MW(IEL) | 34 | 33 | 34 | 35 | 58 | 58 | 59 | 58 | 58 | 59 | 58 | 58 | 59 | 58 | 45 | 42 | 41 | 51 |  | 58 | 59 | 59 | 58 | 58 | 45 | 42 | 1206720
| Meghnaghat 104 MW PP (OPCL) | 54 | 54 | 35 | 35 | 50 | 54 | 54 | 35 | 35 | 35 | 45 | 54 | 54 | 54 | 55 | 55 | 55 | 54 |  | 58 | 72 | 71 | 59 | 70 | 71 | 71 | 1262400
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 35 | 35 | 35 | 35 | 25 | 35 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 25 | 713040
92 | Fenchuganj 44 MW (Energyprima) | 30 | 46 | 46 | 46 | 46 | 46 | 46 | 47 | 47 | 47 | 46 | 46 | 43 | 43 | 45 | 43 | 45 | 43 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1054440
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 955692
94 | Gagnagar 102 MW PP (Digital Power) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 50 | 50 | 50 | 50 | 66 | 66 | 66 | 65 |  | 102 | 102 | 102 | 102 | 102 | 102 | 40 | 1222416
95 | Patenga 50MW PP (Baraka) | 40 | 40 | 36 | 25 | 19 | 19 | 20 | 26 | 26 | 26 | 32 | 32 | 32 | 32 | 32 | 26 | 26 | 39 |  | 40 | 39 | 39 | 39 | 40 | 40 | 40 | 766560
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 |  | 6 | 12 | 11 | 11 | 11 | 12 |  | 16 | 17 | 17 | 18 | 18 |  | 0 | 140160
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 370302
100 | Manikganj 55 MW PP (Northern) | 17 | 17 | [6 empty] | 5 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 318910
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 80 | 112 | 112 | 80 | 80 | 80 | 80 | 80 | 112 | 112 | 80 |  | 80 | 112 | 112 | 112 | 112 | 112 | 112 | 2403081
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [8 empty] | 14850
103 | Kamalaghat 54 MW PP(Banco Energy) | [14 empty] | 17 | 17 | 17 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 272160
104 | Keranigonj 300 MW PP (APR) | 218 | 156 | 157 | 250 | 168 | [6 empty] | 260 | 282 | 250 | 301 | 160 | 30 |  |  |  | 30 | 10 | 296 | 150 | 301 | 300 | 3320335
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 69 | 68 | 67 | 67 | 67 | 68 | 67 | 67 | 67 |  | 87 | 87 | 87 | 87 | 88 | 68 | 68 | 1718400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 36 | 35 | 35 | 68 | 89 | 89 | 89 | 65 | 34 | 35 | 54 |  | 143 | 134 | 135 | 151 | 149 | 78 | 35 | 1588608
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 37 | 37 | 37 | 25 | 25 | 25 | 25 |  | 37 | 37 | 37 | 37 | 37 | 37 | 25 | 696960
116 | Chandpur 200 MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 26 | 35 | 34 | 36 | 36 | 36 | 34 | 34 | 42 |  | 51 | 51 | 51 | 51 | 51 | 51 | 21 | 764640
117 | Ashuganj 150 MW PP (Midland) | 5 | 5 | 5 | 5 | 6 | 5 | 5 | 3 | 5 | 5 | 5 | 5 | 3 | 2 | 5 | 3 | 5 | 5 |  | 36 | 100 | 93 | 125 | 130 | 55 | 6 | 531927
118 | Bibiyana-III 400 MW CCPP | 367 | 390 | 409 | 404 | 403 | 403 | 402 | 317 | 368 | 367 | 368 | 368 | 369 | 390 | 368 | 368 | 368 | 319 |  | 349 | 367 | 414 | 407 | 409 | 404 | 390 | 9233000
| Jamalpur 115 MW PP (United) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 84 | 84 | 84 | 84 | 84 | 18 | 18 | 711600
| Anwara 300 MW PP (United) | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 87 | 87 | 88 | 88 | 88 | 88 | 88 | 104 |  | 221 | 236 | 272 | 276 | 283 | 124 | 124 | 2918073
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 38 | 25 | 38 | 25 | 25 | 28 | 29 |  | 42 | 42 | 43 | 44 | 45 | 46 | 47 | 740160
| Anlima Energy Ltd. | 42 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 41 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 53 |  | 76 | 87 | 87 | 100 | 107 | 107 | 107 | 1372473
| Bhairob 54.5 MW | 17 | 17 | 34 | 35 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 471240
| Spectra Solar Plant Ltd. | [5 empty] | 2 | 6 | 17 | 18 | 30 | 32 | 16 | 34 | 26 | 26 | 18 |  | 2 | [8 empty] | 236363
| Chandpur 115(Doreen) | 58 | 57 | 58 | 58 | 58 | 58 | 57 | 58 | 58 | 65 | 89 | 93 | 93 | 96 | 65 | 56 | 52 | 54 |  | 61 | 96 | 94 | 99 | 93 | 86 | 57 | 1682880
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 20 | 32 | 17 | 17 | 17 | 17 | 447840
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 163 | 163 | 163 | 163 | 163 | 163 | 72 | 1453600
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 3 | 9 | 6 | 5 | 7 | 13 | 6 | 9 | 8 | 9 | 14 | 6 | 12 | 14 | 21 | 12 | 12 | 8 |  | 13 | 10 | 12 | 2 | 12 | 5 | 3 | 215040
120 | Eastern Zone Total | 7417 | 7391 | 7254 | 7207 | 7113 | 7003 | 6996 | 6766 | 6852 | 6950 | 7103 | 7508 | 7585 | 7604 | 7528 | 7300 | 7201 | 7252 |  | 8117 | 8609 | 8725 | 9034 | 8924 | 8589 | 8140 | 181050492
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 48 | 33 | 32 | 32 | 16 | 16 | 15 |  | 16 | 16 | 16 |  | 47 | 56 | 81 | 86 | 97 | 32 | 32 | 948480
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL) | 234 | 235 | 234 | 234 | 235 | 25 | [10 empty] | 50 | 50 |  | 50 | 232 | 232 | 233 | 233 | 234 | 231 | 2503821
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 11 | 25 |  | 26 | 32 | 21 | 21 | 16 | 16 | 10 | 285600
| Khulna 225 MW CCPP | 224 | 223 | 221 | 221 | 224 | 222 | 224 | 223 | 221 | 222 | 220 | 218 | 218 | 203 | 204 | 202 | 202 | 205 |  | 221 | 207 | 207 | 208 | 207 | 208 | 205 | 5192237
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 37 | 41 | 53 | 43 | 35 | 35 |  | 35 | 35 | 36 | 36 | 35 | 35 | 36 | 880320
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 7 | 26 | 59 | 66 | 83 | 98 | 107 | 99 | 29 | 48 | 54 | 38 | 16 | [8 empty] | 712800
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [12 empty] | 19 | 150 | 404400
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 221 | 221 | 221 | 221 | 221 | 221 | 221 | 221 | 221 |  | 221 | 221 | 220 | 220 | 220 | 220 | 220 | 5287909
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 48 | 48 | 48 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 622560
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 134 | 134 | 135 | 132 | 134 | 136 | 122 | 132 | 126 | 124 | 124 | 124 | 132 | 128 | 128 | 130 | 132 | 124 |  | 132 | 132 | 132 | 132 | 132 | 130 | 130 | 3107000
140 | Bhola 33 MW PP (Venture) | 34 | 34 | 32 | 31 | 28 | 27 | 24 | 21 | 20 | 22 | 15 | 22 | 23 | 24 | 25 | 25 | 25 | 23 |  | 30 | 32 | 32 | 34 | 35 | 35 | 35 | 648144
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 32 | 32 | 40 | 40 | 40 | 32 | 32 | 421500
143 | Gopalganj 100 MW Peaking PP | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 26 | 26 | 23 | 24 | 25 | 30 | 25 | 22 | 22 | 22 | 30 |  | 50 | 55 | 60 | 54 | 54 | 51 | 51 | 907904
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 37 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1339632
146 | Bheramara HVDC | 908 | 909 | 909 | 909 | 906 | 905 | 905 | 906 | 906 | 905 | 906 | 904 | 906 | 905 | 907 | 906 | 907 | 907 |  | 906 | 907 | 766 | 764 | 764 | 764 | 781 | 21067887
147 | Bheramara 410 MW CCPP | 150 | 150 | 150 | 160 | 160 | 170 | 170 | 160 | 160 | 155 | 150 | 145 | 140 | 140 | 140 | 140 | 140 | 145 |  | 150 | 155 | 155 | 160 | 160 | 145 | 150 | 2510496
148 | Payra 1320 MW | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1232 | 1232 | 1222 | 1222 | 1222 | 1232 | 1244 | 1244 | 1244 | 1220 |  | 1222 | 1222 | 1222 | 1222 | 1232 | 1244 | 1244 | 31443100
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 230 | 230 | 235 | 235 | 235 | 235 | 235 | 4461900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 215024
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 2 | 2 | 5 | 5 | 5 | 5 | 4 | 3 | 2 | 1 | 0 | [8 empty] | 38580
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 153 | 154 | 155 | 158 | 160 | 161 | 160 | 159 | 156 | 154 | 152 | 150 | 148 | 147 | 146 | 147 | 148 | 149 |  | 153 | 157 | 156 | 155 | 153 | 153 | 152 | 3933918
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 414 | 414 | 409 | 414 | 414 | 414 | 390 | 380 | 414 | 350 | 414 | 380 | 380 | 362 | 414 | 414 | 370 |  | 330 | 414 | 414 | 414 | 380 | 414 | 414 | 9555454
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 |  |  |  |  | 0 | 133400
165 | Amnura 50 MW PP(Sinha) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 494720
166 | Katakhali 50 MW PP (Northern) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 25 | 25 | 34 |  | 34 | 34 | 34 | 25 | 25 | 34 | 34 | 843208
167 | Katakhali 50 MW Peaking PP | 21 | 21 | [15 empty] | 28 |  | 29 | 30 | 30 | 29 | 29 | 27 | 27 | 215077
168 | Santahar 50 MW Peaking PP | [16 empty] | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 241060
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200150
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 20 |  | 63 | 92 | 90 | 90 | 90 | 90 | 90 | 508544
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 37 | 50 | 50 | 50 |  | 55 | 60 | 70 | 70 | 70 | 70 | 35 | 1136352
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 55 | 55 |  | 55 | 75 | 75 | 75 | 75 | 75 | 57 | 1172448
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 24 | 60 | 70 |  | 70 | 80 | 84 | 84 | 84 | 84 | 34 | 1115990
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 3 | 5 | 6 | 7 | 7 | 7 | 7 | 6 | 4 | 3 | 1 | [8 empty] | 56487
178 | Energypac Power Venture Thakurgaon Ltd. | [9 empty] | 5 | 35 | 75 | 75 | 75 | 75 | 75 | 36 | 36 |  | 36 | 72 | 75 | 75 | 75 | 75 | 0 | 855360
| Intraco Solar 30 MW | [5 empty] | 1 | 6 | 12 | 23 | 16 | 34 | 19 | 32 | 32 | 23 | 19 | 10 | 2 |  | 0 | [6 empty] | 226130
| Adani Power Jharkhanda Ltd | 718 | 721 | 722 | 719 | 714 | 738 | 725 | 717 | 717 | 720 | 719 | 716 | 712 | 718 | 713 | 718 | 719 | 721 |  | 725 | 715 | 715 | 716 | 720 | 722 | 717 | 17198182
178 | Teesta Solar Limited | [5 empty] | 11 | 35 | 91 | 148 | 185 | 179 | 207 | 206 | 190 | 117 | 107 | 46 | 14 | [8 empty] | 1499830