## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-07-30 | Sunday
|  | Date (day): | 2023-07-30 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13379.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15455 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-07-29 | 2023-07-30 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 180 | 210 | 210 | 210
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 6 | 12 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 367 | 368 | 350 | 370 |  |  | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 326 | 332 | 300 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 45 | 66 | 50 | 64 | 36 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Under maint
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 20 | 85 | 96 | 96 |  | 6 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 15 | 15 | 15 | 30 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 21 | 11 | 22 |  | 53 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  | 3 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 193 | 193 | 195 | 195 | 15
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 12 | 80 | 25 | 80 | 20 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 326 | 327 | 330 | 330 |  | 115
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 25 | 102 | 32 | 84 |  | 18 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 35 | 17 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 64 | 130 | 64 | 130 | 19 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 |  |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 35 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 39 | 41 | 41 | 41 |  | 39 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 24 | 23 | 24 | 24 |  | 9 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 52 | 25 | 51 | 51 | 1
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 80 | 112 | 112 | 115 | 185 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 150 | 300 | 50
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
33 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
34 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 70 | 135 | 70 | 149
35 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 105 | 35 | 105
36 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 53 | 72 | 53 | 72 | 32 |  | Fuel shortage
37 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 108 | 54 | 162
38 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 35 | 0 | 35 | 0
39 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 34 | 21 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6063 | 5722 | 2781 | 3366 | 3089 | 3786 | 1057 | 1003
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 122 | 120 | 120 | 120 |  | 60
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
41 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 22 | 8 | 25
42 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 18 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 46 | 6 | 46
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 110 | 110 | 110 | 110 | 120 |  | Low Water Level
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 218 | 221 | 220 | 225
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 97 | 97 | 8 |  | Engine problem
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 32 | 57 | 40 | 64 | 34 |  | Fuel shortage
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 46 | 50 | 50 | 50 | 52 |  | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 46 | 68 | 45 | 70 | 30 |  | Fuel shortage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 50 | 100 | 50 | 100
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 11 | 11 | 11 | 11 | 11 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 26 | 41 | 20 | 35
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 24 | 0 | 24 | 84 |  | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 122 | 267 | 120 | 300
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 55 | 54 | 54 | 56 |  | Fuel shortage
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 38 | 88 | 38 | 88 | 12 |  | Fuel shortage
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 34 | 68 | 34 | 68 | 48 |  | Fuel shortage
60 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 17 | 143 | 52 | 163
| SS Power I |  | Coal | SS Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 1 | 7 | 20 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 18 | 150 | 0 | 0
| Chattogram area Total |  |  |  |  | 2605 | 2545 | 979 | 1682 | 1137 | 1677 | 492 | 390
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 153 | 204 | 190 | 200 | 21 |  | Gas shortage
62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 270 | 270 | 270 | 90 |  | Gas shortage
63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 240 | 240 | 240 | 120 |  | Gas shortage
64 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 270 | 270 | 270 | 270 | 130 |  | Gas shortage
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 0 | 0 | 0 | 45 |  | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 0 | 0 | 0 | 195 |  | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  |  | Engine problem
69 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 5 | 57 | 6 | 60
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 24 | 46 | 44 | 46 |  | 6 | Machine problem
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
72 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 157 | 51 | 150 | 50 |  | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 19 | 20 | 20
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 120 | 98 | 146 | 169
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 43 | 43 |  | 9 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 12 | 20 | 20 |  | 5 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Contract Expired
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 70 | 106 | 17 | 17 | 97 |  | Fuel shortage
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 28 | 58 | 27 | 75 | 38 |  | Fuel shortage
81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 3 | 17 | 17 | 17 |  | 37 | Engine problem
82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 72 | 114 | 72 | 115
| Cumilla Area Total |  |  |  |  | 3159 | 3096 | 1426 | 1763 | 1520 | 1799 | 786 | 220
83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 66 | 97 | 50 | 98 | 104 |  | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 16 | 18 | 18 |  | 4 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 68 | 97 | 68 | 98 | 102 |  | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 84 | 18 | 85 | 30 |  | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 28 | 0 | 50 | 0
90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 12 | 6 | 12 | 10 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 206 | 306 | 211.6 | 311 | 104 | 4
91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Under maint
93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 112 | 112 |  | 51 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 50 | 50
96 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 40 | 43 | 48 | 48
97 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 25 | 20 | 30 | 30 |  |  | Unit-9 under maint
99 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 86 | 80 | 86
100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 185 | 182 | 185 | 185 |  | 46 | ST Under maint
102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 17 | 17
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
103 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
104 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 290 | 300 | 300 |  |  | FGMO
105 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 368 | 368 | 400 | 400 |  |  | FGMO
106 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
107 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 350 | 350 | 350 | 350
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1594 | 1590 | 1647 | 1653 | 0 | 657
108 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 912 | 912 | 930 | 930
109 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 8 | 16 | 16 | 16 |  | 99 | Fuel shortage
110 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 22 | 20 | 30 |  | 24 | Engine problem
111 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 120 | 120 | 120
112 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 53 | 40 | 55 |  | 54 | Engine problem
113 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 240 | 205 | 235 | 235 | 175 |  | Gas shortage
114 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 24 | 32 | 32 | 40
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
115 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 35 | 35 | 35 | 70 |  | Fuel shortage
116 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 25 | 105 | 70 | 105
117 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 13 | 0 | 100 | 0
118 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 220 | 220 | 0 | 0 | 0 | 0 |  |  | Fuel shortage
119 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 414 | 380 | 0 | 0 |  | 617 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3125 | 3121 | 1791 | 1880 | 1598 | 1566 | 261 | 794
120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 110 | 16 | 110
121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 22 | 34 | 22 | 34 |  | 6 | Engine problem
122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 130 | 120 | 120 | 120 |  | 74 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1130 | 1230 | 1244 | 1244
124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 221 | 220 | 220 | 220
125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 150 | 17 | 150
126 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 250 | 250 | 250 | 250 | 57 |  | Coal shortage
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1786 | 2114 | 1889 | 2128 | 57 | 80
127 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
128 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 35 | 0 | 35 | 17 |  | Fuel shortage
129 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 31 | 0 | 32 |  | 39 | Engine problem
130 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 21 | 21 | 21 | 21
131 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 42 | 34 | 42 |  | 8 | Engine problem
132 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 35 | 35 |  | 15 | Engine problem
133 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Under maint
134 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 140 | 140 | 140 |  |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 163 | 181 | 160 | 181 | 39 |  | Gas shortage
136 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 414 | 414 | 414
137 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 24 | 25 | 25 | 25 |  | Fuel shortage
138 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 |  | 44 | Fuel shortage
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 0 | 93 | 11 |  | Fuel shortage
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 200 | 200
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 95 | 35 | 95 | 18 |  | Fuel shortage
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 55 | 35 | 55 | 58 |  | Fuel shortage
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 748*2 | 1496 | 1496 | 756 | 764 | 750 | 750
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 1585 | 1946 | 1871 | 2134 | 339 | 319
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 208 | 210 | 180 | 210
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 28 | 78 | 34 | 78 | 35 |  | Fuel shortage
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 36 | 114 | 35 | 113
153 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 16 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 144 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 439 | 402 | 417 | 401 | 160 | 85
| Total |  |  |  |  | 24911 | 24171 | 12587 | 15049 | 13379.6 | 15455 | 3256 | 3552
A. |  | 2023-07-29 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 15060 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 11678 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 15175 | MW
3 | Day peak Generation : |  |  | 12587 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14463.62 | MW
4 | Evening peak Generation : |  |  | 15049 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 120 | MW
5 | Total Energy Generation : |  | 315.2399 | MKWHr | By Solar | 2.217 | MKWHr
| By Gas : | 154.5988 | MKWHr |  | By Oil: | 60.9656 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 69.9875 | MKWHr |  | By Hydro: | 2.6658 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.14208 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3256 | MW | Dhaka | 4920.32 | 4895.32 |  | 25 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3552 | MW | Chittagong | 1355.5 | 1355.5 |  | 0 |  | 19:00 |  | 150
|  |  | Total = |  |  | 6808 | MW | Khulna | 1785.2 | 1785.2 |  | 0 |  | 19:30 |  | 272
7 | Total Gas Supplied : |  |  | 1178.29 | MMCFD |  |  | Rajshahi | 1645.2 | 1645.2 |  | 0 |  | 20:00 |  | 139.43
8 | Fuel Cost : | i) Gas : | Taka | 171118879.528 | ii) Oil : | Taka | 828833423.12 | Comilla | 1447 | 1415 |  | 32 |  | 21:00 |  | 120.33
|  | iii) Coal : | Taka | 300218739 | Total | Taka | 1300171041.648 | Mymensingh | 1221 | 1169 |  | 52 |  | 22:00 |  | 133.7
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 622 | 611 |  | 11 |  | 23:00 |  | 340.935
| ii) During Peak Demand : |  |  | 630 | MW (E to W) at | 21:00 | hrs | Barisal | 474.4 | 474.4 |  | 0 |  | 24:00 |  | 1029.49
| iii) Maximum : |  |  | 604 | MW at | 20:00 | hrs | Rangpur | 993 | 993 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 34.2° C |  |  | Total | 14463.62 | 14343.62 |  | 120
B. |  | 2023-07-30 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 34.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 15700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 226 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15455 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 14200 | MW
4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 329.8694 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 12232 | MW at | 8:00 | 65 | 27 | 28 | 22 | 22 | 20 | 12 | 10 | 20
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.7862 | MKWHr. | ii) HVDC Flow at Peak Time |  | 912 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.8771 | MKWHr. | iii) Maximum HVDC Flow : |  | 918 | MW at | 14:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 80.46 |  | (b) Today: | 80.5 |  | (c) Rule Curve: |  | 88.66
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-07-29 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 210 | 180 | 0 | 0 | 0 | 367 | 332 |  | 0 | 450 | 159 | 33 | 95 | 15 | 332 | 0 | 137 | 48 | 92 | 82 | 5 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 19 | 20 | 25 | 24 | 8 | 0 | 80 | 30 | 122 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 42 | 37 | 68 | 0 | 6 | 10 | 42 | 0 | 0 | 0 | 270 | 230 | 209 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 38 | 8 | 20 | 11 | 33 | 20 | 132 | 101 | 0 | 18 | 0 | 30 | 0 | 50 | 45 | 112 | 0 | 25 | 81 | 0 | 98 | 17 | 0 | 10 | 275 | 24 | 8 | 0 | 115 | 0 | 0 | 68 | 0 | 36 | 0 | 25 | 100 | 5 | 402 | 18 | 35 | 17 | 0 | 225 | 36 | 55 | 51 | 9 | 75 | 340 | 48 | 0 | 35 | 34 | 0 | 17 | 0 | 53 | 17 | 285 | 70 | 0 | 0 | 4 | 0 |  | 917 | 0 | 190 | 0 | 16 | 120 | 0 | 0 | 11 | 49 | 8 | 120 | 33 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 42 | 21 | 8 | 30 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 174 | 0 | 370 | 35 | 0 | 35 | 85 | 34 | 0 | 0 | 55 | 1244 | 220 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 250 | 764 | 0 | 0 |  | 7445 | 5891 | 13336 | 4322 | 917 | 2222 | 0 | 2031 | 2938 | 110 | 280 | 380 | 132 | 0 | 4 | 634.12 | 80.41
2:00 | 0 | 0 | 210 | 180 | 0 | 0 | 0 | 367 | 332 |  | 0 | 450 | 150 | 33 | 95 | 15 | 280 | 0 | 136 | 48 | 92 | 82 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 20 | 25 | 24 | 8 | 0 | 80 | 30 | 120 | 0 | 8 | 225 | 0 | 0 | 0 |  | 6 | 41 | 51 | 68 | 0 | 6 | 10 | 42 | 0 | 0 | 0 | 270 | 230 | 198 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 31 | 8 | 20 | 11 | 33 | 20 | 140 | 101 | 0 | 18 | 0 | 30 | 0 | 50 | 45 | 112 | 0 | 25 | 81 | 0 | 106 | 17 | 0 | 10 | 265 | 24 | 8 | 0 | 112 | 0 | 0 | 68 | 0 | 36 | 0 | 25 | 100 | 6 | 402 | 18 | 35 | 17 | 0 | 87 | 36 | 55 | 51 | 9 | 75 | 350 | 36 | 0 | 35 | 34 | 0 | 17 | 0 | 18 | 17 | 405 | 17 | 0 | 0 | 7 | 0 |  | 917 | 0 | 200 | 0 | 16 | 120 | 0 | 0 | 5 | 0 | 8 | 128 | 32 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 16 | 6 | 8 | 30 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 179 | 0 | 370 | 35 | 0 | 35 | 85 | 34 | 0 | 0 | 55 | 1244 | 220 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 250 | 763 | 0 | 0 |  | 7253 | 5803 | 13056 | 4416 | 917 | 2202 | 0 | 1804 | 2937 | 110 | 260 | 263 | 140 | 0 | 7 | 424.02 | 80.42
3:00 | 0 | 0 | 210 | 180 | 0 | 0 | 0 | 367 | 332 |  | 0 | 450 | 137 | 33 | 68 | 15 | 280 | 0 | 137 | 34 | 50 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 20 | 25 | 24 | 8 | 0 | 80 | 30 | 118 | 0 | 8 | 223 | 0 | 0 | 0 |  | 6 | 41 | 51 | 68 | 0 | 6 | 10 | 42 | 0 | 0 | 0 | 270 | 230 | 201 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 31 | 8 | 20 | 11 | 33 | 20 | 142 | 101 | 0 | 18 | 0 | 30 | 0 | 50 | 45 | 112 | 0 | 25 | 81 | 0 | 120 | 17 | 0 | 10 | 280 | 24 | 8 | 0 | 115 | 0 | 0 | 68 | 0 | 36 | 0 | 25 | 60 | 5 | 403 | 18 | 35 | 17 | 0 | 87 | 36 | 55 | 51 | 9 | 75 | 350 | 35 | 0 | 35 | 34 | 0 | 17 | 0 | 18 | 17 | 270 | 17 | 0 | 0 | 8 | 0 |  | 913 | 0 | 205 | 0 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 133 | 30 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 16 | 0 | 8 | 30 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 181 | 0 | 414 | 35 | 0 | 35 | 50 | 34 | 0 | 0 | 55 | 1244 | 220 | 0 | 116 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 250 | 763 | 0 | 0 |  | 6997 | 5773 | 12770 | 4308 | 913 | 2246 | 0 | 1594 | 2937 | 110 | 260 | 252 | 142 | 0 | 8 | 382 | 80.43
4:00 | 0 | 0 | 210 | 180 | 0 | 0 | 0 | 367 | 332 |  | 0 | 450 | 127 | 34 | 51 | 15 | 280 | 0 | 137 | 24 | 24 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 20 | 25 | 24 | 8 | 0 | 80 | 30 | 120 | 0 | 8 | 225 | 0 | 0 | 0 |  | 6 | 41 | 51 | 68 | 0 | 6 | 10 | 42 | 0 | 0 | 0 | 270 | 230 | 207 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 31 | 8 | 20 | 11 | 33 | 20 | 114 | 101 | 0 | 18 | 0 | 30 | 0 | 50 | 45 | 112 | 0 | 22 | 81 | 0 | 127 | 17 | 0 | 10 | 290 | 24 | 8 | 0 | 115 | 0 | 0 | 68 | 0 | 36 | 0 | 25 | 34 | 5 | 403 | 18 | 35 | 17 | 0 | 87 | 36 | 55 | 51 | 9 | 50 | 350 | 35 | 0 | 35 | 34 | 0 | 17 | 0 | 17 | 17 | 270 | 17 | 0 | 0 | 6 | 0 |  | 912 | 0 | 205 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 8 | 124 | 30 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 180 | 0 | 414 | 35 | 0 | 35 | 50 | 34 | 0 | 0 | 37 | 1244 | 220 | 0 | 116 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 250 | 764 | 0 | 0 |  | 6859 | 5648 | 12507 | 4309 | 912 | 2246 | 0 | 1408 | 2938 | 110 | 260 | 204 | 114 | 0 | 6 | 356.215 | 80.44
5:00 | 0 | 0 | 210 | 180 | 0 | 0 | 0 | 367 | 332 |  | 0 | 450 | 109 | 33 | 51 | 15 | 333 | 0 | 138 | 24 | 24 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 20 | 25 | 24 | 8 | 0 | 80 | 30 | 123 | 0 | 8 | 229 | 0 | 0 | 0 |  | 6 | 41 | 51 | 45 | 0 | 6 | 10 | 42 | 0 | 0 | 0 | 270 | 230 | 208 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 31 | 8 | 20 | 11 | 33 | 20 | 126 | 100 | 0 | 18 | 0 | 30 | 0 | 50 | 45 | 112 | 0 | 20 | 78 | 0 | 131 | 17 | 0 | 10 | 285 | 24 | 8 | 0 | 115 | 0 | 0 | 68 | 0 | 35 | 0 | 25 | 34 | 6 | 403 | 19 | 35 | 17 | 0 | 87 | 36 | 51 | 17 | 9 | 38 | 350 | 43 | 0 | 35 | 34 | 0 | 17 | 0 | 17 | 17 | 270 | 17 | 0 | 0 | 4 | 0 |  | 912 | 0 | 205 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 8 | 122 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 183 | 0 | 414 | 35 | 0 | 35 | 50 | 34 | 0 | 0 | 37 | 1244 | 220 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 502 | 0 | 250 | 766 | 0 | 0 |  | 6841 | 5553 | 12394 | 4373 | 912 | 2219 | 0 | 1244 | 2942 | 110 | 260 | 204 | 126 | 0 | 4 | 330.43 | 80.45
6:00 | 0 | 0 | 150 | 180 | 0 | 0 | 0 | 354 | 295 |  | 0 | 400 | 57 | 33 | 51 | 15 | 335 | 0 | 120 | 24 | 24 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 20 | 25 | 24 | 27 | 0 | 80 | 30 | 118 | 0 | 8 | 227 | 0 | 0 | 0 |  | 6 | 41 | 51 | 45 | 0 | 6 | 10 | 42 | 0 | 0 | 0 | 310 | 230 | 209 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 30 | 8 | 20 | 11 | 33 | 20 | 116 | 100 | 0 | 18 | 0 | 30 | 0 | 50 | 43 | 80 | 0 | 25 | 78 | 0 | 152 | 17 | 0 | 10 | 275 | 24 | 8 | 0 | 115 | 0 | 0 | 68 | 0 | 36 | 0 | 25 | 34 | 5 | 322 | 19 | 35 | 17 | 0 | 87 | 36 | 17 | 17 | 9 | 38 | 350 | 51 | 2 | 35 | 34 | 0 | 17 | 1 | 18 | 17 | 230 | 17 | 0 | 0 | 6 | 0 |  | 913 | 0 | 205 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 8 | 117 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 188 | 0 | 390 | 35 | 0 | 35 | 50 | 34 | 0 | 0 | 37 | 1160 | 170 | 0 | 17 | 0 | 1 | 0 | 0 | 0 | 501 | 1 | 250 | 754 | 2 | 0 |  | 6496 | 5384 | 11880 | 4223 | 913 | 1959 | 0 | 1238 | 2845 | 110 | 260 | 203 | 116 | 7 | 6 | 296.05 | 80.46
7:00 | 0 | 0 | 150 | 180 | 0 | 0 | 0 | 341 | 295 |  | 0 | 350 | 52 | 33 | 40 | 15 | 333 | 0 | 122 | 14 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 20 | 25 | 24 | 51 | 0 | 80 | 30 | 120 | 0 | 8 | 224 | 0 | 0 | 0 |  | 6 | 41 | 50 | 46 | 0 | 6 | 10 | 38 | 0 | 0 | 0 | 270 | 340 | 209 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 19 | 8 | 20 | 11 | 33 | 16 | 110 | 100 | 0 | 18 | 0 | 30 | 0 | 50 | 43 | 80 | 0 | 25 | 78 | 0 | 185 | 17 | 0 | 10 | 280 | 24 | 8 | 0 | 115 | 0 | 0 | 68 | 0 | 36 | 1 | 25 | 34 | 5 | 320 | 19 | 35 | 17 | 1 | 88 | 36 | 17 | 17 | 9 | 38 | 350 | 53 | 4 | 35 | 34 | 0 | 17 | 3 | 18 | 17 | 230 | 17 | 0 | 0 | 9 | 0 |  | 913 | 0 | 235 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 117 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 192 | 0 | 350 | 35 | 0 | 35 | 15 | 34 | 0 | 0 | 37 | 1100 | 170 | 0 | 17 | 0 | 10 | 0 | 0 | 0 | 501 | 0 | 250 | 762 | 26 | 0 |  | 6507 | 5311 | 11818 | 4343 | 913 | 1858 | 0 | 1186 | 2793 | 110 | 260 | 191 | 110 | 45 | 9 | 364.81 | 80.47
8:00 | 0 | 0 | 150 | 180 | 0 | 0 | 0 | 341 | 295 |  | 0 | 350 | 56 | 34 | 20 | 15 | 327 | 0 | 126 | 8 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 20 | 25 | 24 | 51 | 0 | 80 | 30 | 120 | 0 | 8 | 221 | 0 | 0 | 0 |  | 6 | 41 | 50 | 46 | 0 | 6 | 10 | 17 | 0 | 0 | 0 | 275 | 240 | 202 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 27 | 8 | 20 | 11 | 0 | 13 | 114 | 86 | 0 | 18 | 1 | 30 | 0 | 50 | 42 | 80 | 0 | 25 | 78 | 0 | 185 | 17 | 0 | 10 | 290 | 24 | 8 | 0 | 75 | 0 | 0 | 68 | 0 | 34 | 4 | 25 | 34 | 6 | 320 | 19 | 35 | 17 | 2 | 88 | 36 | 17 | 17 | 9 | 38 | 350 | 38 | 6 | 35 | 34 | 0 | 17 | 9 | 18 | 17 | 270 | 17 | 0 | 0 | 4 | 0 |  | 913 | 0 | 235 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 132 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 160 | 0 | 350 | 35 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 1100 | 176 | 0 | 17 | 1 | 21 | 0 | 0 | 0 | 501 | 0 | 250 | 756 | 85 | 0 |  | 6321 | 5357 | 11678 | 4201 | 913 | 1858 | 0 | 1103 | 2787 | 110 | 260 | 199 | 114 | 129 | 4 | 345.71 | 80.48
9:00 | 0 | 0 | 180 | 180 | 0 | 0 | 0 | 360 | 327 |  | 0 | 350 | 5 | 33 | 17 | 15 | 333 | 0 | 122 | 8 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 17 | 19 | 20 | 25 | 24 | 51 | 0 | 80 | 30 | 120 | 0 | 8 | 224 | 0 | 0 | 0 |  | 6 | 32 | 48 | 46 | 0 | 6 | 10 | 24 | 0 | 0 | 0 | 270 | 240 | 204 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 32 | 8 | 0 | 11 | 33 | 15 | 108 | 87 | 0 | 18 | 1 | 30 | 0 | 50 | 42 | 112 | 0 | 20 | 78 | 0 | 185 | 17 | 0 | 10 | 310 | 24 | 8 | 0 | 75 | 0 | 0 | 68 | 0 | 60 | 6 | 25 | 0 | 5 | 364 | 19 | 35 | 17 | 3 | 88 | 35 | 17 | 17 | 9 | 38 | 350 | 35 | 34 | 35 | 34 | 0 | 17 | 21 | 17 | 17 | 270 | 17 | 0 | 0 | 4 | 0 |  | 912 | 0 | 245 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 132 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 160 | 0 | 380 | 35 | 0 | 35 | 15 | 34 | 0 | 1 | 35 | 1120 | 172 | 0 | 17 | 0 | 4 | 0 | 0 | 0 | 499 | 6 | 250 | 758 | 63 | 0 |  | 6486 | 5387 | 11873 | 4325 | 912 | 1924 | 0 | 1091 | 2807 | 110 | 260 | 193 | 108 | 139 | 4 | 312.285 | 80.48
10:00 | 0 | 0 | 180 | 180 | 0 | 0 | 0 | 366 | 326 |  | 0 | 350 | 0 | 41 | 17 | 15 | 333 | 0 | 122 | 8 | 8 | 64 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 19 | 19 | 20 | 25 | 24 | 51 | 0 | 80 | 30 | 121 | 0 | 8 | 223 | 0 | 0 | 0 |  | 6 | 32 | 47 | 46 | 0 | 6 | 11 | 23 | 0 | 0 | 0 | 270 | 240 | 206 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 32 | 8 | 0 | 8 | 28 | 12 | 110 | 68 | 0 | 18 | 1 | 30 | 0 | 47 | 41 | 112 | 0 | 28 | 78 | 0 | 185 | 17 | 0 | 10 | 285 | 24 | 8 | 0 | 75 | 0 | 0 | 68 | 0 | 71 | 0 | 50 | 0 | 5 | 368 | 19 | 35 | 17 | 5 | 88 | 17 | 17 | 17 | 12 | 38 | 350 | 35 | 29 | 54 | 34 | 0 | 17 | 29 | 25 | 17 | 270 | 17 | 0 | 0 | 4 | 0 |  | 912 | 0 | 240 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 132 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 160 | 0 | 380 | 35 | 0 | 35 | 15 | 34 | 0 | 4 | 35 | 1100 | 176 | 0 | 17 | 3 | 26 | 0 | 0 | 0 | 502 | 15 | 250 | 757 | 148 | 0 |  | 6527 | 5490 | 12017 | 4313 | 912 | 1892 | 0 | 1175 | 2789 | 110 | 260 | 192 | 110 | 260 | 4 | 270.265 | 80.48
11:00 | 0 | 0 | 180 | 180 | 0 | 0 | 0 | 366 | 332 |  | 0 | 350 | 0 | 42 | 17 | 15 | 325 | 0 | 125 | 8 | 8 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 5 | 19 | 19 | 20 | 25 | 24 | 52 | 0 | 80 | 30 | 118 | 0 | 8 | 216 | 0 | 0 | 0 |  | 6 | 32 | 47 | 46 | 0 | 6 | 11 | 16 | 0 | 0 | 0 | 270 | 280 | 204 | 26 | 0 | 3 | 0 | 0 | 43 | 0 | 24 | 8 | 0 | 11 | 33 | 12 | 116 | 68 | 0 | 18 | 2 | 30 | 0 | 47 | 41 | 112 | 0 | 25 | 78 | 0 | 186 | 17 | 0 | 10 | 270 | 24 | 8 | 0 | 75 | 0 | 0 | 68 | 0 | 71 | 20 | 50 | 0 | 5 | 350 | 19 | 35 | 17 | 4 | 121 | 17 | 17 | 65 | 28 | 38 | 350 | 49 | 50 | 54 | 34 | 0 | 15 | 32 | 71 | 17 | 270 | 17 | 0 | 0 | 8 | 0 |  | 913 | 0 | 240 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 132 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 160 | 0 | 300 | 35 | 0 | 35 | 15 | 34 | 0 | 5 | 35 | 1100 | 176 | 0 | 17 | 5 | 6 | 36 | 0 | 0 | 488 | 0 | 250 | 761 | 95 | 0 |  | 6777 | 5353 | 12130 | 4327 | 913 | 1823 | 0 | 1391 | 2779 | 110 | 260 | 184 | 116 | 219 | 8 | 181.45 | 80.48
12:00 | 0 | 0 | 180 | 180 | 0 | 6 | 0 | 367 | 326 |  | 0 | 450 | 0 | 45 | 20 | 15 | 326 | 0 | 193 | 12 | 25 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 19 | 20 | 25 | 24 | 52 | 0 | 80 | 30 | 122 | 0 | 8 | 218 | 0 | 0 | 0 |  | 6 | 32 | 46 | 46 | 0 | 6 | 11 | 26 | 0 | 0 | 0 | 270 | 270 | 153 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 24 | 8 | 16 | 11 | 33 | 12 | 120 | 66 | 0 | 18 | 1 | 30 | 0 | 47 | 40 | 112 | 0 | 25 | 78 | 0 | 185 | 17 | 0 | 10 | 300 | 24 | 8 | 0 | 80 | 0 | 0 | 68 | 0 | 70 | 18 | 50 | 0 | 5 | 368 | 19 | 35 | 17 | 5 | 122 | 17 | 17 | 70 | 28 | 38 | 350 | 53 | 28 | 54 | 34 | 0 | 3 | 35 | 72 | 17 | 270 | 17 | 0 | 0 | 1 | 18 |  | 912 | 0 | 240 | 0 | 8 | 120 | 0 | 0 | 0 | 0 | 24 | 130 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 208 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 163 | 0 | 414 | 35 | 0 | 35 | 25 | 28 | 0 | 7 | 35 | 1130 | 221 | 0 | 17 | 5 | 13 | 36 | 0 | 0 | 414 | 16 | 250 | 756 | 144 | 0 |  | 6986 | 5601 | 12587 | 4381 | 912 | 2103 | 0 | 1469 | 2758 | 110 | 260 | 183 | 120 | 272 | 1 | 83.085 | 80.48
13:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 367 | 327 |  | 0 | 450 | 0 | 51 | 68 | 15 | 320 | 0 | 193 | 36 | 32 | 64 | 14 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 19 | 22 | 25 | 24 | 52 | 0 | 80 | 60 | 122 | 0 | 8 | 223 | 0 | 0 | 0 |  | 12 | 32 | 45 | 46 | 0 | 6 | 11 | 28 | 0 | 0 | 0 | 270 | 240 | 178 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 37 | 8 | 16 | 11 | 33 | 12 | 122 | 64 | 0 | 18 | 1 | 30 | 0 | 47 | 40 | 112 | 0 | 25 | 78 | 0 | 185 | 17 | 0 | 10 | 290 | 24 | 8 | 0 | 110 | 0 | 0 | 68 | 0 | 71 | 5 | 50 | 0 | 5 | 368 | 19 | 35 | 17 | 4 | 123 | 17 | 24 | 70 | 28 | 38 | 330 | 53 | 30 | 72 | 34 | 0 | 17 | 16 | 72 | 17 | 270 | 17 | 0 | 0 | 9 | 30 |  | 912 | 0 | 235 | 0 | 16 | 120 | 0 | 0 | 0 | 15 | 32 | 100 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 48 | 21 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 150 | 0 | 393 | 35 | 0 | 35 | 105 | 34 | 0 | 7 | 35 | 1244 | 221 | 0 | 17 | 5 | 96 | 36 | 0 | 0 | 392 | 0 | 250 | 757 | 204 | 0 |  | 7198 | 5960 | 13158 | 4327 | 912 | 2076 | 0 | 1773 | 2883 | 140 | 260 | 258 | 122 | 368 | 9 | 0 | 80.48
14:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 367 | 327 |  | 0 | 450 | 0 | 50 | 96 | 15 | 280 | 0 | 157 | 50 | 33 | 64 | 22 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 19 | 20 | 25 | 24 | 52 | 0 | 80 | 60 | 126 | 0 | 8 | 219 | 0 | 0 | 0 |  | 12 | 32 | 45 | 46 | 3 | 6 | 11 | 23 | 0 | 0 | 0 | 270 | 240 | 186 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 30 | 8 | 16 | 11 | 33 | 12 | 128 | 65 | 0 | 18 | 2 | 30 | 0 | 50 | 40 | 112 | 0 | 25 | 78 | 0 | 184 | 17 | 0 | 10 | 285 | 16 | 8 | 0 | 112 | 0 | 0 | 68 | 0 | 70 | 6 | 50 | 17 | 5 | 368 | 19 | 35 | 17 | 2 | 123 | 17 | 53 | 70 | 12 | 38 | 350 | 53 | 42 | 72 | 34 | 0 | 34 | 25 | 72 | 17 | 270 | 17 | 0 | 0 | 6 | 60 |  | 918 | 0 | 210 | 0 | 16 | 120 | 0 | 0 | 10 | 25 | 32 | 128 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 48 | 21 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 150 | 0 | 326 | 35 | 0 | 35 | 105 | 34 | 0 | 4 | 55 | 1244 | 220 | 0 | 17 | 5 | 44 | 36 | 0 | 0 | 380 | 0 | 250 | 760 | 188 | 0 |  | 7281 | 5861 | 13142 | 4272 | 918 | 2001 | 0 | 1894 | 2874 | 140 | 260 | 271 | 128 | 318 | 6 | 0 | 80.48
15:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 367 | 326 |  | 0 | 450 | 0 | 58 | 96 | 15 | 326 | 0 | 194 | 44 | 33 | 64 | 22 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 19 | 21 | 25 | 24 | 25 | 0 | 78 | 30 | 120 | 0 | 8 | 215 | 0 | 0 | 0 |  | 12 | 32 | 47 | 46 | 8 | 6 | 11 | 23 | 0 | 0 | 0 | 270 | 240 | 195 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 31 | 8 | 16 | 11 | 33 | 12 | 128 | 65 | 0 | 15 | 1 | 30 | 0 | 50 | 40 | 112 | 0 | 20 | 78 | 0 | 182 | 17 | 0 | 10 | 310 | 24 | 8 | 0 | 112 | 0 | 0 | 68 | 0 | 70 | 6 | 50 | 51 | 5 | 368 | 19 | 35 | 17 | 4 | 123 | 17 | 53 | 70 | 9 | 38 | 350 | 53 | 29 | 72 | 34 | 0 | 0 | 20 | 72 | 17 | 270 | 17 | 0 | 0 | 7 | 150 |  | 918 | 0 | 210 | 0 | 16 | 120 | 0 | 0 | 10 | 26 | 32 | 132 | 25 | 16 | 0 | 0 | 0 | 0 | 5 | 48 | 21 | 16 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 161 | 0 | 414 | 35 | 0 | 35 | 105 | 34 | 0 | 2 | 55 | 1244 | 220 | 0 | 17 | 4 | 46 | 36 | 0 | 0 | 380 | 2 | 250 | 763 | 167 | 0 |  | 7408 | 5961 | 13369 | 4368 | 918 | 2113 | 0 | 1879 | 2877 | 108 | 260 | 280 | 128 | 281 | 7 | 90 | 80.49
16:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 367 | 327 |  | 0 | 450 | 0 | 67 | 96 | 15 | 319 | 0 | 156 | 60 | 33 | 64 | 24 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 19 | 21 | 25 | 23 | 8 | 0 | 80 | 30 | 123 | 0 | 8 | 219 | 0 | 0 | 0 |  | 12 | 32 | 47 | 46 | 12 | 35 | 11 | 22 | 0 | 0 | 0 | 270 | 240 | 203 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 39 | 8 | 17 | 11 | 0 | 12 | 126 | 65 | 0 | 15 | 1 | 30 | 0 | 50 | 40 | 112 | 0 | 20 | 84 | 0 | 182 | 17 | 0 | 10 | 285 | 24 | 8 | 0 | 112 | 0 | 0 | 68 | 0 | 71 | 7 | 50 | 51 | 3 | 368 | 19 | 35 | 17 | 3 | 123 | 17 | 53 | 70 | 9 | 38 | 350 | 53 | 6 | 72 | 34 | 0 | 13 | 14 | 72 | 17 | 270 | 17 | 0 | 0 | 9 | 150 |  | 916 | 0 | 210 | 0 | 16 | 120 | 0 | 0 | 10 | 28 | 32 | 128 | 22 | 16 | 0 | 0 | 0 | 0 | 16 | 48 | 21 | 16 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 176 | 0 | 370 | 35 | 0 | 35 | 105 | 34 | 0 | 2 | 55 | 1244 | 220 | 0 | 17 | 3 | 12 | 36 | 0 | 0 | 382 | 0 | 250 | 756 | 86 | 0 |  | 7362 | 5813 | 13175 | 4316 | 916 | 2047 | 0 | 1934 | 2872 | 110 | 260 | 301 | 126 | 134 | 9 | 149.935 | 80.49
17:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 367 | 328 |  | 0 | 350 | 0 | 66 | 96 | 15 | 280 | 0 | 78 | 72 | 33 | 64 | 23 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 19 | 21 | 25 | 23 | 8 | 0 | 80 | 30 | 117 | 0 | 8 | 219 | 0 | 0 | 0 |  | 12 | 40 | 48 | 46 | 11 | 44 | 11 | 27 | 0 | 0 | 0 | 270 | 240 | 199 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 39 | 8 | 18 | 11 | 25 | 12 | 134 | 68 | 0 | 15 | 1 | 30 | 0 | 50 | 40 | 80 | 0 | 20 | 86 | 0 | 181 | 17 | 0 | 10 | 290 | 24 | 8 | 0 | 112 | 0 | 0 | 68 | 0 | 71 | 0 | 50 | 55 | 5 | 368 | 19 | 35 | 17 | 1 | 123 | 17 | 55 | 70 | 9 | 38 | 350 | 53 | 4 | 89 | 34 | 0 | 17 | 3 | 72 | 17 | 270 | 17 | 0 | 0 | 7 | 150 |  | 917 | 0 | 205 | 0 | 16 | 120 | 0 | 0 | 10 | 35 | 24 | 130 | 21 | 16 | 0 | 0 | 0 | 0 | 20 | 48 | 21 | 34 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 173 | 0 | 365 | 35 | 0 | 35 | 105 | 49 | 0 | 3 | 55 | 1160 | 182 | 0 | 17 | 0 | 8 | 36 | 0 | 0 | 373 | 4 | 250 | 769 | 41 | 0 |  | 7202 | 5613 | 12815 | 4211 | 917 | 1884 | 0 | 2024 | 2732 | 110 | 260 | 321 | 134 | 65 | 7 | 114.6 | 80.49
18:00 | 0 | 0 | 150 | 180 | 0 | 12 | 0 | 342 | 292 |  | 0 | 320 | 0 | 66 | 96 | 15 | 250 | 0 | 76 | 77 | 33 | 64 | 23 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 21 | 25 | 23 | 8 | 0 | 80 | 30 | 120 | 0 | 8 | 219 | 0 | 0 | 0 |  | 12 | 64 | 48 | 46 | 19 | 46 | 11 | 28 | 0 | 0 | 0 | 270 | 240 | 183 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 39 | 8 | 18 | 11 | 33 | 12 | 128 | 69 | 0 | 15 | 0 | 30 | 0 | 50 | 42 | 80 | 0 | 25 | 86 | 0 | 182 | 17 | 0 | 10 | 270 | 24 | 8 | 0 | 112 | 0 | 0 | 68 | 0 | 111 | 1 | 50 | 51 | 6 | 368 | 19 | 35 | 17 | 0 | 122 | 17 | 55 | 70 | 9 | 38 | 350 | 45 | 2 | 90 | 38 | 0 | 17 | 1 | 90 | 17 | 270 | 17 | 0 | 0 | 3 | 150 |  | 918 | 0 | 205 | 0 | 16 | 120 | 0 | 0 | 10 | 50 | 8 | 120 | 21 | 46 | 0 | 0 | 0 | 0 | 20 | 48 | 21 | 42 | 0 | 8 | 9 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 150 | 0 | 269 | 35 | 0 | 35 | 50 | 49 | 0 | 1 | 55 | 1120 | 182 | 0 | 17 | 0 | 4 | 36 | 0 | 0 | 392 | 2 | 250 | 760 | 9 | 0 |  | 7099 | 5406 | 12505 | 4063 | 918 | 1705 | 0 | 2077 | 2702 | 110 | 260 | 369 | 128 | 20 | 3 | 0 | 80.49
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 323 | 336 |  | 0 | 450 | 0 | 66 | 96 | 15 | 322 | 0 | 157 | 80 | 48 | 98 | 25 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 22 | 33 | 23 | 25 | 0 | 80 | 30 | 120 | 0 | 8 | 219 | 0 | 0 | 0 |  | 12 | 57 | 51 | 68 | 22 | 46 | 11 | 37 | 0 | 0 | 0 | 270 | 240 | 196 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 44 | 8 | 19 | 11 | 33 | 12 | 124 | 69 | 0 | 16 | 0 | 30 | 0 | 50 | 45 | 0 | 0 | 25 | 86 | 0 | 183 | 17 | 0 | 10 | 290 | 24 | 8 | 0 | 112 | 50 | 0 | 87 | 0 | 134 | 0 | 100 | 54 | 22 | 405 | 84 | 105 | 17 | 0 | 200 | 17 | 55 | 106 | 57 | 88 | 350 | 53 | 0 | 90 | 53 | 0 | 17 | 0 | 112 | 17 | 270 | 60 | 0 | 0 | 1 | 150 |  | 917 | 0 | 200 | 0 | 16 | 120 | 0 | 0 | 25 | 56 | 32 | 120 | 30 | 75 | 0 | 0 | 0 | 0 | 23 | 87 | 21 | 42 | 30 | 8 | 21 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 159 | 0 | 337 | 35 | 0 | 35 | 70 | 77 | 0 | 0 | 55 | 1080 | 220 | 0 | 150 | 0 | 0 | 76 | 0 | 0 | 381 | 0 | 217 | 761 | 0 | 0 |  | 8164 | 5844 | 14008 | 4323 | 917 | 1946 | 50 | 2916 | 2659 | 110 | 260 | 552 | 124 | 0 | 1 | 150 | 80.49
19:30 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 362 | 333 |  | 0 | 450 | 0 | 66 | 96 | 15 | 326 | 0 | 155 | 80 | 92 | 130 | 25 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 22 | 33 | 23 | 25 | 0 | 80 | 30 | 122 | 0 | 17 | 221 | 0 | 0 | 0 |  | 12 | 57 | 51 | 68 | 18 | 46 | 11 | 37 | 0 | 0 | 0 | 270 | 240 | 199 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 46 | 8 | 19 | 11 | 33 | 12 | 112 | 71 | 0 | 16 | 0 | 30 | 0 | 50 | 45 | 0 | 0 | 25 | 86 | 0 | 181 | 17 | 0 | 10 | 275 | 24 | 8 | 0 | 112 | 11 | 0 | 87 | 0 | 134 | 0 | 100 | 150 | 52 | 368 | 84 | 105 | 17 | 0 | 256 | 17 | 55 | 106 | 57 | 88 | 350 | 72 | 0 | 105 | 68 | 0 | 17 | 0 | 115 | 34 | 270 | 90 | 0 | 0 | 1 | 150 |  | 914 | 0 | 200 | 0 | 16 | 120 | 0 | 0 | 40 | 60 | 32 | 118 | 31 | 80 | 0 | 0 | 0 | 35 | 24 | 90 | 21 | 42 | 36 | 8 | 22 | 0 | 0 | 8 | 0 | 0 | 219 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 179 | 0 | 341 | 35 | 50 | 70 | 105 | 78 | 0 | 0 | 55 | 1200 | 220 | 0 | 150 | 0 | 0 | 110 | 0 | 0 | 382 | 0 | 250 | 754 | 0 | 0 |  | 8470 | 6235 | 14705 | 4352 | 914 | 1933 | 61 | 3326 | 2805 | 110 | 260 | 681 | 112 | 0 | 1 | 272 | 0
20:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 367 | 331 |  | 0 | 450 | 0 | 67 | 96 | 15 | 325 | 0 | 155 | 80 | 102 | 130 | 23 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 22 | 33 | 23 | 25 | 0 | 80 | 30 | 120 | 0 | 16 | 222 | 0 | 0 | 0 |  | 12 | 57 | 50 | 68 | 20 | 46 | 11 | 39 | 0 | 0 | 0 | 270 | 240 | 202 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 46 | 8 | 19 | 11 | 33 | 12 | 96 | 93 | 0 | 16 | 0 | 30 | 0 | 50 | 42 | 112 | 0 | 25 | 86 | 0 | 183 | 17 | 0 | 10 | 270 | 24 | 8 | 0 | 112 | 0 | 0 | 88 | 0 | 135 | 0 | 100 | 118 | 52 | 368 | 84 | 105 | 17 | 0 | 259 | 17 | 55 | 106 | 55 | 88 | 350 | 72 | 0 | 108 | 68 | 0 | 17 | 0 | 114 | 34 | 270 | 143 | 0 | 0 | 6 | 150 |  | 914 | 0 | 200 | 0 | 16 | 120 | 0 | 0 | 27 | 64 | 32 | 115 | 32 | 98 | 0 | 0 | 0 | 35 | 24 | 90 | 21 | 42 | 39 | 8 | 23 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 181 | 0 | 330 | 35 | 10 | 75 | 105 | 78 | 0 | 0 | 55 | 1230 | 220 | 0 | 150 | 0 | 0 | 113 | 0 | 0 | 382 | 0 | 250 | 765 | 0 | 0 |  | 8617 | 6237 | 14854 | 4381 | 914 | 2027 | 10 | 3335 | 2837 | 110 | 260 | 728 | 96 | 0 | 6 | 139.43 | 80.49
21:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 368 | 332 |  | 0 | 450 | 0 | 66 | 85 | 15 | 327 | 0 | 193 | 80 | 102 | 130 | 21 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 19 | 22 | 33 | 23 | 25 | 0 | 80 | 30 | 120 | 0 | 22 | 221 | 0 | 0 | 0 |  | 12 | 57 | 50 | 68 | 24 | 46 | 11 | 41 | 0 | 0 | 0 | 270 | 240 | 204 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 46 | 8 | 19 | 11 | 33 | 12 | 98 | 97 | 0 | 16 | 0 | 30 | 0 | 50 | 43 | 112 | 0 | 20 | 86 | 0 | 182 | 17 | 0 | 10 | 290 | 24 | 8 | 0 | 112 | 0 | 0 | 97 | 0 | 135 | 0 | 100 | 157 | 57 | 368 | 84 | 105 | 17 | 0 | 267 | 17 | 55 | 106 | 58 | 88 | 350 | 72 | 0 | 108 | 68 | 0 | 17 | 0 | 114 | 17 | 270 | 143 | 0 | 0 | 7 | 150 |  | 912 | 0 | 205 | 0 | 16 | 120 | 0 | 0 | 22 | 53 | 32 | 120 | 34 | 110 | 0 | 0 | 0 | 35 | 31 | 90 | 21 | 42 | 38 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 181 | 0 | 414 | 35 | 0 | 95 | 105 | 78 | 0 | 0 | 55 | 1230 | 220 | 0 | 150 | 0 | 0 | 114 | 0 | 0 | 380 | 0 | 250 | 764 | 0 | 0 |  | 8707 | 6342 | 15049 | 4431 | 912 | 2137 | 0 | 3391 | 2834 | 110 | 260 | 719 | 98 | 0 | 7 | 120.33 | 80.49
22:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 368 | 328 |  | 0 | 450 | 0 | 66 | 96 | 15 | 328 | 0 | 193 | 80 | 102 | 130 | 22 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 22 | 33 | 23 | 25 | 0 | 80 | 30 | 120 | 0 | 25 | 221 | 0 | 0 | 0 |  | 12 | 57 | 50 | 68 | 24 | 46 | 11 | 42 | 0 | 0 | 0 | 270 | 240 | 205 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 46 | 8 | 19 | 11 | 33 | 12 | 100 | 96 | 0 | 16 | 0 | 30 | 0 | 47 | 48 | 112 | 0 | 20 | 84 | 0 | 183 | 17 | 0 | 10 | 280 | 24 | 8 | 0 | 112 | 0 | 0 | 97 | 0 | 135 | 0 | 100 | 155 | 62 | 367 | 84 | 105 | 17 | 0 | 268 | 17 | 55 | 106 | 58 | 88 | 350 | 72 | 0 | 108 | 68 | 0 | 17 | 0 | 114 | 17 | 270 | 143 | 0 | 0 | 9 | 150 |  | 914 | 0 | 205 | 0 | 16 | 120 | 0 | 0 | 22 | 50 | 32 | 120 | 35 | 110 | 0 | 0 | 0 | 35 | 24 | 90 | 21 | 42 | 38 | 8 | 25 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 179 | 0 | 414 | 35 | 0 | 95 | 105 | 78 | 0 | 0 | 55 | 1244 | 220 | 0 | 150 | 0 | 0 | 114 | 0 | 0 | 382 | 0 | 250 | 766 | 0 | 0 |  | 8738 | 6322 | 15060 | 4430 | 914 | 2125 | 0 | 3430 | 2822 | 110 | 260 | 710 | 100 | 0 | 9 | 133.7 | 80.49
23:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 392 | 328 |  | 0 | 450 | 0 | 67 | 96 | 15 | 330 | 0 | 197 | 80 | 34 | 130 | 22 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 19 | 22 | 33 | 23 | 25 | 0 | 80 | 30 | 120 | 0 | 8 | 225 | 0 | 0 | 0 |  | 12 | 57 | 50 | 68 | 0 | 46 | 11 | 42 | 0 | 0 | 0 | 270 | 240 | 206 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 38 | 8 | 20 | 11 | 33 | 15 | 104 | 97 | 0 | 16 | 0 | 30 | 0 | 47 | 48 | 112 | 0 | 25 | 84 | 0 | 185 | 17 | 0 | 10 | 300 | 24 | 5 | 0 | 112 | 33 | 0 | 68 | 0 | 97 | 0 | 100 | 155 | 62 | 367 | 19 | 105 | 17 | 0 | 268 | 17 | 55 | 106 | 57 | 88 | 350 | 72 | 0 | 108 | 68 | 0 | 17 | 0 | 68 | 17 | 270 | 17 | 0 | 0 | 5 | 150 |  | 914 | 0 | 195 | 0 | 16 | 120 | 0 | 0 | 21 | 50 | 24 | 120 | 35 | 110 | 0 | 0 | 0 | 34 | 24 | 90 | 21 | 42 | 38 | 8 | 25 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 176 | 0 | 414 | 35 | 54 | 95 | 105 | 78 | 0 | 0 | 55 | 1244 | 220 | 0 | 150 | 0 | 0 | 114 | 0 | 0 | 381 | 0 | 250 | 763 | 0 | 0 |  | 8394 | 6349 | 14743 | 4461 | 914 | 2145 | 87 | 3115 | 2818 | 110 | 260 | 574 | 104 | 0 | 5 | 340.935 | 80.49
24:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 381 | 328 |  | 0 | 450 | 0 | 67 | 95 | 15 | 331 | 0 | 195 | 80 | 16 | 130 | 22 | 0 | 0 | 0 | 17 | 0 | 35 | 19 | 19 | 22 | 33 | 24 | 8 | 0 | 80 | 30 | 120 | 0 | 8 | 222 | 0 | 0 | 0 |  | 12 | 50 | 50 | 47 | 0 | 46 | 11 | 42 | 0 | 0 | 0 | 270 | 240 | 199 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 38 | 8 | 20 | 11 | 33 | 14 | 106 | 97 | 0 | 16 | 0 | 30 | 0 | 47 | 48 | 112 | 0 | 20 | 84 | 0 | 185 | 17 | 0 | 10 | 295 | 24 | 5 | 0 | 115 | 206 | 0 | 68 | 0 | 39 | 0 | 25 | 70 | 12 | 355 | 19 | 35 | 17 | 0 | 158 | 17 | 55 | 17 | 9 | 88 | 350 | 52 | 0 | 17 | 68 | 0 | 17 | 0 | 48 | 17 | 270 | 17 | 0 | 0 | 2 | 150 |  | 914 | 0 | 190 | 0 | 16 | 120 | 0 | 0 | 11 | 50 | 24 | 132 | 35 | 110 | 0 | 0 | 0 | 0 | 24 | 0 | 21 | 42 | 24 | 8 | 25 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 172 | 0 | 414 | 35 | 200 | 35 | 105 | 34 | 0 | 0 | 55 | 1244 | 220 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 250 | 760 | 0 | 0 |  | 7692 | 6130 | 13822 | 4425 | 914 | 2140 | 406 | 2074 | 2816 | 110 | 260 | 419 | 106 | 0 | 2 | 1029.49 | 80.49
KWH | 0 | 0 | 4706406 | 4315500 | 0 | 145318 | 0 | 8730620 | 7744000 |  | 0 | 9715500 | 1005644 | 1171200 | 1563928 | 366311 | 7600458 | 0 | 3726000 | 1047360 | 978192 | 1949280 | 305433 | 0 | 0 | 0 | 387360 | 537422 | 509562 | 436068 | 456000 | 475920 | 662200 | 565100 | 696000 | 0 | 1897800 | 768000 | 2800000 | 0 | 244371 | 5253865 | 0 | 0 | 0 |  | 223440 | 1010640 | 1143539 | 1269840 | 149760 | 476640 | 242544 | 842400 | 0 | 0 | 0 | 7006800 | 5956000 | 4805000 | 33454 | 0 | 13392 | 0 | 0 | 972128 | 0 | 818544 | 203179 | 378936 | 246060 | 755000 | 332500 | 2877120 | 1942080 | 0 | 390744 | 11550 | 716000 | 0 | 1185000 | 1031112 | 2357918 | 0 | 551808 | 1938240 | 0 | 4441360 | 392000 | 0 | 252000 | 7036500 | 565776 | 186432 | 0 | 2581855 | 194218 | 0 | 1716000 | 0 | 1717632 | 83565 | 1163520 | 1414080 | 361309 | 9020000 | 706800 | 1183680 | 420690 | 34680 | 3414873 | 621887 | 1042940 | 1407900 | 462840 | 1336320 | 8418200 | 1207680 | 227830 | 1553760 | 1045036 | 0 | 439560 | 206061 | 1389120 | 455400 | 6647900 | 861454 | 0 | 0 | 142080 | 1182545 |  | 21786181 | 0 | 5355648 | 0 | 239040 | 3001066 | 0 | 0 | 180960 | 524288 | 378000 | 3013000 | 626626 | 1013 | 0 | 0 | 0 | 148991 | 177172 | 724040 | 483630 | 401999 | 204557 | 200501 | 245840 | 0 | 0 | 178704 | 0 | 0 | 4772600 | 0 | 0 | 0 | 0 | 0 | 3626609 | 0 | 0 | 4407882 | 0 | 9041090 | 847680 | 260485 | 1145952 | 1735632 | 1093238 | 0 | 41737 | 1144608 | 30518500 | 4979918 | 0 | 1603200 | 34920 | 304560 | 846528 | 0 | 0 | 10560000 | 90943 | 5890900 | 18245455 | 1181110 | 0 |  | 176177669 | 140244803 | 316422472 | 105691903 | 21786181 | 48906848 | 454703 | 45893901 | 69987455 | 2665800 | 6627675 | 7989305 | 2877120 | 2216956 | 142080 | 0
Fuel Cost | 0 | 0 | 6871352.76 | 6430095 | 0 | 193272.94 | 0 | 9167151 | 8363520 |  | 0 | 10589895 | 1116264.84 | 13094016 | 20722046 | 4853620.75 | 8512512.96 | 0 | 6520500 | 15312403.2 | 13763161.44 | 31597828.8 | 2816092.26 | 0 | 0 | 0 | 4927219.2 | 7255197 | 6833226.42 | 327051 | 342000 | 0 | 0 | 0 | 11838960 | 0 | 512406 | 207360 | 5292000 | 0 | 3995465.85 | 5464019.6 | 0 | 0 | 0 |  | 2915892 | 16857475.2 | 19463033.78 | 17155538.4 | 1898956.8 | 5514724.8 | 308030.88 | 2805192 | 0 | 0 | 0 | 7777548 | 6492040 | 5573800 | 43155.66 | 0 | 15132.96 | 0 | 0 | 1623453.76 | 0 | 14136254.88 | 2732757.55 | 519142.32 | 184545 | 1321250 | 249375 | 20657721.6 | 2116867.2 | 0 | 531411.84 | 184107 | 980920 | 0 | 2061900 | 1783823.76 | 2711605.7 | 0 | 1070507.52 | 4419187.2 | 0 | 4485773.6 | 842800 | 0 | 498960 | 7036500 | 424332 | 141688.32 | 0 | 35242320.75 | 4070809.28 | 0 | 23131680 | 0 | 23789203.2 | 976874.85 | 12007526.4 | 19316332.8 | 4794570.43 | 8298400 | 8594688 | 17116012.8 | 5321728.5 | 0 | 40090609.02 | 6772349.43 | 11086452.2 | 19105203 | 5966007.6 | 15741849.6 | 7744744 | 15639456 | 3292143.5 | 19717214.4 | 11892509.68 | 0 | 5740653.6 | 2462428.95 | 20795126.4 | 5997618 | 0 | 0 | 0 | 0 | 0 | 0 |  | 65358543 | 0 | 5998325.76 | 0 | 2488406.4 | 49517589 | 0 | 0 | 3259089.6 | 9437184 | 5431860 | 3374560 | 1215654.44 | 11041.7 | 0 | 0 | 0 | 2498579.07 | 3098738.28 | 11323985.6 | 3723951 | 6657103.44 | 3459058.87 | 2732828.63 | 4147320.8 | 0 | 0 | 135278.928 | 0 | 0 | 25247054 | 0 | 0 | 0 | 0 | 0 | 63320593.14 | 0 | 0 | 5113143.12 | 0 | 8950679.1 | 11392819.2 | 5462370.45 | 13556612.16 | 25079882.4 | 13884122.6 | 0 | 461193.85 | 13895541.12 | 274971685 | 5079516.36 | 0 | 11863680 | 394945.2 | 3572488.8 | 12977274.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 719158555.14 | 679092699.258 | 1398251254.398 | 112626298.768 | 65358543 | 58492580.76 | 9533179.73 | 587183512.37 | 300218739 | 719766 | 112838182.14 | 119278548.88 | 20657721.6 | 11344182.15 | 0 | 0
Yesterday Day Peak | 0 | 0 | 180 | 180 | 0 | 6 | 0 | 367 | 326 |  | 0 | 450 | 0 | 45 | 20 | 15 | 326 | 0 | 193 | 12 | 25 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 19 | 20 | 25 | 24 | 52 | 0 | 80 | 30 | 122 | 0 | 8 | 218 | 0 | 0 | 0 |  | 6 | 32 | 46 | 46 | 0 | 6 | 11 | 26 | 0 | 0 | 0 | 270 | 270 | 153 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 24 | 8 | 16 | 11 | 33 | 12 | 120 | 66 | 0 | 18 | 1 | 30 | 0 | 47 | 40 | 112 | 0 | 25 | 78 | 0 | 185 | 17 | 0 | 10 | 300 | 24 | 8 | 0 | 80 | 0 | 0 | 68 | 0 | 70 | 18 | 50 | 0 | 5 | 368 | 19 | 35 | 17 | 5 | 122 | 17 | 17 | 70 | 28 | 38 | 350 | 53 | 28 | 54 | 34 | 0 | 3 | 35 | 72 | 17 | 270 | 17 | 0 | 0 | 1 | 18 |  | 912 | 0 | 240 | 0 | 8 | 120 | 0 | 0 | 0 | 0 | 24 | 130 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 208 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 163 | 0 | 414 | 35 | 0 | 35 | 25 | 28 | 0 | 7 | 35 | 1130 | 221 | 0 | 17 | 5 | 13 | 36 | 0 | 0 | 414 | 16 | 250 | 756 | 144 | 0 |  | 12587 | DayPeak
Yesterday Evening Peak | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 368 | 332 | 0 | 0 | 450 | 0 | 66 | 85 | 15 | 327 | 0 | 193 | 80 | 102 | 130 | 21 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 19 | 22 | 33 | 23 | 25 | 0 | 80 | 30 | 120 | 0 | 22 | 221 | 0 | 0 | 0 | 0 | 12 | 57 | 50 | 68 | 24 | 46 | 11 | 41 | 0 | 0 | 0 | 270 | 240 | 204 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 46 | 8 | 19 | 11 | 33 | 12 | 98 | 97 | 0 | 16 | 0 | 30 | 0 | 50 | 43 | 112 | 0 | 20 | 86 | 0 | 182 | 17 | 0 | 10 | 290 | 24 | 8 | 0 | 112 | 0 | 0 | 97 | 0 | 135 | 0 | 100 | 157 | 57 | 368 | 84 | 105 | 17 | 0 | 267 | 17 | 55 | 106 | 58 | 88 | 350 | 72 | 0 | 108 | 68 | 0 | 17 | 0 | 114 | 17 | 270 | 143 | 0 | 0 | 7 | 150 |  | 912 | 0 | 205 | 0 | 16 | 120 | 0 | 0 | 22 | 53 | 32 | 120 | 34 | 110 | 0 | 0 | 0 | 35 | 31 | 90 | 21 | 42 | 38 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 181 | 0 | 414 | 35 | 0 | 95 | 105 | 78 | 0 | 0 | 55 | 1230 | 220 | 0 | 150 | 0 | 0 | 114 | 0 | 0 | 380 | 0 | 250 | 764 | 0 | 0 |  | 15049 | EvPeak
Forecast for Evening | 0 | 0 | 210 | 180 | 0 | 0 | 0 | 370 | 330 | 0 | 0 | 450 | 0 | 64 | 96 | 15 | 330 | 0 | 195 | 80 | 84 | 130 | 22 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 22 | 33 | 24 | 51 | 0 | 80 | 30 | 120 | 0 | 25 | 225 |  | 0 | 0 | 0 | 12 | 64 | 50 | 70 | 24 | 46 | 11 | 35 | 0 | 0 | 0 | 270 | 240 | 200 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 46 | 43 | 20 | 11 | 33 | 20 | 169 | 98 | 0 | 18 | 0 | 30 | 0 | 50 | 48 | 112 | 0 | 30 | 86 | 0 | 185 | 17 | 0 | 10 | 300 | 24 | 11 | 0 | 115 | 300 | 0 | 98 | 0 | 149 | 0 | 100 | 150 | 60 | 400 | 85 | 105 | 97 | 0 | 300 | 17 | 54 | 17 | 75 | 88 | 350 | 72 | 0 | 162 | 68 | 0 | 17 |  | 115 | 34 | 270 | 163 |  | 0 | 10 | 0 |  | 930 | 0 | 235 |  | 16 | 120 | 0 | 0 | 30 | 55 | 40 | 120 | 34 | 110 | 0 | 0 | 0 | 35 | 32 | 93 | 21 | 42 | 35 | 8 | 25 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 |  | 0 | 140 | 0 | 0 | 181 | 0 | 414 | 35 | 200 | 95 | 105 | 78 | 0 | 0 | 55 | 1244 | 220 |  | 150 |  |  | 113 | 0 |  | 0 |  | 250 | 750 |  | 0
Forecast for Day | 0 | 0 | 210 | 180 | 0 | 0 | 0 | 350 | 300 | 0 | 0 | 450 | 0 | 50 | 96 | 15 | 330 | 0 | 195 | 25 | 32 | 64 | 11 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 19 | 22 | 33 | 24 | 51 | 0 | 80 | 30 | 120 | 0 | 8 | 220 |  | 0 | 0 | 0 | 6 | 40 | 50 | 45 | 0 | 6 | 11 | 20 | 0 | 0 | 0 | 270 | 240 | 190 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 44 | 43 | 20 | 11 | 33 | 20 | 146 | 50 | 0 | 18 | 1.6 | 30 | 0 | 50 | 48 | 112 | 0 | 30 | 80 | 0 | 185 | 17 | 0 | 10 | 300 | 24 | 11 | 0 | 112 | 150 | 0 | 68 | 0 | 70 | 20 | 50 | 51 | 6 | 400 | 18 | 35 | 97 | 5 | 120 | 17 | 54 | 17 | 27 | 38 | 350 | 53 | 50 | 54 | 34 | 0 | 17 | 35 | 72 | 17 | 270 | 52 |  | 0 | 20 | 0 |  | 930 | 0 | 235 | 0 | 16 | 120 | 0 | 0 | 20 | 40 | 32 | 120 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 34 | 35 | 8 | 25 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 160 | 0 | 414 | 35 | 200 | 35 | 70 | 34 | 0 | 8 | 35 | 1244 | 220 |  | 17 | 6 | 100 | 35 | 0 |  | 0 | 30 | 250 | 750 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 378 | 332 | 0 | 0 | 450 | 0 | 49 | 96 | 15 | 326 | 0 | 185 | 50 | 25 | 48 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 22 | 33 | 24 | 8 | 0 | 80 | 30 | 119 | 0 | 8 | 220 | 0 | 0 | 0 | 0 | 6 | 33 | 50 | 47 | 0 | 6 | 11 | 16 | 0 | 0 | 0 | 270 | 240 | 192 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 38 | 8 | 18 | 11 | 33 | 12 | 84 | 44 | 0 | 13 | 1 | 30 | 0 | 45 | 41 | 112 | 0 | 27 | 75 | 0 | 185 | 17 | 0 | 10 | 315 | 24 | 11 | 0 | 112 | 0 | 0 | 68 | 0 | 36 | 10 | 25 | 34 | 5 | 403 | 19 | 35 | 17 | 3 | 88 | 17 | 74 | 17 | 9 | 38 | 350 | 53 | 25 | 17 | 34 | 0 | 17 | 15 | 18 | 17 | 270 | 17 | 0 | 0 | 1 | 150 | 0 | 913 | 0 | 170 | 0 | 16 | 120 | 0 | 0 | 11 | 20 | 24 | 120 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 163 | 0 | 414 | 35 | 0 | 35 | 105 | 34 | 0 | 0 | 35 | 1230 | 220 | 0 | 17 | 1 | 31 | 0 | 0 | 0 | 0 | 1 | 250 | 760 | 58 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
292.3904
| Minimum Generation |  | 11678 | 8:00
| Highest Generation |  | 15060 | 22:00
| Day Peak Generation |  | 12587 | 12:00
| Evening Peak Generation |  | 15049 | 21:00
| HVDC Max Flow |  | 918 | 14:00
| HVDC EvPeak Flow |  | 912 | 21:00
| Load factor L.F |  | 87.54% | [164 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-07-30
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-07-29 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 12587 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 12232
Evening Peak Generation : |  |  | 15049 | MW Hour : | 21:00 | Available Max Generation : |  | 15455
E.P. Demand (at gen end) : |  |  | 15175 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 15700
Maximum Generation : |  |  | 15060 | MW Hour : | 22:00 | Reserve(Generation end) |  | -
Total Gen. (MKWH) : |  |  | 315.2399 | System Load Factor : | 87.54% | Load Shed : |  | 226
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 604 | MW at | 20:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-07-30
Actual : |  | 80.5 | Ft.(MSL) , | Rule curve : | 88.66 | Ft.( MSL )
Gas Consumed : |  | Total = | 1178.29 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 171118879.528
: |  |  | Coal : | 300218739 | Oil : | 828833423.12 | Total : | 1300171041.648
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 25 | 600:00 | 4857.5703 |  |  | 65 | 1.338%
Chittagong Area |  | 0 | 0:00 | 1336.484 |  |  | 27 | 2.02%
Khulna Area |  | 0 | 0:00 | 1872.677 |  |  | 28 | 1.495%
Rajshahi Area |  | 0 | 0:00 | 1628.1782 |  |  | 22 | 1.351%
Cumilla Area |  | 32 | 768:00 | 1339.4547 |  |  | 22 | 1.642%
Mymensingh Area |  | 52 | 1248:00 | 996.477 |  |  | 20 | 2.007%
Sylhet Area |  | 11 | 264:00 | 558.2777 |  |  | 12 | 2.149%
Barisal Area |  | 0 | 0:00 | 465.5121 |  |  | 10 | 2.148%
Rangpur Area |  | 0 | 0:00 | 910.4541 |  |  | 20 | 2.197%
Total |  | 120 |  | 13965.0851 |  |  | 226
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar-9
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:34 |  | Meghnaghat Summit CCPP GT1 tripped
08:35 | 09:24 | Fenchuganj 230/132/33kV S/S TR-01 HT Scheduled S/D Due to OLTC Silica Gel changing.
08:35 | 09:24 | Fenchuganj 230/132/33kV S/S TR-01 LT Scheduled S/D Due to OLTC Silica Gel changing.
08:53 |  | Meghnaghat Summit CCPP ST tripped
09:11 |  | Meghnaghat Summit CCPP GT2 was forced shutdown
| 09:20 | Kabirpur 132/33kV S/S Main bus is restored.
| 09:51 | Kabirpur - Manikganj 132kV Ckt-1 is restored.
11:51 | 13:08 | Agargaon 230/132kV S/S 230kV Transformer-1 ( 705T1) HT Tripped showing Differential Relay relays Due to
When the Auxiliary drop out fuse is installed it bursts at 33kv LA.
11:51 | 13:09 | Agargaon 230/132kV S/S 230kV Transformer-1 ( 705T1) LT Tripped showing Differential Relay relays Due to
When the Auxiliary drop out fuse is installed it bursts at 33kv LA.
11:58 |  | Matarbari Unit-1 was sync.
12:00 |  | Day Peak Generation = 12,587MW
| 13:30 | Lalmonirhat 132/33kV S/S Transformer T-1 425T HT is restored.
| 13:30 | Lalmonirhat 132/33kV S/S Transformer T-1 425T LT is restored.
| 18:24 | Magura 132/33kV S/S T-3 HT is restored.
18:25 |  | AKSML-Baroaulia 132kV Ckt-1 Forced S/D from AKS 132/33kV end Due to R-phase CT leakage.
18:25 |  | AKS 132/33kV S/S Bus Coupler Forced S/D Due to R- phase CT leakage
18:40 | 18:51 | Bhaluka 132/33kV S/S Transformer- 02 LT Tripped showing Alston, P40 Agile relays Due to 33 kv pbs feeder trip |  |  |  |  | 64.0MW load interrup.
18:40 | 18:51 | Bhaluka 132/33kV S/S Transformer- 01 LT Tripped showing Alstom, p40 Agile relays Due to 33 kv pbs feeder trip |  |  |  |  | 64.0MW load interrup.
18:48 |  | Kushiara 163MW tripped |  |  |  |  | 110MW generation interrup.
19:34 |  | Kushiara 163MW GT was sync.
20:30 | 21:26 | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-1 Forced S/D from Bog-Sherpur 132/33kV end Due to recommendation
by ALDC
20:31 |  | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-2 Forced S/D from Bog-Sherpur 132/33kV end Due to recommendation
by ALDC
21:00 |  | Evening Peak Gen. 15050 MW
03:15 |  | Magura T3 Transformer S/D.
03:38 |  | Rampal 1320 MW (BIFPCL) unit-1 was forced shutdown due to coal shortage. |  |  |  |  | 660MW generation interrup.
04:00 |  | Minimum Generation: 12237 MW
06:17 |  | Chandpur 132/33kV S/S 422T LT Scheduled S/D Due to For 33 KV T-5 Bus section red Hot maintenance |  |  |  |  | 33.0MW load interrup.
06:18 |  | Chandpur 132/33kV S/S 422T HT Scheduled S/D Due to For 33 KV T-5 Bus section red Hot maintenance |  |  |  |  | 33.0MW load interrup.
07:14 |  | Hathazari 230/132/33kV S/S T-02 HT Forced S/D Due to PDB and PBS 33 kv bus-01 S/D for emergency disk insuletor |  |  |  |  | 33.0MW load interrup.
replacement work.
07:15 |  | Hathazari 230/132/33kV S/S T-02 LT Forced S/D Due to PDB and PBS 33 kv bus-01 S/D for emergency disk insuletor |  |  |  |  | 33.0MW load interrup.
replacement work.
07:16 |  | Kushtia 132/33kV S/S T2 LT Forced S/D Due to Redhot maintenance . |  |  |  |  | 30.0MW load interrup.
07:17 |  | Kushtia 132/33kV S/S T2 HT Forced S/D Due to Redhot maintenance . |  |  |  |  | 30.0MW load interrup.
07:28 |  | Naogaon 132/33kV S/S T-3 LT Forced S/D Due to T-3 33 kv C.B Maintanance.(SF6 GAS Lekage)
07:35 |  | Naogaon 132/33kV S/S T-3 HT Forced S/D Due to T-3 33 kv C.B Maintanance.(SF6 GAS Lekage)
06:30 |  | Kabirpur 132/33kV S/S Main bus Scheduled S/D Due to Red hot maintenance of 132 KV Manikganj-1, B phase CT
conductor & main bus isolator bus side connector
06:31 |  | Kabirpur - Manikganj 132kV Ckt-1 Scheduled S/D from Kabirpur 132/33kV end Due to Red Hot maintenance
07:00 |  | Minimum generation 11818 MW

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-07-29 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 210 | 4706406
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4315500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 145318 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 368 | 8730620 | Machine problem
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 332 | 7744000 | Machine problem
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9715500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 66 | 1171200 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 1005644 | Under maint.
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 85 | 1563928 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 366311 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 21 | 305433 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 436068 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 193 | 3726000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 80 | 1047360 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 327 | 7600458
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 978192
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 387360 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 130 | 1949280 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 537422 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 509562 | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 41 | 931920 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 662200 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 23 | 565100 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 696000 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 112 | 2581855 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 194218 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 135 | 1717632 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1183680
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 72 | 1207680 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 1553760 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 206061
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 455400 | Fuel shortage
| Dhaka area Total |  |  |  | 5722 | 3366 | 68897068
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2800000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 22 | 244371 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 83565
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 46 | 476640 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 110 | 2665800 | Low Water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 221 | 5253865
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 420690 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 57 | 1010640 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 1143539 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 68 | 1269840 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1163520
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 11 | 242544 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 41 | 842400
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 24 | 149760 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 34680
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 267 | 3414873 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 621887 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 55 | 1042940 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 88 | 1336320 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 68 | 1045036 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 143 | 861454 | Engine problem
| SS Power I |  | SS Power | 0 | 0 | 0 | 0 | On test.
| Cox's Bazar Wind |  | IPP | 66 | 0 | 7 | 142080 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 150 | 1182545 | On test.
| Chattogram area Total |  |  |  | 2545 | 1682 | 27448989
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 204 | 4805000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 270 | 7006800 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 240 | 5956000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 270 | 6647900 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 0 | 13392 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 33454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 972128 | Engine problem
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 57 | 361309 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 46 | 818544 | Machine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 157 | 1414080 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 378936
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 246060
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 98 | 2877120 | Restriction by India
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 755000
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 203179 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 12 | 332500 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 106 | 1407900 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 58 | 462840 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 439560 | Fuel shortage
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 114 | 1389120
| Cumilla Area Total |  |  |  | 3096 | 1763 | 36520822
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 97 | 1942080 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 390744 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11550
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 97 | 1716000 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 84 | 706800 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 227830
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 223440 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 306 | 5218444
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 716000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2357918 | ST under maint
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1185000
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 43 | 1031112
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 186432
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 20 | 551808
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1938240
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 182 | 4441360 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 392000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 565776
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7036500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 368 | 9020000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 252000
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 350 | 8418200
| Sylhet Area Total |  |  |  | 2427 | 1590 | 38092346
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 912 | 21786181
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 239040 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 22 | 180960 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 120 | 3001066 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 53 | 524288 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 205 | 5355648 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 32 | 378000 | Engine problem
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 847680 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 1735632
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 304560
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 220 | 0 | 0 | Reserve
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 380 | 10560000 | Coal shortage.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 3121 | 1880 | 44913055
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1013 | High voltage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 34 | 626626 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 120 | 3013000 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1230 | 30518500
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4979918
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1603200
| Barisal 307 MW |  | IPP | 307*1 | 307 | 250 | 5890900 | Coal shortage.
| Barisal Area Total |  |  |  | 2265 | 2114 | 46633157
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 35 | 148991 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 31 | 177172 | Fuel shortage
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 21 | 483630 | Fuel shortage
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 401999 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 204557 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Under maint.
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 140 | 3626609
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 181 | 4407882 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 9041090 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 245840 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 178704 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 200501
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 724040 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 260485 | Fuel conservation
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 95 | 1145952 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 55 | 1144608 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 34920
| Adani Power Jharkhanda Ltd |  | Import | 748*2 | 1496 | 764 | 18245455
| Rajshahi Area Total |  |  |  | 3631 | 1946 | 40672435
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 210 | 4772600 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 78 | 1093238 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 41737
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 114 | 846528
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 90943
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 1181110
| Rangpur Area Total |  |  |  | 750 | 402 | 8026156
| Total |  |  |  | 24171 | 15049 | 316422472
| Eastern Grid Total |  |  |  | 14404 | 8707 | 176177669
| Western Grid Total |  |  |  | 9767 | 6342 | 140244803
| National Grid Total |  |  |  | 24171 | 15049 | 316422472
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-07-29
| (a) ENTIRE EASTERN GRID : |  | 9445.82 | MW | (b) ENTIRE WESTERN GRID : |  | 4897.8 | MW
| i) Dhaka area |  | 4895.32 | MW | i) Khulna area |  | 1785.2 | MW
| ii) Chittagong area |  | 1355.5 | MW | ii) Rajshahi area |  | 1645.2 | MW
| iii) Comilla area |  | 1415 | MW | iii) Barisal area |  | 474.4 | MW
| iv) Mymensingh area |  | 1169 | MW | iv) Rangpur area |  | 993 | MW
| v) Sylhet area |  | 611 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 14343.62 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 21 | 15:00 | Chhatak | 34 | 19:30 | Kamrangirchar | 43.92 | 01:00 | Natore | 161 | 23:00 | Sholosohor | 34 | 19:00
2 | AKSML | 84 | 07:00 | Chowmuhani | 241 | 19:30 | Kaptai | N/A | N/A | Nawabganj | 51 | 22:00 | Shyampur | 156 | 13:00
3 | Aftabnagar | 36 | 23:00 | Chuadanga | 121 | 21:00 | Kazla | 87 | 12:00 | Netrakona | 144 | 22:00 | Siddhirganj | 110 | 09:00
4 | Agargaon | 84 | 23:00 | Coxsbazar | 128 | 19:30 | Keranigonj | 74 | 00:00 | New | 80 | 12:00 | Sirajganj | 122 | 20:00
5 | Agrabad | 66 | 19:30 | Cumilla(N) | 197 | 19:30 | Khagrachori | 32 | 19:00 | Niamatpur | 100 | 00:00 | Sonargaon | 85 | 16:00
6 | Amnura | 72 | 21:00 | Cumilla(S) | 142 | 03:00 | Khulna | 98 | 22:00 | Noapara | 49 | 20:00 | Sreemongol | 72 | 22:00
7 | Ashuganj | 74 | 00:00 | Daudkandi | 149 | 20:00 | Khulshi | 183 | 19:30 | PHP | 4 | 17:00 | Sreepur | 76 | 09:00
8 | BIPTC | N/A | N/A | Dhaka | 18 | 13:00 | Kishoreganj | 146 | 19:00 | Pabna | 127 | 21:00 | Srinagar | 48.55 | 23:00
9 | BSRM | 160 | 02:00 | Dhamrai | 124 | 15:00 | Kodda | 302 | 10:00 | Palashbari | 138 | 19:30 | Sunamganj | 63 | 22:00
10 | Bagerhat | 95 | 22:00 | Dhanmondi | 120 | 13:00 | Kulaura | 60 | 21:00 | Panchagarh | 60 | 19:30 | Sylhet | 171 | 22:00
11 | Bakulia | 95 | 20:00 | Dohazari | 106 | 00:00 | Kurigram | 67 | 19:30 | Patuakhali | 116 | 23:00 | TK | 33.5 | 21:00
12 | Banani | 33 | 15:00 | Faridpur | 166 | 22:00 | Kushtia | 144 | 19:30 | Payra | 24 | 23:00 | Tangail | 242 | 22:00
13 | Bangabhaban | 6 | 12:00 | Fatullah | 63 | 10:00 | Lalbag | 63 | 19:00 | Postogola | 57 | 23:00 | Thakurgaon | 108 | 22:00
14 | Barapukuria | 68 | 19:30 | Fenchuganj | 49 | 22:00 | Lalmonirhat | 56 | 21:00 | Purbachal | 21 | 21:00 | Tongi | 111 | 15:00
15 | Barguna | 22 | 22:00 | Feni | 122 | 19:00 | Madanganj | 39 | 19:00 | Purbasadipur | 142 | 20:00 | Ullon | 42 | 20:00
16 | Barishal | 106 | 23:00 | GPH | 91 | 10:00 | Madaripur | 108 | 22:00 | Rahim | 36 | 09:00 | Uttara | 68 | 19:30
17 | Barishal-230 | 106 | 22:00 | Ghorashal | 76 | 21:00 | Madartek | 90.5 | 23:00 | Rajbari | 76 | 23:00 | UttaraNew | 65 | 19:00
18 | Baroaulia | 65 | 00:00 | Goalpara | 36 | 00:00 | Madunaghat | 56 | 19:00 | Rajendrapur | 104 | 15:00 | Zigatola | 89 | 20:00
19 | Baroirhat | 60 | 20:00 | Gollamari | 51 | 00:00 | Magura | 74 | 19:30 | Rajshahi | 185 | 23:00
20 | Bashundhara | 160 | 19:00 | Gopalganj | 106.8 | 00:00 | Mahasthangarh | 80 | 22:00 | Rajshahi-230 | 43 | 22:00
21 | BashundharaCement | 0 | 00:00 | Gulshan | 100 | 15:00 | Manikganj | 113 | 21:00 | Ramganj | 122 | 21:00
22 | Beanibazar | 80 | 20:00 | Halishahar | 77.5 | 20:00 | Maniknagar | 74 | 00:00 | Rampur | 31 | 00:00
23 | Benapole | 66 | 20:00 | HaripurSBU | 146 | 09:00 | Matarbari | 47 | 20:00 | Rangamati | 20 | 19:00
24 | Bhaluka | 136 | 16:00 | Hasnabad | 83 | 22:00 | Matuail | 69 | 10:00 | Rangpur | 156 | 18:30
25 | Bhandaria | 56 | 21:00 | Hathazari | 78 | 21:00 | Millgate | 95 | 15:00 | Ruppur | 3.8 | 10:00
26 | Bhangura | 38 | 22:00 | Ishurdi | 77 | 21:00 | Mirpur | 137 | 19:00 | SSM | 0 | 00:00
27 | Bheramara(GK) | 68 | 22:00 | Jaldhaka | 80 | 19:30 | Mirsorai | 4 | 00:00 | Saidpur | 114 | 19:30
28 | Bhulta | 265 | 12:00 | Jamalpur | 169 | 20:00 | Mithapukur | 44 | 19:30 | Satkhira | 131 | 21:00
29 | Bog-Sherpur | 72 | 19:30 | Jashore | 148 | 19:00 | Modern | 0 | 00:00 | Satmasjid | 105 | 19:30
30 | Bogura | 190 | 21:00 | Jhenaidah | 145 | 19:30 | Mogbazar | 111.7 | 19:00 | Savar | 180 | 19:00
31 | Borhanuddin | 62 | 00:00 | Joydebpur | 168 | 19:30 | Mongla | 30 | 15:00 | Shahjadpur | 108 | 21:00
32 | Brahmanbaria | 152 | 21:00 | Joypurhat | 66 | 23:00 | Motijheel | 34 | 19:00 | Shahjibazar | 126 | 20:00
33 | Cantonment | 134 | 19:00 | Juldah | 24 | 00:00 | Munshiganj | 114 | 00:00 | Shahmirpur | 43 | 22:00
34 | Chandpur | 82 | 20:00 | KSRM | 25 | 02:00 | Mymensingh | 243 | 19:00 | Shariatpur | 88 | 22:00
35 | Chandraghona | 33 | 23:00 | Kabirpur | 276 | 11:00 | Naogaon | 155 | 23:00 | Sherpur | 150 | 21:00
36 | Chapai | 84 | 21:00 | Kachua | 92 | 22:00 | Narail | 60 | 19:30 | Shikalbaha | 28 | 23:00
37 | Charsaidpur | 45 | 00:00 | Kallyanpur | 111 | 13:00 | Narinda | 56 | 19:00 | Shikalbaha-230 | N/A | N/A
38 | Chauddagram | 63 | 21:00 | Kalurghat | 32 | 10:00 | Narshingdi | 184 | 00:00 | Shitalakhya | 95.3 | 12:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-07-29 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 398 | 06:00 | 390 | 11:00 | Gopalganj | 405 | 18:00 | 396 | 01:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 381 | 18:00 | 372 | 11:00
| Bhulta | 397 | 06:00 | 388 | 15:00 | Madunaghat_I | 390 | 19:30 | 374 | 11:00
| Bibiana | 405 | 13:00 | 397 | 13:00 | Payra | 411 | 18:30 | 407 | 02:00
| BIPTC | 401 | 06:00 | 391 | 23:00 | Rampal | 407 | 18:00 | 399 | 00:00
| Bogura | N/A | N/A | N/A | N/A
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 233 | 00:00 | 227 | 11:00 | Hasnabad | 233 | 00:00 | 225 | 10:00
| AKSML | 233 | 21:00 | 224 | 14:00 | Hathazari | 234 | 23:00 | 225 | 11:00
| Aminbazar | 234 | 00:00 | 229 | 12:00 | Ishurdi | 235 | 18:00 | 225 | 19:30
| Ashuganj | 233 | 00:00 | 229 | 15:00 | Jhenaidah | 228 | 18:00 | 216 | 19:30
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 234 | 18:00 | 228 | 11:00
| Baghabari | 229 | 16:00 | 222 | 21:00 | Keranigonj | 232 | 00:00 | 226 | 11:00
| Barapukuria | 216 | 11:00 | 204 | 21:00 | Khulna(S) | 234 | 17:00 | 225 | 21:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | 235 | 19:00 | 225 | 11:00
| Barishal | 236 | 07:00 | 232 | 00:00 | Maniknagar | 231 | 00:00 | 226 | 11:00
| Bheramara | 232 | 17:00 | 223 | 19:30 | Meghnaghat | 238 | 01:00 | 232 | 09:00
| Bhulta | 235 | 06:00 | 229 | 15:00 | Mirsorai | 237 | 00:00 | 223 | 09:00
| Bibiana | 234 | 00:00 | 228 | 10:00 | Rajshahi | 230 | 17:00 | 218 | 19:30
| BIPTC | 235 | 18:00 | 222 | 19:30 | Rampal | 234 | 18:00 | 225 | 23:00
| Bogura | 224 | 18:00 | 214 | 21:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 241 | 18:30 | 238 | 00:00 | Rampura | 231 | 00:00 | 228 | 11:00
| BSRM | 236 | 00:00 | 224 | 08:00 | Shikalbaha | 233 | 19:30 | 222 | 09:00
| Cumilla(N) | 232 | 00:00 | 224 | 15:00 | Shyampur | 232 | 00:00 | 226 | 11:00
| Fenchuganj | 238 | 18:00 | 230 | 19:00 | Siddhirganj | 234 | 01:00 | 229 | 12:00
| Ghorashal | 230 | 00:00 | 230 | 00:00 | Sirajgonj | 236 | 18:00 | 230 | 21:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 228 | 07:00 | 223 | 21:00
| GPH | 234 | 00:00 | 224 | 08:00 | Tongi | 234 | 04:00 | 225 | 15:00
| Haripur | 232 | 00:00 | 227 | 12:00
| 132 kV | KV |  | KV |  | Tongi | KV |  | KV
| Aftabnagar | 134 | 03:00 | 129 | 14:00 | Lalbag | 136 | 06:00 | 132 | 11:00
| Agargaon | 134 | 06:00 | 126 | 12:00 | Lalmonirhat | 127 | 11:00 | 112 | 21:00
| Agrabad | 137 | 20:00 | 130 | 11:00 | Madanganj | 134 | 19:30 | 129 | 08:00
| AKS | 135 | 00:00 | 128 | 08:00 | Madaripur | 132 | 18:30 | 128 | 00:00
| Aminbazar | 136 | 06:00 | 132 | 08:00 | Madartek | 135 | 06:00 | 129 | 14:00
| Amnura | 138 | 17:00 | 121 | 21:00 | Madunaghat | 138 | 00:00 | 131 | 14:00
| Ashuganj | 140 | 07:00 | 136 | 15:00 | Magura | 138 | 18:00 | 128 | 19:30
| Bagerhat | 135 | 09:00 | 128 | 22:00 | Mahasthangarh | 130 | 18:00 | 120 | 21:00
| Bakulia | 139 | 00:00 | 134 | 11:00 | Manikganj | 134 | 18:00 | 127 | 08:00
| Banani | 136 | 06:00 | 129 | 16:00 | Maniknagar | 135 | 06:00 | 131 | 11:00
| Bangabhaban | 134 | 00:00 | 131 | 11:00 | Matarbari | 128 | 23:00 | 117 | 19:00
| Barapukuria | 132 | 11:00 | 123 | 21:00 | Matuail | 134 | 00:00 | 129 | 13:00
| Barguna | 137 | 10:00 | 132 | 00:00 | Millgate | 136 | 06:00 | 128 | 12:00
| Barishal | 136 | 09:00 | 131 | 13:00 | Mirpur | 135 | 00:00 | 130 | 11:00
| Barishal-230 | 136 | 18:00 | 132 | 00:00 | Mithapukur | 129 | 04:00 | 116 | 21:00
| Baroaulia | 138 | 23:00 | 131 | 16:00 | Modern | 138 | 23:00 | 130 | 11:00
| Baroirhat | 131 | 23:00 | 124 | 05:00 | Mogbazar | 135 | 00:00 | 130 | 12:00
| Bashundhara | 135 | 00:00 | 128 | 13:00 | Mongla | 135 | 10:00 | 129 | 00:00
| BashundharaCement | 134 | 19:30 | 129 | 08:00 | Motijheel | 135 | 07:00 | 131 | 11:00
| Beanibazar | 127 | 00:00 | 122 | 22:00 | Munshiganj | 135 | 18:30 | 130 | 09:00
| Benapole | 136 | 18:00 | 127 | 22:00 | Mymensingh | 132 | 19:30 | 115 | 22:00
| Bhaluka | 126 | 09:00 | 119 | 21:00 | Naogaon | 125 | 18:00 | 110 | 21:00
| Bhandaria | 135 | 09:00 | 123 | 01:00 | Narail | 138 | 18:00 | 126 | 19:30
| Bhangura | 135 | 17:00 | 129 | 21:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 134 | 18:00 | 128 | 00:00 | Narshingdi | 131 | 18:30 | 122 | 08:00
| Bheramara(GK) | 135 | 17:00 | 130 | 19:30 | Natore | 132 | 17:00 | 125 | 21:00
| Bhulta | 126 | 19:00 | 119 | 12:00 | Nawabganj | 136 | 07:00 | 131 | 11:00
| Bog-Sherpur | 132 | 18:00 | 120 | 21:00 | Netrakona | 130 | 19:30 | 115 | 22:00
| Bogura | 132 | 18:30 | 124 | 21:00 | New | 137 | 06:00 | 129 | 11:00
| Bogura-230 | 132 | 18:00 | 123 | 21:00 | Niamatpur | 123 | 18:00 | 101 | 21:00
| Brahmanbaria | 128 | 10:00 | 121 | 21:00 | Noapara | 138 | 17:00 | 131 | 22:00
| Cantonment | 134 | 06:00 | 126 | 12:00 | Pabna | 133 | 18:00 | 125 | 21:00
| Chandpur | 133 | 00:00 | 118 | 04:00 | Palashbari | 124 | 17:00 | 113 | 21:00
| Chandraghona | 138 | 00:00 | 132 | 14:00 | Panchagarh | 124 | 00:00 | 109 | 08:00
| Chapai | 132 | 18:00 | 123 | 21:00 | Patuakhali | 137 | 01:00 | 134 | 05:00
| Charsaidpur | 135 | 18:00 | 131 | 08:00 | Payra | 138 | 01:00 | 137 | 00:00
| Chauddagram | 131 | 18:00 | 122 | 14:00 | PHP | 130 | 00:00 | 122 | 09:00
| Chhatak | 129 | 01:00 | 122 | 22:00 | Postogola | 136 | 00:00 | 132 | 09:00
| Chowmuhani | 127 | 23:00 | 116 | 04:00 | Purbachal | 136 | 07:00 | 128 | 12:00
| Chuadanga | 131 | 18:00 | 118 | 22:00 | Purbasadipur | 123 | 11:00 | 109 | 08:00
| Coxsbazar | 128 | 23:00 | 117 | 14:00 | Rahim | 134 | 00:00 | 131 | 09:00
| Cumilla(N) | 134 | 00:00 | 128 | 08:00 | Rajbari | 129 | 18:00 | 123 | 21:00
| Cumilla(S) | 132 | 00:00 | 126 | 09:00 | Rajendrapur | 137 | 19:30 | 127 | 15:00
| Daudkandi | 133 | 00:00 | 127 | 09:00 | Rajshahi | 135 | 18:00 | 127 | 21:00
| Dhaka | 135 | 04:00 | 130 | 12:00 | Rajshahi-230 | 136 | 00:00 | 125 | 02:00
| Dhamrai | 135 | 06:00 | 130 | 11:00 | Ramganj | 128 | 00:00 | 114 | 03:00
| Dhanmondi | 134 | 00:00 | 130 | 12:00 | Rampur | 137 | 19:30 | 130 | 13:00
| Dohazari | 136 | 23:00 | 131 | 11:00 | Rampura | 133 | 01:00 | 130 | 11:00
| Faridpur | 130 | 18:00 | 124 | 22:00 | Rangamati | 138 | 23:00 | 131 | 14:00
| Fatullah | 131 | 00:00 | 126 | 11:00 | Rangpur | 126 | 10:00 | 115 | 21:00
| Fenchuganj | 134 | 18:00 | 130 | 19:00 | Ruppur | 134 | 17:00 | 129 | 19:30
| Feni | 131 | 00:00 | 125 | 05:00 | Saidpur | 126 | 11:00 | 112 | 21:00
| Ghorashal | 138 | 00:00 | 137 | 22:00 | Satkhira | 137 | 17:00 | 127 | 00:00
| Goalpara | 140 | 17:00 | 132 | 02:00 | Satmasjid | 134 | 06:00 | 126 | 12:00
| Gollamari | 138 | 18:00 | 133 | 00:00 | Savar | 136 | 00:00 | 125 | 08:00
| Gopalganj | 135 | 17:00 | 130 | 02:00 | Shahjadpur | 140 | 18:00 | 132 | 21:00
| Gopalganj-400 | 130 | 17:00 | 126 | 03:00 | Shahjibazar | 132 | 10:00 | 124 | 22:00
| Gulshan | 134 | 06:00 | 129 | 15:00 | Shahmirpur | 140 | 20:00 | 132 | 15:00
| Halishahar | 139 | 23:00 | 131 | 11:00 | Shariatpur | 131 | 18:00 | 125 | 22:00
| Haripur | 134 | 00:00 | 131 | 09:00 | Sherpur | 126 | 19:30 | 110 | 23:00
| HaripurSBU | 134 | 00:00 | 131 | 09:00 | Shikalbaha | 128 | 19:30 | 121 | 14:00
| Hasnabad | 136 | 17:00 | 132 | 10:00 | Shikalbaha-230 | 141 | 20:00 | 134 | 09:00
| Hathazari | 138 | 20:00 | 132 | 09:00 | Shitalakhya | 135 | 19:30 | 130.1 | 11:00
| Ishurdi | 135 | 17:00 | 129 | 21:00 | Sholosohor | 138 | 23:00 | 131 | 08:00
| Jaldhaka | 125 | 17:00 | 111 | 21:00 | Shyampur | 130 | 00:00 | 127 | 16:00
| Jamalpur | 131 | 19:30 | 115 | 23:00 | Shyampur-230 | 130 | 00:00 | 126 | 11:00
| Jashore | 137 | 17:00 | 128 | 22:00 | Siddhirganj | 135 | 00:00 | 132 | 08:00
| Jhenaidah | 139 | 18:00 | 129 | 22:00 | Sirajganj | 132 | 18:00 | 121 | 21:00
| Jhenaidah-230 | 139 | 18:00 | 131 | 19:30 | Sonargaon | 134 | 00:00 | 130 | 11:00
| Joydebpur | 139 | 06:00 | 131 | 16:00 | Sreemongol | 130 | 00:00 | 124 | 22:00
| Joypurhat | 123 | 18:00 | 106 | 21:00 | Sreepur | 127 | 06:00 | 123 | 21:00
| Juldah | 141 | 23:00 | 133 | 11:00 | Srinagar | 136 | 06:00 | 131 | 11:00
| Kabirpur | 137 | 19:30 | 125 | 12:00 | SSM | 140 | 18:00 | 134 | 03:00
| Kachua | 132 | 00:00 | 121 | 03:00 | Sunamganj | 128 | 00:00 | 117 | 22:00
| Kaliakoir | 138 | 19:30 | 132 | 11:00 | Sylhet | 130 | 00:00 | 128 | 15:00
| Kallyanpur | 129 | 18:00 | 125 | 12:00 | Tangail | 132 | 19:30 | 123 | 22:00
| Kalurghat | 137 | 21:00 | 131 | 08:00 | Thakurgaon | 122 | 11:00 | 106 | 08:00
| Kamrangirchar | 136 | 01:00 | 123 | 12:00 | TK | 139 | 20:00 | 132 | 15:00
| Kaptai | N/A | N/A | N/A | N/A | Tongi | 137 | 04:00 | 131 | 12:00
| Kazla | 134 | 00:00 | 131 | 11:00 | Ullon | 134 | 07:00 | 130 | 11:00
| Keranigonj | 136 | 00:00 | 132 | 12:00 | Uttara | 134 | 00:00 | 130 | 09:00
| Khagrachori | 137 | 23:00 | 130 | 14:00 | UttaraNew | 135 | 06:00 | 130 | 11:00
| Khulna | 138 | 17:00 | 133 | 00:00 | Zigatola | 136 | 06:00 | 132 | 12:00
| Khulna(S) | 138 | 17:00 | 132 | 22:00
| Khulshi | 136 | 00:00 | 130 | 08:00
| Kishoreganj | 131 | 09:00 | 124 | 21:00
| Kodda | 138 | 06:00 | 128 | 11:00
| KSRM | 137 | 00:00 | 130 | 15:00
| Kulaura | 132 | 00:00 | 128 | 21:00
| Kurigram | 126 | 11:00 | 110 | 19:30
| Kushtia | 135 | 18:00 | 128 | 19:30

## L-Curve
Date | 2023-07-29
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 904 | 7692 | 6130 | 13822 |  |  |  | QF-LDC-11
0:30 | 767 | 7568.5 | 6010.5 | 13579 | Date: | 2023-07-29
1:00 | 630 | 7445 | 5891 | 13336
1:30 | 640 | 7349 | 5847 | 13196
2:00 | 650 | 7253 | 5803 | 13056
2:30 | 663 | 7125 | 5788 | 12913 | [5 empty] | Gen. at Eve. Peak | 15049 | 15049 MW (21:00 )
3:00 | 676 | 6997 | 5773 | 12770 | [6 empty] | 21:00
3:30 | 678 | 6928 | 5710.5 | 12638.5 | [5 empty] | Gen. at Day Peak | 12587 | 12587 MW (12:00 )
4:00 | 680 | 6859 | 5648 | 12507 | [6 empty] | 12:00
4:30 | 682 | 6850 | 5600.5 | 12450.5 | [5 empty] | Highest Generation | 15060
5:00 | 684 | 6841 | 5553 | 12394 | [6 empty] | 22:00
5:30 | 687 | 6668.5 | 5468.5 | 12137
6:00 | 690 | 6496 | 5384 | 11880
6:30 | 695 | 6501.5 | 5347.5 | 11849
7:00 | 700 | 6507 | 5311 | 11818
7:30 | 770 | 6414 | 5334 | 11748
8:00 | 840 | 6321 | 5357 | 11678
8:30 | 890 | 6403.5 | 5372 | 11775.5
9:00 | 940 | 6486 | 5387 | 11873
9:30 | 1022 | 6506.5 | 5438.5 | 11945
10:00 | 1104 | 6527 | 5490 | 12017
10:30 | 1085 | 6652 | 5421.5 | 12073.5
11:00 | 1066 | 6777 | 5353 | 12130
11:30 | 1049 | 6881.5 | 5477 | 12358.5
12:00 | 1032 | 6986 | 5601 | 12587
12:30 | 1034 | 7092 | 5780.5 | 12872.5
13:00 | 1036 | 7198 | 5960 | 13158
13:30 | 1040 | 7239.5 | 5910.5 | 13150
14:00 | 1044 | 7281 | 5861 | 13142
14:30 | 1092 | 7344.5 | 5911 | 13255.5
15:00 | 1140 | 7408 | 5961 | 13369
15:30 | 1135 | 7385 | 5887 | 13272
16:00 | 1130 | 7362 | 5813 | 13175
16:30 | 1147 | 7282 | 5713 | 12995
17:00 | 1164 | 7202 | 5613 | 12815
17:30 | 1065 | 7150.5 | 5509.5 | 12660
18:00 | 966 | 7099 | 5406 | 12505
18:30 | 865 | 7631.5 | 5625 | 13256.5
19:00 | 764 | 8164 | 5844 | 14008
19:30 | 700 | 8470 | 6235 | 14705
20:00 | 604 | 8617 | 6237 | 14854 |  |  |  | Executive Engineer
20:30 | 617 | 8662 | 6289.5 | 14951.5 |  |  |  | Network Operation Division
21:00 | 630 | 8707 | 6342 | 15049
21:30 | 625 | 8722.5 | 6332 | 15054.5
22:00 | 620 | 8738 | 6322 | 15060 |  |  |  |  | Page 6 of 7
22:30 | 650 | 8566 | 6335.5 | 14901.5
23:00 | 680 | 8394 | 6349 | 14743
23:30 | 792 | 8043 | 6239.5 | 14282.5
24:00 | 904 | 7692 | 6130 | 13822
15049 MW (21:00 )
12587 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-07-29 |  | Energy |  | 316422472
[15 empty] | 43674 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 4425 | 914 | 2140 | 406 | 2074 | 2816 | 110 | 260 | 419 | 106 | 0 | 2 | 1029.49
0:30 | 4373.5 | 915.5 | 2181 | 203 | 2052.5 | 2877 | 110 | 270 | 399.5 | 119 | 0 | 3 | 831.805 |  |  | Date: | 43674
1:00 | 4322 | 917 | 2222 | 0 | 2031 | 2938 | 110 | 280 | 380 | 132 | 0 | 4 | 634.12
1:30 | 4369 | 917 | 2212 | 0 | 1917.5 | 2937.5 | 110 | 270 | 321.5 | 136 | 0 | 5.5 | 529.07 | [9 empty] | Total Energy | 316.4225 | 316.4225 | Total Energy Gen 316.422 MKWHr Energy Not Served 6.493 MKWHr Energy Requirement 322.916 MKWHr
2:00 | 4416 | 917 | 2202 | 0 | 1804 | 2937 | 110 | 260 | 263 | 140 | 0 | 7 | 424.02 | [9 empty] | Energy not Served | 6.4931 | 6.4931
2:30 | 4362 | 915 | 2224 | 0 | 1699 | 2937 | 110 | 260 | 257.5 | 141 | 0 | 7.5 | 403.01 | [9 empty] | Energy Requirement | 322.9155 | 322.9155
3:00 | 4308 | 913 | 2246 | 0 | 1594 | 2937 | 110 | 260 | 252 | 142 | 0 | 8 | 382
3:30 | 4308.5 | 912.5 | 2246 | 0 | 1501 | 2937.5 | 110 | 260 | 228 | 128 | 0 | 7 | 369.1075 | [8 empty] | Shortage
4:00 | 4309 | 912 | 2246 | 0 | 1408 | 2938 | 110 | 260 | 204 | 114 | 0 | 6 | 356.215
4:30 | 4341 | 912 | 2232.5 | 0 | 1326 | 2940 | 110 | 260 | 204 | 120 | 0 | 5 | 343.3225
5:00 | 4373 | 912 | 2219 | 0 | 1244 | 2942 | 110 | 260 | 204 | 126 | 0 | 4 | 330.43
5:30 | 4298 | 912.5 | 2089 | 0 | 1241 | 2893.5 | 110 | 260 | 203.5 | 121 | 3.5 | 5 | 313.24
6:00 | 4223 | 913 | 1959 | 0 | 1238 | 2845 | 110 | 260 | 203 | 116 | 7 | 6 | 296.05
6:30 | 4283 | 913 | 1908.5 | 0 | 1212 | 2819 | 110 | 260 | 197 | 113 | 26 | 7.5 | 330.43 | [7 empty] | Coal
7:00 | 4343 | 913 | 1858 | 0 | 1186 | 2793 | 110 | 260 | 191 | 110 | 45 | 9 | 364.81
7:30 | 4272 | 913 | 1858 | 0 | 1144.5 | 2790 | 110 | 260 | 195 | 112 | 87 | 6.5 | 355.26 | [6 empty] | Oil
8:00 | 4201 | 913 | 1858 | 0 | 1103 | 2787 | 110 | 260 | 199 | 114 | 129 | 4 | 345.71
8:30 | 4263 | 912.5 | 1891 | 0 | 1097 | 2797 | 110 | 260 | 196 | 111 | 134 | 4 | 328.9975
9:00 | 4325 | 912 | 1924 | 0 | 1091 | 2807 | 110 | 260 | 193 | 108 | 139 | 4 | 312.285
9:30 | 4319 | 912 | 1908 | 0 | 1133 | 2798 | 110 | 260 | 192.5 | 109 | 199.5 | 4 | 291.275
10:00 | 4313 | 912 | 1892 | 0 | 1175 | 2789 | 110 | 260 | 192 | 110 | 260 | 4 | 270.265
10:30 | 4320 | 912.5 | 1857.5 | 0 | 1283 | 2784 | 110 | 260 | 188 | 113 | 239.5 | 6 | 225.8575
11:00 | 4327 | 913 | 1823 | 0 | 1391 | 2779 | 110 | 260 | 184 | 116 | 219 | 8 | 181.45
11:30 | 4354 | 912.5 | 1963 | 0 | 1430 | 2768.5 | 110 | 260 | 183.5 | 118 | 245.5 | 4.5 | 132.2675
12:00 | 4381 | 912 | 2103 | 0 | 1469 | 2758 | 110 | 260 | 183 | 120 | 272 | 1 | 83.085
12:30 | 4354 | 912 | 2089.5 | 0 | 1621 | 2820.5 | 125 | 260 | 220.5 | 121 | 320 | 5 | 41.5425
13:00 | 4327 | 912 | 2076 | 0 | 1773 | 2883 | 140 | 260 | 258 | 122 | 368 | 9 | 0
13:30 | 4327 | 912 | 2076 | 0 | 1773 | 2883 | 140 | 260 | 258 | 122 | 368 | 9 | 0
14:00 | 4327 | 912 | 2076 | 0 | 1773 | 2883 | 140 | 260 | 258 | 122 | 368 | 9 | 0
14:30 | 4347.5 | 915 | 2094.5 | 0 | 1826 | 2880 | 124 | 260 | 269 | 125 | 324.5 | 8 | 45
15:00 | 4368 | 918 | 2113 | 0 | 1879 | 2877 | 108 | 260 | 280 | 128 | 281 | 7 | 90
15:30 | 4342 | 917 | 2080 | 0 | 1906.5 | 2874.5 | 109 | 260 | 290.5 | 127 | 207.5 | 8 | 119.9675
16:00 | 4316 | 916 | 2047 | 0 | 1934 | 2872 | 110 | 260 | 301 | 126 | 134 | 9 | 149.935
16:30 | 4263.5 | 916.5 | 1965.5 | 0 | 1979 | 2802 | 110 | 260 | 311 | 130 | 99.5 | 8 | 132.2675
17:00 | 4211 | 917 | 1884 | 0 | 2024 | 2732 | 110 | 260 | 321 | 134 | 65 | 7 | 114.6
17:30 | 4137 | 917.5 | 1794.5 | 0 | 2050.5 | 2717 | 110 | 260 | 345 | 131 | 42.5 | 5 | 57.3
18:00 | 4063 | 918 | 1705 | 0 | 2077 | 2702 | 110 | 260 | 369 | 128 | 20 | 3 | 0
18:30 | 4193 | 917.5 | 1825.5 | 25 | 2496.5 | 2680.5 | 110 | 260 | 460.5 | 126 | 10 | 2 | 75
19:00 | 4323 | 917 | 1946 | 50 | 2916 | 2659 | 110 | 260 | 552 | 124 | 0 | 1 | 150
19:30 | 4352 | 914 | 1933 | 61 | 3326 | 2805 | 110 | 260 | 681 | 112 | 0 | 1 | 144.715
20:00 | 4381 | 914 | 2027 | 10 | 3335 | 2837 | 110 | 260 | 728 | 96 | 0 | 6 | 139.43
20:30 | 4406 | 913 | 2082 | 5 | 3363 | 2835.5 | 110 | 260 | 723.5 | 97 | 0 | 6.5 | 129.88
21:00 | 4431 | 912 | 2137 | 0 | 3391 | 2834 | 110 | 260 | 719 | 98 | 0 | 7 | 120.33
21:30 | 4430.5 | 913 | 2131 | 0 | 3410.5 | 2828 | 110 | 260 | 714.5 | 99 | 0 | 8 | 127.015
22:00 | 4430 | 914 | 2125 | 0 | 3430 | 2822 | 110 | 260 | 710 | 100 | 0 | 9 | 133.7
22:30 | 4445.5 | 914 | 2135 | 43.5 | 3272.5 | 2820 | 110 | 260 | 642 | 102 | 0 | 7 | 237.3175
23:00 | 4461 | 914 | 2145 | 87 | 3115 | 2818 | 110 | 260 | 574 | 104 | 0 | 5 | 340.935
23:30 | 4443 | 914 | 2142.5 | 246.5 | 2594.5 | 2817 | 110 | 260 | 496.5 | 105 | 0 | 3.5 | 685.2125 |  |  | Max Temp. in Dhaka |  | 34.2° C
24:00 | 4425 | 914 | 2140 | 406 | 2074 | 2816 | 110 | 260 | 419 | 106 | 0 | 2 | 1029.49
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 316.422 MKWHr Energy Not Served 6.493 MKWHr Energy Requirement 322.916 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-07-29
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 78 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1897800
2 | Karnaphuli Hydro PP Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 60 | 60 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 768000
3 | Chattogram TPP-1 | 122 | 120 | 118 | 120 | 123 | 118 | 120 | 120 | 120 | 121 | 118 | 122 | 122 | 126 | 120 | 123 | 117 | 120 |  | 120 | 122 | 120 | 120 | 120 | 120 | 120 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 17 | 16 | 22 | 25 | 8 | 8 | 244371
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 1 | 4 | 6 | 0 | 20 | 18 | 5 | 6 | 6 | 7 |  | 1 | [8 empty] | 83565
6 | Sikalbaha 225MW CCPP (Gas) | 226 | 225 | 223 | 225 | 229 | 227 | 224 | 221 | 224 | 223 | 216 | 218 | 223 | 219 | 215 | 219 | 219 | 219 |  | 219 | 221 | 222 | 221 | 221 | 225 | 222 | 5253865
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 37 | 51 | 51 | 51 | 51 | 51 | 50 | 50 | 48 | 47 | 47 | 46 | 45 | 45 | 47 | 47 | 48 | 48 |  | 51 | 51 | 50 | 50 | 50 | 50 | 50 | 1143539
12 | Hathazari 100 MW peaking PP | 42 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 40 | 64 |  | 57 | 57 | 57 | 57 | 57 | 57 | 50 | 1010640
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 420690
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 38 | 31 | 31 | 31 | 31 | 30 | 19 | 27 | 32 | 32 | 24 | 24 | 37 | 30 | 31 | 39 | 39 | 39 |  | 44 | 46 | 46 | 46 | 46 | 38 | 38 | 818544
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 137 | 136 | 137 | 137 | 138 | 120 | 122 | 126 | 122 | 122 | 125 | 193 | 193 | 157 | 194 | 156 | 78 | 76 |  | 157 | 155 | 155 | 193 | 193 | 197 | 195 | 3726000
17 | Siddhirganj 335 MW CCPP | 332 | 280 | 280 | 280 | 333 | 335 | 333 | 327 | 333 | 333 | 325 | 326 | 320 | 280 | 326 | 319 | 280 | 250 |  | 322 | 326 | 325 | 327 | 328 | 330 | 331 | 7600458
18 | Kodda 300 MW PP Unit-2 (Summit) | 115 | 112 | 115 | 115 | 115 | 115 | 115 | 75 | 75 | 75 | 75 | 80 | 110 | 112 | 112 | 112 | 112 | 112 |  | 112 | 112 | 112 | 112 | 112 | 112 | 115 | 2581855
19 | Ashuganj 195 MW PP (APSCL-United) | [9 empty] | 0 | 26 | 8 | 0 | [12 empty] | 0 | 33454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 210 | 210 | 210 | 210 | 210 | 150 | 150 | 150 | 180 | 180 | 180 | 180 | 210 | 210 | 210 | 210 | 210 | 150 |  | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 4706406
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4315500
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | [9 empty] | 0 | 3 | 10 | 0 | [12 empty] | 0 | 13392
33 | Ashuganj 225 MW CCPP | 209 | 198 | 201 | 207 | 208 | 209 | 209 | 202 | 204 | 206 | 204 | 153 | 178 | 186 | 195 | 203 | 199 | 183 |  | 196 | 199 | 202 | 204 | 205 | 206 | 199 | 4805000
34 | Ashuganj 450 MW CCPP(South) | 230 | 230 | 230 | 230 | 230 | 230 | 340 | 240 | 240 | 240 | 280 | 270 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 5956000
| Ashuganj 450 MW CCPP(North) | 270 | 270 | 270 | 270 | 270 | 310 | 270 | 275 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 7006800
| Ashuganj 420 MW CCPP(East) | 285 | 405 | 270 | 270 | 270 | 230 | 230 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6647900
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 367 | 367 | 367 | 367 | 367 | 354 | 341 | 341 | 360 | 366 | 366 | 367 | 367 | 367 | 367 | 367 | 367 | 342 |  | 323 | 362 | 367 | 368 | 368 | 392 | 381 | 8730620
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 400 | 350 | 350 | 350 | 350 | 350 | 450 | 450 | 450 | 450 | 450 | 350 | 320 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 9715500
41 | Haripur 360 MW CCPP(HPL) | 332 | 332 | 332 | 332 | 332 | 295 | 295 | 295 | 327 | 326 | 332 | 326 | 327 | 327 | 326 | 327 | 328 | 292 |  | 336 | 333 | 331 | 332 | 328 | 328 | 328 | 7744000
42 | RPCL 210MW CCPP | 101 | 101 | 101 | 101 | 100 | 100 | 100 | 86 | 87 | 68 | 68 | 66 | 64 | 65 | 65 | 65 | 68 | 69 |  | 69 | 71 | 93 | 97 | 96 | 97 | 97 | 1942080
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 4 | 6 | 34 | 29 | 50 | 28 | 30 | 42 | 29 | 6 | 4 | 2 | [8 empty] | 227830
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 716000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 25 | 25 | 25 | 22 | 20 | 25 | 25 | 25 | 20 | 28 | 25 | 25 | 25 | 25 | 20 | 20 | 20 | 25 |  | 25 | 25 | 25 | 20 | 20 | 25 | 20 | 551808
48 | Shahjibazar 86 MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 84 | 86 | 86 |  | 86 | 86 | 86 | 86 | 84 | 84 | 84 | 1938240
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 98 | 106 | 120 | 127 | 131 | 152 | 185 | 185 | 185 | 185 | 186 | 185 | 185 | 184 | 182 | 182 | 181 | 182 |  | 183 | 181 | 183 | 182 | 183 | 185 | 185 | 4441360
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 392000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 252000
54 | Hobiganj 11 MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 186432
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 47 | 47 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 47 | 47 | 47 | 1185000
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 565776
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 265 | 280 | 290 | 285 | 275 | 280 | 290 | 310 | 285 | 270 | 300 | 290 | 285 | 310 | 285 | 290 | 270 |  | 290 | 275 | 270 | 290 | 280 | 300 | 295 | 7036500
| Bibiyana South 400 MW | 340 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 330 | 350 | 350 | 350 | 350 | 350 |  | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 8418200
58 | Nababganj 55 MW PP (Southern power ) | [9 empty] | 0 | 5 | 17 | 35 | 35 | 35 | 35 | 35 | 55 |  | 55 | 55 | 55 | 35 | 55 | 35 | 35 | 509562
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 223440
60 | Barabkunda 22 MW PP (Regent) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 242544
61 | Narshingdi 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 436068
62 | Tangail 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 15 | 15 | 15 | 15 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 390744
63 | Impoprt (Tripura) | 132 | 140 | 142 | 114 | 126 | 116 | 110 | 114 | 108 | 110 | 116 | 120 | 122 | 128 | 128 | 126 | 134 | 128 |  | 124 | 112 | 96 | 98 | 100 | 104 | 106 | 2877120
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 38 | 17 | 24 | 23 | 16 | 26 | 28 | 23 | 23 | 22 | 27 | 28 |  | 37 | 37 | 39 | 41 | 42 | 42 | 42 | 842400
65 | Feni 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 |  | 0 | 16 | 16 | 16 | 16 | 17 | 18 | 18 |  | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 378936
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 246060
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 33 | 28 | 33 | 33 | 33 | 33 | 33 |  | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 755000
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 16 | 13 | 15 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 15 | 14 | 332500
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456000
70 | Summit Madhabdi | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 22 | 20 | 21 | 21 | 21 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 475920
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 662200
72 | Rupganj 33 MW PP(Summit) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 24 | 565100
73 | Ghorashal 108 MW PP (Regent) | [10 empty] | 0 | 6 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 145318
| Feni Lanka Power | 51 | 51 | 51 | 51 | 17 | 17 | 17 | 17 | 17 | 17 | 65 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 106 | 106 | 106 | 106 | 106 | 106 | 17 | 1407900
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 28 | 28 | 28 | 12 | 9 | 9 | 9 | 9 |  | 57 | 57 | 55 | 58 | 58 | 57 | 9 | 462840
| Manikgonj 162MW PP(MPGL) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 54 | 54 | 54 | 72 | 72 | 72 | 72 | 89 | 90 |  | 90 | 105 | 108 | 108 | 108 | 108 | 17 | 1553760
77 | Siddhirganj 100 PP(Dutch Bangla) | 48 | 48 | 34 | 24 | 24 | 24 | 14 | 8 | 8 | 8 | 8 | 12 | 36 | 50 | 44 | 60 | 72 | 77 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1047360
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 27 | 51 | 51 | 51 | 51 | 52 | 52 | 52 | 52 | 25 | 8 | 8 | 8 |  | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 696000
79 | Kodda 150 MW PP | 82 | 82 | 82 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 |  | 98 | 130 | 130 | 130 | 130 | 130 | 130 | 1949280
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 203179
| Gazipur 100 MW PP | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 105 | 105 | 105 | 105 | 105 | 105 | 35 | 1183680
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 2 | 3 | 5 | 4 | 5 | 4 | 2 | 4 | 3 | 1 | [9 empty] | 34680
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 621887
| Karnaphuli Power Ltd. | 55 | 55 | 55 | 55 | 51 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 24 | 53 | 53 | 53 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1042940
82 | Madanganj 102 PP(Summit) | 95 | 95 | 68 | 51 | 51 | 51 | 40 | 20 | 17 | 17 | 17 | 20 | 68 | 96 | 96 | 96 | 96 | 96 |  | 96 | 96 | 96 | 85 | 96 | 96 | 95 | 1563928
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 5 | 19 | [9 empty] | 0 | 14 | 22 | 22 | 24 | 23 | 23 |  | 25 | 25 | 23 | 21 | 22 | 22 | 22 | 305433
86 | Meghnaghat CCPP ( Summit) | 159 | 150 | 137 | 127 | 109 | 57 | 52 | 56 | 5 | 0 | [15 empty] | 0 | 1005644
87 | Meghnaghat 100 MW(IEL) | 33 | 33 | 33 | 34 | 33 | 33 | 33 | 34 | 33 | 41 | 42 | 45 | 51 | 50 | 58 | 67 | 66 | 66 |  | 66 | 66 | 67 | 66 | 66 | 67 | 67 | 1171200
| Meghnaghat 104 MW PP (OPCL) | 48 | 36 | 35 | 35 | 43 | 51 | 53 | 38 | 35 | 35 | 49 | 53 | 53 | 53 | 53 | 53 | 53 | 45 |  | 53 | 72 | 72 | 72 | 72 | 72 | 52 | 1207680
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 68 | 68 | 68 | 68 | 45 | 45 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 68 | 68 | 68 | 68 | 68 | 68 | 47 | 1269840
92 | Fenchuganj 44 MW (Energyprima) | 45 | 45 | 45 | 45 | 45 | 43 | 43 | 42 | 42 | 41 | 41 | 40 | 40 | 40 | 40 | 40 | 40 | 42 |  | 45 | 45 | 42 | 43 | 48 | 48 | 48 | 1031112
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 972128
94 | Gagnagar 102 MW PP (Digital Power) | 92 | 92 | 50 | 24 | 24 | 24 | 8 | 8 | 8 | 8 | 8 | 25 | 32 | 33 | 33 | 33 | 33 | 33 |  | 48 | 92 | 102 | 102 | 102 | 34 | 16 | 978192
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 35 | 44 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 476640
96 | Chattogram 108 MW PP (ECPV) | [13 empty] | 3 | 8 | 12 | 11 | 19 |  | 22 | 18 | 20 | 24 | 24 |  | 0 | 149760
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 366311
100 | Manikganj 55 MW PP (Northern) | 35 | [6 empty] | 0 | 6 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 0 | 537422
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 112 | 80 | 80 | 80 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 80 | 80 |  |  |  | 112 | 112 | 112 | 112 | 112 | 2357918
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 0 | [8 empty] | 11550
103 | Kamalaghat 54 MW PP(Banco Energy) | [8 empty] | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 387360
104 | Keranigonj 300 MW PP (APR) | [19 empty] | 50 | 11 |  |  |  | 33 | 206 | 194218
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 |  | 87 | 87 | 88 | 97 | 97 | 68 | 68 | 1716000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 36 | 36 | 36 | 36 | 35 | 36 | 36 | 34 | 60 | 71 | 71 | 70 | 71 | 70 | 70 | 71 | 71 | 111 |  | 134 | 134 | 135 | 135 | 135 | 97 | 39 | 1717632
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 100 | 100 | 100 | 100 | 100 | 100 | 25 | 1163520
116 | Chandpur 200 MW (Desh energy) | 100 | 100 | 60 | 34 | 34 | 34 | 34 | 34 | 0 |  |  |  |  | 17 | 51 | 51 | 55 | 51 |  | 54 | 150 | 118 | 157 | 155 | 155 | 70 | 1414080
117 | Ashuganj 150 MW PP (Midland) | 5 | 6 | 5 | 5 | 6 | 5 | 5 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 3 | 5 | 6 |  | 22 | 52 | 52 | 57 | 62 | 62 | 12 | 361309
118 | Bibiyana-III 400 MW CCPP | 402 | 402 | 403 | 403 | 403 | 322 | 320 | 320 | 364 | 368 | 350 | 368 | 368 | 368 | 368 | 368 | 368 | 368 |  | 405 | 368 | 368 | 368 | 367 | 367 | 355 | 9020000
| Jamalpur 115 MW PP (United) | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 84 | 84 | 84 | 84 | 84 | 19 | 19 | 706800
| Anwara 300 MW PP (United) | 225 | 87 | 87 | 87 | 87 | 87 | 88 | 88 | 88 | 88 | 121 | 122 | 123 | 123 | 123 | 123 | 123 | 122 |  | 200 | 256 | 259 | 267 | 268 | 268 | 158 | 3414873
| Juldah unit-2 (Acorn) | 75 | 75 | 75 | 50 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 1336320
| Anlima Energy Ltd. | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 38 |  | 53 | 68 | 68 | 68 | 68 | 68 | 68 | 1045036
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 15 | 3 | 17 | 34 |  | 13 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 439560
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 3 | 9 | 21 | 29 | 32 | 35 | 16 | 25 | 20 | 14 | 3 | 1 | [8 empty] | 206061
| Chandpur 115(Doreen) | 53 | 18 | 18 | 17 | 17 | 18 | 18 | 18 | 17 | 25 | 71 | 72 | 72 | 72 | 72 | 72 | 72 | 90 |  | 112 | 115 | 114 | 114 | 114 | 68 | 48 | 1389120
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 34 | 34 | 17 | 17 | 17 | 17 | 455400
| Mirsharai 150 MW (Oil) | 70 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 60 | 90 | 143 | 143 | 143 | 17 | 17 | 861454
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 4 | 7 | 8 | 6 | 4 | 6 | 9 | 4 | 4 | 4 | 8 | 1 | 9 | 6 | 7 | 9 | 7 | 3 |  | 1 | 1 | 6 | 7 | 9 | 5 | 2 | 142080
| Matarbari 2*600 MW (CPGCL) | [11 empty] | 18 | 30 | 60 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 1182545
120 | Eastern Zone Total | 7445 | 7253 | 6997 | 6859 | 6841 | 6496 | 6507 | 6321 | 6486 | 6527 | 6777 | 6986 | 7198 | 7281 | 7408 | 7362 | 7202 | 7099 |  | 8164 | 8470 | 8617 | 8707 | 8738 | 8394 | 7692 | 176177669
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | [7 empty] | 0 | 8 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 239040
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 11 | 5 | [11 empty] | 10 | 10 | 10 | 10 | 10 |  | 25 | 40 | 27 | 22 | 22 | 21 | 11 | 180960
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3001066
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 847680
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 1 | 10 | 21 | 4 | 26 | 6 | 13 | 96 | 44 | 46 | 12 | 8 | 4 | [8 empty] | 304560
131 | Rampal 1320 MW (BIFPCL) | 500 | 500 | 500 | 500 | 502 | 501 | 501 | 501 | 499 | 502 | 488 | 414 | 392 | 380 | 380 | 382 | 373 | 392 |  | 381 | 382 | 382 | 380 | 382 | 381 | 382 | 10560000
132 | United Payra Power Ltd. | 150 | 150 | 116 | 116 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 1603200
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 170 | 170 | 176 | 172 | 176 | 176 | 221 | 221 | 220 | 220 | 220 | 182 | 182 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 4979918
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 48 | 48 | 48 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 46 |  | 75 | 80 | 98 | 110 | 110 | 110 | 110 | 1013
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 217 | 250 | 250 | 250 | 250 | 250 | 250 | 5890900
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 120 | 128 | 133 | 124 | 122 | 117 | 117 | 132 | 132 | 132 | 132 | 130 | 100 | 128 | 132 | 128 | 130 | 120 |  | 120 | 118 | 115 | 120 | 120 | 120 | 132 | 3013000
140 | Bhola 33 MW PP (Venture) | 33 | 32 | 30 | 30 | 29 | 26 | 19 | 21 | 21 | 21 | 22 | 22 | 25 | 25 | 25 | 22 | 21 | 21 |  | 30 | 31 | 32 | 34 | 35 | 35 | 35 | 626626
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | 8 | 8 | 8 |  |  |  |  | 0 | 24 | 32 | 32 | 32 | 32 | 24 | 8 |  | 32 | 32 | 32 | 32 | 32 | 24 | 24 | 378000
143 | Gopalganj 100 MW Peaking PP | 49 | [10 empty] | 0 | 15 | 25 | 26 | 28 | 35 | 50 |  | 56 | 60 | 64 | 53 | 50 | 50 | 50 | 524288
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 85 | 85 | 50 | 50 | 50 | 50 | 15 | 15 | 15 | 15 | 15 | 25 | 105 | 105 | 105 | 105 | 105 | 50 |  | 70 | 105 | 105 | 105 | 105 | 105 | 105 | 1735632
146 | Bheramara HVDC | 917 | 917 | 913 | 912 | 912 | 913 | 913 | 913 | 912 | 912 | 913 | 912 | 912 | 918 | 918 | 916 | 917 | 918 |  | 917 | 914 | 914 | 912 | 914 | 914 | 914 | 21786181
147 | Bheramara 410 MW CCPP | 190 | 200 | 205 | 205 | 205 | 205 | 235 | 235 | 245 | 240 | 240 | 240 | 235 | 210 | 210 | 210 | 205 | 205 |  | 200 | 200 | 200 | 205 | 205 | 195 | 190 | 5355648
148 | Payra 1320 MW | 1244 | 1244 | 1244 | 1244 | 1244 | 1160 | 1100 | 1100 | 1120 | 1100 | 1100 | 1130 | 1244 | 1244 | 1244 | 1244 | 1160 | 1120 |  | 1080 | 1200 | 1230 | 1230 | 1244 | 1244 | 1244 | 30518500
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 208 | 240 | 240 | 240 | 240 | 180 | 180 |  | 220 | 219 | 210 | 210 | 180 | 180 | 180 | 4772600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [20 empty] | 35 | 35 | 35 | 35 | 34 | 0 | 148991
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 0 | 3 | 5 | 5 | 5 | 5 | 4 | 3 | 0 | 0 | [8 empty] | 34920
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 160 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3626609
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 174 | 179 | 181 | 180 | 183 | 188 | 192 | 160 | 160 | 160 | 160 | 163 | 150 | 150 | 161 | 176 | 173 | 150 |  | 159 | 179 | 181 | 181 | 179 | 176 | 172 | 4407882
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 370 | 370 | 414 | 414 | 414 | 390 | 350 | 350 | 380 | 380 | 300 | 414 | 393 | 326 | 414 | 370 | 365 | 269 |  | 337 | 341 | 330 | 414 | 414 | 414 | 414 | 9041090
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [14 empty] | 5 | 16 | 20 | 20 |  | 23 | 24 | 24 | 31 | 24 | 24 | 24 | 177172
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 5 | 5 | 5 | 8 | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 178704
165 | Amnura 50 MW PP(Sinha) | 14 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 483630
166 | Katakhali 50 MW PP (Northern) | 42 | 16 | 16 | [8 empty] | 0 | 8 | 8 | 16 | 16 | 34 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 401999
167 | Katakhali 50 MW Peaking PP | 21 | 6 | [17 empty] | 30 | 36 | 39 | 38 | 38 | 38 | 24 | 204557
168 | Santahar 50 MW Peaking PP | 30 | 30 | 30 | [14 empty] | 9 |  | 21 | 22 | 23 | 24 | 25 | 25 | 25 | 245840
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200501
170 | Chapainawabganj 100 MW Peaking PP | [11 empty] | 0 | 48 | 48 | 48 | 48 | 48 | 48 |  | 87 | 90 | 90 | 90 | 90 | 90 | 0 | 724040
171 | Baghabari 200 MW PP (Paramount) | [20 empty] | 50 | 10 |  |  | 54 | 200 | 260485
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 70 | 75 | 95 | 95 | 95 | 35 | 1145952
172 | Confidence Power Bogura Unit-1 113 MW | 55 | 55 | 55 | 37 | 37 | 37 | 37 | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1144608
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 28 | 34 | 34 | 34 | 34 | 49 | 49 |  | 77 | 78 | 78 | 78 | 78 | 78 | 34 | 1093238
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 1 | 4 | 5 | 7 | 7 | 4 | 2 | 2 | 3 | 1 | [8 empty] | 41737
178 | Energypac Power Venture Thakurgaon Ltd. | [9 empty] | 0 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 76 | 110 | 113 | 114 | 114 | 114 | 0 | 846528
| Intraco Solar 30 MW | [5 empty] | 1 |  | 0 | 6 | 15 |  | 16 | 0 |  | 2 |  | 4 | 2 |  | 0 | [6 empty] | 90943
| Adani Power Jharkhanda Ltd | 764 | 763 | 763 | 764 | 766 | 754 | 762 | 756 | 758 | 757 | 761 | 756 | 757 | 760 | 763 | 756 | 769 | 760 |  | 761 | 754 | 765 | 764 | 766 | 763 | 760 | 18245455
178 | Teesta Solar Limited | [5 empty] | 2 | 26 | 85 | 63 | 148 | 95 | 144 | 204 | 188 | 167 | 86 | 41 | 9 | [8 empty] | 1181110