## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-08-02 | Wednesday
|  | Date (day): | 2023-08-02 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13636.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15549 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-08-01 | 2023-08-02 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 210 | 210 | 210 | 210
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 12 | 12 | 96 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 396 | 399 | 360 | 360 | 52 |  | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 323 | 343 | 325 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 420 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 42 | 50 | 42 | 50 | 50 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 17 | 51 | 17 | 51 |  | 51 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 25 | 15 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 11 | 11 | 50 | 50 |  | 25 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 17 | 19 | 17 | 17 |  | 5 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 179 | 125 | 195 | 195 | 15
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 35 | 20 | 50 | 75 | 25 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 317 | 323 | 330 | 330
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 50 | 85 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 35 | 17 | 34 | 20 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 82 | 115 | 64 | 130 | 19 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 17 | 35 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 33 | 41 | 38 | 41 |  | 39 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 25 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 6 | 23 | 16 | 24 |  | 9 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 25 | 8 | 25 | 27 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 112 | 95 | 112 | 112 | 188 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 200
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
33 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
34 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 70 | 149 | 70 | 149
35 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 105 | 35 | 105
36 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 53 | 72 | 53 | 72 | 32 |  | Fuel shortage
37 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 162 | 54 | 162
38 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 33 | 0 | 35 | 0
39 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6063 | 5722 | 2869 | 3179 | 2977 | 3621 | 808 | 1224
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 118 | 120 | 120 |  | 60
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
41 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 17 | 25 | 17 | 25
42 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 2 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 6 | 46
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 130 | 130 | 130 | 130 | 100 |  | Low Water Level
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 221 | 225 | 220 | 225
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 17 | 51 | 51 | 54 |  | Engine problem
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 34 | 48 | 24 | 40 | 58 |  | Fuel shortage
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 50 | 50 | 50 | 50 | 52 |  | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 46 | 58 | 36 | 80 | 20 |  | Fuel shortage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 100 | 25 | 100
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 12 | 12 | 12 | 10 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 20 | 2 | 30
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 34 | 0 | 24 | 84 |  | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 122 | 221 | 120 | 300
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 36 | 36 | 18 |  | Fuel shortage
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 53 | 51 | 54 | 54 | 56 |  | Fuel shortage
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 38 | 88 | 38 | 88 | 12 |  | Fuel shortage
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 34 | 68 | 34 | 68 | 48 |  | Fuel shortage
60 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 70 | 140 | 54 | 144 | 19 |  | Fuel shortage
| SS Power I |  | Coal | SS Power | 0 | 0 | 0 | 360 | 0 | 0 | 0 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 27 | 28 | 20 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 125 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2605 | 2545 | 1541 | 1450 | 1074 | 1633 | 531 | 390
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 171 | 180 | 170 | 180 | 41 |  | Gas shortage
62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 280 | 280 | 280 | 80 |  | Gas shortage
63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 230 | 270 | 260 | 260 | 100 |  | Gas shortage
64 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 240 | 288 | 250 | 250 | 150 |  | Gas shortage
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 0 | 0 | 0 | 45 |  | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
69 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 6 | 40 | 6 | 60 | 90 |  | Fuel shortage
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 23 | 37 | 44 | 46 |  | 6 | Machine problem
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
72 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 99 | 120 | 68 | 150 | 50 |  | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 20 | 20
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 114 | 134 | 146 | 169
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 17 | 25 | 25 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 34 | 8 | 43 | 43 |  | 9 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 20 | 20 |  | 5 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Contract Expired
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 70 | 52 | 106 | 8 |  | Fuel shortage
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 0 | 113 |  |  | Fuel shortage
81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 17 | 17 | 17 |  | 37 | Engine problem
82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 72 | 115 | 72 | 115
| Cumilla Area Total |  |  |  |  | 3159 | 3096 | 1434 | 1663 | 1527 | 1916 | 759 | 228
83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 43 | 82 | 50 | 98 | 104 |  | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 16 | 18 | 18 |  | 4 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 66 | 85 | 68 | 85 | 115 |  | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 17 | 84 | 18 | 85 | 30 |  | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 51 | 0 | 50 | 0
90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 200 | 273 | 211.6 | 292 | 104 | 4
91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 24 | 30 | 30 | 30 |  | 40 | Machine problem.
92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 10 | 30 |  | 60 | Under maint
93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 80 | 112 | 112 |  | 51 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 41 | 49 | 50 | 50
96 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 39 | 46 | 48 | 48
97 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 20 | 30 | 25 | 30 |  | 36 | Unit-9 under maint
99 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 75 | 86 | 80 | 86
100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 110 | 112 | 112 | 112 |  | 119 | ST Under maint
102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 17 | 17
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
103 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 23 | 24 | 24 | 24
104 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 255 | 300 | 300 |  |  | FGMO
105 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 387 | 368 | 400 | 400 |  |  | FGMO
106 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 9 | 10 | 10
107 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 355 | 355 | 350 | 350
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1386 | 1472 | 1579 | 1610 | 0 | 736
108 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 910 | 911 | 918 | 918
109 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 16 | 16 | 16 | 99 |  | Fuel shortage
110 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 10 | 39 | 20 | 30 |  | 24 | Engine problem
111 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 115 | 115 | 120 | 120 | 110 |  | Fuel shortage
112 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 19 | 60 | 40 | 55 |  | 54 | Engine problem
113 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 130 | 130 | 155 | 155 | 255 |  | Gas shortage
114 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 32 | 40
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
115 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 40 | 53 | 53 | 52 |  | Fuel shortage
116 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 15 | 50 | 50 | 105
117 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 56 | 0 | 100 | 0
118 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 220 | 220 | 15 | 79 | 120 | 120 | 100 |  | Fuel shortage
119 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0 | 617 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3125 | 3121 | 1321 | 1448 | 1624 | 1612 | 1249 | 78
120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 100 | 16 | 16 | 110
121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 11 | 16 | 22 | 34 |  | 6 | Engine problem
122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 132 | 132 | 120 | 120 |  | 74 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1230 | 1244 | 1244 | 1244
124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 100 | 17 | 150
126 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 40 | 0 | 0 | 0 | 307 |  | Coal shortage
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1750 | 1728 | 1639 | 1878 | 307 | 80
127 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
128 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 35 | 0 | 35 | 17 |  | Fuel shortage
129 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 24 | 0 | 32 |  | 39 | Engine problem
130 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 21 | 21 | 21 | 21
131 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 25 | 25 | 34 | 34 | 16 |  | Fuel shortage
132 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 30 | 36 | 36 | 35 | 15 |  | Engine problem
133 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Under maint
134 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 195 | 140 | 214 | 220
135 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 143 | 145 | 160 | 181 | 39 |  | Gas shortage
136 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 338 | 349 | 414 | 414
137 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 18 | 22 | 20 | 33 | 17 |  | Fuel shortage
138 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 47 | 92 | 50 | 90 | 14 |  | Fuel shortage
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 70 | 113 | 113 | 113
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 748*2 | 1496 | 1496 | 760 | 1066 | 1200 | 1200
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 1781 | 2197 | 2397 | 2537 | 333 | 252
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 210 | 240 | 220 | 230
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 98 | 105 | 105 | 105 | 8 |  | Fuel shortage
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 113 | 115 | 115 | 115
153 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 19 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 168 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 615 | 460 | 608 | 450 | 133 | 85
| Total |  |  |  |  | 24911 | 24171 | 12897 | 13870 | 13636.6 | 15549 | 4224 | 3077
A. |  | 2023-08-01 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 13870 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 12246 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13970 | MW
3 | Day peak Generation : |  |  | 12897 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13400.99 | MW
4 | Evening peak Generation : |  |  | 13870 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 96 | MW
5 | Total Energy Generation : |  | 302.9446 | MKWHr | By Solar | 2.5269 | MKWHr
| By Gas : | 146.4043 | MKWHr |  | By Oil: | 63.0411 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 62.9443 | MKWHr |  | By Hydro: | 3.0242 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.54144 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4224 | MW | Dhaka | 5002.89 | 4992.89 |  | 10 |  | 18:00 |  | 20.055
|  |  | For Plants S/D or M/C prob = |  |  | 3077 | MW | Chittagong | 1342.7 | 1342.7 |  | 0 |  | 19:00 |  | 31.515
|  |  | Total = |  |  | 7301 | MW | Khulna | 1529 | 1529 |  | 0 |  | 19:30 |  | 95.5
7 | Total Gas Supplied : |  |  | 1109.89 | MMCFD |  |  | Rajshahi | 1487 | 1487 |  | 0 |  | 20:00 |  | 124.15
8 | Fuel Cost : | i) Gas : | Taka | 161324664.906 | ii) Oil : | Taka | 838507381.72 | Comilla | 1088 | 1052 |  | 36 |  | 21:00 |  | 211.055
|  | iii) Coal : | Taka | 304425147 | Total | Taka | 1304257193.626 | Mymensingh | 1107 | 1107 |  | 0 |  | 22:00 |  | 242.57
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 573 | 548 |  | 25 |  | 23:00 |  | 332.34
| ii) During Peak Demand : |  |  | 1020 | MW (E to W) at | 19:30 | hrs | Barisal | 211.4 | 211.4 |  | 0 |  | 24:00 |  | 412.56
| iii) Maximum : |  |  | 670 | MW at | 3:00 | hrs | Rangpur | 1060 | 1035 |  | 25
10 | Maximum Temperature in Dhaka was |  |  |  | 36.8° C |  |  | Total | 13400.99 | 13304.99 |  | 96
B. |  | 2023-08-02 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 36.8° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 14800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15549 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 12800 | MW
4 | Reserve(Generation end) |  |  |  | 749 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 323.2574 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11306 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.4604 | MKWHr. | ii) HVDC Flow at Peak Time |  | 911 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.0019 | MKWHr. | iii) Maximum HVDC Flow : |  | 912 | MW at | 4:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 79.93 |  | (b) Today: | 79.53 |  | (c) Rule Curve: |  | 89.32
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-08-01 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 396 | 331 |  | 0 | 450 | 0 | 49 | 17 | 15 | 332 | 0 | 177 | 33 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 12 | 8 | 0 | 70 | 60 | 118 | 0 | 8 | 225 | 0 | 0 | 0 |  | 6 | 42 | 50 | 46 | 0 | 46 | 12 | 26 | 0 | 0 | 0 | 280 | 260 | 187 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 46 | 43 | 19 | 11 | 32 | 17 | 138 | 96 | 0 | 16 | 0 | 30 | 0 | 47 | 46 | 0 | 0 | 20 | 78 | 0 | 112 | 17 | 0 | 10 | 310 | 24 | 5 | 0 | 100 | 300 | 0 | 68 | 0 | 35 | 0 | 25 | 34 | 20 | 374 | 18 | 35 | 51 | 0 | 86 | 17 | 55 | 34 | 9 | 50 | 387 | 54 | 0 | 17 | 34 | 0 | 17 | 0 | 18 | 17 | 250 | 17 | 0 | 310 | 1 | 150 |  | 911 | 0 | 145 | 0 | 16 | 120 | 0 | 0 | 11 | 44 | 8 | 132 | 30 | 16 | 0 | 0 | 0 | 0 | 20 | 0 | 21 | 8 | 23 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 10 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 150 | 0 | 390 | 35 | 0 | 35 | 15 | 98 | 0 | 0 | 35 | 1244 | 222 | 0 | 150 | 0 | 0 | 36 | 220 | 0 | 0 | 0 | 150 | 767 | 0 | 0 |  | 7534 | 5499 | 13033 | 4294 | 911 | 1995 | 300 | 1571 | 2831 | 130 | 561 | 301 | 138 | 0 | 1 | 1305.485 | 79.98
2:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 396 | 332 |  | 0 | 450 | 0 | 51 | 17 | 15 | 326 | 0 | 191 | 33 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 12 | 33 | 17 | 8 | 0 | 70 | 60 | 118 | 0 | 8 | 220 | 0 | 0 | 0 |  | 6 | 42 | 50 | 46 | 0 | 6 | 12 | 30 | 0 | 0 | 0 | 335 | 260 | 191 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 39 | 43 | 19 | 11 | 32 | 17 | 140 | 96 | 0 | 16 | 0 | 30 | 0 | 47 | 46 | 0 | 0 | 20 | 78 | 0 | 112 | 17 | 0 | 10 | 300 | 24 | 5 | 0 | 120 | 200 | 0 | 68 | 0 | 35 | 0 | 25 | 34 | 6 | 409 | 18 | 35 | 51 | 0 | 87 | 17 | 55 | 34 | 9 | 50 | 382 | 50 | 0 | 17 | 34 | 0 | 17 | 0 | 17 | 17 | 250 | 17 | 0 | 310 | 11 | 150 |  | 911 | 0 | 150 | 0 | 16 | 120 | 0 | 0 | 11 | 48 | 8 | 132 | 32 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 16 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 150 | 0 | 390 | 36 | 0 | 37 | 15 | 34 | 0 | 0 | 35 | 1244 | 222 | 0 | 54 | 0 | 0 | 36 | 220 | 0 | 0 | 0 | 150 | 764 | 0 | 0 |  | 7516 | 5316 | 12832 | 4417 | 911 | 1992 | 200 | 1378 | 2828 | 130 | 554 | 271 | 140 | 0 | 11 | 1306.44 | 79.97
3:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 397 | 333 |  | 0 | 450 | 0 | 50 | 17 | 15 | 329 | 0 | 180 | 33 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 21 | 33 | 17 | 8 | 0 | 70 | 60 | 115 | 0 | 8 | 221 | 0 | 0 | 0 |  | 6 | 42 | 50 | 46 | 0 | 6 | 12 | 30 | 0 | 0 | 0 | 280 | 260 | 181 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 32 | 43 | 19 | 11 | 32 | 17 | 134 | 95 | 0 | 16 | 0 | 30 | 0 | 47 | 46 | 0 | 0 | 20 | 78 | 0 | 112 | 17 | 0 | 10 | 310 | 24 | 5 | 0 | 115 | 260 | 0 | 68 | 0 | 35 | 0 | 25 | 34 | 6 | 368 | 18 | 35 | 51 | 0 | 87 | 17 | 55 | 34 | 9 | 50 | 389 | 35 | 0 | 17 | 34 | 0 | 17 | 0 | 18 | 17 | 250 | 17 | 0 | 310 | 20 | 150 |  | 911 | 0 | 150 | 0 | 16 | 120 | 0 | 0 | 11 | 38 | 8 | 132 | 30 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 16 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 151 | 0 | 407 | 36 | 0 | 50 | 15 | 34 | 0 | 0 | 56 | 1244 | 222 | 0 | 17 | 0 | 0 | 36 | 220 | 0 | 0 | 0 | 150 | 769 | 0 | 0 |  | 7463 | 5324 | 12787 | 4318 | 911 | 2018 | 260 | 1355 | 2833 | 130 | 554 | 254 | 134 | 0 | 20 | 1253.915 | 79.96
4:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 397 | 332 |  | 0 | 450 | 0 | 50 | 17 | 15 | 327 | 0 | 180 | 33 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 21 | 33 | 17 | 8 | 0 | 70 | 60 | 120 | 0 | 8 | 221 | 0 | 0 | 0 |  | 6 | 42 | 50 | 46 | 0 | 6 | 12 | 29 | 0 | 0 | 0 | 285 | 260 | 189 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 37 | 43 | 19 | 11 | 32 | 17 | 136 | 96 | 0 | 16 | 0 | 30 | 0 | 47 | 47 | 0 | 0 | 20 | 78 | 0 | 112 | 17 | 0 | 10 | 305 | 24 | 5 | 0 | 112 | 150 | 0 | 68 | 0 | 35 | 0 | 25 | 34 | 6 | 397 | 18 | 35 | 51 | 0 | 87 | 17 | 45 | 34 | 9 | 50 | 387 | 35 | 0 | 17 | 34 | 0 | 17 | 0 | 17 | 17 | 250 | 17 | 0 | 310 | 24 | 150 |  | 912 | 0 | 150 | 0 | 16 | 120 | 0 | 0 | 10 | 38 | 8 | 132 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 153 | 0 | 414 | 36 | 0 | 50 | 15 | 34 | 0 | 0 | 56 | 1244 | 222 | 0 | 17 | 0 | 0 | 36 | 220 | 0 | 0 | 0 | 150 | 772 | 0 | 0 |  | 7388 | 5321 | 12709 | 4364 | 912 | 2018 | 150 | 1341 | 2836 | 130 | 556 | 242 | 136 | 0 | 24 | 1232.905 | 79.95
5:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 397 | 332 |  | 0 | 450 | 0 | 50 | 17 | 15 | 325 | 0 | 176 | 33 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 19 | 33 | 17 | 8 | 0 | 70 | 60 | 120 | 0 | 8 | 221 | 0 | 0 | 0 |  | 6 | 42 | 50 | 46 | 0 | 6 | 12 | 29 | 0 | 0 | 0 | 305 | 260 | 186 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 37 | 43 | 19 | 11 | 32 | 17 | 134 | 97 | 0 | 16 | 0 | 30 | 0 | 42 | 43 | 0 | 0 | 20 | 75 | 0 | 112 | 17 | 0 | 10 | 310 | 24 | 5 | 0 | 107 | 150 | 0 | 68 | 0 | 35 | 0 | 25 | 34 | 5 | 403 | 18 | 35 | 51 | 0 | 87 | 17 | 55 | 34 | 9 | 38 | 385 | 53 | 0 | 17 | 34 | 0 | 17 | 0 | 18 | 17 | 250 | 17 | 0 | 310 | 28 | 150 |  | 911 | 0 | 150 | 0 | 16 | 120 | 0 | 0 | 10 | 38 | 8 | 132 | 30 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 154 | 0 | 414 | 36 | 0 | 50 | 15 | 34 | 0 | 0 | 56 | 1244 | 222 | 0 | 17 | 0 | 0 | 36 | 220 | 0 | 0 | 0 | 150 | 774 | 0 | 0 |  | 7408 | 5323 | 12731 | 4379 | 911 | 2012 | 150 | 1352 | 2838 | 130 | 555 | 242 | 134 | 0 | 28 | 1116.395 | 79.94
6:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 397 | 332 |  | 0 | 450 | 0 | 50 | 17 | 15 | 333 | 0 | 179 | 33 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 19 | 33 | 16 | 8 | 0 | 70 | 60 | 120 | 0 | 8 | 223 | 0 | 0 | 0 |  | 6 | 42 | 50 | 46 | 0 | 6 | 12 | 30 | 0 | 0 | 0 | 280 | 260 | 182 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 37 | 43 | 19 | 11 | 32 | 17 | 126 | 98 | 0 | 16 | 0 | 30 | 0 | 42 | 46 | 0 | 0 | 20 | 75 | 0 | 112 | 17 | 0 | 10 | 300 | 24 | 5 | 0 | 112 | 0 | 0 | 68 | 0 | 35 | 0 | 25 | 34 | 6 | 367 | 18 | 35 | 51 | 0 | 87 | 17 | 55 | 34 | 9 | 38 | 385 | 53 | 2 | 17 | 34 | 0 | 17 | 2 | 17 | 17 | 250 | 17 | 0 | 300 | 25 | 150 |  | 911 | 0 | 150 | 0 | 16 | 120 | 0 | 0 | 10 | 38 | 8 | 132 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 155 | 0 | 414 | 36 | 0 | 50 | 15 | 34 | 0 | 0 | 56 | 1244 | 222 | 0 | 17 | 0 | 3 | 36 | 170 | 0 | 0 | 1 | 150 | 769 | 7 | 0 |  | 7188 | 5245 | 12433 | 4328 | 911 | 2000 | 0 | 1357 | 2793 | 130 | 506 | 242 | 126 | 15 | 25 | 1018.985 | 79.93
7:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 396 | 332 |  | 0 | 450 | 0 | 50 | 17 | 15 | 333 | 0 | 180 | 33 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 19 | 33 | 8 | 8 | 0 | 70 | 60 | 118 | 0 | 8 | 223 | 0 | 0 | 0 |  | 6 | 34 | 50 | 46 | 0 | 6 | 12 | 30 | 0 | 0 | 0 | 280 | 260 | 185 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 37 | 43 | 19 | 11 | 32 | 17 | 118 | 44 | 0 | 16 | 0 | 30 | 0 | 42 | 46 | 0 | 0 | 20 | 72 | 0 | 112 | 17 | 0 | 10 | 290 | 24 | 5 | 0 | 115 | 0 | 0 | 68 | 0 | 35 | 1 | 25 | 34 | 6 | 367 | 18 | 35 | 51 | 1 | 87 | 17 | 55 | 34 | 9 | 38 | 385 | 53 | 11 | 17 | 34 | 0 | 17 | 9 | 18 | 17 | 250 | 17 | 0 | 307 | 23 | 150 |  | 910 | 0 | 165 | 0 | 16 | 120 | 0 | 0 | 10 | 35 | 8 | 132 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 154 | 0 | 350 | 36 | 0 | 50 | 15 | 34 | 0 | 1 | 56 | 1244 | 222 | 0 | 17 | 0 | 17 | 36 | 50 | 0 | 0 | 8 | 150 | 780 | 24 | 0 |  | 7125 | 5121 | 12246 | 4281 | 910 | 1923 | 0 | 1361 | 2811 | 130 | 386 | 231 | 118 | 72 | 23 | 1006.57 | 79.92
8:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 397 | 331 |  | 0 | 450 | 0 | 44 | 17 | 15 | 327 | 0 | 186 | 33 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 19 | 33 | 16 | 8 | 0 | 70 | 60 | 118 | 0 | 8 | 221 | 0 | 0 | 0 |  | 6 | 34 | 50 | 46 | 0 | 6 | 12 | 8 | 0 | 0 | 0 | 300 | 260 | 166 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 37 | 43 | 19 | 11 | 25 | 17 | 120 | 44 | 0 | 16 | 1 | 30 | 0 | 42 | 46 | 0 | 0 | 20 | 72 | 0 | 112 | 17 | 0 | 10 | 305 | 24 | 5 | 0 | 112 | 0 | 0 | 68 | 0 | 35 | 5 | 25 | 34 | 5 | 385 | 19 | 35 | 51 | 1 | 88 | 17 | 55 | 34 | 9 | 38 | 380 | 40 | 27 | 17 | 34 | 0 | 17 | 18 | 17 | 17 | 250 | 17 | 0 | 352 | 26 | 150 |  | 911 | 0 | 155 | 0 | 16 | 120 | 0 | 0 | 10 | 20 | 8 | 132 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 152 | 0 | 394 | 36 | 0 | 50 | 15 | 34 | 0 | 3 | 56 | 1244 | 222 | 0 | 17 | 2 | 55 | 36 | 15 | 0 | 0 | 15 | 150 | 776 | 80 | 0 |  | 7189 | 5200 | 12389 | 4283 | 911 | 1956 | 0 | 1339 | 2852 | 130 | 349 | 216 | 120 | 207 | 26 | 1013.255 | 79.91
9:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 397 | 322 |  | 0 | 450 | 0 | 43 | 17 | 15 | 321 | 0 | 185 | 33 | 25 | 48 | 12 | 0 | 0 | 0 | 0 | 4 | 0 | 17 | 19 | 19 | 33 | 16 | 8 | 0 | 35 | 60 | 120 | 0 | 8 | 219 | 0 | 0 | 0 |  | 6 | 34 | 50 | 46 | 0 | 6 | 12 | 2 | 0 | 0 | 0 | 280 | 275 | 168 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 37 | 43 | 15 | 11 | 25 | 17 | 126 | 44 | 0 | 16 | 2 | 30 | 0 | 42 | 46 | 0 | 0 | 20 | 72 | 0 | 110 | 17 | 0 | 10 | 310 | 24 | 5 | 0 | 112 | 0 | 0 | 67 | 0 | 64 | 5 | 25 | 34 | 6 | 383 | 19 | 35 | 51 | 1 | 88 | 17 | 55 | 34 | 9 | 38 | 375 | 35 | 40 | 17 | 34 | 0 | 17 | 24 | 18 | 17 | 230 | 17 | 0 | 423 | 28 | 150 |  | 911 | 0 | 140 | 0 | 16 | 120 | 0 | 0 | 10 | 20 | 8 | 132 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 149 | 0 | 386 | 36 | 0 | 50 | 15 | 34 | 0 | 5 | 56 | 1215 | 222 | 0 | 17 | 3 | 50 | 36 | 15 | 0 | 0 | 13 | 136 | 779 | 116 | 0 |  | 7240 | 5160 | 12400 | 4222 | 911 | 1934 | 0 | 1379 | 2883 | 95 | 347 | 216 | 126 | 259 | 28 | 1098.25 | 79.9
10:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 398 | 322 |  | 0 | 450 | 0 | 42 | 17 | 15 | 320 | 0 | 179 | 33 | 25 | 48 | 21 | 0 | 0 | 0 | 17 | 17 | 0 | 17 | 19 | 22 | 33 | 16 | 8 | 0 | 70 | 60 | 110 | 0 | 10 | 226 | 0 | 0 | 0 |  | 6 | 34 | 50 | 46 | 0 | 6 | 12 | 2 | 0 | 0 | 0 | 280 | 300 | 172 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 37 | 43 | 15 | 11 | 25 | 17 | 140 | 44 | 0 | 16 | 2 | 30 | 0 | 41 | 41 | 0 | 0 | 20 | 72 | 0 | 110 | 17 | 0 | 9 | 300 | 16 | 5 | 0 | 112 | 10 | 0 | 67 | 0 | 71 | 5 | 25 | 56 | 6 | 368 | 19 | 35 | 51 | 2 | 88 | 17 | 55 | 34 | 9 | 25 | 365 | 35 | 49 | 54 | 34 | 0 | 28 | 27 | 26 | 17 | 230 | 53 | 0 | 430 | 28 | 126 |  | 912 | 0 | 140 | 0 | 16 | 115 | 0 | 0 | 10 | 20 | 0 | 122 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 147 | 0 | 365 | 35 | 0 | 70 | 15 | 96 | 0 | 6 | 113 | 1210 | 222 | 0 | 17 | 4 | 90 | 75 | 15 | 0 | 0 | 35 | 111 | 772 | 174 | 0 |  | 7416 | 5378 | 12794 | 4200 | 912 | 1898 | 10 | 1660 | 2829 | 130 | 341 | 252 | 140 | 394 | 28 | 1056.23 | 79.89
11:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 399 | 322 |  | 0 | 450 | 0 | 43 | 17 | 15 | 318 | 0 | 180 | 33 | 42 | 82 | 10 | 0 | 0 | 0 | 17 | 35 | 17 | 17 | 19 | 14 | 33 | 2 | 8 | 0 | 70 | 60 | 115 | 0 | 17 | 224 | 0 | 0 | 0 |  | 6 | 34 | 50 | 46 | 0 | 0 | 12 | 2 | 0 | 0 | 0 | 280 | 295 | 177 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 23 | 40 | 19 | 0 | 20 | 17 | 138 | 44 | 0 | 16 | 2 | 30 | 0 | 38 | 39 | 0 | 0 | 20 | 75 | 0 | 110 | 17 | 0 | 9 | 270 | 16 | 5 | 0 | 112 | 13 | 0 | 67 | 0 | 70 | 0 | 25 | 68 | 5 | 369 | 18 | 35 | 51 | 3 | 121 | 17 | 41 | 34 | 26 | 38 | 360 | 53 | 51 | 54 | 34 | 0 | 35 | 32 | 67 | 16 | 230 | 70 | 0 | 400 | 0 | 18 |  | 911 | 0 | 140 | 0 | 16 | 115 | 0 | 0 | 10 | 20 | 0 | 124 | 4 | 50 | 0 | 0 | 0 | 0 | 0 | 12 | 21 | 8 | 26 | 8 | 6 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 145 | 0 | 353 | 35 | 0 | 70 | 15 | 96 | 0 | 0 | 113 | 1230 | 222 | 0 | 17 | 5 | 100 | 102 | 15 | 0 | 0 | 21 | 63 | 769 | 170 | 0 |  | 7387 | 5441 | 12828 | 4165 | 911 | 1839 | 13 | 1884 | 2690 | 130 | 341 | 333 | 138 | 384 | 0 | 641.76 | 79.88
12:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 396 | 323 |  | 0 | 450 | 0 | 42 | 17 | 25 | 317 | 0 | 179 | 35 | 50 | 82 | 11 | 0 | 0 | 0 | 17 | 35 | 17 | 17 | 19 | 14 | 33 | 6 | 8 | 0 | 70 | 60 | 115 | 0 | 17 | 221 | 0 | 0 | 0 |  | 6 | 34 | 50 | 46 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 280 | 230 | 171 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 23 | 34 | 19 | 0 | 17 | 17 | 114 | 43 | 0 | 15 | 2 | 24 | 0 | 41 | 39 | 0 | 0 | 20 | 75 | 0 | 110 | 17 | 0 | 10 | 280 | 23 | 5 | 0 | 112 | 0 | 0 | 66 | 0 | 70 | 2 | 25 | 99 | 6 | 387 | 17 | 35 | 51 | 2 | 122 | 17 | 53 | 34 | 0 | 38 | 355 | 53 | 51 | 54 | 34 | 0 | 35 | 33 | 72 | 17 | 240 | 70 | 0 | 360 | 27 | 125 |  | 910 | 0 | 130 | 0 | 16 | 115 | 0 | 0 | 10 | 19 | 0 | 132 | 11 | 100 | 0 | 0 | 0 | 0 | 0 | 47 | 21 | 25 | 30 | 8 | 18 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 143 | 0 | 338 | 35 | 0 | 70 | 15 | 98 | 0 | 7 | 113 | 1230 | 220 | 0 | 17 | 5 | 56 | 113 | 15 | 0 | 0 | 19 | 40 | 760 | 168 | 0 |  | 7430 | 5467 | 12897 | 4093 | 910 | 1844 | 0 | 2001 | 2725 | 130 | 325 | 383 | 114 | 345 | 27 | 385 | 79.87
13:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 389 | 281 |  | 0 | 340 | 0 | 42 | 17 | 25 | 280 | 0 | 69 | 42 | 50 | 82 | 12 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 19 | 14 | 33 | 0 | 8 | 0 | 70 | 60 | 110 | 0 | 17 | 225 | 0 | 0 | 0 |  | 6 | 34 | 50 | 46 | 0 | 0 | 12 | 2 | 0 | 0 | 0 | 280 | 230 | 200 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 23 | 8 | 19 | 0 | 16 | 17 | 122 | 32 | 0 | 15 | 2 | 24 | 0 | 41 | 38 | 0 | 0 | 20 | 78 | 0 | 110 | 17 | 0 | 10 | 275 | 23 | 5 | 0 | 112 | 0 | 0 | 66 | 0 | 67 | 5 | 36 | 85 | 5 | 319 | 17 | 35 | 51 | 3 | 124 | 17 | 55 | 34 | 0 | 38 | 345 | 53 | 51 | 54 | 34 | 0 | 35 | 36 | 67 | 0 | 220 | 70 | 0 | 275 | 0 | 124 |  | 911 | 0 | 125 | 0 | 16 | 115 | 0 | 0 | 10 | 20 | 0 | 70 | 11 | 110 | 0 | 0 | 0 | 0 | 5 | 47 | 25 | 34 | 35 | 8 | 22 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 0 | 141 | 0 | 280 | 35 | 0 | 95 | 15 | 86 | 0 | 7 | 113 | 1100 | 182 | 0 | 17 | 5 | 2 | 112 | 15 | 0 | 0 | 32 | 0 | 829 | 152 | 0 |  | 6825 | 5199 | 12024 | 3697 | 911 | 1593 | 0 | 2011 | 2538 | 130 | 329 | 398 | 122 | 295 | 0 | 359 | 79.86
14:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 326 | 282 |  | 0 | 340 | 0 | 15 | 17 | 15 | 250 | 0 | 70 | 24 | 8 | 82 | 32 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 19 | 14 | 33 | 7 | 8 | 0 | 70 | 60 | 120 | 0 | 14 | 220 | 0 | 0 | 0 |  | 6 | 50 | 50 | 46 | 6 | 0 | 12 | 2 | 0 | 0 | 0 | 280 | 230 | 204 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 38 | 8 | 19 | 0 | 0 | 17 | 110 | 32 | 0 | 15 | 2 | 0 | 0 | 41 | 38 | 0 | 0 | 20 | 73 | 0 | 109 | 17 | 0 | 8 | 275 | 16 | 5 | 0 | 112 | 0 | 0 | 66 | 0 | 69 | 2 | 37 | 51 | 6 | 370 | 17 | 35 | 51 | 2 | 105 | 17 | 55 | 17 | 0 | 38 | 355 | 53 | 49 | 54 | 34 | 0 | 25 | 2 | 17 | 10 | 230 | 17 | 0 | 269 | 28 | 150 |  | 912 | 0 | 120 | 0 | 16 | 115 | 0 | 0 | 8 | 20 | 0 | 80 | 9 | 110 | 0 | 0 | 0 | 0 | 5 | 47 | 14 | 8 | 36 | 8 | 22 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 141 | 0 | 280 | 53 | 0 | 95 | 15 | 90 | 0 | 7 | 113 | 1070 | 182 | 0 | 17 | 5 | 8 | 112 | 15 | 0 | 0 | 19 | 0 | 919 | 200 | 0 |  | 6515 | 5229 | 11744 | 3649 | 912 | 1585 | 0 | 1771 | 2618 | 130 | 270 | 375 | 110 | 296 | 28 | 215.83 | 79.88
15:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 364 | 322 |  | 0 | 420 | 0 | 9 | 17 | 15 | 321 | 0 | 154 | 9 | 8 | 82 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 19 | 14 | 0 | 7 | 8 | 0 | 66 | 56 | 122 | 0 | 17 | 217 | 0 | 0 | 0 |  | 6 | 8 | 48 | 12 | 11 | 0 | 12 | 2 | 0 | 0 | 0 | 285 | 250 | 189 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 37 | 0 | 19 | 0 | 16 | 17 | 118 | 32 | 0 | 15 | 2 | 0 | 0 | 41 | 38 | 0 | 0 | 28 | 78 | 0 | 109 | 17 | 0 | 8 | 285 | 16 | 0 | 0 | 112 | 0 | 0 | 66 | 0 | 69 | 2 | 37 | 51 | 5 | 384 | 17 | 35 | 51 | 2 | 65 | 17 | 55 | 0 | 0 | 12 | 355 | 35 | 42 | 54 | 34 | 0 | 17 | 23 | 17 | 17 | 230 | 17 | 0 | 283 | 30 | 0 |  | 911 | 0 | 120 | 0 | 0 | 115 | 0 | 0 | 5 | 0 | 0 | 132 | 8 | 16 | 0 | 0 | 0 | 0 | 21 | 47 | 14 | 8 | 36 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 140 | 0 | 324 | 17 | 0 | 95 | 0 | 80 | 0 | 6 | 113 | 1090 | 220 | 0 | 0 | 1 | 30 | 112 | 15 | 0 | 0 | 27 | 0 | 1010 | 82 | 0 |  | 6514 | 5185 | 11699 | 3902 | 911 | 1801 | 0 | 1410 | 2593 | 122 | 270 | 325 | 118 | 217 | 30 | 109.825 | 79.83
16:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 396 | 330 |  | 0 | 450 | 0 | 8 | 17 | 15 | 320 | 0 | 175 | 9 | 8 | 82 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 19 | 14 | 25 | 23 | 8 | 0 | 66 | 56 | 116 | 0 | 17 | 217 | 0 | 0 | 0 |  | 1 | 8 | 50 | 12 | 12 | 0 | 12 | 2 | 0 | 0 | 0 | 280 | 265 | 184 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 37 | 0 | 19 | 0 | 25 | 17 | 116 | 32 | 0 | 0 | 1 | 10 | 0 | 44 | 43 | 0 | 0 | 30 | 81 | 0 | 109 | 17 | 0 | 8 | 310 | 23 | 0 | 0 | 112 | 0 | 0 | 66 | 0 | 69 | 9 | 25 | 54 | 6 | 368 | 17 | 35 | 51 | 2 | 120 | 17 | 55 | 0 | 0 | 12 | 355 | 48 | 22 | 54 | 34 | 0 | 17 | 6 | 17 | 17 | 230 | 17 | 0 | 280 | 30 | 0 |  | 911 | 0 | 115 | 0 | 16 | 115 | 0 | 0 | 8 | 0 | 8 | 132 | 7 | 32 | 0 | 0 | 0 | 0 | 15 | 0 | 14 | 8 | 0 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 140 | 0 | 325 | 35 | 0 | 95 | 15 | 85 | 0 | 4 | 113 | 1172 | 220 | 0 | 5 | 0 | 14 | 112 | 15 | 0 | 0 | 19 | 0 | 732 | 4 | 0 |  | 6796 | 4889 | 11685 | 4066 | 911 | 1875 | 0 | 1566 | 2394 | 122 | 283 | 241 | 116 | 81 | 30 | 176.675 | 79.81
17:00 | 0 | 0 | 160 | 180 | 0 | 12 | 0 | 397 | 302 |  | 0 | 380 | 0 | 9 | 17 | 15 | 321 | 0 | 75 | 9 | 8 | 64 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 19 | 14 | 25 | 23 | 8 | 0 | 70 | 60 | 122 | 0 | 17 | 219 | 0 | 0 | 0 |  | 3 | 8 | 50 | 12 | 15 | 0 | 12 | 10 | 0 | 0 | 0 | 290 | 280 | 190 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 19 | 0 | 25 | 17 | 110 | 46 | 0 | 0 | 0 | 30 | 0 | 44 | 45 | 80 | 0 | 30 | 86 | 0 | 109 | 17 | 0 | 8 | 270 | 24 | 5 | 0 | 45 | 0 | 0 | 68 | 0 | 70 | 3 | 12 | 84 | 6 | 368 | 18 | 35 | 17 | 1 | 85 | 17 | 34 | 0 | 0 | 12 | 355 | 53 | 3 | 54 | 34 | 0 | 17 | 4 | 32 | 17 | 230 | 17 | 0 | 250 | 30 | 0 |  | 910 | 0 | 120 | 0 | 16 | 115 | 0 | 0 | 5 | 0 | 0 | 80 | 7 | 16 | 0 | 0 | 0 | 0 | 19 | 0 | 20 | 8 | 0 | 8 | 30 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 145 | 0 | 334 | 17 | 0 | 95 | 15 | 103 | 0 | 2 | 113 | 1120 | 168 | 0 | 17 | 1 | 10 | 95 | 31 | 0 | 0 | 7 | 0 | 731 | 12 | 0 |  | 6480 | 4720 | 11200 | 3947 | 910 | 1789 | 0 | 1451 | 2311 | 130 | 286 | 193 | 110 | 43 | 30 | 45.84 | 79.79
18:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 397 | 302 |  | 0 | 340 | 0 | 8 | 17 | 0 | 280 | 0 | 72 | 9 | 8 | 64 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 17 | 19 | 22 | 25 | 23 | 8 | 0 | 40 | 60 | 114 | 0 | 18 | 222 | 0 | 0 | 0 |  | 6 | 8 | 50 | 12 | 25 | 0 | 12 | 25 | 0 | 0 | 0 | 280 | 270 | 180 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 23 | 0 | 19 | 0 | 25 | 17 | 104 | 51 | 0 | 16 | 0 | 30 | 0 | 44 | 45 | 80 | 0 | 30 | 86 | 0 | 111 | 17 | 0 | 9 | 280 | 24 | 5 | 0 | 45 | 0 | 0 | 55 | 0 | 70 | 0 | 12 | 120 | 5 | 318 | 18 | 35 | 17 | 0 | 85 | 17 | 30 | 0 | 0 | 12 | 355 | 53 | 3 | 54 | 34 | 0 | 17 | 1 | 87 | 17 | 230 | 17 | 0 | 213 | 29 | 0 |  | 910 | 0 | 120 | 0 | 16 | 115 | 0 | 0 | 12 | 0 | 0 | 80 | 9 | 16 | 0 | 0 | 0 | 0 | 24 | 16 | 20 | 8 | 0 | 8 | 30 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 144 | 0 | 357 | 35 | 0 | 100 | 15 | 104 | 0 | 1 | 113 | 1110 | 167 | 0 | 17 | 0 | 2 | 95 | 81 | 0 | 0 | 2 | 0 | 803 | 12 | 0 |  | 6368 | 4910 | 11278 | 3843 | 910 | 1799 | 0 | 1546 | 2346 | 100 | 336 | 244 | 104 | 21 | 29 | 20.055 | 79.77
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 190 | 180 | 0 | 12 | 0 | 361 | 336 |  | 0 | 420 | 0 | 9 | 36 | 13 | 290 | 0 | 128 | 10 | 48 | 98 | 4 | 0 | 0 | 0 | 35 | 35 | 0 | 19 | 19 | 22 | 25 | 23 | 25 | 0 | 70 | 60 | 121 | 0 | 25 | 217 | 0 | 0 | 0 |  | 6 | 40 | 50 | 58 | 34 | 0 | 12 | 27 | 0 | 0 | 0 | 330 | 330 | 200 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 37 | 2 | 19 | 0 | 25 | 17 | 136 | 67 | 0 | 16 | 0 | 30 | 0 | 49 | 46 | 80 | 0 | 30 | 86 | 0 | 111 | 17 | 0 | 9 | 300 | 24 | 8 | 0 | 55 | 0 | 0 | 83 | 0 | 92 | 0 | 26 | 120 | 21 | 404 | 84 | 105 | 17 | 0 | 170 | 17 | 36 | 53 | 0 | 36 | 355 | 59 | 0 | 162 | 44 | 0 | 17 | 0 | 115 | 24 | 335 | 70 | 0 | 115 | 29 | 0 |  | 911 | 0 | 120 | 0 | 16 | 115 | 0 | 0 | 25 | 55 | 8 | 132 | 14 | 16 | 0 | 0 | 0 | 35 | 24 | 92 | 20 | 8 | 34 | 8 | 30 | 0 | 0 | 8 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 144 | 0 | 343 | 35 | 0 | 113 | 42 | 105 | 0 | 0 | 113 | 1170 | 220 | 0 | 62 | 0 | 0 | 100 | 86 | 0 | 0 | 0 | 0 | 960 | 0 | 0 |  | 7714 | 5544 | 13258 | 4329 | 911 | 1985 | 0 | 2322 | 2485 | 130 | 341 | 590 | 136 | 0 | 29 | 31.515 | 79.71
19:30 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 399 | 343 |  | 0 | 420 | 0 | 50 | 51 | 15 | 323 | 0 | 125 | 20 | 85 | 115 | 11 | 0 | 0 | 0 | 35 | 35 | 17 | 19 | 19 | 22 | 25 | 23 | 25 | 0 | 70 | 60 | 118 | 0 | 25 | 225 | 0 | 0 | 0 |  | 6 | 48 | 50 | 58 | 34 | 0 | 12 | 20 | 0 | 0 | 0 | 280 | 270 | 180 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 37 | 8 | 19 | 0 | 25 | 17 | 134 | 82 | 0 | 16 | 0 | 30 | 0 | 49 | 46 | 80 | 0 | 30 | 86 | 0 | 112 | 17 | 0 | 9 | 255 | 24 | 11 | 0 | 95 | 0 | 0 | 85 | 0 | 149 | 0 | 100 | 120 | 40 | 368 | 84 | 105 | 17 | 0 | 221 | 17 | 51 | 70 | 0 | 88 | 355 | 72 | 0 | 162 | 68 | 0 | 17 | 0 | 115 | 17 | 288 | 140 | 0 | 0 | 28 | 0 |  | 911 | 0 | 130 | 0 | 16 | 115 | 0 | 0 | 39 | 60 | 8 | 132 | 16 | 16 | 0 | 0 | 0 | 35 | 24 | 92 | 21 | 25 | 36 | 8 | 22 | 0 | 0 | 8 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 145 | 0 | 349 | 40 | 0 | 113 | 50 | 105 | 0 | 0 | 113 | 1244 | 220 | 0 | 100 | 0 | 0 | 115 | 79 | 0 | 0 | 0 | 0 | 1066 | 0 | 0 |  | 8037 | 5833 | 13870 | 4239 | 911 | 1948 | 0 | 2898 | 2550 | 130 | 334 | 698 | 134 | 0 | 28 | 95.5 | 0
20:00 | 0 | 0 | 206 | 180 | 0 | 12 | 0 | 397 | 301 |  | 0 | 420 | 0 | 44 | 51 | 15 | 324 | 0 | 126 | 30 | 102 | 130 | 11 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 19 | 22 | 25 | 23 | 25 | 0 | 70 | 60 | 112 | 0 | 25 | 224 | 0 | 0 | 0 |  | 6 | 48 | 50 | 12 | 31 | 0 | 12 | 31 | 0 | 0 | 0 | 280 | 270 | 180 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 37 | 8 | 19 | 0 | 25 | 17 | 134 | 82 | 0 | 16 | 0 | 30 | 0 | 50 | 46 | 80 | 0 | 30 | 86 | 0 | 112 | 17 | 0 | 9 | 260 | 24 | 11 | 0 | 95 | 0 | 0 | 87 | 0 | 144 | 0 | 100 | 145 | 45 | 368 | 84 | 105 | 17 | 0 | 220 | 27 | 48 | 26 | 0 | 38 | 328 | 72 | 0 | 162 | 68 | 0 | 17 | 0 | 114 | 22 | 285 | 142 | 0 | 0 | 29 | 0 |  | 870 | 0 | 125 | 0 | 16 | 115 | 0 | 0 | 35 | 60 | 8 | 124 | 15 | 16 | 0 | 0 | 0 | 35 | 24 | 92 | 21 | 34 | 39 | 8 | 22 | 0 | 0 | 8 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 146 | 0 | 367 | 45 | 0 | 113 | 50 | 105 | 0 | 0 | 113 | 1244 | 217 | 0 | 100 | 0 | 0 | 115 | 84 | 0 | 0 | 0 | 0 | 1162 | 0 | 0 |  | 7922 | 5898 | 13820 | 4186 | 870 | 1937 | 0 | 2845 | 2636 | 130 | 339 | 714 | 134 | 0 | 29 | 124.15 | 79.73
21:00 | 0 | 0 | 144 | 180 | 0 | 12 | 0 | 399 | 332 |  | 0 | 450 | 0 | 28 | 51 | 15 | 325 | 0 | 95 | 62 | 66 | 130 | 10 | 0 | 0 | 0 | 35 | 35 | 17 | 19 | 19 | 22 | 25 | 23 | 25 | 0 | 70 | 60 | 116 | 0 | 25 | 225 | 0 | 0 | 0 |  | 6 | 50 | 50 | 25 | 32 | 0 | 12 | 33 | 0 | 0 | 0 | 280 | 270 | 180 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 37 | 8 | 19 | 11 | 25 | 20 | 128 | 82 | 0 | 16 | 0 | 30 | 10 | 50 | 46 | 80 | 0 | 28 | 86 | 0 | 112 | 17 | 0 | 9 | 260 | 24 | 10 | 0 | 105 | 0 | 0 | 88 | 0 | 147 | 0 | 100 | 155 | 55 | 368 | 84 | 105 | 17 | 0 | 220 | 36 | 55 | 17 | 0 | 38 | 328 | 72 | 0 | 162 | 68 | 0 | 17 | 0 | 114 | 24 | 285 | 142 | 0 | 0 | 29 | 0 |  | 870 | 0 | 130 | 0 | 16 | 115 | 0 | 0 | 26 | 58 | 8 | 130 | 15 | 16 | 0 | 0 | 0 | 35 | 35 | 90 | 21 | 34 | 35 | 8 | 22 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 147 | 0 | 363 | 53 | 0 | 113 | 50 | 105 | 0 | 0 | 113 | 1244 | 217 | 0 | 100 | 0 | 0 | 115 | 108 | 0 | 0 | 0 | 0 | 1154 | 0 | 0 |  | 7935 | 5894 | 13829 | 4134 | 870 | 1996 | 0 | 2871 | 2598 | 130 | 363 | 710 | 128 | 0 | 29 | 211.055 | 79.71
22:00 | 0 | 0 | 150 | 180 | 0 | 12 | 0 | 399 | 331 |  | 0 | 450 | 0 | 9 | 34 | 15 | 327 | 0 | 103 | 39 | 32 | 130 | 15 | 0 | 0 | 0 | 35 | 35 | 7 | 19 | 19 | 22 | 25 | 23 | 25 | 0 | 70 | 60 | 118 | 0 | 25 | 221 | 0 | 0 | 0 |  | 6 | 50 | 50 | 25 | 36 | 30 | 12 | 36 | 0 | 0 | 0 | 300 | 290 | 189 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 37 | 8 | 20 | 11 | 25 | 20 | 134 | 82 | 0 | 16 | 0 | 30 | 10 | 50 | 46 | 80 | 0 | 25 | 84 | 0 | 112 | 17 | 0 | 9 | 290 | 24 | 5 | 0 | 115 | 0 | 0 | 88 | 0 | 149 | 0 | 100 | 155 | 62 | 372 | 84 | 105 | 17 | 0 | 170 | 36 | 55 | 17 | 0 | 38 | 355 | 72 | 0 | 162 | 68 | 0 | 17 | 0 | 115 | 17 | 295 | 70 | 0 | 0 | 30 | 0 |  | 783 | 0 | 130 | 0 | 16 | 115 | 0 | 0 | 21 | 58 | 0 | 132 | 18 | 16 | 0 | 0 | 0 | 35 | 23 | 90 | 21 | 34 | 35 | 8 | 23 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 147 | 0 | 370 | 53 | 0 | 113 | 50 | 105 | 0 | 0 | 113 | 1244 | 220 | 0 | 54 | 0 | 0 | 115 | 107 | 0 | 0 | 0 | 0 | 1153 | 0 | 0 |  | 7896 | 5750 | 13646 | 4233 | 783 | 2039 | 0 | 2716 | 2597 | 130 | 362 | 622 | 134 | 0 | 30 | 242.57 | 79.69
23:00 | 0 | 0 | 150 | 180 | 0 | 12 | 0 | 399 | 333 |  | 0 | 450 | 0 | 8 | 22 | 15 | 326 | 0 | 102 | 32 | 32 | 130 | 23 | 0 | 0 | 0 | 35 | 35 | 17 | 0 | 19 | 22 | 25 | 8 | 25 | 0 | 70 | 60 | 110 | 0 | 17 | 220 | 0 | 0 | 0 |  | 6 | 50 | 50 | 25 | 0 | 44 | 12 | 36 | 0 | 0 | 0 | 300 | 290 | 175 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 37 | 8 | 20 | 11 | 25 | 20 | 144 | 54 | 0 | 16 | 0 | 30 | 10 | 50 | 46 | 80 | 0 | 20 | 84 | 0 | 112 | 17 | 0 | 9 | 300 | 24 | 9 | 0 | 115 | 0 | 0 | 68 | 0 | 149 | 0 | 100 | 155 | 51 | 386 | 28 | 105 | 17 | 0 | 170 | 36 | 55 | 17 | 0 | 38 | 355 | 72 | 0 | 162 | 68 | 0 | 17 | 0 | 115 | 17 | 260 | 70 | 0 | 0 | 22 | 0 |  | 782 | 0 | 130 | 0 | 16 | 115 | 0 | 0 | 21 | 53 | 0 | 132 | 14 | 16 | 0 | 0 | 0 | 35 | 23 | 90 | 21 | 25 | 36 | 8 | 23 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 147 | 0 | 376 | 53 | 0 | 113 | 50 | 105 | 0 | 0 | 113 | 1244 | 222 | 0 | 54 | 0 | 0 | 114 | 107 | 0 | 0 | 0 | 0 | 1184 | 0 | 0 |  | 7682 | 5770 | 13452 | 4124 | 782 | 2055 | 0 | 2587 | 2628 | 130 | 362 | 618 | 144 | 0 | 22 | 332.34 | 79.67
24:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 399 | 332 |  | 0 | 450 | 0 | 8 | 17 | 15 | 326 | 0 | 187 | 32 | 102 | 130 | 30 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 19 | 14 | 25 | 8 | 8 | 0 | 70 | 60 | 122 | 0 | 17 | 219 | 0 | 0 | 0 |  | 6 | 50 | 50 | 46 | 0 | 46 | 12 | 36 | 0 | 0 | 0 | 290 | 250 | 175 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 28 | 34 | 20 | 11 | 32 | 20 | 132 | 67 | 0 | 16 | 0 | 30 | 10 | 50 | 46 | 112 | 0 | 20 | 84 | 0 | 112 | 17 | 0 | 9 | 310 | 24 | 9 | 0 | 115 | 0 | 0 | 68 | 0 | 63 | 0 | 25 | 110 | 13 | 386 | 19 | 35 | 17 | 0 | 190 | 36 | 55 | 88 | 0 | 88 | 355 | 54 | 0 | 144 | 68 | 0 | 17 | 0 | 85 | 17 | 240 | 70 | 0 | 0 | 28 | 0 |  | 782 | 0 | 135 | 0 | 16 | 115 | 0 | 0 | 10 | 50 | 0 | 130 | 13 | 16 | 0 | 0 | 0 | 0 | 23 | 27 | 21 | 34 | 28 | 8 | 23 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 147 | 0 | 369 | 54 | 0 | 113 | 105 | 105 | 0 | 0 | 113 | 1244 | 223 | 0 | 54 | 0 | 0 | 113 | 109 | 0 | 0 | 0 | 0 | 1196 | 0 | 0 |  | 7644 | 5724 | 13368 | 4225 | 782 | 2089 | 0 | 2489 | 2640 | 130 | 364 | 489 | 132 | 0 | 28 | 412.56 | 0
KWH | 0 | 0 | 4450847 | 4315500 | 0 | 288545 | 0 | 9510910 | 7762000 |  | 0 | 9884300 | 0 | 751680 | 463493 | 380346 | 7618858 | 0 | 3744000 | 664320 | 747936 | 1799520 | 222362 | 0 | 0 | 0 | 386172 | 525969 | 285061 | 297432 | 456000 | 411480 | 651240 | 366600 | 281318 | 0 | 1580160 | 1444000 | 2700000 | 0 | 358417 | 5183038 | 0 | 0 | 0 |  | 140640 | 844704 | 1193680 | 826680 | 214080 | 210720 | 250416 | 444480 | 0 | 0 | 0 | 7290600 | 6483000 | 4463000 | 0 | 0 | 0 | 0 | 0 | 948056 | 0 | 780496 | 588643 | 441136 | 158040 | 534700 | 404760 | 3001920 | 1464000 | 0 | 342504 | 16350 | 624000 | 24960 | 1068600 | 1052640 | 636054 | 0 | 554112 | 1846084 | 0 | 2681190 | 380000 | 0 | 218160 | 7193500 | 533976 | 132288 | 0 | 2561780 | 1231708 | 0 | 1639200 | 0 | 1739088 | 41985 | 925440 | 1889280 | 373018 | 8996000 | 718800 | 1172189 | 1009491 | 21117 | 2913055 | 526871 | 1271279 | 664620 | 112560 | 912960 | 8768200 | 1230720 | 398750 | 1530720 | 1032027 | 0 | 511560 | 203683 | 1234560 | 435600 | 6170800 | 1006981 | 0 | 5901818 | 541440 | 1658181 |  | 21460363 | 0 | 3507264 | 0 | 360000 | 2916666 | 0 | 0 | 276480 | 678528 | 104250 | 2914000 | 421567 | 725760 | 0 | 0 | 0 | 185380 | 306632 | 682072 | 480890 | 308471 | 374716 | 200515 | 276726 | 0 | 0 | 159498 | 0 | 0 | 4973000 | 0 | 0 | 0 | 0 | 0 | 4540127 | 0 | 0 | 3780291 | 0 | 8753381 | 938016 | 0 | 1967904 | 617472 | 1812892 | 0 | 55750 | 2148480 | 30867700 | 5122309 | 0 | 884400 | 37080 | 425520 | 1873152 | 2071840 | 0 | 0 | 232602 | 1680000 | 17863636 | 1094110 | 0 |  | 174865154 | 128079440 | 302944594 | 100764640 | 21460363 | 45639676 | 1231708 | 43874857 | 62944335 | 3024160 | 9528633 | 8405915 | 3001920 | 2526947 | 541440 | 0
Fuel Cost | 0 | 0 | 6498236.62 | 6430095 | 0 | 383764.85 | 0 | 9986455.5 | 8382960 |  | 0 | 10773887 | 0 | 8403782.4 | 6141282.25 | 5039584.5 | 8533120.96 | 0 | 6552000 | 9712358.4 | 10523459.52 | 29170219.2 | 2050177.64 | 0 | 0 | 0 | 4912107.84 | 7100581.5 | 3822668.01 | 223074 | 342000 | 0 | 0 | 0 | 4785219.18 | 0 | 426643.2 | 389880 | 5103000 | 0 | 5860117.95 | 5390359.52 | 0 | 0 | 0 |  | 1835352 | 14089662.72 | 20316433.6 | 11168446.8 | 2714534.4 | 2438030.4 | 318028.32 | 1480118.4 | 0 | 0 | 0 | 8092566 | 7066470 | 5177080 | 0 | 0 | 0 | 0 | 0 | 1583253.52 | 0 | 13479165.92 | 7917248.35 | 604356.32 | 118530 | 935725 | 303570 | 21553785.6 | 1595760 | 0 | 465805.44 | 260619 | 854880 | 32947.2 | 1859364 | 1821067.2 | 731462.1 | 0 | 1074977.28 | 4209071.52 | 0 | 2708001.9 | 817000 | 0 | 431956.8 | 7193500 | 400482 | 100538.88 | 0 | 34968297 | 25816599.68 | 0 | 22096416 | 0 | 24086368.8 | 490804.65 | 9550540.8 | 25807564.8 | 4949948.86 | 8276320 | 8740608 | 16949852.94 | 12770061.15 | 0 | 34199265.7 | 5737625.19 | 13513695.77 | 9018893.4 | 1450898.4 | 10754668.8 | 8066744 | 15937824 | 5761937.5 | 19424836.8 | 11744467.26 | 0 | 6680973.6 | 2434011.85 | 18481363.2 | 5736852 | 0 | 0 | 0 | 0 | 0 | 0 |  | 64381089 | 0 | 3928135.68 | 0 | 3747600 | 48124989 | 0 | 0 | 4979404.8 | 12213504 | 1498072.5 | 3263680 | 817839.98 | 7910784 | 0 | 0 | 0 | 3108822.6 | 5362993.68 | 10667606.08 | 3702853 | 5108279.76 | 6336447.56 | 2733019.45 | 4668367.62 | 0 | 0 | 120739.986 | 0 | 0 | 26307170 | 0 | 0 | 0 | 0 | 0 | 79270617.42 | 0 | 0 | 4385137.56 | 0 | 8665847.19 | 12606935.04 | 0 | 23280304.32 | 8922470.4 | 23023728.4 | 0 | 616037.5 | 26082547.2 | 278117977 | 5224755.18 | 0 | 6544560 | 419374.8 | 4991349.6 | 28715420.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 676134265.86 | 729848460.466 | 1405982726.326 | 107765817.166 | 64381089 | 53558847.74 | 25816599.68 | 560902547.84 | 304425147 | 816523.2 | 127395606.42 | 124392627.78 | 21553785.6 | 14974134.9 | 0 | 0
Yesterday Day Peak | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 396 | 323 |  | 0 | 450 | 0 | 42 | 17 | 25 | 317 | 0 | 179 | 35 | 50 | 82 | 11 | 0 | 0 | 0 | 17 | 35 | 17 | 17 | 19 | 14 | 33 | 6 | 8 | 0 | 70 | 60 | 115 | 0 | 17 | 221 | 0 | 0 | 0 |  | 6 | 34 | 50 | 46 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 280 | 230 | 171 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 23 | 34 | 19 | 0 | 17 | 17 | 114 | 43 | 0 | 15 | 2 | 24 | 0 | 41 | 39 | 0 | 0 | 20 | 75 | 0 | 110 | 17 | 0 | 10 | 280 | 23 | 5 | 0 | 112 | 0 | 0 | 66 | 0 | 70 | 2 | 25 | 99 | 6 | 387 | 17 | 35 | 51 | 2 | 122 | 17 | 53 | 34 | 0 | 38 | 355 | 53 | 51 | 54 | 34 | 0 | 35 | 33 | 72 | 17 | 240 | 70 | 0 | 360 | 27 | 125 |  | 910 | 0 | 130 | 0 | 16 | 115 | 0 | 0 | 10 | 19 | 0 | 132 | 11 | 100 | 0 | 0 | 0 | 0 | 0 | 47 | 21 | 25 | 30 | 8 | 18 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 143 | 0 | 338 | 35 | 0 | 70 | 15 | 98 | 0 | 7 | 113 | 1230 | 220 | 0 | 17 | 5 | 56 | 113 | 15 | 0 | 0 | 19 | 40 | 760 | 168 | 0 |  | 12897 | DayPeak
Yesterday Evening Peak | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 399 | 343 | 0 | 0 | 420 | 0 | 50 | 51 | 15 | 323 | 0 | 125 | 20 | 85 | 115 | 11 | 0 | 0 | 0 | 35 | 35 | 17 | 19 | 19 | 22 | 25 | 23 | 25 | 0 | 70 | 60 | 118 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 6 | 48 | 50 | 58 | 34 | 0 | 12 | 20 | 0 | 0 | 0 | 280 | 270 | 180 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 37 | 8 | 19 | 0 | 25 | 17 | 134 | 82 | 0 | 16 | 0 | 30 | 0 | 49 | 46 | 80 | 0 | 30 | 86 | 0 | 112 | 17 | 0 | 9 | 255 | 24 | 11 | 0 | 95 | 0 | 0 | 85 | 0 | 149 | 0 | 100 | 120 | 40 | 368 | 84 | 105 | 17 | 0 | 221 | 17 | 51 | 70 | 0 | 88 | 355 | 72 | 0 | 162 | 68 | 0 | 17 | 0 | 115 | 17 | 288 | 140 | 0 | 0 | 28 | 0 |  | 911 | 0 | 130 | 0 | 16 | 115 | 0 | 0 | 39 | 60 | 8 | 132 | 16 | 16 | 0 | 0 | 0 | 35 | 24 | 92 | 21 | 25 | 36 | 8 | 22 | 0 | 0 | 8 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 145 | 0 | 349 | 40 | 0 | 113 | 50 | 105 | 0 | 0 | 113 | 1244 | 220 | 0 | 100 | 0 | 0 | 115 | 79 | 0 | 0 | 0 | 0 | 1066 | 0 | 0 |  | 13870 | EvPeak
Forecast for Evening | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 360 | 330 | 0 | 0 | 450 | 0 | 50 | 51 | 15 | 330 | 0 | 195 | 75 | 102 | 130 | 50 | 0 | 0 | 0 | 34 | 35 | 55 | 17 | 19 | 22 | 33 | 24 | 25 | 0 | 70 | 60 | 120 | 0 | 25 | 225 |  | 0 | 0 | 0 | 6 | 40 | 50 | 80 | 24 | 46 | 12 | 30 | 0 | 0 | 0 | 280 | 260 | 180 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 46 | 43 | 20 | 11 | 33 | 20 | 169 | 98 | 0 | 18 | 0 | 30 | 30 | 50 | 48 | 112 | 0 | 30 | 86 | 0 | 112 | 17 | 0 | 10 | 300 | 24 | 11 | 0 | 112 | 200 | 0 | 85 | 0 | 149 | 0 | 100 | 150 | 60 | 400 | 85 | 105 | 51 | 0 | 300 | 36 | 54 | 106 | 113 | 88 | 350 | 72 | 0 | 162 | 68 | 0 | 17 |  | 115 | 17 | 250 | 144 |  | 0 | 10 | 0 |  | 918 | 0 | 155 |  | 16 | 120 | 0 | 0 | 30 | 55 | 40 | 120 | 34 | 110 | 0 | 0 | 0 | 35 | 32 | 90 | 21 | 34 | 35 | 8 | 33 | 0 | 0 | 8 | 0 | 0 | 230 | 0 | 0 | 0 |  | 0 | 220 | 0 | 0 | 181 | 0 | 414 | 53 | 0 | 113 | 105 | 105 | 0 | 0 | 113 | 1244 | 220 |  | 150 |  |  | 115 | 120 |  | 0 |  | 0 | 1200 |  | 0
Forecast for Day | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 360 | 325 | 0 | 0 | 450 | 0 | 42 | 17 | 15 | 330 | 0 | 195 | 50 | 102 | 64 | 50 | 0 | 0 | 0 | 17 | 35 | 35 | 17 | 19 | 19 | 33 | 16 | 8 | 0 | 70 | 60 | 120 | 0 | 17 | 220 |  | 0 | 0 | 0 | 6 | 24 | 50 | 36 | 0 | 6 | 12 | 2 | 0 | 0 | 0 | 280 | 260 | 170 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 44 | 43 | 20 | 11 | 25 | 20 | 146 | 50 | 0 | 18 | 1.6 | 30 | 10 | 50 | 48 | 112 | 0 | 25 | 80 | 0 | 112 | 17 | 0 | 10 | 300 | 24 | 11 | 0 | 112 | 0 | 0 | 68 | 0 | 70 | 20 | 25 | 68 | 6 | 400 | 18 | 35 | 51 | 5 | 120 | 36 | 54 | 52 | 0 | 38 | 350 | 53 | 50 | 54 | 34 | 0 | 17 | 35 | 72 | 17 | 250 | 54 |  | 0 | 20 | 0 |  | 918 | 0 | 155 | 0 | 16 | 120 | 0 | 0 | 20 | 40 | 32 | 120 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 21 | 34 | 36 | 8 | 20 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 160 | 0 | 414 | 53 | 0 | 113 | 50 | 105 | 0 | 8 | 113 | 1244 | 220 |  | 17 | 6 | 100 | 115 | 120 |  | 0 | 30 | 0 | 1200 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 170 | 180 | 0 | 12 | 0 | 359 | 325 | 0 | 0 | 420 | 0 | 8 | 17 | 15 | 322 | 0 | 193 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 25 | 24 | 8 | 0 | 70 | 60 | 115 | 0 | 17 | 215 | 0 | 0 | 0 | 0 | 6 | 0 | 33 | 36 | 0 | 6 | 11 | 2 | 0 | 0 | 0 | 270 | 240 | 155 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 30 | 16 | 19 | 11 | 25 | 18 | 116 | 44 | 0 | 16 | 1 | 30 | 10 | 47 | 47 | 112 | 0 | 25 | 78 | 0 | 112 | 17 | 0 | 9 | 310 | 24 | 0 | 0 | 112 | 0 | 0 | 68 | 0 | 38 | 0 | 25 | 34 | 6 | 407 | 18 | 35 | 17 | 1 | 87 | 17 | 55 | 52 | 0 | 38 | 355 | 35 | 12 | 17 | 34 | 0 | 17 | 9 | 18 | 17 | 225 | 17 | 0 | 0 | 22 | 0 | 0 | 897 | 0 | 155 | 0 | 0 | 116 | 0 | 0 | 0 | 0 | 0 | 132 | 14 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 8 | 23 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 149 | 0 | 350 | 53 | 0 | 70 | 15 | 70 | 0 | 2 | 70 | 1010 | 170 | 0 | 17 | 1 | 15 | 56 | 110 | 0 | 0 | 6 | 0 | 1148 | 31 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
292.3904
| Minimum Generation |  | 12246 | 7:00
| Highest Generation |  | 13870 | 19:30
| Day Peak Generation |  | 12897 | 12:00
| Evening Peak Generation |  | 13870 | 19:30
| HVDC Max Flow |  | 912 | 4:00
| HVDC EvPeak Flow |  | 911 | 19:30
| Load factor L.F |  | 91.01% | [164 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-08-02
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-08-01 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 12897 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 11306
Evening Peak Generation : |  |  | 13870 | MW Hour : | 19:30 | Available Max Generation : |  | 15549
E.P. Demand (at gen end) : |  |  | 13970 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 14800
Maximum Generation : |  |  | 13870 | MW Hour : | 19:30 | Reserve(Generation end) |  | 749
Total Gen. (MKWH) : |  |  | 302.9446 | System Load Factor : | 91.01% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 670 | MW at | 3:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-08-02
Actual : |  | 79.53 | Ft.(MSL) , | Rule curve : | 89.32 | Ft.( MSL )
Gas Consumed : |  | Total = | 1109.89 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 161324664.906
: |  |  | Coal : | 304425147 | Oil : | 838507381.72 | Total : | 1304257193.626
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 10 | 240:00 | 4954.5545 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1363.7216 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1911.0082 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1661.6578 |  |  | 0 | 0%
Cumilla Area |  | 36 | 864:00 | 1366.9193 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 1016.9903 |  |  | 0 | 0%
Sylhet Area |  | 25 | 600:00 | 569.6834 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 475.102 |  |  | 0 | 0%
Rangpur Area |  | 25 | 600:00 | 929.2083 |  |  | 0 | 0%
Total |  | 96 |  | 14248.8454 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar-9
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
8:30 | 10:23 | Tangail 132/33kV S/S Tr-3 LT Forced S/D Due to Red hot at 33kv Jamuna feeder(PBS) at 33kv T3 bus section.
8:31 | 10:23 | Tangail 132/33kV S/S Tr-3 HT Forced S/D Due to Red hot at 33kv Jamuna feeder(PBS) at 33kv T3 bus section.
8:42 | 12:45 | Jamalpur 132/33kV S/S T-3 HT Scheduled S/D Due to Neutral grounding conductor replacement work.
8:42 | 12:45 | Jamalpur 132/33kV S/S T-3 LT Scheduled S/D Due to Neutral grounding conductor replacement work.
8:44 | - | TK chemical S/S 48/64MVA T-2(415T) HT Tripped showing Self Diffential And Whole Diffential relays Due to Trip, |  |  |  |  | 5.0MW load interrup.
Diffential, y-Phase Diffential, R-Phase Diffential.
8:44 | - | TK chemical S/S 48/64MVA T-2(415T) LT Tripped showing -86 Lockout Relay Operated relays. |  |  |  |  | 5.0MW load interrup.
9:53 | 10:45 | Shahjadpur 132/33kV S/S T-3(425T) LT Forced S/D Due to 132 kV T-3 X-Former LT Busing (R-Phase) red-hot maintenance.
9:54 | 10:45 | Shahjadpur 132/33kV S/S T-3(425T) HT Forced S/D Due to 132 kV T-3 X-Former LT Busing (R-Phase) red-hot maintenance.
10:26 | 11:18 | Noapara 33Kv Bus Section S/D. |  |  |  |  | 15MW load interrup.
- | 11:08 | Dohazari-Sikalbaha 132 kV Ckt-2 is restored.
11:18 | 12:26 | Rampal 230Kv Bus Coupler Breaker.
11:19 | 11:26 | Barishal-Bhandaria 132 kV Ckt-1 Tripped from Barishal 132/33kV end showing Distance,Z-1, A phase relays Due to Bad weather.
11:30 | - | Chowmuhani 132/33kV S/S HFPL line Tripped showing Diffeential Relay Optd, GR-A & GR-B, 86A,86B. relays Due to Tripped. |  |  |  |  | 56.0MW load interrup.
12:00 | 12:04 | Shahjibazar 132/33kV S/S TR-02 LT Forced S/D Due to Emergency loadshed Instructed by NLDC for Mainten Grid Voltage. |  |  |  |  | 32.0MW load interrup.
12:00 | - | Day peak Generation: 12898 MW.
12:04 | - | Barisal Electric 307 MW was shutdown due to coal shortage. |  |  |  |  | 150MW generation interrup.
12:06 | 12:34 | Ashuganj-Ghorasal 132kV Ckt-1 Tripped from Ashuganj 230/132/33kV end showing Distance-C phase relays.
- | 12:13 | Adani Power Jharkhand Ltd. unit-1 was sync.
12:28 | 13:32 | Khulna (S)-Rampal Ckt-2 Scheduled S/D from Khulna(S) 230/132kV end Due to Protection test work and from
Rampal 400/230kV end Due to Remote command checking from NLDC.
12:48 | 13:16 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Tripped showing MiCOM P441: PH Y, Z 1, Dist. SEND. relays Due to Storm. |  |  |  |  | 55.0MW load interrup.
12:56 | 13:41 | Bagerhat-Bhandaria 132 kV Ckt-1 Forced S/D from Bagerhat 132/33kV end Due to Emergency tree trimming of span
12 to 13 Tower middle spot of 132 Kv Bagerhat- Bhandaria Line.
12:59 | 13:11 | Bashundhara-Rampura 132 kV Ckt-2 Tripped from Rampura 230/132kV end showing * Distance protection 21/1: |  |  |  |  | 30.0MW load interrup. Rampura 230/132kV end
Z1-BN. trip relays Due to Trip due to Thunderstorm.
12:59 | 13:13 | Bashundhara-Rampura 132 kV Ckt-1 Tripped from Rampura 230/132kV end showing * Distance protection 21/1: |  |  |  |  | 30.0MW load interrup. Rampura 230/132kV end
Z1-BN. trip * High impedance diff 87 TEE-2 FDR : B&C ph * Master trip 86 T2 relays Due to Trip due to Thunderstorm.
15:00 | - | Matarbari Unit-1 was shutdown.
15:27 | - | Adani Power Jharkhand Ltd. unit-1 tripped. |  |  |  |  | 352MW generation interrup.
15:40 | 15:46 | Sreemongol 132/33kV S/S 132/33kv T-2 LT Tripped showing E/F relays Due to heavy rain and thundering. |  |  |  |  | 35.0MW load interrup.
15:40 | 15:44 | Sreemongol 132/33kV S/S 132/33kv T-2 HT Tripped showing O/C relays Due to heavy rain and thundering. |  |  |  |  | 35.0MW load interrup.
15:58 | 17:50 | Shahjadpur 132/33kV S/S T-4(435T) LT Forced S/D Due to S/D.
- | 16:21 | Kushiara 163MW GT was sync.
16:28 | 17:59 | Dohazari 132/33kV S/S Power Transformer -T-1 HT Forced S/D Due to Banshkhali 33KV PBS feeder taken T-01 |  |  |  |  | 15.0MW load interrup.
33KV Bus shutdown for redhot maintenance at Banshkhali 33KV PBS bus DS.
- | 16:52 | Khulna 330 MW CCPP ST was sync.
16:58 | 17:48 | Shahjadpur 132/33kV S/S T-4(435T) HT Forced S/D Due to 33 kV D/S R-Phase red hot.
- | 17:05 | Chapai 132/33kV S/S T-4 (435T) HT is restored.
17:08 | 17:17 | Sherpur 132/33kV S/S Transformer- 02 LT Tripped showing IDMT-O/C. relays. |  |  |  |  | 40.0MW load interrup.
17:08 | 17:17 | Sherpur 132/33kV S/S Transformer- 01 LT Tripped showing IDMT-O/C. relays. |  |  |  |  | 40.0MW load interrup.
17:08 | 17:16 | Sherpur 132/33kV S/S Transformer- 01 HT Tripped showing IDMT-O/C. relays. |  |  |  |  | 40.0MW load interrup.
17:09 | 17:25 | Hasnabad-Sitalakhya 132kV Ckt-1 Tripped from Shitalakhya 132/33kV end showing Gen. Trip Z-1,B-Phase relays Due to General Trip.
17:30 | 20:20 | Naogaon 132/33kV S/S T-3 LT Forced S/D Due to Emergency red hot maintenance.
- | 17:48 | Adani Power Jharkhand Ltd. unit-1 was sync.
17:50 | 18:50 | Hathazari 230/132/33kV S/S T-01 HT Scheduled S/D Due to 33 kV XLPE B Ph Cable Fixing.
- | 17:53 | Chapai 132/33kV S/S T-4 (435T) LT is restored.
18:15 | 20:15 | Naogaon 132/33kV S/S T-3 HT Forced S/D Due to Emergency red hot maintenance.
19:30 | - | Evening peak generation: 13870 MW.
19:30 | - | Banshkhali SS Power unit-2 was forced shutdown. |  |  |  |  | 300MW generation interrup.
21:12 | 23:32 | Jamalpur 132/33kV S/S 132KV PPM Jamalpur Power Plant Scheduled S/D Due to Line D.S maintenance work purpose.
- | 23:04 | Bogura 132/33kV S/S Transformer-2 HT is restored.
- | 23:04 | Bogura 132/33kV S/S Transformer-2 LT is restored.
- | 23:04 | Bogura 132/33kV S/S Transformer-2 LT is restored.
23:32 | 23:40 | Jamalpur 132/33kV S/S T-2 LT Tripped showing SPS relays Due to SPS trip. |  |  |  |  | 35.0MW load interrup.
23:32 | 2:05 | Jamalpur 132/33kV S/S T-1 LT Tripped showing SPS relays Due to SPS trip. |  |  |  |  | 35.0MW load interrup.
0:07 | 0:52 | Tangail 132/33kV S/S Tr-4 LT Forced S/D Due to Red hot at 33kV bus side. |  |  |  |  | 14.0MW load interrup.
0:07 | - | Tangail 132/33kV S/S Tr-3 LT Forced S/D Due to Red hot at 33kV bus side. |  |  |  |  | 14.0MW load interrup.
0:10 | 0:51 | Tangail 132/33kV S/S Tr-4 HT Forced S/D Due to Red hot at 33kV bus side. |  |  |  |  | 14.0MW load interrup.
1:55 | 2:10 | Haripur. 230/132kV S/S Ullon (Maniknagar-2) Tripped showing Ph Y, Z1, DIST. send (MiCOM p441) relays Due to Unknown. |  |  |  |  | 21.0MW load interrup.
5:58 | 7:27 | Dohazari 132/33kV S/S Power Transformer -T-2 HT Scheduled S/D Due to Keranihat 33 kv pbs maintenance work. |  |  |  |  | 40.0MW load interrup.
6:16 | - | Ishurdi 132/33kV S/S 132/33 kV T-1 HT Scheduled S/D Due to 33 kv bus maintenance. |  |  |  |  | 30.0MW load interrup.
6:16 | - | Ishurdi 132/33kV S/S 132/33 kV T-1 LT Scheduled S/D Due to 33 kv bus maintenance. |  |  |  |  | 30.0MW load interrup.
7:00 | - | Minimum generation 11306 MW.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-08-01 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 210 | 4450847
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4315500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 288545 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 399 | 9510910
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 343 | 7762000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9884300
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 50 | 751680 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Under maint.
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 51 | 463493 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 380346 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 11 | 222362 | Low demand
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 297432 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 125 | 3744000 | FGMO
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 20 | 664320 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 323 | 7618858
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 85 | 747936 | High voltage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 386172 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 115 | 1799520 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 525969 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 285061 | Engine problem
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 41 | 867480 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 651240 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 23 | 366600 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 281318 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 95 | 2561780 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 1231708 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1739088
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1172189
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 72 | 1230720 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1530720
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 203683
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 435600 | Fuel shortage
| Dhaka area Total |  |  |  | 5722 | 3179 | 66371377
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 118 | 2700000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 358417
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 41985
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 210720 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 130 | 3024160
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 225 | 5183038
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 1009491 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 48 | 844704 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 1193680 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 58 | 826680 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 925440
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 12 | 250416 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 20 | 444480
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 34 | 214080 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 21117
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 221 | 2913055 | High voltage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 526871 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 51 | 1271279 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 88 | 912960 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 68 | 1032027 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 140 | 1006981 | Fuel shortage
| SS Power I |  | SS Power | 0 | 0 | 0 | 5901818 | Machine problem
| Cox's Bazar Wind |  | IPP | 66 | 0 | 28 | 541440 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 0 | 1658181 | On test.
| Chattogram area Total |  |  |  | 2545 | 1450 | 33013020
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 180 | 4463000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7290600 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 6483000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 288 | 6170800 | FGMO
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 0 | 0 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 948056 | Engine problem
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 40 | 373018 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 37 | 780496 | Machine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 120 | 1889280 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 441136
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 158040
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 134 | 3001920 | Restriction by India
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 534700 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 588643 | Low demand
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 17 | 404760 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 70 | 664620 | Low demand
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 112560 | Engine problem
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 511560 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1234560
| Cumilla Area Total |  |  |  | 3096 | 1663 | 36050749
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 82 | 1464000 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 342504 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 16350
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 85 | 1639200 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 84 | 718800 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 398750
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 140640 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 273 | 4720244
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 624000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 24960 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 80 | 636054
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 49 | 1068600
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 46 | 1052640
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 132288
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 554112 | GT-9 Under maint.
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1846084
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 112 | 2681190 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 380000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 533976
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 255 | 7193500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 368 | 8996000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 218160
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 355 | 8768200
| Sylhet Area Total |  |  |  | 2427 | 1472 | 34709764
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 911 | 21460363
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 360000 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 39 | 276480 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 115 | 2916666 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 60 | 678528 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 130 | 3507264 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 104250 | Low demand
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 40 | 938016 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 50 | 617472 | Low demand
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 425520
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 220 | 79 | 2071840 | Fuel shortage
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | Coal shortage.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 3121 | 1448 | 33356399
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 725760 | High voltage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 16 | 421567 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 132 | 2914000 | ST Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 30867700
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5122309
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 100 | 884400 | High voltage
| Barisal 307 MW |  | IPP | 307*1 | 307 | 0 | 1680000 | Coal shortage.
| Barisal Area Total |  |  |  | 2265 | 1728 | 42615736
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 35 | 185380 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 24 | 306632 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 21 | 480890 | Engine problem
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 25 | 308471 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 36 | 374716 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Under maint.
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 140 | 4540127
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 145 | 3780291 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 349 | 8753381 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 276726 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 159498 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 200515 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 682072 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1967904
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2148480
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 37080
| Adani Power Jharkhanda Ltd |  | Import | 748*2 | 1496 | 1066 | 17863636
| Rajshahi Area Total |  |  |  | 3631 | 2197 | 42065799
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 240 | 4973000
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 105 | 1812892 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 55750
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1873152
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 232602
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 1094110
| Rangpur Area Total |  |  |  | 750 | 460 | 10041506
| Total |  |  |  | 24171 | 13870 | 302944594
| Eastern Grid Total |  |  |  | 14404 | 8037 | 174865154
| Western Grid Total |  |  |  | 9767 | 5833 | 128079440
| National Grid Total |  |  |  | 24171 | 13870 | 302944594
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-08-01
| (a) ENTIRE EASTERN GRID : |  | 9042.59 | MW | (b) ENTIRE WESTERN GRID : |  | 4262.4 | MW
| i) Dhaka area |  | 4992.89 | MW | i) Khulna area |  | 1529 | MW
| ii) Chittagong area |  | 1342.7 | MW | ii) Rajshahi area |  | 1487 | MW
| iii) Comilla area |  | 1052 | MW | iii) Barisal area |  | 211.4 | MW
| iv) Mymensingh area |  | 1107 | MW | iv) Rangpur area |  | 1035 | MW
| v) Sylhet area |  | 548 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 13304.99 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 16 | 01:00 | Chhatak | 31 | 20:00 | Kamrangirchar | 54.3 | 12:00 | Natore | 163 | 22:00 | Sholosohor | 36 | 13:00
2 | AKSML | 101 | 22:00 | Chowmuhani | 152 | 00:00 | Kaptai | N/A | N/A | Nawabganj | 57.4 | 23:00 | Shyampur | 142 | 10:00
3 | Aftabnagar | 36 | 00:00 | Chuadanga | 117 | 21:00 | Kazla | 90 | 13:00 | Netrakona | 129 | 19:30 | Siddhirganj | 118 | 14:00
4 | Agargaon | 107 | 13:00 | Coxsbazar | 122 | 22:00 | Keranigonj | 74 | 00:00 | New | 88 | 12:00 | Sirajganj | 130 | 21:00
5 | Agrabad | 76 | 14:00 | Cumilla(N) | 191 | 23:00 | Khagrachori | 32 | 20:00 | Niamatpur | 100 | 13:00 | Sonargaon | 88 | 12:00
6 | Amnura | 70 | 23:00 | Cumilla(S) | 144 | 23:00 | Khulna | 86 | 12:00 | Noapara | 38 | 19:30 | Sreemongol | 65 | 01:00
7 | Ashuganj | 72 | 21:00 | Daudkandi | 149 | 21:00 | Khulshi | 180 | 19:30 | PHP | 9 | 19:00 | Sreepur | 82 | 12:00
8 | BIPTC | N/A | N/A | Dhaka | 32 | 11:00 | Kishoreganj | 156 | 20:00 | Pabna | 122 | 19:30 | Srinagar | 47.15 | 22:00
9 | BSRM | 162 | 05:00 | Dhamrai | 126 | 13:00 | Kodda | 287 | 19:00 | Palashbari | 142 | 19:00 | Sunamganj | 56 | 20:00
10 | Bagerhat | 77 | 02:00 | Dhanmondi | 155.5 | 12:00 | Kulaura | 48 | 14:00 | Panchagarh | 64 | 20:00 | Sylhet | 178 | 20:00
11 | Bakulia | 106 | 11:00 | Dohazari | 100 | 20:00 | Kurigram | 70 | 20:00 | Patuakhali | 103 | 01:00 | TK | 25 | 06:00
12 | Banani | 43 | 14:00 | Faridpur | 148 | 22:00 | Kushtia | 148 | 19:30 | Payra | 18.2 | 02:00 | Tangail | 227 | 20:00
13 | Bangabhaban | 22 | 10:00 | Fatullah | 71 | 16:00 | Lalbag | 81 | 11:00 | Postogola | 57 | 11:00 | Thakurgaon | 112 | 20:00
14 | Barapukuria | 76 | 19:30 | Fenchuganj | 48 | 19:00 | Lalmonirhat | 61 | 19:30 | Purbachal | 20 | 12:00 | Tongi | 114 | 18:30
15 | Barguna | 16 | 00:00 | Feni | 125 | 20:00 | Madanganj | 35 | 10:00 | Purbasadipur | 165 | 12:00 | Ullon | 51 | 15:00
16 | Barishal | 96 | 01:00 | GPH | 87 | 05:00 | Madaripur | 92 | 02:00 | Rahim | 44 | 08:00 | Uttara | 85 | 12:00
17 | Barishal-230 | 88 | 05:00 | Ghorashal | 73 | 21:00 | Madartek | 88.17 | 00:00 | Rajbari | 72 | 01:00 | UttaraNew | 73 | 13:00
18 | Baroaulia | 66 | 11:00 | Goalpara | 36 | 12:00 | Madunaghat | 54 | 19:00 | Rajendrapur | 98 | 19:30 | Zigatola | 94 | 12:00
19 | Baroirhat | 52 | 22:00 | Gollamari | 51 | 12:00 | Magura | 62 | 21:00 | Rajshahi | 178 | 21:00
20 | Bashundhara | 163 | 12:00 | Gopalganj | 95 | 19:30 | Mahasthangarh | 84 | 22:00 | Rajshahi-230 | 44 | 00:00
21 | BashundharaCement | 1 | 10:00 | Gulshan | 148 | 12:00 | Manikganj | 112 | 19:30 | Ramganj | 90 | 08:00
22 | Beanibazar | 82 | 19:00 | Halishahar | 81 | 09:00 | Maniknagar | 110 | 13:00 | Rampur | 31 | 00:00
23 | Benapole | 54 | 03:00 | HaripurSBU | 152 | 11:00 | Matarbari | 44 | 18:30 | Rangamati | 20 | 19:30
24 | Bhaluka | 146 | 19:30 | Hasnabad | 123 | 20:00 | Matuail | 74 | 12:00 | Rangpur | 157 | 09:00
25 | Bhandaria | 50 | 01:00 | Hathazari | 79 | 00:00 | Millgate | 105 | 10:00 | Ruppur | 6 | 11:00
26 | Bhangura | 38 | 20:00 | Ishurdi | 79 | 15:00 | Mirpur | 146 | 13:00 | SSM | 0 | 00:00
27 | Bheramara(GK) | 68 | 19:30 | Jaldhaka | 83 | 19:30 | Mirsorai | 3 | 07:00 | Saidpur | 125 | 23:00
28 | Bhulta | 238 | 19:30 | Jamalpur | 162 | 19:00 | Mithapukur | 60 | 23:00 | Satkhira | 111 | 19:30
29 | Bog-Sherpur | 86 | 19:30 | Jashore | 144 | 12:00 | Modern | 0 | 00:00 | Satmasjid | 111 | 13:00
30 | Bogura | 163 | 19:30 | Jhenaidah | 129 | 19:30 | Mogbazar | 147 | 13:00 | Savar | 176 | 19:30
31 | Borhanuddin | 51 | 00:00 | Joydebpur | 173 | 19:30 | Mongla | 34 | 10:00 | Shahjadpur | 115 | 20:00
32 | Brahmanbaria | 146 | 21:00 | Joypurhat | 69 | 19:30 | Motijheel | 43 | 12:00 | Shahjibazar | 103 | 23:00
33 | Cantonment | 171 | 13:00 | Juldah | 22 | 10:00 | Munshiganj | 104 | 00:00 | Shahmirpur | 50.6 | 21:00
34 | Chandpur | 58 | 11:00 | KSRM | 46 | 02:00 | Mymensingh | 243 | 00:00 | Shariatpur | 71 | 01:00
35 | Chandraghona | 31 | 19:30 | Kabirpur | 304 | 15:00 | Naogaon | 158 | 22:00 | Sherpur | 152 | 21:00
36 | Chapai | 83 | 23:00 | Kachua | 67 | 21:00 | Narail | 56 | 19:30 | Shikalbaha | 32 | 00:00
37 | Charsaidpur | 45 | 00:00 | Kallyanpur | 111 | 00:00 | Narinda | 92 | 16:00 | Shikalbaha-230 | N/A | N/A
38 | Chauddagram | 63 | 21:00 | Kalurghat | 34 | 09:00 | Narshingdi | 179 | 21:00 | Shitalakhya | 104.8 | 12:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-08-01 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 399 | 21:00 | 386 | 12:00 | Gopalganj | 407 | 13:00 | 394 | 12:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 380 | 21:00 | 369 | 15:00
| Bhulta | 396 | 13:00 | 386 | 12:00 | Madunaghat_I | 391 | 11:00 | 382 | 04:00
| Bibiana | 405 | 20:00 | 395 | 15:00 | Payra | 412 | 13:00 | 407 | 10:00
| BIPTC | 401 | 06:00 | 393 | 01:00 | Rampal | 409 | 13:00 | 396 | 11:00
| Bogura | N/A | N/A | N/A | N/A
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 233 | 21:00 | 222 | 12:00 | Hasnabad | 232 | 19:30 | 224 | 12:00
| AKSML | 233 | 13:00 | 227 | 01:00 | Hathazari | 236 | 21:00 | 227 | 09:00
| Aminbazar | 235 | 13:00 | 226 | 11:00 | Ishurdi | 235 | 18:00 | 227 | 12:00
| Ashuganj | 233 | 18:00 | 228 | 12:00 | Jhenaidah | 228 | 00:00 | 219 | 12:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 233 | 21:00 | 225 | 15:00
| Baghabari | 231 | 17:00 | 225 | 05:00 | Keranigonj | 232 | 21:00 | 222 | 12:00
| Barapukuria | 223 | 17:00 | 205 | 06:00 | Khulna(S) | 234 | 00:00 | 228 | 12:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | 234 | 06:00 | 228 | 04:00
| Barishal | 238 | 12:00 | 232 | 01:00 | Maniknagar | 231 | 20:00 | 223 | 12:00
| Bheramara | 234 | 00:00 | 226 | 05:00 | Meghnaghat | 239 | 00:00 | 231 | 10:00
| Bhulta | 235 | 13:00 | 227 | 12:00 | Mirsorai | 238 | 13:00 | 226 | 10:00
| Bibiana | 232 | 10:00 | 226 | 15:00 | Rajshahi | 230 | 18:00 | 219 | 08:00
| BIPTC | 235 | 00:00 | 225 | 08:00 | Rampal | 233 | 13:00 | 226 | 11:00
| Bogura | 233 | 18:00 | 217 | 05:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 244 | 12:00 | 238 | 03:00 | Rampura | 232 | 04:00 | 224 | 12:00
| BSRM | 236 | 19:30 | 226 | 02:00 | Shikalbaha | 233 | 19:30 | 227 | 02:00
| Cumilla(N) | 232 | 13:00 | 224 | 15:00 | Shyampur | 231 | 20:00 | 223 | 12:00
| Fenchuganj | 236 | 21:00 | 227 | 15:00 | Siddhirganj | 234 | 13:00 | 227 | 12:00
| Ghorashal | 232 | 00:00 | 230 | 05:00 | Sirajgonj | 239 | 18:00 | 231 | 05:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 231 | 17:00 | 226 | 02:00
| GPH | 234 | 11:00 | 227 | 02:00 | Tongi | 230 | 04:00 | 222 | 16:00
| Haripur | 232 | 13:00 | 225 | 12:00
| 132 kV | KV |  | KV |  | Tongi | KV |  | KV
| Aftabnagar | 135 | 05:00 | 127 | 12:00 | Lalbag | 136 | 21:00 | 129 | 12:00
| Agargaon | 133 | 21:00 | 126 | 12:00 | Lalmonirhat | 130 | 17:00 | 114 | 05:00
| Agrabad | 137 | 00:00 | 131 | 06:00 | Madanganj | 135 | 20:00 | 127 | 15:00
| AKS | 134 | 00:00 | 130 | 04:00 | Madaripur | 130 | 00:00 | 127 | 15:00
| Aminbazar | 135 | 13:00 | 130 | 00:00 | Madartek | 135 | 07:00 | 127 | 12:00
| Amnura | 142 | 18:00 | 125 | 10:00 | Madunaghat | 139 | 11:00 | 135 | 02:00
| Ashuganj | 140 | 18:00 | 136 | 06:00 | Magura | 138 | 00:00 | 130 | 12:00
| Bagerhat | 139 | 13:00 | 132 | 11:00 | Mahasthangarh | 137 | 18:00 | 121 | 05:00
| Bakulia | 141 | 13:00 | 136 | 01:00 | Manikganj | 135 | 14:00 | 127 | 16:00
| Banani | 135 | 06:00 | 127 | 12:00 | Maniknagar | 134 | 06:00 | 127 | 12:00
| Bangabhaban | 133 | 06:00 | 127 | 12:00 | Matarbari | 139 | 14:00 | 124 | 01:00
| Barapukuria | 138 | 17:00 | 124 | 06:00 | Matuail | 134.5 | 13:00 | 129 | 12:00
| Barguna | 141 | 23:00 | 133 | 05:00 | Millgate | 134 | 05:00 | 127 | 12:00
| Barishal | 140 | 20:00 | 130 | 01:00 | Mirpur | 134 | 21:00 | 127 | 12:00
| Barishal-230 | 138 | 12:00 | 132 | 01:00 | Mithapukur | 132 | 17:00 | 116 | 05:00
| Baroaulia | 139 | 13:00 | 133 | 04:00 | Modern | 138 | 06:00 | 133 | 08:00
| Baroirhat | 137 | 13:00 | 125 | 04:00 | Mogbazar | 135 | 00:00 | 128 | 12:00
| Bashundhara | 135 | 03:00 | 126 | 15:00 | Mongla | 138 | 13:00 | 132 | 02:00
| BashundharaCement | 135 | 20:00 | 127 | 15:00 | Motijheel | 133 | 03:00 | 127 | 12:00
| Beanibazar | 127 | 11:00 | 121 | 04:00 | Munshiganj | 135 | 13:00 | 128 | 12:00
| Benapole | 135 | 15:00 | 128 | 12:00 | Mymensingh | 132 | 18:00 | 116 | 07:00
| Bhaluka | 130 | 15:00 | 121 | 01:00 | Naogaon | 131 | 18:00 | 112 | 04:00
| Bhandaria | 142 | 20:00 | 125 | 04:00 | Narail | 138 | 00:00 | 125 | 01:00
| Bhangura | 138 | 18:00 | 130 | 08:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 134 | 00:00 | 130 | 12:00 | Narshingdi | 133 | 13:00 | 122 | 14:00
| Bheramara(GK) | 135 | 16:00 | 130 | 12:00 | Natore | 135 | 18:00 | 127 | 06:00
| Bhulta | 126 | 13:00 | 118 | 16:00 | Nawabganj | 136 | 13:00 | 129 | 12:00
| Bog-Sherpur | 138 | 18:00 | 124 | 05:00 | Netrakona | 129 | 11:00 | 117 | 23:00
| Bogura | 140 | 18:00 | 125 | 05:00 | New | 134 | 00:00 | 127 | 15:00
| Bogura-230 | 140 | 18:00 | 125 | 05:00 | Niamatpur | 132 | 18:00 | 107 | 06:00
| Brahmanbaria | 128 | 14:00 | 122 | 12:00 | Noapara | 138 | 00:00 | 129 | 19:00
| Cantonment | 132 | 04:00 | 125 | 12:00 | Pabna | 134 | 18:00 | 120 | 19:30
| Chandpur | 142 | 12:00 | 120 | 02:00 | Palashbari | 132 | 18:00 | 114 | 05:00
| Chandraghona | 139 | 16:00 | 134 | 03:00 | Panchagarh | 135 | 18:30 | 112 | 21:00
| Chapai | 136 | 18:00 | 124 | 04:00 | Patuakhali | 140 | 19:30 | 134 | 03:00
| Charsaidpur | 136 | 13:00 | 129 | 12:00 | Payra | 140 | 13:00 | 137 | 02:00
| Chauddagram | 136 | 11:00 | 124 | 15:00 | PHP | 137 | 13:00 | 124 | 15:00
| Chhatak | 128 | 17:00 | 120 | 19:00 | Postogola | 136 | 13:00 | 130 | 12:00
| Chowmuhani | 135 | 11:00 | 120 | 02:00 | Purbachal | 135 | 02:00 | 126 | 12:00
| Chuadanga | 132 | 00:00 | 123 | 12:00 | Purbasadipur | 132 | 18:00 | 111 | 06:00
| Coxsbazar | 137 | 14:00 | 120 | 18:30 | Rahim | 136 | 13:00 | 130 | 12:00
| Cumilla(N) | 136 | 13:00 | 128 | 15:00 | Rajbari | 130 | 14:00 | 124 | 01:00
| Cumilla(S) | 138 | 13:00 | 126 | 23:00 | Rajendrapur | 137 | 22:00 | 128 | 12:00
| Daudkandi | 135 | 13:00 | 126 | 16:00 | Rajshahi | 136 | 18:00 | 128 | 07:00
| Dhaka | 135 | 21:00 | 128 | 12:00 | Rajshahi-230 | 137 | 00:00 | 124 | 05:00
| Dhamrai | 136 | 14:00 | 128 | 12:00 | Ramganj | 138 | 11:00 | 117 | 07:00
| Dhanmondi | 134.5 | 20:00 | 127.5 | 12:00 | Rampur | 138 | 14:00 | 132 | 15:00
| Dohazari | 140 | 13:00 | 132 | 01:00 | Rampura | 135 | 04:00 | 127 | 12:00
| Faridpur | 131 | 18:00 | 125 | 01:00 | Rangamati | 139 | 13:00 | 134 | 07:00
| Fatullah | 131 | 21:00 | 125 | 12:00 | Rangpur | 133 | 18:00 | 116 | 05:00
| Fenchuganj | 132 | 13:00 | 129 | 02:00 | Ruppur | 135 | 17:00 | 130 | 04:00
| Feni | 138 | 13:00 | 125 | 05:00 | Saidpur | 133 | 18:00 | 114 | 03:00
| Ghorashal | 138 | 00:00 | 135 | 15:00 | Satkhira | 138 | 14:00 | 129 | 12:00
| Goalpara | 139 | 13:00 | 135 | 12:00 | Satmasjid | 132 | 07:00 | 125 | 12:00
| Gollamari | 138 | 14:00 | 133 | 12:00 | Savar | 136 | 21:00 | 128 | 12:00
| Gopalganj | 134 | 13:00 | 128 | 12:00 | Shahjadpur | 139 | 17:00 | 133 | 07:00
| Gopalganj-400 | 130 | 13:00 | 126 | 14:00 | Shahjibazar | 131 | 18:00 | 119 | 12:00
| Gulshan | 134 | 03:00 | 126 | 12:00 | Shahmirpur | 140 | 13:00 | 134 | 18:30
| Halishahar | 138 | 11:00 | 134 | 05:00 | Shariatpur | 131 | 13:00 | 126 | 01:00
| Haripur | 136 | 13:00 | 130 | 12:00 | Sherpur | 127 | 18:00 | 110 | 16:00
| HaripurSBU | 136 | 13:00 | 130 | 12:00 | Shikalbaha | 129 | 11:00 | 124 | 02:00
| Hasnabad | 136 | 13:00 | 131 | 10:00 | Shikalbaha-230 | 140 | 00:00 | 137 | 02:00
| Hathazari | 139 | 13:00 | 135 | 06:00 | Shitalakhya | 136 | 20:00 | 128.3 | 16:00
| Ishurdi | 136 | 18:00 | 131 | 05:00 | Sholosohor | 137 | 11:00 | 133 | 03:00
| Jaldhaka | 132 | 18:00 | 113 | 04:00 | Shyampur | 130 | 20:00 | 125 | 11:00
| Jamalpur | 132 | 18:30 | 116 | 12:00 | Shyampur-230 | 130 | 20:00 | 125 | 12:00
| Jashore | 137 | 00:00 | 127 | 12:00 | Siddhirganj | 135 | 20:00 | 129 | 12:00
| Jhenaidah | 138 | 00:00 | 131 | 12:00 | Sirajganj | 135 | 16:00 | 125 | 21:00
| Jhenaidah-230 | 139 | 00:00 | 132 | 12:00 | Sonargaon | 133 | 00:00 | 127 | 15:00
| Joydebpur | 137 | 14:00 | 129 | 15:00 | Sreemongol | 131 | 18:00 | 126 | 00:00
| Joypurhat | 130 | 18:00 | 108 | 06:00 | Sreepur | 130 | 15:00 | 125 | 02:00
| Juldah | 140 | 19:30 | 135 | 07:00 | Srinagar | 137 | 13:00 | 129 | 12:00
| Kabirpur | 137 | 21:00 | 123 | 15:00 | SSM | 141 | 19:00 | 136 | 03:00
| Kachua | 137 | 11:00 | 123 | 02:00 | Sunamganj | 128 | 17:00 | 117 | 20:00
| Kaliakoir | 138 | 21:00 | 130 | 15:00 | Sylhet | 129 | 17:00 | 125 | 20:00
| Kallyanpur | 130 | 20:00 | 123 | 12:00 | Tangail | 131 | 07:00 | 123 | 12:00
| Kalurghat | 137 | 19:00 | 134 | 03:00 | Thakurgaon | 133 | 18:00 | 111 | 05:00
| Kamrangirchar | 136 | 20:00 | 130 | 14:00 | TK | 140 | 21:00 | 138 | 06:00
| Kaptai | N/A | N/A | N/A | N/A | Tongi | 136 | 04:00 | 130 | 12:00
| Kazla | 133 | 03:00 | 127 | 12:00 | Ullon | 135 | 04:00 | 127 | 16:00
| Keranigonj | 136 | 20:00 | 129 | 12:00 | Uttara | 133 | 21:00 | 107 | 23:00
| Khagrachori | 139 | 13:00 | 133 | 05:00 | UttaraNew | 135 | 20:00 | 126 | 12:00
| Khulna | 138 | 00:00 | 133 | 12:00 | Zigatola | 137 | 14:00 | 130 | 12:00
| Khulna(S) | 138 | 14:00 | 133 | 12:00
| Khulshi | 136 | 19:30 | 132 | 02:00
| Kishoreganj | 133 | 16:00 | 125 | 02:00
| Kodda | 138 | 21:00 | 127 | 16:00
| KSRM | 139 | 13:00 | 134 | 05:00
| Kulaura | 131 | 17:00 | 127 | 12:00
| Kurigram | 131 | 18:00 | 112 | 06:00
| Kushtia | 135 | 00:00 | 129 | 12:00

## L-Curve
Date | 2023-08-01
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1040 | 7644 | 5724 | 13368 |  |  |  | QF-LDC-11
0:30 | 860 | 7589 | 5611.5 | 13200.5 | Date: | 2023-08-01
1:00 | 680 | 7534 | 5499 | 13033
1:30 | 680 | 7525 | 5407.5 | 12932.5
2:00 | 680 | 7516 | 5316 | 12832
2:30 | 675 | 7489.5 | 5320 | 12809.5 | [5 empty] | Gen. at Eve. Peak | 13870 | 13870 MW (19:30 )
3:00 | 670 | 7463 | 5324 | 12787 | [6 empty] | 19:30
3:30 | 675 | 7425.5 | 5322.5 | 12748 | [5 empty] | Gen. at Day Peak | 12897 | 12897 MW (12:00 )
4:00 | 680 | 7388 | 5321 | 12709 | [6 empty] | 12:00
4:30 | 685 | 7398 | 5322 | 12720 | [5 empty] | Highest Generation | 13870
5:00 | 690 | 7408 | 5323 | 12731 | [6 empty] | 19:30
5:30 | 700 | 7298 | 5284 | 12582
6:00 | 710 | 7188 | 5245 | 12433
6:30 | 710 | 7156.5 | 5183 | 12339.5
7:00 | 710 | 7125 | 5121 | 12246
7:30 | 765 | 7157 | 5160.5 | 12317.5
8:00 | 820 | 7189 | 5200 | 12389
8:30 | 885 | 7214.5 | 5180 | 12394.5
9:00 | 950 | 7240 | 5160 | 12400
9:30 | 1010 | 7328 | 5269 | 12597
10:00 | 1070 | 7416 | 5378 | 12794
10:30 | 1055 | 7401.5 | 5409.5 | 12811
11:00 | 1040 | 7387 | 5441 | 12828
11:30 | 1030 | 7408.5 | 5454 | 12862.5
12:00 | 1020 | 7430 | 5467 | 12897
12:30 | 885 | 7127.5 | 5333 | 12460.5
13:00 | 750 | 6825 | 5199 | 12024
13:30 | 855 | 6670 | 5214 | 11884
14:00 | 960 | 6515 | 5229 | 11744
14:30 | 1125 | 6514.5 | 5207 | 11721.5
15:00 | 1290 | 6514 | 5185 | 11699
15:30 | 1215 | 6655 | 5037 | 11692
16:00 | 1140 | 6796 | 4889 | 11685
16:30 | 1125 | 6638 | 4804.5 | 11442.5
17:00 | 1110 | 6480 | 4720 | 11200
17:30 | 1190 | 6424 | 4815 | 11239
18:00 | 1270 | 6368 | 4910 | 11278
18:30 | 1200 | 7041 | 5227 | 12268
19:00 | 1130 | 7714 | 5544 | 13258
19:30 | 1020 | 8037 | 5833 | 13870
20:00 | 960 | 7922 | 5898 | 13820 |  |  |  | Executive Engineer
20:30 | 885 | 7928.5 | 5896 | 13824.5 |  |  |  | Network Operation Division
21:00 | 810 | 7935 | 5894 | 13829
21:30 | 795 | 7915.5 | 5822 | 13737.5
22:00 | 780 | 7896 | 5750 | 13646 |  |  |  |  | Page 6 of 7
22:30 | 880 | 7789 | 5760 | 13549
23:00 | 980 | 7682 | 5770 | 13452
23:30 | 1010 | 7663 | 5747 | 13410
24:00 | 1040 | 7644 | 5724 | 13368
13870 MW (19:30 )
12897 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-08-01 |  | Energy |  | 302944594
QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 4225 | 782 | 2089 | 0 | 2489 | 2640 | 130 | 364 | 489 | 132 | 0 | 28 | 412.56
0:30 | 4259.5 | 846.5 | 2042 | 150 | 2030 | 2735.5 | 130 | 462.5 | 395 | 135 | 0 | 14.5 | 859.0225 |  | Date: | 43677
1:00 | 4294 | 911 | 1995 | 300 | 1571 | 2831 | 130 | 561 | 301 | 138 | 0 | 1 | 1305.485
1:30 | 4355.5 | 911 | 1993.5 | 250 | 1474.5 | 2829.5 | 130 | 557.5 | 286 | 139 | 0 | 6 | 1305.9625 | [7 empty] | Total Energy | 302.9446 | 302.9446 | Total Energy Gen 302.945 MKWHr Energy Not Served 14.189 MKWHr Energy Requirement 317.133 MKWHr
2:00 | 4417 | 911 | 1992 | 200 | 1378 | 2828 | 130 | 554 | 271 | 140 | 0 | 11 | 1306.44 | [7 empty] | Energy not Served | 14.1885 | 14.1885
2:30 | 4367.5 | 911 | 2005 | 230 | 1366.5 | 2830.5 | 130 | 554 | 262.5 | 137 | 0 | 15.5 | 1280.1775 | [7 empty] | Energy Requirement | 317.1331 | 317.1331
3:00 | 4318 | 911 | 2018 | 260 | 1355 | 2833 | 130 | 554 | 254 | 134 | 0 | 20 | 1253.915
3:30 | 4341 | 911.5 | 2018 | 205 | 1348 | 2834.5 | 130 | 555 | 248 | 135 | 0 | 22 | 1243.41
4:00 | 4364 | 912 | 2018 | 150 | 1341 | 2836 | 130 | 556 | 242 | 136 | 0 | 24 | 1232.905
4:30 | 4371.5 | 911.5 | 2015 | 150 | 1346.5 | 2837 | 130 | 555.5 | 242 | 135 | 0 | 26 | 1174.65
5:00 | 4379 | 911 | 2012 | 150 | 1352 | 2838 | 130 | 555 | 242 | 134 | 0 | 28 | 1116.395
5:30 | 4353.5 | 911 | 2006 | 75 | 1354.5 | 2815.5 | 130 | 530.5 | 242 | 130 | 7.5 | 26.5 | 1067.69
6:00 | 4328 | 911 | 2000 | 0 | 1357 | 2793 | 130 | 506 | 242 | 126 | 15 | 25 | 1018.985
6:30 | 4304.5 | 910.5 | 1961.5 | 0 | 1359 | 2802 | 130 | 446 | 236.5 | 122 | 43.5 | 24 | 1012.7775 | [6 empty] | Coal
7:00 | 4281 | 910 | 1923 | 0 | 1361 | 2811 | 130 | 386 | 231 | 118 | 72 | 23 | 1006.57
7:30 | 4282 | 910.5 | 1939.5 | 0 | 1350 | 2831.5 | 130 | 367.5 | 223.5 | 119 | 139.5 | 24.5 | 1009.9125 | [5 empty] | Oil
8:00 | 4283 | 911 | 1956 | 0 | 1339 | 2852 | 130 | 349 | 216 | 120 | 207 | 26 | 1013.255
8:30 | 4252.5 | 911 | 1945 | 0 | 1359 | 2867.5 | 112.5 | 348 | 216 | 123 | 233 | 27 | 1055.7525
9:00 | 4222 | 911 | 1934 | 0 | 1379 | 2883 | 95 | 347 | 216 | 126 | 259 | 28 | 1098.25
9:30 | 4211 | 911.5 | 1916 | 5 | 1519.5 | 2856 | 112.5 | 344 | 234 | 133 | 326.5 | 28 | 1077.24
10:00 | 4200 | 912 | 1898 | 10 | 1660 | 2829 | 130 | 341 | 252 | 140 | 394 | 28 | 1056.23
10:30 | 4182.5 | 911.5 | 1868.5 | 11.5 | 1772 | 2759.5 | 130 | 341 | 292.5 | 139 | 389 | 14 | 848.995
11:00 | 4165 | 911 | 1839 | 13 | 1884 | 2690 | 130 | 341 | 333 | 138 | 384 | 0 | 641.76
11:30 | 4129 | 910.5 | 1841.5 | 6.5 | 1942.5 | 2707.5 | 130 | 333 | 358 | 126 | 364.5 | 13.5 | 513.38
12:00 | 4093 | 910 | 1844 | 0 | 2001 | 2725 | 130 | 325 | 383 | 114 | 345 | 27 | 385
12:30 | 3895 | 910.5 | 1718.5 | 0 | 2006 | 2631.5 | 130 | 327 | 390.5 | 118 | 320 | 13.5 | 300.415
13:00 | 3697 | 911 | 1593 | 0 | 2011 | 2538 | 130 | 329 | 398 | 122 | 295 | 0 | 215.83
13:30 | 3697 | 911 | 1593 | 0 | 2011 | 2538 | 130 | 329 | 398 | 122 | 295 | 0 | 215.83
14:00 | 3697 | 911 | 1593 | 0 | 2011 | 2538 | 130 | 329 | 398 | 122 | 295 | 0 | 215.83
14:30 | 3799.5 | 911 | 1697 | 0 | 1710.5 | 2565.5 | 126 | 299.5 | 361.5 | 120 | 256 | 15 | 162.8275
15:00 | 3902 | 911 | 1801 | 0 | 1410 | 2593 | 122 | 270 | 325 | 118 | 217 | 30 | 109.825
15:30 | 3984 | 911 | 1838 | 0 | 1488 | 2493.5 | 122 | 276.5 | 283 | 117 | 149 | 30 | 143.25
16:00 | 4066 | 911 | 1875 | 0 | 1566 | 2394 | 122 | 283 | 241 | 116 | 81 | 30 | 176.675
16:30 | 4006.5 | 910.5 | 1832 | 0 | 1508.5 | 2352.5 | 126 | 284.5 | 217 | 113 | 62 | 30 | 111.2575
17:00 | 3947 | 910 | 1789 | 0 | 1451 | 2311 | 130 | 286 | 193 | 110 | 43 | 30 | 45.84
17:30 | 3895 | 910 | 1794 | 0 | 1498.5 | 2328.5 | 115 | 311 | 218.5 | 107 | 32 | 29.5 | 32.9475
18:00 | 3843 | 910 | 1799 | 0 | 1546 | 2346 | 100 | 336 | 244 | 104 | 21 | 29 | 20.055
18:30 | 4086 | 910.5 | 1892 | 0 | 1934 | 2415.5 | 115 | 338.5 | 417 | 120 | 10.5 | 29 | 25.785
19:00 | 4329 | 911 | 1985 | 0 | 2322 | 2485 | 130 | 341 | 590 | 136 | 0 | 29 | 31.515
19:30 | 4239 | 911 | 1948 | 0 | 2898 | 2550 | 130 | 334 | 698 | 134 | 0 | 28 | 77.8325
20:00 | 4186 | 870 | 1937 | 0 | 2845 | 2636 | 130 | 339 | 714 | 134 | 0 | 29 | 124.15
20:30 | 4160 | 870 | 1966.5 | 0 | 2858 | 2617 | 130 | 351 | 712 | 131 | 0 | 29 | 167.6025
21:00 | 4134 | 870 | 1996 | 0 | 2871 | 2598 | 130 | 363 | 710 | 128 | 0 | 29 | 211.055
21:30 | 4183.5 | 826.5 | 2017.5 | 0 | 2793.5 | 2597.5 | 130 | 362.5 | 666 | 131 | 0 | 29.5 | 226.8125
22:00 | 4233 | 783 | 2039 | 0 | 2716 | 2597 | 130 | 362 | 622 | 134 | 0 | 30 | 242.57
22:30 | 4178.5 | 782.5 | 2047 | 0 | 2651.5 | 2612.5 | 130 | 362 | 620 | 139 | 0 | 26 | 287.455
23:00 | 4124 | 782 | 2055 | 0 | 2587 | 2628 | 130 | 362 | 618 | 144 | 0 | 22 | 332.34
23:30 | 4174.5 | 782 | 2072 | 0 | 2538 | 2634 | 130 | 363 | 553.5 | 138 | 0 | 25 | 372.45 |  | Max Temp. in Dhaka |  | 36.8° C
24:00 | 4225 | 782 | 2089 | 0 | 2489 | 2640 | 130 | 364 | 489 | 132 | 0 | 28 | 412.56
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 302.945 MKWHr Energy Not Served 14.189 MKWHr Energy Requirement 317.133 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-08-01
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 35 | 70 | 70 | 70 | 70 | 70 | 66 | 66 | 70 | 40 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1580160
2 | Karnaphuli Hydro PP Unit-4 & 5 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 56 | 56 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1444000
3 | Chattogram TPP-1 | 118 | 118 | 115 | 120 | 120 | 120 | 118 | 118 | 120 | 110 | 115 | 115 | 110 | 120 | 122 | 116 | 122 | 114 |  | 121 | 118 | 112 | 116 | 118 | 110 | 122 | 2700000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 17 | 17 | 17 | 14 | 17 | 17 | 17 | 18 |  | 25 | 25 | 25 | 25 | 25 | 17 | 17 | 358417
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 5 | 5 | 5 | 0 | 2 | 5 | 2 | 2 | 9 | 3 | 0 | [8 empty] | 41985
6 | Sikalbaha 225MW CCPP (Gas) | 225 | 220 | 221 | 221 | 221 | 223 | 223 | 221 | 219 | 226 | 224 | 221 | 225 | 220 | 217 | 217 | 219 | 222 |  | 217 | 225 | 224 | 225 | 221 | 220 | 219 | 5183038
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 48 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1193680
12 | Hathazari 100 MW peaking PP | 42 | 42 | 42 | 42 | 42 | 42 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 50 | 8 | 8 | 8 | 8 |  | 40 | 48 | 48 | 50 | 50 | 50 | 50 | 844704
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 1009491
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 46 | 39 | 32 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 23 | 23 | 23 | 38 | 37 | 37 |  | 23 |  | 37 | 37 | 37 | 37 | 37 | 37 | 28 | 780496
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 177 | 191 | 180 | 180 | 176 | 179 | 180 | 186 | 185 | 179 | 180 | 179 | 69 | 70 | 154 | 175 | 75 | 72 |  | 128 | 125 | 126 | 95 | 103 | 102 | 187 | 3744000
17 | Siddhirganj 335 MW CCPP | 332 | 326 | 329 | 327 | 325 | 333 | 333 | 327 | 321 | 320 | 318 | 317 | 280 | 250 | 321 | 320 | 321 | 280 |  | 290 | 323 | 324 | 325 | 327 | 326 | 326 | 7618858
18 | Kodda 300 MW PP Unit-2 (Summit) | 100 | 120 | 115 | 112 | 107 | 112 | 115 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 45 | 45 |  | 55 | 95 | 95 | 105 | 115 | 115 | 115 | 2561780
19 | Ashuganj 195 MW PP (APSCL-United) | [25 empty] | 0 | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 130 | 130 | 130 | 210 | 160 | 130 |  | 190 | 210 | 206 | 144 | 150 | 150 | 210 | 4450847
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4315500
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 310 | 310 | 310 | 310 | 310 | 300 | 307 | 352 | 423 | 430 | 400 | 360 | 275 | 269 | 283 | 280 | 250 | 213 |  | 115 | 0 |  |  |  |  | 0 | 5901818
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP
33 | Ashuganj 225 MW CCPP | 187 | 191 | 181 | 189 | 186 | 182 | 185 | 166 | 168 | 172 | 177 | 171 | 200 | 204 | 189 | 184 | 190 | 180 |  | 200 | 180 | 180 | 180 | 189 | 175 | 175 | 4463000
34 | Ashuganj 450 MW CCPP(South) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 275 | 300 | 295 | 230 | 230 | 230 | 250 | 265 | 280 | 270 |  | 330 | 270 | 270 | 270 | 290 | 290 | 250 | 6483000
| Ashuganj 450 MW CCPP(North) | 280 | 335 | 280 | 285 | 305 | 280 | 280 | 300 | 280 | 280 | 280 | 280 | 280 | 280 | 285 | 280 | 290 | 280 |  | 330 | 280 | 280 | 280 | 300 | 300 | 290 | 7290600
| Ashuganj 420 MW CCPP(East) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 230 | 230 | 230 | 240 | 220 | 230 | 230 | 230 | 230 | 230 |  | 335 | 288 | 285 | 285 | 295 | 260 | 240 | 6170800
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 396 | 396 | 397 | 397 | 397 | 397 | 396 | 397 | 397 | 398 | 399 | 396 | 389 | 326 | 364 | 396 | 397 | 397 |  | 361 | 399 | 397 | 399 | 399 | 399 | 399 | 9510910
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 340 | 340 | 420 | 450 | 380 | 340 |  | 420 | 420 | 420 | 450 | 450 | 450 | 450 | 9884300
41 | Haripur 360 MW CCPP(HPL) | 331 | 332 | 333 | 332 | 332 | 332 | 332 | 331 | 322 | 322 | 322 | 323 | 281 | 282 | 322 | 330 | 302 | 302 |  | 336 | 343 | 301 | 332 | 331 | 333 | 332 | 7762000
42 | RPCL 210MW CCPP | 96 | 96 | 95 | 96 | 97 | 98 | 44 | 44 | 44 | 44 | 44 | 43 | 32 | 32 | 32 | 32 | 46 | 51 |  | 67 | 82 | 82 | 82 | 82 | 54 | 67 | 1464000
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 11 | 27 | 40 | 49 | 51 | 51 | 51 | 49 | 42 | 22 | 3 | 3 |  | 0 | [6 empty] | 398750
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 0 |  | 10 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 624000
45 | Fenchugonj CCPP Phase-2 | [21 empty] | 0 | 10 | 10 | 10 | 10 | 24960
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 28 | 30 | 30 | 30 |  | 30 | 30 | 30 | 28 | 25 | 20 | 20 | 554112
48 | Shahjibazar 86 MW PP (Shahjibazar) | 78 | 78 | 78 | 78 | 75 | 75 | 72 | 72 | 72 | 72 | 75 | 75 | 78 | 73 | 78 | 81 | 86 | 86 |  | 86 | 86 | 86 | 86 | 84 | 84 | 84 | 1846084
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 110 | 110 | 110 | 110 | 110 | 109 | 109 | 109 | 109 | 111 |  | 111 | 112 | 112 | 112 | 112 | 112 | 112 | 2681190
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 380000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 10 | 10 | 8 | 8 | 8 | 8 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 218160
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  |  | 5 | 5 |  | 8 | 11 | 11 | 10 | 5 | 9 | 9 | 132288
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 42 | 42 | 42 | 42 | 42 | 41 | 38 | 41 | 41 | 41 | 41 | 44 | 44 | 44 |  | 49 | 49 | 50 | 50 | 50 | 50 | 50 | 1068600
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 23 | 23 | 16 | 16 | 23 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 533976
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 300 | 310 | 305 | 310 | 300 | 290 | 305 | 310 | 300 | 270 | 280 | 275 | 275 | 285 | 310 | 270 | 280 |  | 300 | 255 | 260 | 260 | 290 | 300 | 310 | 7193500
| Bibiyana South 400 MW | 387 | 382 | 389 | 387 | 385 | 385 | 385 | 380 | 375 | 365 | 360 | 355 | 345 | 355 | 355 | 355 | 355 | 355 |  | 355 | 355 | 328 | 328 | 355 | 355 | 355 | 8768200
58 | Nababganj 55 MW PP (Southern power ) | [10 empty] | 17 | 17 | 35 |  | 17 | 35 | 35 | 35 |  |  | 17 | 35 | 17 | 7 | 17 | 17 | 285061
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 1 | 3 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 140640
60 | Barabkunda 22 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 250416
61 | Narshingdi 22 MW PP (Doreen) |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [5 empty] | 17 |  | 19 | 19 | 19 | 19 | 19 |  | 0 | 297432
62 | Tangail 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 15 | 15 | 15 | 15 |  |  | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 342504
63 | Impoprt (Tripura) | 138 | 140 | 134 | 136 | 134 | 126 | 118 | 120 | 126 | 140 | 138 | 114 | 122 | 110 | 118 | 116 | 110 | 104 |  | 136 | 134 | 134 | 128 | 134 | 144 | 132 | 3001920
64 | Malancha, Ctg. EPZ (United) | 26 | 30 | 30 | 29 | 29 | 30 | 30 | 8 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 10 | 25 |  | 27 | 20 | 31 | 33 | 36 | 36 | 36 | 444480
65 | Feni 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15 | 15 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 20 | 20 | 20 | 441136
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 | [11 empty] | 11 | 11 | 11 | 11 | 158040
67 | Jangalia 33 MW PP (Summit) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 25 | 25 | 25 | 20 | 17 | 16 |  | 16 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 32 | 534700
68 | Cumilla 25 MW PP (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 20 | 20 | 20 | 20 | 404760
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456000
70 | Summit Madhabdi | 8 | 12 | 21 | 21 | 19 | 19 | 19 | 19 | 19 | 22 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 14 | 411480
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 651240
72 | Rupganj 33 MW PP(Summit) | 12 | 17 | 17 | 17 | 17 | 16 | 8 | 16 | 16 | 16 | 2 | 6 | 0 | 7 | 7 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 8 | 8 | 366600
73 | Ghorashal 108 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 288545
| Feni Lanka Power | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 17 | [5 empty] | 53 | 70 | 26 | 17 | 17 | 17 | 88 | 664620
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 26 | [14 empty] | 0 | 112560
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 162 | 162 | 162 | 162 | 162 | 162 | 144 | 1530720
77 | Siddhirganj 100 PP(Dutch Bangla) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 35 | 42 | 24 | 9 | 9 | 9 | 9 |  | 10 | 20 | 30 | 62 | 39 | 32 | 32 | 664320
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 281318
79 | Kodda 150 MW PP | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 82 | 82 | 82 | 82 | 82 | 82 | 64 | 64 |  | 98 | 115 | 130 | 130 | 130 | 130 | 130 | 1799520
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 40 | 34 | 8 | 8 | [5 empty] | 2 | 8 | 8 | 8 | 8 | 8 | 34 | 588643
| Gazipur 100 MW PP | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 105 | 105 | 105 | 105 | 105 | 105 | 35 | 1172189
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 1 | 1 | 2 | 3 | 2 | 3 | 2 | 2 | 2 | 1 | 0 | [8 empty] | 21117
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 27 | 36 | 36 | 36 | 36 | 526871
| Karnaphuli Power Ltd. | 55 | 55 | 55 | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 41 | 53 | 55 | 55 | 55 | 55 | 34 | 30 |  | 36 | 51 | 48 | 55 | 55 | 55 | 55 | 1271279
82 | Madanganj 102 PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 36 | 51 | 51 | 51 | 34 | 22 | 17 | 463493
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [8 empty] | 12 | 21 | 10 | 11 | 12 | 32 | [5 empty] | 4 | 11 | 11 | 10 | 15 | 23 | 30 | 222362
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 49 | 51 | 50 | 50 | 50 | 50 | 50 | 44 | 43 | 42 | 43 | 42 | 42 | 15 | 9 | 8 | 9 | 8 |  | 9 | 50 | 44 | 28 | 9 | 8 | 8 | 751680
| Meghnaghat 104 MW PP (OPCL) | 54 | 50 | 35 | 35 | 53 | 53 | 53 | 40 | 35 | 35 | 53 | 53 | 53 | 53 | 35 | 48 | 53 | 53 |  | 59 | 72 | 72 | 72 | 72 | 72 | 54 | 1230720
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 12 | 12 | 12 | 12 |  | 58 | 58 | 12 | 25 | 25 | 25 | 46 | 826680
92 | Fenchuganj 44 MW (Energyprima) | 46 | 46 | 46 | 47 | 43 | 46 | 46 | 46 | 46 | 41 | 39 | 39 | 38 | 38 | 38 | 43 | 45 | 45 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1052640
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 948056
94 | Gagnagar 102 MW PP (Digital Power) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 42 | 50 | 50 | 8 | 8 | 8 | 8 | 8 |  | 48 | 85 | 102 | 66 | 32 | 32 | 102 | 747936
95 | Patenga 50MW PP (Baraka) | 46 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | [13 empty] | 30 | 44 | 46 | 210720
96 | Chattogram 108 MW PP (ECPV) | [9 empty] | 0 |  |  |  | 6 | 11 | 12 | 15 | 25 |  | 34 | 34 | 31 | 32 | 36 |  | 0 | 214080
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 25 | 25 | 15 | 15 | 15 | 15 | 0 |  | 13 | 15 | 15 | 15 | 15 | 15 | 15 | 380346
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 4 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 525969
101 | Kushiara 163 MW CCPP (KP) | [16 empty] | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 112 | 636054
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 16350
103 | Kamalaghat 54 MW PP(Banco Energy) | [9 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 386172
104 | Keranigonj 300 MW PP (APR) | 300 | 200 | 260 | 150 | 150 |  |  |  |  | 10 | 13 | [14 empty] | 0 | 1231708
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 67 | 67 | 67 | 66 | 66 | 66 | 66 | 66 | 68 | 55 |  | 83 | 85 | 87 | 88 | 88 | 68 | 68 | 1639200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 64 | 71 | 70 | 70 | 67 | 69 | 69 | 69 | 70 | 70 |  | 92 | 149 | 144 | 147 | 149 | 149 | 63 | 1739088
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 36 | 37 | 37 | 25 | 12 | 12 |  | 26 | 100 | 100 | 100 | 100 | 100 | 25 | 925440
116 | Chandpur 200 MW (Desh energy) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 56 | 68 | 99 | 85 | 51 | 51 | 54 | 84 | 120 |  | 120 | 120 | 145 | 155 | 155 | 155 | 110 | 1889280
117 | Ashuganj 150 MW PP (Midland) | 20 | 6 | 6 | 6 | 5 | 6 | 6 | 5 | 6 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | 6 | 5 |  | 21 | 40 | 45 | 55 | 62 | 51 | 13 | 373018
118 | Bibiyana-III 400 MW CCPP | 374 | 409 | 368 | 397 | 403 | 367 | 367 | 385 | 383 | 368 | 369 | 387 | 319 | 370 | 384 | 368 | 368 | 318 |  | 404 | 368 | 368 | 368 | 372 | 386 | 386 | 8996000
| Jamalpur 115 MW PP (United) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 18 | 17 | 17 | 17 | 17 | 17 | 18 | 18 |  | 84 | 84 | 84 | 84 | 84 | 28 | 19 | 718800
| Anwara 300 MW PP (United) | 86 | 87 | 87 | 87 | 87 | 87 | 87 | 88 | 88 | 88 | 121 | 122 | 124 | 105 | 65 | 120 | 85 | 85 |  | 170 | 221 | 220 | 220 | 170 | 170 | 190 | 2913055
| Juldah unit-2 (Acorn) | 50 | 50 | 50 | 50 | 38 | 38 | 38 | 38 | 38 | 25 | 38 | 38 | 38 | 38 | 12 | 12 | 12 | 12 |  | 36 | 88 | 38 | 38 | 38 | 38 | 88 | 912960
| Anlima Energy Ltd. | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 44 | 68 | 68 | 68 | 68 | 68 | 68 | 1032027
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 28 | 35 | 35 | 35 | 25 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 511560
| Spectra Solar Plant Ltd. | [5 empty] | 2 | 9 | 18 | 24 | 27 | 32 | 33 | 36 | 2 | 23 | 6 | 4 | 1 | [8 empty] | 203683
| Chandpur 115(Doreen) | 18 | 17 | 18 | 17 | 18 | 17 | 18 | 17 | 18 | 26 | 67 | 72 | 67 | 17 | 17 | 17 | 32 | 87 |  | 115 | 115 | 114 | 114 | 115 | 115 | 85 | 1234560
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 17 |  | 10 | 17 | 17 | 17 | 17 |  | 24 | 17 | 22 | 24 | 17 | 17 | 17 | 435600
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 53 | 70 | 70 | 70 | 17 | 17 | 17 | 17 | 17 |  | 70 | 140 | 142 | 142 | 70 | 70 | 70 | 1006981
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 1 | 11 | 20 | 24 | 28 | 25 | 23 | 26 | 28 | 28 | 0 | 27 | 0 | 28 | 30 | 30 | 30 | 29 |  | 29 | 28 | 29 | 29 | 30 | 22 | 28 | 541440
| Matarbari 2*600 MW (CPGCL) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 126 | 18 | 125 | 124 | 150 | 0 | [10 empty] | 0 | 1658181
120 | Eastern Zone Total | 7534 | 7516 | 7463 | 7388 | 7408 | 7188 | 7125 | 7189 | 7240 | 7416 | 7387 | 7430 | 6825 | 6515 | 6514 | 6796 | 6480 | 6368 |  | 7714 | 8037 | 7922 | 7935 | 7896 | 7682 | 7644 | 174865154
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 360000
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL) | 220 | 220 | 220 | 220 | 220 | 170 | 50 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 31 | 81 |  | 86 | 79 | 84 | 108 | 107 | 107 | 109 | 2071840
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 11 | 11 | 11 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 5 | 8 | 5 | 12 |  | 25 | 39 | 35 | 26 | 21 | 21 | 10 | 276480
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2916666
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 35 | 35 | 35 | 35 | 53 | 17 | 35 | 17 | 35 |  | 35 | 40 | 45 | 53 | 53 | 53 | 54 | 938016
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 3 | 17 | 55 | 50 | 90 | 100 | 56 | 2 | 8 | 30 | 14 | 10 | 2 |  | 0 | [6 empty] | 425520
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | 150 | 54 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 5 | 17 | 17 |  | 62 | 100 | 100 | 100 | 54 | 54 | 54 | 884400
133 | Bhola Nutan Biddut BD LTD (GAS) | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 220 | 182 | 182 | 220 | 220 | 168 | 167 |  | 220 | 220 | 217 | 217 | 220 | 222 | 223 | 5122309
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 50 | 100 | 110 | 110 | 16 | 32 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 725760
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 136 | 111 | 63 | 40 | [14 empty] | 1680000
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 122 | 124 | 132 | 70 | 80 | 132 | 132 | 80 | 80 |  | 132 | 132 | 124 | 130 | 132 | 132 | 130 | 2914000
140 | Bhola 33 MW PP (Venture) | 30 | 32 | 30 | 29 | 30 | 24 | 24 | 21 | 17 | 19 | 4 | 11 | 11 | 9 | 8 | 7 | 7 | 9 |  | 14 | 16 | 15 | 15 | 18 | 14 | 13 | 421567
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [6 empty] | 8 |  |  |  | 8 | 8 | 8 | 8 |  |  | 0 | 104250
143 | Gopalganj 100 MW Peaking PP | 44 | 48 | 38 | 38 | 38 | 38 | 35 | 20 | 20 | 20 | 20 | 19 | 20 | 20 |  |  |  | 0 |  | 55 | 60 | 60 | 58 | 58 | 53 | 50 | 678528
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 |  | 42 | 50 | 50 | 50 | 50 | 50 | 105 | 617472
146 | Bheramara HVDC | 911 | 911 | 911 | 912 | 911 | 911 | 910 | 911 | 911 | 912 | 911 | 910 | 911 | 912 | 911 | 911 | 910 | 910 |  | 911 | 911 | 870 | 870 | 783 | 782 | 782 | 21460363
147 | Bheramara 410 MW CCPP | 145 | 150 | 150 | 150 | 150 | 150 | 165 | 155 | 140 | 140 | 140 | 130 | 125 | 120 | 120 | 115 | 120 | 120 |  | 120 | 130 | 125 | 130 | 130 | 130 | 135 | 3507264
148 | Payra 1320 MW | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1215 | 1210 | 1230 | 1230 | 1100 | 1070 | 1090 | 1172 | 1120 | 1110 |  | 1170 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 30867700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 210 | 210 | 210 | 210 | 210 | 180 | 180 | 180 | 180 | 180 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 220 |  | 240 | 240 | 230 | 200 | 200 | 200 | 200 | 4973000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 0 | 185380
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 3 | 4 | 5 | 5 | 5 | 5 | 1 | 0 | 1 | 0 | [8 empty] | 37080
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 211 | 214 | 214 | 216 | 215 | 216 | 216 | 214 | 212 | 211 | 211 | 195 | 199 | 140 | 140 | 153 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 4540127
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 150 | 150 | 151 | 153 | 154 | 155 | 154 | 152 | 149 | 147 | 145 | 143 | 141 | 141 | 140 | 140 | 145 | 144 |  | 144 | 145 | 146 | 147 | 147 | 147 | 147 | 3780291
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 390 | 390 | 407 | 414 | 414 | 414 | 350 | 394 | 386 | 365 | 353 | 338 | 280 | 280 | 324 | 325 | 334 | 357 |  | 343 | 349 | 367 | 363 | 370 | 376 | 369 | 8753381
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 20 | [11 empty] | 5 | 5 | 21 | 15 | 19 | 24 |  | 24 | 24 | 24 | 35 | 23 | 23 | 23 | 306632
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 159498
165 | Amnura 50 MW PP(Sinha) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 25 | 14 | 14 | 14 | 20 | 20 |  | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 480890
166 | Katakhali 50 MW PP (Northern) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 25 | 34 | 8 | 8 | 8 | 8 | 8 |  | 8 | 25 | 34 | 34 | 34 | 25 | 34 | 308471
167 | Katakhali 50 MW Peaking PP | 23 | 16 | 16 | [7 empty] | 26 | 30 | 35 | 36 | 36 |  |  |  |  | 34 | 36 | 39 | 35 | 35 | 36 | 28 | 374716
168 | Santahar 50 MW Peaking PP | [10 empty] | 6 | 18 | 22 | 22 | 24 | 24 | 30 | 30 |  | 30 | 22 | 22 | 22 | 23 | 23 | 23 | 276726
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200515
170 | Chapainawabganj 100 MW Peaking PP | [10 empty] | 12 | 47 | 47 | 47 | 47 |  |  | 16 |  | 92 | 92 | 92 | 90 | 90 | 90 | 27 | 682072
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 37 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 70 | 70 | 70 | 95 | 95 | 95 | 95 | 95 | 100 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1967904
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2148480
173 | Rangpur 20 MW GTPP | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 98 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 96 | 96 | 98 | 86 | 90 | 80 | 85 | 103 | 104 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1812892
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 3 | 5 | 6 |  | 7 | 7 | 7 | 6 | 4 | 2 | 1 | [8 empty] | 55750
178 | Energypac Power Venture Thakurgaon Ltd. | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 75 | 102 | 113 | 112 | 112 | 112 | 112 | 95 | 95 |  | 100 | 115 | 115 | 115 | 115 | 114 | 113 | 1873152
| Intraco Solar 30 MW | [5 empty] | 1 | 8 | 15 | 13 | 35 | 21 | 19 | 32 | 19 | 27 | 19 | 7 | 2 |  | 0 | [6 empty] | 232602
| Adani Power Jharkhanda Ltd | 767 | 764 | 769 | 772 | 774 | 769 | 780 | 776 | 779 | 772 | 769 | 760 | 829 | 919 | 1010 | 732 | 731 | 803 |  | 960 | 1066 | 1162 | 1154 | 1153 | 1184 | 1196 | 17863636
178 | Teesta Solar Limited | [5 empty] | 7 | 24 | 80 | 116 | 174 | 170 | 168 | 152 | 200 | 82 | 4 | 12 | 12 | [8 empty] | 1094110