## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-08-05 | Saturday
|  | Date (day): | 2023-08-05 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13101.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14855 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-08-04 | 2023-08-05 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 140 | 210 | 160 | 180
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 12 | 12 | 96 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 357 | 393 | 390 | 393 | 19
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 332 | 342 | 325 | 340 | 20 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 9 | 42 | 50 | 50 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 17 | 12 | 17 | 50 | 52 |  | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 15 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 57 | 60 | 60
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 10 | 20 | 17 | 20
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 123 | 197 | 190 | 190 | 20
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 9 | 32 | 55 | 55 | 45 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 328 | 331 | 330 | 330
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 25 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 17 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 64 | 130 | 64 | 130 | 19 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 20 | 35 | 35 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 35 | 35 | 20 |  | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 41 | 38 | 39 | 41 |  | 39 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 25 | 25 | 25 |  | 8 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 16 | 30 | 30 | 30
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 25 | 8 | 25 | 27 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 15 | 30 | 96 | 96 | 204 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 100 | 200
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
33 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
34 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 35 | 116 | 35 | 116 | 33 |  | Fuel shortage
35 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 105 | 35 | 105
36 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 25 | 72 | 53 | 72 | 32 |  | Fuel shortage
37 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 54 | 54 | 108 | 54 |  | Fuel shortage
38 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 10 | 0 | 35 | 0
39 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 30 | 17 | 30 | 25 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6063 | 5722 | 2324 | 3045 | 2923 | 3410 | 1151 | 1142
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 116 | 115 | 120 | 120 |  | 60
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
41 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 25 | 8 | 25
42 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 11 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 6 | 6 | 45
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 106 | 104 | 100 | 104 | 130 |  | Low Water Level
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 224 | 222 | 225 | 225
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 17 | 17 | 88 |  | Fuel shortage
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 25 | 50 | 25 | 50 | 48 |  | Fuel shortage
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 34 | 49 | 50 | 50 | 52 |  | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 12 | 25 | 70 | 80 | 20 |  | Fuel shortage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 86 | 85 | 85 | 15 |  | Fuel shortage
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 12 | 11 | 12 | 12 | 10 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 16 | 38 | 10 | 25
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 37 | 12 | 37 | 71 |  | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 1 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 66 | 100 | 120 | 300
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 42 | 54 | 55 | 55 | 55 |  | Fuel shortage
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 32 | 25 | 38 | 88 | 12 |  | Fuel shortage
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 34 | 34 | 34 | 34 | 82 |  | Fuel shortage
60 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 43 | 17 | 54 | 144 | 19 |  | Fuel shortage
| SS Power I |  | Coal | SS Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 22 | 7 | 22 | 22 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 150 | 150 | 0 | 0
| Chattogram area Total |  |  |  |  | 2605 | 2545 | 1013 | 1189 | 1105 | 1535 | 639 | 390
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 168 | 185 | 180 | 180 | 41 |  | Gas shortage
62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 275 | 270 | 270 | 270 | 90 |  | Gas shortage
63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 240 | 230 | 230 | 230 | 130 |  | Gas shortage
64 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 230 | 220 | 230 | 230 | 170 |  | Gas shortage
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 0 | 0 | 0 | 45 |  | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
69 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 5 | 60 | 6 | 60 | 90 |  | Fuel shortage
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 25 | 25 | 25 | 25 |  | 27 | Machine problem
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
72 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 70 | 100 | 68 | 150 | 50 |  | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 20 | 22
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 6 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 132 | 154 | 146 | 160
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 32 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 42 |  | 10 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 21 | 20 | 21 |  | 4 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Contract Expired
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 34 | 17 | 17 | 97 |  | Fuel shortage
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 59 | 9 | 60 | 57 |  | Fuel shortage
81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 46 | 112 | 72 | 115
| Cumilla Area Total |  |  |  |  | 3159 | 3096 | 1338 | 1601 | 1404 | 1686 | 965 | 249
83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 33 | 83 | 35 | 85 | 117 |  | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 17 | 17 |  | 5 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 68 | 88 | 68 | 88 | 112 |  | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 85 | 18 | 85 | 30 |  | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 11 | 0 | 50 | 0
90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 156 | 279 | 195.6 | 281 | 117 | 5
91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 40 | 40 | 40 |  | 50
93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 112 | 112 |  | 51 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 50 | 50
96 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 46 | 46 | 48 | 48
97 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 25 | 25 | 30 | 30 |  | 36 | Unit-9 under maint
99 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 86 | 80 | 86
100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 65 | 130 | 80 | 130 |  | 101 | ST Under maint
102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 17 | 17
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
103 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 24 | 24
104 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 295 | 300 | 300 |  |  | FGMO
105 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 366 | 403 | 400 | 400 |  |  | FGMO
106 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
107 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 355 | 355 | 355 | 355
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1503 | 1644 | 1597 | 1653 | 0 | 698
108 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 905 | 851 | 910 | 910
109 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 5 | 16 | 32 | 66 | 49 |  | Fuel shortage
110 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 40 |  | 14 | Engine problem
111 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 115 | 115 | 120 | 120 | 110 |  | Fuel shortage
112 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 40 | 70 |  | 39 | Engine problem
113 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 100 | 270 | 200 | 250 | 160 |  | Gas shortage
114 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 8 | 8 | 8 | 8 | 32 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
115 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 35 | 35 | 35 | 70 |  | Fuel shortage
116 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 5 | 15 | 15 | 85 | 20 |  | Fuel shortage
117 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 36 | 0 | 100 | 0
118 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 220 | 220 | 105 | 105 | 120 | 120 | 100 |  | Fuel shortage
119 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0 | 617 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3125 | 3121 | 1279 | 1415 | 1580 | 1704 | 1174 | 53
120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 16 | 64 | 46 |  | Fuel shortage
121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 20 | 30 | 22 | 30 |  | 10 | Engine problem
122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 132 | 132 | 132 | 132 |  | 62 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244
124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 225 | 220 | 220 | 220
125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 17 | 150
126 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 | 307 |  | Coal shortage
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1621 | 1659 | 1651 | 1840 | 353 | 72
127 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
128 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
129 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 16 | 0 | 30 |  | 41 | Engine problem
130 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0
131 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 8 | 42 | 42 |  | 8 | Engine problem
132 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 | 20 |  | Engine problem
133 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Under maint
134 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 140 | 200 | 220
135 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 170 | 158 | 160 | 160 | 60 |  | Gas shortage
136 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 320 | 414 | 414 | 414
137 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 20 | 30 | 20 |  | Fuel shortage
138 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 8 | 44 |  | Fuel shortage
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 92 | 50 | 92 | 12 |  | Fuel shortage
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 50 | 35 | 50 | 63 |  | Fuel shortage
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 55 | 35 | 55 | 58 |  | Fuel shortage
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 1 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 748*2 | 1496 | 1496 | 1211 | 1209 | 1200 | 1200
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 1920 | 2218 | 2208 | 2339 | 500 | 262
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 200 | 200
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 70 | 35 | 92 |  | 21 | Engine problem
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 75 | 35 | 115
153 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 205 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 472 | 345 | 438 | 407 | 125 | 106
| Total |  |  |  |  | 24911 | 24171 | 11626 | 13395 | 13101.6 | 14855 | 5024 | 2977
A. |  | 2023-08-04 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 13554 | MW at | 23:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 10838 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13395 | MW
3 | Day peak Generation : |  |  | 11626 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12803.99 | MW
4 | Evening peak Generation : |  |  | 13395 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 285.3019 | MKWHr | By Solar | 2.028 | MKWHr
| By Gas : | 144.6455 | MKWHr |  | By Oil: | 47.5662 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 65.0576 | MKWHr |  | By Hydro: | 0.901 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.4296 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5024 | MW | Dhaka | 4209.99 | 4209.99 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2977 | MW | Chittagong | 1240.5 | 1240.5 |  | 0 |  | 19:00 |  | 9.55
|  |  | Total = |  |  | 8001 | MW | Khulna | 1619.5 | 1619.5 |  | 0 |  | 19:30 |  | 9.55
7 | Total Gas Supplied : |  |  | 1125.55 | MMCFD |  |  | Rajshahi | 1538.6 | 1538.6 |  | 0 |  | 20:00 |  | 20.055
8 | Fuel Cost : | i) Gas : | Taka | 160820776.838 | ii) Oil : | Taka | 622090837.14 | Comilla | 1236 | 1236 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 295618435 | Total | Taka | 1078530048.978 | Mymensingh | 1129 | 1129 |  | 0 |  | 22:00 |  | 24.83
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 545 | 545 |  | 0 |  | 23:00 |  | 91.68
| ii) During Peak Demand : |  |  | 970 | MW (E to W) at | 21:00 | hrs | Barisal | 408.4 | 408.4 |  | 0 |  | 24:00 |  | 149.935
| iii) Maximum : |  |  | 630 | MW at | 19:30 | hrs | Rangpur | 877 | 877 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31.8° C |  |  | Total | 12803.99 | 12803.99 |  | 0
B. |  | 2023-08-05 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 31.8° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 14500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14855 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 12500 | MW
4 | Reserve(Generation end) |  |  |  | 355 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 305.2146 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11130 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.5185 | MKWHr. | ii) HVDC Flow at Peak Time |  | 851 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.1555 | MKWHr. | iii) Maximum HVDC Flow : |  | 906 | MW at | 10:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 79.53 |  | (b) Today: | 80.57 |  | (c) Rule Curve: |  | 90.28
.

## YesterdayGen
2023-08-04 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 190 | 180 | 0 | 12 | 0 | 397 | 336 |  | 0 | 450 | 0 | 42 | 17 | 15 | 334 | 0 | 179 | 33 | 25 | 48 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 25 | 31 | 8 | 0 | 75 | 30 | 118 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 34 | 50 | 80 | 0 | 43 | 12 | 33 | 0 | 0 | 0 | 280 | 220 | 166 | 8 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 43 | 19 | 11 | 33 | 20 | 154 | 71 | 0 | 17 | 0 | 43 | 30 | 47 | 48 | 112 | 0 | 25 | 81 | 0 | 112 | 17 | 0 | 10 | 290 | 24 | 8 | 0 | 47 | 0 | 0 | 68 | 0 | 35 | 0 | 25 | 34 | 11 | 402 | 19 | 35 | 34 | 0 | 68 | 36 | 55 | 105 | 9 | 25 | 355 | 57 | 0 | 17 | 34 | 0 | 17 | 0 | 17 | 17 | 230 | 17 | 0 | 0 | 24 | 0 |  | 901 | 0 | 225 | 0 | 19 | 115 | 0 | 0 | 10 | 52 | 0 | 130 | 31 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 22 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 190 | 0 | 414 | 35 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 1244 | 225 | 0 | 17 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0 | 1210 | 0 | 0 |  | 6878 | 5527 | 12405 | 4367 | 901 | 2140 | 0 | 1393 | 2644 | 105 | 419 | 258 | 154 | 0 | 24 | 1141.225 | 79.43
2:00 | 0 | 0 | 190 | 180 | 0 | 12 | 0 | 397 | 337 |  | 0 | 450 | 0 | 42 | 17 | 15 | 335 | 0 | 181 | 33 | 25 | 48 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 25 | 31 | 8 | 0 | 73 | 30 | 116 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 34 | 50 | 80 | 0 | 17 | 10 | 33 | 0 | 0 | 0 | 280 | 220 | 163 | 8 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 43 | 19 | 11 | 33 | 20 | 154 | 70 | 0 | 17 | 0 | 43 | 30 | 47 | 48 | 112 | 0 | 25 | 81 | 0 | 112 | 17 | 0 | 10 | 290 | 24 | 8 | 0 | 47 | 0 | 0 | 68 | 0 | 35 | 0 | 25 | 34 | 6 | 402 | 19 | 35 | 17 | 0 | 69 | 36 | 55 | 34 | 9 | 25 | 355 | 34 | 0 | 17 | 34 | 0 | 17 | 0 | 17 | 17 | 230 | 17 | 0 | 0 | 26 | 0 |  | 902 | 0 | 200 | 0 | 16 | 115 | 0 | 0 | 10 | 46 | 0 | 125 | 31 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 190 | 0 | 414 | 35 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 1244 | 225 | 0 | 17 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0 | 1213 | 0 | 0 |  | 6738 | 5488 | 12226 | 4332 | 902 | 2141 | 0 | 1254 | 2647 | 103 | 437 | 230 | 154 | 0 | 26 | 1121.17 | 79.45
3:00 | 0 | 0 | 188 | 180 | 0 | 12 | 0 | 397 | 336 |  | 0 | 450 | 0 | 41 | 17 | 15 | 335 | 0 | 181 | 33 | 25 | 48 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 25 | 31 | 8 | 0 | 71 | 30 | 114 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 34 | 50 | 80 | 0 | 6 | 10 | 33 | 0 | 0 | 0 | 280 | 220 | 163 | 8 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 43 | 19 | 11 | 33 | 20 | 144 | 69 | 0 | 17 | 0 | 43 | 30 | 47 | 48 | 112 | 0 | 25 | 81 | 0 | 112 | 17 | 0 | 10 | 295 | 24 | 8 | 0 | 47 | 0 | 0 | 68 | 0 | 35 | 0 | 25 | 34 | 6 | 402 | 19 | 35 | 17 | 0 | 69 | 36 | 55 | 17 | 9 | 25 | 355 | 34 | 0 | 17 | 34 | 0 | 17 | 0 | 17 | 17 | 230 | 17 | 0 | 0 | 14 | 0 |  | 904 | 0 | 180 | 0 | 16 | 115 | 0 | 0 | 10 | 46 | 0 | 130 | 30 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 187 | 0 | 414 | 35 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 1244 | 225 | 0 | 17 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0 | 1210 | 0 | 0 |  | 6671 | 5445 | 12116 | 4309 | 904 | 2144 | 0 | 1204 | 2644 | 101 | 422 | 230 | 144 | 0 | 14 | 1035.22 | 79.47
4:00 | 0 | 0 | 190 | 180 | 0 | 12 | 0 | 397 | 337 |  | 0 | 450 | 0 | 42 | 17 | 15 | 335 | 0 | 181 | 33 | 25 | 48 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 33 | 31 | 8 | 0 | 69 | 30 | 116 | 0 | 8 | 224 | 0 | 0 | 0 |  | 6 | 34 | 50 | 80 | 0 | 6 | 10 | 34 | 0 | 0 | 0 | 280 | 220 | 164 | 8 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 43 | 19 | 11 | 33 | 20 | 144 | 70 | 0 | 16 | 0 | 43 | 30 | 47 | 48 | 112 | 0 | 25 | 81 | 0 | 112 | 17 | 0 | 10 | 270 | 24 | 8 | 0 | 47 | 0 | 0 | 68 | 0 | 35 | 0 | 25 | 34 | 5 | 402 | 19 | 35 | 17 | 0 | 69 | 36 | 46 | 17 | 9 | 25 | 355 | 34 | 0 | 17 | 34 | 0 | 17 | 0 | 17 | 17 | 230 | 17 | 0 | 0 | 12 | 0 |  | 903 | 0 | 160 | 0 | 16 | 115 | 0 | 0 | 10 | 46 | 0 | 130 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 182 | 0 | 414 | 35 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 1244 | 225 | 0 | 17 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0 | 1207 | 0 | 0 |  | 6649 | 5350 | 11999 | 4295 | 903 | 2118 | 0 | 1198 | 2641 | 99 | 359 | 230 | 144 | 0 | 12 | 955.955 | 79.49
5:00 | 0 | 0 | 190 | 180 | 0 | 12 | 0 | 397 | 336 |  | 0 | 450 | 0 | 41 | 17 | 15 | 337 | 0 | 151 | 33 | 25 | 48 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 33 | 31 | 8 | 0 | 69 | 30 | 117 | 0 | 8 | 227 | 0 | 0 | 0 |  | 6 | 25 | 50 | 80 | 0 | 6 | 12 | 40 | 0 | 0 | 0 | 280 | 220 | 164 | 8 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 43 | 19 | 11 | 33 | 20 | 142 | 70 | 0 | 16 | 0 | 43 | 30 | 47 | 48 | 112 | 0 | 25 | 78 | 0 | 112 | 17 | 0 | 10 | 280 | 24 | 11 | 0 | 47 | 0 | 0 | 68 | 0 | 35 | 0 | 25 | 34 | 6 | 402 | 19 | 35 | 17 | 0 | 69 | 17 | 55 | 17 | 9 | 25 | 355 | 44 | 0 | 17 | 34 | 0 | 17 | 0 | 17 | 17 | 230 | 17 | 0 | 0 | 27 | 0 |  | 904 | 0 | 155 | 0 | 16 | 115 | 0 | 0 | 10 | 36 | 0 | 130 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 176 | 0 | 414 | 35 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 1244 | 224 | 0 | 17 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0 | 1206 | 0 | 0 |  | 6655 | 5326 | 11981 | 4265 | 904 | 2127 | 0 | 1207 | 2640 | 99 | 359 | 211 | 142 | 0 | 27 | 782.145 | 79.51
6:00 | 0 | 0 | 150 | 180 | 0 | 12 | 0 | 392 | 301 |  | 0 | 360 | 0 | 42 | 17 | 15 | 335 | 0 | 121 | 33 | 25 | 48 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 13 | 33 | 32 | 8 | 0 | 70 | 30 | 118 | 0 | 8 | 220 | 0 | 0 | 0 |  | 6 | 25 | 50 | 80 | 0 | 6 | 12 | 30 | 0 | 0 | 0 | 280 | 220 | 164 | 8 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 43 | 19 | 11 | 33 | 20 | 126 | 70 | 0 | 16 | 0 | 43 | 30 | 47 | 48 | 80 | 0 | 25 | 78 | 0 | 112 | 17 | 0 | 10 | 275 | 24 | 11 | 0 | 47 | 0 | 0 | 68 | 0 | 35 | 0 | 25 | 34 | 6 | 318 | 19 | 35 | 17 | 0 | 69 | 17 | 55 | 17 | 9 | 25 | 355 | 52 | 1 | 17 | 34 | 0 | 17 | 1 | 17 | 17 | 230 | 17 | 0 | 0 | 27 | 0 |  | 905 | 0 | 135 | 0 | 16 | 115 | 0 | 0 | 10 | 36 | 0 | 100 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 176 | 0 | 360 | 35 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 1120 | 185 | 0 | 17 | 0 | 2 | 0 | 104 | 0 | 0 | 1 | 0 | 1216 | 2 | 0 |  | 6307 | 5071 | 11378 | 4042 | 905 | 1858 | 0 | 1217 | 2526 | 100 | 359 | 211 | 126 | 7 | 27 | 641.76 | 79.53
7:00 | 0 | 0 | 140 | 180 | 0 | 12 | 0 | 352 | 302 |  | 0 | 360 | 0 | 41 | 17 | 15 | 335 | 0 | 121 | 33 | 8 | 48 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 33 | 32 | 8 | 0 | 71 | 30 | 120 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 25 | 33 | 70 | 0 | 6 | 12 | 42 | 0 | 0 | 0 | 360 | 220 | 147 | 8 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 43 | 19 | 8 | 33 | 20 | 64 | 33 | 0 | 17 | 0 | 43 | 30 | 47 | 47 | 80 | 0 | 25 | 75 | 0 | 75 | 17 | 0 | 10 | 280 | 24 | 11 | 0 | 47 | 0 | 0 | 68 | 0 | 35 | 0 | 25 | 34 | 6 | 319 | 19 | 35 | 17 | 0 | 69 | 17 | 62 | 17 | 9 | 25 | 355 | 47 | 2 | 17 | 34 | 0 | 17 | 4 | 17 | 17 | 230 | 17 | 0 | 0 | 30 | 0 |  | 905 | 0 | 95 | 0 | 16 | 115 | 0 | 0 | 10 | 36 | 0 | 100 | 14 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 160 | 0 | 320 | 35 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 1100 | 185 | 0 | 17 | 0 | 12 | 0 | 105 | 0 | 0 | 3 | 0 | 1198 | 34 | 0 |  | 6165 | 4975 | 11140 | 3939 | 905 | 1825 | 0 | 1179 | 2488 | 101 | 360 | 194 | 64 | 55 | 30 | 391.55 | 79.55
8:00 | 0 | 0 | 140 | 180 | 0 | 12 | 0 | 352 | 302 |  | 0 | 360 | 0 | 16 | 17 | 15 | 334 | 0 | 121 | 9 | 8 | 48 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 33 | 32 | 8 | 0 | 72 | 30 | 113 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 25 | 34 | 70 | 0 | 6 | 12 | 30 | 0 | 0 | 0 | 280 | 220 | 151 | 8 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 43 | 19 | 8 | 33 | 20 | 108 | 35 | 0 | 17 | 0 | 43 | 30 | 44 | 47 | 80 | 0 | 25 | 75 | 0 | 25 | 17 | 0 | 10 | 300 | 24 | 11 | 0 | 15 | 0 | 0 | 68 | 0 | 35 | 1 | 25 | 34 | 5 | 317 | 19 | 35 | 17 | 0 | 69 | 17 | 55 | 17 | 9 | 25 | 355 | 34 | 8 | 17 | 34 | 0 | 17 | 7 | 18 | 17 | 230 | 17 | 0 | 0 | 18 | 0 |  | 905 | 0 | 75 | 0 | 32 | 115 | 0 | 0 | 10 | 22 | 0 | 100 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 160 | 0 | 320 | 35 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 1100 | 185 | 0 | 17 | 1 | 19 | 0 | 105 | 0 | 0 | 7 | 0 | 1199 | 68 | 0 |  | 5956 | 5000 | 10956 | 3785 | 905 | 1826 | 0 | 1071 | 2489 | 102 | 360 | 181 | 108 | 111 | 18 | 328.52 | 79.57
9:00 | 0 | 0 | 140 | 180 | 0 | 12 | 0 | 351 | 302 |  | 0 | 360 | 0 | 7 | 17 | 15 | 336 | 0 | 119 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 33 | 30 | 8 | 0 | 75 | 30 | 116 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 25 | 34 | 70 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 280 | 220 | 161 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 0 | 19 | 8 | 33 | 20 | 94 | 34 | 0 | 17 | 1 | 43 | 30 | 44 | 47 | 80 | 0 | 30 | 75 | 0 | 25 | 17 | 0 | 9 | 290 | 24 | 11 | 0 | 15 | 0 | 0 | 68 | 0 | 35 | 2 | 25 | 34 | 6 | 317 | 19 | 35 | 17 | 0 | 69 | 17 | 51 | 7 | 8 | 25 | 355 | 35 | 13 | 17 | 34 | 0 | 17 | 0 | 18 | 17 | 230 | 17 | 0 | 0 | 19 | 0 |  | 905 | 0 | 75 | 0 | 0 | 115 | 0 | 0 | 10 | 22 | 0 | 100 | 12 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 160 | 0 | 320 | 35 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 1100 | 185 | 0 | 17 | 4 | 17 | 0 | 105 | 0 | 0 | 11 | 0 | 1153 | 155 | 0 |  | 5822 | 5016 | 10838 | 3787 | 905 | 1795 | 0 | 946 | 2443 | 105 | 360 | 181 | 94 | 203 | 19 | 250.21 | 79.59
10:00 | 0 | 0 | 140 | 180 | 0 | 12 | 0 | 352 | 302 |  | 0 | 360 | 0 | 0 | 17 | 15 | 280 | 0 | 125 | 9 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 33 | 30 | 8 | 0 | 75 | 30 | 120 | 0 | 8 | 221 | 0 | 0 | 0 |  | 6 | 25 | 34 | 12 | 0 | 0 | 10 | 16 | 0 | 0 | 0 | 280 | 220 | 169 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 0 | 19 | 6 | 33 | 20 | 104 | 35 | 0 | 17 | 1 | 43 | 20 | 44 | 45 | 80 | 0 | 28 | 75 | 0 | 22 | 17 | 0 | 9 | 300 | 24 | 11 | 0 | 15 | 0 | 0 | 68 | 0 | 35 | 6 | 25 | 59 | 6 | 319 | 19 | 35 | 17 | 0 | 69 | 17 | 55 | 0 | 9 | 25 | 355 | 35 | 48 | 17 | 34 | 0 | 17 | 12 | 24 | 17 | 230 | 17 | 0 | 0 | 20 | 15 |  | 906 | 0 | 155 | 0 | 0 | 115 | 0 | 0 | 10 | 22 | 0 | 100 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 160 | 0 | 320 | 0 | 0 | 35 | 0 | 28 | 0 | 1 | 35 | 1100 | 185 | 0 | 0 | 4 | 2 | 0 | 105 | 0 | 0 | 11 | 0 | 1154 | 118 | 0 |  | 5843 | 4936 | 10779 | 3823 | 906 | 1805 | 0 | 787 | 2469 | 105 | 360 | 197 | 104 | 203 | 20 | 122.24 | 79.61
11:00 | 0 | 0 | 140 | 180 | 0 | 12 | 0 | 352 | 302 |  | 0 | 360 | 0 | 0 | 17 | 15 | 280 | 0 | 121 | 9 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 10 | 19 | 22 | 33 | 16 | 8 | 0 | 75 | 30 | 117 | 0 | 8 | 225 | 0 | 0 | 0 |  | 6 | 25 | 34 | 12 | 0 | 0 | 12 | 16 | 0 | 0 | 0 | 280 | 220 | 171 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 0 | 19 | 6 | 31 | 20 | 114 | 34 | 0 | 17 | 2 | 43 | 20 | 45 | 44 | 80 | 0 | 25 | 78 | 0 | 64 | 17 | 0 | 9 | 300 | 16 | 8 | 0 | 15 | 0 | 0 | 68 | 0 | 35 | 4 | 25 | 70 | 6 | 316 | 19 | 35 | 17 | 1 | 15 | 17 | 55 | 0 | 9 | 12 | 355 | 40 | 30 | 17 | 34 | 0 | 17 | 0 | 61 | 17 | 230 | 17 | 0 | 0 | 18 | 85 |  | 906 | 0 | 180 | 0 | 0 | 115 | 0 | 0 | 10 | 0 | 0 | 80 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 160 | 0 | 320 | 0 | 0 | 35 | 0 | 28 | 0 | 1 | 35 | 1220 | 185 | 0 | 0 | 3 | 21 | 0 | 105 | 0 | 0 | 19 | 0 | 1177 | 202 | 0 |  | 5916 | 5168 | 11084 | 3847 | 906 | 1812 | 0 | 782 | 2682 | 105 | 360 | 175 | 114 | 283 | 18 | 24.83 | 79.64
12:00 | 0 | 0 | 140 | 180 | 0 | 12 | 0 | 357 | 332 |  | 0 | 420 | 0 | 0 | 17 | 15 | 328 | 0 | 123 | 9 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 10 | 19 | 22 | 33 | 16 | 8 | 0 | 76 | 30 | 116 | 0 | 8 | 224 | 0 | 0 | 0 |  | 6 | 25 | 34 | 12 | 0 | 0 | 12 | 16 | 0 | 0 | 0 | 275 | 240 | 168 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 0 | 19 | 6 | 33 | 20 | 132 | 33 | 0 | 17 | 2 | 43 | 20 | 47 | 46 | 112 | 0 | 25 | 78 | 0 | 65 | 17 | 0 | 10 | 295 | 16 | 8 | 0 | 15 | 0 | 0 | 68 | 0 | 35 | 11 | 25 | 70 | 5 | 366 | 19 | 35 | 17 | 1 | 66 | 17 | 42 | 0 | 9 | 32 | 355 | 25 | 11 | 54 | 34 | 0 | 17 | 10 | 46 | 17 | 230 | 43 | 0 | 0 | 22 | 150 |  | 905 | 0 | 100 | 0 | 5 | 115 | 0 | 0 | 0 | 0 | 8 | 132 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 170 | 0 | 320 | 0 | 0 | 35 | 5 | 34 | 0 | 1 | 35 | 1244 | 225 | 0 | 0 | 1 | 36 | 0 | 105 | 0 | 0 | 32 | 0 | 1211 | 205 | 0 |  | 6334 | 5292 | 11626 | 3946 | 905 | 1976 | 0 | 873 | 2805 | 106 | 360 | 191 | 132 | 310 | 22 | 60.165 | 79.67
13:00 | 0 | 0 | 180 | 180 | 0 | 12 | 0 | 400 | 332 |  | 0 | 420 | 0 | 0 | 17 | 15 | 325 | 0 | 97 | 20 | 25 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 10 | 19 | 15 | 33 | 26 | 8 | 0 | 76 | 30 | 117 | 0 | 8 | 223 | 0 | 0 | 0 |  | 6 | 25 | 50 | 70 | 0 | 6 | 12 | 10 | 0 | 0 | 0 | 275 | 240 | 165 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 26 | 0 | 20 | 11 | 33 | 20 | 132 | 33 | 0 | 17 | 2 | 43 | 22 | 46 | 47 | 112 | 0 | 25 | 78 | 0 | 73 | 17 | 0 | 10 | 290 | 16 | 8 | 0 | 15 | 0 | 0 | 68 | 0 | 35 | 18 | 25 | 68 | 6 | 346 | 19 | 35 | 17 | 1 | 68 | 17 | 55 | 0 | 26 | 38 | 355 | 53 | 35 | 54 | 34 | 0 | 17 | 20 | 70 | 22 | 230 | 54 | 0 | 0 | 19 | 150 |  | 905 | 0 | 60 | 0 | 32 | 115 | 0 | 0 | 0 | 0 | 8 | 133 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 13 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 191 | 0 | 414 | 5 | 0 | 35 | 15 | 28 | 0 | 2 | 35 | 1244 | 220 | 0 | 17 | 1 | 38 | 35 | 105 | 0 | 0 | 21 | 0 | 1164 | 206 | 0 |  | 6674 | 5452 | 12126 | 3978 | 905 | 2056 | 0 | 1236 | 2758 | 106 | 360 | 232 | 132 | 344 | 19 | 89.77 | 79.7
14:00 | 0 | 0 | 140 | 180 | 0 | 12 | 0 | 343 | 245 |  | 0 | 360 | 0 | 0 | 17 | 15 | 250 | 0 | 97 | 40 | 25 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 10 | 19 | 7 | 33 | 30 | 8 | 0 | 76 | 30 | 110 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 25 | 50 | 70 | 0 | 6 | 12 | 15 | 0 | 0 | 0 | 280 | 240 | 150 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 0 | 19 | 11 | 33 | 20 | 136 | 33 | 0 | 17 | 0 | 43 | 40 | 47 | 44 | 80 | 0 | 25 | 78 | 0 | 88 | 17 | 0 | 10 | 275 | 16 | 8 | 0 | 15 | 0 | 0 | 68 | 0 | 35 | 9 | 25 | 68 | 6 | 346 | 19 | 35 | 17 | 0 | 68 | 17 | 55 | 0 | 27 | 38 | 320 | 53 | 38 | 54 | 34 | 0 | 17 | 16 | 72 | 17 | 230 | 54 | 0 | 0 | 24 | 150 |  | 906 | 0 | 50 | 0 | 32 | 115 | 0 | 0 | 0 | 0 | 0 | 80 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 28 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 140 | 0 | 320 | 11 | 0 | 35 | 15 | 34 | 0 | 3 | 35 | 1120 | 185 | 0 | 17 | 3 | 40 | 36 | 105 | 0 | 0 | 13 | 0 | 1167 | 81 | 0 |  | 6311 | 4965 | 11276 | 3669 | 906 | 1736 | 0 | 1253 | 2637 | 106 | 360 | 246 | 136 | 203 | 24 | 70.67 | 79.64
15:00 | 0 | 0 | 120 | 180 | 0 | 12 | 0 | 321 | 250 |  | 0 | 300 | 0 | 0 | 17 | 15 | 240 | 0 | 97 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 10 | 19 | 7 | 25 | 30 | 8 | 0 | 70 | 30 | 115 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 25 | 50 | 25 | 2 | 6 | 12 | 12 | 0 | 0 | 0 | 270 | 230 | 153 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 0 | 19 | 11 | 33 | 8 | 138 | 34 | 0 | 17 | 1 | 43 | 40 | 47 | 47 | 80 | 0 | 30 | 78 | 0 | 90 | 17 | 0 | 10 | 280 | 16 | 8 | 0 | 15 | 0 | 0 | 68 | 0 | 35 | 4 | 25 | 68 | 5 | 331 | 19 | 35 | 17 | 1 | 69 | 17 | 55 | 0 | 28 | 38 | 320 | 53 | 15 | 54 | 34 | 0 | 17 | 7 | 72 | 17 | 220 | 17 | 0 | 0 | 21 | 150 |  | 900 | 0 | 75 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 80 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 140 | 0 | 240 | 20 | 0 | 35 | 0 | 34 | 0 | 3 | 55 | 1060 | 180 | 0 | 17 | 5 | 46 | 36 | 104 | 0 | 0 | 8 | 0 | 1177 | 165 | 0 |  | 5971 | 4889 | 10860 | 3590 | 900 | 1600 | 0 | 1104 | 2582 | 100 | 359 | 211 | 138 | 255 | 21 | 57.3 | 79.78
16:00 | 0 | 0 | 120 | 180 | 0 | 12 | 0 | 322 | 250 |  | 0 | 300 | 0 | 0 | 17 | 15 | 240 | 0 | 97 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 10 | 19 | 14 | 25 | 30 | 8 | 0 | 67 | 30 | 116 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 25 | 47 | 12 | 10 | 6 | 11 | 4 | 0 | 0 | 0 | 270 | 230 | 153 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 0 | 20 | 11 | 33 | 8 | 126 | 34 | 0 | 17 | 0 | 43 | 40 | 47 | 49 | 80 | 0 | 30 | 81 | 0 | 95 | 17 | 0 | 10 | 290 | 16 | 8 | 0 | 15 | 0 | 0 | 68 | 0 | 34 | 4 | 25 | 68 | 6 | 339 | 19 | 35 | 17 | 0 | 15 | 17 | 55 | 0 | 29 | 12 | 320 | 35 | 4 | 17 | 34 | 0 | 17 | 5 | 72 | 0 | 220 | 0 | 0 | 0 | 15 | 150 |  | 900 | 0 | 105 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 80 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 140 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 55 | 1060 | 180 | 0 | 0 | 1 | 18 | 0 | 105 | 0 | 0 | 0 | 0 | 1170 | 65 | 0 |  | 5788 | 4600 | 10388 | 3642 | 900 | 1607 | 0 | 806 | 2575 | 97 | 360 | 161 | 126 | 99 | 15 | 0 | 79.82
17:00 | 0 | 0 | 120 | 180 | 0 | 12 | 0 | 322 | 250 |  | 0 | 300 | 0 | 0 | 17 | 15 | 240 | 0 | 95 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 10 | 19 | 14 | 25 | 16 | 8 | 0 | 67 | 30 | 117 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 25 | 48 | 12 | 2 | 6 | 11 | 5 | 0 | 0 | 0 | 270 | 230 | 156 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 0 | 20 | 11 | 33 | 21 | 102 | 35 | 0 | 17 | 0 | 43 | 40 | 49 | 45 | 112 | 0 | 30 | 86 | 0 | 105 | 17 | 0 | 10 | 300 | 16 | 0 | 0 | 15 | 0 | 0 | 68 | 0 | 35 | 2 | 35 | 68 | 6 | 332 | 19 | 35 | 17 | 1 | 15 | 17 | 17 | 0 | 28 | 12 | 320 | 17 | 7 | 17 | 34 | 0 | 17 | 5 | 70 | 0 | 220 | 0 | 0 | 0 | 17 | 150 |  | 901 | 0 | 105 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 80 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 140 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 55 | 1060 | 180 | 0 | 0 | 1 | 9 | 0 | 104 | 0 | 0 | 1 | 0 | 1162 | 10 | 0 |  | 5755 | 4512 | 10267 | 3638 | 901 | 1651 | 0 | 750 | 2552 | 97 | 359 | 162 | 102 | 38 | 17 | 0 | 79.86
18:00 | 0 | 0 | 100 | 180 | 0 | 12 | 0 | 322 | 250 |  | 0 | 300 | 0 | 0 | 17 | 15 | 240 | 0 | 97 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 10 | 19 | 14 | 25 | 30 | 8 | 0 | 69 | 30 | 115 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 41 | 47 | 12 | 25 | 6 | 11 | 27 | 0 | 0 | 0 | 270 | 230 | 153 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 29 | 0 | 16 | 11 | 33 | 21 | 120 | 35 | 0 | 17 | 0 | 43 | 40 | 50 | 45 | 80 | 0 | 20 | 86 | 0 | 106 | 17 | 0 | 10 | 290 | 16 | 8 | 0 | 15 | 0 | 0 | 78 | 0 | 55 | 0 | 35 | 69 | 6 | 332 | 19 | 35 | 17 | 2 | 15 | 17 | 17 | 0 | 29 | 12 | 320 | 17 | 2 | 17 | 31 | 0 | 17 | 1 | 71 | 0 | 220 | 0 | 0 | 0 | 19 | 150 |  | 900 | 0 | 140 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 80 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 140 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 55 | 960 | 180 | 0 | 0 | 0 | 4 | 0 | 104 | 0 | 0 | 0 | 0 | 1161 | 7 | 0 |  | 5807 | 4423 | 10230 | 3660 | 900 | 1621 | 0 | 803 | 2451 | 99 | 359 | 181 | 120 | 17 | 19 | 0 | 79.91
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 118 | 180 | 0 | 12 | 0 | 343 | 336 |  | 0 | 420 | 0 | 2 | 17 | 15 | 330 | 0 | 98 | 10 | 50 | 130 | 19 | 0 | 0 | 0 | 35 | 35 | 35 | 10 | 19 | 14 | 25 | 30 | 25 | 0 | 71 | 30 | 115 | 0 | 3 | 222 | 0 | 0 | 0 |  | 6 | 50 | 49 | 57 | 35 | 6 | 11 | 35 | 0 | 0 | 0 | 270 | 230 | 155 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 18 | 0 | 20 | 11 | 33 | 21 | 154 | 53 | 0 | 17 | 0 | 43 | 40 | 50 | 46 | 80 | 0 | 20 | 86 | 0 | 121 | 17 | 0 | 10 | 300 | 24 | 8 | 0 | 18 | 0 | 0 | 86 | 0 | 112 | 0 | 86 | 74 | 28 | 397 | 85 | 105 | 17 | 0 | 190 | 17 | 20 | 34 | 43 | 74 | 355 | 53 | 0 | 34 | 34 | 0 | 17 | 0 | 79 | 3 | 220 | 100 | 0 | 0 | 11 | 150 |  | 900 | 0 | 165 | 0 | 20 | 115 | 0 | 0 | 27 | 0 | 8 | 132 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 8 | 28 | 8 | 30 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 140 | 0 | 230 | 10 | 0 | 17 | 62 | 57 | 0 | 0 | 55 | 1000 | 180 | 0 | 4 | 0 | 0 | 72 | 105 | 0 | 0 | 0 | 0 | 1210 | 0 | 0 |  | 7310 | 5024 | 12334 | 4015 | 900 | 1854 | 0 | 1896 | 2560 | 101 | 360 | 483 | 154 | 0 | 11 | 9.55 | 80.06
19:30 | 0 | 0 | 120 | 180 | 0 | 12 | 0 | 357 | 265 |  | 0 | 340 | 0 | 24 | 17 | 15 | 290 | 0 | 99 | 30 | 92 | 130 | 55 | 0 | 0 | 0 | 35 | 35 | 35 | 10 | 19 | 20 | 25 | 30 | 25 | 0 | 73 | 30 | 115 | 0 | 20 | 223 | 0 | 0 | 0 |  | 6 | 50 | 49 | 57 | 37 | 6 | 11 | 37 | 0 | 0 | 0 | 270 | 230 | 156 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 24 | 8 | 19 | 11 | 33 | 21 | 154 | 67 | 0 | 17 | 0 | 43 | 40 | 50 | 46 | 80 | 0 | 20 | 86 | 0 | 121 | 17 | 0 | 10 | 270 | 24 | 8 | 0 | 48 | 0 | 0 | 87 | 0 | 116 | 0 | 86 | 103 | 65 | 352 | 85 | 105 | 17 | 0 | 176 | 17 | 20 | 34 | 58 | 88 | 355 | 71 | 0 | 108 | 34 | 0 | 17 | 0 | 115 | 12 | 220 | 142 | 0 | 0 | 12 | 150 |  | 900 | 0 | 215 | 0 | 27 | 115 | 0 | 0 | 34 | 0 | 8 | 132 | 28 | 20 | 0 | 0 | 0 | 0 | 5 | 88 | 0 | 16 | 29 | 8 | 30 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 140 | 0 | 230 | 20 | 0 | 50 | 51 | 71 | 0 | 0 | 55 | 1200 | 180 | 0 | 150 | 0 | 0 | 72 | 106 | 0 | 0 | 0 | 0 | 1210 | 0 | 0 |  | 7535 | 5538 | 13073 | 4018 | 900 | 1677 | 0 | 2507 | 2760 | 103 | 361 | 581 | 154 | 0 | 12 | 9.55 | 0
20:00 | 0 | 0 | 160 | 180 | 0 | 12 | 0 | 371 | 300 |  | 0 | 340 | 0 | 18 | 17 | 15 | 290 | 0 | 188 | 55 | 58 | 130 | 51 | 0 | 0 | 0 | 35 | 35 | 35 | 10 | 19 | 18 | 25 | 30 | 25 | 0 | 74 | 30 | 120 | 0 | 22 | 221 | 0 | 0 | 0 |  | 6 | 50 | 48 | 68 | 36 | 6 | 11 | 37 | 0 | 0 | 0 | 270 | 230 | 173 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 8 | 19 | 11 | 33 | 21 | 152 | 92 | 0 | 17 | 0 | 43 | 40 | 50 | 46 | 80 | 0 | 25 | 86 | 0 | 128 | 17 | 0 | 10 | 275 | 24 | 8 | 0 | 30 | 0 | 0 | 88 | 0 | 115 | 0 | 86 | 100 | 62 | 400 | 85 | 105 | 17 | 0 | 153 | 17 | 53 | 34 | 56 | 88 | 355 | 70 | 0 | 72 | 34 | 0 | 17 | 0 | 114 | 24 | 220 | 17 | 0 | 0 | 11 | 150 |  | 851 | 0 | 255 | 0 | 16 | 115 | 0 | 0 | 4 | 0 | 8 | 132 | 28 | 18 | 0 | 0 | 0 | 0 | 5 | 91 | 0 | 8 | 30 | 8 | 30 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 140 | 0 | 230 | 21 | 0 | 50 | 15 | 70 | 0 | 0 | 55 | 1220 | 180 | 0 | 62 | 0 | 0 | 75 | 104 | 0 | 0 | 0 | 0 | 1209 | 0 | 0 |  | 7645 | 5378 | 13023 | 4304 | 851 | 1717 | 0 | 2316 | 2779 | 104 | 359 | 430 | 152 | 0 | 11 | 20.055 | 80.01
21:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 393 | 342 |  | 0 | 450 | 0 | 9 | 12 | 15 | 331 | 0 | 197 | 32 | 25 | 130 | 57 | 0 | 0 | 0 | 35 | 35 | 35 | 20 | 19 | 19 | 25 | 30 | 25 | 0 | 74 | 30 | 115 | 0 | 25 | 222 | 0 | 0 | 0 |  | 6 | 50 | 49 | 25 | 37 | 6 | 11 | 38 | 0 | 0 | 0 | 270 | 230 | 185 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 8 | 19 | 11 | 33 | 21 | 154 | 83 | 0 | 17 | 0 | 43 | 40 | 50 | 46 | 112 | 0 | 25 | 86 | 0 | 130 | 17 | 0 | 10 | 295 | 24 | 8 | 0 | 30 | 0 | 0 | 88 | 0 | 116 | 0 | 86 | 100 | 60 | 403 | 85 | 105 | 17 | 0 | 100 | 17 | 54 | 34 | 59 | 25 | 355 | 72 | 0 | 54 | 34 | 0 | 17 | 0 | 112 | 30 | 220 | 17 | 0 | 0 | 7 | 150 |  | 851 | 0 | 270 | 0 | 16 | 115 | 0 | 0 | 0 | 0 | 8 | 132 | 30 | 16 | 0 | 0 | 0 | 0 | 16 | 92 | 0 | 8 | 30 | 8 | 30 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 158 | 0 | 414 | 35 | 0 | 50 | 15 | 70 | 0 | 0 | 55 | 1244 | 220 | 0 | 17 | 0 | 0 | 75 | 105 | 0 | 0 | 0 | 0 | 1209 | 0 | 0 |  | 7758 | 5637 | 13395 | 4474 | 851 | 2148 | 0 | 2055 | 2803 | 104 | 360 | 439 | 154 | 0 | 7 | 0 | 80.06
22:00 | 0 | 0 | 208 | 180 | 0 | 12 | 0 | 396 | 332 |  | 0 | 450 | 0 | 9 | 12 | 15 | 328 | 0 | 195 | 24 | 25 | 130 | 40 | 0 | 0 | 0 | 35 | 35 | 35 | 20 | 19 | 21 | 25 | 30 | 25 | 0 | 74 | 30 | 115 | 0 | 25 | 223 | 0 | 0 | 0 |  | 6 | 50 | 50 | 80 | 37 | 6 | 11 | 32 | 0 | 0 | 0 | 270 | 230 | 193 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 8 | 19 | 11 | 33 | 21 | 152 | 83 | 0 | 17 | 0 | 43 | 40 | 50 | 46 | 112 | 0 | 25 | 84 | 0 | 130 | 17 | 0 | 10 | 300 | 24 | 8 | 0 | 30 | 0 | 0 | 88 | 0 | 118 | 0 | 86 | 104 | 60 | 403 | 84 | 105 | 17 | 0 | 122 | 17 | 54 | 34 | 57 | 60 | 355 | 72 | 0 | 74 | 34 | 0 | 17 | 0 | 110 | 17 | 220 | 40 | 0 | 0 | 4 | 150 |  | 795 | 0 | 255 | 0 | 16 | 115 | 0 | 0 | 0 | 0 | 8 | 132 | 31 | 16 | 0 | 0 | 0 | 0 | 26 | 92 | 0 | 8 | 28 | 8 | 30 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 160 | 0 | 414 | 35 | 0 | 50 | 15 | 92 | 0 | 0 | 55 | 1244 | 220 | 0 | 17 | 0 | 0 | 84 | 104 | 0 | 0 | 0 | 0 | 1211 | 0 | 0 |  | 7866 | 5609 | 13475 | 4468 | 795 | 2136 | 0 | 2181 | 2805 | 104 | 359 | 471 | 152 | 0 | 4 | 24.83 | 80.11
23:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 395 | 343 |  | 0 | 450 | 0 | 16 | 17 | 15 | 332 | 0 | 138 | 47 | 94 | 130 | 44 | 0 | 0 | 0 | 35 | 35 | 35 | 20 | 19 | 21 | 25 | 30 | 25 | 0 | 73 | 30 | 118 | 0 | 25 | 225 | 0 | 0 | 0 |  | 6 | 50 | 50 | 80 | 37 | 6 | 11 | 40 | 0 | 0 | 0 | 270 | 230 | 193 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 8 | 19 | 11 | 33 | 21 | 150 | 83 | 0 | 17 | 0 | 43 | 40 | 50 | 46 | 112 | 0 | 25 | 84 | 0 | 177 | 17 | 0 | 10 | 265 | 24 | 8 | 0 | 30 | 0 | 0 | 69 | 0 | 68 | 0 | 86 | 141 | 28 | 403 | 18 | 105 | 17 | 0 | 170 | 17 | 54 | 34 | 28 | 88 | 355 | 71 | 0 | 108 | 34 | 0 | 17 | 0 | 114 | 17 | 220 | 53 | 0 | 0 | 7 | 150 |  | 795 | 0 | 245 | 0 | 16 | 115 | 0 | 0 | 0 | 0 | 8 | 132 | 30 | 16 | 0 | 0 | 0 | 0 | 24 | 63 | 0 | 8 | 28 | 8 | 30 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 157 | 0 | 414 | 35 | 0 | 50 | 50 | 92 | 0 | 0 | 55 | 1244 | 223 | 0 | 17 | 0 | 0 | 113 | 104 | 0 | 0 | 0 | 0 | 1209 | 0 | 0 |  | 7925 | 5629 | 13554 | 4455 | 795 | 2122 | 0 | 2307 | 2803 | 103 | 359 | 453 | 150 | 0 | 7 | 91.68 | 80.16
24:00 | 0 | 0 | 210 | 180 | 0 | 13 | 0 | 403 | 341 |  | 0 | 450 | 0 | 47 | 17 | 15 | 331 | 0 | 139 | 50 | 102 | 130 | 44 | 0 | 0 | 0 | 35 | 0 | 35 | 20 | 19 | 21 | 25 | 30 | 8 | 0 | 77 | 30 | 117 | 0 | 8 | 225 | 0 | 0 | 0 |  | 6 | 50 | 50 | 80 | 0 | 6 | 11 | 42 | 0 | 0 | 0 | 270 | 230 | 199 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 9 | 19 | 11 | 33 | 20 | 154 | 84 | 0 | 17 | 0 | 43 | 40 | 50 | 48 | 112 | 0 | 25 | 84 | 0 | 110 | 17 | 0 | 10 | 310 | 24 | 8 | 0 | 35 | 0 | 0 | 68 | 0 | 43 | 0 | 25 | 156 | 6 | 403 | 18 | 35 | 17 | 0 | 170 | 17 | 55 | 34 | 9 | 25 | 355 | 72 | 0 | 108 | 34 | 0 | 17 | 0 | 78 | 17 | 220 | 53 | 0 | 0 | 14 | 150 |  | 891 | 0 | 225 | 0 | 50 | 115 | 0 | 0 | 0 | 0 | 8 | 132 | 31 | 16 | 0 | 0 | 0 | 0 | 24 | 14 | 0 | 8 | 28 | 8 | 30 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 173 | 0 | 414 | 35 | 0 | 35 | 15 | 91 | 0 | 0 | 55 | 1244 | 222 | 0 | 72 | 0 | 0 | 114 | 104 | 0 | 0 | 0 | 0 | 1206 | 0 | 0 |  | 7596 | 5708 | 13304 | 4397 | 891 | 2170 | 0 | 2008 | 2800 | 107 | 359 | 404 | 154 | 0 | 14 | 149.935 | 80.21
KWH | 0 | 0 | 3826500 | 4347000 | 0 | 593818 | 0 | 8947720 | 7360000 |  | 0 | 9356300 | 0 | 408000 | 368284 | 378968 | 7343903 | 0 | 3460000 | 543360 | 595296 | 1786560 | 674640 | 0 | 0 | 0 | 298800 | 413009 | 394362 | 184716 | 456000 | 424620 | 716600 | 661800 | 277920 | 0 | 177000 | 724000 | 2700000 | 0 | 205574 | 5465072 | 0 | 0 | 0 |  | 148800 | 787584 | 1087067 | 1232160 | 236160 | 171360 | 246576 | 570720 | 0 | 0 | 0 | 6995000 | 5596000 | 4021000 | 83636 | 0 | 0 | 0 | 0 | 1015236 | 0 | 594944 | 413544 | 450576 | 238140 | 819100 | 477540 | 3155520 | 1213440 | 0 | 384156 | 10400 | 1019000 | 863160 | 1147200 | 1111824 | 2329691 | 0 | 615360 | 1918080 | 0 | 1730230 | 397000 | 0 | 247860 | 7101000 | 507120 | 209248 | 0 | 757745 | 0 | 0 | 1716000 | 0 | 1244880 | 53730 | 929280 | 1622400 | 364654 | 8725000 | 700800 | 1171210 | 460000 | 4918 | 1861745 | 526068 | 1215230 | 484500 | 530880 | 760320 | 8316200 | 1151040 | 241190 | 914400 | 840545 | 0 | 442080 | 102445 | 1331520 | 389520 | 5615100 | 644000 | 0 | 0 | 429600 | 1600000 |  | 21518545 | 0 | 3968064 | 0 | 341760 | 2868778 | 0 | 0 | 138720 | 371200 | 50250 | 2625000 | 545011 | 299424 | 0 | 0 | 0 | 0 | 81709 | 379888 | 0 | 473969 | 224836 | 70440 | 166610 | 0 | 0 | 192204 | 0 | 0 | 4699400 | 0 | 0 | 0 | 0 | 0 | 3809473 | 0 | 0 | 4248700 | 0 | 8353600 | 530880 | 0 | 859680 | 390672 | 961075 | 0 | 14493 | 1090944 | 30050900 | 4904645 | 0 | 475200 | 30240 | 253440 | 566208 | 2339309 | 0 | 0 | 111426 | 0 | 28707273 | 1205720 | 0 |  | 157382254 | 127919686 | 285301940 | 98006845 | 21518545 | 46638621 | 0 | 32285556 | 65057573 | 901000 | 9017560 | 6263118 | 3155520 | 2028002 | 429600 | 0
Fuel Cost | 0 | 0 | 5586690 | 6477030 | 0 | 789777.94 | 0 | 9395106 | 7948800 |  | 0 | 10198367 | 0 | 4561440 | 4879763 | 5021326 | 8225171.36 | 0 | 6055000 | 7943923.2 | 8375814.72 | 28960137.6 | 6220180.8 | 0 | 0 | 0 | 3800736 | 5575621.5 | 5288394.42 | 138537 | 342000 | 0 | 0 | 0 | 4727419.2 | 0 | 47790 | 195480 | 5103000 | 0 | 3361134.9 | 5683674.88 | 0 | 0 | 0 |  | 1941840 | 13136901.12 | 18501880.34 | 16646481.6 | 2994508.8 | 1982635.2 | 313151.52 | 1900497.6 | 0 | 0 | 0 | 7764450 | 6099640 | 4664360 | 107890.44 | 0 | 0 | 0 | 0 | 1695444.12 | 0 | 10274682.88 | 5562166.8 | 617289.12 | 178605 | 1433425 | 358155 | 22656633.6 | 1322649.6 | 0 | 522452.16 | 165776 | 1396030 | 1139371.2 | 1996128 | 1923455.52 | 2679144.65 | 0 | 1193798.4 | 4373222.4 | 0 | 1747532.3 | 853550 | 0 | 490762.8 | 7101000 | 380340 | 159028.48 | 0 | 10343219.25 | 0 | 0 | 23131680 | 0 | 17241588 | 628103.7 | 9590169.6 | 22161984 | 4838958.58 | 8027000 | 8521728 | 16935696.6 | 5819000 | 0 | 21856886.3 | 5728880.52 | 12917894.9 | 6574665 | 6843043.2 | 8956569.6 | 7650904 | 14905968 | 3485195.5 | 11603736 | 9565402.1 | 0 | 5773564.8 | 1224217.75 | 19932854.4 | 5129978.4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 64555635 | 0 | 4444231.68 | 0 | 3557721.6 | 47334837 | 0 | 0 | 2498347.2 | 6681600 | 722092.5 | 2940000 | 1057321.34 | 3263721.6 | 0 | 0 | 0 | 0 | 1429090.41 | 5941448.32 | 0 | 7848926.64 | 3801976.76 | 960097.2 | 2810710.7 | 0 | 0 | 145498.428 | 0 | 0 | 24859826 | 0 | 0 | 0 | 0 | 0 | 66513398.58 | 0 | 0 | 4928492 | 0 | 8270064 | 7135027.2 | 0 | 10170014.4 | 5645210.4 | 12205652.5 | 0 | 160147.65 | 13244060.16 | 270758609 | 5002737.9 | 0 | 3516480 | 342014.4 | 2972851.2 | 8679968.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 570566083.37 | 604397810.408 | 1174963893.778 | 105286163.128 | 64555635 | 55534613.71 | 0 | 414205826.23 | 295618435 | 243270 | 113848235.58 | 94036775.33 | 22656633.6 | 8978306.2 | 0 | 0
Yesterday Day Peak | 0 | 0 | 140 | 180 | 0 | 12 | 0 | 357 | 332 |  | 0 | 420 | 0 | 0 | 17 | 15 | 328 | 0 | 123 | 9 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 10 | 19 | 22 | 33 | 16 | 8 | 0 | 76 | 30 | 116 | 0 | 8 | 224 | 0 | 0 | 0 |  | 6 | 25 | 34 | 12 | 0 | 0 | 12 | 16 | 0 | 0 | 0 | 275 | 240 | 168 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 0 | 19 | 6 | 33 | 20 | 132 | 33 | 0 | 17 | 2 | 43 | 20 | 47 | 46 | 112 | 0 | 25 | 78 | 0 | 65 | 17 | 0 | 10 | 295 | 16 | 8 | 0 | 15 | 0 | 0 | 68 | 0 | 35 | 11 | 25 | 70 | 5 | 366 | 19 | 35 | 17 | 1 | 66 | 17 | 42 | 0 | 9 | 32 | 355 | 25 | 11 | 54 | 34 | 0 | 17 | 10 | 46 | 17 | 230 | 43 | 0 | 0 | 22 | 150 |  | 905 | 0 | 100 | 0 | 5 | 115 | 0 | 0 | 0 | 0 | 8 | 132 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 170 | 0 | 320 | 0 | 0 | 35 | 5 | 34 | 0 | 1 | 35 | 1244 | 225 | 0 | 0 | 1 | 36 | 0 | 105 | 0 | 0 | 32 | 0 | 1211 | 205 | 0 |  | 11626 | DayPeak
Yesterday Evening Peak | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 393 | 342 | 0 | 0 | 450 | 0 | 9 | 12 | 15 | 331 | 0 | 197 | 32 | 25 | 130 | 57 | 0 | 0 | 0 | 35 | 35 | 35 | 20 | 19 | 19 | 25 | 30 | 25 | 0 | 74 | 30 | 115 | 0 | 25 | 222 | 0 | 0 | 0 | 0 | 6 | 50 | 49 | 25 | 37 | 6 | 11 | 38 | 0 | 0 | 0 | 270 | 230 | 185 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 8 | 19 | 11 | 33 | 21 | 154 | 83 | 0 | 17 | 0 | 43 | 40 | 50 | 46 | 112 | 0 | 25 | 86 | 0 | 130 | 17 | 0 | 10 | 295 | 24 | 8 | 0 | 30 | 0 | 0 | 88 | 0 | 116 | 0 | 86 | 100 | 60 | 403 | 85 | 105 | 17 | 0 | 100 | 17 | 54 | 34 | 59 | 25 | 355 | 72 | 0 | 54 | 34 | 0 | 17 | 0 | 112 | 30 | 220 | 17 | 0 | 0 | 7 | 150 |  | 851 | 0 | 270 | 0 | 16 | 115 | 0 | 0 | 0 | 0 | 8 | 132 | 30 | 16 | 0 | 0 | 0 | 0 | 16 | 92 | 0 | 8 | 30 | 8 | 30 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 158 | 0 | 414 | 35 | 0 | 50 | 15 | 70 | 0 | 0 | 55 | 1244 | 220 | 0 | 17 | 0 | 0 | 75 | 105 | 0 | 0 | 0 | 0 | 1209 | 0 | 0 |  | 13395 | EvPeak
Forecast for Evening | 0 | 0 | 180 | 180 | 0 | 12 | 0 | 393 | 340 | 0 | 0 | 450 | 0 | 50 | 50 | 15 | 330 | 0 | 190 | 55 | 102 | 130 | 60 | 0 | 0 | 0 | 35 | 35 | 35 | 20 | 19 | 22 | 25 | 30 | 25 | 0 | 74 | 30 | 120 | 0 | 25 | 225 |  | 0 | 0 | 0 | 6 | 50 | 50 | 80 | 37 | 45 | 12 | 25 | 0 | 0 | 0 | 270 | 230 | 180 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 42 | 22 | 11 | 33 | 21 | 160 | 85 | 0 | 17 | 0 | 43 | 40 | 50 | 48 | 112 | 0 | 30 | 86 | 0 | 130 | 17 | 0 | 10 | 300 | 24 | 8 | 0 | 96 | 100 | 0 | 88 | 0 | 116 | 0 | 85 | 150 | 60 | 400 | 85 | 105 | 17 | 0 | 300 | 17 | 55 | 17 | 60 | 88 | 355 | 72 | 0 | 108 | 34 | 0 | 17 |  | 115 | 30 | 230 | 144 |  | 0 | 22 | 0 |  | 910 | 0 | 250 |  | 66 | 120 | 0 | 0 | 40 | 70 | 8 | 132 | 30 | 64 | 0 | 0 | 0 | 0 | 30 | 92 | 0 | 42 | 30 | 8 | 30 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 |  | 0 | 220 | 0 | 0 | 160 | 0 | 414 | 35 | 0 | 50 | 85 | 92 | 0 | 0 | 55 | 1244 | 220 |  | 150 |  |  | 115 | 120 |  | 0 |  | 0 | 1200 |  | 0
Forecast for Day | 0 | 0 | 160 | 180 | 0 | 12 | 0 | 390 | 325 | 0 | 0 | 450 | 0 | 42 | 17 | 15 | 330 | 0 | 190 | 55 | 102 | 64 | 60 | 0 | 0 | 0 | 17 | 35 | 35 | 17 | 19 | 20 | 25 | 30 | 8 | 0 | 70 | 30 | 120 | 0 | 8 | 225 |  | 0 | 0 | 0 | 6 | 25 | 50 | 70 | 12 | 6 | 12 | 10 | 0 | 0 | 0 | 270 | 230 | 180 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 8 | 20 | 11 | 32 | 20 | 146 | 35 | 0 | 17 | 1.6 | 43 | 40 | 50 | 48 | 112 | 0 | 30 | 80 | 0 | 80 | 17 | 0 | 10 | 300 | 24 | 8 | 0 | 96 | 0 | 0 | 68 | 0 | 35 | 20 | 85 | 68 | 6 | 400 | 18 | 35 | 17 | 5 | 120 | 17 | 55 | 17 | 9 | 38 | 355 | 53 | 50 | 54 | 34 | 0 | 17 | 35 | 72 | 17 | 230 | 54 |  | 0 | 22 | 0 |  | 910 | 0 | 200 | 0 | 32 | 120 | 0 | 0 | 0 | 40 | 8 | 132 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 42 | 30 | 8 | 20 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 160 | 0 | 414 | 35 | 0 | 35 | 15 | 35 | 0 | 8 | 35 | 1244 | 220 |  | 17 | 6 | 100 | 35 | 120 |  | 0 | 30 | 0 | 1200 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 160 | 180 | 0 | 12 | 0 | 350 | 298 | 0 | 0 | 390 | 0 | 17 | 17 | 15 | 290 | 0 | 137 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 19 | 20 | 25 | 16 | 8 | 0 | 74 | 30 | 115 | 0 | 8 | 226 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 12 | 0 | 6 | 11 | 10 | 0 | 0 | 0 | 270 | 230 | 184 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 50 | 8 | 19 | 11 | 33 | 21 | 120 | 32 | 0 | 0 | 0 | 43 | 40 | 31 | 30 | 80 | 0 | 25 | 20 | 0 | 178 | 17 | 0 | 10 | 290 | 24 | 11 | 0 | 15 | 0 | 0 | 58 | 0 | 35 | 2 | 25 | 34 | 5 | 410 | 18 | 0 | 17 | 1 | 69 | 17 | 55 | 17 | 9 | 25 | 355 | 47 | 14 | 17 | 34 | 0 | 17 | 21 | 18 | 17 | 220 | 17 | 0 | 0 | 6 | 150 | 0 | 892 | 0 | 175 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 132 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 160 | 0 | 350 | 35 | 0 | 35 | 15 | 34 | 0 | 1 | 35 | 1040 | 180 | 0 | 17 | 0 | 18 | 0 | 105 | 0 | 0 | 12 | 0 | 1217 | 67 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
292.3904
| Minimum Generation |  | 10838 | 9:00
| Highest Generation |  | 13554 | 23:00
| Day Peak Generation |  | 11626 | 12:00
| Evening Peak Generation |  | 13395 | 21:00
| HVDC Max Flow |  | 906 | 10:00
| HVDC EvPeak Flow |  | 851 | 21:00
| Load factor L.F |  | 87.71% | [164 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-08-05
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-08-04 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 11626 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 11130
Evening Peak Generation : |  |  | 13395 | MW Hour : | 21:00 | Available Max Generation : |  | 14855
E.P. Demand (at gen end) : |  |  | 13395 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14500
Maximum Generation : |  |  | 13554 | MW Hour : | 23:00 | Reserve(Generation end) |  | 355
Total Gen. (MKWH) : |  |  | 285.3019 | System Load Factor : | 87.71% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 630 | MW at | 19:30 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-08-05
Actual : |  | 80.57 | Ft.(MSL) , | Rule curve : | 90.28 | Ft.( MSL )
Gas Consumed : |  | Total = | 1125.55 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 160820776.838
: |  |  | Coal : | 295618435 | Oil : | 622090837.14 | Total : | 1078530048.978
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4954.5545 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1363.7216 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1911.0082 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1661.6578 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1366.9193 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 1016.9903 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 569.6834 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 475.102 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 929.2083 |  |  | 0 | 0%
Total |  | 0 |  | 14248.8454 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar-9
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:04 | 08:39 | Halishahar 132/33kV S/S 403T(TR-1) LT Tripped showing Over Current relays Due to Due to 33 kv Baraka ckt-01 fault | [5 empty] | 2.5 MW load interrup.
08:04 | 08:39 | Halishahar 132/33kV S/S 413T(TR-2) LT Tripped showing Over Current relays Due to Due to 33 kv Baraka ckt-01 fault
09:04 | 11:05 | Satkhira 132/33kV S/S Transformer-2 (T-2) LT Scheduled S/D Due to Red hot maintenance | [5 empty] | 25 MW load interrup.
09:05 | 11:04 | Satkhira 132/33kV S/S Transformer-2 (T-2) HT Scheduled S/D Due to Red hot maintenance
09:15 |  | Matarbari coal power Unit-1 was sync.
09:37 | 17:47 | Gopalganj 400/132kV S/S ATR-03 LT Scheduled S/D Due to Fire fighting work
09:38 | 17:42 | Gopalganj 400/132kV S/S ATR-03 HT Scheduled S/D Due to Fire fighting work
10:01 | 12:35 | Ishurdi 132/33kV S/S 132/33 kV T-2 LT Scheduled S/D Due to station auxilari x-former maintenance work
10:01 | 12:35 | Ishurdi 132/33kV S/S 132/33 kV T-2 HT Scheduled S/D Due to station auxilari x-former maintenance work
| 10:12 | Agargaon 230/132kV S/S 230kV Transformer-1 ( 705T1) HT is restored.
| 10:14 | Agargaon 230/132kV S/S 230kV Transformer-1 ( 705T1) LT is restored.
10:19 |  | Sylhet CCPP 225 MW ST was sync.
| 10:37 | Faridpur 132/33kV S/S Transformer-2 HT is restored.
| 10:38 | Faridpur 132/33kV S/S Transformer-2 LT is restored.
12:00 |  | Day peak generation: 11627 MW.
12:48 |  | Siddhirganj GT: Unit-1 was shutdown due to hydraulic oil leakage. | [5 empty] | 105 MW generation interrup.
15:33 | 17:21 | Bogura 132/33kV S/S Transformer-1 LT Scheduled S/D Due to 33kv nesco work | [5 empty] | 45 MW load interrup.
15:33 | 17:21 | Bogura 132/33kV S/S Transformer-1 HT Scheduled S/D Due to 33kv nesco work
15:59 | 16:02 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing O/C, E/F relay 33 kv. C phase Inst. relays Due to due to PBS
33kv Chunarughat feeder trip showing E/F
16:09 | 17:39 | Cumilla(S) 132/33kV S/S TR-2 LT Scheduled S/D Due to PDB taken S/D for Work. | [5 empty] | 20 MW load interrup.
16:10 | 17:39 | Cumilla(S) 132/33kV S/S TR-2 HT Scheduled S/D Due to PDB taken S/D for Work.
| 17:42 | Gopalganj 400/132kV S/S ATR-03 HT is restored.
19:21 |  | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-2 Forced S/D from Bogura 230/132kV end Due to Transformer Overload.
19:56 |  | Siddhirganj GT-1 was sync.
21:00 |  | Evening Peak Gen. 13395 MW
01:17 |  | Bogura West 430/230 KV ATR-1 S/D
01:29 |  | Bogura West 430/230 KV ATR-1 Sync
05:40 | 07:04 | Sylhet 132/33kV S/S T1 LT Scheduled S/D Due to Red hot Maintenance
05:40 | 07:04 | Sylhet 132/33kV S/S T1 LT Scheduled S/D Due to Red hot Maintenance
05:41 | 07:03 | Sylhet 132/33kV S/S T1 HT Scheduled S/D Due to Red hot Maintenance CT to CB (33 KV R&Y Phase)
06:10 |  | Mymensingh 132/33kV S/S Transformer-2 (414T) LT Scheduled S/D Due to S/D due to Red hot maintenance work
for 33kV Gafagaon Feeders 33kV Bus DS(R-Ph) upper clamp
06:10 |  | Mymensingh 132/33kV S/S Transformer-2 (414T) HT Scheduled S/D Due to S/D due to Red hot maintenance work | [5 empty] | 85 MW load interrup.
for 33kV Gafagaon Feeders 33kV Bus DS(R-Ph) upper clamp.
06:51 |  | Tangail 132/33kV S/S Tr-4 LT Scheduled S/D Due to 33kv T2 bus red hot | [5 empty] | 10 MW load interrup.
06:51 |  | Tangail 132/33kV S/S Tr-4 HT Scheduled S/D Due to 33kv T2 bus red hot
06:51 |  | Chapainawabganj-Rahanpur 132kV Ckt-1 Scheduled S/D from Chapai 132/33kV end Due to Project work
06:57 |  | Tangail 132/33kV S/S Tr-2 HT Scheduled S/D Due to 33kv T2 bus red hot | [5 empty] | 40 MW load interrup.
06:57 |  | Tangail 132/33kV S/S Tr-2 LT Scheduled S/D Due to 33kv T2 bus red hot
07:00 |  | Minimum generation 11130 MW

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-08-04 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 210 | 3826500
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 593818 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 393 | 8947720 | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 342 | 7360000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9356300
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 9 | 408000 | Low demand.
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Under maint.
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 12 | 368284 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 378968 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 57 | 674640 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 20 | 184716
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 197 | 3460000
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 32 | 543360 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 331 | 7343903
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 25 | 595296 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 298800 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 130 | 1786560 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 413009 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 394362 | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 38 | 880620 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 716600
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 30 | 661800 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 277920 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 30 | 757745 | Low demand.
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Low demand.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 116 | 1244880 | Low demand.
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1171210
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 72 | 1151040 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 914400 | Low demand.
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 102445
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 30 | 389520 | Fuel shortage
| Dhaka area Total |  |  |  | 5722 | 3045 | 59549416
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2700000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 205574
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 53730
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 6 | 171360 | Low demand.
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 104 | 901000
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 222 | 5465072
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 460000 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 50 | 787584 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 49 | 1087067 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 25 | 1232160 | Low demand.
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 86 | 929280 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 11 | 246576 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 38 | 570720
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 37 | 236160 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 4918
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 100 | 1861745 | Low demand.
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 526068 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 54 | 1215230 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 760320 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 34 | 840545 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 17 | 644000 | Low demand.
| SS Power I |  | SS Power | 0 | 0 | 0 | 0 | Machine problem
| Cox's Bazar Wind |  | IPP | 66 | 0 | 7 | 429600 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 150 | 1600000 | On test.
| Chattogram area Total |  |  |  | 2545 | 1189 | 22928709
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 185 | 4021000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 270 | 6995000 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 230 | 5596000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 220 | 5615100 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 0 | 0 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 83636 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 1015236 | Engine problem
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 60 | 364654 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 25 | 594944 | Machine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 100 | 1622400 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 450576
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 238140
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 154 | 3155520
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 819100
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 413544 | Low demand.
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 21 | 477540 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 484500 | Low demand.
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 59 | 530880 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 442080 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 112 | 1331520
| Cumilla Area Total |  |  |  | 3096 | 1601 | 34251370
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 83 | 1213440 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 384156 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10400
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 88 | 1716000 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 85 | 700800 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 241190
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 148800 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 279 | 4414786
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1019000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 863160 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2329691 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1147200
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 46 | 1111824
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 209248
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 25 | 615360 | GT-9 Under maint.
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1918080
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 130 | 1730230 | ST Under maint.
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 397000 | Machine problem
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 507120
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7101000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 403 | 8725000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 247860
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 355 | 8316200
| Sylhet Area Total |  |  |  | 2427 | 1644 | 36237973
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 851 | 21518545
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 341760 | Low demand.
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 138720 | reserve.
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 115 | 2868778 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 371200 | reserve.
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 270 | 3968064 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 50250 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 530880 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 390672 | Low demand.
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 253440
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 220 | 105 | 2339309 | Fuel shortage
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | Coal shortage.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 3121 | 1415 | 32771618
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 299424 | Low demand.
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 30 | 545011 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 132 | 2625000 | ST Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 30050900
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4904645
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 475200 | Low demand.
| Barisal 307 MW |  | IPP | 307*1 | 307 | 0 | 0 | Coal shortage.
| Barisal Area Total |  |  |  | 2265 | 1659 | 38900180
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 16 | 81709 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Engine problem
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 473969 | Low demand.
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 224836 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Under maint.
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 140 | 3809473
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 158 | 4248700 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 8353600
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 166610 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 192204 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 70440 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 379888 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 859680 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 55 | 1090944 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 30240
| Adani Power Jharkhanda Ltd |  | Import | 748*2 | 1496 | 1209 | 28707273
| Rajshahi Area Total |  |  |  | 3631 | 2218 | 48689566
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4699400 | Coal shortage.
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 961075 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 14493
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 75 | 566208 | Low demand.
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 111426
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 1205720
| Rangpur Area Total |  |  |  | 750 | 345 | 7558322
| Total |  |  |  | 24171 | 13395 | 285301940
| Eastern Grid Total |  |  |  | 14404 | 7758 | 157382254
| Western Grid Total |  |  |  | 9767 | 5637 | 127919686
| National Grid Total |  |  |  | 24171 | 13395 | 285301940
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-08-04
| (a) ENTIRE EASTERN GRID : |  | 8360.49 | MW | (b) ENTIRE WESTERN GRID : |  | 4443.5 | MW
| i) Dhaka area |  | 4209.99 | MW | i) Khulna area |  | 1619.5 | MW
| ii) Chittagong area |  | 1240.5 | MW | ii) Rajshahi area |  | 1538.6 | MW
| iii) Comilla area |  | 1236 | MW | iii) Barisal area |  | 408.4 | MW
| iv) Mymensingh area |  | 1129 | MW | iv) Rangpur area |  | 877 | MW
| v) Sylhet area |  | 545 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 12803.99 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 32 | 22:00 | Kamrangirchar | 52.5 | 12:00 | Natore | 157 | 21:00 | Sholosohor | 31 | 00:00
2 | AKSML | 84.5 | 00:00 | Chowmuhani | 213 | 22:00 | Kaptai | N/A | N/A | Nawabganj | 46 | 00:00 | Shyampur | 154 | 01:00
3 | Aftabnagar | 32 | 00:00 | Chuadanga | 116 | 22:00 | Kazla | 87 | 13:00 | Netrakona | 130 | 22:00 | Siddhirganj | 102 | 00:00
4 | Agargaon | 69 | 00:00 | Coxsbazar | 126 | 22:00 | Keranigonj | 60 | 00:00 | New | 72 | 00:00 | Sirajganj | 108 | 00:00
5 | Agrabad | 82 | 19:30 | Cumilla(N) | 157 | 23:00 | Khagrachori | 32 | 19:30 | Niamatpur | 100 | 21:00 | Sonargaon | 67 | 03:00
6 | Amnura | 73 | 22:00 | Cumilla(S) | 154 | 01:00 | Khulna | 88 | 21:00 | Noapara | 36 | 22:00 | Sreemongol | 63 | 23:00
7 | Ashuganj | 71 | 00:00 | Daudkandi | 130 | 00:00 | Khulshi | 160 | 00:00 | PHP | 10 | 12:00 | Sreepur | 62 | 02:00
8 | BIPTC | N/A | N/A | Dhaka | 18 | 13:00 | Kishoreganj | 152 | 22:00 | Pabna | 114 | 21:00 | Srinagar | 43.12 | 22:00
9 | BSRM | 168 | 20:00 | Dhamrai | 104 | 22:00 | Kodda | 247 | 12:00 | Palashbari | 137 | 23:00 | Sunamganj | 54 | 21:00
10 | Bagerhat | 95 | 22:00 | Dhanmondi | 118 | 12:00 | Kulaura | 50 | 19:00 | Panchagarh | 53 | 19:30 | Sylhet | 143 | 00:00
11 | Bakulia | 84 | 21:00 | Dohazari | 104 | 22:00 | Kurigram | 66 | 19:30 | Patuakhali | 93 | 00:00 | TK | 0 | 03:00
12 | Banani | 23 | 19:00 | Faridpur | 152 | 22:00 | Kushtia | 140 | 21:00 | Payra | 22.6 | 22:00 | Tangail | 219 | 21:00
13 | Bangabhaban | 4 | 00:00 | Fatullah | 61 | 00:00 | Lalbag | 60 | 00:00 | Postogola | 56 | 00:00 | Thakurgaon | 92 | 20:00
14 | Barapukuria | 61 | 21:00 | Fenchuganj | 45 | 19:00 | Lalmonirhat | 48 | 19:30 | Purbachal | 19 | 00:00 | Tongi | 88 | 00:00
15 | Barguna | 20 | 23:00 | Feni | 114 | 19:30 | Madanganj | 44 | 23:00 | Purbasadipur | 125 | 12:00 | Ullon | 50 | 00:00
16 | Barishal | 91 | 23:00 | GPH | 92 | 17:00 | Madaripur | 94 | 23:00 | Rahim | 41 | 00:00 | Uttara | 63 | 02:00
17 | Barishal-230 | 88 | 22:00 | Ghorashal | 64 | 22:00 | Madartek | 82.12 | 00:00 | Rajbari | 70 | 19:30 | UttaraNew | 62 | 00:00
18 | Baroaulia | 68 | 00:00 | Goalpara | 34 | 21:00 | Madunaghat | 50 | 20:00 | Rajendrapur | 82 | 14:00 | Zigatola | 68 | 13:00
19 | Baroirhat | 53 | 22:00 | Gollamari | 46 | 00:00 | Magura | 62 | 19:30 | Rajshahi | 164 | 22:00
20 | Bashundhara | 128 | 12:00 | Gopalganj | 95 | 19:30 | Mahasthangarh | 76 | 23:00 | Rajshahi-230 | 43 | 23:00
21 | BashundharaCement | 0 | 00:00 | Gulshan | 86 | 12:00 | Manikganj | 104 | 21:00 | Ramganj | 112 | 22:00
22 | Beanibazar | 64 | 22:00 | Halishahar | 62 | 03:00 | Maniknagar | 54 | 13:00 | Rampur | 27 | 00:00
23 | Benapole | 60 | 19:30 | HaripurSBU | 143 | 00:00 | Matarbari | 46 | 23:00 | Rangamati | 15 | 20:00
24 | Bhaluka | 118 | 02:00 | Hasnabad | 89 | 00:00 | Matuail | 60 | 00:00 | Rangpur | 139 | 00:00
25 | Bhandaria | 50 | 20:00 | Hathazari | 64 | 19:00 | Millgate | 77 | 03:00 | Ruppur | 5 | 11:00
26 | Bhangura | 34 | 01:00 | Ishurdi | 73 | 21:00 | Mirpur | 120 | 12:00 | SSM | 0 | 00:00
27 | Bheramara(GK) | 63 | 21:00 | Jaldhaka | 70 | 00:00 | Mirsorai | 4 | 00:00 | Saidpur | 108 | 12:00
28 | Bhulta | 251 | 00:00 | Jamalpur | 163 | 21:00 | Mithapukur | 56 | 19:30 | Satkhira | 123 | 00:00
29 | Bog-Sherpur | 66 | 22:00 | Jashore | 137 | 21:00 | Modern | 0 | 00:00 | Satmasjid | 103 | 00:00
30 | Bogura | 165 | 21:00 | Jhenaidah | 127 | 19:00 | Mogbazar | 103.2 | 12:00 | Savar | 162 | 12:00
31 | Borhanuddin | 65 | 21:00 | Joydebpur | 147 | 22:00 | Mongla | 28 | 00:00 | Shahjadpur | 97 | 21:00
32 | Brahmanbaria | 153 | 22:00 | Joypurhat | 60 | 23:00 | Motijheel | 32 | 00:00 | Shahjibazar | 117 | 22:00
33 | Cantonment | 126 | 12:00 | Juldah | 19 | 23:00 | Munshiganj | 97 | 23:00 | Shahmirpur | 54 | 00:00
34 | Chandpur | 69 | 23:00 | KSRM | 33 | 17:00 | Mymensingh | 238 | 19:30 | Shariatpur | 75 | 22:00
35 | Chandraghona | 27 | 21:00 | Kabirpur | 238 | 00:00 | Naogaon | 147 | 23:00 | Sherpur | 148 | 19:00
36 | Chapai | 83 | 22:00 | Kachua | 74 | 19:30 | Narail | 54 | 19:30 | Shikalbaha | 33 | 22:00
37 | Charsaidpur | 44 | 00:00 | Kallyanpur | 105 | 00:00 | Narinda | 58 | 13:00 | Shikalbaha-230 | N/A | N/A
38 | Chauddagram | 52 | 00:00 | Kalurghat | 24 | 00:00 | Narshingdi | 170 | 00:00 | Shitalakhya | 79 | 01:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-08-04 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 408 | 17:00 | 393 | 00:00 | Gopalganj | 409 | 14:00 | 400 | 00:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | N/A | N/A | N/A | N/A
| Bhulta | 398 | 14:00 | 392 | 00:00 | Madunaghat_I | 392 | 20:00 | 380 | 00:00
| Bibiana | 407 | 18:00 | 399 | 03:00 | Payra | 414 | 18:00 | 408 | 12:00
| BIPTC | 399 | 03:00 | 393 | 00:00 | Rampal | 411 | 14:00 | 400 | 12:00
| Bogura | N/A | N/A | N/A | N/A
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 236 | 14:00 | 230 | 00:00 | Hasnabad | 235 | 13:00 | 229 | 00:00
| AKSML | 236 | 19:00 | 227 | 04:00 | Hathazari | 233 | 19:00 | 228 | 16:00
| Aminbazar | 239 | 13:00 | 233 | 00:00 | Ishurdi | 235 | 18:30 | 227 | 21:00
| Ashuganj | 236 | 18:00 | 232 | 00:00 | Jhenaidah | 227 | 18:00 | 218 | 00:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | N/A | N/A | N/A | N/A
| Baghabari | 231 | 18:00 | 224 | 20:00 | Keranigonj | 235 | 14:00 | 229 | 12:00
| Barapukuria | 223 | 15:00 | 210 | 00:00 | Khulna(S) | 236 | 18:00 | 228 | 21:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | 237 | 08:00 | 228 | 00:00
| Barishal | 237 | 07:00 | 232 | 01:00 | Maniknagar | 234 | 14:00 | 229 | 12:00
| Bheramara | 233 | 18:00 | 226 | 12:00 | Meghnaghat | 240 | 18:00 | 234 | 10:00
| Bhulta | 237 | 14:00 | 232 | 00:00 | Mirsorai | 237 | 19:30 | 226 | 02:00
| Bibiana | 234 | 18:00 | 228 | 02:00 | Rajshahi | 228 | 14:00 | 220 | 22:00
| BIPTC | 234 | 18:00 | 225 | 12:00 | Rampal | 234 | 14:00 | 228 | 12:00
| Bogura | 227 | 13:00 | 220 | 05:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 241 | 08:00 | 233 | 07:00 | Rampura | 235 | 14:00 | 231 | 00:00
| BSRM | 235 | 19:00 | 227 | 04:00 | Shikalbaha | 234 | 19:30 | 226 | 17:00
| Cumilla(N) | 233 | 14:00 | 228 | 00:00 | Shyampur | 235 | 14:00 | 229 | 00:00
| Fenchuganj | 237 | 13:00 | 233 | 23:00 | Siddhirganj | 236 | 18:30 | 232 | 00:00
| Ghorashal | 240 | 15:00 | 230 | 00:00 | Sirajgonj | 238 | 18:30 | 228 | 11:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 233 | 18:00 | 225 | 04:00
| GPH | 237 | 19:30 | 226 | 04:00 | Tongi | 234 | 07:00 | 228 | 00:00
| Haripur | 235 | 14:00 | 230 | 00:00
| 132 kV | KV |  | KV |  | Tongi | KV |  | KV
| Aftabnagar | 137 | 06:00 | 133 | 20:00 | Lalbag | 139 | 14:00 | 130 | 18:00
| Agargaon | 135 | 14:00 | 130 | 10:00 | Lalmonirhat | 130 | 15:00 | 120 | 00:00
| Agrabad | 137 | 00:00 | 132 | 17:00 | Madanganj | 135 | 14:00 | 131 | 00:00
| AKS | 134 | 19:00 | 132 | 00:00 | Madaripur | 131 | 14:00 | 127 | 22:00
| Aminbazar | 138 | 13:00 | 133 | 00:00 | Madartek | 136 | 05:00 | 133 | 12:00
| Amnura | 133 | 20:00 | 121 | 05:00 | Madunaghat | 138 | 00:00 | 134 | 04:00
| Ashuganj | 140 | 06:00 | 137 | 00:00 | Magura | 136 | 18:00 | 127 | 23:00
| Bagerhat | 135 | 08:00 | 129 | 23:00 | Mahasthangarh | 133 | 15:00 | 125 | 12:00
| Bakulia | 140 | 08:00 | 134 | 17:00 | Manikganj | 136 | 19:00 | 128 | 01:00
| Banani | 137 | 06:00 | 133 | 00:00 | Maniknagar | 136 | 07:00 | 133 | 12:00
| Bangabhaban | 136 | 14:00 | 133 | 00:00 | Matarbari | 130 | 06:00 | 120 | 23:00
| Barapukuria | 139 | 15:00 | 127 | 00:00 | Matuail | 135.6 | 19:30 | 132.3 | 01:00
| Barguna | 137 | 00:00 | 131 | 21:00 | Millgate | 136 | 14:00 | 133 | 07:00
| Barishal | 137 | 00:00 | 128 | 22:00 | Mirpur | 137 | 14:00 | 131 | 00:00
| Barishal-230 | 136 | 08:00 | 131 | 22:00 | Mithapukur | 132 | 15:00 | 121 | 12:00
| Baroaulia | 138 | 19:00 | 134 | 02:00 | Modern | 136 | 04:00 | 133 | 17:00
| Baroirhat | 133 | 10:00 | 124 | 02:00 | Mogbazar | 137 | 05:00 | 135 | 00:00
| Bashundhara | 137 | 06:00 | 132 | 00:00 | Mongla | 135 | 09:00 | 128 | 23:00
| BashundharaCement | 135 | 14:00 | 131 | 00:00 | Motijheel | 136 | 18:00 | 133 | 00:00
| Beanibazar | 130 | 18:00 | 124 | 02:00 | Munshiganj | 136 | 19:30 | 131 | 01:00
| Benapole | 134 | 17:00 | 127 | 23:00 | Mymensingh | 128 | 06:00 | 115 | 21:00
| Bhaluka | 129 | 16:00 | 118 | 21:00 | Naogaon | 129 | 18:30 | 118 | 22:00
| Bhandaria | 134 | 18:00 | 124 | 22:00 | Narail | 135 | 18:00 | 126 | 00:00
| Bhangura | 136 | 15:00 | 131 | 21:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 134 | 18:00 | 130 | 21:00 | Narshingdi | 131 | 14:00 | 125 | 00:00
| Bheramara(GK) | 134 | 04:00 | 130 | 21:00 | Natore | 134 | 18:30 | 128 | 00:00
| Bhulta | 126 | 14:00 | 120 | 01:00 | Nawabganj | 139 | 14:00 | 134 | 00:00
| Bog-Sherpur | 134 | 16:00 | 123 | 21:00 | Netrakona | 129 | 10:00 | 116 | 12:00
| Bogura | 136 | 17:00 | 130 | 04:00 | New | 137 | 14:00 | 133 | 12:00
| Bogura-230 | 136 | 13:00 | 128 | 08:00 | Niamatpur | 127 | 18:00 | 114 | 08:00
| Brahmanbaria | 133 | 16:00 | 120 | 23:00 | Noapara | 136 | 14:00 | 131 | 23:00
| Cantonment | 135 | 14:00 | 129 | 10:00 | Pabna | 134 | 18:00 | 128 | 22:00
| Chandpur | 134 | 14:00 | 119 | 00:00 | Palashbari | 129 | 15:00 | 119 | 08:00
| Chandraghona | 138 | 07:00 | 134 | 17:00 | Panchagarh | 135 | 15:00 | 111 | 12:00
| Chapai | 127 | 18:00 | 123 | 12:00 | Patuakhali | 140 | 00:00 | 133 | 21:00
| Charsaidpur | 136 | 14:00 | 132 | 00:00 | Payra | 140 | 14:00 | 137 | 01:00
| Chauddagram | 136 | 00:00 | 125 | 02:00 | PHP | 131 | 19:30 | 123 | 03:00
| Chhatak | 131 | 18:00 | 125 | 00:00 | Postogola | 137 | 14:00 | 133 | 00:00
| Chowmuhani | 129 | 11:00 | 120 | 23:00 | Purbachal | 138 | 08:00 | 131 | 12:00
| Chuadanga | 132 | 18:00 | 121 | 21:00 | Purbasadipur | 133 | 15:00 | 112 | 12:00
| Coxsbazar | 129 | 07:00 | 120 | 22:00 | Rahim | 136 | 14:00 | 133 | 00:00
| Cumilla(N) | 135 | 11:00 | 130 | 23:00 | Rajbari | 130 | 16:00 | 123 | 22:00
| Cumilla(S) | 135 | 19:30 | 126 | 19:00 | Rajendrapur | 137 | 18:30 | 130 | 05:00
| Daudkandi | 134 | 11:00 | 128 | 00:00 | Rajshahi | 135 | 18:00 | 129 | 12:00
| Dhaka | 137 | 06:00 | 134 | 00:00 | Rajshahi-230 | 136 | 14:00 | 121 | 07:00
| Dhamrai | 137 | 14:00 | 132 | 00:00 | Ramganj | 131 | 10:00 | 116 | 02:00
| Dhanmondi | 135 | 14:00 | 132 | 12:00 | Rampur | 137 | 19:00 | 132 | 01:00
| Dohazari | 137 | 19:00 | 132 | 11:00 | Rampura | 137 | 08:00 | 133 | 21:00
| Faridpur | 130 | 05:00 | 124 | 22:00 | Rangamati | 138 | 19:30 | 134 | 02:00
| Fatullah | 133 | 19:30 | 128 | 00:00 | Rangpur | 129 | 14:00 | 118 | 01:00
| Fenchuganj | 135 | 01:00 | 131 | 05:00 | Ruppur | 135 | 18:00 | 130 | 22:00
| Feni | 132 | 10:00 | 124 | 03:00 | Saidpur | 132 | 15:00 | 117 | 00:00
| Ghorashal | 140 | 07:00 | 138 | 00:00 | Satkhira | 136 | 18:00 | 128 | 21:00
| Goalpara | 139 | 14:00 | 134 | 13:00 | Satmasjid | 135 | 14:00 | 129 | 10:00
| Gollamari | 137 | 08:00 | 133 | 21:00 | Savar | 138 | 14:00 | 131 | 00:00
| Gopalganj | 133 | 14:00 | 129 | 12:00 | Shahjadpur | 138 | 18:00 | 135 | 00:00
| Gopalganj-400 | 131 | 07:00 | 127 | 00:00 | Shahjibazar | 134 | 16:00 | 124 | 23:00
| Gulshan | 136 | 06:00 | 133 | 00:00 | Shahmirpur | 140 | 19:00 | 134 | 17:00
| Halishahar | 140 | 19:30 | 133 | 16:00 | Shariatpur | 131 | 14:00 | 125 | 22:00
| Haripur | 136 | 14:00 | 133 | 00:00 | Sherpur | 122 | 07:00 | 108 | 16:00
| HaripurSBU | 136 | 14:00 | 133 | 00:00 | Shikalbaha | 129 | 19:30 | 122 | 00:00
| Hasnabad | 138 | 14:00 | 134 | 00:00 | Shikalbaha-230 | 141 | 19:30 | 136 | 04:00
| Hathazari | 138 | 19:00 | 135 | 05:00 | Shitalakhya | 137 | 19:30 | 132 | 01:00
| Ishurdi | 135 | 16:00 | 131 | 12:00 | Sholosohor | 137 | 07:00 | 132 | 17:00
| Jaldhaka | 133 | 15:00 | 115 | 00:00 | Shyampur | 132 | 18:00 | 125 | 00:00
| Jamalpur | 126 | 10:00 | 117 | 12:00 | Shyampur-230 | 132 | 14:00 | 128 | 00:00
| Jashore | 135 | 18:00 | 128 | 21:00 | Siddhirganj | 136 | 14:00 | 133 | 00:00
| Jhenaidah | 138 | 18:00 | 131 | 21:00 | Sirajganj | 135 | 18:30 | 125 | 21:00
| Jhenaidah-230 | 138 | 18:00 | 131 | 00:00 | Sonargaon | 136 | 19:30 | 131 | 00:00
| Joydebpur | 140 | 00:00 | 135 | 04:00 | Sreemongol | 133 | 16:00 | 126 | 23:00
| Joypurhat | 128 | 18:30 | 116 | 22:00 | Sreepur | 131 | 14:00 | 123 | 21:00
| Juldah | 141 | 19:30 | 135 | 11:00 | Srinagar | 166 | 23:00 | 131 | 09:00
| Kabirpur | 140 | 18:30 | 131 | 00:00 | SSM | 141 | 19:00 | 137 | 09:00
| Kachua | 134 | 10:00 | 122 | 00:00 | Sunamganj | 128 | 18:00 | 121 | 22:00
| Kaliakoir | N/A | N/A | N/A | N/A | Sylhet | 132 | 18:00 | 128 | 00:00
| Kallyanpur | 131 | 14:00 | 126 | 12:00 | Tangail | 131 | 10:00 | 123 | 12:00
| Kalurghat | 139 | 07:00 | 133 | 17:00 | Thakurgaon | 134 | 15:00 | 110 | 12:00
| Kamrangirchar | 140 | 14:00 | 125 | 00:00 | TK | 140 | 19:00 | 135 | 11:00
| Kaptai | N/A | N/A | N/A | N/A | Tongi | 138 | 07:00 | 134 | 11:00
| Kazla | 136 | 09:00 | 133 | 12:00 | Ullon | 136 | 07:00 | 133 | 23:00
| Keranigonj | 139 | 14:00 | 135 | 12:00 | Uttara | 137 | 14:00 | 131 | 01:00
| Khagrachori | 138 | 07:00 | 133 | 17:00 | UttaraNew | 137 | 15:00 | 130 | 00:00
| Khulna | 138 | 18:00 | 133 | 22:00 | Zigatola | 139 | 15:00 | 135 | 01:00
| Khulna(S) | 138 | 14:00 | 133 | 22:00
| Khulshi | 137 | 19:00 | 131 | 17:00
| Kishoreganj | 133 | 15:00 | 124 | 21:00
| Kodda | 140 | 18:30 | 130 | 05:00
| KSRM | 137 | 06:00 | 133 | 05:00
| Kulaura | 133 | 16:00 | 129 | 01:00
| Kurigram | 132 | 15:00 | 118 | 00:00
| Kushtia | 134 | 18:00 | 129 | 21:00

## L-Curve
Date | 2023-08-04
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1040 | 7596 | 5708 | 13304 |  |  |  | QF-LDC-11
0:30 | 1100 | 7237 | 5617.5 | 12854.5 | Date: | 2023-08-04
1:00 | 1160 | 6878 | 5527 | 12405
1:30 | 1165 | 6808 | 5507.5 | 12315.5
2:00 | 1170 | 6738 | 5488 | 12226
2:30 | 1163 | 6704.5 | 5466.5 | 12171 | [5 empty] | Gen. at Eve. Peak | 13395 | 13395 MW (21:00 )
3:00 | 1156 | 6671 | 5445 | 12116 | [6 empty] | 21:00
3:30 | 1143 | 6660 | 5397.5 | 12057.5 | [5 empty] | Gen. at Day Peak | 11626 | 11626 MW (12:00 )
4:00 | 1130 | 6649 | 5350 | 11999 | [6 empty] | 12:00
4:30 | 1133 | 6652 | 5338 | 11990 | [5 empty] | Highest Generation | 13554
5:00 | 1136 | 6655 | 5326 | 11981 | [6 empty] | 23:00
5:30 | 1138 | 6481 | 5198.5 | 11679.5
6:00 | 1140 | 6307 | 5071 | 11378
6:30 | 1025 | 6236 | 5023 | 11259
7:00 | 910 | 6165 | 4975 | 11140
7:30 | 955 | 6060.5 | 4987.5 | 11048
8:00 | 1000 | 5956 | 5000 | 10956
8:30 | 1020 | 5889 | 5008 | 10897
9:00 | 1040 | 5822 | 5016 | 10838
9:30 | 1070 | 5832.5 | 4976 | 10808.5
10:00 | 1100 | 5843 | 4936 | 10779
10:30 | 1108 | 5879.5 | 5052 | 10931.5
11:00 | 1116 | 5916 | 5168 | 11084
11:30 | 1128 | 6125 | 5230 | 11355
12:00 | 1140 | 6334 | 5292 | 11626
12:30 | 1123 | 6504 | 5372 | 11876
13:00 | 1106 | 6674 | 5452 | 12126
13:30 | 1068 | 6492.5 | 5208.5 | 11701
14:00 | 1030 | 6311 | 4965 | 11276
14:30 | 1080 | 6141 | 4927 | 11068
15:00 | 1130 | 5971 | 4889 | 10860
15:30 | 1101 | 5879.5 | 4744.5 | 10624
16:00 | 1072 | 5788 | 4600 | 10388
16:30 | 1071 | 5771.5 | 4556 | 10327.5
17:00 | 1070 | 5755 | 4512 | 10267
17:30 | 1055 | 5781 | 4467.5 | 10248.5
18:00 | 1040 | 5807 | 4423 | 10230
18:30 | 910 | 6558.5 | 4723.5 | 11282
19:00 | 780 | 7310 | 5024 | 12334
19:30 | 630 | 7535 | 5538 | 13073
20:00 | 730 | 7645 | 5378 | 13023 |  |  |  | Executive Engineer
20:30 | 850 | 7701.5 | 5507.5 | 13209 |  |  |  | Network Operation Division
21:00 | 970 | 7758 | 5637 | 13395
21:30 | 955 | 7812 | 5623 | 13435
22:00 | 940 | 7866 | 5609 | 13475 |  |  |  |  | Page 6 of 7
22:30 | 940 | 7895.5 | 5619 | 13514.5
23:00 | 940 | 7925 | 5629 | 13554
23:30 | 990 | 7760.5 | 5668.5 | 13429
24:00 | 1040 | 7596 | 5708 | 13304
13395 MW (21:00 )
11626 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-08-04 |  | Energy |  | 285301940
QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 4397 | 891 | 2170 | 0 | 2008 | 2800 | 107 | 359 | 404 | 154 | 0 | 14 | 149.935
0:30 | 4382 | 896 | 2155 | 0 | 1700.5 | 2722 | 106 | 389 | 331 | 154 | 0 | 19 | 645.58 |  | Date: | 43680
1:00 | 4367 | 901 | 2140 | 0 | 1393 | 2644 | 105 | 419 | 258 | 154 | 0 | 24 | 1141.225
1:30 | 4349.5 | 901.5 | 2140.5 | 0 | 1323.5 | 2645.5 | 104 | 428 | 244 | 154 | 0 | 25 | 1131.1975 | [8 empty] | Total Energy | 285.3019 | 285.3019 | Total Energy Gen 285.302 MKWHr Energy Not Served 7.128 MKWHr Energy Requirement 292.430 MKWHr
2:00 | 4332 | 902 | 2141 | 0 | 1254 | 2647 | 103 | 437 | 230 | 154 | 0 | 26 | 1121.17 | [8 empty] | Energy not Served | 7.1277 | 7.1277
2:30 | 4320.5 | 903 | 2142.5 | 0 | 1229 | 2645.5 | 102 | 429.5 | 230 | 149 | 0 | 20 | 1078.195 | [8 empty] | Energy Requirement | 292.4296 | 292.4296
3:00 | 4309 | 904 | 2144 | 0 | 1204 | 2644 | 101 | 422 | 230 | 144 | 0 | 14 | 1035.22
3:30 | 4302 | 903.5 | 2131 | 0 | 1201 | 2642.5 | 100 | 390.5 | 230 | 144 | 0 | 13 | 995.5875 | [7 empty] | Shortage
4:00 | 4295 | 903 | 2118 | 0 | 1198 | 2641 | 99 | 359 | 230 | 144 | 0 | 12 | 955.955
4:30 | 4280 | 903.5 | 2122.5 | 0 | 1202.5 | 2640.5 | 99 | 359 | 220.5 | 143 | 0 | 19.5 | 869.05
5:00 | 4265 | 904 | 2127 | 0 | 1207 | 2640 | 99 | 359 | 211 | 142 | 0 | 27 | 782.145
5:30 | 4153.5 | 904.5 | 1992.5 | 0 | 1212 | 2583 | 99.5 | 359 | 211 | 134 | 3.5 | 27 | 711.9525
6:00 | 4042 | 905 | 1858 | 0 | 1217 | 2526 | 100 | 359 | 211 | 126 | 7 | 27 | 641.76
6:30 | 3990.5 | 905 | 1841.5 | 0 | 1198 | 2507 | 100.5 | 359.5 | 202.5 | 95 | 31 | 28.5 | 516.655 | [6 empty] | Coal
7:00 | 3939 | 905 | 1825 | 0 | 1179 | 2488 | 101 | 360 | 194 | 64 | 55 | 30 | 391.55
7:30 | 3862 | 905 | 1825.5 | 0 | 1125 | 2488.5 | 101.5 | 360 | 187.5 | 86 | 83 | 24 | 360.035 | [5 empty] | Oil
8:00 | 3785 | 905 | 1826 | 0 | 1071 | 2489 | 102 | 360 | 181 | 108 | 111 | 18 | 328.52
8:30 | 3786 | 905 | 1810.5 | 0 | 1008.5 | 2466 | 103.5 | 360 | 181 | 101 | 157 | 18.5 | 289.365
9:00 | 3787 | 905 | 1795 | 0 | 946 | 2443 | 105 | 360 | 181 | 94 | 203 | 19 | 250.21
9:30 | 3805 | 905.5 | 1800 | 0 | 866.5 | 2456 | 105 | 360 | 189 | 99 | 203 | 19.5 | 186.225
10:00 | 3823 | 906 | 1805 | 0 | 787 | 2469 | 105 | 360 | 197 | 104 | 203 | 20 | 122.24
10:30 | 3835 | 906 | 1808.5 | 0 | 784.5 | 2575.5 | 105 | 360 | 186 | 109 | 243 | 19 | 73.535
11:00 | 3847 | 906 | 1812 | 0 | 782 | 2682 | 105 | 360 | 175 | 114 | 283 | 18 | 24.83
11:30 | 3896.5 | 905.5 | 1894 | 0 | 827.5 | 2743.5 | 105.5 | 360 | 183 | 123 | 296.5 | 20 | 42.4975
12:00 | 3946 | 905 | 1976 | 0 | 873 | 2805 | 106 | 360 | 191 | 132 | 310 | 22 | 60.165
12:30 | 3962 | 905 | 2016 | 0 | 1054.5 | 2781.5 | 106 | 360 | 211.5 | 132 | 327 | 20.5 | 65.4175
13:00 | 3978 | 905 | 2056 | 0 | 1236 | 2758 | 106 | 360 | 232 | 132 | 344 | 19 | 70.67
13:30 | 3978 | 905 | 2056 | 0 | 1236 | 2758 | 106 | 360 | 232 | 132 | 344 | 19 | 70.67
14:00 | 3978 | 905 | 2056 | 0 | 1236 | 2758 | 106 | 360 | 232 | 132 | 344 | 19 | 70.67
14:30 | 3784 | 902.5 | 1828 | 0 | 1170 | 2670 | 103 | 359.5 | 221.5 | 135 | 299.5 | 20 | 63.985
15:00 | 3590 | 900 | 1600 | 0 | 1104 | 2582 | 100 | 359 | 211 | 138 | 255 | 21 | 57.3
15:30 | 3616 | 900 | 1603.5 | 0 | 955 | 2578.5 | 98.5 | 359.5 | 186 | 132 | 177 | 18 | 28.65
16:00 | 3642 | 900 | 1607 | 0 | 806 | 2575 | 97 | 360 | 161 | 126 | 99 | 15 | 0
16:30 | 3640 | 900.5 | 1629 | 0 | 778 | 2563.5 | 97 | 359.5 | 161.5 | 114 | 68.5 | 16 | 0
17:00 | 3638 | 901 | 1651 | 0 | 750 | 2552 | 97 | 359 | 162 | 102 | 38 | 17 | 0
17:30 | 3649 | 900.5 | 1636 | 0 | 776.5 | 2501.5 | 98 | 359 | 171.5 | 111 | 27.5 | 18 | 0
18:00 | 3660 | 900 | 1621 | 0 | 803 | 2451 | 99 | 359 | 181 | 120 | 17 | 19 | 0
18:30 | 3837.5 | 900 | 1737.5 | 0 | 1349.5 | 2505.5 | 100 | 359.5 | 332 | 137 | 8.5 | 15 | 4.775
19:00 | 4015 | 900 | 1854 | 0 | 1896 | 2560 | 101 | 360 | 483 | 154 | 0 | 11 | 9.55
19:30 | 4018 | 900 | 1677 | 0 | 2507 | 2760 | 103 | 361 | 581 | 154 | 0 | 12 | 14.8025
20:00 | 4304 | 851 | 1717 | 0 | 2316 | 2779 | 104 | 359 | 430 | 152 | 0 | 11 | 20.055
20:30 | 4389 | 851 | 1932.5 | 0 | 2185.5 | 2791 | 104 | 359.5 | 434.5 | 153 | 0 | 9 | 10.0275
21:00 | 4474 | 851 | 2148 | 0 | 2055 | 2803 | 104 | 360 | 439 | 154 | 0 | 7 | 0
21:30 | 4471 | 823 | 2142 | 0 | 2118 | 2804 | 104 | 359.5 | 455 | 153 | 0 | 5.5 | 12.415
22:00 | 4468 | 795 | 2136 | 0 | 2181 | 2805 | 104 | 359 | 471 | 152 | 0 | 4 | 24.83
22:30 | 4461.5 | 795 | 2129 | 0 | 2244 | 2804 | 103.5 | 359 | 462 | 151 | 0 | 5.5 | 58.255
23:00 | 4455 | 795 | 2122 | 0 | 2307 | 2803 | 103 | 359 | 453 | 150 | 0 | 7 | 91.68
23:30 | 4426 | 843 | 2146 | 0 | 2157.5 | 2801.5 | 105 | 359 | 428.5 | 152 | 0 | 10.5 | 120.8075 |  | Max Temp. in Dhaka |  | 31.8° C
24:00 | 4397 | 891 | 2170 | 0 | 2008 | 2800 | 107 | 359 | 404 | 154 | 0 | 14 | 149.935
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 285.302 MKWHr Energy Not Served 7.128 MKWHr Energy Requirement 292.430 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-08-04
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 75 | 73 | 71 | 69 | 69 | 70 | 71 | 72 | 75 | 75 | 75 | 76 | 76 | 76 | 70 | 67 | 67 | 69 |  | 71 | 73 | 74 | 74 | 74 | 73 | 77 | 177000
2 | Karnaphuli Hydro PP Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 724000
3 | Chattogram TPP-1 | 118 | 116 | 114 | 116 | 117 | 118 | 120 | 113 | 116 | 120 | 117 | 116 | 117 | 110 | 115 | 116 | 117 | 115 |  | 115 | 115 | 120 | 115 | 115 | 118 | 117 | 2700000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | [5 empty] | 3 | 20 | 22 | 25 | 25 | 25 | 8 | 205574
| Teknaf 20MW PP (Solartech) | [6 empty] | 0 | 1 | 2 | 6 | 4 | 11 | 18 | 9 | 4 | 4 | 2 | 0 | [8 empty] | 53730
6 | Sikalbaha 225MW CCPP (Gas) | 226 | 226 | 226 | 224 | 227 | 220 | 226 | 226 | 226 | 221 | 225 | 224 | 223 | 224 | 221 | 221 | 220 | 221 |  | 222 | 223 | 221 | 222 | 223 | 225 | 225 | 5465072
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 50 | 50 | 50 | 50 | 50 | 50 | 33 | 34 | 34 | 34 | 34 | 34 | 50 | 50 | 50 | 47 | 48 | 47 |  | 49 | 49 | 48 | 49 | 50 | 50 | 50 | 1087067
12 | Hathazari 100 MW peaking PP | 34 | 34 | 34 | 34 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 41 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 787584
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 460000
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 26 | 25 | 25 | 25 | 25 | 29 |  | 18 | 24 | 25 | 25 | 25 | 25 | 25 | 594944
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 179 | 181 | 181 | 181 | 151 | 121 | 121 | 121 | 119 | 125 | 121 | 123 | 97 | 97 | 97 | 97 | 95 | 97 |  | 98 | 99 | 188 | 197 | 195 | 138 | 139 | 3460000
17 | Siddhirganj 335 MW CCPP | 334 | 335 | 335 | 335 | 337 | 335 | 335 | 334 | 336 | 280 | 280 | 328 | 325 | 250 | 240 | 240 | 240 | 240 |  | 330 | 290 | 290 | 331 | 328 | 332 | 331 | 7343903
18 | Kodda 300 MW PP Unit-2 (Summit) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 18 | 48 | 30 | 30 | 30 | 30 | 35 | 757745
19 | Ashuganj 195 MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [18 empty] | 83636
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 190 | 190 | 188 | 190 | 190 | 150 | 140 | 140 | 140 | 140 | 140 | 140 | 180 | 140 | 120 | 120 | 120 | 100 |  | 118 | 120 | 160 | 210 | 208 | 210 | 210 | 3826500
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP
33 | Ashuganj 225 MW CCPP | 166 | 163 | 163 | 164 | 164 | 164 | 147 | 151 | 161 | 169 | 171 | 168 | 165 | 150 | 153 | 153 | 156 | 153 |  | 155 | 156 | 173 | 185 | 193 | 193 | 199 | 4021000
34 | Ashuganj 450 MW CCPP(South) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 240 | 240 | 240 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5596000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 360 | 280 | 280 | 280 | 280 | 275 | 275 | 280 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6995000
| Ashuganj 420 MW CCPP(East) | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5615100
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 397 | 397 | 397 | 397 | 397 | 392 | 352 | 352 | 351 | 352 | 352 | 357 | 400 | 343 | 321 | 322 | 322 | 322 |  | 343 | 357 | 371 | 393 | 396 | 395 | 403 | 8947720
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 360 | 360 | 360 | 360 | 360 | 360 | 420 | 420 | 360 | 300 | 300 | 300 | 300 |  | 420 | 340 | 340 | 450 | 450 | 450 | 450 | 9356300
41 | Haripur 360 MW CCPP(HPL) | 336 | 337 | 336 | 337 | 336 | 301 | 302 | 302 | 302 | 302 | 302 | 332 | 332 | 245 | 250 | 250 | 250 | 250 |  | 336 | 265 | 300 | 342 | 332 | 343 | 341 | 7360000
42 | RPCL 210MW CCPP | 71 | 70 | 69 | 70 | 70 | 70 | 33 | 35 | 34 | 35 | 34 | 33 | 33 | 33 | 34 | 34 | 35 | 35 |  | 53 | 67 | 92 | 83 | 83 | 83 | 84 | 1213440
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 2 | 8 | 13 | 48 | 30 | 11 | 35 | 38 | 15 | 4 | 7 | 2 |  | 0 | [6 empty] | 241190
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1019000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 20 | 20 | 20 | 22 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 863160
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 30 | 28 | 25 | 25 | 25 | 25 | 30 | 30 | 30 | 20 |  | 20 | 20 | 25 | 25 | 25 | 25 | 25 | 615360
48 | Shahjibazar 86 MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 78 | 78 | 75 | 75 | 75 | 75 | 78 | 78 | 78 | 78 | 78 | 81 | 86 | 86 |  | 86 | 86 | 86 | 86 | 84 | 84 | 84 | 1918080
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 112 | 112 | 112 | 112 | 112 | 112 | 75 | 25 | 25 | 22 | 64 | 65 | 73 | 88 | 90 | 95 | 105 | 106 |  | 121 | 121 | 128 | 130 | 130 | 177 | 110 | 1730230
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 397000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 247860
54 | Hobiganj 11 MW PP Cofidence-E | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 209248
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 44 | 44 | 45 | 47 | 46 | 47 | 47 | 47 | 49 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1147200
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 507120
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 290 | 295 | 270 | 280 | 275 | 280 | 300 | 290 | 300 | 300 | 295 | 290 | 275 | 280 | 290 | 300 | 290 |  | 300 | 270 | 275 | 295 | 300 | 265 | 310 | 7101000
| Bibiyana South 400 MW | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 320 | 320 | 320 | 320 | 320 |  | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 8316200
58 | Nababganj 55 MW PP (Southern power ) | [12 empty] | 17 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 394362
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 148800
60 | Barabkunda 22 MW PP (Regent) | 12 | 10 | 10 | 10 | 12 | 12 | 12 | 12 |  | 10 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 246576
61 | Narshingdi 22 MW PP (Doreen) | [10 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 20 | 20 | 20 | 20 | 184716
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 16 | 16 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 384156
63 | Impoprt (Tripura) | 154 | 154 | 144 | 144 | 142 | 126 | 64 | 108 | 94 | 104 | 114 | 132 | 132 | 136 | 138 | 126 | 102 | 120 |  | 154 | 154 | 152 | 154 | 152 | 150 | 154 | 3155520
64 | Malancha, Ctg. EPZ (United) | 33 | 33 | 33 | 34 | 40 | 30 | 42 | 30 | 16 | 16 | 16 | 16 | 10 | 15 | 12 | 4 | 5 | 27 |  | 35 | 37 | 37 | 38 | 32 | 40 | 42 | 570720
65 | Feni 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 19 | 19 | 20 | 20 | 16 |  | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 450576
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 6 | 6 | 6 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 238140
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 31 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 819100
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 8 | 8 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 477540
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456000
70 | Summit Madhabdi | 20 | 20 | 20 | 20 | 20 | 13 | 20 | 20 | 20 | 22 | 22 | 22 | 15 | 7 | 7 | 14 | 14 | 14 |  | 14 | 20 | 18 | 19 | 21 | 21 | 21 | 424620
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 716600
72 | Rupganj 33 MW PP(Summit) | 31 | 31 | 31 | 31 | 31 | 32 | 32 | 32 | 30 | 30 | 16 | 16 | 26 | 30 | 30 | 30 | 16 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 661800
73 | Ghorashal 108 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 593818
| Feni Lanka Power | 105 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 7 | [10 empty] | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 484500
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 9 | 9 | 9 | 26 | 27 | 28 | 29 | 28 | 29 |  | 43 | 58 | 56 | 59 | 57 | 28 | 9 | 530880
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 17 | 17 | 17 |  | 34 | 108 | 72 | 54 | 74 | 108 | 108 | 914400
77 | Siddhirganj 100 PP(Dutch Bangla) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 9 | 9 | 9 | 9 | 9 | 20 | 40 | 0 |  |  |  |  | 10 | 30 | 55 | 32 | 24 | 47 | 50 | 543360
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 277920
79 | Kodda 150 MW PP | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 1786560
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | [12 empty] | 8 | 8 | 8 | 8 | 8 | 9 | 413544
| Gazipur 100 MW PP | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 105 | 105 | 105 | 105 | 105 | 105 | 35 | 1171210
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 2 |  | 0 | [6 empty] | 4918
| Jodiac Power | 36 | 36 | 36 | 36 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 526068
| Karnaphuli Power Ltd. | 55 | 55 | 55 | 46 | 55 | 55 | 62 | 55 | 51 | 55 | 55 | 42 | 55 | 55 | 55 | 55 | 17 | 17 |  | 20 | 20 | 53 | 54 | 54 | 54 | 55 | 1215230
82 | Madanganj 102 PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 12 | 12 | 17 | 17 | 368284
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 52 | 57 | 44 | 47 | 56 | 57 | 45 | 22 | [11 empty] | 19 | 55 | 51 | 57 | 40 | 44 | 44 | 674640
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 42 | 42 | 41 | 42 | 41 | 42 | 41 | 16 | 7 | [10 empty] | 2 | 24 | 18 | 9 | 9 | 16 | 47 | 408000
| Meghnaghat 104 MW PP (OPCL) | 57 | 34 | 34 | 34 | 44 | 52 | 47 | 34 | 35 | 35 | 40 | 25 | 53 | 53 | 53 | 35 | 17 | 17 |  | 53 | 71 | 70 | 72 | 72 | 71 | 72 | 1151040
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 80 | 80 | 80 | 80 | 80 | 80 | 70 | 70 | 70 | 12 | 12 | 12 | 70 | 70 | 25 | 12 | 12 | 12 |  | 57 | 57 | 68 | 25 | 80 | 80 | 80 | 1232160
92 | Fenchuganj 44 MW (Energyprima) | 48 | 48 | 48 | 48 | 48 | 48 | 47 | 47 | 47 | 45 | 44 | 46 | 47 | 44 | 47 | 49 | 45 | 45 |  | 46 | 46 | 46 | 46 | 46 | 46 | 48 | 1111824
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1015236
94 | Gagnagar 102 MW PP (Digital Power) | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 25 | 25 | 0 |  |  |  |  | 50 | 92 | 58 | 25 | 25 | 94 | 102 | 595296
95 | Patenga 50MW PP (Baraka) | 43 | 17 | 6 | 6 | 6 | 6 | 6 | 6 |  |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 171360
96 | Chattogram 108 MW PP (ECPV) | [13 empty] | 0 | 2 | 10 | 2 | 25 |  | 35 | 37 | 36 | 37 | 37 | 37 |  | 236160
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 378968
100 | Manikganj 55 MW PP (Northern) | [10 empty] | 17 | 20 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 413009
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 112 | 80 | 80 | 80 | 80 | 80 | 80 | 112 | 112 | 80 | 80 | 80 | 112 | 80 |  | 80 | 80 | 80 | 112 | 112 | 112 | 112 | 2329691
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 0 | 1 | 0 | 0 | 0 | [8 empty] | 10400
103 | Kamalaghat 54 MW PP(Banco Energy) | [12 empty] | 17 | 17 | 17 | 17 | 17 | 17 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 298800
104 | Keranigonj 300 MW PP (APR) | [26 empty] | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 78 |  | 86 | 87 | 88 | 88 | 88 | 69 | 68 | 1716000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 34 | 35 | 55 |  | 112 | 116 | 115 | 116 | 118 | 68 | 43 | 1244880
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 35 | 35 |  | 86 | 86 | 86 | 86 | 86 | 86 | 25 | 929280
116 | Chandpur 200 MW (Desh energy) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 59 | 70 | 70 | 68 | 68 | 68 | 68 | 68 | 69 |  | 74 | 103 | 100 | 100 | 104 | 141 | 156 | 1622400
117 | Ashuganj 150 MW PP (Midland) | 11 | 6 | 6 | 5 | 6 | 6 | 6 | 5 | 6 | 6 | 6 | 5 | 6 | 6 | 5 | 6 | 6 | 6 |  | 28 | 65 | 62 | 60 | 60 | 28 | 6 | 364654
118 | Bibiyana-III 400 MW CCPP | 402 | 402 | 402 | 402 | 402 | 318 | 319 | 317 | 317 | 319 | 316 | 366 | 346 | 346 | 331 | 339 | 332 | 332 |  | 397 | 352 | 400 | 403 | 403 | 403 | 403 | 8725000
| Jamalpur 115 MW PP (United) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 85 | 85 | 85 | 85 | 84 | 18 | 18 | 700800
| Anwara 300 MW PP (United) | 68 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 15 | 66 | 68 | 68 | 69 | 15 | 15 | 15 |  | 190 | 176 | 153 | 100 | 122 | 170 | 170 | 1861745
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 12 | 32 | 38 | 38 | 38 | 12 | 12 | 12 |  | 74 | 88 | 88 | 25 | 60 | 88 | 25 | 760320
| Anlima Energy Ltd. | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 31 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 840545
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 442080
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 4 | 7 |  | 12 |  | 10 | 20 | 16 | 7 | 5 | 5 | 1 |  | 0 | [6 empty] | 102445
| Chandpur 115(Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 18 | 24 | 61 | 46 | 70 | 72 | 72 | 72 | 70 | 71 |  | 79 | 115 | 114 | 112 | 110 | 114 | 78 | 1331520
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 22 | 17 | 17 | 0 |  |  |  | 3 | 12 | 24 | 30 | 17 | 17 | 17 | 389520
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 43 | 54 | 54 | 17 | 0 |  |  |  | 100 | 142 | 17 | 17 | 40 | 53 | 53 | 644000
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 24 | 26 | 14 | 12 | 27 | 27 | 30 | 18 | 19 | 20 | 18 | 22 | 19 | 24 | 21 | 15 | 17 | 19 |  | 11 | 12 | 11 | 7 | 4 | 7 | 14 | 429600
| Matarbari 2*600 MW (CPGCL) | [9 empty] | 15 | 85 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 1600000
120 | Eastern Zone Total | 6878 | 6738 | 6671 | 6649 | 6655 | 6307 | 6165 | 5956 | 5822 | 5843 | 5916 | 6334 | 6674 | 6311 | 5971 | 5788 | 5755 | 5807 |  | 7310 | 7535 | 7645 | 7758 | 7866 | 7925 | 7596 | 157382254
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 32 |  |  |  | 5 | 32 | 32 | 0 |  |  |  |  | 20 | 27 | 16 | 16 | 16 | 16 | 50 | 341760
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL) | 104 | 104 | 104 | 104 | 104 | 104 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 104 | 105 | 104 | 104 |  | 105 | 106 | 104 | 105 | 104 | 104 | 104 | 2339309
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [8 empty] | 27 | 34 | 4 | 0 |  |  |  | 138720
| Khulna 225 MW CCPP | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2868778
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  |  | 5 | 11 | 20 | 0 |  |  |  | 10 | 20 | 21 | 35 | 35 | 35 | 35 | 530880
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 2 | 12 | 19 | 17 | 2 | 21 | 36 | 38 | 40 | 46 | 18 | 9 | 4 |  | 0 | [6 empty] | 253440
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 17 | 17 | 17 | 0 |  |  |  | 4 | 150 | 62 | 17 | 17 | 17 | 72 | 475200
133 | Bhola Nutan Biddut BD LTD (GAS) | 225 | 225 | 225 | 225 | 224 | 185 | 185 | 185 | 185 | 185 | 185 | 225 | 220 | 185 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 220 | 220 | 223 | 222 | 4904645
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  |  | 16 | 16 | 0 |  |  |  |  | 16 | 20 | 18 | 16 | 16 | 16 | 16 | 299424
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 130 | 125 | 130 | 130 | 130 | 100 | 100 | 100 | 100 | 100 | 80 | 132 | 133 | 80 | 80 | 80 | 80 | 80 |  | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 2625000
140 | Bhola 33 MW PP (Venture) | 31 | 31 | 30 | 27 | 25 | 21 | 14 | 10 | 12 | 14 | 18 | 20 | 22 | 22 | 21 | 21 | 19 | 18 |  | 26 | 28 | 28 | 30 | 31 | 30 | 31 | 545011
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [11 empty] | 8 | 8 | 0 | [5 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 50250
143 | Gopalganj 100 MW Peaking PP | 52 | 46 | 46 | 46 | 36 | 36 | 36 | 22 | 22 | 22 | [16 empty] | 371200
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  |  | 5 | 15 | 15 | 0 |  |  |  |  | 62 | 51 | 15 | 15 | 15 | 50 | 15 | 390672
146 | Bheramara HVDC | 901 | 902 | 904 | 903 | 904 | 905 | 905 | 905 | 905 | 906 | 906 | 905 | 905 | 906 | 900 | 900 | 901 | 900 |  | 900 | 900 | 851 | 851 | 795 | 795 | 891 | 21518545
147 | Bheramara 410 MW CCPP | 225 | 200 | 180 | 160 | 155 | 135 | 95 | 75 | 75 | 155 | 180 | 100 | 60 | 50 | 75 | 105 | 105 | 140 |  | 165 | 215 | 255 | 270 | 255 | 245 | 225 | 3968064
148 | Payra 1320 MW | 1244 | 1244 | 1244 | 1244 | 1244 | 1120 | 1100 | 1100 | 1100 | 1100 | 1220 | 1244 | 1244 | 1120 | 1060 | 1060 | 1060 | 960 |  | 1000 | 1200 | 1220 | 1244 | 1244 | 1244 | 1244 | 30050900
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 200 | 200 | 200 | 200 | 200 | 195 | 195 | 180 | 180 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4699400
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [26 empty] | 0
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 4 | 4 | 3 | 1 | 1 | 3 | 5 | 1 | 1 | 0 | [8 empty] | 30240
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 200 | 218 | 203 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3809473
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 190 | 190 | 187 | 182 | 176 | 176 | 160 | 160 | 160 | 160 | 160 | 170 | 191 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 158 | 160 | 157 | 173 | 4248700
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 414 | 414 | 414 | 414 | 360 | 320 | 320 | 320 | 320 | 320 | 320 | 414 | 320 | 240 | 240 | 240 | 230 |  | 230 | 230 | 230 | 414 | 414 | 414 | 414 | 8353600
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [20 empty] | 5 | 5 | 16 | 26 | 24 | 24 | 81709
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 192204
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 8 |  |  | 24 | 8 | 0 |  |  |  |  | 8 | 16 | 8 | 8 | 8 | 8 | 8 | 473969
167 | Katakhali 50 MW Peaking PP | 22 | [11 empty] | 13 | 28 | 30 | 0 |  |  |  | 28 | 29 | 30 | 30 | 28 | 28 | 28 | 224836
168 | Santahar 50 MW Peaking PP | [19 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 166610
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | [17 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 70440
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 51 | 88 | 91 | 92 | 92 | 63 | 14 | 379888
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 0 |  |  |  | 17 | 50 | 50 | 50 | 50 | 50 | 35 | 859680
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1090944
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 28 | 28 | 34 | 28 | 34 | 34 | 0 |  |  |  | 57 | 71 | 70 | 70 | 92 | 92 | 91 | 961075
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 3 | 3 | 2 | 2 | 1 |  | 0 | [6 empty] | 14493
178 | Energypac Power Venture Thakurgaon Ltd. | [12 empty] | 35 | 36 | 36 | 0 |  |  |  | 72 | 72 | 75 | 75 | 84 | 113 | 114 | 566208
| Intraco Solar 30 MW | [5 empty] | 1 | 3 | 7 | 11 | 11 | 19 | 32 | 21 | 13 | 8 | 0 | 1 | 0 | [8 empty] | 111426
| Adani Power Jharkhanda Ltd | 1210 | 1213 | 1210 | 1207 | 1206 | 1216 | 1198 | 1199 | 1153 | 1154 | 1177 | 1211 | 1164 | 1167 | 1177 | 1170 | 1162 | 1161 |  | 1210 | 1210 | 1209 | 1209 | 1211 | 1209 | 1206 | 28707273
178 | Teesta Solar Limited | [5 empty] | 2 | 34 | 68 | 155 | 118 | 202 | 205 | 206 | 81 | 165 | 65 | 10 | 7 |  | 0 | [6 empty] | 1205720