## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-08-17 | Thursday
|  | Date (day): | 2023-08-17 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12502.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14909 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-08-16 | 2023-08-17 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 116 | 170 | 140 | 170
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 12 | 12 | 96 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 400 | 404 | 400 | 400 | 12
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 331 | 332 | 330 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 9 | 9 | 8 | 16 | 67 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 30 | 31 | 17 | 30 | 72 |  | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 15 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 46 | 56 | 60 | 60 | 15 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 20 | 20
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 131 | 75 | 90 | 90 | 120 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 42 | 33 | 24 | 32 |  | 68 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 318 | 318 | 330 | 330
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 42 | 16 | 74
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 35 | 17 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 64 | 16 | 64 | 85 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 35 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 38 | 39 | 40 | 40 |  | 40 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 24 | 31 | 32 | 32
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 25 | 8 | 25 | 27 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 63 | 145 | 65 | 145 | 155 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
33 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
34 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 75 | 149 | 70 | 149
35 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 88 | 35 | 88 | 17 |  | Fuel shortage
36 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 27 | 54 | 34 | 55 | 49 |  | Fuel shortage
37 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 162 | 54 | 162
38 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 23 | 0 | 35 | 0
39 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6063 | 5722 | 2569 | 3078 | 2618 | 3144 | 1018 | 1203
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 113 | 115 | 120 | 120 |  | 60
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
41 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 16 | 8 | 25
42 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 7 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 46 | 6 | 47 | 3
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 201 | 201 | 195 | 195
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 222 | 222 | 225 | 225
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 51 | 51 | 51 | 54 |  | Fuel shortage
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 16 | 42 | 40 | 40 | 58 |  | Fuel shortage
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 32 | 34 | 34 |  | 68 | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 35 | 46 | 35 | 46 | 54 |  | Fuel shortage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 50 | 25 | 50 | 50 |  | Fuel shortage
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 10 | 10 | 10 | 10 | 12 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 26 | 5 | 25
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 11 | 0 | 12 | 96 |  | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 78 | 285 | 70 | 280 | 20 |  | Fuel shortage
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 55 | 55 | 55 | 55 | 55 |  | Engine problem.
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 50 | 25 | 50 | 50 |  | Fuel shortage
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 27 | 51 | 34 | 51 | 65 |  | Fuel shortage
60 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 17 | 140 | 17 | 142 | 21 |  | Fuel shortage
| SS Power I |  | Coal | SS Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 1 | 2 | 10 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 129 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2605 | 2545 | 1064 | 1468 | 1007 | 1485 | 575 | 458
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 192 | 187 | 170 | 200 | 21 |  | Gas shortage
62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 280 | 280 | 280 | 80 |  | Gas shortage
63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 240 | 240 | 270 | 270 | 90 |  | Gas shortage
64 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 240 | 240 | 240 | 240 | 160 |  | Gas shortage
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 5 | 5 | 5 | 40 |  | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
69 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 5 | 87 | 6 | 150 |  |  | Fuel shortage
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 47 | 47 | 47 | 47
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
72 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 68 | 103 | 51 | 100 | 100 |  | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 13 | 15 | 20 | 22
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 148 | 130 | 146 | 163
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 25 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Contract Expired
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 17 | 17 | 105 | 9 |  | Fuel shortage
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 28 | 9 | 28 | 85 |  | Fuel shortage
81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 72 | 101 | 72 | 115
| Cumilla Area Total |  |  |  |  | 3159 | 3096 | 1424 | 1603 | 1465 | 1857 | 832 | 205
83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 81 | 85 | 50 | 85 | 117 |  | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 16 | 16 | 16 |  | 6 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 18 | 83 | 18 | 88 | 112 |  | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 65 | 85 | 68 | 85 | 30 |  | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 42 | 0 | 50 | 0
90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 230 | 275 | 209.6 | 280 | 117 | 6
91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 42 | 42 |  | 48 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 112 | 112 |  | 51 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 50 | 50 | 50
96 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 43 | 46 | 46 | 46
97 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 11 | 11
98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 50 | 50 | 50 | 50 |  | 16
99 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 72 | 81 | 86 | 86
100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 181 | 178 | 180 | 180 |  | 51 | Machine problem
102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 17 | 17
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
103 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
104 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 290 | 300 | 300 |  |  | FGMO
105 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 232 | 280 | 280 |  | 120 | ST under maint
106 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
107 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 340 | 350 | 360 | 360
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1276 | 1528 | 1611 | 1611 | 0 | 743
108 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 911 | 795 | 911 | 911
109 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 65 | 16 | 48 |  | 67 | Engine problem
110 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 21 | 0 | 40 |  | 14 | Engine problem
111 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
112 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 42 | 40 | 51 | 58 |  | Fuel shortage
113 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 280 | 260 | 290 | 290 | 120 |  | Gas shortage
114 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 16 | 8 | 8 | 32 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
115 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 17 | 17 | 17 | 88 |  | Fuel shortage
116 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 15 | 67 | 15 | 105
117 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 59 | 0 | 100 | 0
118 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 220 | 220 | 50 | 50 | 0 | 0
119 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 373 | 517 | 500 | 500 | 117 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3125 | 3121 | 1705 | 1850 | 1897 | 1970 | 661 | 81
120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 110 | 16 | 110
121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 22 | 32 | 22 | 30 |  | 10 | Engine problem
122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 124 | 130 | 130 | 132 |  | 62 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244
124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 221 | 220 | 220 | 220
125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 150 | 17 | 150
126 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 | 307 |  | Coal shortage
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1644 | 1886 | 1649 | 1886 | 307 | 72
127 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
128 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 35 | 0 | 35 | 17 |  | Fuel shortage
129 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 16 | 0 | 30 |  | 41 | Engine problem
130 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 28 | 28 | 28 | 28
131 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 8 | 34 | 16 |  | Fuel shortage
132 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 23 | 30 | 35 | 15 |  | Fuel shortage
133 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Gas shortage
134 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 |  |  | Fuel shortage
135 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 196 | 190 | 200 | 200 | 20
136 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 414 | 0 | 400 | 14
137 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 23 | 0 | 30 | 20 |  | Fuel shortage
138 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 92 | 50 | 90 | 14 |  | Fuel shortage
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 50 | 35 | 50 | 63 |  | Fuel shortage
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 55 | 35 | 57 | 56 |  | Fuel shortage
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 748*2 | 1496 | 1496 | 1311 | 1357 | 1200 | 1300
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 2040 | 2299 | 1608 | 2305 | 450 | 254
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 220 | 200 | 200 | 200
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 49 | 35 | 56 | 57 |  | Fuel shortage
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 75 | 35 | 115
153 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 29 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 182 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 472 | 324 | 438 | 371 | 182 | 85
| Total |  |  |  |  | 24911 | 24171 | 12424 | 14311 | 12502.6 | 14909 | 4142 | 3107
A. |  | 2023-08-16 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 14311 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 11437 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14750 | MW
3 | Day peak Generation : |  |  | 12424 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14047.16 | MW
4 | Evening peak Generation : |  |  | 14311 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 419 | MW
5 | Total Energy Generation : |  | 304.1319 | MKWHr | By Solar | 2.1767 | MKWHr
| By Gas : | 152.6662 | MKWHr |  | By Oil: | 42.5782 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 77.3482 | MKWHr |  | By Hydro: | 4.4622 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.0288 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4142 | MW | Dhaka | 4902.36 | 4902.36 |  | 0 |  | 18:00 |  | 191.955
|  |  | For Plants S/D or M/C prob = |  |  | 3107 | MW | Chittagong | 1346.7 | 1346.7 |  | 0 |  | 19:00 |  | 426.885
|  |  | Total = |  |  | 7249 | MW | Khulna | 1736.1 | 1736.1 |  | 0 |  | 19:30 |  | 508.06
7 | Total Gas Supplied : |  |  | 1155.58 | MMCFD |  |  | Rajshahi | 1509.2 | 1479.2 |  | 30 |  | 20:00 |  | 473.68
8 | Fuel Cost : | i) Gas : | Taka | 169627974.776 | ii) Oil : | Taka | 535794820.85 | Comilla | 1230 | 1140 |  | 90 |  | 21:00 |  | 419.245
|  | iii) Coal : | Taka | 291957311 | Total | Taka | 997380106.626 | Mymensingh | 1201 | 1041 |  | 160 |  | 22:00 |  | 586.37
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 648 | 609 |  | 39 |  | 23:00 |  | 970.28
| ii) During Peak Demand : |  |  | 860 | MW (E to W) at | 21:00 | hrs | Barisal | 472.8 | 472.8 |  | 0 |  | 24:00 |  | 1120.215
| iii) Maximum : |  |  | 580 | MW at | 19:00 | hrs | Rangpur | 1001 | 901 |  | 100
10 | Maximum Temperature in Dhaka was |  |  |  | 32° C |  |  | Total | 14047.16 | 13628.16 |  | 419
B. |  | 2023-08-17 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 32° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 14900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14909 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 12900 | MW
4 | Reserve(Generation end) |  |  |  | 9 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 316.6491 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11389 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.5491 | MKWHr. | ii) HVDC Flow at Peak Time |  | 795 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.3226 | MKWHr. | iii) Maximum HVDC Flow : |  | 912 | MW at | 8:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 102.08 |  | (b) Today: | 102.09 |  | (c) Rule Curve: |  | 94.12
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-08-16 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 170 | 180 | 0 | 12 | 0 | 406 | 307 |  | 0 | 450 | 0 | 51 | 25 | 15 | 290 | 0 | 126 | 72 | 102 | 32 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 19 | 16 | 32 | 8 | 0 | 128 | 75 | 120 | 0 | 8 | 223 | 0 | 0 | 0 |  | 6 | 16 | 34 | 35 | 0 | 6 | 9 | 42 | 0 | 0 | 0 | 280 | 270 | 174 | 0 | 0 | 20 | 0 | 0 | 51 | 0 | 45 | 0 | 13 | 10 | 33 | 20 | 152 | 153 | 0 | 16 | 0 | 43 | 40 | 50 | 46 | 112 | 0 | 40 | 81 | 0 | 181 | 17 | 0 | 10 | 280 | 24 | 5 | 0 | 65 | 0 | 0 | 18 | 0 | 34 | 0 | 25 | 49 | 5 | 368 | 68 | 35 | 51 | 0 | 71 | 36 | 55 | 17 | 9 | 25 | 360 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 17 | 17 | 240 | 17 | 0 | 0 | 0 | 275 |  | 861 | 0 | 305 | 0 | 16 | 0 | 0 | 0 | 0 | 26 | 0 | 124 | 33 | 64 | 0 | 0 | 0 | 0 | 0 | 24 | 28 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 300 | 17 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 1244 | 180 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 1259 | 0 | 0 |  | 7171 | 5502 | 12673 | 4555 | 861 | 1954 | 0 | 1421 | 3333 | 203 | 0 | 194 | 152 | 0 | 0 | 312.285 | 102.08
2:00 | 0 | 0 | 170 | 180 | 0 | 12 | 0 | 384 | 306 |  | 0 | 450 | 0 | 51 | 10 | 15 | 290 | 0 | 130 | 40 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 19 | 16 | 32 | 8 | 0 | 127 | 75 | 115 | 0 | 8 | 222 | 0 | 0 | 0 |  | 6 | 16 | 34 | 35 | 0 | 6 | 9 | 42 | 0 | 0 | 0 | 280 | 270 | 180 | 0 | 0 | 20 | 0 | 0 | 51 | 0 | 47 | 0 | 13 | 10 | 33 | 20 | 140 | 151 | 0 | 16 | 0 | 43 | 40 | 50 | 46 | 112 | 0 | 40 | 81 | 0 | 181 | 17 | 0 | 10 | 285 | 24 | 5 | 0 | 37 | 0 | 0 | 18 | 0 | 34 | 0 | 25 | 34 | 6 | 368 | 69 | 35 | 51 | 0 | 70 | 36 | 55 | 17 | 9 | 25 | 360 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 18 | 17 | 240 | 17 | 0 | 0 | 0 | 302 |  | 861 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 130 | 32 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 300 | 17 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 1244 | 180 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 1260 | 0 | 0 |  | 6980 | 5281 | 12261 | 4545 | 861 | 1957 | 0 | 1033 | 3351 | 202 | 0 | 172 | 140 | 0 | 0 | 295.095 | 102.08
3:00 | 0 | 0 | 170 | 180 | 0 | 12 | 0 | 359 | 306 |  | 0 | 450 | 0 | 48 | 0 | 15 | 290 | 0 | 157 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 16 | 16 | 32 | 8 | 0 | 125 | 75 | 115 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 16 | 34 | 35 | 0 | 6 | 9 | 42 | 0 | 0 | 0 | 280 | 270 | 178 | 0 | 0 | 20 | 0 | 0 | 51 | 0 | 47 | 0 | 13 | 10 | 33 | 20 | 130 | 152 | 0 | 16 | 0 | 43 | 40 | 50 | 46 | 112 | 0 | 40 | 75 | 0 | 181 | 17 | 0 | 10 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 18 | 0 | 34 | 0 | 25 | 34 | 6 | 367 | 69 | 17 | 51 | 0 | 70 | 36 | 55 | 17 | 9 | 25 | 360 | 0 | 0 | 17 | 17 | 0 | 17 | 0 | 17 | 17 | 240 | 17 | 0 | 0 | 0 | 265 |  | 911 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 300 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 1244 | 180 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 1258 | 0 | 0 |  | 6799 | 5291 | 12090 | 4571 | 911 | 1960 | 0 | 859 | 3313 | 200 | 0 | 146 | 130 | 0 | 0 | 296.05 | 102.08
4:00 | 0 | 0 | 170 | 180 | 0 | 12 | 0 | 355 | 307 |  | 0 | 450 | 0 | 45 | 0 | 15 | 290 | 0 | 103 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 16 | 16 | 32 | 8 | 0 | 125 | 75 | 123 | 0 | 8 | 224 | 0 | 0 | 0 |  | 6 | 16 | 34 | 35 | 0 | 6 | 9 | 42 | 0 | 0 | 0 | 280 | 270 | 178 | 0 | 0 | 20 | 0 | 0 | 51 | 0 | 47 | 0 | 13 | 10 | 33 | 20 | 128 | 151 | 0 | 16 | 0 | 43 | 40 | 50 | 46 | 112 | 0 | 40 | 75 | 0 | 181 | 17 | 0 | 10 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 18 | 0 | 34 | 0 | 25 | 34 | 5 | 367 | 69 | 17 | 51 | 0 | 70 | 36 | 55 | 17 | 7 | 25 | 360 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 18 | 17 | 240 | 0 | 0 | 0 | 0 | 303 |  | 911 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 300 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 940 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 1262 | 0 | 0 |  | 6744 | 4992 | 11736 | 4537 | 911 | 1960 | 0 | 820 | 3051 | 200 | 0 | 129 | 128 | 0 | 0 | 252.12 | 102.08
5:00 | 0 | 0 | 170 | 180 | 0 | 12 | 0 | 355 | 307 |  | 0 | 450 | 0 | 48 | 0 | 15 | 290 | 0 | 103 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 16 | 16 | 16 | 8 | 0 | 126 | 75 | 123 | 0 | 8 | 224 | 0 | 0 | 0 |  | 6 | 16 | 34 | 35 | 0 | 6 | 9 | 42 | 0 | 0 | 0 | 300 | 290 | 171 | 0 | 0 | 20 | 0 | 0 | 51 | 0 | 47 | 0 | 13 | 10 | 24 | 20 | 126 | 151 | 0 | 16 | 0 | 43 | 40 | 50 | 43 | 80 | 0 | 40 | 72 | 0 | 181 | 17 | 0 | 10 | 305 | 24 | 11 | 0 | 0 | 0 | 0 | 18 | 0 | 34 | 0 | 25 | 34 | 6 | 378 | 69 | 17 | 51 | 0 | 70 | 17 | 55 | 17 | 5 | 25 | 360 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 17 | 17 | 240 | 0 | 0 | 0 | 0 | 301 |  | 911 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 300 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 940 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 1260 | 0 | 0 |  | 6714 | 4965 | 11679 | 4559 | 911 | 1931 | 0 | 774 | 3048 | 201 | 0 | 129 | 126 | 0 | 0 | 211.055 | 102.08
6:00 | 0 | 0 | 170 | 180 | 0 | 12 | 0 | 355 | 307 |  | 0 | 450 | 0 | 50 | 0 | 15 | 290 | 0 | 96 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 16 | 16 | 32 | 8 | 0 | 126 | 75 | 120 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 16 | 0 | 35 | 0 | 6 | 9 | 42 | 0 | 0 | 0 | 280 | 270 | 180 | 0 | 0 | 20 | 0 | 0 | 51 | 0 | 47 | 0 | 13 | 10 | 33 | 20 | 120 | 151 | 0 | 16 | 0 | 43 | 40 | 50 | 46 | 80 | 0 | 40 | 72 | 0 | 181 | 17 | 0 | 10 | 285 | 24 | 11 | 0 | 0 | 0 | 0 | 18 | 0 | 34 | 0 | 25 | 34 | 0 | 367 | 78 | 17 | 51 | 0 | 30 | 17 | 55 | 17 | 7 | 25 | 360 | 17 | 1 | 0 | 17 | 0 | 17 | 0 | 18 | 17 | 240 | 0 | 0 | 0 | 0 | 270 |  | 911 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 300 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 930 | 180 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 377 | 0 | 0 | 1258 | 8 | 0 |  | 6587 | 4954 | 11541 | 4536 | 911 | 1912 | 0 | 751 | 3005 | 201 | 0 | 95 | 120 | 10 | 0 | 84.995 | 102.08
7:00 | 0 | 0 | 120 | 180 | 0 | 12 | 0 | 355 | 307 |  | 0 | 400 | 0 | 20 | 0 | 15 | 290 | 0 | 102 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 16 | 16 | 32 | 8 | 0 | 78 | 40 | 120 | 0 | 8 | 223 | 0 | 0 | 0 |  | 6 | 16 | 0 | 35 | 0 | 6 | 9 | 42 | 0 | 0 | 0 | 300 | 340 | 145 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 47 | 0 | 13 | 10 | 33 | 20 | 118 | 151 | 0 | 16 | 0 | 43 | 40 | 50 | 46 | 80 | 0 | 45 | 72 | 0 | 181 | 17 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 18 | 0 | 34 | 3 | 25 | 34 | 0 | 384 | 69 | 17 | 51 | 0 | 30 | 17 | 55 | 17 | 2 | 25 | 360 | 17 | 4 | 0 | 17 | 0 | 17 | 3 | 17 | 17 | 280 | 0 | 0 | 0 | 0 | 301 |  | 911 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 300 | 17 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 930 | 180 | 0 | 0 | 1 | 16 | 0 | 0 | 0 | 377 | 5 | 0 | 1259 | 15 | 0 |  | 6507 | 4930 | 11437 | 4608 | 911 | 1867 | 0 | 636 | 3037 | 118 | 0 | 95 | 118 | 47 | 0 | 79.265 | 102.08
8:00 | 0 | 0 | 120 | 180 | 0 | 12 | 0 | 356 | 306 |  | 0 | 400 | 0 | 17 | 0 | 15 | 326 | 0 | 102 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 2 | 16 | 31 | 8 | 0 | 71 | 40 | 118 | 0 | 8 | 224 | 0 | 0 | 0 |  | 6 | 16 | 0 | 35 | 0 | 6 | 9 | 17 | 0 | 0 | 0 | 280 | 270 | 168 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 47 | 0 | 13 | 10 | 33 | 20 | 124 | 152 | 0 | 16 | 1 | 43 | 40 | 50 | 46 | 112 | 0 | 55 | 72 | 0 | 181 | 17 | 0 | 10 | 305 | 24 | 11 | 0 | 0 | 0 | 0 | 18 | 0 | 36 | 4 | 25 | 34 | 0 | 367 | 69 | 17 | 51 | 1 | 66 | 17 | 55 | 17 | 0 | 25 | 360 | 17 | 15 | 0 | 17 | 0 | 17 | 9 | 18 | 17 | 240 | 17 | 0 | 0 | 0 | 296 |  | 912 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 350 | 17 | 0 | 3 | 0 | 34 | 0 | 1 | 35 | 940 | 184 | 0 | 0 | 1 | 28 | 0 | 0 | 0 | 377 | 8 | 0 | 1260 | 49 | 0 |  | 6501 | 5084 | 11585 | 4521 | 912 | 1937 | 0 | 708 | 3043 | 111 | 0 | 112 | 124 | 117 | 0 | 76.4 | 102.08
9:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 381 | 307 |  | 0 | 400 | 0 | 9 | 0 | 15 | 327 | 0 | 127 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 0 | 25 | 32 | 8 | 0 | 76 | 40 | 115 | 0 | 8 | 224 | 0 | 0 | 0 |  | 6 | 16 | 0 | 35 | 0 | 6 | 9 | 7 | 0 | 0 | 0 | 280 | 240 | 179 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 47 | 0 | 14 | 10 | 33 | 20 | 120 | 151 | 0 | 16 | 1 | 43 | 40 | 50 | 46 | 112 | 0 | 58 | 72 | 0 | 181 | 17 | 0 | 10 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 18 | 0 | 69 | 6 | 25 | 34 | 0 | 368 | 68 | 35 | 51 | 2 | 70 | 17 | 55 | 17 | 3 | 25 | 360 | 17 | 15 | 0 | 17 | 0 | 17 | 18 | 18 | 17 | 240 | 17 | 0 | 0 | 0 | 293 |  | 912 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 414 | 17 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 1020 | 184 | 0 | 0 | 1 | 62 | 0 | 0 | 0 | 378 | 6 | 0 | 1257 | 120 | 0 |  | 6592 | 5350 | 11942 | 4562 | 912 | 1981 | 0 | 789 | 3118 | 116 | 0 | 112 | 120 | 232 | 0 | 84.04 | 102.08
10:00 | 0 | 0 | 125 | 180 | 0 | 12 | 0 | 398 | 320 |  | 0 | 450 | 0 | 8 | 2 | 15 | 328 | 0 | 138 | 8 | 16 | 32 | 9 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 0 | 25 | 32 | 8 | 0 | 126 | 75 | 118 | 0 | 8 | 222 | 0 | 0 | 0 |  | 6 | 16 | 0 | 35 | 0 | 6 | 9 | 8 | 0 | 0 | 0 | 280 | 240 | 157 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 47 | 0 | 14 | 10 | 33 | 20 | 128 | 119 | 0 | 16 | 2 | 43 | 40 | 47 | 46 | 112 | 0 | 56 | 72 | 0 | 181 | 17 | 0 | 9 | 300 | 24 | 11 | 0 | 5 | 0 | 0 | 18 | 0 | 72 | 11 | 25 | 55 | 1 | 367 | 67 | 35 | 51 | 3 | 75 | 17 | 55 | 17 | 9 | 25 | 360 | 17 | 43 | 12 | 20 | 0 | 17 | 21 | 23 | 17 | 240 | 17 | 0 | 0 | 0 | 297 |  | 912 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 414 | 17 | 0 | 35 | 15 | 34 | 0 | 1 | 35 | 1170 | 184 | 0 | 1 | 3 | 50 | 0 | 0 | 0 | 374 | 21 | 0 | 1260 | 73 | 0 |  | 6860 | 5467 | 12327 | 4492 | 912 | 2045 | 0 | 908 | 3301 | 201 | 0 | 112 | 128 | 228 | 0 | 117.465 | 102.08
11:00 | 0 | 0 | 138 | 180 | 0 | 12 | 0 | 400 | 332 |  | 0 | 450 | 0 | 9 | 17 | 15 | 326 | 0 | 156 | 42 | 24 | 32 | 41 | 0 | 0 | 0 | 17 | 17 | 0 | 17 | 19 | 19 | 0 | 32 | 8 | 0 | 92 | 75 | 118 | 0 | 8 | 222 | 0 | 0 | 0 |  | 6 | 16 | 0 | 46 | 0 | 6 | 10 | 6 | 0 | 0 | 0 | 270 | 240 | 170 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 45 | 0 | 13 | 10 | 33 | 20 | 138 | 104 | 0 | 16 | 2 | 43 | 40 | 50 | 43 | 112 | 0 | 50 | 72 | 0 | 181 | 17 | 0 | 9 | 305 | 24 | 5 | 0 | 60 | 0 | 0 | 18 | 0 | 70 | 17 | 25 | 68 | 2 | 0 | 67 | 35 | 51 | 3 | 75 | 17 | 55 | 17 | 9 | 25 | 360 | 17 | 49 | 54 | 17 | 0 | 17 | 30 | 63 | 17 | 240 | 17 | 0 | 0 | 0 | 0 |  | 911 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 414 | 17 | 0 | 35 | 15 | 34 | 0 | 1 | 35 | 1222 | 221 | 0 | 17 | 4 | 67 | 0 | 100 | 0 | 377 | 21 | 0 | 1258 | 137 | 0 |  | 6471 | 5799 | 12270 | 4109 | 911 | 2097 | 0 | 1240 | 3067 | 167 | 100 | 110 | 138 | 331 | 0 | 362.9 | 102.08
12:00 | 0 | 0 | 116 | 180 | 0 | 12 | 0 | 400 | 331 |  | 0 | 450 | 0 | 9 | 30 | 15 | 318 | 0 | 131 | 42 | 24 | 32 | 46 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 19 | 19 | 0 | 24 | 8 | 0 | 126 | 75 | 113 | 0 | 8 | 222 | 0 | 0 | 0 |  | 6 | 16 | 17 | 35 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 270 | 240 | 192 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 47 | 0 | 13 | 10 | 0 | 20 | 148 | 81 | 0 | 16 | 2 | 43 | 40 | 50 | 43 | 112 | 0 | 50 | 72 | 0 | 181 | 17 | 0 | 9 | 290 | 24 | 5 | 0 | 63 | 0 | 0 | 18 | 0 | 75 | 7 | 25 | 68 | 5 | 0 | 65 | 52 | 51 | 2 | 78 | 17 | 55 | 17 | 9 | 25 | 340 | 27 | 42 | 54 | 27 | 0 | 17 | 23 | 72 | 17 | 240 | 17 | 0 | 0 | 1 | 129 |  | 911 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 414 | 17 | 0 | 35 | 15 | 34 | 0 | 7 | 35 | 1244 | 221 | 0 | 17 | 5 | 59 | 0 | 50 | 0 | 373 | 29 | 0 | 1311 | 182 | 0 |  | 6563 | 5861 | 12424 | 3947 | 911 | 2079 | 0 | 1323 | 3277 | 201 | 50 | 129 | 148 | 358 | 1 | 550.08 | 102.08
13:00 | 0 | 0 | 118 | 180 | 0 | 12 | 0 | 383 | 331 |  | 0 | 450 | 0 | 8 | 34 | 15 | 320 | 0 | 124 | 42 | 24 | 32 | 53 | 0 | 0 | 0 | 17 | 35 | 17 | 17 | 19 | 18 | 0 | 24 | 8 | 0 | 126 | 75 | 120 | 0 | 8 | 223 | 0 | 0 | 0 |  | 6 | 16 | 16 | 35 | 0 | 6 | 10 | 6 | 0 | 0 | 0 | 270 | 240 | 203 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 47 | 0 | 13 | 10 | 25 | 20 | 158 | 81 | 0 | 16 | 2 | 43 | 40 | 50 | 46 | 112 | 0 | 50 | 72 | 0 | 181 | 17 | 0 | 10 | 285 | 24 | 5 | 0 | 133 | 0 | 0 | 18 | 0 | 96 | 6 | 27 | 68 | 5 | 0 | 65 | 52 | 51 | 2 | 73 | 17 | 55 | 0 | 9 | 25 | 360 | 34 | 32 | 54 | 34 | 0 | 17 | 17 | 72 | 17 | 240 | 17 | 0 | 0 | 0 | 168 |  | 911 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 47 | 28 | 0 | 20 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 414 | 17 | 0 | 35 | 15 | 34 | 0 | 4 | 35 | 1244 | 221 | 0 | 17 | 5 | 36 | 0 | 20 | 0 | 381 | 36 | 0 | 1310 | 173 | 0 |  | 6768 | 5879 | 12647 | 4001 | 911 | 2084 | 0 | 1451 | 3313 | 201 | 20 | 195 | 158 | 313 | 0 | 432.615 | 102.08
14:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 400 | 331 |  | 0 | 450 | 0 | 8 | 34 | 15 | 280 | 0 | 125 | 33 | 24 | 32 | 58 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 19 | 18 | 25 | 31 | 8 | 0 | 126 | 75 | 113 | 0 | 8 | 220 | 0 | 0 | 0 |  | 6 | 17 | 16 | 46 | 0 | 6 | 10 | 7 | 0 | 0 | 0 | 280 | 240 | 200 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 47 | 0 | 14 | 10 | 25 | 20 | 164 | 82 | 0 | 0 | 0 | 43 | 40 | 50 | 45 | 80 | 0 | 50 | 69 | 0 | 178 | 17 | 0 | 10 | 285 | 24 | 5 | 0 | 145 | 0 | 0 | 18 | 0 | 98 | 11 | 29 | 68 | 5 | 0 | 65 | 52 | 64 | 3 | 83 | 17 | 55 | 0 | 9 | 25 | 360 | 54 | 44 | 54 | 34 | 0 | 17 | 14 | 72 | 17 | 240 | 17 | 0 | 0 | 4 | 180 |  | 911 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 26 | 64 | 0 | 0 | 0 | 16 | 0 | 47 | 28 | 0 | 22 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 350 | 17 | 0 | 35 | 15 | 34 | 0 | 3 | 35 | 1200 | 221 | 0 | 17 | 0 | 14 | 0 | 50 | 0 | 377 | 0 | 0 | 1308 | 162 | 0 |  | 6820 | 5767 | 12587 | 3981 | 911 | 1987 | 0 | 1549 | 3275 | 201 | 50 | 214 | 164 | 251 | 4 | 442.165 | 102.08
15:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 398 | 324 |  | 0 | 450 | 0 | 9 | 34 | 15 | 315 | 0 | 102 | 33 | 16 | 32 | 57 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 19 | 15 | 33 | 31 | 8 | 0 | 126 | 73 | 118 | 0 | 8 | 220 | 0 | 0 | 0 |  | 6 | 17 | 32 | 35 | 0 | 6 | 10 | 5 | 0 | 0 | 0 | 280 | 240 | 186 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 38 | 0 | 14 | 10 | 25 | 20 | 162 | 81 | 0 | 0 | 2 | 43 | 40 | 50 | 45 | 112 | 0 | 50 | 69 | 0 | 178 | 17 | 0 | 10 | 315 | 24 | 0 | 0 | 102 | 0 | 0 | 18 | 0 | 71 | 9 | 31 | 68 | 5 | 0 | 65 | 52 | 51 | 3 | 73 | 17 | 55 | 0 | 9 | 25 | 360 | 54 | 38 | 54 | 34 | 0 | 17 | 16 | 72 | 17 | 240 | 17 | 0 | 0 | 5 | 175 |  | 911 | 0 | 295 | 0 | 16 | 0 | 0 | 0 | 0 | 5 | 0 | 124 | 27 | 48 | 0 | 0 | 0 | 35 | 0 | 47 | 28 | 0 | 22 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 350 | 17 | 0 | 35 | 15 | 41 | 0 | 2 | 35 | 1210 | 218 | 0 | 17 | 0 | 40 | 0 | 46 | 0 | 382 | 1 | 0 | 1320 | 22 | 0 |  | 6758 | 5712 | 12470 | 3988 | 911 | 2038 | 0 | 1446 | 3297 | 199 | 46 | 245 | 162 | 133 | 5 | 697.15 | 102.08
16:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 402 | 324 |  | 0 | 450 | 0 | 16 | 25 | 15 | 313 | 0 | 101 | 25 | 24 | 32 | 57 | 0 | 0 | 0 | 35 | 35 | 17 | 16 | 19 | 15 | 33 | 31 | 8 | 0 | 126 | 73 | 117 | 0 | 8 | 220 | 0 | 0 | 0 |  | 6 | 35 | 32 | 46 | 0 | 6 | 10 | 11 | 0 | 0 | 0 | 280 | 240 | 190 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 38 | 0 | 14 | 10 | 25 | 20 | 158 | 84 | 0 | 0 | 1 | 43 | 40 | 50 | 45 | 112 | 0 | 50 | 75 | 0 | 178 | 17 | 0 | 10 | 290 | 24 | 0 | 0 | 62 | 0 | 0 | 18 | 0 | 54 | 5 | 33 | 68 | 5 | 15 | 67 | 60 | 51 | 1 | 70 | 17 | 55 | 0 | 9 | 25 | 360 | 54 | 15 | 54 | 34 | 0 | 17 | 8 | 72 | 17 | 240 | 17 | 0 | 0 | 5 | 0 |  | 911 | 0 | 290 | 0 | 32 | 0 | 0 | 0 | 10 | 12 | 0 | 124 | 23 | 48 | 0 | 0 | 0 | 35 | 0 | 47 | 28 | 0 | 15 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 300 | 17 | 0 | 35 | 15 | 41 | 0 | 1 | 35 | 1244 | 217 | 0 | 17 | 1 | 28 | 5 | 50 | 0 | 375 | 2 | 0 | 1310 | 1 | 0 |  | 6563 | 5672 | 12235 | 4021 | 911 | 1970 | 0 | 1446 | 3139 | 199 | 50 | 273 | 158 | 63 | 5 | 587.325 | 102.08
17:00 | 0 | 0 | 122 | 180 | 0 | 12 | 0 | 402 | 323 |  | 0 | 450 | 0 | 17 | 17 | 15 | 314 | 0 | 100 | 25 | 24 | 32 | 55 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 19 | 15 | 33 | 31 | 8 | 0 | 126 | 73 | 116 | 0 | 8 | 221 | 0 | 0 | 0 |  | 6 | 35 | 32 | 46 | 0 | 6 | 10 | 20 | 0 | 0 | 0 | 310 | 240 | 186 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 38 | 0 | 16 | 10 | 25 | 20 | 152 | 84 | 0 | 0 | 0 | 43 | 40 | 50 | 45 | 112 | 0 | 50 | 81 | 0 | 178 | 17 | 0 | 10 | 290 | 24 | 5 | 0 | 65 | 0 | 0 | 18 | 0 | 53 | 3 | 34 | 68 | 8 | 80 | 67 | 52 | 51 | 0 | 87 | 17 | 55 | 0 | 9 | 25 | 360 | 54 | 4 | 54 | 41 | 0 | 17 | 4 | 72 | 17 | 240 | 17 | 0 | 0 | 6 | 0 |  | 911 | 0 | 280 | 0 | 40 | 0 | 0 | 0 | 10 | 20 | 8 | 124 | 24 | 48 | 0 | 0 | 0 | 35 | 0 | 47 | 14 | 0 | 15 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 300 | 17 | 0 | 35 | 15 | 48 | 0 | 1 | 55 | 1160 | 216 | 0 | 17 | 1 | 13 | 36 | 50 | 0 | 376 | 1 | 0 | 1246 | 5 | 0 |  | 6677 | 5540 | 12217 | 4103 | 911 | 1984 | 0 | 1537 | 2962 | 199 | 50 | 281 | 152 | 32 | 6 | 414 | 102.08
18:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 398 | 291 |  | 0 | 450 | 0 | 10 | 15 | 15 | 280 | 0 | 119 | 25 | 24 | 32 | 56 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 19 | 0 | 33 | 31 | 8 | 0 | 126 | 73 | 118 | 0 | 11 | 222 | 0 | 0 | 0 |  | 4 | 42 | 32 | 46 | 4 | 28 | 10 | 13 | 0 | 0 | 0 | 280 | 240 | 192 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 38 | 0 | 16 | 10 | 25 | 20 | 144 | 84 | 0 | 0 | 0 | 43 | 40 | 50 | 45 | 80 | 0 | 50 | 81 | 0 | 178 | 17 | 0 | 10 | 280 | 24 | 5 | 0 | 75 | 0 | 0 | 18 | 0 | 107 | 0 | 35 | 73 | 10 | 80 | 77 | 52 | 51 | 0 | 121 | 17 | 55 | 0 | 24 | 25 | 340 | 54 | 1 | 54 | 51 | 0 | 17 | 2 | 85 | 17 | 240 | 17 | 0 | 0 | 2 | 0 |  | 911 | 0 | 275 | 0 | 32 | 0 | 0 | 0 | 10 | 30 | 8 | 124 | 23 | 48 | 0 | 0 | 0 | 35 | 5 | 48 | 14 | 0 | 15 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 300 | 17 | 0 | 35 | 15 | 49 | 0 | 0 | 55 | 1100 | 216 | 0 | 35 | 0 | 3 | 36 | 50 | 0 | 490 | 1 | 0 | 1213 | 12 | 0 |  | 6689 | 5560 | 12249 | 4014 | 911 | 1902 | 0 | 1721 | 2983 | 199 | 50 | 304 | 144 | 19 | 2 | 191.955 | 102.08
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 190 | 180 | 0 | 12 | 0 | 371 | 331 |  | 0 | 450 | 0 | 9 | 34 | 22 | 318 | 0 | 98 | 40 | 24 | 64 | 50 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 12 | 33 | 31 | 25 | 0 | 126 | 75 | 118 | 0 | 25 | 220 | 0 | 0 | 0 |  | 6 | 42 | 32 | 46 | 11 | 39 | 10 | 17 | 0 | 0 | 0 | 310 | 240 | 181 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 44 | 0 | 16 | 10 | 25 | 20 | 158 | 82 | 0 | 0 | 0 | 43 | 40 | 50 | 45 | 112 | 0 | 45 | 81 | 0 | 179 | 17 | 0 | 9 | 300 | 24 | 5 | 0 | 140 | 0 | 0 | 84 | 0 | 134 | 0 | 37 | 104 | 23 | 100 | 85 | 88 | 51 | 0 | 270 | 17 | 55 | 0 | 27 | 25 | 360 | 54 | 0 | 72 | 51 | 0 | 17 | 0 | 115 | 17 | 240 | 36 | 0 | 0 | 2 | 0 |  | 911 | 0 | 275 | 0 | 58 | 0 | 0 | 0 | 41 | 40 | 16 | 128 | 32 | 110 | 0 | 0 | 0 | 35 | 15 | 92 | 28 | 0 | 15 | 8 | 23 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 414 | 17 | 0 | 35 | 47 | 49 | 0 | 0 | 55 | 1150 | 220 | 0 | 150 | 0 | 0 | 75 | 50 | 0 | 518 | 0 | 0 | 1299 | 0 | 0 |  | 7520 | 6263 | 13783 | 4121 | 911 | 2124 | 0 | 2570 | 3167 | 201 | 50 | 479 | 158 | 0 | 2 | 426.885 | 102.08
19:30 | 0 | 0 | 180 | 180 | 0 | 12 | 0 | 396 | 332 |  | 0 | 450 | 0 | 9 | 34 | 25 | 316 | 0 | 77 | 40 | 33 | 64 | 56 | 0 | 0 | 0 | 35 | 35 | 55 | 0 | 19 | 16 | 33 | 31 | 25 | 0 | 126 | 75 | 118 | 0 | 25 | 220 | 0 | 0 | 0 |  | 6 | 42 | 32 | 46 | 11 | 46 | 10 | 21 | 0 | 0 | 0 | 325 | 240 | 180 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 46 | 0 | 16 | 10 | 25 | 20 | 152 | 84 | 0 | 0 | 0 | 43 | 40 | 50 | 45 | 112 | 0 | 45 | 81 | 0 | 179 | 17 | 0 | 10 | 320 | 24 | 5 | 0 | 145 | 0 | 0 | 84 | 0 | 149 | 0 | 50 | 104 | 50 | 151 | 85 | 88 | 51 | 0 | 272 | 17 | 55 | 0 | 29 | 25 | 360 | 54 | 0 | 120 | 51 | 0 | 17 | 0 | 115 | 17 | 240 | 127 | 0 | 0 | 3 | 0 |  | 795 | 0 | 265 | 0 | 64 | 0 | 0 | 0 | 28 | 46 | 16 | 128 | 32 | 110 | 0 | 0 | 0 | 35 | 19 | 92 | 28 | 0 | 20 | 8 | 23 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 414 | 17 | 0 | 50 | 67 | 49 | 0 | 0 | 55 | 1244 | 218 | 0 | 150 | 0 | 0 | 75 | 50 | 0 | 519 | 0 | 0 | 1314 | 0 | 0 |  | 7815 | 6303 | 14118 | 4170 | 795 | 2148 | 0 | 2748 | 3277 | 201 | 50 | 574 | 152 | 0 | 3 | 508.06 | 0
20:00 | 0 | 0 | 170 | 180 | 0 | 12 | 0 | 401 | 332 |  | 0 | 450 | 0 | 8 | 34 | 15 | 318 | 0 | 75 | 36 | 50 | 64 | 56 | 0 | 0 | 0 | 35 | 35 | 55 | 0 | 19 | 17 | 33 | 31 | 25 | 0 | 126 | 75 | 118 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 42 | 32 | 46 | 9 | 46 | 10 | 24 | 0 | 0 | 0 | 280 | 240 | 184 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 47 | 0 | 16 | 10 | 25 | 20 | 148 | 85 | 0 | 0 | 0 | 43 | 40 | 50 | 46 | 112 | 0 | 50 | 81 | 0 | 178 | 17 | 0 | 10 | 290 | 24 | 5 | 0 | 145 | 0 | 0 | 83 | 0 | 149 | 0 | 50 | 104 | 50 | 220 | 85 | 88 | 51 | 0 | 279 | 17 | 55 | 0 | 29 | 50 | 350 | 54 | 0 | 162 | 51 | 0 | 17 | 0 | 115 | 17 | 240 | 140 | 0 | 0 | 4 | 0 |  | 795 | 0 | 265 | 0 | 65 | 0 | 0 | 0 | 17 | 50 | 16 | 124 | 32 | 110 | 0 | 0 | 0 | 35 | 15 | 92 | 28 | 0 | 23 | 8 | 23 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 414 | 17 | 0 | 50 | 67 | 49 | 0 | 0 | 55 | 1244 | 220 | 0 | 150 | 0 | 0 | 75 | 50 | 0 | 518 | 0 | 0 | 1302 | 0 | 0 |  | 7871 | 6283 | 14154 | 4191 | 795 | 2124 | 0 | 2797 | 3264 | 201 | 50 | 580 | 148 | 0 | 4 | 473.68 | 102.08
21:00 | 0 | 0 | 170 | 180 | 0 | 12 | 0 | 404 | 332 |  | 0 | 450 | 0 | 9 | 31 | 15 | 318 | 0 | 75 | 33 | 42 | 64 | 56 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 20 | 33 | 31 | 25 | 0 | 126 | 75 | 115 | 0 | 16 | 222 | 0 | 0 | 0 |  | 6 | 42 | 32 | 46 | 11 | 46 | 10 | 26 | 0 | 0 | 0 | 280 | 240 | 187 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 47 | 0 | 15 | 10 | 25 | 20 | 130 | 85 | 0 | 16 | 0 | 43 | 40 | 50 | 46 | 112 | 0 | 50 | 81 | 0 | 178 | 17 | 0 | 10 | 290 | 24 | 5 | 0 | 145 | 0 | 0 | 83 | 0 | 149 | 0 | 50 | 103 | 87 | 232 | 85 | 88 | 51 | 0 | 285 | 17 | 55 | 17 | 28 | 50 | 350 | 54 | 0 | 162 | 51 | 0 | 17 | 0 | 101 | 17 | 240 | 140 | 0 | 0 | 2 | 0 |  | 795 | 0 | 260 | 0 | 65 | 0 | 0 | 0 | 21 | 42 | 16 | 130 | 32 | 110 | 0 | 0 | 0 | 35 | 16 | 92 | 28 | 0 | 23 | 8 | 23 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 414 | 17 | 0 | 50 | 67 | 49 | 0 | 0 | 55 | 1244 | 220 | 0 | 150 | 0 | 0 | 75 | 50 | 0 | 517 | 0 | 0 | 1357 | 0 | 0 |  | 7952 | 6359 | 14311 | 4266 | 795 | 2126 | 0 | 2846 | 3318 | 201 | 50 | 577 | 130 | 0 | 2 | 419.245 | 102.08
22:00 | 0 | 0 | 150 | 180 | 0 | 12 | 0 | 404 | 332 |  | 0 | 450 | 0 | 8 | 17 | 15 | 318 | 0 | 73 | 33 | 42 | 16 | 57 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 20 | 33 | 31 | 25 | 0 | 126 | 75 | 118 | 0 | 25 | 220 | 0 | 0 | 0 |  | 6 | 42 | 32 | 46 | 11 | 46 | 10 | 21 | 0 | 0 | 0 | 310 | 240 | 179 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 47 | 0 | 15 | 10 | 25 | 20 | 114 | 84 | 0 | 16 | 0 | 43 | 40 | 50 | 46 | 112 | 0 | 50 | 81 | 0 | 178 | 17 | 0 | 10 | 300 | 24 | 5 | 0 | 145 | 0 | 0 | 83 | 0 | 149 | 0 | 50 | 103 | 95 | 232 | 85 | 88 | 51 | 0 | 135 | 17 | 55 | 17 | 28 | 50 | 350 | 54 | 0 | 162 | 51 | 0 | 17 | 0 | 103 | 17 | 240 | 140 | 0 | 0 | 4 | 0 |  | 795 | 0 | 250 | 0 | 65 | 0 | 0 | 0 | 21 | 41 | 16 | 126 | 34 | 110 | 0 | 0 | 0 | 35 | 15 | 92 | 28 | 0 | 23 | 8 | 23 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 300 | 17 | 0 | 50 | 67 | 49 | 0 | 0 | 55 | 1244 | 216 | 0 | 150 | 0 | 0 | 75 | 50 | 0 | 519 | 0 | 0 | 1363 | 0 | 0 |  | 7750 | 6236 | 13986 | 4253 | 795 | 2015 | 0 | 2701 | 3326 | 201 | 50 | 527 | 114 | 0 | 4 | 586.37 | 102.07
23:00 | 0 | 0 | 140 | 180 | 0 | 12 | 0 | 398 | 301 |  | 0 | 450 | 0 | 8 | 17 | 15 | 285 | 0 | 70 | 33 | 42 | 16 | 57 | 0 | 0 | 0 | 17 | 17 | 55 | 19 | 19 | 20 | 33 | 32 | 25 | 0 | 126 | 75 | 118 | 0 | 8 | 224 | 0 | 0 | 0 |  | 6 | 42 | 32 | 46 | 0 | 46 | 10 | 24 | 0 | 0 | 0 | 280 | 240 | 179 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 47 | 0 | 15 | 10 | 25 | 20 | 126 | 84 | 0 | 16 | 0 | 43 | 40 | 50 | 46 | 80 | 0 | 50 | 81 | 0 | 180 | 17 | 0 | 10 | 300 | 24 | 5 | 0 | 145 | 0 | 0 | 18 | 0 | 94 | 0 | 50 | 103 | 97 | 380 | 69 | 88 | 51 | 0 | 87 | 17 | 55 | 17 | 21 | 50 | 350 | 52 | 0 | 162 | 51 | 0 | 17 | 0 | 115 | 17 | 240 | 140 | 0 | 0 | 1 | 0 |  | 813 | 0 | 235 | 0 | 65 | 0 | 0 | 0 | 21 | 40 | 16 | 72 | 34 | 110 | 0 | 0 | 0 | 35 | 15 | 92 | 28 | 0 | 23 | 8 | 23 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 220 | 17 | 0 | 50 | 67 | 34 | 0 | 0 | 55 | 1244 | 180 | 0 | 150 | 0 | 0 | 75 | 50 | 0 | 520 | 0 | 0 | 1363 | 0 | 0 |  | 7529 | 6055 | 13584 | 4258 | 813 | 1839 | 0 | 2443 | 3327 | 201 | 50 | 526 | 126 | 0 | 1 | 970.28 | 102.07
24:00 | 0 | 0 | 160 | 180 | 0 | 12 | 0 | 368 | 322 |  | 0 | 420 | 0 | 8 | 17 | 15 | 260 | 0 | 75 | 20 | 8 | 16 | 45 | 0 | 0 | 0 | 17 | 0 | 35 | 19 | 19 | 20 | 0 | 32 | 8 | 0 | 126 | 75 | 115 | 0 | 8 | 221 | 0 | 0 | 0 |  | 6 | 42 | 34 | 35 | 0 | 46 | 10 | 35 | 0 | 0 | 0 | 280 | 240 | 185 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 47 | 0 | 15 | 10 | 25 | 20 | 110 | 84 | 0 | 16 | 0 | 43 | 40 | 50 | 46 | 80 | 0 | 55 | 81 | 0 | 181 | 17 | 0 | 10 | 280 | 16 | 5 | 0 | 82 | 0 | 0 | 18 | 0 | 35 | 0 | 22 | 54 | 97 | 237 | 69 | 35 | 51 | 0 | 88 | 17 | 55 | 17 | 9 | 25 | 350 | 17 | 0 | 162 | 51 | 0 | 17 | 0 | 67 | 17 | 240 | 17 | 0 | 0 | 0 | 0 |  | 813 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 11 | 38 | 16 | 130 | 34 | 110 | 0 | 0 | 0 | 0 | 15 | 32 | 28 | 0 | 15 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 200 | 17 | 0 | 35 | 67 | 34 | 0 | 0 | 55 | 1220 | 220 | 0 | 150 | 0 | 0 | 0 | 50 | 0 | 519 | 0 | 0 | 1360 | 0 | 0 |  | 6665 | 5812 | 12477 | 4103 | 813 | 1841 | 0 | 1793 | 3299 | 201 | 50 | 267 | 110 | 0 | 0 | 1120.215 | 102.07
KWH | 0 | 0 | 3523719 | 4299750 | 0 | 305272 | 0 | 9367550 | 7648000 |  | 0 | 10112000 | 0 | 473280 | 317269 | 386220 | 7419803 | 0 | 2863000 | 552000 | 600624 | 854400 | 811731 | 0 | 0 | 0 | 357120 | 445762 | 440115 | 367704 | 456000 | 338040 | 491040 | 717800 | 272640 | 0 | 2786160 | 1676000 | 2800000 | 0 | 261828 | 5328187 | 0 | 0 | 0 |  | 145200 | 675257 | 541839 | 903000 | 50880 | 392640 | 220704 | 603840 | 0 | 0 | 0 | 7233500 | 6247000 | 4358000 | 0 | 0 | 227736 | 0 | 0 | 1189540 | 0 | 1075648 | 0 | 332640 | 252000 | 671600 | 498400 | 3322560 | 2626560 | 0 | 266364 | 11600 | 1021000 | 960360 | 1200600 | 1086696 | 2436954 | 0 | 1137984 | 1772160 | 0 | 4693380 | 388000 | 0 | 238500 | 7207500 | 572088 | 158000 | 0 | 1648473 | 0 | 0 | 693600 | 0 | 1778112 | 89640 | 745920 | 1515840 | 531927 | 5347000 | 1710000 | 1120762 | 1262909 | 21121 | 2391164 | 517027 | 1346540 | 283860 | 298200 | 690240 | 8607000 | 753600 | 298720 | 1340640 | 776564 | 0 | 443880 | 166288 | 1386240 | 432000 | 6036900 | 859782 | 0 | 0 | 28800 | 2178545 |  | 21549090 | 0 | 7221024 | 0 | 430080 | 0 | 0 | 0 | 155520 | 345216 | 112875 | 3020000 | 651081 | 1075872 | 0 | 0 | 0 | 335259 | 84905 | 787184 | 477520 | 0 | 206790 | 167654 | 112146 | 0 | 0 | 193968 | 0 | 0 | 4629500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4767064 | 0 | 8336872 | 404640 | 0 | 921504 | 595152 | 913977 | 0 | 22525 | 993792 | 29685600 | 4846309 | 0 | 1226400 | 25080 | 440366 | 502080 | 644920 | 0 | 9992727 | 119626 | 0 | 30861818 | 981720 | 0 |  | 166294038 | 137837856 | 304131894 | 105030865 | 21549090 | 47635324 | 0 | 35899353 | 77348190 | 4462160 | 644920 | 6033946 | 3322560 | 2176686 | 28800 | 0
Fuel Cost | 0 | 0 | 5144629.74 | 6406627.5 | 0 | 406011.76 | 0 | 9835927.5 | 8259840 |  | 0 | 11022080 | 0 | 5291270.4 | 4203814.25 | 5117415 | 8310179.36 | 0 | 5010250 | 8070240 | 8450779.68 | 13849824 | 7484159.82 | 0 | 0 | 0 | 4542566.4 | 6017787 | 5901942.15 | 275778 | 342000 | 0 | 0 | 0 | 4637606.4 | 0 | 752263.2 | 452520 | 5292000 | 0 | 4280887.8 | 5541314.48 | 0 | 0 | 0 |  | 1894860 | 11263286.76 | 9222099.78 | 12199530 | 645158.4 | 4542844.8 | 280294.08 | 2010787.2 | 0 | 0 | 0 | 8029185 | 6809230 | 5055280 | 0 | 0 | 257341.68 | 0 | 0 | 1986531.8 | 0 | 18576440.96 | 0 | 455716.8 | 189000 | 1175300 | 373800 | 23855980.8 | 2862950.4 | 0 | 362255.04 | 184904 | 1398770 | 1267675.2 | 2089044 | 1879984.08 | 2802497.1 | 0 | 2207688.96 | 4040524.8 | 0 | 4740313.8 | 834200 | 0 | 472230 | 7207500 | 429066 | 120080 | 0 | 22501656.45 | 0 | 0 | 9349728 | 0 | 24626851.2 | 1047891.6 | 7697894.4 | 20706374.4 | 7058671.29 | 4919240 | 20793600 | 16206218.52 | 15975798.85 | 0 | 28072265.36 | 5630424.03 | 14313720.2 | 3851980.2 | 3843798 | 8131027.2 | 7918440 | 9759120 | 4316504 | 17012721.6 | 8837298.32 | 0 | 5797072.8 | 1987141.6 | 20752012.8 | 5689440 | 0 | 0 | 0 | 0 | 0 | 0 |  | 64647270 | 0 | 8087546.88 | 0 | 4477132.8 | 0 | 0 | 0 | 2800915.2 | 6213888 | 1622013.75 | 3382400 | 1263097.14 | 11727004.8 | 0 | 0 | 0 | 5622293.43 | 1484988.45 | 12311557.76 | 3676904 | 0 | 3496818.9 | 2285124.02 | 1891903.02 | 0 | 0 | 146833.776 | 0 | 0 | 24490055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5529794.24 | 0 | 8253503.28 | 5438361.6 | 0 | 10901392.32 | 8599946.4 | 11607507.9 | 0 | 248901.25 | 12064634.88 | 267467256 | 4943235.18 | 0 | 9075360 | 283654.8 | 5165493.18 | 7696886.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 583418956.7 | 516903674.356 | 1100322631.056 | 112991108.436 | 64647270 | 56636866.34 | 0 | 449060804.59 | 291957311 | 1204783.2 | 0 | 86734016.26 | 23855980.8 | 13234490.43 | 0 | 0
Yesterday Day Peak | 0 | 0 | 116 | 180 | 0 | 12 | 0 | 400 | 331 |  | 0 | 450 | 0 | 9 | 30 | 15 | 318 | 0 | 131 | 42 | 24 | 32 | 46 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 19 | 19 | 0 | 24 | 8 | 0 | 126 | 75 | 113 | 0 | 8 | 222 | 0 | 0 | 0 |  | 6 | 16 | 17 | 35 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 270 | 240 | 192 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 47 | 0 | 13 | 10 | 0 | 20 | 148 | 81 | 0 | 16 | 2 | 43 | 40 | 50 | 43 | 112 | 0 | 50 | 72 | 0 | 181 | 17 | 0 | 9 | 290 | 24 | 5 | 0 | 63 | 0 | 0 | 18 | 0 | 75 | 7 | 25 | 68 | 5 | 0 | 65 | 52 | 51 | 2 | 78 | 17 | 55 | 17 | 9 | 25 | 340 | 27 | 42 | 54 | 27 | 0 | 17 | 23 | 72 | 17 | 240 | 17 | 0 | 0 | 1 | 129 |  | 911 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 414 | 17 | 0 | 35 | 15 | 34 | 0 | 7 | 35 | 1244 | 221 | 0 | 17 | 5 | 59 | 0 | 50 | 0 | 373 | 29 | 0 | 1311 | 182 | 0 |  | 12424 | DayPeak
Yesterday Evening Peak | 0 | 0 | 170 | 180 | 0 | 12 | 0 | 404 | 332 | 0 | 0 | 450 | 0 | 9 | 31 | 15 | 318 | 0 | 75 | 33 | 42 | 64 | 56 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 20 | 33 | 31 | 25 | 0 | 126 | 75 | 115 | 0 | 16 | 222 | 0 | 0 | 0 | 0 | 6 | 42 | 32 | 46 | 11 | 46 | 10 | 26 | 0 | 0 | 0 | 280 | 240 | 187 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 47 | 0 | 15 | 10 | 25 | 20 | 130 | 85 | 0 | 16 | 0 | 43 | 40 | 50 | 46 | 112 | 0 | 50 | 81 | 0 | 178 | 17 | 0 | 10 | 290 | 24 | 5 | 0 | 145 | 0 | 0 | 83 | 0 | 149 | 0 | 50 | 103 | 87 | 232 | 85 | 88 | 51 | 0 | 285 | 17 | 55 | 17 | 28 | 50 | 350 | 54 | 0 | 162 | 51 | 0 | 17 | 0 | 101 | 17 | 240 | 140 | 0 | 0 | 2 | 0 |  | 795 | 0 | 260 | 0 | 65 | 0 | 0 | 0 | 21 | 42 | 16 | 130 | 32 | 110 | 0 | 0 | 0 | 35 | 16 | 92 | 28 | 0 | 23 | 8 | 23 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 414 | 17 | 0 | 50 | 67 | 49 | 0 | 0 | 55 | 1244 | 220 | 0 | 150 | 0 | 0 | 75 | 50 | 0 | 517 | 0 | 0 | 1357 | 0 | 0 |  | 14311 | EvPeak
Forecast for Evening | 0 | 0 | 170 | 180 | 0 | 12 | 0 | 400 | 330 | 0 | 0 | 450 | 0 | 16 | 30 | 15 | 330 | 0 | 90 | 32 | 74 | 64 | 60 | 0 | 0 | 0 | 35 | 35 | 55 | 20 | 19 | 21 | 33 | 32 | 25 | 0 | 120 | 75 | 120 | 0 | 25 | 225 |  | 0 | 0 | 0 | 6 | 40 | 34 | 46 | 12 | 47 | 10 | 25 | 0 | 0 | 0 | 280 | 270 | 200 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 47 | 0 | 22 | 11 | 33 | 20 | 163 | 85 | 0 | 16 | 0 | 43 | 42 | 50 | 46 | 112 | 0 | 50 | 86 | 0 | 180 | 17 | 0 | 10 | 300 | 24 | 11 | 0 | 145 | 0 | 0 | 88 | 0 | 149 | 0 | 50 | 100 | 150 | 280 | 85 | 88 | 51 | 0 | 280 | 17 | 55 | 105 | 28 | 50 | 360 | 55 | 0 | 162 | 51 | 0 | 17 |  | 115 | 17 | 240 | 142 |  | 0 | 10 | 0 |  | 911 | 0 | 290 |  | 48 | 0 | 0 | 0 | 40 | 51 | 8 | 132 | 30 | 110 | 0 | 0 | 0 | 35 | 30 | 90 | 28 | 34 | 35 | 8 | 30 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 200 | 0 | 400 | 17 | 0 | 50 | 105 | 56 | 0 | 0 | 57 | 1244 | 220 |  | 150 |  |  | 115 | 0 |  | 500 |  | 0 | 1300 |  | 0
Forecast for Day | 0 | 0 | 140 | 180 | 0 | 12 | 0 | 400 | 330 | 0 | 0 | 450 | 0 | 8 | 17 | 15 | 330 | 0 | 90 | 24 | 16 | 16 | 60 | 0 | 0 | 0 | 17 | 35 | 35 | 20 | 19 | 21 | 33 | 32 | 8 | 0 | 120 | 75 | 120 | 0 | 8 | 225 |  | 0 | 0 | 0 | 6 | 40 | 34 | 35 | 0 | 6 | 10 | 5 | 0 | 0 | 0 | 280 | 270 | 170 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 47 | 0 | 20 | 11 | 33 | 20 | 146 | 50 | 0 | 16 | 1.6 | 43 | 42 | 50 | 46 | 112 | 0 | 50 | 86 | 0 | 180 | 17 | 0 | 10 | 300 | 24 | 11 | 0 | 65 | 0 | 0 | 18 | 0 | 70 | 20 | 25 | 51 | 6 | 280 | 68 | 35 | 51 | 5 | 70 | 17 | 55 | 17 | 9 | 25 | 360 | 34 | 50 | 54 | 34 | 0 | 17 | 35 | 72 | 17 | 240 | 17 |  | 0 | 10 | 0 |  | 911 | 0 | 290 | 0 | 16 | 0 | 0 | 0 | 0 | 40 | 8 | 130 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 28 | 8 | 30 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 17 | 0 | 35 | 15 | 35 | 0 | 8 | 35 | 1244 | 220 |  | 17 | 6 | 100 | 35 | 0 |  | 500 | 30 | 0 | 1200 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 140 | 180 | 0 | 12 | 0 | 397 | 337 | 0 | 0 | 450 | 0 | 8 | 17 | 15 | 332 | 0 | 62 | 17 | 8 | 16 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 33 | 24 | 8 | 0 | 46 | 0 | 112 | 0 | 8 | 225 | 0 | 0 | 0 | 0 | 6 | 40 | 34 | 35 | 0 | 6 | 10 | 7 | 0 | 0 | 0 | 270 | 240 | 159 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 47 | 0 | 13 | 10 | 25 | 20 | 104 | 51 | 0 | 16 | 1 | 43 | 40 | 50 | 43 | 80 | 0 | 53 | 81 | 0 | 181 | 17 | 0 | 10 | 285 | 24 | 8 | 0 | 65 | 0 | 0 | 18 | 0 | 37 | 2 | 23 | 17 | 5 | 280 | 68 | 35 | 34 | 3 | 70 | 17 | 55 | 17 | 9 | 25 | 350 | 17 | 23 | 17 | 17 | 0 | 17 | 12 | 17 | 17 | 240 | 17 | 0 | 0 | 0 | 0 | 0 | 911 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 5 | 20 | 0 | 124 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 17 | 0 | 35 | 15 | 34 | 0 | 3 | 35 | 1244 | 220 | 0 | 17 | 1 | 29 | 0 | 0 | 0 | 523 | 12 | 0 | 1210 | 52 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
292.3904
| Minimum Generation |  | 11437 | 7:00
| Highest Generation |  | 14311 | 21:00
| Day Peak Generation |  | 12424 | 12:00
| Evening Peak Generation |  | 14311 | 21:00
| HVDC Max Flow |  | 912 | 8:00
| HVDC EvPeak Flow |  | 795 | 21:00
| Load factor L.F |  | 88.55% | [164 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-08-17
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-08-16 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 12424 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 11389
Evening Peak Generation : |  |  | 14311 | MW Hour : | 21:00 | Available Max Generation : |  | 14909
E.P. Demand (at gen end) : |  |  | 14750 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14900
Maximum Generation : |  |  | 14311 | MW Hour : | 21:00 | Reserve(Generation end) |  | 9
Total Gen. (MKWH) : |  |  | 304.1319 | System Load Factor : | 88.55% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 580 | MW at | 19:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-08-17
Actual : |  | 102.09 | Ft.(MSL) , | Rule curve : | 94.12 | Ft.( MSL )
Gas Consumed : |  | Total = | 1155.58 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 169627974.776
: |  |  | Coal : | 291957311 | Oil : | 535794820.85 | Total : | 997380106.626
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4986.8826 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1372.8008 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1923.7853 |  |  | 0 | 0%
Rajshahi Area |  | 30 | 720:00 | 1672.8176 |  |  | 0 | 0%
Cumilla Area |  | 90 | 2160:00 | 1376.0741 |  |  | 0 | 0%
Mymensingh Area |  | 160 | 3840:00 | 1023.8281 |  |  | 0 | 0%
Sylhet Area |  | 39 | 936:00 | 573.4853 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 478.2986 |  |  | 0 | 0%
Rangpur Area |  | 100 | 2400:00 | 935.4597 |  |  | 0 | 0%
Total |  | 419 |  | 14343.4322 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
8:20 | 9:56 | Jamalpur 132/33kV S/S T-4 LT Scheduled S/D Due to High temperature reduce maintenance work.
8:20 | 9:56 | Jamalpur 132/33kV S/S T-4 HT Scheduled S/D Due to High temperature reduce maintenance work.
8:37 | 12:23 | Sikalbaha-TKCL 132kV Ckt-1 Scheduled S/D from Shikalbaha 230/132kV end Due to Maintenance at T.K.Chemical end.
- | 9:20 | Kushtia 132/33kV S/S T2 HT is restored.
- | 9:20 | Kushtia 132/33kV S/S T2 LT is restored.
9:50 | 11:17 | Shahjadpur 132/33kV S/S T-2(415T) LT Forced S/D Due to LT side B-phase redhot and 33 kv বাসবারের রেড হট |  |  |  |  | 12.0MW load interrup.
পল্লী বিদ্যুৎ বাসবারে কাজ করবে ।
9:51 | 11:15 | Shahjadpur 132/33kV S/S T-2(415T) HT Forced S/D Due to কাজ করবে ৩৩ কে বি এল টি সাইডের bushing এর রেড |  |  |  |  | 12.0MW load interrup.
হট। ৩৩ কেবি বাসে রেড হট পল্লী বিদ্যুৎ কর্তৃপক্ষ কাজ করবে।
9:58 | 17:36 | Gopalganj 400/132kV S/S ATR-02 LT Project Work S/D.
9:59 | 17:35 | Gopalganj 400/132kV S/S ATR-03 HT Project Work S/D.
10:02 | - | Matarbari coal power Unit-1 half-load rejection was done. |  |  |  |  | 300MW generation interrup.
10:18 | 15:52 | Savar 132/33kV S/S Bus-B Scheduled S/D Due to DPBS-3 Shutdown for Red hot maintenance.
10:26 | - | Bibiyana-3 tripped due to GBC trip. |  |  |  |  | 400MW generation interrup.
10:45 | 15:30 | Naogaon 132/33kV S/S T-1 LT Tripped showing Over current Earth fault. relays Due to Heavy flashing when closing |  |  |  |  | 50.0MW load interrup.
to capacitor bank-6 33 kv bus isolator.
10:45 | 11:05 | Naogaon 132/33kV S/S T-2 LT Tripped showing Overcurrent earth fault. relays Due to Heavy flashing when closing to |  |  |  |  | 50.0MW load interrup.
capacitor bank-6 33 kv bus isolator.
- | 11:00 | New Tongi-Tongi 132kV Ckt-2 is restored.
11:23 | - | Shahjibazar 86 MW PP tripped. |  |  |  |  | 72MW generation interrup.
11:24 | 11:33 | Shahjibazar-Sreemangal 132kV Ckt-2 Tripped from Sreemongol 132/33kV end showing Distance Relay relays Due
to N/A and from Shahjibazar 132/33kV end showing Distance Relay relays Due to None.
11:30 | 15:10 | Naogaon 132/33kV S/S T-1 HT Forced S/D Due to Showing Buchholze relay trip signal.
11:30 | - | Matarbari coal power Unit-1 was sync.
11:42 | - | Shahjibazar 86 MW PP was sync.
12:00 | - | Day peak Generation is 12424 MW
13:04 | 13:45 | Bagerhat-Bhandaria 132 kV Ckt-1 Forced S/D from Bagerhat 132/33kV end Due to Emergengy Tree trimming.
13:28 | 13:49 | Chandraghona-Madunaghat 132 kV Ckt-2 Tripped from Madunaghat 132/33kV end showing REL-670 relays Due to
General trip Zone-01,Zcom B-phase Fault.
15:52 | - | Matarbari 2*600 MW (CPGCL) was shutdown.
- | 15:54 | Bibiyana-3 400MW GT was sync.
16:19 | 16:31 | Kallyanpur 132/33kV S/S GT-2 (132kV) HT Scheduled S/D Due to 33 kV CB SF6 Gass Refill Work.
- | 19:08 | Bibiyana-3 400MW ST was sync.
21:00 | - | Peak generation 14311 MW
22:33 | 0:02 | Sirajganj 132/33kV S/S T2-(425) LT Forced S/D Due to Emergency Red Hot Maintenance. |  |  |  |  | 15.0MW load interrup.
22:34 | 0:02 | Sirajganj 132/33kV S/S T2-(425) HT Forced S/D Due to Emergency Red Hot Maintenance.
23:30 | 0:14 | Bhaluka-Mymensingh 132 kV Ckt-2 Tripped from Bhaluka 132/33kV end showing Differential protection relay ( 87L)
relays Due to Over Current.
23:30 | 0:14 | Bhaluka-Mymensingh 132 kV Ckt-1 Tripped from Bhaluka 132/33kV end showing Differential protection relay ( 87L)
relays Due to Over current.
23:33 | 23:40 | Ashuganj 230/132/33kV S/S TR-OAT-12 HT Tripped showing Master Trip-2 relays.
23:33 | 23:40 | Ashuganj 230/132/33kV S/S TR-OAT-12 LT Tripped showing Over Current Relay Master trip-2 relays Due to O/C.
0:02 | - | Bibiyana-3 400MW ST tripped due to HRSG HP safety valve problem. |  |  |  |  | 130MW generation interrup.
4:09 | - | Siddirgonj GT unit-1 S/D due to gas shortage.
5:12 | - | Sirajgonj 410 MW Unit-4 was shut down due to Red hot maintenance. |  |  |  |  | 300MW generation interrup.
6:02 | - | Netrokona 132/33 kV T-2 was shutdown due to D/W.
6:15 | - | Sirajgonj 230 S/S SNWPCL (Unit-04) Forced S/D Due to Bay DS, Y Phase Red Hot detected.
7:00 | - | Minimum generation: 11454 MW.
7:30 | 7:50 | Shahjadpur 132/33kV S/S T-3(425T) HT Forced S/D Due to T-3 50/75 MVA X-former LT side R-phase redhot maintenance.
7:30 | 7:50 | Shahjadpur 132/33kV S/S T-3(425T) LT Forced S/D Due to Shutdown for X-former LT side R- phase Bushing.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-08-16 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 170 | 3523719
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4299750
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 305272 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 404 | 9367550
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 332 | 7648000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10112000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 9 | 473280 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Under maint.
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 31 | 317269 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 386220 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 56 | 811731 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 367704 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 75 | 2863000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 33 | 552000 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 318 | 7419803
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 42 | 600624 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 357120 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 64 | 854400 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 445762 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 440115
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 39 | 794040 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 491040
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 31 | 717800
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 272640 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 145 | 1648473 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Contract Expired
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1778112
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1120762 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 54 | 753600 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1340640
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 166288
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 432000 | Fuel shortage
| Dhaka area Total |  |  |  | 5722 | 3078 | 60660714
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2800000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 16 | 261828 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 89640
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 46 | 392640
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 201 | 4462160
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 222 | 5328187
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 1262909 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 42 | 675257 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 32 | 541839 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 46 | 903000 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 745920 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 10 | 220704 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 603840
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 11 | 50880 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 21121
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 285 | 2391164 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 517027 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 55 | 1346540 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 690240 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 51 | 776564 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 140 | 859782
| SS Power I |  | SS Power | 0 | 0 | 0 | 0 | On test.
| Cox's Bazar Wind |  | IPP | 66 | 0 | 2 | 28800 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 0 | 2178545 | On test.
| Chattogram area Total |  |  |  | 2545 | 1468 | 27148587
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 187 | 4358000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7233500 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 240 | 6247000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 240 | 6036900 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 227736 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1189540
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 87 | 531927 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 47 | 1075648
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 103 | 1515840 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 15 | 332640 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 252000
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 130 | 3322560
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 671600 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 498400 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 283860 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 298200 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 443880 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 101 | 1386240
| Cumilla Area Total |  |  |  | 3096 | 1603 | 35905471
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 85 | 2626560 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 266364 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11600
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 83 | 693600 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 85 | 1710000 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 298720
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 145200 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 275 | 5752044
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1021000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 960360 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2436954 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1200600
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 46 | 1086696
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 158000 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 50 | 1137984
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1772160
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 178 | 4693380 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 388000 | Machine problem
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 572088
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7207500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 232 | 5347000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 238500
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 350 | 8607000
| Sylhet Area Total |  |  |  | 2427 | 1528 | 36827222
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 795 | 21549090
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 65 | 430080 | Low demand
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 21 | 155520 | Low demand
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 42 | 345216 | Low demand
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 260 | 7221024 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 16 | 112875 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 404640 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 67 | 595152 | Low demand
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 440366
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 220 | 50 | 644920 | Fuel shortage
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 517 | 9992727
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 3121 | 1850 | 41891610
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1075872
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 32 | 651081 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 130 | 3020000 | ST Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 29685600
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4846309
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1226400
| Barisal 307 MW |  | IPP | 307*1 | 307 | 0 | 0 | Coal shortage.
| Barisal Area Total |  |  |  | 2265 | 1886 | 40505262
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 35 | 335259 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 16 | 84905 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 28 | 477520
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 23 | 206790 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage.
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 190 | 4767064 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 8336872
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 23 | 112146 | Fuel shortage
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 193968 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 167654 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 787184 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 921504 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 55 | 993792 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 25080
| Adani Power Jharkhanda Ltd |  | Import | 748*2 | 1496 | 1357 | 30861818
| Rajshahi Area Total |  |  |  | 3631 | 2299 | 48271556
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4629500 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 49 | 913977 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 22525
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 75 | 502080 | Fuel shortage
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 119626
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 981720
| Rangpur Area Total |  |  |  | 750 | 324 | 7169428
| Total |  |  |  | 24171 | 14311 | 304131894
| Eastern Grid Total |  |  |  | 14404 | 7952 | 166294038
| Western Grid Total |  |  |  | 9767 | 6359 | 137837856
| National Grid Total |  |  |  | 24171 | 14311 | 304131894
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-08-16
| (a) ENTIRE EASTERN GRID : |  | 9039.06 | MW | (b) ENTIRE WESTERN GRID : |  | 4589.1 | MW
| i) Dhaka area |  | 4902.36 | MW | i) Khulna area |  | 1736.1 | MW
| ii) Chittagong area |  | 1346.7 | MW | ii) Rajshahi area |  | 1479.2 | MW
| iii) Comilla area |  | 1140 | MW | iii) Barisal area |  | 472.8 | MW
| iv) Mymensingh area |  | 1041 | MW | iv) Rangpur area |  | 901 | MW
| v) Sylhet area |  | 609 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 13628.16 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 34 | 21:00 | Kamrangirchar | 53.61 | 13:00 | Natore | 151 | 21:00 | Sholosohor | 35 | 19:00
2 | AKSML | 112 | 23:00 | Chowmuhani | 191 | 18:30 | Kaptai | N/A | N/A | Nawabganj | 49 | 22:00 | Shyampur | 160 | 10:00
3 | Aftabnagar | 58 | 11:00 | Chuadanga | 114 | 20:00 | Kazla | 95 | 17:00 | Netrakona | 124 | 02:00 | Siddhirganj | 118 | 12:00
4 | Agargaon | 89 | 11:00 | Coxsbazar | 130 | 21:00 | Keranigonj | 74 | 19:30 | New | 27.5 | 16:00 | Sirajganj | 128 | 20:00
5 | Agrabad | 84 | 15:00 | Cumilla(N) | 155 | 19:00 | Khagrachori | 34 | 19:30 | Niamatpur | 85 | 23:00 | Sonargaon | 103 | 18:30
6 | Amnura | 55 | 00:00 | Cumilla(S) | 164 | 14:00 | Khulna | 99 | 21:00 | Noapara | 48.5 | 21:00 | Sreemongol | 66 | 20:00
7 | Ashuganj | 69 | 21:00 | Daudkandi | 136 | 19:00 | Khulshi | 183 | 20:00 | PHP | 4 | 00:00 | Sreepur | 74 | 19:00
8 | BIPTC | N/A | N/A | Dhaka | 44 | 11:00 | Kishoreganj | 146 | 00:00 | Pabna | 124 | 19:30 | Srinagar | 46.7 | 22:00
9 | BSRM | 164 | 09:00 | Dhamrai | 124 | 19:00 | Kodda | 275 | 10:00 | Palashbari | 134 | 20:00 | Sunamganj | 54 | 20:00
10 | Bagerhat | 97 | 23:00 | Dhanmondi | 152 | 11:00 | Kulaura | 56 | 21:00 | Panchagarh | 55 | 19:30 | Sylhet | 167 | 20:00
11 | Bakulia | 100 | 19:00 | Dohazari | 96 | 20:00 | Kurigram | 60 | 21:00 | Patuakhali | 116 | 00:00 | TK | 0 | 00:00
12 | Banani | 59.2 | 16:00 | Faridpur | 162 | 21:00 | Kushtia | 130 | 19:00 | Payra | 25.6 | 23:00 | Tangail | 225 | 21:00
13 | Bangabhaban | 17 | 10:00 | Fatullah | 60 | 15:00 | Lalbag | 79 | 12:00 | Postogola | 58 | 19:00 | Thakurgaon | 98 | 22:00
14 | Barapukuria | 64 | 21:00 | Fenchuganj | 48 | 21:00 | Lalmonirhat | 52 | 10:00 | Purbachal | 20 | 19:00 | Tongi | 146 | 12:00
15 | Barguna | 22 | 00:00 | Feni | 112 | 19:00 | Madanganj | 36 | 14:00 | Purbasadipur | 132 | 20:00 | Ullon | 54 | 23:00
16 | Barishal | 108 | 19:00 | GPH | 11 | 16:00 | Madaripur | 107 | 00:00 | Rahim | 50 | 18:00 | Uttara | 72 | 11:00
17 | Barishal-230 | 100 | 21:00 | Ghorashal | 72 | 10:00 | Madartek | 88.03 | 23:00 | Rajbari | 70 | 19:00 | UttaraNew | 65 | 15:00
18 | Baroaulia | 68 | 12:00 | Goalpara | 36 | 21:00 | Madunaghat | 56 | 19:30 | Rajendrapur | 96 | 21:00 | Zigatola | 74 | 15:00
19 | Baroirhat | 66 | 23:00 | Gollamari | 54 | 20:00 | Magura | 64 | 19:00 | Rajshahi | 161 | 20:00
20 | Bashundhara | 141 | 15:00 | Gopalganj | 108.6 | 21:00 | Mahasthangarh | 78 | 19:30 | Rajshahi-230 | 36 | 23:00
21 | BashundharaCement | 0 | 00:00 | Gulshan | 72 | 10:00 | Manikganj | 118 | 20:00 | Ramganj | 114 | 19:00
22 | Beanibazar | 78 | 21:00 | Halishahar | 76.5 | 15:00 | Maniknagar | 78 | 11:00 | Rampur | 20 | 00:00
23 | Benapole | 64 | 00:00 | HaripurSBU | 160 | 20:00 | Matarbari | 47 | 21:00 | Rangamati | 14 | 19:00
24 | Bhaluka | 116 | 19:00 | Hasnabad | 90 | 21:00 | Matuail | 69 | 12:00 | Rangpur | 131 | 12:00
25 | Bhandaria | 52 | 22:00 | Hathazari | 73 | 19:00 | Millgate | 115 | 12:00 | Ruppur | 6 | 12:00
26 | Bhangura | 35 | 19:30 | Ishurdi | 77 | 19:30 | Mirpur | 132 | 19:00 | SSM | 0 | 00:00
27 | Bheramara(GK) | 65 | 19:30 | Jaldhaka | 76 | 19:30 | Mirsorai | 0 | 00:00 | Saidpur | 115 | 19:00
28 | Bhulta | 232 | 00:00 | Jamalpur | 139 | 20:00 | Mithapukur | 61 | 19:00 | Satkhira | 125 | 19:30
29 | Bog-Sherpur | 66 | 18:30 | Jashore | 137 | 19:30 | Modern | 0 | 00:00 | Satmasjid | 113 | 15:00
30 | Bogura | 171 | 19:30 | Jhenaidah | 130 | 19:00 | Mogbazar | 137.9 | 11:00 | Savar | 174 | 19:00
31 | Borhanuddin | 70 | 23:00 | Joydebpur | 177 | 18:30 | Mongla | 30 | 11:00 | Shahjadpur | 111 | 21:00
32 | Brahmanbaria | 158 | 03:00 | Joypurhat | 60 | 22:00 | Motijheel | 41 | 15:00 | Shahjibazar | 115 | 19:00
33 | Cantonment | 146 | 11:00 | Juldah | 20 | 13:00 | Munshiganj | 105 | 20:00 | Shahmirpur | 54 | 00:00
34 | Chandpur | 70 | 22:00 | KSRM | 28 | 12:00 | Mymensingh | 232 | 00:00 | Shariatpur | 84 | 21:00
35 | Chandraghona | 32 | 19:00 | Kabirpur | 286 | 20:00 | Naogaon | 134 | 19:30 | Sherpur | 122 | 05:00
36 | Chapai | 72 | 21:00 | Kachua | 72 | 18:30 | Narail | 56 | 19:00 | Shikalbaha | 41 | 21:00
37 | Charsaidpur | 50 | 10:00 | Kallyanpur | 108 | 19:30 | Narinda | 72 | 13:00 | Shikalbaha-230 | N/A | N/A
38 | Chauddagram | 61 | 18:30 | Kalurghat | 36 | 15:00 | Narshingdi | 162 | 00:00 | Shitalakhya | 107.4 | 12:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-08-16 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 398 | 06:00 | 387 | 11:00 | Gopalganj | 404 | 06:00 | 395 | 10:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 380 | 00:00 | 368 | 10:00
| Bhulta | 393 | 01:00 | 384 | 10:00 | Madunaghat_I | 386 | 03:00 | 379 | 10:00
| Bibiana | 405 | 20:00 | 394 | 13:00 | Payra | 412 | 06:00 | 407 | 11:00
| BIPTC | 398 | 20:00 | 388 | 13:00 | Rampal | 405 | 06:00 | 398 | 19:30
| Bogura | N/A | N/A | N/A | N/A
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 232 | 06:00 | 224 | 10:00 | Hasnabad | 231 | 01:00 | 223 | 09:00
| AKSML | 235 | 20:00 | 225 | 12:00 | Hathazari | 235 | 20:00 | 225 | 09:00
| Aminbazar | 233 | 21:00 | 228 | 11:00 | Ishurdi | 233 | 18:00 | 226 | 12:00
| Ashuganj | 233 | 23:00 | 228 | 09:00 | Jhenaidah | 226 | 18:00 | 217 | 01:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 233 | 06:00 | 225 | 09:00
| Baghabari | 228 | 18:00 | 221 | 11:00 | Keranigonj | 231 | 06:00 | 223 | 10:00
| Barapukuria | 219 | 17:00 | 205 | 02:00 | Khulna(S) | 232 | 18:00 | 224 | 01:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | 231 | 00:00 | 226 | 10:00
| Barishal | 238 | 20:00 | 232 | 02:00 | Maniknagar | 231 | 00:00 | 224 | 10:00
| Bheramara | 232 | 18:00 | 225 | 01:00 | Meghnaghat | 233 | 00:00 | 229 | 10:00
| Bhulta | 233 | 01:00 | 225 | 10:00 | Mirsorai | 237 | 20:00 | 224 | 07:00
| Bibiana | 231 | 00:00 | 227 | 10:00 | Rajshahi | 228 | 18:00 | 219 | 12:00
| BIPTC | 233 | 18:00 | 224 | 01:00 | Rampal | 232 | 18:00 | 225 | 00:00
| Bogura | 227 | 18:00 | 216 | 19:30 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 240 | 21:00 | 236 | 03:00 | Rampura | 231 | 02:00 | 223 | 09:00
| BSRM | 237 | 23:00 | 223 | 09:00 | Shikalbaha | 235 | 19:30 | 22 | 04:00
| Cumilla(N) | 231 | 20:00 | 223 | 09:00 | Shyampur | 230 | 06:00 | 223 | 10:00
| Fenchuganj | 235 | 20:00 | 231 | 13:00 | Siddhirganj | 232 | 00:00 | 226 | 10:00
| Ghorashal | 235 | 00:00 | 230 | 15:00 | Sirajgonj | 235 | 18:00 | 231 | 02:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 228 | 00:00 | 227 | 10:00
| GPH | 234 | 20:00 | 224 | 09:00 | Tongi | 232 | 04:00 | 222 | 09:00
| Haripur | 231 | 21:00 | 224 | 11:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 134 | 09:00 | 126 | 10:00 | Lalbag | 136 | 06:00 | 130 | 11:00
| Agargaon | 134 | 06:00 | 127 | 10:00 | Lalmonirhat | 128 | 17:00 | 115 | 01:00
| Agrabad | 135 | 00:00 | 128 | 14:00 | Madanganj | 132 | 07:00 | 126 | 09:00
| AKS | 132 | 00:00 | 127 | 09:00 | Madaripur | 130 | 06:00 | 128 | 00:00
| Aminbazar | 134 | 00:00 | 124 | 11:00 | Madartek | 133 | 03:00 | 126 | 10:00
| Amnura | 140 | 15:00 | 120 | 01:00 | Madunaghat | 137 | 20:00 | 130 | 14:00
| Ashuganj | 139 | 07:00 | 136 | 01:00 | Magura | 135 | 06:00 | 127 | 22:00
| Bagerhat | 130 | 13:00 | 122 | 00:00 | Mahasthangarh | 134 | 17:00 | 123 | 07:00
| Bakulia | 136 | 00:00 | 131 | 09:00 | Manikganj | 134 | 19:30 | 125 | 10:00
| Banani | 134 | 06:00 | 126 | 10:00 | Maniknagar | 134 | 00:00 | 129 | 10:00
| Bangabhaban | 133 | 00:00 | 129 | 10:00 | Matarbari | 128 | 15:00 | 115 | 01:00
| Barapukuria | 135 | 17:00 | 124 | 02:00 | Matuail | 132.2 | 23:00 | 121 | 04:00
| Barguna | 139 | 19:00 | 133 | 05:00 | Millgate | 134 | 02:00 | 126 | 10:00
| Barishal | 138 | 19:00 | 132 | 07:00 | Mirpur | 133 | 00:00 | 127 | 09:00
| Barishal-230 | 137 | 20:00 | 133 | 00:00 | Mithapukur | 131 | 17:00 | 12 | 13:00
| Baroaulia | 137 | 23:00 | 129 | 10:00 | Modern | 135 | 00:00 | 129 | 13:00
| Baroirhat | 130 | 18:00 | 121 | 07:00 | Mogbazar | 135 | 02:00 | 127 | 10:00
| Bashundhara | 134 | 00:00 | 126 | 10:00 | Mongla | 130 | 13:00 | 123 | 00:00
| BashundharaCement | 132 | 07:00 | 126 | 09:00 | Motijheel | 133 | 00:00 | 129 | 10:00
| Beanibazar | 128 | 07:00 | 123 | 18:30 | Munshiganj | 131 | 01:00 | 126 | 10:00
| Benapole | 135 | 18:00 | 126 | 00:00 | Mymensingh | 135 | 22:00 | 115 | 00:00
| Bhaluka | 123 | 06:00 | 119 | 00:00 | Naogaon | 130 | 18:00 | 118 | 01:00
| Bhandaria | 138 | 18:30 | 124 | 00:00 | Narail | 137 | 17:00 | 126 | 19:30
| Bhangura | 135 | 18:00 | 130 | 00:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 134 | 18:00 | 131 | 00:00 | Narshingdi | 126 | 18:00 | 121 | 10:00
| Bheramara(GK) | 136 | 18:00 | 131 | 00:00 | Natore | 135 | 18:00 | 128 | 00:00
| Bhulta | 125 | 05:00 | 121 | 11:00 | Nawabganj | 136 | 06:00 | 130 | 10:00
| Bog-Sherpur | 130 | 23:00 | 120 | 21:00 | Netrakona | 132 | 00:00 | 118 | 04:00
| Bogura | 136 | 18:00 | 128 | 01:00 | New | 135 | 00:00 | 127 | 10:00
| Bogura-230 | 137 | 18:00 | 127 | 04:00 | Niamatpur | 131 | 17:00 | 115 | 12:00
| Brahmanbaria | 127 | 12:00 | 121 | 02:00 | Noapara | 134 | 18:00 | 127 | 01:00
| Cantonment | 133 | 06:00 | 126 | 11:00 | Pabna | 133 | 18:00 | 128 | 10:00
| Chandpur | 133 | 18:00 | 115 | 06:00 | Palashbari | 130 | 17:00 | 116 | 01:00
| Chandraghona | 136 | 20:00 | 130 | 14:00 | Panchagarh | 129 | 17:00 | 107 | 08:00
| Chapai | 128 | 17:00 | 121 | 21:00 | Patuakhali | 142 | 19:00 | 133 | 03:00
| Charsaidpur | 132 | 01:00 | 127 | 10:00 | Payra | 139 | 00:00 | 137 | 02:00
| Chauddagram | 131 | 23:00 | 121 | 00:00 | PHP | 128 | 12:00 | 120 | 01:00
| Chhatak | 129 | 07:00 | 124 | 00:00 | Postogola | 134 | 00:00 | 128 | 10:00
| Chowmuhani | 127 | 18:00 | 113 | 00:00 | Purbachal | 134 | 03:00 | 126 | 10:00
| Chuadanga | 132 | 16:00 | 121 | 00:00 | Purbasadipur | 128 | 17:00 | 109 | 02:00
| Coxsbazar | 128 | 12:00 | 116 | 00:00 | Rahim | 132 | 00:00 | 128 | 11:00
| Cumilla(N) | 133 | 20:00 | 127 | 01:00 | Rajbari | 128 | 18:00 | 124 | 01:00
| Cumilla(S) | 131 | 05:00 | 124 | 15:00 | Rajendrapur | 136 | 19:30 | 126 | 11:00
| Daudkandi | 130 | 18:00 | 126 | 02:00 | Rajshahi | 136 | 18:00 | 129 | 10:00
| Dhaka | 134 | 23:00 | 127 | 10:00 | Rajshahi-230 | 136 | 18:00 | 119 | 21:00
| Dhamrai | 135 | 23:00 | 130 | 11:00 | Ramganj | 127 | 12:00 | 111 | 06:00
| Dhanmondi | 133 | 00:00 | 128 | 10:00 | Rampur | 135 | 22:00 | 127 | 13:00
| Dohazari | 133 | 12:00 | 128 | 00:00 | Rampura | 134 | 23:00 | 126 | 10:00
| Faridpur | 128 | 13:00 | 125 | 00:00 | Rangamati | 136 | 23:00 | 131 | 09:00
| Fatullah | 130 | 20:00 | 125 | 09:00 | Rangpur | 130 | 18:00 | 116 | 05:00
| Fenchuganj | 133 | 16:00 | 131 | 00:00 | Ruppur | 134 | 05:00 | 131 | 00:00
| Feni | 129 | 18:00 | 121 | 18:30 | Saidpur | 131 | 17:00 | 112 | 02:00
| Ghorashal | 138 | 00:00 | 136 | 15:00 | Satkhira | 131 | 18:00 | 122 | 00:00
| Goalpara | 135 | 18:00 | 128 | 00:00 | Satmasjid | 133 | 06:00 | 126 | 11:00
| Gollamari | 134 | 18:00 | 127 | 01:00 | Savar | 133 | 13:00 | 126 | 09:00
| Gopalganj | 132 | 20:00 | 126 | 03:00 | Shahjadpur | 137 | 17:00 | 133 | 01:00
| Gopalganj-400 | 159 | 20:00 | 126 | 10:00 | Shahjibazar | 129 | 12:00 | 124 | 22:00
| Gulshan | 133 | 05:00 | 126 | 10:00 | Shahmirpur | 136 | 21:00 | 129 | 14:00
| Halishahar | 136 | 21:00 | 128 | 14:00 | Shariatpur | 130 | 18:00 | 126 | 00:00
| Haripur | 132 | 00:00 | 128 | 11:00 | Sherpur | 133 | 22:00 | 107 | 07:00
| HaripurSBU | 141 | 23:00 | 128 | 11:00 | Shikalbaha | 127 | 22:00 | 118 | 14:00
| Hasnabad | 134 | 00:00 | 130 | 09:00 | Shikalbaha-230 | 136 | 19:30 | 132 | 01:00
| Hathazari | 138 | 20:00 | 132 | 09:00 | Shitalakhya | 133 | 00:00 | 127.1 | 10:00
| Ishurdi | 135 | 18:00 | 131 | 01:00 | Sholosohor | 136 | 23:00 | 129 | 09:00
| Jaldhaka | 129 | 17:00 | 112 | 01:00 | Shyampur | 129 | 18:00 | 124 | 10:00
| Jamalpur | 133 | 22:00 | 111 | 06:00 | Shyampur-230 | 130 | 23:00 | 124 | 10:00
| Jashore | 134 | 18:00 | 126 | 00:00 | Siddhirganj | 133 | 23:00 | 129 | 09:00
| Jhenaidah | 137 | 18:00 | 130 | 22:00 | Sirajganj | 132 | 23:00 | 122 | 21:00
| Jhenaidah-230 | 138 | 18:00 | 130 | 00:00 | Sonargaon | 132 | 00:00 | 127 | 10:00
| Joydebpur | 140 | 23:00 | 129 | 10:00 | Sreemongol | 129 | 07:00 | 125 | 21:00
| Joypurhat | 128 | 18:00 | 115 | 12:00 | Sreepur | 128 | 00:00 | 126 | 10:00
| Juldah | 137 | 20:00 | 131 | 04:00 | Srinagar | 135 | 06:00 | 130 | 09:00
| Kabirpur | 137 | 19:30 | 123 | 10:00 | SSM | 140 | 20:00 | 132 | 10:00
| Kachua | 133 | 20:00 | 117 | 06:00 | Sunamganj | 126 | 08:00 | 120 | 20:00
| Kaliakoir | 137 | 13:00 | 131 | 10:00 | Sylhet | 130 | 03:00 | 127 | 22:00
| Kallyanpur | 130 | 03:00 | 112 | 19:00 | Tangail | 132 | 00:00 | 125 | 04:00
| Kalurghat | 137 | 20:00 | 130 | 09:00 | Thakurgaon | 128 | 17:00 | 105 | 08:00
| Kamrangirchar | 136 | 04:00 | 123 | 10:00 | TK | 135 | 00:00 | 132 | 06:00
| Kaptai | N/A | N/A | N/A | N/A | Tongi | 137 | 04:00 | 129 | 09:00
| Kazla | 134 | 04:00 | 128 | 11:00 | Ullon | 134 | 00:00 | 127 | 10:00
| Keranigonj | 136 | 06:00 | 131 | 10:00 | Uttara | 134 | 21:00 | 127 | 10:00
| Khagrachori | 135 | 00:00 | 130 | 14:00 | UttaraNew | 134 | 05:00 | 123 | 12:00
| Khulna | 134 | 17:00 | 127 | 00:00 | Zigatola | 136 | 06:00 | 131 | 10:00
| Khulna(S) | 134 | 18:00 | 128 | 00:00
| Khulshi | 134 | 21:00 | 127 | 10:00
| Kishoreganj | 129 | 07:00 | 1 | 05:00
| Kodda | 137 | 15:00 | 127 | 10:00
| KSRM | 137 | 21:00 | 129 | 09:00
| Kulaura | 131 | 07:00 | 129 | 00:00
| Kurigram | 128 | 17:00 | 113 | 02:00
| Kushtia | 135 | 18:00 | 129 | 21:00

## L-Curve
Date | 2023-08-16
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 740 | 6665 | 5812 | 12477 |  |  |  | QF-LDC-11
0:30 | 850 | 6918 | 5657 | 12575 | Date: | 2023-08-16
1:00 | 960 | 7171 | 5502 | 12673
1:30 | 945 | 7075.5 | 5391.5 | 12467
2:00 | 930 | 6980 | 5281 | 12261
2:30 | 915 | 6889.5 | 5286 | 12175.5 | [5 empty] | Gen. at Eve. Peak | 14311 | 14311 MW (21:00 )
3:00 | 900 | 6799 | 5291 | 12090 | [6 empty] | 21:00
3:30 | 880 | 6771.5 | 5141.5 | 11913 | [5 empty] | Gen. at Day Peak | 12424 | 12424 MW (12:00 )
4:00 | 860 | 6744 | 4992 | 11736 | [6 empty] | 12:00
4:30 | 865 | 6729 | 4978.5 | 11707.5 | [5 empty] | Highest Generation | 14311
5:00 | 870 | 6714 | 4965 | 11679 | [6 empty] | 21:00
5:30 | 825 | 6650.5 | 4959.5 | 11610
6:00 | 780 | 6587 | 4954 | 11541
6:30 | 770 | 6547 | 4942 | 11489
7:00 | 760 | 6507 | 4930 | 11437
7:30 | 775 | 6504 | 5007 | 11511
8:00 | 790 | 6501 | 5084 | 11585
8:30 | 845 | 6546.5 | 5217 | 11763.5
9:00 | 900 | 6592 | 5350 | 11942
9:30 | 930 | 6726 | 5408.5 | 12134.5
10:00 | 960 | 6860 | 5467 | 12327
10:30 | 945 | 6665.5 | 5633 | 12298.5
11:00 | 930 | 6471 | 5799 | 12270
11:30 | 940 | 6517 | 5830 | 12347
12:00 | 950 | 6563 | 5861 | 12424
12:30 | 965 | 6665.5 | 5870 | 12535.5
13:00 | 980 | 6768 | 5879 | 12647
13:30 | 990 | 6794 | 5823 | 12617
14:00 | 1000 | 6820 | 5767 | 12587
14:30 | 980 | 6789 | 5739.5 | 12528.5
15:00 | 960 | 6758 | 5712 | 12470
15:30 | 940 | 6660.5 | 5692 | 12352.5
16:00 | 920 | 6563 | 5672 | 12235
16:30 | 890 | 6620 | 5606 | 12226
17:00 | 860 | 6677 | 5540 | 12217
17:30 | 885 | 6683 | 5550 | 12233
18:00 | 910 | 6689 | 5560 | 12249
18:30 | 745 | 7104.5 | 5911.5 | 13016
19:00 | 580 | 7520 | 6263 | 13783
19:30 | 590 | 7815 | 6303 | 14118
20:00 | 590 | 7871 | 6283 | 14154 |  |  |  | Executive Engineer
20:30 | 725 | 7911.5 | 6321 | 14232.5 |  |  |  | Network Operation Division
21:00 | 860 | 7952 | 6359 | 14311
21:30 | 860 | 7851 | 6297.5 | 14148.5
22:00 | 860 | 7750 | 6236 | 13986 |  |  |  |  | Page 6 of 7
22:30 | 815 | 7639.5 | 6145.5 | 13785
23:00 | 770 | 7529 | 6055 | 13584
23:30 | 755 | 7097 | 5933.5 | 13030.5
24:00 | 740 | 6665 | 5812 | 12477
14311 MW (21:00 )
12424 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-08-16 |  | Energy |  | 304131894
QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 4103 | 813 | 1841 | 0 | 1793 | 3299 | 201 | 50 | 267 | 110 | 0 | 0 | 1120.215
0:30 | 4329 | 837 | 1897.5 | 0 | 1607 | 3316 | 202 | 25 | 230.5 | 131 | 0 | 0 | 716.25 |  | Date: | 43692
1:00 | 4555 | 861 | 1954 | 0 | 1421 | 3333 | 203 | 0 | 194 | 152 | 0 | 0 | 312.285
1:30 | 4550 | 861 | 1955.5 | 0 | 1227 | 3342 | 202.5 | 0 | 183 | 146 | 0 | 0 | 303.69 | [8 empty] | Total Energy | 304.1319 | 304.1319 | Total Energy Gen 304.132 MKWHr Energy Not Served 9.651 MKWHr Energy Requirement 313.783 MKWHr
2:00 | 4545 | 861 | 1957 | 0 | 1033 | 3351 | 202 | 0 | 172 | 140 | 0 | 0 | 295.095 | [8 empty] | Energy not Served | 9.6512 | 9.6512
2:30 | 4558 | 886 | 1958.5 | 0 | 946 | 3332 | 201 | 0 | 159 | 135 | 0 | 0 | 295.5725 | [8 empty] | Energy Requirement | 313.7831 | 313.7831
3:00 | 4571 | 911 | 1960 | 0 | 859 | 3313 | 200 | 0 | 146 | 130 | 0 | 0 | 296.05
3:30 | 4554 | 911 | 1960 | 0 | 839.5 | 3182 | 200 | 0 | 137.5 | 129 | 0 | 0 | 274.085 | [7 empty] | Shortage
4:00 | 4537 | 911 | 1960 | 0 | 820 | 3051 | 200 | 0 | 129 | 128 | 0 | 0 | 252.12
4:30 | 4548 | 911 | 1945.5 | 0 | 797 | 3049.5 | 200.5 | 0 | 129 | 127 | 0 | 0 | 231.5875
5:00 | 4559 | 911 | 1931 | 0 | 774 | 3048 | 201 | 0 | 129 | 126 | 0 | 0 | 211.055
5:30 | 4547.5 | 911 | 1921.5 | 0 | 762.5 | 3026.5 | 201 | 0 | 112 | 123 | 5 | 0 | 148.025
6:00 | 4536 | 911 | 1912 | 0 | 751 | 3005 | 201 | 0 | 95 | 120 | 10 | 0 | 84.995
6:30 | 4572 | 911 | 1889.5 | 0 | 693.5 | 3021 | 159.5 | 0 | 95 | 119 | 28.5 | 0 | 82.13 | [6 empty] | Coal
7:00 | 4608 | 911 | 1867 | 0 | 636 | 3037 | 118 | 0 | 95 | 118 | 47 | 0 | 79.265
7:30 | 4564.5 | 911.5 | 1902 | 0 | 672 | 3040 | 114.5 | 0 | 103.5 | 121 | 82 | 0 | 77.8325 | [5 empty] | Oil
8:00 | 4521 | 912 | 1937 | 0 | 708 | 3043 | 111 | 0 | 112 | 124 | 117 | 0 | 76.4
8:30 | 4541.5 | 912 | 1959 | 0 | 748.5 | 3080.5 | 113.5 | 0 | 112 | 122 | 174.5 | 0 | 80.22
9:00 | 4562 | 912 | 1981 | 0 | 789 | 3118 | 116 | 0 | 112 | 120 | 232 | 0 | 84.04
9:30 | 4527 | 912 | 2013 | 0 | 848.5 | 3209.5 | 158.5 | 0 | 112 | 124 | 230 | 0 | 100.7525
10:00 | 4492 | 912 | 2045 | 0 | 908 | 3301 | 201 | 0 | 112 | 128 | 228 | 0 | 117.465
10:30 | 4300.5 | 911.5 | 2071 | 0 | 1074 | 3184 | 184 | 50 | 111 | 133 | 279.5 | 0 | 240.1825
11:00 | 4109 | 911 | 2097 | 0 | 1240 | 3067 | 167 | 100 | 110 | 138 | 331 | 0 | 362.9
11:30 | 4028 | 911 | 2088 | 0 | 1281.5 | 3172 | 184 | 75 | 119.5 | 143 | 344.5 | 0.5 | 456.49
12:00 | 3947 | 911 | 2079 | 0 | 1323 | 3277 | 201 | 50 | 129 | 148 | 358 | 1 | 550.08
12:30 | 3974 | 911 | 2081.5 | 0 | 1387 | 3295 | 201 | 35 | 162 | 153 | 335.5 | 0.5 | 496.1225
13:00 | 4001 | 911 | 2084 | 0 | 1451 | 3313 | 201 | 20 | 195 | 158 | 313 | 0 | 442.165
13:30 | 4001 | 911 | 2084 | 0 | 1451 | 3313 | 201 | 20 | 195 | 158 | 313 | 0 | 442.165
14:00 | 4001 | 911 | 2084 | 0 | 1451 | 3313 | 201 | 20 | 195 | 158 | 313 | 0 | 442.165
14:30 | 3994.5 | 911 | 2061 | 0 | 1448.5 | 3305 | 200 | 33 | 220 | 160 | 223 | 2.5 | 569.6575
15:00 | 3988 | 911 | 2038 | 0 | 1446 | 3297 | 199 | 46 | 245 | 162 | 133 | 5 | 697.15
15:30 | 4004.5 | 911 | 2004 | 0 | 1446 | 3218 | 199 | 48 | 259 | 160 | 98 | 5 | 642.2375
16:00 | 4021 | 911 | 1970 | 0 | 1446 | 3139 | 199 | 50 | 273 | 158 | 63 | 5 | 587.325
16:30 | 4062 | 911 | 1977 | 0 | 1491.5 | 3050.5 | 199 | 50 | 277 | 155 | 47.5 | 5.5 | 500.6625
17:00 | 4103 | 911 | 1984 | 0 | 1537 | 2962 | 199 | 50 | 281 | 152 | 32 | 6 | 414
17:30 | 4058.5 | 911 | 1943 | 0 | 1629 | 2972.5 | 199 | 50 | 292.5 | 148 | 25.5 | 4 | 302.9775
18:00 | 4014 | 911 | 1902 | 0 | 1721 | 2983 | 199 | 50 | 304 | 144 | 19 | 2 | 191.955
18:30 | 4067.5 | 911 | 2013 | 0 | 2145.5 | 3075 | 200 | 50 | 391.5 | 151 | 9.5 | 2 | 309.42
19:00 | 4121 | 911 | 2124 | 0 | 2570 | 3167 | 201 | 50 | 479 | 158 | 0 | 2 | 426.885
19:30 | 4170 | 795 | 2148 | 0 | 2748 | 3277 | 201 | 50 | 574 | 152 | 0 | 3 | 450.2825
20:00 | 4191 | 795 | 2124 | 0 | 2797 | 3264 | 201 | 50 | 580 | 148 | 0 | 4 | 473.68
20:30 | 4228.5 | 795 | 2125 | 0 | 2821.5 | 3291 | 201 | 50 | 578.5 | 139 | 0 | 3 | 446.4625
21:00 | 4266 | 795 | 2126 | 0 | 2846 | 3318 | 201 | 50 | 577 | 130 | 0 | 2 | 419.245
21:30 | 4259.5 | 795 | 2070.5 | 0 | 2773.5 | 3322 | 201 | 50 | 552 | 122 | 0 | 3 | 502.8075
22:00 | 4253 | 795 | 2015 | 0 | 2701 | 3326 | 201 | 50 | 527 | 114 | 0 | 4 | 586.37
22:30 | 4255.5 | 804 | 1927 | 0 | 2572 | 3326.5 | 201 | 50 | 526.5 | 120 | 0 | 2.5 | 778.325
23:00 | 4258 | 813 | 1839 | 0 | 2443 | 3327 | 201 | 50 | 526 | 126 | 0 | 1 | 970.28
23:30 | 4180.5 | 813 | 1840 | 0 | 2118 | 3313 | 201 | 50 | 396.5 | 118 | 0 | 0.5 | 1045.2475 |  | Max Temp. in Dhaka |  | 32° C
24:00 | 4103 | 813 | 1841 | 0 | 1793 | 3299 | 201 | 50 | 267 | 110 | 0 | 0 | 1120.215
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 304.132 MKWHr Energy Not Served 9.651 MKWHr Energy Requirement 313.783 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-08-16
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 128 | 127 | 125 | 125 | 126 | 126 | 78 | 71 | 76 | 126 | 92 | 126 | 126 | 126 | 126 | 126 | 126 | 126 |  | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 2786160
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 40 | 40 | 40 | 75 | 75 | 75 | 75 | 75 | 73 | 73 | 73 | 73 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1676000
3 | Chattogram TPP-1 | 120 | 115 | 115 | 123 | 123 | 120 | 120 | 118 | 115 | 118 | 118 | 113 | 120 | 113 | 118 | 117 | 116 | 118 |  | 118 | 118 | 118 | 115 | 118 | 118 | 115 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 25 | 25 |  | 16 | 25 | 8 | 8 | 261828
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 3 | 4 | 6 | 11 | 17 | 7 | 6 | 11 | 9 | 5 | 3 | 0 | [8 empty] | 89640
6 | Sikalbaha 225MW CCPP (Gas) | 223 | 222 | 226 | 224 | 224 | 226 | 223 | 224 | 224 | 222 | 222 | 222 | 223 | 220 | 220 | 220 | 221 | 222 |  | 220 | 220 | 224 | 222 | 220 | 224 | 221 | 5328187
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 34 | 34 | 34 | 34 | 34 | 0 | [5 empty] | 17 | 16 | 16 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 34 | 541839
12 | Hathazari 100 MW peaking PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 17 | 35 | 35 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 675257
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 64 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1262909
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 45 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 45 | 47 | 47 | 47 | 38 | 38 | 38 | 38 |  | 44 | 46 | 47 | 47 | 47 | 47 | 47 | 1075648
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 126 | 130 | 157 | 103 | 103 | 96 | 102 | 102 | 127 | 138 | 156 | 131 | 124 | 125 | 102 | 101 | 100 | 119 |  | 98 | 77 | 75 | 75 | 73 | 70 | 75 | 2863000
17 | Siddhirganj 335 MW CCPP | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 326 | 327 | 328 | 326 | 318 | 320 | 280 | 315 | 313 | 314 | 280 |  | 318 | 316 | 318 | 318 | 318 | 285 | 260 | 7419803
18 | Kodda 300 MW PP Unit-2 (Summit) | 65 | 37 | [7 empty] | 5 | 60 | 63 | 133 | 145 | 102 | 62 | 65 | 75 |  | 140 | 145 | 145 | 145 | 145 | 145 | 82 | 1648473
19 | Ashuganj 195 MW PP (APSCL-United) | [25 empty] | 0 | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 170 | 170 | 170 | 170 | 170 | 170 | 120 | 120 | 130 | 125 | 138 | 116 | 118 | 130 | 130 | 130 | 122 | 130 |  | 190 | 180 | 170 | 170 | 150 | 140 | 160 | 3523719
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4299750
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 20 | 20 | 20 | 20 | 20 | 20 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 0 | 227736
33 | Ashuganj 225 MW CCPP | 174 | 180 | 178 | 178 | 171 | 180 | 145 | 168 | 179 | 157 | 170 | 192 | 203 | 200 | 186 | 190 | 186 | 192 |  | 181 | 180 | 184 | 187 | 179 | 179 | 185 | 4358000
34 | Ashuganj 450 MW CCPP(South) | 270 | 270 | 270 | 270 | 290 | 270 | 340 | 270 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 6247000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 300 | 280 | 300 | 280 | 280 | 280 | 270 | 270 | 270 | 280 | 280 | 280 | 310 | 280 |  | 310 | 325 | 280 | 280 | 310 | 280 | 280 | 7233500
| Ashuganj 420 MW CCPP(East) | 240 | 240 | 240 | 240 | 240 | 240 | 280 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 6036900
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 406 | 384 | 359 | 355 | 355 | 355 | 355 | 356 | 381 | 398 | 400 | 400 | 383 | 400 | 398 | 402 | 402 | 398 |  | 371 | 396 | 401 | 404 | 404 | 398 | 368 | 9367550
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 400 | 400 | 400 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 420 | 10112000
41 | Haripur 360 MW CCPP(HPL) | 307 | 306 | 306 | 307 | 307 | 307 | 307 | 306 | 307 | 320 | 332 | 331 | 331 | 331 | 324 | 324 | 323 | 291 |  | 331 | 332 | 332 | 332 | 332 | 301 | 322 | 7648000
42 | RPCL 210MW CCPP | 153 | 151 | 152 | 151 | 151 | 151 | 151 | 152 | 151 | 119 | 104 | 81 | 81 | 82 | 81 | 84 | 84 | 84 |  | 82 | 84 | 85 | 85 | 84 | 84 | 84 | 2626560
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 4 | 15 | 15 | 43 | 49 | 42 | 32 | 44 | 38 | 15 | 4 | 1 | [8 empty] | 298720
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1021000
45 | Fenchugonj CCPP Phase-2 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960360
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 45 | 55 | 58 | 56 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 45 | 45 | 50 | 50 | 50 | 50 | 55 | 1137984
48 | Shahjibazar 86 MW PP (Shahjibazar) | 81 | 81 | 75 | 75 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 69 | 69 | 75 | 81 | 81 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1772160
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 178 | 178 | 178 | 178 | 178 |  | 179 | 179 | 178 | 178 | 178 | 180 | 181 | 4693380
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 388000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 |  | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 238500
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 5 | 5 | 5 |  |  | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 158000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200600
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 572088
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 285 | 295 | 295 | 305 | 285 | 290 | 305 | 295 | 300 | 305 | 290 | 285 | 285 | 315 | 290 | 290 | 280 |  | 300 | 320 | 290 | 290 | 300 | 300 | 280 | 7207500
| Bibiyana South 400 MW | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 340 | 360 | 360 | 360 | 360 | 360 | 340 |  | 360 | 360 | 350 | 350 | 350 | 350 | 350 | 8607000
58 | Nababganj 55 MW PP (Southern power ) | [12 empty] | 17 | 17 | 17 | 17 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 440115
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 4 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 145200
60 | Barabkunda 22 MW PP (Regent) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 220704
61 | Narshingdi 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 |  | 17 |  |  | 16 | 19 | 19 |  | 19 |  |  | 19 | 19 | 19 | 19 | 367704
62 | Tangail 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [9 empty] | 16 | 16 | 16 | 16 | 266364
63 | Impoprt (Tripura) | 152 | 140 | 130 | 128 | 126 | 120 | 118 | 124 | 120 | 128 | 138 | 148 | 158 | 164 | 162 | 158 | 152 | 144 |  | 158 | 152 | 148 | 130 | 114 | 126 | 110 | 3322560
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 17 | 7 | 8 | 6 | 2 | 6 | 7 | 5 | 11 | 20 | 13 |  | 17 | 21 | 24 | 26 | 21 | 24 | 35 | 603840
65 | Feni 22 MW PP (Doreen) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 14 | 14 | 13 | 13 | 13 | 14 | 14 | 14 | 16 | 16 |  | 16 | 16 | 16 | 15 | 15 | 15 | 15 | 332640
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 252000
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 33 | 24 | 33 | 33 | 33 | 33 | 33 | 33 |  | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 671600
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 498400
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456000
70 | Summit Madhabdi | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 2 | 0 | 0 | 19 | 19 | 18 | 18 | 15 | 15 | 15 |  |  | 12 | 16 | 17 | 20 | 20 | 20 | 20 | 338040
71 | Maona 33 MW PP(Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 25 | 25 |  | 0 | 0 | 25 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 491040
72 | Rupganj 33 MW PP(Summit) | 32 | 32 | 32 | 32 | 16 | 32 | 32 | 31 | 32 | 32 | 32 | 24 | 24 | 31 | 31 | 31 | 31 | 31 |  | 31 | 31 | 31 | 31 | 31 | 32 | 32 | 717800
73 | Ghorashal 108 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 305272
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [10 empty] | 17 | 17 | 17 | 17 | 283860
| Chowmuhani 113 MW | 9 | 9 | 9 | 7 | 5 | 7 | 2 |  | 3 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 24 |  | 27 | 29 | 29 | 28 | 28 | 21 | 9 | 298200
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | [6 empty] | 12 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 72 | 120 | 162 | 162 | 162 | 162 | 162 | 1340640
77 | Siddhirganj 100 PP(Dutch Bangla) | 72 | 40 | [7 empty] | 8 | 42 | 42 | 42 | 33 | 33 | 25 | 25 | 25 |  | 40 | 40 | 36 | 33 | 33 | 33 | 20 | 552000
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 272640
79 | Kodda 150 MW PP | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 64 | 64 | 64 | 64 | 16 | 16 | 16 | 854400
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [26 empty] | 0
| Gazipur 100 MW PP | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 52 | 52 | 52 | 52 | 60 | 52 | 52 |  | 88 | 88 | 88 | 88 | 88 | 88 | 35 | 1120762
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 2 | 3 | 3 | 2 | 2 | 3 | 3 | 1 | 0 | [9 empty] | 21121
| Jodiac Power | 36 | 36 | 36 | 36 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 517027
| Karnaphuli Power Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1346540
82 | Madanganj 102 PP(Summit) | 25 | 10 | [7 empty] | 2 | 17 | 30 | 34 | 34 | 34 | 25 | 17 | 15 |  | 34 | 34 | 34 | 31 | 17 | 17 | 17 | 317269
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 26 | [8 empty] | 9 | 41 | 46 | 53 | 58 | 57 | 57 | 55 | 56 |  | 50 | 56 | 56 | 56 | 57 | 57 | 45 | 811731
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 51 | 51 | 48 | 45 | 48 | 50 | 20 | 17 | 9 | 8 | 9 | 9 | 8 | 8 | 9 | 16 | 17 | 10 |  | 9 | 9 | 8 | 9 | 8 | 8 | 8 | 473280
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 |  |  |  | 17 | 17 | 17 | 17 | 17 | 17 | 27 | 34 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 52 | 17 | 753600
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 46 | 35 | 35 | 46 | 35 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 35 | 903000
92 | Fenchuganj 44 MW (Energyprima) | 46 | 46 | 46 | 46 | 43 | 46 | 46 | 46 | 46 | 46 | 43 | 43 | 46 | 45 | 45 | 45 | 45 | 45 |  | 45 | 45 | 46 | 46 | 46 | 46 | 46 | 1086696
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1189540
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 24 | 24 | 24 | 24 | 16 | 24 | 24 | 24 |  | 24 | 33 | 50 | 42 | 42 | 42 | 8 | 600624
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 28 |  | 39 | 46 | 46 | 46 | 46 | 46 | 46 | 392640
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 4 |  | 11 | 11 | 9 | 11 | 11 |  | 0 | 50880
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 22 | 25 | 15 | 15 | 15 | 15 | 15 | 386220
100 | Manikganj 55 MW PP (Northern) | [9 empty] | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 17 | 0 | 445762
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 80 | 80 | 80 | 112 | 112 | 112 | 112 | 112 | 112 | 80 | 112 | 112 | 112 | 80 |  | 112 | 112 | 112 | 112 | 112 | 80 | 80 | 2436954
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 0 | 2 | 1 | 0 | 0 | [8 empty] | 11600
103 | Kamalaghat 54 MW PP(Banco Energy) | [10 empty] | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 357120
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 84 | 84 | 83 | 83 | 83 | 18 | 18 | 693600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 36 | 69 | 72 | 70 | 75 | 96 | 98 | 71 | 54 | 53 | 107 |  | 134 | 149 | 149 | 149 | 149 | 94 | 35 | 1778112
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 27 | 29 | 31 | 33 | 34 | 35 |  | 37 | 50 | 50 | 50 | 50 | 50 | 22 | 745920
116 | Chandpur 200 MW (Desh energy) | 49 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 55 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 73 |  | 104 | 104 | 104 | 103 | 103 | 103 | 54 | 1515840
117 | Ashuganj 150 MW PP (Midland) | 5 | 6 | 6 | 5 | 6 |  |  |  |  | 1 | 2 | 5 | 5 | 5 | 5 | 5 | 8 | 10 |  | 23 | 50 | 50 | 87 | 95 | 97 | 97 | 531927
118 | Bibiyana-III 400 MW CCPP | 368 | 368 | 367 | 367 | 378 | 367 | 384 | 367 | 368 | 367 | [5 empty] | 15 | 80 | 80 |  | 100 | 151 | 220 | 232 | 232 | 380 | 237 | 5347000
| Jamalpur 115 MW PP (United) | 68 | 69 | 69 | 69 | 69 | 78 | 69 | 69 | 68 | 67 | 67 | 65 | 65 | 65 | 65 | 67 | 67 | 77 |  | 85 | 85 | 85 | 85 | 85 | 69 | 69 | 1710000
| Anwara 300 MW PP (United) | 71 | 70 | 70 | 70 | 70 | 30 | 30 | 66 | 70 | 75 | 75 | 78 | 73 | 83 | 73 | 70 | 87 | 121 |  | 270 | 272 | 279 | 285 | 135 | 87 | 88 | 2391164
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 50 | 50 | 50 | 50 | 25 | 690240
| Anlima Energy Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 17 | 27 | 34 | 34 | 34 | 34 | 41 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 776564
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 443880
| Spectra Solar Plant Ltd. | [6 empty] | 3 | 9 | 18 | 21 | 30 | 23 | 17 | 14 | 16 | 8 | 4 | 2 | [8 empty] | 166288
| Chandpur 115(Doreen) | 17 | 18 | 17 | 18 | 17 | 18 | 17 | 18 | 18 | 23 | 63 | 72 | 72 | 72 | 72 | 72 | 72 | 85 |  | 115 | 115 | 115 | 101 | 103 | 115 | 67 | 1386240
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 432000
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 0 |  |  |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 36 | 127 | 140 | 140 | 140 | 140 | 17 | 859782
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4 | 5 | 5 | 6 | 2 |  | 2 | 3 | 4 | 2 | 4 | 1 | 0 | 28800
| Matarbari 2*600 MW (CPGCL) | 275 | 302 | 265 | 303 | 301 | 270 | 301 | 296 | 293 | 297 | 0 | 129 | 168 | 180 | 175 | 0 | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 0 | 2178545
120 | Eastern Zone Total | 7171 | 6980 | 6799 | 6744 | 6714 | 6587 | 6507 | 6501 | 6592 | 6860 | 6471 | 6563 | 6768 | 6820 | 6758 | 6563 | 6677 | 6689 |  | 7520 | 7815 | 7871 | 7952 | 7750 | 7529 | 6665 | 166294038
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 0 | [12 empty] | 16 | 32 | 40 | 32 |  | 58 | 64 | 65 | 65 | 65 | 65 | 0 | 430080
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL) | [10 empty] | 100 | 50 | 20 | 50 | 46 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 644920
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [15 empty] | 10 | 10 | 10 |  | 41 | 28 | 17 | 21 | 21 | 21 | 11 | 155520
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 404640
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 1 | 16 | 28 | 62 | 50 | 67 | 59 | 36 | 14 | 40 | 28 | 13 | 3 | [8 empty] | 440366
131 | Rampal 1320 MW (BIFPCL) | 375 | 375 | 376 | 376 | 377 | 377 | 377 | 377 | 378 | 374 | 377 | 373 | 381 | 377 | 382 | 375 | 376 | 490 |  | 518 | 519 | 518 | 517 | 519 | 520 | 519 | 9992727
132 | United Payra Power Ltd. | 150 | 17 | 17 | 0 | [5 empty] | 1 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 1226400
133 | Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 184 | 184 | 184 | 221 | 221 | 221 | 221 | 218 | 217 | 216 | 216 |  | 220 | 218 | 220 | 220 | 216 | 180 | 220 | 4846309
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 64 | 16 | [8 empty] | 16 | 16 | 32 | 64 | 48 | 48 | 48 | 48 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1075872
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 124 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 128 | 124 | 124 | 124 | 124 | 124 | 124 | 124 |  | 128 | 128 | 124 | 130 | 126 | 72 | 130 | 3020000
140 | Bhola 33 MW PP (Venture) | 33 | 32 | 31 | 30 | 29 | 27 | 27 | 22 | 21 | 20 | 20 | 22 | 24 | 26 | 27 | 23 | 24 | 23 |  | 32 | 32 | 32 | 32 | 34 | 34 | 34 | 651081
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [16 empty] | 8 | 8 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 112875
143 | Gopalganj 100 MW Peaking PP | 26 | 26 | [12 empty] | 5 | 12 | 20 | 30 |  | 40 | 46 | 50 | 42 | 41 | 40 | 38 | 345216
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 15 | 15 | [7 empty] | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 47 | 67 | 67 | 67 | 67 | 67 | 67 | 595152
146 | Bheramara HVDC | 861 | 861 | 911 | 911 | 911 | 911 | 911 | 912 | 912 | 912 | 911 | 911 | 911 | 911 | 911 | 911 | 911 | 911 |  | 911 | 795 | 795 | 795 | 795 | 813 | 813 | 21549090
147 | Bheramara 410 MW CCPP | 305 | 305 | 315 | 325 | 330 | 330 | 345 | 350 | 340 | 305 | 295 | 280 | 300 | 300 | 295 | 290 | 280 | 275 |  | 275 | 265 | 265 | 260 | 250 | 235 | 235 | 7221024
148 | Payra 1320 MW | 1244 | 1244 | 1244 | 940 | 940 | 930 | 930 | 940 | 1020 | 1170 | 1222 | 1244 | 1244 | 1200 | 1210 | 1244 | 1160 | 1100 |  | 1150 | 1244 | 1244 | 1244 | 1244 | 1244 | 1220 | 29685600
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 180 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 200 | 210 | 220 | 210 | 210 | 210 | 210 | 180 | 180 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4629500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [13 empty] | 16 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 0 | 335259
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 1 | 1 | 3 | 4 | 5 | 5 | 0 | 0 | 1 | 1 | 0 | [8 empty] | 25080
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 181 | 185 | 194 | 203 | 201 | 203 | 205 | 205 | 205 | 205 | 200 | 196 | 170 | 165 | 177 | 177 | 176 | 159 |  | 149 | 164 | 166 | 190 | 191 | 192 | 192 | 4767064
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 350 | 414 | 414 | 414 | 414 | 414 | 350 | 350 | 300 | 300 | 300 |  | 414 | 414 | 414 | 414 | 300 | 220 | 200 | 8336872
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 5 |  | 15 | 19 | 15 | 16 | 15 | 15 | 15 | 84905
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 193968
165 | Amnura 50 MW PP(Sinha) | 28 | 28 | 28 | 28 | [6 empty] | 28 | 28 | 28 | 28 | 28 | 28 | 14 | 14 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 477520
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [12 empty] | 20 | 22 | 22 | 15 | 15 | 15 |  | 15 | 20 | 23 | 23 | 23 | 23 | 15 | 206790
168 | Santahar 50 MW Peaking PP | [19 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 0 | 112146
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | [5 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 167654
170 | Chapainawabganj 100 MW Peaking PP | 24 | [11 empty] | 47 | 47 | 47 | 47 | 47 | 48 |  | 92 | 92 | 92 | 92 | 92 | 92 | 32 | 787184
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 | 35 | 35 |  | 3 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 50 | 50 | 50 | 50 | 50 | 35 | 921504
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 993792
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 41 | 41 | 48 | 49 |  | 49 | 49 | 49 | 49 | 49 | 34 | 34 | 913977
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 7 | 4 | 3 | 2 | 1 | 1 | 0 | [8 empty] | 22525
178 | Energypac Power Venture Thakurgaon Ltd. | [15 empty] | 5 | 36 | 36 |  | 75 | 75 | 75 | 75 | 75 | 75 | 0 | 502080
| Intraco Solar 30 MW | [5 empty] | 0 | 5 | 8 | 6 | 21 | 21 | 29 | 36 | 0 | 1 | 2 | 1 | 1 | [8 empty] | 119626
| Adani Power Jharkhanda Ltd | 1259 | 1260 | 1258 | 1262 | 1260 | 1258 | 1259 | 1260 | 1257 | 1260 | 1258 | 1311 | 1310 | 1308 | 1320 | 1310 | 1246 | 1213 |  | 1299 | 1314 | 1302 | 1357 | 1363 | 1363 | 1360 | 30861818
178 | Teesta Solar Limited | [5 empty] | 8 | 15 | 49 | 120 | 73 | 137 | 182 | 173 | 162 | 22 | 1 | 5 | 12 | [8 empty] | 981720