## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-08-18 | Friday
|  | Date (day): | 2023-08-18 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13177.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15312 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-08-17 | 2023-08-18 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 136 | 120 | 140 | 170
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 12 | 12 | 96 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 395 | 390 | 400 | 400 | 12
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 321 | 332 | 330 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 9 | 49 | 34 | 49 | 67 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 17 | 51 | 17 | 51 | 51 |  | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 15 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 23 | 33 | 33 | 33 | 15 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 20 | 20
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 62 | 37 | 93 | 93 | 117 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 25 | 38 | 24 | 38 |  | 62 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 316 | 318 | 330 | 330
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 33 | 102 | 16 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 35 | 17 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 32 | 16 | 64 | 85 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 35 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 37 | 38 | 40 | 40 |  | 40 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 22 | 8 | 32 | 32
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 24 | 8 | 25 | 27 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 65 | 148 | 65 | 145 | 155 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
33 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
34 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 72 | 149 | 70 | 149
35 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 88 | 35 | 88 | 17 |  | Fuel shortage
36 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 45 | 43 | 34 | 55 | 49 |  | Fuel shortage
37 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 162 | 54 | 162
38 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 31 | 0 | 35 | 0
39 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6063 | 5722 | 2481 | 2994 | 2620 | 3208 | 994 | 1197
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 119 | 123 | 120 | 120 |  | 60
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
41 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 0 | 8 | 25
42 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 14 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 40 | 6 | 47 | 3
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 167 | 211 | 211 | 211
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 218 | 224 | 225 | 225
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 68 | 68 | 68 | 68 | 37 |  | Fuel shortage
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 32 | 59 | 40 | 59 | 39 |  | Fuel shortage
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 32 | 32 | 34 | 34 |  | 68 | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 35 | 46 | 35 | 46 | 54 |  | Fuel shortage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 50 | 25 | 50 | 50 |  | Fuel shortage
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 10 | 10 | 10 | 10 | 12 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 6 | 33 | 42 | 30
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 12 | 0 | 12 | 96 |  | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 70 | 297 | 70 | 297 | 3 |  | Fuel shortage
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 41 | 55 | 55 | 55 | 55 |  | Engine problem.
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 50 | 25 | 50 | 50 |  | Fuel shortage
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 34 | 51 | 34 | 51 | 65 |  | Fuel shortage
60 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 17 | 125 | 17 | 142 | 21 |  | Fuel shortage
| SS Power I |  | Coal | SS Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 4 | 21 | 10 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2605 | 2545 | 951 | 1524 | 1077 | 1559 | 522 | 458
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 170 | 188 | 170 | 200 | 21 |  | Gas shortage
62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 270 | 280 | 280 | 80 |  | Gas shortage
63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 240 | 240 | 270 | 270 | 90 |  | Gas shortage
64 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 240 | 230 | 240 | 240 | 160 |  | Gas shortage
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 0 | 0 | 0 | 45 |  | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
69 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 8 | 135 | 6 | 150
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 32 | 38 | 47 | 47
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
72 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 51 | 103 | 51 | 100 | 100 |  | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 13 | 14 | 20 | 22
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 124 | 106 | 146 | 163
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 17 | 20 | 20 |  | 5 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Contract Expired
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 106 | 17 | 105 | 9 |  | Fuel shortage
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 29 | 9 | 28 | 85 |  | Fuel shortage
81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 72 | 96 | 72 | 115
| Cumilla Area Total |  |  |  |  | 3159 | 3096 | 1389 | 1675 | 1460 | 1852 | 837 | 205
83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 46 | 85 | 65 | 85 | 117 |  | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 16 | 16 | 16 |  | 6 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 18 | 147 | 95 | 142 | 58 |  | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 71 | 84 | 68 | 85 | 30 |  | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 46 | 0 | 50 | 0
90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 205 | 338 | 301.6 | 334 | 117 | 6
91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 39 | 40 | 42 | 42 |  | 48 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 112 | 112 |  | 51 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 50 | 50 | 50
96 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 40 | 45 | 46 | 46
97 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 3 | 11 | 11
98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 48 | 55 | 50 | 50 |  | 16
99 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 86 | 86 | 86
100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 179 | 181 | 180 | 180 |  | 51 | Machine problem
102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 17 | 17
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
103 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
104 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 300 | 300 | 300 |  |  | FGMO
105 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 260 | 80 | 350 | 350 |  | 50
106 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
107 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 350 | 350 | 360 | 360
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1559 | 1396 | 1681 | 1681 | 0 | 673
108 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 912 | 794 | 911 | 911
109 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 64 | 16 | 48 |  | 67 | Engine problem
110 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 5 | 21 | 0 | 40 |  | 14 | Engine problem
111 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
112 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 18 | 37 | 40 | 51 | 58 |  | Fuel shortage
113 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 300 | 210 | 290 | 290 | 120 |  | Gas shortage
114 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 8 | 8 | 32 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
115 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 35 | 35 | 70 |  | Fuel shortage
116 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 15 | 67 | 15 | 105
117 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 87 | 0 | 100 | 0
118 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 220 | 220 | 100 | 150 | 0 | 0
119 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 499 | 564 | 568 | 568 | 49 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3125 | 3121 | 1936 | 1932 | 1983 | 2056 | 575 | 81
120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 32 | 110 | 16 | 110
121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 23 | 33 | 22 | 30 |  | 10 | Engine problem
122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 126 | 130 | 130 | 132 |  | 62 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244
124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 217 | 222 | 220 | 220
125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 150 | 17 | 150
126 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 | 307 |  | Coal shortage
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1659 | 1889 | 1649 | 1886 | 307 | 72
127 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
128 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 28 | 0 | 35 | 17 |  | Fuel shortage
129 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 26 | 0 | 30 |  | 41 | Engine problem
130 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 28 | 28 | 28 | 28
131 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 8 | 34 | 16 |  | Fuel shortage
132 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 30 | 35 | 15 |  | Fuel shortage
133 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Gas shortage
134 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 |  |  | Fuel shortage
135 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 208 | 194 | 200 | 200 | 20
136 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 414 | 360 | 400 | 14
137 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 23 | 0 | 30 | 20 |  | Fuel shortage
138 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 22 | 92 | 50 | 90 | 14 |  | Fuel shortage
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 50 | 35 | 50 | 63 |  | Fuel shortage
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 35 | 35 | 57 | 56 |  | Fuel shortage
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 748*2 | 1496 | 1496 | 1291 | 1362 | 1200 | 1360
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 1638 | 2293 | 1968 | 2365 | 450 | 254
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 220 | 220 | 200 | 200
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 56 | 35 | 56 | 57 |  | Fuel shortage
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 75 | 35 | 115
153 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 194 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 491 | 351 | 438 | 371 | 182 | 85
| Total |  |  |  |  | 24911 | 24171 | 12309 | 14392 | 13177.6 | 15312 | 3984 | 3031
A. |  | 2023-08-17 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 14392 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 11389 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14850 | MW
3 | Day peak Generation : |  |  | 12309 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14253.06 | MW
4 | Evening peak Generation : |  |  | 14392 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 437 | MW
5 | Total Energy Generation : |  | 299.3278 | MKWHr | By Solar | 2.7714 | MKWHr
| By Gas : | 143.2392 | MKWHr |  | By Oil: | 45.1603 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 79.6185 | MKWHr |  | By Hydro: | 4.2992 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.2328 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3984 | MW | Dhaka | 5017.56 | 4972.56 |  | 45 |  | 18:00 |  | 417.335
|  |  | For Plants S/D or M/C prob = |  |  | 3031 | MW | Chittagong | 1304 | 1304 |  | 0 |  | 19:00 |  | 622.66
|  |  | Total = |  |  | 7015 | MW | Khulna | 1754 | 1744 |  | 10 |  | 19:30 |  | 486.095
7 | Total Gas Supplied : |  |  | 1122.1 | MMCFD |  |  | Rajshahi | 1562 | 1517 |  | 45 |  | 20:00 |  | 402.055
8 | Fuel Cost : | i) Gas : | Taka | 159064268.938 | ii) Oil : | Taka | 561350207.2 | Comilla | 1354 | 1241 |  | 113 |  | 21:00 |  | 437.39
|  | iii) Coal : | Taka | 308335337 | Total | Taka | 1028749813.138 | Mymensingh | 1215 | 1101 |  | 114 |  | 22:00 |  | 748.72
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 602 | 592 |  | 10 |  | 23:00 |  | 947.36
| ii) During Peak Demand : |  |  | 860 | MW (E to W) at | 21:00 | hrs | Barisal | 477.5 | 477.5 |  | 0 |  | 24:00 |  | 1295.935
| iii) Maximum : |  |  | 580 | MW at | 19:00 | hrs | Rangpur | 967 | 867 |  | 100
10 | Maximum Temperature in Dhaka was |  |  |  | 35.8° C |  |  | Total | 14253.06 | 13816.06 |  | 437
B. |  | 2023-08-18 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 35.8° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 14300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15312 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 12000 | MW
4 | Reserve(Generation end) |  |  |  | 1012 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 297.4144 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11235 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.2829 | MKWHr. | ii) HVDC Flow at Peak Time |  | 794 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.7235 | MKWHr. | iii) Maximum HVDC Flow : |  | 913 | MW at | 10:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 102.09 |  | (b) Today: | 102.65 |  | (c) Rule Curve: |  | 94.44
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-08-17 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 160 | 180 | 0 | 12 | 0 | 385 | 343 |  | 0 | 450 | 0 | 9 | 17 | 15 | 322 | 0 | 68 | 17 | 8 | 16 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 20 | 30 | 32 | 8 | 0 | 127 | 75 | 115 | 0 | 8 | 224 | 0 | 0 | 0 |  | 6 | 40 | 34 | 35 | 0 | 46 | 10 | 35 | 0 | 0 | 0 | 290 | 240 | 182 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 47 | 0 | 16 | 8 | 25 | 20 | 130 | 87 | 0 | 16 | 0 | 43 | 40 | 50 | 46 | 112 | 0 | 55 | 81 | 0 | 181 | 17 | 0 | 10 | 300 | 16 | 5 | 0 | 65 | 0 | 0 | 18 | 0 | 34 | 0 | 22 | 17 | 30 | 280 | 72 | 35 | 51 | 0 | 70 | 17 | 55 | 17 | 9 | 25 | 350 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 17 | 17 | 240 | 17 | 0 | 0 | 0 | 0 |  | 911 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 11 | 38 | 0 | 130 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 15 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 200 | 17 | 0 | 35 | 20 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 17 | 0 | 0 | 0 | 100 | 0 | 518 | 0 | 0 | 1263 | 0 | 0 |  | 6523 | 5612 | 12135 | 4270 | 911 | 1943 | 0 | 1156 | 3205 | 202 | 100 | 218 | 130 | 0 | 0 | 1160.325 | 102.07
2:00 | 0 | 0 | 160 | 180 | 0 | 12 | 0 | 420 | 342 |  | 0 | 450 | 0 | 8 | 17 | 15 | 320 | 0 | 67 | 17 | 8 | 16 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 0 | 33 | 32 | 8 | 0 | 126 | 75 | 120 | 0 | 8 | 225 | 0 | 0 | 0 |  | 6 | 40 | 34 | 35 | 0 | 46 | 10 | 35 | 0 | 0 | 0 | 280 | 240 | 175 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 47 | 0 | 16 | 10 | 25 | 20 | 128 | 86 | 0 | 16 | 0 | 43 | 40 | 50 | 46 | 112 | 0 | 45 | 81 | 0 | 181 | 17 | 0 | 10 | 310 | 24 | 5 | 0 | 65 | 0 | 0 | 18 | 0 | 34 | 0 | 22 | 17 | 10 | 280 | 68 | 35 | 51 | 0 | 70 | 17 | 55 | 17 | 9 | 25 | 350 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 18 | 17 | 240 | 17 | 0 | 0 | 0 | 0 |  | 864 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 11 | 38 | 0 | 130 | 32 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 15 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 200 | 17 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 17 | 0 | 0 | 0 | 50 | 0 | 521 | 0 | 0 | 1275 | 0 | 0 |  | 6506 | 5519 | 12025 | 4268 | 864 | 1951 | 0 | 1125 | 3220 | 201 | 50 | 218 | 128 | 0 | 0 | 1169.875 | 102.07
3:00 | 0 | 0 | 160 | 180 | 0 | 12 | 0 | 401 | 342 |  | 0 | 450 | 0 | 8 | 17 | 15 | 322 | 0 | 62 | 17 | 8 | 16 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 20 | 33 | 32 | 8 | 0 | 125 | 75 | 120 | 0 | 8 | 224 | 0 | 0 | 0 |  | 6 | 40 | 34 | 35 | 0 | 6 | 10 | 35 | 0 | 0 | 0 | 310 | 240 | 170 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 47 | 0 | 15 | 10 | 25 | 20 | 110 | 87 | 0 | 16 | 0 | 43 | 40 | 50 | 46 | 112 | 0 | 45 | 81 | 0 | 181 | 17 | 0 | 10 | 305 | 24 | 5 | 0 | 65 | 0 | 0 | 18 | 0 | 35 | 0 | 22 | 17 | 11 | 280 | 68 | 35 | 51 | 0 | 70 | 17 | 55 | 17 | 9 | 25 | 350 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 17 | 17 | 240 | 17 | 0 | 0 | 0 | 0 |  | 864 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 5 | 30 | 0 | 130 | 32 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 15 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 200 | 17 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 17 | 0 | 0 | 0 | 50 | 0 | 519 | 0 | 0 | 1266 | 0 | 0 |  | 6465 | 5405 | 11870 | 4295 | 864 | 1946 | 0 | 992 | 3209 | 200 | 50 | 204 | 110 | 0 | 0 | 1031.4 | 102.08
4:00 | 0 | 0 | 160 | 180 | 0 | 12 | 0 | 398 | 343 |  | 0 | 450 | 0 | 8 | 17 | 15 | 330 | 0 | 59 | 17 | 8 | 16 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 18 | 33 | 32 | 8 | 0 | 124 | 75 | 115 | 0 | 8 | 225 | 0 | 0 | 0 |  | 6 | 40 | 34 | 35 | 0 | 6 | 10 | 36 | 0 | 0 | 0 | 270 | 240 | 177 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 47 | 0 | 15 | 10 | 25 | 20 | 112 | 96 | 0 | 16 | 0 | 43 | 40 | 50 | 46 | 112 | 0 | 45 | 81 | 0 | 181 | 17 | 0 | 10 | 310 | 24 | 5 | 0 | 65 | 0 | 0 | 18 | 0 | 35 | 0 | 23 | 17 | 11 | 280 | 68 | 35 | 51 | 0 | 70 | 17 | 55 | 17 | 9 | 25 | 350 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 18 | 17 | 240 | 17 | 0 | 0 | 0 | 0 |  | 912 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 5 | 30 | 0 | 130 | 30 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 150 | 17 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 1244 | 222 | 0 | 17 | 0 | 0 | 0 | 50 | 0 | 520 | 0 | 0 | 1256 | 0 | 0 |  | 6436 | 5380 | 11816 | 4268 | 912 | 1903 | 0 | 983 | 3200 | 199 | 50 | 189 | 112 | 0 | 0 | 939.72 | 102.08
5:00 | 0 | 0 | 160 | 180 | 0 | 12 | 0 | 398 | 343 |  | 0 | 450 | 0 | 8 | 17 | 15 | 330 | 0 | 59 | 17 | 8 | 16 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 18 | 33 | 32 | 8 | 0 | 125 | 75 | 120 | 0 | 8 | 225 | 0 | 0 | 0 |  | 6 | 40 | 34 | 35 | 0 | 6 | 10 | 36 | 0 | 0 | 0 | 270 | 240 | 182 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 47 | 0 | 15 | 10 | 25 | 20 | 112 | 96 | 0 | 16 | 0 | 43 | 40 | 50 | 43 | 112 | 0 | 45 | 81 | 0 | 181 | 17 | 0 | 10 | 310 | 24 | 5 | 0 | 65 | 0 | 0 | 18 | 0 | 35 | 0 | 23 | 17 | 11 | 280 | 68 | 35 | 51 | 0 | 70 | 17 | 55 | 17 | 9 | 25 | 350 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 18 | 17 | 240 | 17 | 0 | 0 | 0 | 0 |  | 912 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 5 | 30 | 0 | 130 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 77 | 17 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 1244 | 222 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 519 | 0 | 0 | 1257 | 0 | 0 |  | 6457 | 5267 | 11724 | 4289 | 912 | 1826 | 0 | 996 | 3200 | 200 | 0 | 189 | 112 | 0 | 0 | 836.58 | 102.09
6:00 | 0 | 0 | 160 | 180 | 0 | 12 | 0 | 397 | 337 |  | 0 | 450 | 0 | 8 | 17 | 15 | 333 | 0 | 60 | 17 | 8 | 16 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 33 | 32 | 8 | 0 | 125 | 75 | 123 | 0 | 8 | 228 | 0 | 0 | 0 |  | 6 | 40 | 34 | 35 | 0 | 6 | 10 | 36 | 0 | 0 | 0 | 270 | 240 | 182 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 47 | 0 | 15 | 10 | 25 | 20 | 98 | 95 | 0 | 16 | 0 | 43 | 40 | 50 | 43 | 112 | 0 | 45 | 81 | 0 | 181 | 17 | 0 | 10 | 275 | 24 | 5 | 0 | 65 | 0 | 0 | 18 | 0 | 35 | 0 | 23 | 17 | 8 | 280 | 78 | 35 | 34 | 0 | 70 | 17 | 55 | 17 | 9 | 25 | 350 | 17 | 2 | 17 | 17 | 0 | 17 | 1 | 17 | 17 | 240 | 17 | 0 | 0 | 4 | 0 |  | 912 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 5 | 25 | 0 | 124 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 17 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 1244 | 221 | 0 | 17 | 0 | 1 | 0 | 0 | 0 | 520 | 0 | 0 | 1208 | 1 | 0 |  | 6407 | 5150 | 11557 | 4311 | 912 | 1706 | 0 | 985 | 3152 | 200 | 0 | 184 | 98 | 5 | 4 | 661.815 | 102.09
7:00 | 0 | 0 | 170 | 180 | 0 | 12 | 0 | 397 | 336 |  | 0 | 450 | 0 | 9 | 17 | 15 | 333 | 0 | 62 | 17 | 8 | 16 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 33 | 24 | 8 | 0 | 46 | 0 | 120 | 0 | 8 | 225 | 0 | 0 | 0 |  | 6 | 40 | 34 | 35 | 0 | 6 | 10 | 32 | 0 | 0 | 0 | 270 | 240 | 179 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 47 | 0 | 13 | 10 | 25 | 20 | 102 | 52 | 0 | 16 | 0 | 43 | 40 | 50 | 43 | 112 | 0 | 53 | 81 | 0 | 181 | 17 | 0 | 10 | 300 | 24 | 8 | 0 | 65 | 0 | 0 | 18 | 0 | 34 | 2 | 23 | 17 | 6 | 280 | 68 | 35 | 34 | 1 | 70 | 17 | 55 | 17 | 9 | 25 | 350 | 17 | 10 | 17 | 17 | 0 | 17 | 4 | 18 | 17 | 240 | 17 | 0 | 0 | 2 | 0 |  | 912 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 5 | 20 | 0 | 130 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 17 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 1244 | 222 | 0 | 17 | 0 | 12 | 0 | 0 | 0 | 522 | 6 | 0 | 1208 | 35 | 0 |  | 6236 | 5218 | 11454 | 4296 | 912 | 1722 | 0 | 971 | 3154 | 46 | 0 | 179 | 102 | 70 | 2 | 521.43 | 102.09
8:00 | 0 | 0 | 140 | 180 | 0 | 12 | 0 | 397 | 337 |  | 0 | 450 | 0 | 8 | 17 | 15 | 332 | 0 | 62 | 17 | 8 | 16 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 33 | 24 | 8 | 0 | 46 | 0 | 112 | 0 | 8 | 225 | 0 | 0 | 0 |  | 6 | 40 | 34 | 35 | 0 | 6 | 10 | 7 | 0 | 0 | 0 | 270 | 240 | 159 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 47 | 0 | 13 | 10 | 25 | 20 | 104 | 51 | 0 | 16 | 1 | 43 | 40 | 50 | 43 | 80 | 0 | 53 | 81 | 0 | 181 | 17 | 0 | 10 | 285 | 24 | 8 | 0 | 65 | 0 | 0 | 18 | 0 | 37 | 2 | 23 | 17 | 5 | 280 | 68 | 35 | 34 | 3 | 70 | 17 | 55 | 17 | 9 | 25 | 350 | 17 | 23 | 17 | 17 | 0 | 17 | 12 | 17 | 17 | 240 | 17 | 0 | 0 | 0 | 0 |  | 911 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 5 | 20 | 0 | 124 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 17 | 0 | 35 | 15 | 34 | 0 | 3 | 35 | 1244 | 220 | 0 | 17 | 1 | 29 | 0 | 0 | 0 | 523 | 12 | 0 | 1210 | 52 | 0 |  | 6132 | 5257 | 11389 | 4232 | 911 | 1648 | 0 | 974 | 3157 | 46 | 0 | 179 | 104 | 138 | 0 | 774.505 | 102.1
9:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 398 | 313 |  | 0 | 450 | 0 | 8 | 17 | 15 | 328 | 0 | 64 | 20 | 8 | 16 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 33 | 24 | 8 | 0 | 71 | 20 | 120 | 0 | 8 | 224 | 0 | 0 | 0 |  | 6 | 40 | 34 | 35 | 0 | 6 | 5 | 2 | 0 | 0 | 0 | 270 | 240 | 153 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 47 | 0 | 13 | 10 | 25 | 20 | 110 | 51 | 0 | 16 | 2 | 43 | 40 | 50 | 42 | 80 | 0 | 53 | 81 | 0 | 179 | 17 | 0 | 10 | 300 | 24 | 5 | 0 | 65 | 0 | 0 | 18 | 0 | 70 | 8 | 23 | 17 | 10 | 280 | 68 | 35 | 34 | 4 | 70 | 17 | 55 | 17 | 9 | 25 | 350 | 17 | 37 | 17 | 17 | 0 | 17 | 18 | 18 | 17 | 240 | 17 | 0 | 0 | 4 | 0 |  | 912 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 5 | 17 | 0 | 130 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 17 | 0 | 35 | 15 | 34 | 0 | 4 | 35 | 1232 | 220 | 0 | 17 | 3 | 34 | 0 | 0 | 0 | 520 | 22 | 0 | 1208 | 96 | 0 |  | 6220 | 5319 | 11539 | 4232 | 912 | 1632 | 0 | 1014 | 3140 | 91 | 0 | 176 | 110 | 228 | 4 | 870.005 | 102.11
10:00 | 0 | 0 | 150 | 180 | 0 | 12 | 0 | 374 | 332 |  | 0 | 450 | 0 | 9 | 17 | 15 | 322 | 0 | 62 | 25 | 16 | 16 | 34 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 19 | 20 | 33 | 24 | 8 | 0 | 92 | 75 | 115 | 0 | 8 | 224 | 0 | 0 | 0 |  | 6 | 40 | 34 | 35 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 270 | 240 | 166 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 47 | 0 | 13 | 10 | 25 | 20 | 114 | 50 | 0 | 16 | 2 | 43 | 40 | 50 | 42 | 112 | 0 | 53 | 78 | 0 | 178 | 17 | 0 | 10 | 300 | 24 | 5 | 0 | 65 | 0 | 0 | 18 | 0 | 72 | 12 | 23 | 38 | 12 | 280 | 67 | 35 | 51 | 5 | 70 | 17 | 53 | 17 | 9 | 25 | 350 | 17 | 44 | 17 | 17 | 0 | 17 | 23 | 30 | 17 | 240 | 17 | 0 | 0 | 8 | 0 |  | 913 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 5 | 17 | 0 | 130 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 17 | 0 | 35 | 15 | 34 | 0 | 7 | 35 | 1210 | 220 | 0 | 17 | 4 | 44 | 0 | 0 | 0 | 500 | 28 | 0 | 1207 | 135 | 0 |  | 6441 | 5336 | 11777 | 4212 | 913 | 1681 | 0 | 1105 | 3097 | 167 | 0 | 176 | 114 | 304 | 8 | 785.965 | 102.12
11:00 | 0 | 0 | 140 | 180 | 0 | 12 | 0 | 394 | 332 |  | 0 | 450 | 0 | 7 | 17 | 15 | 318 | 0 | 64 | 25 | 42 | 16 | 22 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 19 | 7 | 33 | 8 | 8 | 0 | 92 | 75 | 115 | 0 | 8 | 218 | 0 | 0 | 0 |  | 6 | 32 | 34 | 35 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 270 | 240 | 170 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 38 | 0 | 13 | 8 | 25 | 20 | 122 | 50 | 0 | 16 | 1 | 43 | 40 | 50 | 41 | 112 | 0 | 53 | 81 | 0 | 179 | 17 | 0 | 10 | 300 | 24 | 5 | 0 | 65 | 0 | 0 | 18 | 0 | 72 | 17 | 25 | 51 | 12 | 278 | 67 | 35 | 68 | 5 | 70 | 17 | 35 | 17 | 9 | 25 | 350 | 22 | 50 | 54 | 34 | 0 | 17 | 15 | 60 | 17 | 240 | 17 | 0 | 0 | 7 | 0 |  | 912 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 5 | 17 | 0 | 130 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 35 | 15 | 34 | 0 | 7 | 35 | 1220 | 220 | 0 | 17 | 5 | 83 | 0 | 0 | 0 | 500 | 34 | 0 | 1260 | 177 | 0 |  | 6542 | 5513 | 12055 | 4190 | 912 | 1683 | 0 | 1221 | 3200 | 167 | 0 | 159 | 122 | 394 | 7 | 902.475 | 102.13
12:00 | 0 | 0 | 136 | 180 | 0 | 12 | 0 | 395 | 321 |  | 0 | 450 | 0 | 9 | 17 | 15 | 316 | 0 | 62 | 25 | 33 | 16 | 23 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 19 | 18 | 33 | 22 | 8 | 0 | 92 | 75 | 119 | 0 | 8 | 218 | 0 | 0 | 0 |  | 6 | 32 | 32 | 35 | 0 | 6 | 10 | 6 | 0 | 0 | 0 | 290 | 240 | 170 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 32 | 0 | 13 | 10 | 25 | 20 | 124 | 46 | 0 | 16 | 2 | 43 | 39 | 50 | 40 | 112 | 0 | 48 | 82 | 0 | 179 | 17 | 0 | 10 | 300 | 24 | 5 | 0 | 65 | 0 | 0 | 18 | 0 | 72 | 14 | 25 | 51 | 8 | 260 | 71 | 35 | 68 | 3 | 70 | 17 | 41 | 17 | 9 | 25 | 350 | 45 | 46 | 54 | 34 | 0 | 17 | 31 | 72 | 17 | 240 | 17 | 0 | 0 | 4 | 0 |  | 912 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 5 | 18 | 0 | 126 | 23 | 32 | 0 | 0 | 0 | 0 | 0 | 22 | 28 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 0 | 0 | 0 | 35 | 15 | 34 | 0 | 7 | 35 | 1244 | 217 | 0 | 17 | 3 | 87 | 0 | 100 | 0 | 499 | 36 | 0 | 1291 | 194 | 0 |  | 6585 | 5724 | 12309 | 4205 | 912 | 1674 | 0 | 1272 | 3254 | 167 | 100 | 174 | 124 | 423 | 4 | 1041.905 | 102.14
13:00 | 0 | 0 | 120 | 180 | 0 | 12 | 0 | 394 | 317 |  | 0 | 450 | 0 | 8 | 17 | 15 | 315 | 0 | 59 | 25 | 33 | 16 | 24 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 19 | 17 | 33 | 22 | 8 | 0 | 92 | 75 | 114 | 0 | 1 | 219 | 0 | 0 | 0 |  | 6 | 32 | 32 | 35 | 0 | 6 | 10 | 6 | 0 | 0 | 0 | 310 | 330 | 136 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 22 | 0 | 15 | 8 | 25 | 20 | 132 | 45 | 0 | 16 | 2 | 41 | 40 | 50 | 39 | 112 | 0 | 48 | 84 | 0 | 179 | 17 | 0 | 10 | 310 | 24 | 5 | 0 | 65 | 0 | 0 | 18 | 0 | 72 | 14 | 25 | 51 | 8 | 250 | 71 | 35 | 68 | 5 | 70 | 17 | 48 | 17 | 9 | 25 | 376 | 53 | 52 | 54 | 34 | 0 | 17 | 28 | 72 | 17 | 240 | 17 | 0 | 0 | 4 | 0 |  | 911 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 5 | 16 | 8 | 128 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 48 | 28 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 35 | 15 | 34 | 0 | 7 | 35 | 1244 | 217 | 0 | 17 | 5 | 34 | 0 | 100 | 0 | 500 | 34 | 0 | 1287 | 189 | 0 |  | 6684 | 5710 | 12394 | 4268 | 911 | 1682 | 0 | 1321 | 3251 | 167 | 100 | 188 | 132 | 370 | 4 | 1151.73 | 102.14
14:00 | 0 | 0 | 113 | 180 | 0 | 12 | 0 | 394 | 317 |  | 0 | 450 | 0 | 8 | 17 | 15 | 0 | 0 | 92 | 25 | 30 | 16 | 35 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 19 | 18 | 33 | 22 | 8 | 0 | 92 | 75 | 118 | 0 | 8 | 221 | 0 | 0 | 0 |  | 6 | 36 | 32 | 35 | 0 | 6 | 10 | 10 | 0 | 0 | 0 | 290 | 260 | 130 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 15 | 0 | 13 | 10 | 25 | 20 | 154 | 45 | 0 | 16 | 1 | 39 | 39 | 48 | 39 | 112 | 0 | 48 | 82 | 0 | 179 | 17 | 0 | 10 | 290 | 24 | 5 | 0 | 65 | 0 | 0 | 18 | 0 | 57 | 7 | 25 | 51 | 12 | 280 | 71 | 35 | 68 | 5 | 70 | 17 | 48 | 17 | 9 | 25 | 350 | 53 | 41 | 54 | 34 | 0 | 17 | 28 | 72 | 17 | 240 | 17 | 0 | 0 | 12 | 0 |  | 912 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 5 | 15 | 8 | 124 | 25 | 48 | 0 | 0 | 0 | 35 | 0 | 48 | 28 | 0 | 10 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 0 | 35 | 15 | 34 | 0 | 7 | 35 | 1244 | 220 | 0 | 17 | 4 | 95 | 0 | 100 | 0 | 500 | 24 | 0 | 1283 | 170 | 0 |  | 6318 | 5799 | 12117 | 3907 | 912 | 1666 | 0 | 1341 | 3247 | 167 | 100 | 229 | 154 | 382 | 12 | 1320.765 | 102.13
15:00 | 0 | 0 | 120 | 180 | 0 | 12 | 0 | 394 | 318 |  | 0 | 450 | 0 | 14 | 17 | 15 | 0 | 0 | 148 | 25 | 33 | 16 | 23 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 19 | 18 | 33 | 14 | 8 | 0 | 132 | 75 | 115 | 0 | 8 | 215 | 0 | 0 | 0 |  | 6 | 48 | 32 | 35 | 0 | 7 | 10 | 10 | 0 | 0 | 0 | 270 | 240 | 154 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 18 | 5 | 14 | 10 | 25 | 17 | 114 | 45 | 0 | 16 | 2 | 38 | 39 | 49 | 39 | 112 | 0 | 48 | 82 | 0 | 179 | 17 | 0 | 10 | 305 | 24 | 5 | 0 | 65 | 0 | 0 | 18 | 0 | 53 | 15 | 25 | 51 | 12 | 80 | 66 | 35 | 68 | 3 | 69 | 17 | 55 | 17 | 9 | 25 | 350 | 53 | 27 | 54 | 34 | 0 | 17 | 22 | 72 | 17 | 230 | 17 | 0 | 0 | 14 | 0 |  | 912 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 5 | 15 | 8 | 124 | 25 | 48 | 0 | 0 | 0 | 35 | 0 | 48 | 28 | 0 | 23 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 35 | 15 | 34 | 0 | 6 | 35 | 1244 | 215 | 0 | 17 | 4 | 80 | 0 | 126 | 0 | 500 | 24 | 0 | 1286 | 127 | 0 |  | 6156 | 5768 | 11924 | 3723 | 912 | 1678 | 0 | 1333 | 3250 | 207 | 126 | 257 | 114 | 310 | 14 | 1648.33 | 102.2
16:00 | 0 | 0 | 120 | 180 | 0 | 12 | 0 | 394 | 318 |  | 0 | 450 | 0 | 45 | 17 | 15 | 11 | 0 | 150 | 25 | 33 | 16 | 33 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 19 | 18 | 33 | 14 | 8 | 0 | 132 | 75 | 113 | 0 | 8 | 217 | 0 | 0 | 0 |  | 6 | 56 | 32 | 35 | 0 | 16 | 10 | 10 | 0 | 0 | 0 | 270 | 240 | 161 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 22 | 7 | 9 | 10 | 25 | 17 | 116 | 47 | 0 | 16 | 1 | 38 | 39 | 48 | 39 | 112 | 0 | 48 | 82 | 0 | 179 | 17 | 0 | 10 | 310 | 16 | 3 | 0 | 65 | 0 | 0 | 18 | 0 | 52 | 11 | 25 | 49 | 30 | 80 | 74 | 35 | 68 | 3 | 69 | 17 | 55 | 17 | 9 | 25 | 350 | 52 | 28 | 54 | 34 | 0 | 17 | 14 | 55 | 17 | 230 | 17 | 0 | 0 | 18 | 0 |  | 912 | 0 | 295 | 0 | 32 | 0 | 0 | 0 | 5 | 19 | 8 | 128 | 25 | 48 | 0 | 0 | 0 | 35 | 0 | 48 | 28 | 0 | 15 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204 | 0 | 96 | 0 | 0 | 35 | 15 | 34 | 0 | 4 | 35 | 1244 | 216 | 0 | 17 | 2 | 10 | 0 | 125 | 0 | 494 | 16 | 0 | 1288 | 22 | 0 |  | 6230 | 5691 | 11921 | 3728 | 912 | 1779 | 0 | 1414 | 3246 | 207 | 125 | 265 | 116 | 111 | 18 | 1364.695 | 102.22
17:00 | 0 | 0 | 110 | 180 | 0 | 12 | 0 | 394 | 317 |  | 0 | 450 | 0 | 49 | 17 | 15 | 27 | 0 | 121 | 26 | 33 | 16 | 34 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 19 | 17 | 33 | 0 | 8 | 0 | 132 | 75 | 118 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 24 | 32 | 46 | 11 | 18 | 10 | 15 | 0 | 0 | 0 | 270 | 240 | 166 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 26 | 0 | 12 | 10 | 24 | 17 | 92 | 47 | 0 | 16 | 1 | 40 | 39 | 48 | 39 | 112 | 0 | 53 | 84 | 0 | 179 | 17 | 0 | 10 | 300 | 24 | 3 | 0 | 65 | 0 | 0 | 18 | 0 | 56 | 2 | 25 | 51 | 68 | 15 | 75 | 35 | 68 | 0 | 69 | 17 | 55 | 17 | 9 | 25 | 330 | 55 | 13 | 54 | 34 | 0 | 17 | 8 | 72 | 17 | 230 | 17 | 0 | 0 | 27 | 0 |  | 912 | 0 | 295 | 0 | 32 | 0 | 0 | 0 | 5 | 18 | 0 | 124 | 24 | 48 | 0 | 0 | 0 | 28 | 0 | 48 | 28 | 0 | 15 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 370 | 0 | 0 | 35 | 67 | 40 | 0 | 2 | 35 | 1220 | 212 | 0 | 17 | 1 | 7 | 35 | 100 | 0 | 506 | 2 | 0 | 1285 | 6 | 0 |  | 6154 | 5919 | 12073 | 3614 | 912 | 2044 | 0 | 1615 | 3191 | 207 | 100 | 229 | 92 | 42 | 27 | 933.035 | 102.24
18:00 | 0 | 0 | 120 | 180 | 0 | 12 | 0 | 393 | 321 |  | 0 | 450 | 0 | 49 | 21 | 15 | 26 | 0 | 98 | 26 | 48 | 16 | 34 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 19 | 17 | 33 | 15 | 8 | 0 | 132 | 75 | 114 | 0 | 0 | 226 | 0 | 0 | 0 |  | 6 | 50 | 34 | 46 | 12 | 32 | 10 | 19 | 0 | 0 | 0 | 270 | 240 | 176 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 24 | 0 | 13 | 10 | 25 | 17 | 100 | 47 | 0 | 16 | 0 | 41 | 38 | 50 | 43 | 112 | 0 | 58 | 85 | 0 | 179 | 17 | 0 | 10 | 290 | 24 | 3 | 0 | 67 | 0 | 0 | 27 | 0 | 131 | 0 | 35 | 78 | 100 | 80 | 75 | 35 | 68 | 0 | 122 | 17 | 55 | 17 | 26 | 25 | 335 | 57 | 1 | 54 | 36 | 0 | 17 | 2 | 83 | 17 | 230 | 17 | 0 | 0 | 17 | 0 |  | 912 | 0 | 270 | 0 | 32 | 0 | 0 | 0 | 14 | 25 | 0 | 124 | 27 | 48 | 0 | 0 | 0 | 21 | 0 | 48 | 28 | 0 | 15 | 0 | 9 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 370 | 2 | 0 | 35 | 67 | 45 | 0 | 1 | 35 | 1190 | 213 | 0 | 17 | 0 | 1 | 35 | 100 | 0 | 557 | 0 | 0 | 1284 | 0 | 0 |  | 6544 | 5919 | 12463 | 3697 | 912 | 2053 | 0 | 1888 | 3211 | 207 | 100 | 273 | 100 | 5 | 17 | 417.335 | 102.26
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 120 | 180 | 0 | 12 | 0 | 395 | 332 |  | 0 | 450 | 0 | 48 | 51 | 15 | 36 | 0 | 121 | 32 | 78 | 32 | 34 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 17 | 33 | 16 | 24 | 0 | 132 | 75 | 120 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 50 | 34 | 46 | 12 | 33 | 10 | 26 | 0 | 0 | 0 | 270 | 240 | 187 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 35 | 0 | 14 | 10 | 25 | 17 | 110 | 47 | 0 | 16 | 0 | 43 | 40 | 50 | 42 | 112 | 0 | 49 | 85 | 0 | 179 | 17 | 0 | 10 | 300 | 24 | 3 | 0 | 143 | 0 | 0 | 112 | 0 | 149 | 0 | 50 | 102 | 118 | 80 | 84 | 88 | 68 | 0 | 250 | 17 | 55 | 17 | 26 | 25 | 350 | 52 | 0 | 144 | 51 | 0 | 17 | 0 | 96 | 17 | 230 | 69 | 0 | 0 | 20 | 0 |  | 911 | 0 | 255 | 0 | 46 | 0 | 0 | 0 | 32 | 35 | 8 | 124 | 29 | 110 | 0 | 0 | 0 | 21 | 5 | 92 | 28 | 0 | 22 | 0 | 23 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 414 | 6 | 0 | 35 | 67 | 55 | 0 | 0 | 35 | 1160 | 220 | 0 | 45 | 0 | 0 | 75 | 150 | 0 | 565 | 0 | 0 | 1362 | 0 | 0 |  | 7361 | 6337 | 13698 | 3735 | 911 | 2133 | 0 | 2695 | 3287 | 207 | 150 | 450 | 110 | 0 | 20 | 622.66 | 102.35
19:30 | 0 | 0 | 114 | 180 | 0 | 12 | 0 | 393 | 321 |  | 0 | 450 | 0 | 50 | 51 | 15 | 140 | 0 | 121 | 38 | 102 | 32 | 34 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 17 | 33 | 16 | 24 | 0 | 132 | 75 | 120 | 0 | 0 | 226 | 0 | 0 | 0 |  | 6 | 50 | 32 | 46 | 12 | 36 | 10 | 26 | 0 | 0 | 0 | 270 | 240 | 185 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 38 | 0 | 14 | 10 | 25 | 17 | 104 | 53 | 0 | 16 | 0 | 43 | 40 | 50 | 45 | 112 | 0 | 51 | 86 | 0 | 179 | 17 | 0 | 10 | 260 | 24 | 3 | 0 | 145 | 0 | 0 | 157 | 0 | 149 | 0 | 50 | 102 | 135 | 80 | 84 | 88 | 68 | 0 | 287 | 17 | 55 | 50 | 29 | 25 | 320 | 53 | 0 | 162 | 51 | 0 | 17 | 0 | 95 | 17 | 230 | 108 | 0 | 0 | 18 | 0 |  | 795 | 0 | 240 | 0 | 46 | 0 | 0 | 0 | 45 | 40 | 8 | 124 | 31 | 110 | 0 | 0 | 0 | 21 | 10 | 92 | 28 | 0 | 24 | 0 | 23 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 416 | 9 | 0 | 35 | 67 | 55 | 0 | 0 | 35 | 1232 | 220 | 0 | 137 | 0 | 0 | 75 | 233 | 0 | 536 | 0 | 0 | 1359 | 0 | 0 |  | 7612 | 6479 | 14091 | 3802 | 795 | 2090 | 0 | 2980 | 3347 | 207 | 233 | 515 | 104 | 0 | 18 | 486.095 | 0
20:00 | 0 | 0 | 120 | 180 | 0 | 12 | 0 | 394 | 327 |  | 0 | 450 | 0 | 49 | 51 | 15 | 264 | 0 | 77 | 38 | 102 | 32 | 34 | 0 | 0 | 0 | 35 | 35 | 55 | 0 | 19 | 17 | 33 | 16 | 24 | 0 | 132 | 75 | 120 | 0 | 0 | 225 | 0 | 0 | 0 |  | 6 | 50 | 32 | 46 | 12 | 40 | 10 | 15 | 0 | 0 | 0 | 270 | 240 | 185 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 32 | 0 | 15 | 10 | 25 | 17 | 106 | 70 | 0 | 16 | 0 | 43 | 40 | 50 | 45 | 112 | 0 | 50 | 86 | 0 | 179 | 17 | 0 | 10 | 260 | 24 | 3 | 0 | 145 | 0 | 0 | 157 | 0 | 149 | 0 | 50 | 104 | 134 | 80 | 84 | 88 | 68 | 0 | 284 | 17 | 55 | 106 | 29 | 50 | 350 | 54 | 0 | 162 | 51 | 0 | 17 | 0 | 96 | 17 | 230 | 141 | 0 | 0 | 17 | 0 |  | 794 | 0 | 240 | 0 | 54 | 0 | 0 | 0 | 31 | 45 | 8 | 130 | 31 | 110 | 0 | 0 | 0 | 28 | 18 | 92 | 28 | 0 | 22 | 0 | 23 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 414 | 12 | 0 | 40 | 67 | 56 | 0 | 0 | 35 | 1232 | 220 | 0 | 137 | 0 | 0 | 75 | 150 | 0 | 565 | 0 | 0 | 1359 | 0 | 0 |  | 7833 | 6446 | 14279 | 3919 | 794 | 2083 | 0 | 3081 | 3376 | 207 | 150 | 546 | 106 | 0 | 17 | 402.055 | 102.32
21:00 | 0 | 0 | 120 | 180 | 0 | 12 | 0 | 390 | 332 |  | 0 | 450 | 0 | 49 | 51 | 15 | 318 | 0 | 37 | 38 | 102 | 32 | 33 | 0 | 0 | 0 | 35 | 35 | 55 | 0 | 19 | 19 | 33 | 8 | 24 | 0 | 136 | 75 | 123 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 59 | 32 | 46 | 12 | 40 | 10 | 33 | 0 | 0 | 0 | 270 | 240 | 188 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 38 | 0 | 14 | 10 | 25 | 17 | 106 | 85 | 0 | 16 | 0 | 43 | 40 | 50 | 45 | 112 | 0 | 55 | 86 | 0 | 181 | 17 | 0 | 10 | 300 | 24 | 3 | 0 | 148 | 0 | 0 | 147 | 0 | 149 | 0 | 50 | 103 | 135 | 80 | 84 | 88 | 68 | 0 | 297 | 17 | 55 | 106 | 29 | 50 | 350 | 43 | 0 | 162 | 51 | 0 | 17 | 0 | 96 | 17 | 230 | 125 | 0 | 0 | 21 | 0 |  | 794 | 0 | 210 | 0 | 64 | 0 | 0 | 0 | 21 | 37 | 8 | 130 | 33 | 110 | 0 | 0 | 0 | 28 | 26 | 92 | 28 | 0 | 25 | 8 | 23 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 414 | 17 | 0 | 50 | 67 | 56 | 0 | 0 | 35 | 1244 | 222 | 0 | 150 | 0 | 0 | 75 | 150 | 0 | 564 | 0 | 0 | 1362 | 0 | 0 |  | 7927 | 6465 | 14392 | 3911 | 794 | 2150 | 0 | 3121 | 3390 | 211 | 150 | 538 | 106 | 0 | 21 | 437.39 | 102.35
22:00 | 0 | 0 | 140 | 180 | 0 | 12 | 0 | 392 | 332 |  | 0 | 450 | 0 | 38 | 36 | 15 | 322 | 0 | 37 | 40 | 41 | 16 | 34 | 0 | 0 | 0 | 35 | 35 | 55 | 0 | 19 | 18 | 33 | 20 | 24 | 0 | 136 | 75 | 120 | 0 | 0 | 226 | 0 | 0 | 0 |  | 6 | 59 | 32 | 46 | 12 | 2 | 10 | 35 | 0 | 0 | 0 | 270 | 240 | 191 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 36 | 0 | 14 | 10 | 25 | 17 | 118 | 85 | 0 | 16 | 0 | 43 | 40 | 50 | 45 | 112 | 0 | 51 | 84 | 0 | 181 | 17 | 0 | 10 | 290 | 24 | 3 | 0 | 148 | 0 | 0 | 156 | 0 | 149 | 0 | 50 | 105 | 142 | 118 | 84 | 88 | 68 | 0 | 132 | 17 | 55 | 106 | 29 | 50 | 350 | 34 | 0 | 162 | 51 | 0 | 17 | 0 | 96 | 17 | 230 | 141 | 0 | 0 | 15 | 0 |  | 765 | 0 | 200 | 0 | 64 | 0 | 0 | 0 | 21 | 37 | 8 | 124 | 33 | 110 | 0 | 0 | 0 | 28 | 14 | 92 | 28 | 0 | 25 | 8 | 23 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 414 | 22 | 0 | 50 | 67 | 49 | 0 | 0 | 35 | 1244 | 222 | 0 | 150 | 0 | 0 | 75 | 50 | 0 | 566 | 0 | 0 | 1359 | 0 | 0 |  | 7716 | 6300 | 14016 | 3963 | 765 | 2140 | 0 | 2841 | 3389 | 211 | 50 | 524 | 118 | 0 | 15 | 748.72 | 102.39
23:00 | 0 | 0 | 140 | 180 | 0 | 12 | 0 | 387 | 333 |  | 0 | 450 | 0 | 25 | 34 | 15 | 317 | 0 | 37 | 33 | 16 | 16 | 34 | 0 | 0 | 0 | 35 | 17 | 55 | 15 | 19 | 18 | 30 | 24 | 25 | 0 | 137 | 75 | 120 | 0 | 1 | 220 | 0 | 0 | 0 |  | 4 | 59 | 32 | 46 | 0 | 6 | 10 | 41 | 0 | 0 | 0 | 270 | 240 | 195 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 31 | 0 | 14 | 10 | 25 | 17 | 120 | 85 | 0 | 16 | 0 | 43 | 40 | 50 | 45 | 112 | 0 | 49 | 84 | 0 | 180 | 17 | 0 | 10 | 300 | 24 | 3 | 0 | 145 | 0 | 0 | 18 | 0 | 110 | 0 | 25 | 101 | 142 | 248 | 67 | 88 | 68 | 0 | 88 | 17 | 55 | 106 | 15 | 50 | 350 | 34 | 0 | 36 | 51 | 0 | 17 | 0 | 96 | 17 | 230 | 141 | 0 | 0 | 18 | 0 |  | 765 | 0 | 190 | 0 | 64 | 0 | 0 | 0 | 21 | 28 | 8 | 128 | 34 | 110 | 0 | 0 | 0 | 28 | 15 | 92 | 28 | 0 | 28 | 8 | 23 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 414 | 32 | 0 | 35 | 67 | 49 | 0 | 0 | 35 | 1244 | 222 | 0 | 150 | 0 | 0 | 75 | 50 | 0 | 567 | 0 | 0 | 1361 | 0 | 0 |  | 7374 | 6284 | 13658 | 4084 | 765 | 2150 | 0 | 2353 | 3392 | 212 | 50 | 514 | 120 | 0 | 18 | 947.36 | 102.43
24:00 | 0 | 0 | 140 | 180 | 0 | 12 | 0 | 393 | 332 |  | 0 | 450 | 0 | 24 | 22 | 15 | 323 | 0 | 38 | 28 | 16 | 16 | 34 | 0 | 0 | 0 | 17 | 0 | 35 | 19 | 19 | 18 | 30 | 32 | 8 | 0 | 138 | 75 | 120 | 0 | 8 | 223 | 0 | 0 | 0 |  | 4 | 50 | 28 | 35 | 0 | 6 | 10 | 41 | 0 | 0 | 0 | 270 | 240 | 197 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 23 | 0 | 14 | 10 | 25 | 17 | 118 | 85 | 0 | 16 | 0 | 43 | 40 | 50 | 45 | 112 | 0 | 50 | 84 | 0 | 180 | 17 | 0 | 10 | 320 | 24 | 3 | 0 | 122 | 0 | 0 | 18 | 0 | 72 | 0 | 25 | 60 | 143 | 400 | 67 | 17 | 68 | 0 | 88 | 17 | 55 | 52 | 9 | 25 | 350 | 34 | 0 | 17 | 51 | 0 | 17 | 0 | 96 | 17 | 230 | 17 | 0 | 0 | 24 | 0 |  | 788 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 10 | 32 | 8 | 122 | 34 | 110 | 0 | 0 | 0 | 0 | 15 | 92 | 28 | 0 | 23 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 414 | 35 | 0 | 35 | 32 | 49 | 0 | 0 | 35 | 1244 | 220 | 0 | 150 | 0 | 0 | 37 | 50 | 0 | 566 | 0 | 0 | 1361 | 0 | 0 |  | 7066 | 6077 | 13143 | 4237 | 788 | 2167 | 0 | 1849 | 3391 | 213 | 50 | 306 | 118 | 0 | 24 | 1295.935 | 102.47
KWH | 0 | 0 | 3309906 | 4252500 | 0 | 296909 | 0 | 9566120 | 7924000 |  | 0 | 10281000 | 0 | 498240 | 496877 | 371551 | 5790148 | 0 | 2020000 | 555840 | 687600 | 415680 | 877297 | 0 | 0 | 0 | 388800 | 0 | 440847 | 300708 | 456000 | 408960 | 759960 | 540500 | 277920 | 0 | 2707167 | 1592000 | 2600000 | 0 | 143782 | 5262440 | 0 | 0 | 0 |  | 144720 | 992352 | 782001 | 881400 | 74880 | 364320 | 233952 | 526080 | 0 | 0 | 0 | 7019500 | 5986000 | 4206000 | 0 | 0 | 0 | 0 | 0 | 1142864 | 0 | 890416 | 17731 | 327384 | 240480 | 610100 | 455280 | 2723520 | 1498560 | 0 | 360108 | 14700 | 988500 | 921720 | 1198200 | 1023192 | 2506582 | 0 | 1193760 | 1961280 | 0 | 4629040 | 382000 | 0 | 243900 | 7347000 | 517320 | 108000 | 0 | 2034871 | 0 | 0 | 924000 | 0 | 1785456 | 111915 | 691200 | 1223040 | 1184290 | 5039000 | 1718400 | 1090166 | 1435199 | 30084 | 2421273 | 434261 | 1308070 | 799140 | 319200 | 690240 | 8357800 | 821760 | 359630 | 1355040 | 775309 | 0 | 441720 | 201830 | 1332480 | 430920 | 5838600 | 936727 | 0 | 0 | 232800 | 0 |  | 21282909 | 0 | 6416640 | 0 | 400320 | 0 | 0 | 0 | 231360 | 597248 | 76875 | 3049000 | 650861 | 1376 | 0 | 0 | 0 | 278794 | 73270 | 1635258 | 658180 | 0 | 240130 | 177758 | 112220 | 0 | 0 | 182034 | 0 | 0 | 4797200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5058327 | 0 | 3996981 | 297600 | 0 | 963360 | 832752 | 939091 | 0 | 52954 | 908832 | 31404900 | 5254036 | 0 | 1161600 | 37860 | 525262 | 494016 | 1625222 | 0 | 12581820 | 226987 | 0 | 30834545 | 1210200 | 0 |  | 160060015 | 139267778 | 299327793 | 98886347 | 21282909 | 44352885 | 0 | 36349600 | 79618465 | 4299167 | 1625222 | 7185456 | 2723520 | 2771422 | 232800 | 0
Fuel Cost | 0 | 0 | 4832462.76 | 6336225 | 0 | 394888.97 | 0 | 10044426 | 8557920 |  | 0 | 11206290 | 0 | 5570323.2 | 6583620.25 | 4923050.75 | 6484965.76 | 0 | 3535000 | 8126380.8 | 9674532 | 6738172.8 | 8088678.34 | 0 | 0 | 0 | 4945536 | 0 | 5911758.27 | 225531 | 342000 | 0 | 0 | 0 | 4727419.2 | 0 | 730935.09 | 429840 | 4914000 | 0 | 2350835.7 | 5472937.6 | 0 | 0 | 0 |  | 1888596 | 16552431.36 | 13309657.02 | 11907714 | 949478.4 | 4215182.4 | 297119.04 | 1751846.4 | 0 | 0 | 0 | 7791645 | 6524740 | 4878960 | 0 | 0 | 0 | 0 | 0 | 1908582.88 | 0 | 15377484.32 | 238481.95 | 448516.08 | 180360 | 1067675 | 341460 | 19554873.6 | 1633430.4 | 0 | 489746.88 | 234318 | 1354245 | 1216670.4 | 2084868 | 1770122.16 | 2882569.3 | 0 | 2315894.4 | 4471718.4 | 0 | 4675330.4 | 821300 | 0 | 482922 | 7347000 | 387990 | 82080 | 0 | 27775989.15 | 0 | 0 | 12455520 | 0 | 24728565.6 | 1308286.35 | 7133184 | 16706726.4 | 15715528.3 | 4635880 | 20895744 | 15763800.36 | 18155267.35 | 0 | 28425745.02 | 4729102.29 | 13904784.1 | 10844329.8 | 4114488 | 8131027.2 | 7689176 | 10641792 | 5196653.5 | 17195457.6 | 8823016.42 | 0 | 5768863.2 | 2411868.5 | 19947225.6 | 5675216.4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 63848727 | 0 | 7186636.8 | 0 | 4167331.2 | 0 | 0 | 0 | 4166793.6 | 10750464 | 1104693.75 | 3414880 | 1262670.34 | 14998.4 | 0 | 0 | 0 | 4675375.38 | 1281492.3 | 25575435.12 | 5067986 | 0 | 4060598.3 | 2422841.54 | 1893151.4 | 0 | 0 | 137799.738 | 0 | 0 | 25377188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5867659.32 | 0 | 3957011.19 | 3999744 | 0 | 11396548.8 | 12033266.4 | 11926455.7 | 0 | 585141.7 | 11033220.48 | 282958149 | 5359116.72 | 0 | 8595840 | 428196.6 | 6161323.26 | 7573265.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 591355975.42 | 538284001.318 | 1129639976.738 | 105626742.578 | 63848727 | 53437526.36 | 0 | 456969151.6 | 308335337 | 1160775.09 | 0 | 104381055.6 | 19554873.6 | 16325787.91 | 0 | 0
Yesterday Day Peak | 0 | 0 | 136 | 180 | 0 | 12 | 0 | 395 | 321 |  | 0 | 450 | 0 | 9 | 17 | 15 | 316 | 0 | 62 | 25 | 33 | 16 | 23 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 19 | 18 | 33 | 22 | 8 | 0 | 92 | 75 | 119 | 0 | 8 | 218 | 0 | 0 | 0 |  | 6 | 32 | 32 | 35 | 0 | 6 | 10 | 6 | 0 | 0 | 0 | 290 | 240 | 170 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 32 | 0 | 13 | 10 | 25 | 20 | 124 | 46 | 0 | 16 | 2 | 43 | 39 | 50 | 40 | 112 | 0 | 48 | 82 | 0 | 179 | 17 | 0 | 10 | 300 | 24 | 5 | 0 | 65 | 0 | 0 | 18 | 0 | 72 | 14 | 25 | 51 | 8 | 260 | 71 | 35 | 68 | 3 | 70 | 17 | 41 | 17 | 9 | 25 | 350 | 45 | 46 | 54 | 34 | 0 | 17 | 31 | 72 | 17 | 240 | 17 | 0 | 0 | 4 | 0 |  | 912 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 5 | 18 | 0 | 126 | 23 | 32 | 0 | 0 | 0 | 0 | 0 | 22 | 28 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 0 | 0 | 0 | 35 | 15 | 34 | 0 | 7 | 35 | 1244 | 217 | 0 | 17 | 3 | 87 | 0 | 100 | 0 | 499 | 36 | 0 | 1291 | 194 | 0 |  | 12309 | DayPeak
Yesterday Evening Peak | 0 | 0 | 120 | 180 | 0 | 12 | 0 | 390 | 332 | 0 | 0 | 450 | 0 | 49 | 51 | 15 | 318 | 0 | 37 | 38 | 102 | 32 | 33 | 0 | 0 | 0 | 35 | 35 | 55 | 0 | 19 | 19 | 33 | 8 | 24 | 0 | 136 | 75 | 123 | 0 | 0 | 224 | 0 | 0 | 0 | 0 | 6 | 59 | 32 | 46 | 12 | 40 | 10 | 33 | 0 | 0 | 0 | 270 | 240 | 188 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 38 | 0 | 14 | 10 | 25 | 17 | 106 | 85 | 0 | 16 | 0 | 43 | 40 | 50 | 45 | 112 | 0 | 55 | 86 | 0 | 181 | 17 | 0 | 10 | 300 | 24 | 3 | 0 | 148 | 0 | 0 | 147 | 0 | 149 | 0 | 50 | 103 | 135 | 80 | 84 | 88 | 68 | 0 | 297 | 17 | 55 | 106 | 29 | 50 | 350 | 43 | 0 | 162 | 51 | 0 | 17 | 0 | 96 | 17 | 230 | 125 | 0 | 0 | 21 | 0 |  | 794 | 0 | 210 | 0 | 64 | 0 | 0 | 0 | 21 | 37 | 8 | 130 | 33 | 110 | 0 | 0 | 0 | 28 | 26 | 92 | 28 | 0 | 25 | 8 | 23 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 414 | 17 | 0 | 50 | 67 | 56 | 0 | 0 | 35 | 1244 | 222 | 0 | 150 | 0 | 0 | 75 | 150 | 0 | 564 | 0 | 0 | 1362 | 0 | 0 |  | 14392 | EvPeak
Forecast for Evening | 0 | 0 | 170 | 180 | 0 | 12 | 0 | 400 | 330 | 0 | 0 | 450 | 0 | 49 | 51 | 15 | 330 | 0 | 93 | 38 | 102 | 64 | 33 | 0 | 0 | 0 | 35 | 35 | 55 | 20 | 19 | 21 | 33 | 32 | 25 | 0 | 136 | 75 | 120 | 0 | 25 | 225 |  | 0 | 0 | 0 | 6 | 59 | 34 | 46 | 12 | 47 | 10 | 30 | 0 | 0 | 0 | 280 | 270 | 200 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 47 | 0 | 22 | 11 | 33 | 20 | 163 | 85 | 0 | 16 | 0 | 43 | 42 | 50 | 46 | 112 | 0 | 50 | 86 | 0 | 180 | 17 | 0 | 10 | 300 | 24 | 11 | 0 | 145 | 0 | 0 | 142 | 0 | 149 | 0 | 50 | 100 | 150 | 350 | 85 | 88 | 68 | 0 | 297 | 17 | 55 | 105 | 28 | 50 | 360 | 55 | 0 | 162 | 51 | 0 | 17 |  | 115 | 17 | 240 | 142 |  | 0 | 10 | 0 |  | 911 | 0 | 290 |  | 48 | 0 | 0 | 0 | 40 | 51 | 8 | 132 | 30 | 110 | 0 | 0 | 0 | 35 | 30 | 90 | 28 | 34 | 35 | 8 | 30 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 200 | 0 | 400 | 35 | 0 | 50 | 105 | 56 | 0 | 0 | 57 | 1244 | 220 |  | 150 |  |  | 115 | 0 |  | 568 |  | 0 | 1360 |  | 0
Forecast for Day | 0 | 0 | 140 | 180 | 0 | 12 | 0 | 400 | 330 | 0 | 0 | 450 | 0 | 34 | 17 | 15 | 330 | 0 | 93 | 24 | 16 | 16 | 33 | 0 | 0 | 0 | 17 | 35 | 35 | 20 | 19 | 21 | 33 | 32 | 8 | 0 | 136 | 75 | 120 | 0 | 8 | 225 |  | 0 | 0 | 0 | 6 | 40 | 34 | 35 | 0 | 6 | 10 | 42 | 0 | 0 | 0 | 280 | 270 | 170 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 47 | 0 | 20 | 11 | 33 | 20 | 146 | 65 | 0 | 16 | 1.6 | 43 | 42 | 50 | 46 | 112 | 0 | 50 | 86 | 0 | 180 | 17 | 0 | 10 | 300 | 24 | 11 | 0 | 65 | 0 | 0 | 95 | 0 | 70 | 20 | 25 | 51 | 6 | 350 | 68 | 35 | 68 | 5 | 70 | 17 | 55 | 17 | 9 | 25 | 360 | 34 | 50 | 54 | 34 | 0 | 17 | 35 | 72 | 17 | 240 | 17 |  | 0 | 10 | 0 |  | 911 | 0 | 290 | 0 | 16 | 0 | 0 | 0 | 0 | 40 | 8 | 130 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 28 | 8 | 30 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 360 | 35 | 0 | 35 | 15 | 35 | 0 | 8 | 35 | 1244 | 220 |  | 17 | 6 | 100 | 35 | 0 |  | 568 | 30 | 0 | 1200 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 140 | 180 | 0 | 12 | 0 | 355 | 301 | 0 | 0 | 350 | 0 | 34 | 17 | 15 | 280 | 0 | 93 | 17 | 8 | 16 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 21 | 30 | 33 | 8 | 0 | 136 | 75 | 120 | 0 | 8 | 224 | 0 | 0 | 0 | 0 | 6 | 34 | 16 | 35 | 0 | 6 | 10 | 42 | 0 | 0 | 0 | 270 | 240 | 172 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 23 | 0 | 14 | 10 | 25 | 17 | 110 | 65 | 0 | 16 | 1 | 43 | 40 | 50 | 45 | 80 | 0 | 59 | 75 | 0 | 181 | 0 | 0 | 10 | 290 | 24 | 11 | 0 | 65 | 0 | 0 | 18 | 0 | 35 | 2 | 25 | 17 | 18 | 353 | 67 | 17 | 34 | 3 | 70 | 17 | 55 | 17 | 9 | 25 | 350 | 53 | 19 | 17 | 17 | 0 | 17 | 19 | 18 | 17 | 230 | 17 | 0 | 0 | 19 | 0 | 0 | 439 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 124 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 360 | 35 | 0 | 35 | 15 | 34 | 0 | 1 | 35 | 1244 | 188 | 0 | 17 | 2 | 27 | 0 | 0 | 0 | 568 | 10 | 0 | 1206 | 92 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
292.3904
| Minimum Generation |  | 11389 | 8:00
| Highest Generation |  | 14392 | 21:00
| Day Peak Generation |  | 12309 | 12:00
| Evening Peak Generation |  | 14392 | 21:00
| HVDC Max Flow |  | 913 | 10:00
| HVDC EvPeak Flow |  | 794 | 21:00
| Load factor L.F |  | 86.66% | [164 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-08-18
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-08-17 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 12309 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 11235
Evening Peak Generation : |  |  | 14392 | MW Hour : | 21:00 | Available Max Generation : |  | 15312
E.P. Demand (at gen end) : |  |  | 14850 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14300
Maximum Generation : |  |  | 14392 | MW Hour : | 21:00 | Reserve(Generation end) |  | 1012
Total Gen. (MKWH) : |  |  | 299.3278 | System Load Factor : | 86.66% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 580 | MW at | 19:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-08-18
Actual : |  | 102.65 | Ft.(MSL) , | Rule curve : | 94.44 | Ft.( MSL )
Gas Consumed : |  | Total = | 1122.1 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 159064268.938
: |  |  | Coal : | 308335337 | Oil : | 561350207.2 | Total : | 1028749813.138
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 45 | 1080:00 | 4986.8826 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1372.8008 |  |  | 0 | 0%
Khulna Area |  | 10 | 240:00 | 1923.7853 |  |  | 0 | 0%
Rajshahi Area |  | 45 | 1080:00 | 1672.8176 |  |  | 0 | 0%
Cumilla Area |  | 113 | 2712:00 | 1376.0741 |  |  | 0 | 0%
Mymensingh Area |  | 114 | 2736:00 | 1023.8281 |  |  | 0 | 0%
Sylhet Area |  | 10 | 240:00 | 573.4853 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 478.2986 |  |  | 0 | 0%
Rangpur Area |  | 100 | 2400:00 | 935.4597 |  |  | 0 | 0%
Total |  | 437 |  | 14343.4322 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
09:06 | 13:52 | Kabirpur - Manikganj 132kV Ckt-1 Scheduled S/D from Manikganj 132/33kV end Due to Red hot removal.
09:06 | 13:52 | Manikganj 132/33kV Transformer GT-4 (50/75 MVA) LT Scheduled S/D Due to Red hot removal.
09:06 | 16:03 | Madunaghat-Sikalbaha 132kV Ckt-2 Scheduled S/D from Madunaghat 132/33kV end Due to For line inspection and
river-crossing conductor(Karnafully River) maintenance work.
09:07 | 16:03 | Shikalbaha 230/132kV S/S Modunaghat Ckt-1 Scheduled S/D Due to Maintenance at Madunaghat end.
09:18 | 11:28 | Chandraghona-Rangamati 132 kV Ckt-2 Scheduled S/D from Rangamati 132/33kV end Due to Red hot.
09:24 | 17:55 | Gopalganj 400/132kV S/S ATR-03 LT Project Work S/D
| 10:33 | Sirajgonj 230 S/S SNWPCL (Unit-04) is restored.
11:10 |  | Khulna 330 MW CCPP GT was sync.
13:13 |  | Siddirganj CCPP 335MW tripped
13:13 | 14:25 | Siddhirganj 230/132kV S/S 335MW EGCB 1 Tripped showing CB Lock out relays. |  |  |  |  | 210MW generation interrup.
14:06 |  | Siddhirganj GT:Unit-1 was sync.
14:20 | 16:25 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75MVA) HT Scheduled S/D
15:01 |  | Sirajganj unit-4 GT was sync
15:20 | 16:04 | Purbasadipur 132/33kV S/S T-1 Transformer (403T) HT Tripped showing No Operated relays. |  |  |  |  | 40 MW Load interrupt.
15:20 | 15:57 | Purbasadipur 132/33kV S/S T-3 Transformer (423T) LT Tripped showing ALSOM MCGG relays. |  |  |  |  | 20 MW Load interrupt.
15:37 | 19:35 | Chauddagram-Feni 132 kV Ckt-2 Tripped from Feni end showing Distance C phase, SOTF relays Due to Un known |  |  |  |  | 40 MW Load interrupt.
and from Chauddagram 132/33kV end showing REL 670 & REC650 relays Due to Line to ground fault.
15:58 |  | Siddirganj CCPP 335MW GT was sync .
16:15 |  | Sirajganj unit-4 ST was sync
17:24 | 18:49 | Madunaghat 132/33kV S/S TR-1 S/D Due to For hot spot and loose connection tightening at 132kV GIS Duck end. |  |  |  |  | 27 MW Load interrupt.
18:58 |  | Siddirganj CCPP 335MW ST was sync
20:20 |  | Siddhirganj GT:Unit-2 was shutdown due to gas shortage.
21:43 |  | Bibiyana-3 400MW ST was sync.
| 22:55 | New Tongi S/S Tr-2(4161-3) is restored.
05:10 |  | HVDC 500 MW BLOCK-1 was shutdown.- due to corrective maintenance.
05:52 |  | Mymensing 132kV BUS Coupler Close due to 132kV B-Bus Shut down purposes of High Temperature Maintenance . |  |  |  |  | 150 MW Load interrupt.
06:01 |  | 132kV Bhaluka Ckt-2 Shut down due to High Temperature Maintenance in 132kV B-Bus DS R Phase T- Clamp of |  |  |  |  | 40 MW Load interrupt.
132kV Bhaluka Ckt-2.
06:15 |  | Narshingdi 132/33kV S/S T-3 HT Forced S/D Due to heating issues . |  |  |  |  | 47 MW Load interrupt.
06:52 |  | APR-Hasnabad 230kV Ckt-2 S/D from Hasnabad 230/132kV end Due to LILO Connection out at APR Power Plant.
06:55 |  | Shyampur 230/132kV S/S 230 kV APR (D04) Scheduled S/D Due to Hasnabad grid will work at APR END.
07:18 |  | HVDC 500 MW BLOCK-1 was switched on.
07:29 |  | Maniknagar 230/132kV S/S Auxiliary Transformer-02 HT Scheduled S/D Due to Oil Filling Work.
07:31 |  | Maniknagar-Siddhirganj 230kV Ckt-2 S/D from Siddhirganj end Due to Transformer will work for Maniknagar end.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-08-17 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 120 | 3309906
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4252500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 296909 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 390 | 9566120
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 332 | 7924000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10281000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 49 | 498240 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Under maint.
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 51 | 496877 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 371551 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 33 | 877297 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 300708 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 37 | 2020000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 38 | 555840 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 318 | 5790148 | gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 687600
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 388800 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 415680 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 0 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 440847
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 38 | 864960 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 759960
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 8 | 540500
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 24 | 277920 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 148 | 2034871 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Contract Expired
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1785456
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1090166 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 43 | 821760 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1355040
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 201830
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 430920 | Fuel shortage
| Dhaka area Total |  |  |  | 5722 | 2994 | 58637406
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 123 | 2600000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 143782
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 111915
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 40 | 364320
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 211 | 4299167
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 224 | 5262440
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 68 | 1435199 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 59 | 992352 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 32 | 782001 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 46 | 881400 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 691200 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 10 | 233952 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 33 | 526080
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 12 | 74880 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30084
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 297 | 2421273
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 434261 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 55 | 1308070 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 690240 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 51 | 775309 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 125 | 936727 | Fuel shortage
| SS Power I |  | SS Power | 0 | 0 | 0 | 0 | On test.
| Cox's Bazar Wind |  | IPP | 66 | 0 | 21 | 232800 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2545 | 1524 | 25227452
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 188 | 4206000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 270 | 7019500 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 240 | 5986000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 230 | 5838600 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 0 | 0 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1142864
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 135 | 1184290 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 38 | 890416
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 103 | 1223040 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 14 | 327384 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 240480
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 106 | 2723520
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 610100 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 17731 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 17 | 455280 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 106 | 799140 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 29 | 319200 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 441720 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 96 | 1332480 | Fuel shortage
| Cumilla Area Total |  |  |  | 3096 | 1675 | 34757745
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 85 | 1498560 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 360108 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14700
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 147 | 924000 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 84 | 1718400 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 359630
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 144720 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 338 | 5020118
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 988500 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 921720 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2506582 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1198200
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 45 | 1023192
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 3 | 108000 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 55 | 1193760
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1961280
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 181 | 4629040 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 382000 | Machine problem
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 517320
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7347000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 80 | 5039000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 243900
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 350 | 8357800
| Sylhet Area Total |  |  |  | 2427 | 1396 | 36417294
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 794 | 21282909
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 64 | 400320
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 21 | 231360
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 37 | 597248
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 210 | 6416640 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 76875 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 297600 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 67 | 832752
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 525262
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 220 | 150 | 1625222
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 564 | 12581820
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 3121 | 1932 | 44868008
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1376
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 33 | 650861 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 130 | 3049000 | ST Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 31404900
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 222 | 5254036
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1161600
| Barisal 307 MW |  | IPP | 307*1 | 307 | 0 | 0 | Coal shortage.
| Barisal Area Total |  |  |  | 2265 | 1889 | 41521773
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 28 | 278794 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 26 | 73270 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 28 | 658180
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 240130 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage.
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 194 | 5058327 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 3996981
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 23 | 112220 | Fuel shortage
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 182034 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 177758 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 1635258 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 963360 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 908832 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 37860
| Adani Power Jharkhanda Ltd |  | Import | 748*2 | 1496 | 1362 | 30834545
| Rajshahi Area Total |  |  |  | 3631 | 2293 | 45157549
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 220 | 4797200 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 56 | 939091 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 52954
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 75 | 494016 | Fuel shortage
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 226987
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 1210200
| Rangpur Area Total |  |  |  | 750 | 351 | 7720448
| Total |  |  |  | 24171 | 14392 | 299327793
| Eastern Grid Total |  |  |  | 14404 | 7927 | 160060015
| Western Grid Total |  |  |  | 9767 | 6465 | 139267778
| National Grid Total |  |  |  | 24171 | 14392 | 299327793
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-08-17
| (a) ENTIRE EASTERN GRID : |  | 9210.56 | MW | (b) ENTIRE WESTERN GRID : |  | 4605.5 | MW
| i) Dhaka area |  | 4972.56 | MW | i) Khulna area |  | 1744 | MW
| ii) Chittagong area |  | 1304 | MW | ii) Rajshahi area |  | 1517 | MW
| iii) Comilla area |  | 1241 | MW | iii) Barisal area |  | 477.5 | MW
| iv) Mymensingh area |  | 1101 | MW | iv) Rangpur area |  | 867 | MW
| v) Sylhet area |  | 592 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 13816.06 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 35 | 19:00 | Kamrangirchar | 56.7 | 13:00 | Natore | 162 | 21:00 | Sholosohor | 39 | 18:00
2 | AKSML | 99 | 14:00 | Chowmuhani | 194 | 22:00 | Kaptai | N/A | N/A | Nawabganj | 52.3 | 22:00 | Shyampur | 162 | 11:00
3 | Aftabnagar | 60 | 12:00 | Chuadanga | 121 | 22:00 | Kazla | 94 | 20:00 | Netrakona | 125 | 20:00 | Siddhirganj | 102 | 12:00
4 | Agargaon | 91 | 15:00 | Coxsbazar | 122 | 19:30 | Keranigonj | 78 | 19:30 | New | 29 | 16:00 | Sirajganj | 122 | 19:00
5 | Agrabad | 78 | 17:00 | Cumilla(N) | 176 | 20:00 | Khagrachori | 34 | 18:30 | Niamatpur | 81 | 00:00 | Sonargaon | 82 | 20:00
6 | Amnura | 56 | 21:00 | Cumilla(S) | 154 | 13:00 | Khulna | 102 | 20:00 | Noapara | 50 | 20:00 | Sreemongol | 73 | 21:00
7 | Ashuganj | 71 | 21:00 | Daudkandi | 140 | 21:00 | Khulshi | 187 | 20:00 | PHP | 5 | 02:00 | Sreepur | 76 | 18:30
8 | BIPTC | N/A | N/A | Dhaka | 44 | 11:00 | Kishoreganj | 128 | 22:00 | Pabna | 130 | 21:00 | Srinagar | 49.16 | 22:00
9 | BSRM | 161 | 09:00 | Dhamrai | 120 | 19:30 | Kodda | 270 | 21:00 | Palashbari | 119 | 07:00 | Sunamganj | 61 | 20:00
10 | Bagerhat | 88 | 00:00 | Dhanmondi | 162 | 13:00 | Kulaura | 56 | 21:00 | Panchagarh | 53 | 18:30 | Sylhet | 182 | 18:30
11 | Bakulia | 104 | 20:00 | Dohazari | 102 | 19:30 | Kurigram | 65 | 18:30 | Patuakhali | 112 | 00:00 | TK | 0 | 00:00
12 | Banani | 64 | 15:00 | Faridpur | 166 | 20:00 | Kushtia | 142 | 20:00 | Payra | 25.2 | 00:00 | Tangail | 231 | 22:00
13 | Bangabhaban | 16 | 10:00 | Fatullah | 67 | 10:00 | Lalbag | 78 | 18:00 | Postogola | 59 | 00:00 | Thakurgaon | 93 | 21:00
14 | Barapukuria | 64 | 21:00 | Fenchuganj | 50 | 19:30 | Lalmonirhat | 53 | 18:00 | Purbachal | 20 | 15:00 | Tongi | 142 | 18:30
15 | Barguna | 20 | 00:00 | Feni | 128 | 22:00 | Madanganj | 34 | 19:00 | Purbasadipur | 118 | 19:00 | Ullon | 52 | 19:00
16 | Barishal | 106 | 19:30 | GPH | 11 | 14:00 | Madaripur | 114 | 21:00 | Rahim | 44 | 11:00 | Uttara | 80 | 13:00
17 | Barishal-230 | 106 | 19:30 | Ghorashal | 60 | 23:00 | Madartek | 86.33 | 19:30 | Rajbari | 78 | 21:00 | UttaraNew | 69 | 19:00
18 | Baroaulia | 79 | 00:00 | Goalpara | 36 | 00:00 | Madunaghat | 46 | 23:00 | Rajendrapur | 100 | 21:00 | Zigatola | 76 | 13:00
19 | Baroirhat | 71 | 19:00 | Gollamari | 53 | 00:00 | Magura | 68 | 20:00 | Rajshahi | 172 | 19:30
20 | Bashundhara | 157 | 16:00 | Gopalganj | 108 | 20:00 | Mahasthangarh | 78 | 19:00 | Rajshahi-230 | 38 | 22:00
21 | BashundharaCement | 1 | 09:00 | Gulshan | 80 | 15:00 | Manikganj | 120 | 22:00 | Ramganj | 110 | 21:00
22 | Beanibazar | 64 | 05:00 | Halishahar | 76.5 | 19:30 | Maniknagar | 76 | 14:00 | Rampur | 30 | 18:30
23 | Benapole | 66 | 20:00 | HaripurSBU | 154 | 21:00 | Matarbari | 49 | 20:00 | Rangamati | 14 | 18:30
24 | Bhaluka | 118 | 19:00 | Hasnabad | 99 | 19:30 | Matuail | 70 | 11:00 | Rangpur | 134 | 20:00
25 | Bhandaria | 52 | 21:00 | Hathazari | 83 | 19:00 | Millgate | 117 | 12:00 | Ruppur | 6.2 | 16:00
26 | Bhangura | 38 | 19:00 | Ishurdi | 84 | 19:30 | Mirpur | 138 | 19:00 | SSM | 0 | 00:00
27 | Bheramara(GK) | 69 | 21:00 | Jaldhaka | 77 | 20:00 | Mirsorai | 0 | 00:00 | Saidpur | 94 | 23:00
28 | Bhulta | 234 | 20:00 | Jamalpur | 160 | 20:00 | Mithapukur | 50 | 21:00 | Satkhira | 120 | 22:00
29 | Bog-Sherpur | 70 | 19:30 | Jashore | 148 | 19:30 | Modern | 0 | 00:00 | Satmasjid | 116 | 19:00
30 | Bogura | 189 | 20:00 | Jhenaidah | 131 | 20:00 | Mogbazar | 145.8 | 14:00 | Savar | 204 | 18:30
31 | Borhanuddin | 68 | 00:00 | Joydebpur | 185 | 21:00 | Mongla | 28 | 00:00 | Shahjadpur | 117 | 21:00
32 | Brahmanbaria | 158 | 20:00 | Joypurhat | 59 | 19:00 | Motijheel | 41 | 13:00 | Shahjibazar | 130 | 19:00
33 | Cantonment | 149 | 16:00 | Juldah | 21 | 11:00 | Munshiganj | 111 | 23:00 | Shahmirpur | 77 | 23:00
34 | Chandpur | 64 | 21:00 | KSRM | 31.5 | 23:00 | Mymensingh | 226 | 21:00 | Shariatpur | 84 | 21:00
35 | Chandraghona | 31 | 19:00 | Kabirpur | 294 | 19:30 | Naogaon | 132 | 21:00 | Sherpur | 142 | 21:00
36 | Chapai | 69 | 00:00 | Kachua | 74 | 21:00 | Narail | 61 | 20:00 | Shikalbaha | 36 | 04:00
37 | Charsaidpur | 47 | 02:00 | Kallyanpur | 114 | 19:00 | Narinda | 72 | 13:00 | Shikalbaha-230 | N/A | N/A
38 | Chauddagram | 55 | 18:30 | Kalurghat | 30 | 18:30 | Narshingdi | 170 | 21:00 | Shitalakhya | 110 | 16:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-08-17 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 397 | 06:00 | 385 | 12:00 | Gopalganj | 403 | 06:00 | 394 | 15:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 380 | 19:30 | 367 | 12:00
| Bhulta | 394 | 06:00 | 384 | 11:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 402 | 10:00 | 396 | 00:00 | Payra | 411 | 19:00 | 406 | 13:00
| BIPTC | 401 | 22:00 | 392 | 12:00 | Rampal | N/A | N/A | N/A | N/A
| Bogura | N/A | N/A | N/A | N/A |  | 404 | 06:00 | 397 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 231 | 00:00 | 223 | 12:00 | Hasnabad | 230 | 00:00 | 222 | 15:00
| AKSML | 237 | 20:00 | 227 | 02:00 | Hathazari | 236 | 20:00 | 227 | 08:00
| Aminbazar | 234 | 01:00 | 225 | 12:00 | Ishurdi | 232 | 22:00 | 225 | 12:00
| Ashuganj | 234 | 00:00 | 225 | 12:00 | Jhenaidah | 223 | 09:00 | 218 | 11:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 236 | 07:00 | 224 | 12:00
| Baghabari | 226 | 18:00 | 220 | 11:00 | Keranigonj | 230 | 06:00 | 222 | 12:00
| Barapukuria | 217 | 08:00 | 210 | 00:00 | Khulna(S) | 230 | 09:00 | 226 | 11:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 238 | 18:00 | 233 | 04:00 | Maniknagar | 230 | 05:00 | 221 | 13:00
| Bheramara | 232 | 22:00 | 224 | 11:00 | Meghnaghat | 232 | 00:00 | 227 | 12:00
| Bhulta | 233 | 06:00 | 225 | 12:00 | Mirsorai | 238 | 20:00 | 224 | 09:00
| Bibiana | 232 | 07:00 | 227 | 10:00 | Rajshahi | 229 | 18:00 | 220 | 11:00
| BIPTC | 231 | 14:00 | 223 | 12:00 | Rampal | 230 | 06:00 | 225 | 10:00
| Bogura | 223 | 09:00 | 217 | 19:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 240 | 01:00 | 238 | 03:00 | Rampura | 232 | 04:00 | 223 | 12:00
| BSRM | 236 | 20:00 | 224 | 09:00 | Shikalbaha | 237 | 21:00 | 228 | 09:00
| Cumilla(N) | 229 | 19:30 | 223 | 12:00 | Shyampur | 230 | 06:00 | 222 | 12:00
| Fenchuganj | 236 | 19:30 | 231 | 12:00 | Siddhirganj | 232 | 02:00 | 224 | 11:00
| Ghorashal | 235 | 00:00 | 230 | 12:00 | Sirajgonj | 236 | 19:00 | 226 | 12:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 228 | 00:00 | 223 | 16:00
| GPH | 236 | 21:00 | 226 | 11:00 | Tongi | 230 | 00:00 | 219 | 13:00
| Haripur | 230 | 03:00 | 223 | 15:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 135 | 06:00 | 127 | 12:00 | Lalbag | 136 | 06:00 | 129 | 13:00
| Agargaon | 133 | 05:00 | 126 | 12:00 | Lalmonirhat | 126 | 08:00 | 118 | 00:00
| Agrabad | 136 | 21:00 | 130 | 17:00 | Madanganj | 132 | 07:00 | 125 | 13:00
| AKS | 134 | 21:00 | 130 | 02:00 | Madaripur | 131 | 17:00 | 128 | 11:00
| Aminbazar | 134 | 00:00 | 123 | 12:00 | Madartek | 134 | 02:00 | 127 | 15:00
| Amnura | 138 | 00:00 | 121 | 00:00 | Madunaghat | 137 | 21:00 | 132 | 07:00
| Ashuganj | 140 | 00:00 | 135 | 12:00 | Magura | 133 | 17:00 | 126 | 20:00
| Bagerhat | 130 | 09:00 | 122 | 00:00 | Mahasthangarh | 132 | 09:00 | 125 | 04:00
| Bakulia | 138 | 14:00 | 133 | 07:00 | Manikganj | 134 | 19:00 | 125 | 10:00
| Banani | 136 | 05:00 | 126 | 15:00 | Maniknagar | 134 | 04:00 | 127 | 16:00
| Bangabhaban | 134 | 03:00 | 127 | 16:00 | Matarbari | 135 | 11:00 | 114 | 18:30
| Barapukuria | 134 | 08:00 | 129 | 00:00 | Matuail | 132 | 19:30 | 128 | 11:00
| Barguna | 138 | 19:00 | 133 | 03:00 | Millgate | 134 | 00:00 | 126 | 12:00
| Barishal | 138 | 19:00 | 131 | 05:00 | Mirpur | 133 | 05:00 | 127 | 12:00
| Barishal-230 | 137 | 14:00 | 133 | 04:00 | Mithapukur | 129 | 08:00 | 120 | 04:00
| Baroaulia | 136 | 20:00 | 132 | 07:00 | Modern | 136 | 20:00 | 131 | 08:00
| Baroirhat | 130 | 20:00 | 123 | 04:00 | Mogbazar | 136 | 01:00 | 127 | 14:00
| Bashundhara | 135 | 03:00 | 126 | 12:00 | Mongla | 129 | 09:00 | 122 | 00:00
| BashundharaCement | 132 | 07:00 | 125 | 13:00 | Motijheel | 134 | 03:00 | 127 | 16:00
| Beanibazar | 130 | 19:00 | 126 | 00:00 | Munshiganj | 131 | 03:00 | 126 | 13:00
| Benapole | 132 | 18:00 | 124 | 20:00 | Mymensingh | 135 | 22:00 | 114 | 12:00
| Bhaluka | 127 | 00:00 | 116 | 12:00 | Naogaon | 128 | 09:00 | 120 | 01:00
| Bhandaria | 137 | 19:00 | 129 | 00:00 | Narail | 132 | 09:00 | 125 | 20:00
| Bhangura | 134 | 00:00 | 128 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 133 | 06:00 | 131 | 11:00 | Narshingdi | 130 | 20:00 | 118 | 11:00
| Bheramara(GK) | 134 | 03:00 | 131 | 20:00 | Natore | 132 | 06:00 | 128 | 19:00
| Bhulta | 123 | 00:00 | 118 | 12:00 | Nawabganj | 135 | 01:00 | 128 | 13:00
| Bog-Sherpur | 131 | 00:00 | 121 | 19:00 | Netrakona | 133 | 22:00 | 118 | 03:00
| Bogura | 134 | 08:00 | 129 | 03:00 | New | 135 | 00:00 | 126 | 12:00
| Bogura-230 | 134 | 18:00 | 128 | 19:00 | Niamatpur | 130 | 07:00 | 116 | 19:00
| Brahmanbaria | 127 | 17:00 | 120 | 18:30 | Noapara | 132 | 18:00 | 127 | 01:00
| Cantonment | 133 | 06:00 | 126 | 12:00 | Pabna | 131 | 00:00 | 128 | 12:00
| Chandpur | 130 | 18:00 | 116 | 03:00 | Palashbari | 127 | 08:00 | 119 | 03:00
| Chandraghona | 138 | 21:00 | 133 | 08:00 | Panchagarh | 128 | 17:00 | 112 | 06:00
| Chapai | 128 | 17:00 | 122 | 00:00 | Patuakhali | 139 | 00:00 | 135 | 01:00
| Charsaidpur | 133 | 19:30 | 127 | 12:00 | Payra | 139 | 00:00 | 137 | 01:00
| Chauddagram | 130 | 18:00 | 125 | 21:00 | PHP | 130 | 20:00 | 122 | 03:00
| Chhatak | 128 | 02:00 | 124 | 19:00 | Postogola | 139 | 11:00 | 129 | 11:00
| Chowmuhani | 127 | 18:00 | 117 | 01:00 | Purbachal | 135 | 02:00 | 126 | 11:00
| Chuadanga | 128 | 06:00 | 120 | 21:00 | Purbasadipur | 125 | 08:00 | 111 | 03:00
| Coxsbazar | 129 | 00:00 | 118 | 22:00 | Rahanpur | N/A | N/A | N/A | N/A
| Cumilla(N) | 132 | 18:00 | 127 | 11:00 | Rahim | 133 | 20:00 | 128 | 11:00
| Cumilla(S) | 132 | 03:00 | 126 | 06:00 | Rajbari | 128 | 09:00 | 124 | 19:00
| Daudkandi | 130 | 18:00 | 125 | 12:00 | Rajendrapur | 135 | 19:30 | 125 | 13:00
| Dhaka | 136 | 05:00 | 127 | 12:00 | Rajshahi | 134 | 09:00 | 129 | 13:00
| Dhamrai | 135 | 00:00 | 129 | 12:00 | Rajshahi-230 | 136 | 17:00 | 120 | 21:00
| Dhanmondi | 132.5 | 06:00 | 126.5 | 13:00 | Ramganj | 130 | 18:00 | 112 | 06:00
| Dohazari | 134 | 10:00 | 128 | 23:00 | Rampur | 136 | 19:30 | 130 | 09:00
| Faridpur | 128 | 07:00 | 125 | 04:00 | Rampura | 135 | 04:00 | 127 | 13:00
| Fatullah | 130 | 19:30 | 124 | 11:00 | Rangamati | 136 | 00:00 | 132 | 08:00
| Fenchuganj | 134 | 17:00 | 131 | 01:00 | Rangpur | 128 | 09:00 | 113 | 04:00
| Feni | 130 | 20:00 | 122 | 03:00 | Ruppur | 134 | 06:00 | 130 | 11:00
| Ghorashal | 140 | 00:00 | 135 | 12:00 | Saidpur | 128 | 16:00 | 116 | 05:00
| Goalpara | 133 | 17:00 | 127 | 01:00 | Satkhira | 130 | 18:00 | 123 | 00:00
| Gollamari | 133 | 18:00 | 129 | 00:00 | Satmasjid | 133 | 06:00 | 126 | 12:00
| Gopalganj | 132 | 18:00 | 127 | 01:00 | Savar | 133 | 04:00 | 128 | 08:00
| Gopalganj-400 | 129 | 06:00 | 126 | 11:00 | Shahjadpur | 137 | 00:00 | 133 | 12:00
| Gulshan | 135 | 06:00 | 126 | 13:00 | Shahjibazar | 129 | 17:00 | 125 | 02:00
| Halishahar | 137 | 20:00 | 131 | 23:00 | Shahmirpur | 137 | 19:30 | 133 | 07:00
| Haripur | 133 | 20:00 | 128 | 11:00 | Shariatpur | 130 | 18:00 | 126 | 21:00
| HaripurSBU | 133 | 20:00 | 128 | 11:00 | Sherpur | 133 | 22:00 | 116 | 08:00
| Hasnabad | 134 | 02:00 | 129 | 12:00 | Shikalbaha | 125 | 00:00 | 122 | 08:00
| Hathazari | 139 | 21:00 | 133 | 17:00 | Shikalbaha-230 | 138 | 21:00 | 134 | 04:00
| Ishurdi | 134 | 00:00 | 131 | 11:00 | Shitalakhya | 133 | 19:30 | 127.4 | 12:00
| Jaldhaka | 127 | 09:00 | 115 | 04:00 | Sholosohor | 135 | 00:00 | 131 | 09:00
| Jamalpur | 135 | 22:00 | 120 | 05:00 | Shyampur | 129 | 19:30 | 124 | 11:00
| Jashore | 131 | 08:00 | 126 | 20:00 | Shyampur-230 | 129 | 00:00 | 123 | 12:00
| Jhenaidah | 135 | 09:00 | 130 | 20:00 | Siddhirganj | 133 | 19:30 | 128 | 12:00
| Jhenaidah-230 | 135 | 06:00 | 130 | 20:00 | Sirajganj | 132 | 00:00 | 123 | 11:00
| Joydebpur | 140 | 00:00 | 131 | 15:00 | Sonargaon | 130 | 00:00 | 126 | 14:00
| Joypurhat | 127 | 18:00 | 118 | 19:00 | Sreemongol | 129 | 09:00 | 126 | 21:00
| Juldah | 138 | 21:00 | 134 | 00:00 | Sreepur | 128 | 00:00 | 121 | 18:30
| Kabirpur | 136 | 19:30 | 124 | 11:00 | Srinagar | 135 | 04:00 | 129 | 12:00
| Kachua | 131 | 18:00 | 120 | 01:00 | SSM | 140 | 00:00 | 128 | 13:00
| Kaliakoir | 137 | 19:00 | 130 | 02:00 | Sunamganj | 126 | 09:00 | 120 | 19:00
| Kallyanpur | 129 | 04:00 | 124 | 12:00 | Sylhet | 130 | 05:00 | 128 | 20:00
| Kalurghat | 135 | 00:00 | 132 | 09:00 | Tangail | 133 | 19:30 | 125 | 18:30
| Kamrangirchar | 136 | 06:00 | 122 | 12:00 | Thakurgaon | 126 | 17:00 | 110 | 01:00
| Kaptai | N/A | N/A | N/A | N/A | TK | 138 | 00:00 | 134 | 07:00
| Kazla | 134 | 04:00 | 128 | 13:00 | Tongi | 136 | 04:00 | 129 | 11:00
| Keranigonj | 136 | 05:00 | 131 | 11:00 | Ullon | 135 | 06:00 | 127 | 11:00
| Khagrachori | 136 | 19:30 | 132 | 09:00 | Uttara | 134 | 06:00 | 127 | 12:00
| Khulna | 132 | 18:00 | 127 | 00:00 | UttaraNew | 133 | 05:00 | 126 | 13:00
| Khulna(S) | 133 | 22:00 | 128 | 11:00 | Zigatola | 136 | 06:00 | 129 | 13:00
| Khulshi | 134 | 00:00 | 130 | 09:00
| Kishoreganj | 131 | 00:00 | 124 | 12:00
| Kodda | 137 | 00:00 | 128 | 08:00
| KSRM | 137 | 19:00 | 130 | 11:00
| Kulaura | 131 | 17:00 | 129 | 21:00
| Kurigram | 127 | 09:00 | 115 | 05:00
| Kushtia | 133 | 08:00 | 130 | 11:00

## L-Curve
Date | 2023-08-17
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 740 | 7066 | 6077 | 13143 |  |  |  | QF-LDC-11
0:30 | 850 | 6794.5 | 5844.5 | 12639 | Date: | 2023-08-17
1:00 | 960 | 6523 | 5612 | 12135
1:30 | 945 | 6514.5 | 5565.5 | 12080
2:00 | 930 | 6506 | 5519 | 12025
2:30 | 915 | 6485.5 | 5462 | 11947.5 | [5 empty] | Gen. at Eve. Peak | 14392 | 14392 MW (21:00 )
3:00 | 900 | 6465 | 5405 | 11870 | [6 empty] | 21:00
3:30 | 880 | 6450.5 | 5392.5 | 11843 | [5 empty] | Gen. at Day Peak | 12309 | 12309 MW (12:00 )
4:00 | 860 | 6436 | 5380 | 11816 | [6 empty] | 12:00
4:30 | 865 | 6446.5 | 5323.5 | 11770 | [5 empty] | Highest Generation | 14392
5:00 | 870 | 6457 | 5267 | 11724 | [6 empty] | 21:00
5:30 | 825 | 6432 | 5208.5 | 11640.5
6:00 | 780 | 6407 | 5150 | 11557
6:30 | 770 | 6321.5 | 5184 | 11505.5
7:00 | 760 | 6236 | 5218 | 11454
7:30 | 775 | 6184 | 5237.5 | 11421.5
8:00 | 790 | 6132 | 5257 | 11389
8:30 | 845 | 6176 | 5288 | 11464
9:00 | 900 | 6220 | 5319 | 11539
9:30 | 930 | 6330.5 | 5327.5 | 11658
10:00 | 960 | 6441 | 5336 | 11777
10:30 | 945 | 6491.5 | 5424.5 | 11916
11:00 | 930 | 6542 | 5513 | 12055
11:30 | 940 | 6563.5 | 5618.5 | 12182
12:00 | 950 | 6585 | 5724 | 12309
12:30 | 965 | 6634.5 | 5717 | 12351.5
13:00 | 980 | 6684 | 5710 | 12394
13:30 | 990 | 6501 | 5754.5 | 12255.5
14:00 | 1000 | 6318 | 5799 | 12117
14:30 | 980 | 6237 | 5783.5 | 12020.5
15:00 | 960 | 6156 | 5768 | 11924
15:30 | 940 | 6193 | 5729.5 | 11922.5
16:00 | 920 | 6230 | 5691 | 11921
16:30 | 890 | 6192 | 5805 | 11997
17:00 | 860 | 6154 | 5919 | 12073
17:30 | 885 | 6349 | 5919 | 12268
18:00 | 910 | 6544 | 5919 | 12463
18:30 | 745 | 6952.5 | 6128 | 13080.5
19:00 | 580 | 7361 | 6337 | 13698
19:30 | 590 | 7612 | 6479 | 14091
20:00 | 590 | 7833 | 6446 | 14279 |  |  |  | Executive Engineer
20:30 | 725 | 7880 | 6455.5 | 14335.5 |  |  |  | Network Operation Division
21:00 | 860 | 7927 | 6465 | 14392
21:30 | 860 | 7821.5 | 6382.5 | 14204
22:00 | 860 | 7716 | 6300 | 14016 |  |  |  |  | Page 6 of 7
22:30 | 815 | 7545 | 6292 | 13837
23:00 | 770 | 7374 | 6284 | 13658
23:30 | 755 | 7220 | 6180.5 | 13400.5
24:00 | 740 | 7066 | 6077 | 13143
14392 MW (21:00 )
12309 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-08-17 |  | Energy |  | 299327793
[15 empty] | 43693 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 4237 | 788 | 2167 | 0 | 1849 | 3391 | 213 | 50 | 306 | 118 | 0 | 24 | 1295.935
0:30 | 4253.5 | 849.5 | 2055 | 0 | 1502.5 | 3298 | 207.5 | 75 | 262 | 124 | 0 | 12 | 1228.13 |  |  | Date: | 43693
1:00 | 4270 | 911 | 1943 | 0 | 1156 | 3205 | 202 | 100 | 218 | 130 | 0 | 0 | 1160.325
1:30 | 4269 | 887.5 | 1947 | 0 | 1140.5 | 3212.5 | 201.5 | 75 | 218 | 129 | 0 | 0 | 1165.1 | [9 empty] | Total Energy | 299.3278 | 299.3278 | Total Energy Gen 299.328 MKWHr Energy Not Served 21.891 MKWHr Energy Requirement 321.219 MKWHr
2:00 | 4268 | 864 | 1951 | 0 | 1125 | 3220 | 201 | 50 | 218 | 128 | 0 | 0 | 1169.875 | [9 empty] | Energy not Served | 21.8909 | 21.8909
2:30 | 4281.5 | 864 | 1948.5 | 0 | 1058.5 | 3214.5 | 200.5 | 50 | 211 | 119 | 0 | 0 | 1100.6375 | [9 empty] | Energy Requirement | 321.2187 | 321.2187
3:00 | 4295 | 864 | 1946 | 0 | 992 | 3209 | 200 | 50 | 204 | 110 | 0 | 0 | 1031.4
3:30 | 4281.5 | 888 | 1924.5 | 0 | 987.5 | 3204.5 | 199.5 | 50 | 196.5 | 111 | 0 | 0 | 985.56 | [8 empty] | Shortage
4:00 | 4268 | 912 | 1903 | 0 | 983 | 3200 | 199 | 50 | 189 | 112 | 0 | 0 | 939.72
4:30 | 4278.5 | 912 | 1864.5 | 0 | 989.5 | 3200 | 199.5 | 25 | 189 | 112 | 0 | 0 | 888.15
5:00 | 4289 | 912 | 1826 | 0 | 996 | 3200 | 200 | 0 | 189 | 112 | 0 | 0 | 836.58
5:30 | 4300 | 912 | 1766 | 0 | 990.5 | 3176 | 200 | 0 | 186.5 | 105 | 2.5 | 2 | 749.1975
6:00 | 4311 | 912 | 1706 | 0 | 985 | 3152 | 200 | 0 | 184 | 98 | 5 | 4 | 661.815
6:30 | 4303.5 | 912 | 1714 | 0 | 978 | 3153 | 123 | 0 | 181.5 | 100 | 37.5 | 3 | 591.6225 | [7 empty] | Coal
7:00 | 4296 | 912 | 1722 | 0 | 971 | 3154 | 46 | 0 | 179 | 102 | 70 | 2 | 521.43
7:30 | 4264 | 911.5 | 1685 | 0 | 972.5 | 3155.5 | 46 | 0 | 179 | 103 | 104 | 1 | 647.9675 | [6 empty] | Oil
8:00 | 4232 | 911 | 1648 | 0 | 974 | 3157 | 46 | 0 | 179 | 104 | 138 | 0 | 774.505
8:30 | 4232 | 911.5 | 1640 | 0 | 994 | 3148.5 | 68.5 | 0 | 177.5 | 107 | 183 | 2 | 822.255
9:00 | 4232 | 912 | 1632 | 0 | 1014 | 3140 | 91 | 0 | 176 | 110 | 228 | 4 | 870.005
9:30 | 4222 | 912.5 | 1656.5 | 0 | 1059.5 | 3118.5 | 129 | 0 | 176 | 112 | 266 | 6 | 827.985
10:00 | 4212 | 913 | 1681 | 0 | 1105 | 3097 | 167 | 0 | 176 | 114 | 304 | 8 | 785.965
10:30 | 4201 | 912.5 | 1682 | 0 | 1163 | 3148.5 | 167 | 0 | 167.5 | 118 | 349 | 7.5 | 844.22
11:00 | 4190 | 912 | 1683 | 0 | 1221 | 3200 | 167 | 0 | 159 | 122 | 394 | 7 | 902.475
11:30 | 4197.5 | 912 | 1678.5 | 0 | 1246.5 | 3227 | 167 | 50 | 166.5 | 123 | 408.5 | 5.5 | 972.19
12:00 | 4205 | 912 | 1674 | 0 | 1272 | 3254 | 167 | 100 | 174 | 124 | 423 | 4 | 1041.905
12:30 | 4236.5 | 911.5 | 1678 | 0 | 1296.5 | 3252.5 | 167 | 100 | 181 | 128 | 396.5 | 4 | 1181.335
13:00 | 4268 | 911 | 1682 | 0 | 1321 | 3251 | 167 | 100 | 188 | 132 | 370 | 4 | 1320.765
13:30 | 4268 | 911 | 1682 | 0 | 1321 | 3251 | 167 | 100 | 188 | 132 | 370 | 4 | 1320.765
14:00 | 4268 | 911 | 1682 | 0 | 1321 | 3251 | 167 | 100 | 188 | 132 | 370 | 4 | 1320.765
14:30 | 3995.5 | 911.5 | 1680 | 0 | 1327 | 3250.5 | 187 | 113 | 222.5 | 123 | 340 | 9 | 1484.5475
15:00 | 3723 | 912 | 1678 | 0 | 1333 | 3250 | 207 | 126 | 257 | 114 | 310 | 14 | 1648.33
15:30 | 3725.5 | 912 | 1728.5 | 0 | 1373.5 | 3248 | 207 | 125.5 | 261 | 115 | 210.5 | 16 | 1506.5125
16:00 | 3728 | 912 | 1779 | 0 | 1414 | 3246 | 207 | 125 | 265 | 116 | 111 | 18 | 1364.695
16:30 | 3671 | 912 | 1911.5 | 0 | 1514.5 | 3218.5 | 207 | 112.5 | 247 | 104 | 76.5 | 22.5 | 1148.865
17:00 | 3614 | 912 | 2044 | 0 | 1615 | 3191 | 207 | 100 | 229 | 92 | 42 | 27 | 933.035
17:30 | 3655.5 | 912 | 2048.5 | 0 | 1751.5 | 3201 | 207 | 100 | 251 | 96 | 23.5 | 22 | 675.185
18:00 | 3697 | 912 | 2053 | 0 | 1888 | 3211 | 207 | 100 | 273 | 100 | 5 | 17 | 417.335
18:30 | 3716 | 911.5 | 2093 | 0 | 2291.5 | 3249 | 207 | 125 | 361.5 | 105 | 2.5 | 18.5 | 519.9975
19:00 | 3735 | 911 | 2133 | 0 | 2695 | 3287 | 207 | 150 | 450 | 110 | 0 | 20 | 622.66
19:30 | 3802 | 795 | 2090 | 0 | 2980 | 3347 | 207 | 233 | 515 | 104 | 0 | 18 | 512.3575
20:00 | 3919 | 794 | 2083 | 0 | 3081 | 3376 | 207 | 150 | 546 | 106 | 0 | 17 | 402.055
20:30 | 3915 | 794 | 2116.5 | 0 | 3101 | 3383 | 209 | 150 | 542 | 106 | 0 | 19 | 419.7225
21:00 | 3911 | 794 | 2150 | 0 | 3121 | 3390 | 211 | 150 | 538 | 106 | 0 | 21 | 437.39
21:30 | 3937 | 779.5 | 2145 | 0 | 2981 | 3389.5 | 211 | 100 | 531 | 112 | 0 | 18 | 593.055
22:00 | 3963 | 765 | 2140 | 0 | 2841 | 3389 | 211 | 50 | 524 | 118 | 0 | 15 | 748.72
22:30 | 4023.5 | 765 | 2145 | 0 | 2597 | 3390.5 | 211.5 | 50 | 519 | 119 | 0 | 16.5 | 848.04
23:00 | 4084 | 765 | 2150 | 0 | 2353 | 3392 | 212 | 50 | 514 | 120 | 0 | 18 | 947.36
23:30 | 4160.5 | 776.5 | 2158.5 | 0 | 2101 | 3391.5 | 212.5 | 50 | 410 | 119 | 0 | 21 | 1121.6475 |  |  | Max Temp. in Dhaka |  | 35.8° C
24:00 | 4237 | 788 | 2167 | 0 | 1849 | 3391 | 213 | 50 | 306 | 118 | 0 | 24 | 1295.935
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 299.328 MKWHr Energy Not Served 21.891 MKWHr Energy Requirement 321.219 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-08-17
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 127 | 126 | 125 | 124 | 125 | 125 | 46 | 46 | 71 | 92 | 92 | 92 | 92 | 92 | 132 | 132 | 132 | 132 |  | 132 | 132 | 132 | 136 | 136 | 137 | 138 | 2707167
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 0 |  | 20 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1592000
3 | Chattogram TPP-1 | 115 | 120 | 120 | 115 | 120 | 123 | 120 | 112 | 120 | 115 | 115 | 119 | 114 | 118 | 115 | 113 | 118 | 114 |  | 120 | 120 | 120 | 123 | 120 | 120 | 120 | 2600000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 1 | 8 | 8 | 8 | [8 empty] | 1 | 8 | 143782
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 2 | 2 | 8 | 12 | 17 | 14 | 14 | 7 | 15 | 11 | 2 | 0 | [8 empty] | 111915
6 | Sikalbaha 225MW CCPP (Gas) | 224 | 225 | 224 | 225 | 225 | 228 | 225 | 225 | 224 | 224 | 218 | 218 | 219 | 221 | 215 | 217 | 220 | 226 |  | 222 | 226 | 225 | 224 | 226 | 220 | 223 | 5262440
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 32 | 32 | 32 | 32 | 32 | 32 | 34 |  | 34 | 32 | 32 | 32 | 32 | 32 | 28 | 782001
12 | Hathazari 100 MW peaking PP | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 32 | 32 | 32 | 36 | 48 | 56 | 24 | 50 |  | 50 | 50 | 50 | 59 | 59 | 59 | 50 | 992352
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 51 | 51 | 51 | 51 | 51 | 34 | 34 | 34 | 34 | 51 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1435199
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 38 | 32 | 22 | 15 | 18 | 22 | 26 | 24 |  | 35 | 38 | 32 | 38 | 36 | 31 | 23 | 890416
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 68 | 67 | 62 | 59 | 59 | 60 | 62 | 62 | 64 | 62 | 64 | 62 | 59 | 92 | 148 | 150 | 121 | 98 |  | 121 | 121 | 77 | 37 | 37 | 37 | 38 | 2020000
17 | Siddhirganj 335 MW CCPP | 322 | 320 | 322 | 330 | 330 | 333 | 333 | 332 | 328 | 322 | 318 | 316 | 315 |  |  | 11 | 27 | 26 |  | 36 | 140 | 264 | 318 | 322 | 317 | 323 | 5790148
18 | Kodda 300 MW PP Unit-2 (Summit) | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 67 |  | 143 | 145 | 145 | 148 | 148 | 145 | 122 | 2034871
19 | Ashuganj 195 MW PP (APSCL-United) | [26 empty] | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 160 | 160 | 160 | 160 | 160 | 160 | 170 | 140 | 130 | 150 | 140 | 136 | 120 | 113 | 120 | 120 | 110 | 120 |  | 120 | 114 | 120 | 120 | 140 | 140 | 140 | 3309906
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4252500
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP
33 | Ashuganj 225 MW CCPP | 182 | 175 | 170 | 177 | 182 | 182 | 179 | 159 | 153 | 166 | 170 | 170 | 136 | 130 | 154 | 161 | 166 | 176 |  | 187 | 185 | 185 | 188 | 191 | 195 | 197 | 4206000
34 | Ashuganj 450 MW CCPP(South) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 330 | 260 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 5986000
| Ashuganj 450 MW CCPP(North) | 290 | 280 | 310 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 290 | 310 | 290 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 7019500
| Ashuganj 420 MW CCPP(East) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5838600
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 385 | 420 | 401 | 398 | 398 | 397 | 397 | 397 | 398 | 374 | 394 | 395 | 394 | 394 | 394 | 394 | 394 | 393 |  | 395 | 393 | 394 | 390 | 392 | 387 | 393 | 9566120
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 10281000
41 | Haripur 360 MW CCPP(HPL) | 343 | 342 | 342 | 343 | 343 | 337 | 336 | 337 | 313 | 332 | 332 | 321 | 317 | 317 | 318 | 318 | 317 | 321 |  | 332 | 321 | 327 | 332 | 332 | 333 | 332 | 7924000
42 | RPCL 210MW CCPP | 87 | 86 | 87 | 96 | 96 | 95 | 52 | 51 | 51 | 50 | 50 | 46 | 45 | 45 | 45 | 47 | 47 | 47 |  | 47 | 53 | 70 | 85 | 85 | 85 | 85 | 1498560
43 | Sutiakhali 50 MW Solar PP |  |  |  |  | 0 | 2 | 10 | 23 | 37 | 44 | 50 | 46 | 52 | 41 | 27 | 28 | 13 | 1 | [8 empty] | 359630
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 41 | 39 | 38 | 38 | 40 | 41 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 988500
45 | Fenchugonj CCPP Phase-2 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 39 | 40 | 39 | 39 | 39 | 39 | 38 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 921720
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 55 | 45 | 45 | 45 | 45 | 45 | 53 | 53 | 53 | 53 | 53 | 48 | 48 | 48 | 48 | 48 | 53 | 58 |  | 49 | 51 | 50 | 55 | 51 | 49 | 50 | 1193760
48 | Shahjibazar 86 MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 78 | 81 | 82 | 84 | 82 | 82 | 82 | 84 | 85 |  | 85 | 86 | 86 | 86 | 84 | 84 | 84 | 1961280
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 179 | 178 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179 |  | 179 | 179 | 179 | 181 | 181 | 180 | 180 | 4629040
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 382000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 243900
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 3 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 108000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 48 | 49 | 48 | 48 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1198200
56 | Shahjahanulla 25 MW PP | 16 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 517320
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 310 | 305 | 310 | 310 | 275 | 300 | 285 | 300 | 300 | 300 | 300 | 310 | 290 | 305 | 310 | 300 | 290 |  | 300 | 260 | 260 | 300 | 290 | 300 | 320 | 7347000
| Bibiyana South 400 MW | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 376 | 350 | 350 | 350 | 330 | 335 |  | 350 | 320 | 350 | 350 | 350 | 350 | 350 | 8357800
58 | Nababganj 55 MW PP (Southern power ) | [12 empty] | 17 | 17 | 17 | 17 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 440847
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 4 | 4 | 144720
60 | Barabkunda 22 MW PP (Regent) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 233952
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  |  |  |  | 19 | 19 | 19 |  | 19 |  | 19 | 19 |  |  |  | 15 | 19 | 300708
62 | Tangail 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 360108
63 | Impoprt (Tripura) | 130 | 128 | 110 | 112 | 112 | 98 | 102 | 104 | 110 | 114 | 122 | 124 | 132 | 154 | 114 | 116 | 92 | 100 |  | 110 | 104 | 106 | 106 | 118 | 120 | 118 | 2723520
64 | Malancha, Ctg. EPZ (United) | 35 | 35 | 35 | 36 | 36 | 36 | 32 | 7 | 2 | 2 | 2 | 6 | 6 | 10 | 10 | 10 | 15 | 19 |  | 26 | 26 | 15 | 33 | 35 | 41 | 41 | 526080
65 | Feni 22 MW PP (Doreen) | 16 | 16 | 15 | 15 | 15 | 15 | 13 | 13 | 13 | 13 | 13 | 13 | 15 | 13 | 14 | 9 | 12 | 13 |  | 14 | 14 | 15 | 14 | 14 | 14 | 14 | 327384
66 | Feni 11 MW PP (Doreen) | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 10 | 8 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 240480
67 | Jangalia 33 MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 610100
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 455280
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456000
70 | Summit Madhabdi | 20 | 0 | 20 | 18 | 18 | 19 | 19 | 19 | 19 | 20 | 7 | 18 | 17 | 18 | 18 | 18 | 17 | 17 |  | 17 | 17 | 17 | 19 | 18 | 18 | 18 | 408960
71 | Maona 33 MW PP(Summit) | 30 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 30 | 30 | 759960
72 | Rupganj 33 MW PP(Summit) | 32 | 32 | 32 | 32 | 32 | 32 | 24 | 24 | 24 | 24 | 8 | 22 | 22 | 22 | 14 | 14 |  | 15 |  | 16 | 16 | 16 | 8 | 20 | 24 | 32 | 540500
73 | Ghorashal 108 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 296909
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 50 | 106 | 106 | 106 | 106 | 52 | 799140
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 26 |  | 26 | 29 | 29 | 29 | 29 | 15 | 9 | 319200
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 144 | 162 | 162 | 162 | 162 | 36 | 17 | 1355040
77 | Siddhirganj 100 PP(Dutch Bangla) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 26 | 26 |  | 32 | 38 | 38 | 38 | 40 | 33 | 28 | 555840
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 24 | 24 | 24 | 24 | 24 | 25 | 8 | 277920
79 | Kodda 150 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 415680
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [14 empty] | 5 | 7 | [10 empty] | 17731
| Gazipur 100 MW PP | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 88 | 88 | 88 | 88 | 88 | 88 | 17 | 1090166
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 3 | 5 | 5 | 3 | 3 | 0 | [9 empty] | 30084
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 434261
| Karnaphuli Power Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 53 | 35 | 41 | 48 | 48 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1308070
82 | Madanganj 102 PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 21 |  | 51 | 51 | 51 | 51 | 36 | 34 | 22 | 496877
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 44 | 42 | 42 | 31 | 44 | 44 | 41 | 44 | 42 | 34 | 22 | 23 | 24 | 35 | 23 | 33 | 34 | 34 |  | 34 | 34 | 34 | 33 | 34 | 34 | 34 | 877297
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 9 | 8 | 8 | 8 | 8 | 8 | 9 | 8 | 8 | 9 | 7 | 9 | 8 | 8 | 14 | 45 | 49 | 49 |  | 48 | 50 | 49 | 49 | 38 | 25 | 24 | 498240
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 22 | 45 | 53 | 53 | 53 | 52 | 55 | 57 |  | 52 | 53 | 54 | 43 | 34 | 34 | 34 | 821760
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 35 | 881400
92 | Fenchuganj 44 MW (Energyprima) | 46 | 46 | 46 | 46 | 43 | 43 | 43 | 43 | 42 | 42 | 41 | 40 | 39 | 39 | 39 | 39 | 39 | 43 |  | 42 | 45 | 45 | 45 | 45 | 45 | 45 | 1023192
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 1142864
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 42 | 33 | 33 | 30 | 33 | 33 | 33 | 48 |  | 78 | 102 | 102 | 102 | 41 | 16 | 16 | 687600
95 | Patenga 50MW PP (Baraka) | 46 | 46 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 16 | 18 | 32 |  | 33 | 36 | 40 | 40 | 2 | 6 | 6 | 364320
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 11 | 12 |  | 12 | 12 | 12 | 12 | 12 |  |  | 74880
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 371551
100 | Manikganj 55 MW PP (Northern) | [9 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 17
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 80 | 80 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 |  | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 2506582
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 2 | 1 | 2 | 2 | 1 | 2 | 1 | 1 | 0 | [8 empty] | 14700
103 | Kamalaghat 54 MW PP(Banco Energy) | [9 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 388800
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 27 |  | 112 | 157 | 157 | 147 | 156 | 18 | 18 | 924000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 34 | 34 | 35 | 35 | 35 | 35 | 34 | 37 | 70 | 72 | 72 | 72 | 72 | 57 | 53 | 52 | 56 | 131 |  | 149 | 149 | 149 | 149 | 149 | 110 | 72 | 1785456
115 | Juldah 100 MW PP Unit-3 (Acorn) | 22 | 22 | 22 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 35 |  | 50 | 50 | 50 | 50 | 50 | 25 | 25 | 691200
116 | Chandpur 200 MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 38 | 51 | 51 | 51 | 51 | 51 | 49 | 51 | 78 |  | 102 | 102 | 104 | 103 | 105 | 101 | 60 | 1223040
117 | Ashuganj 150 MW PP (Midland) | 30 | 10 | 11 | 11 | 11 | 8 | 6 | 5 | 10 | 12 | 12 | 8 | 8 | 12 | 12 | 30 | 68 | 100 |  | 118 | 135 | 134 | 135 | 142 | 142 | 143 | 1184290
118 | Bibiyana-III 400 MW CCPP | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 278 | 260 | 250 | 280 | 80 | 80 | 15 | 80 |  | 80 | 80 | 80 | 80 | 118 | 248 | 400 | 5039000
| Jamalpur 115 MW PP (United) | 72 | 68 | 68 | 68 | 68 | 78 | 68 | 68 | 68 | 67 | 67 | 71 | 71 | 71 | 66 | 74 | 75 | 75 |  | 84 | 84 | 84 | 84 | 84 | 67 | 67 | 1718400
| Anwara 300 MW PP (United) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 69 | 69 | 69 | 122 |  | 250 | 287 | 284 | 297 | 132 | 88 | 88 | 2421273
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 50 | 50 | 50 | 50 | 25 | 690240
| Anlima Energy Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 36 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 775309
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 441720
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 4 | 12 | 18 | 23 | 15 | 31 | 28 | 28 | 22 | 14 | 8 | 2 | [8 empty] | 201830
| Chandpur 115(Doreen) | 17 | 18 | 17 | 18 | 18 | 17 | 18 | 17 | 18 | 30 | 60 | 72 | 72 | 72 | 72 | 55 | 72 | 83 |  | 96 | 95 | 96 | 96 | 96 | 96 | 96 | 1332480
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 430920
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 69 | 108 | 141 | 125 | 141 | 141 | 17 | 936727
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 0 | 0 | 0 | 0 | 4 | 2 | 0 | 4 | 8 | 7 | 4 | 4 | 12 | 14 | 18 | 27 | 17 |  | 20 | 18 | 17 | 21 | 15 | 18 | 24 | 232800
| Matarbari 2*600 MW (CPGCL) | [26 empty] | 0
120 | Eastern Zone Total | 6523 | 6506 | 6465 | 6436 | 6457 | 6407 | 6236 | 6132 | 6220 | 6441 | 6542 | 6585 | 6684 | 6318 | 6156 | 6230 | 6154 | 6544 | 0 | 7361 | 7612 | 7833 | 7927 | 7716 | 7374 | 7066 | 160060015
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [13 empty] | 16 | 16 | 32 | 32 | 32 |  | 46 | 46 | 54 | 64 | 64 | 64 | 0 | 400320
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL) | 100 | 50 | 50 | 50 | 0 | [6 empty] | 100 | 100 | 100 | 126 | 125 | 100 | 100 |  | 150 | 233 | 150 | 150 | 50 | 50 | 50 | 1625222
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14 |  | 32 | 45 | 31 | 21 | 21 | 21 | 10 | 231360
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [7 empty] | 2 |  | 6 | 9 | 12 | 17 | 22 | 32 | 35 | 297600
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 1 | 12 | 29 | 34 | 44 | 83 | 87 | 34 | 95 | 80 | 10 | 7 | 1 | [8 empty] | 525262
131 | Rampal 1320 MW (BIFPCL) | 518 | 521 | 519 | 520 | 519 | 520 | 522 | 523 | 520 | 500 | 500 | 499 | 500 | 500 | 500 | 494 | 506 | 557 |  | 565 | 536 | 565 | 564 | 566 | 567 | 566 | 12581820
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 45 | 137 | 137 | 150 | 150 | 150 | 150 | 1161600
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 222 | 222 | 221 | 222 | 220 | 220 | 220 | 220 | 217 | 217 | 220 | 215 | 216 | 212 | 213 |  | 220 | 220 | 220 | 222 | 222 | 222 | 220 | 5254036
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 110 | 110 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 48 | 48 | 48 | 48 | 48 | 48 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1376
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 130 | 130 | 130 | 130 | 130 | 124 | 130 | 124 | 130 | 130 | 130 | 126 | 128 | 124 | 124 | 128 | 124 | 124 |  | 124 | 124 | 130 | 130 | 124 | 128 | 122 | 3049000
140 | Bhola 33 MW PP (Venture) | 33 | 32 | 32 | 30 | 29 | 28 | 23 | 22 | 21 | 22 | 22 | 23 | 24 | 25 | 25 | 25 | 24 | 27 |  | 29 | 31 | 31 | 33 | 33 | 34 | 34 | 650861
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [12 empty] | 8 | 8 | 8 | 8 |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 76875
143 | Gopalganj 100 MW Peaking PP | 38 | 38 | 30 | 30 | 30 | 25 | 20 | 20 | 17 | 17 | 17 | 18 | 16 | 15 | 15 | 19 | 18 | 25 |  | 35 | 40 | 45 | 37 | 37 | 28 | 32 | 597248
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 20 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 67 | 67 |  | 67 | 67 | 67 | 67 | 67 | 67 | 32 | 832752
146 | Bheramara HVDC | 911 | 864 | 864 | 912 | 912 | 912 | 912 | 911 | 912 | 913 | 912 | 912 | 911 | 912 | 912 | 912 | 912 | 912 |  | 911 | 795 | 794 | 794 | 765 | 765 | 788 | 21282909
147 | Bheramara 410 MW CCPP | 245 | 245 | 250 | 250 | 255 | 265 | 275 | 275 | 290 | 290 | 295 | 300 | 300 | 300 | 300 | 295 | 295 | 270 |  | 255 | 240 | 240 | 210 | 200 | 190 | 175 | 6416640
148 | Payra 1320 MW | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1232 | 1210 | 1220 | 1244 | 1244 | 1244 | 1244 | 1244 | 1220 | 1190 |  | 1160 | 1232 | 1232 | 1244 | 1244 | 1244 | 1244 | 31404900
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 180 |  | 200 | 220 | 220 | 220 | 220 | 220 | 220 | 4797200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [13 empty] | 35 | 35 | 35 | 28 | 21 |  | 21 | 21 | 28 | 28 | 28 | 28 | 0 | 278794
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 3 | 4 | 5 | 3 | 5 | 4 | 4 | 2 | 1 | 0 | [8 empty] | 37860
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 192 | 187 | 187 | 188 | 194 | 203 | 211 | 213 | 212 | 211 | 210 | 208 | 205 | 206 | 205 | 204 | 206 | 206 |  | 199 | 205 | 202 | 194 | 189 | 185 | 176 | 5058327
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 200 | 200 | 200 | 150 | 77 | 0 | [9 empty] | 96 | 370 | 370 |  | 414 | 416 | 414 | 414 | 414 | 414 | 414 | 3996981
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [19 empty] | 5 | 10 | 18 | 26 | 14 | 15 | 15 | 73270
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 182034
165 | Amnura 50 MW PP(Sinha) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 658180
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 15 | 15 | 15 | 0 | [9 empty] | 10 | 23 | 15 | 15 | 15 |  | 22 | 24 | 22 | 25 | 25 | 28 | 23 | 240130
168 | Santahar 50 MW Peaking PP | [17 empty] | 9 |  | 23 | 23 | 23 | 23 | 23 | 23 |  | 112220
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | [5 empty] | 8 | 8 | 8 | 8 | 177758
170 | Chapainawabganj 100 MW Peaking PP | [11 empty] | 22 | 48 | 48 | 48 | 48 | 48 | 48 |  | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 1635258
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 40 | 50 | 50 | 35 | 35 | 963360
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 908832
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 40 | 45 |  | 55 | 55 | 56 | 56 | 49 | 49 | 49 | 939091
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 3 | 4 | 7 | 7 | 7 | 7 | 7 | 6 | 4 | 2 | 1 | [8 empty] | 52954
178 | Energypac Power Venture Thakurgaon Ltd. | [16 empty] | 35 | 35 |  | 75 | 75 | 75 | 75 | 75 | 75 | 37 | 494016
| Intraco Solar 30 MW | [5 empty] | 0 | 6 | 12 | 22 | 28 | 34 | 36 | 34 | 24 | 24 | 16 | 2 | 0 | [8 empty] | 226987
| Adani Power Jharkhanda Ltd | 1263 | 1275 | 1266 | 1256 | 1257 | 1208 | 1208 | 1210 | 1208 | 1207 | 1260 | 1291 | 1287 | 1283 | 1286 | 1288 | 1285 | 1284 |  | 1362 | 1359 | 1359 | 1362 | 1359 | 1361 | 1361 | 30834545
178 | Teesta Solar Limited | [5 empty] | 1 | 35 | 52 | 96 | 135 | 177 | 194 | 189 | 170 | 127 | 22 | 6 | 0 | [8 empty] | 1210200