## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-08-20 | Sunday
|  | Date (day): | 2023-08-20 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12021.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14191 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-08-19 | 2023-08-20 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 130 | 140 | 140 | 140 | 40 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 60 | 0 | 0 |  | 412 | Under maint
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 327 | 337 | 330 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 42 | 74 | 34 | 74 | 26 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 17 | 34 | 17 | 34 | 68 |  | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 22 | 22 | 22 | 0 | 75 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 121 | 175 | 130 | 150 | 60 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 88 | 60 | 88 |  | 12 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 324 | 327 | 330 | 330
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 33 | 102 | 25 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 35 | 17 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 98 | 16 | 98 | 51 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 5 | 55 | 35 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 42 | 43 | 40 | 40 |  | 40 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 25 | 33 |  |  | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 24 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 25 | 8 | 25 | 27 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 65 | 148 | 65 | 145 | 155 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
33 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
34 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 70 | 135 | 70 | 135 |  | 14 | Engine problem
35 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 88 | 35 | 88 | 17 |  | Fuel shortage
36 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 50 | 71 | 34 | 70 | 34 |  | Fuel shortage
37 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 108 | 54 | 108 | 54 |  | Fuel shortage
38 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 35 | 0 | 35 | 0
39 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6063 | 5722 | 2199 | 2947 | 2271 | 2829 | 1018 | 1573
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 118 | 117 | 120 | 120 |  | 60
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
41 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 25 | 8 | 25
42 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 39 | 6 | 47
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 202 | 201 | 200 | 200
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 220 | 224 | 225 | 225
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 34 | 34 | 51 | 54 |  | Fuel shortage
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 24 | 49 | 34 | 50 | 48 |  | Fuel shortage
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 0 | 0 | 0 |  | 68 | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 25 | 35 | 35 | 35 | 65 |  | Fuel shortage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 50 | 25 | 50 | 50 |  | Fuel shortage
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 10 | 10 | 10 | 10 | 12 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 11 | 24 | 10 | 25
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 12 | 0 | 12 | 96 |  | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 70 | 285 | 70 | 285 | 15 |  | Fuel shortage
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 47 | 60 | 55 | 55 | 55 |  | Fuel shortage
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 50 | 25 | 50 | 50 |  | Fuel shortage
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 34 | 34 | 34 | 34 | 82 |  | Fuel shortage
60 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 17 | 143 | 17 | 143 | 20 |  | Fuel shortage
| SS Power I |  | Coal | SS Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 11 | 2 | 10 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 181 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2605 | 2545 | 1127 | 1411 | 960 | 1444 | 584 | 458
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 181 | 177 | 170 | 180 | 41 |  | Gas shortage
62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 280 | 270 | 280 | 80 |  | Gas shortage
63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 240 | 240 | 240 | 240 | 120 |  | Gas shortage
64 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 240 | 230 | 230 | 230 | 170 |  | Gas shortage
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 0 | 0 | 0 | 45 |  | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
69 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 5 | 33 | 6 | 30 | 120 |  | Fuel shortage
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 11 | 23 | 23 | 23
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
72 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 51 | 103 | 51 | 100 | 100 |  | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 12 | 16 | 16 | 16 |  | 6 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 156 | 140 | 146 | 163
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 17 | 17 |  | 8 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 106 | 34 | 17 | 34 | 80 |  | Fuel shortage
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 29 | 9 | 30 | 83 |  | Fuel shortage
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 73 | 100 | 72 | 115
| Cumilla Area Total |  |  |  |  | 2959 | 2896 | 1474 | 1525 | 1371 | 1562 | 1086 | 222
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 59 | 78 | 70 | 80 | 122 |  | Gas shortage
83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 16 | 16 | 16 |  | 6 | Engine problem
84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 96 | 163 | 95 | 150 | 50 |  | Fuel shortage
87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 28 | 74 | 68 | 85 | 30 |  | Fuel shortage
88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 51 | 0 | 50 | 0
89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 258 | 337 | 306.6 | 337 | 122 | 6
90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 40 | 40 |  | 50 | Machine problem
92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 112 | 112 |  | 51 | ST Under maint.
93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 47 | 50 | 50
95 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 38 | 42 | 42 | 42
96 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 3 | 3 | 3 |  | 8 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 53 | 50 | 50 |  | 16
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 75 | 84 | 86 | 86
99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 181 | 181 | 180 | 180 |  | 51 | Machine problem
101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 24 | 24
103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 290 | 300 | 300 |  |  | FGMO
104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 367 | 366 | 350 | 370 |  | 30
105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 350 | 350 | 350 | 350
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1634 | 1645 | 1640 | 1660 | 0 | 663
107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 909 | 779 | 909 | 909
108 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 63 | 16 | 63 |  | 52 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 26 | 0 | 40 |  | 14 | Engine problem
110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 16 | 52 | 40 | 52 | 57 |  | Fuel shortage
112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 95 | 0 | 0 | 0 | 410 |  | Gas shortage
113 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 8 | 8 | 32 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
114 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 36 | 17 | 17 | 17 | 88 |  | Fuel shortage
115 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 15 | 50 | 15 | 50 | 55 |  | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 64 | 0 | 100 | 0
117 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 220 | 220 | 50 | 234 | 0 | 230
118 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 402 | 500 | 400 | 500 | 117 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3125 | 3121 | 1603 | 1729 | 1505 | 1869 | 1005 | 66
119 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 32 | 110 | 16 | 110
120 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 22 | 30 | 22 | 30 |  | 10 | Engine problem
121 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 130 | 124 | 130 | 132 |  | 62 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
122 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244
123 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 222 | 220 | 220
124 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 150 | 17 | 150
125 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 | 307 |  | Coal shortage
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1648 | 1880 | 1649 | 1886 | 307 | 72
126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 28 | 0 | 35 | 17 |  | Fuel shortage
128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 17 | 0 | 20 |  | 51 | Engine problem
129 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0 | 28 |  | Fuel shortage
130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 39 | 30 | 40 | 10 |  | Fuel shortage
132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 148 | 151 | 150 | 155 | 65 |  | Gas shortage
135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 414 | 414 | 414
136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 24 | 0 | 24 | 26 |  | Fuel shortage
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 40 | 12 |  | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 11 | 92 | 50 | 92 | 12 |  | Fuel shortage
140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0
141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 50 | 35 | 50 | 63 |  | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 55 | 35 | 55 | 58 |  | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | 0 | Imported power | 748*2 | 1496 | 1496 | 1256 | 1365 | 1200 | 1360
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 1920 | 2251 | 1936 | 2293 | 732 | 264
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 220 | 180 | 180 | 180
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 29 | 56 | 35 | 56 | 57 |  | Fuel shortage
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 75 | 0 | 75 |  |  | Fuel shortage
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 11 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 154 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 421 | 311 | 383 | 311 | 182 | 85
| Total |  |  |  |  | 24911 | 24171 | 12284 | 14036 | 12021.6 | 14191 | 5036 | 3409
A. |  | 2023-08-19 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 14036 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 11068 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14700 | MW
3 | Day peak Generation : |  |  | 12284 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13933.51 | MW
4 | Evening peak Generation : |  |  | 14036 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 634 | MW
5 | Total Energy Generation : |  | 297.2138 | MKWHr | By Solar | 2.9615 | MKWHr
| By Gas : | 142.6305 | MKWHr |  | By Oil: | 44.6287 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 77.443 | MKWHr |  | By Hydro: | 4.6509 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.26208 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5036 | MW | Dhaka | 4860.51 | 4850.51 |  | 10 |  | 18:00 |  | 261.67
|  |  | For Plants S/D or M/C prob = |  |  | 3409 | MW | Chittagong | 1368.4 | 1291.4 |  | 77 |  | 19:00 |  | 628.39
|  |  | Total = |  |  | 8445 | MW | Khulna | 1726.9 | 1562.9 |  | 164 |  | 19:30 |  | 742.99
7 | Total Gas Supplied : |  |  | 1112.72 | MMCFD |  |  | Rajshahi | 1372 | 1290 |  | 82 |  | 20:00 |  | 614.065
8 | Fuel Cost : | i) Gas : | Taka | 157885595.51 | ii) Oil : | Taka | 558709953.4 | Comilla | 1320 | 1265 |  | 55 |  | 21:00 |  | 634.12
|  | iii) Coal : | Taka | 307492749 | Total | Taka | 1024088297.91 | Mymensingh | 1204 | 1114 |  | 90 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 620 | 620 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 1010 | MW (E to W) at | 21:00 | hrs | Barisal | 463.7 | 463.7 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 890 | MW at | 2:00 | hrs | Rangpur | 998 | 842 |  | 156
10 | Maximum Temperature in Dhaka was |  |  |  | 32.6° C |  |  | Total | 13933.51 | 13299.51 |  | 634
B. |  | 2023-08-20 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 32.6° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 15200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 950 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14191 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 14000 | MW
4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 321.8616 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11660 | MW at | 7:00 | 200 | 110 | 130 | 130 | 110 | 90 | 50 | 40 | 90
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.1782 | MKWHr. | ii) HVDC Flow at Peak Time |  | 779 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.4589 | MKWHr. | iii) Maximum HVDC Flow : |  | 909 | MW at | 6:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 102.82 |  | (b) Today: | 102.98 |  | (c) Rule Curve: |  | 95.08
.

## YesterdayGen
2023-08-19 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 170 | 180 | 0 | 12 | 0 | 393 | 337 |  | 0 | 450 | 0 | 92 | 51 | 15 | 326 | 0 | 61 | 52 | 102 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 21 | 25 | 33 | 8 | 0 | 125 | 75 | 120 | 0 | 8 | 225 | 0 | 0 | 0 |  | 6 | 33 | 16 | 25 | 0 | 6 | 10 | 42 | 0 | 0 | 0 | 270 | 240 | 202 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 24 | 0 | 16 | 10 | 25 | 17 | 152 | 106 | 0 | 16 | 0 | 43 | 40 | 50 | 39 | 112 | 0 | 50 | 78 | 0 | 179 | 0 | 0 | 10 | 295 | 24 | 5 | 0 | 62 | 0 | 0 | 67 | 0 | 35 | 0 | 25 | 17 | 6 | 368 | 18 | 17 | 34 | 0 | 70 | 17 | 55 | 17 | 9 | 25 | 350 | 36 | 0 | 17 | 20 | 0 | 17 | 0 | 17 | 17 | 230 | 17 | 0 | 0 | 15 | 0 |  | 859 | 0 | 80 | 0 | 80 | 0 | 0 | 0 | 0 | 46 | 0 | 130 | 31 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 414 | 35 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 1309 | 0 | 0 |  | 6727 | 5389 | 12116 | 4160 | 859 | 2141 | 0 | 1275 | 3140 | 200 | 0 | 174 | 152 | 0 | 15 | 1321.72 | 102.81
2:00 | 0 | 0 | 170 | 180 | 0 | 12 | 0 | 392 | 336 |  | 0 | 450 | 0 | 83 | 38 | 15 | 328 | 0 | 92 | 41 | 102 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 21 | 25 | 33 | 8 | 0 | 125 | 75 | 120 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 34 | 16 | 25 | 0 | 6 | 10 | 42 | 0 | 0 | 0 | 270 | 240 | 206 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 13 | 0 | 16 | 10 | 25 | 17 | 148 | 106 | 0 | 16 | 0 | 43 | 40 | 50 | 42 | 112 | 0 | 50 | 78 | 0 | 180 | 0 | 0 | 10 | 275 | 24 | 5 | 0 | 64 | 0 | 0 | 67 | 0 | 35 | 0 | 25 | 17 | 5 | 368 | 18 | 17 | 34 | 0 | 70 | 17 | 55 | 17 | 9 | 25 | 350 | 36 | 0 | 17 | 17 | 0 | 17 | 0 | 17 | 17 | 230 | 17 | 0 | 0 | 9 | 0 |  | 858 | 0 | 80 | 0 | 80 | 0 | 0 | 0 | 0 | 46 | 0 | 128 | 31 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 414 | 35 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 1311 | 0 | 0 |  | 6692 | 5367 | 12059 | 4196 | 858 | 2123 | 0 | 1240 | 3143 | 200 | 0 | 142 | 148 | 0 | 9 | 1185.155 | 102.81
3:00 | 0 | 0 | 170 | 180 | 0 | 12 | 0 | 392 | 337 |  | 0 | 450 | 0 | 82 | 17 | 15 | 327 | 0 | 89 | 41 | 102 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 21 | 25 | 33 | 8 | 0 | 125 | 75 | 120 | 0 | 8 | 227 | 0 | 0 | 0 |  | 6 | 34 | 16 | 25 | 0 | 6 | 10 | 39 | 0 | 0 | 0 | 270 | 240 | 206 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 16 | 0 | 16 | 10 | 25 | 17 | 146 | 108 | 0 | 16 | 0 | 43 | 40 | 50 | 39 | 112 | 0 | 51 | 78 | 0 | 180 | 0 | 0 | 10 | 260 | 24 | 5 | 0 | 65 | 0 | 0 | 68 | 0 | 35 | 0 | 25 | 17 | 6 | 368 | 18 | 17 | 34 | 0 | 70 | 17 | 55 | 17 | 9 | 25 | 350 | 35 | 0 | 17 | 17 | 0 | 17 | 0 | 17 | 17 | 230 | 17 | 0 | 0 | 11 | 0 |  | 859 | 0 | 80 | 0 | 80 | 0 | 0 | 0 | 0 | 42 | 0 | 124 | 30 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 400 | 35 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 1308 | 0 | 0 |  | 6655 | 5353 | 12008 | 4194 | 859 | 2088 | 0 | 1230 | 3139 | 200 | 0 | 141 | 146 | 0 | 11 | 1090.61 | 102.81
4:00 | 0 | 0 | 170 | 180 | 0 | 12 | 0 | 272 | 340 |  | 0 | 450 | 0 | 48 | 17 | 15 | 327 | 0 | 96 | 41 | 33 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 21 | 25 | 33 | 8 | 0 | 125 | 75 | 120 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 34 | 16 | 25 | 0 | 6 | 10 | 39 | 0 | 0 | 0 | 270 | 240 | 206 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 16 | 0 | 16 | 10 | 25 | 17 | 142 | 107 | 0 | 16 | 0 | 43 | 40 | 50 | 42 | 112 | 0 | 51 | 78 | 0 | 180 | 0 | 0 | 10 | 270 | 24 | 5 | 0 | 65 | 0 | 0 | 68 | 0 | 35 | 0 | 25 | 17 | 6 | 368 | 18 | 17 | 34 | 0 | 70 | 17 | 55 | 17 | 9 | 25 | 350 | 49 | 0 | 17 | 17 | 0 | 17 | 0 | 17 | 17 | 230 | 17 | 0 | 0 | 16 | 0 |  | 908 | 0 | 90 | 0 | 80 | 0 | 0 | 0 | 0 | 42 | 0 | 124 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 414 | 35 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 116 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 1307 | 0 | 0 |  | 6460 | 5499 | 11959 | 4090 | 908 | 2109 | 0 | 1215 | 3138 | 200 | 0 | 141 | 142 | 0 | 16 | 994.155 | 102.82
5:00 | 0 | 0 | 170 | 180 | 0 | 12 | 0 | 0 | 336 |  | 0 | 450 | 0 | 43 | 17 | 15 | 330 | 0 | 160 | 41 | 25 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 21 | 25 | 33 | 8 | 0 | 125 | 75 | 120 | 0 | 8 | 227 | 0 | 0 | 0 |  | 6 | 34 | 16 | 25 | 0 | 6 | 10 | 39 | 0 | 0 | 0 | 270 | 240 | 206 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 16 | 0 | 16 | 10 | 25 | 17 | 142 | 105 | 0 | 16 | 0 | 43 | 40 | 50 | 42 | 112 | 0 | 51 | 75 | 0 | 181 | 0 | 0 | 10 | 290 | 24 | 5 | 0 | 65 | 0 | 0 | 68 | 0 | 35 | 0 | 25 | 17 | 5 | 366 | 18 | 17 | 34 | 0 | 70 | 17 | 55 | 17 | 9 | 25 | 350 | 52 | 0 | 17 | 17 | 0 | 17 | 0 | 17 | 17 | 230 | 17 | 0 | 0 | 9 | 0 |  | 907 | 0 | 90 | 0 | 16 | 0 | 0 | 0 | 0 | 42 | 0 | 130 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 414 | 35 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 1314 | 0 | 0 |  | 6248 | 5481 | 11729 | 3890 | 907 | 2121 | 0 | 1174 | 3145 | 200 | 0 | 141 | 142 | 0 | 9 | 1022.805 | 102.82
6:00 | 0 | 0 | 170 | 180 | 0 | 12 | 0 | 0 | 339 |  | 0 | 450 | 0 | 42 | 17 | 15 | 328 | 0 | 131 | 41 | 25 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 21 | 25 | 33 | 8 | 0 | 125 | 75 | 123 | 0 | 8 | 225 | 0 | 0 | 0 |  | 6 | 34 | 16 | 25 | 0 | 6 | 10 | 42 | 0 | 0 | 0 | 320 | 240 | 187 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 16 | 10 | 25 | 17 | 132 | 108 | 0 | 16 | 0 | 43 | 40 | 50 | 42 | 112 | 0 | 51 | 75 | 0 | 181 | 0 | 0 | 10 | 285 | 24 | 5 | 0 | 65 | 0 | 0 | 68 | 0 | 35 | 1 | 25 | 17 | 6 | 412 | 18 | 17 | 34 | 0 | 70 | 17 | 55 | 17 | 9 | 25 | 350 | 35 | 1 | 17 | 17 | 0 | 17 | 1 | 17 | 17 | 230 | 17 | 0 | 0 | 14 | 0 |  | 909 | 0 | 105 | 0 | 16 | 0 | 0 | 0 | 0 | 42 | 0 | 123 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 414 | 35 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 17 | 0 | 2 | 0 | 0 | 0 | 408 | 1 | 0 | 1067 | 5 | 0 |  | 6257 | 5119 | 11376 | 3950 | 909 | 2119 | 0 | 1017 | 2899 | 200 | 0 | 125 | 132 | 11 | 14 | 977.92 | 102.82
7:00 | 0 | 0 | 170 | 180 | 0 | 12 | 0 | 0 | 339 |  | 0 | 450 | 0 | 42 | 17 | 15 | 330 | 0 | 97 | 0 | 25 | 16 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 0 | 25 | 33 | 8 | 0 | 80 | 40 | 120 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 34 | 16 | 25 | 0 | 6 | 10 | 4 | 0 | 0 | 0 | 270 | 265 | 148 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 16 | 10 | 25 | 17 | 118 | 107 | 0 | 16 | 0 | 43 | 40 | 50 | 42 | 112 | 0 | 59 | 75 | 0 | 181 | 0 | 0 | 10 | 290 | 24 | 5 | 0 | 65 | 0 | 0 | 68 | 0 | 35 | 3 | 25 | 17 | 5 | 368 | 18 | 17 | 34 | 1 | 70 | 17 | 55 | 17 | 9 | 25 | 350 | 35 | 2 | 17 | 17 | 0 | 17 | 7 | 18 | 17 | 300 | 17 | 0 | 0 | 10 | 0 |  | 908 | 0 | 105 | 0 | 16 | 0 | 0 | 0 | 0 | 38 | 0 | 130 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 414 | 35 | 0 | 35 | 15 | 34 | 0 | 1 | 35 | 1244 | 220 | 0 | 17 | 0 | 20 | 0 | 0 | 0 | 408 | 7 | 0 | 961 | 21 | 0 |  | 6014 | 5054 | 11068 | 3872 | 908 | 2083 | 0 | 981 | 2793 | 120 | 0 | 121 | 118 | 62 | 10 | 937.81 | 102.83
8:00 | 0 | 0 | 170 | 180 | 0 | 12 | 0 | 0 | 340 |  | 0 | 450 | 0 | 42 | 17 | 15 | 300 | 0 | 101 | 0 | 25 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 0 | 25 | 33 | 8 | 0 | 80 | 40 | 121 | 0 | 8 | 223 | 0 | 0 | 0 |  | 6 | 34 | 16 | 25 | 0 | 6 | 10 | 12 | 0 | 0 | 0 | 270 | 240 | 149 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 13 | 10 | 25 | 17 | 124 | 104 | 0 | 16 | 1 | 43 | 40 | 50 | 42 | 112 | 0 | 58 | 75 | 0 | 181 | 0 | 0 | 10 | 290 | 16 | 5 | 0 | 64 | 0 | 0 | 68 | 0 | 35 | 4 | 25 | 17 | 6 | 405 | 18 | 17 | 34 | 2 | 70 | 17 | 55 | 17 | 9 | 25 | 350 | 38 | 6 | 17 | 17 | 0 | 17 | 20 | 18 | 17 | 230 | 17 | 0 | 0 | 9 | 0 |  | 908 | 0 | 105 | 0 | 16 | 0 | 0 | 0 | 0 | 19 | 0 | 80 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 414 | 35 | 0 | 35 | 15 | 34 | 0 | 2 | 35 | 1244 | 220 | 0 | 17 | 1 | 51 | 0 | 0 | 0 | 408 | 13 | 0 | 1000 | 85 | 0 |  | 5961 | 5126 | 11087 | 3723 | 908 | 2098 | 0 | 986 | 2832 | 120 | 0 | 102 | 124 | 185 | 9 | 728.665 | 102.83
9:00 | 0 | 0 | 170 | 180 | 0 | 12 | 0 | 0 | 327 |  | 0 | 450 | 0 | 42 | 17 | 15 | 300 | 0 | 100 | 0 | 25 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 0 | 25 | 16 | 8 | 0 | 127 | 75 | 120 | 0 | 8 | 223 | 0 | 0 | 0 |  | 6 | 34 | 16 | 25 | 0 | 6 | 10 | 7 | 0 | 0 | 0 | 270 | 240 | 173 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 13 | 10 | 25 | 17 | 130 | 65 | 0 | 16 | 1 | 43 | 40 | 47 | 42 | 80 | 0 | 60 | 72 | 0 | 181 | 0 | 0 | 10 | 290 | 19 | 5 | 0 | 65 | 0 | 0 | 68 | 0 | 62 | 12 | 25 | 17 | 5 | 368 | 18 | 17 | 34 | 4 | 70 | 17 | 55 | 17 | 9 | 25 | 350 | 52 | 40 | 17 | 17 | 0 | 17 | 26 | 17 | 17 | 230 | 17 | 0 | 0 | 16 | 0 |  | 907 | 0 | 110 | 0 | 16 | 0 | 0 | 0 | 0 | 18 | 0 | 124 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 300 | 36 | 0 | 35 | 15 | 34 | 0 | 5 | 35 | 1232 | 220 | 0 | 17 | 3 | 61 | 0 | 0 | 0 | 403 | 18 | 0 | 1143 | 164 | 0 |  | 6016 | 5278 | 11294 | 3702 | 907 | 1917 | 0 | 1027 | 2958 | 202 | 0 | 101 | 130 | 334 | 16 | 721.98 | 102.83
10:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 0 | 327 |  | 0 | 450 | 0 | 42 | 17 | 15 | 322 | 0 | 134 | 0 | 25 | 16 | 23 | 0 | 0 | 0 | 17 | 17 | 0 | 19 | 19 | 14 | 33 | 31 | 8 | 0 | 127 | 75 | 123 | 0 | 8 | 223 | 0 | 0 | 0 |  | 6 | 34 | 16 | 25 | 0 | 6 | 10 | 5 | 0 | 0 | 0 | 270 | 240 | 186 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 13 | 10 | 25 | 17 | 146 | 64 | 0 | 16 | 1 | 43 | 40 | 47 | 42 | 112 | 0 | 60 | 72 | 0 | 181 | 0 | 0 | 10 | 285 | 16 | 5 | 0 | 57 | 0 | 0 | 68 | 0 | 71 | 17 | 25 | 28 | 6 | 367 | 24 | 17 | 34 | 5 | 70 | 17 | 55 | 90 | 18 | 25 | 350 | 55 | 51 | 17 | 17 | 0 | 17 | 29 | 29 | 17 | 235 | 17 | 0 | 0 | 19 | 0 |  | 909 | 0 | 115 | 0 | 16 | 0 | 0 | 0 | 0 | 18 | 0 | 132 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 414 | 36 | 0 | 35 | 15 | 34 | 0 | 7 | 35 | 1210 | 220 | 0 | 0 | 5 | 106 | 0 | 0 | 0 | 402 | 32 | 0 | 1175 | 181 | 0 |  | 6308 | 5482 | 11790 | 3784 | 909 | 2067 | 0 | 1161 | 2967 | 202 | 0 | 101 | 146 | 434 | 19 | 193.865 | 102.84
11:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 0 | 327 |  | 0 | 450 | 0 | 42 | 17 | 15 | 320 | 0 | 133 | 0 | 33 | 22 | 23 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 19 | 21 | 33 | 24 | 8 | 0 | 127 | 75 | 119 | 0 | 8 | 223 | 0 | 0 | 0 |  | 6 | 24 | 16 | 25 | 0 | 6 | 10 | 6 | 0 | 0 | 0 | 270 | 240 | 184 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 12 | 10 | 25 | 17 | 144 | 63 | 0 | 16 | 2 | 43 | 40 | 47 | 42 | 112 | 0 | 60 | 75 | 0 | 181 | 0 | 0 | 10 | 280 | 16 | 5 | 0 | 65 | 0 | 0 | 96 | 0 | 70 | 20 | 25 | 51 | 5 | 363 | 28 | 22 | 34 | 5 | 70 | 17 | 55 | 106 | 14 | 25 | 350 | 48 | 52 | 54 | 25 | 0 | 17 | 37 | 68 | 17 | 240 | 17 | 0 | 0 | 14 | 72 |  | 908 | 0 | 110 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 124 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 350 | 36 | 0 | 35 | 15 | 34 | 0 | 7 | 35 | 1210 | 220 | 0 | 0 | 4 | 47 | 0 | 0 | 0 | 403 | 35 | 0 | 1307 | 150 | 0 |  | 6533 | 5484 | 12017 | 3738 | 908 | 2003 | 0 | 1342 | 3212 | 202 | 0 | 95 | 144 | 359 | 14 | 90.725 | 102.84
12:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 0 | 327 |  | 0 | 450 | 0 | 42 | 17 | 0 | 324 | 0 | 121 | 0 | 33 | 32 | 22 | 0 | 0 | 0 | 17 | 35 | 5 | 19 | 19 | 23 | 33 | 24 | 8 | 0 | 127 | 75 | 118 | 0 | 8 | 220 | 0 | 0 | 0 |  | 6 | 24 | 17 | 25 | 0 | 6 | 10 | 11 | 0 | 0 | 0 | 270 | 240 | 181 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 11 | 0 | 12 | 10 | 25 | 17 | 156 | 59 | 0 | 16 | 2 | 43 | 40 | 47 | 38 | 112 | 0 | 60 | 75 | 0 | 181 | 0 | 0 | 10 | 290 | 16 | 5 | 0 | 65 | 0 | 0 | 96 | 0 | 70 | 20 | 25 | 51 | 5 | 367 | 28 | 35 | 34 | 5 | 70 | 17 | 47 | 106 | 9 | 25 | 350 | 50 | 51 | 54 | 34 | 0 | 17 | 35 | 73 | 17 | 240 | 17 | 0 | 0 | 11 | 181 |  | 909 | 0 | 95 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 130 | 22 | 32 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 414 | 36 | 0 | 35 | 15 | 29 | 0 | 7 | 35 | 1244 | 220 | 0 | 0 | 5 | 64 | 0 | 50 | 0 | 402 | 11 | 0 | 1256 | 154 | 0 |  | 6692 | 5592 | 12284 | 3734 | 909 | 2079 | 0 | 1358 | 3303 | 202 | 50 | 128 | 156 | 354 | 11 | 77.355 | 102.84
13:00 | 0 | 0 | 150 | 180 | 0 | 12 | 0 | 0 | 327 |  | 0 | 450 | 0 | 42 | 17 | 0 | 327 | 0 | 160 | 0 | 33 | 32 | 22 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 19 | 18 | 33 | 24 | 8 | 0 | 127 | 75 | 122 | 0 | 8 | 215 | 0 | 0 | 0 |  | 6 | 41 | 16 | 25 | 0 | 6 | 10 | 14 | 0 | 0 | 0 | 270 | 240 | 183 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 15 | 0 | 14 | 10 | 25 | 17 | 148 | 59 | 0 | 16 | 2 | 43 | 39 | 47 | 38 | 112 | 0 | 55 | 75 | 0 | 181 | 0 | 0 | 10 | 310 | 16 | 5 | 0 | 65 | 0 | 0 | 115 | 0 | 70 | 5 | 25 | 51 | 6 | 405 | 37 | 52 | 34 | 5 | 70 | 17 | 55 | 106 | 9 | 25 | 350 | 52 | 19 | 54 | 34 | 0 | 17 | 3 | 72 | 17 | 230 | 17 | 0 | 0 | 7 | 175 |  | 907 | 0 | 70 | 0 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 126 | 20 | 32 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 352 | 36 | 0 | 35 | 15 | 33 | 0 | 7 | 35 | 1244 | 220 | 0 | 0 | 5 | 50 | 0 | 0 | 0 | 401 | 36 | 0 | 1322 | 194 | 0 |  | 6787 | 5608 | 12395 | 3783 | 907 | 2038 | 0 | 1429 | 3362 | 202 | 0 | 193 | 148 | 326 | 7 | 114.6 | 102.85
14:00 | 0 | 0 | 150 | 180 | 0 | 12 | 0 | 0 | 327 |  | 0 | 450 | 0 | 42 | 17 | 9 | 325 | 0 | 136 | 2 | 33 | 32 | 22 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 19 | 18 | 33 | 26 | 8 | 0 | 126 | 75 | 120 | 0 | 8 | 221 | 0 | 0 | 0 |  | 6 | 41 | 16 | 25 | 0 | 6 | 10 | 11 | 0 | 0 | 0 | 280 | 240 | 177 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 15 | 0 | 14 | 10 | 25 | 17 | 144 | 58 | 0 | 14 | 2 | 43 | 39 | 44 | 38 | 112 | 0 | 60 | 75 | 0 | 181 | 0 | 0 | 10 | 300 | 24 | 5 | 0 | 65 | 0 | 0 | 115 | 0 | 70 | 19 | 25 | 51 | 5 | 367 | 37 | 52 | 34 | 4 | 70 | 17 | 55 | 106 | 9 | 25 | 350 | 53 | 18 | 54 | 34 | 0 | 17 | 22 | 72 | 17 | 230 | 17 | 0 | 0 | 11 | 185 |  | 907 | 0 | 55 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 126 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 371 | 36 | 0 | 35 | 15 | 34 | 0 | 4 | 35 | 1244 | 220 | 0 | 2 | 5 | 84 | 0 | 0 | 0 | 401 | 11 | 0 | 1304 | 124 | 0 |  | 6778 | 5512 | 12290 | 3722 | 907 | 2030 | 0 | 1443 | 3354 | 201 | 0 | 185 | 144 | 293 | 11 | 343.8 | 102.84
15:00 | 0 | 0 | 150 | 180 | 0 | 12 | 0 | 0 | 333 |  | 0 | 450 | 0 | 42 | 17 | 15 | 324 | 0 | 156 | 8 | 33 | 32 | 22 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 19 | 0 | 33 | 30 | 8 | 0 | 124 | 75 | 118 | 0 | 8 | 219 | 0 | 0 | 0 |  | 2 | 41 | 16 | 25 | 0 | 6 | 10 | 8 | 0 | 0 | 0 | 280 | 240 | 166 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 15 | 0 | 15 | 10 | 25 | 17 | 160 | 58 | 0 | 14 | 1 | 43 | 39 | 44 | 38 | 112 | 0 | 60 | 75 | 0 | 181 | 0 | 0 | 10 | 290 | 24 | 5 | 0 | 65 | 0 | 0 | 115 | 0 | 58 | 15 | 25 | 51 | 5 | 343 | 37 | 35 | 34 | 3 | 68 | 17 | 55 | 106 | 9 | 25 | 350 | 53 | 44 | 54 | 34 | 0 | 17 | 27 | 72 | 17 | 230 | 17 | 0 | 0 | 12 | 0 |  | 906 | 0 | 50 | 0 | 21 | 0 | 0 | 0 | 5 | 17 | 0 | 130 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 332 | 36 | 0 | 35 | 15 | 34 | 0 | 5 | 35 | 1244 | 222 | 0 | 17 | 4 | 77 | 0 | 0 | 0 | 401 | 23 | 0 | 1309 | 116 | 0 |  | 6570 | 5515 | 12085 | 3687 | 906 | 2002 | 0 | 1440 | 3174 | 199 | 0 | 190 | 160 | 315 | 12 | 682.825 | 102.86
16:00 | 0 | 0 | 140 | 180 | 0 | 12 | 0 | 0 | 333 |  | 0 | 450 | 0 | 42 | 17 | 15 | 321 | 0 | 155 | 9 | 33 | 32 | 22 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 19 | 0 | 33 | 16 | 8 | 0 | 124 | 75 | 118 | 0 | 8 | 219 | 0 | 0 | 0 |  | 0 | 41 | 16 | 25 | 10 | 6 | 10 | 12 | 0 | 0 | 0 | 295 | 240 | 161 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 19 | 0 | 15 | 10 | 25 | 14 | 154 | 59 | 0 | 14 | 1 | 43 | 39 | 44 | 38 | 112 | 0 | 59 | 81 | 0 | 181 | 0 | 0 | 10 | 315 | 24 | 5 | 0 | 65 | 0 | 0 | 68 | 0 | 53 | 9 | 25 | 51 | 6 | 335 | 18 | 35 | 34 | 1 | 69 | 17 | 55 | 34 | 9 | 25 | 350 | 52 | 7 | 54 | 34 | 0 | 17 | 18 | 72 | 17 | 230 | 17 | 0 | 0 | 16 | 0 |  | 907 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 9 | 16 | 16 | 128 | 23 | 32 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 340 | 36 | 0 | 35 | 15 | 34 | 0 | 2 | 35 | 1244 | 220 | 0 | 17 | 3 | 63 | 35 | 0 | 0 | 402 | 19 | 0 | 1319 | 45 | 0 |  | 6409 | 5449 | 11858 | 3605 | 907 | 2041 | 0 | 1386 | 3185 | 199 | 0 | 197 | 154 | 168 | 16 | 708.61 | 102.86
17:00 | 0 | 0 | 140 | 180 | 0 | 12 | 0 | 0 | 333 |  | 0 | 450 | 0 | 42 | 17 | 15 | 320 | 0 | 129 | 9 | 33 | 32 | 22 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 19 | 24 | 33 | 32 | 8 | 0 | 124 | 75 | 118 | 0 | 19 | 222 | 0 | 0 | 0 |  | 1 | 41 | 0 | 25 | 13 | 6 | 10 | 20 | 0 | 0 | 0 | 280 | 240 | 162 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 23 | 0 | 14 | 10 | 25 | 17 | 150 | 60 | 0 | 14 | 0 | 43 | 39 | 44 | 42 | 112 | 0 | 60 | 84 | 0 | 181 | 0 | 0 | 10 | 290 | 24 | 3 | 0 | 65 | 0 | 0 | 68 | 0 | 52 | 4 | 25 | 51 | 5 | 319 | 18 | 35 | 34 | 1 | 70 | 17 | 55 | 34 | 12 | 25 | 350 | 52 | 8 | 54 | 34 | 0 | 17 | 5 | 72 | 17 | 230 | 17 | 0 | 0 | 24 | 0 |  | 906 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 14 | 15 | 8 | 128 | 21 | 48 | 0 | 0 | 0 | 6 | 0 | 47 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 345 | 17 | 0 | 35 | 53 | 55 | 0 | 2 | 35 | 1244 | 221 | 0 | 17 | 0 | 35 | 36 | 0 | 0 | 402 | 10 | 0 | 1318 | 39 | 0 |  | 6396 | 5425 | 11821 | 3593 | 906 | 2035 | 0 | 1471 | 3144 | 199 | 0 | 195 | 150 | 104 | 24 | 648.445 | 102.87
18:00 | 0 | 0 | 140 | 180 | 0 | 0 | 0 | 0 | 306 |  | 0 | 450 | 0 | 48 | 22 | 15 | 321 | 0 | 102 | 9 | 33 | 32 | 22 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 19 | 24 | 33 | 32 | 8 | 0 | 124 | 75 | 120 | 0 | 23 | 221 | 0 | 0 | 0 |  | 3 | 66 | 0 | 35 | 12 | 6 | 10 | 24 | 0 | 0 | 0 | 280 | 240 | 168 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 23 | 0 | 13 | 10 | 25 | 17 | 148 | 61 | 0 | 14 | 0 | 44 | 39 | 44 | 42 | 113 | 0 | 60 | 84 | 0 | 181 | 0 | 0 | 10 | 280 | 24 | 3 | 0 | 65 | 0 | 0 | 68 | 0 | 64 | 0 | 25 | 81 | 6 | 319 | 18 | 35 | 34 | 0 | 120 | 17 | 54 | 34 | 24 | 25 | 350 | 52 | 2 | 54 | 34 | 0 | 17 | 2 | 80 | 17 | 230 | 17 | 0 | 0 | 6 | 0 |  | 907 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 30 | 25 | 8 | 130 | 20 | 48 | 0 | 0 | 0 | 35 | 5 | 47 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 353 | 17 | 0 | 35 | 50 | 55 | 0 | 1 | 55 | 1200 | 200 | 0 | 17 | 1 | 5 | 36 | 0 | 0 | 505 | 2 | 0 | 1324 | 7 | 0 |  | 6463 | 5487 | 11950 | 3578 | 907 | 1977 | 0 | 1626 | 3209 | 199 | 0 | 280 | 148 | 20 | 6 | 261.67 | 102.87
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 140 | 180 | 0 | 0 | 0 | 14 | 327 |  | 0 | 450 | 0 | 57 | 34 | 15 | 324 | 0 | 192 | 14 | 85 | 98 | 22 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 0 | 33 | 32 | 25 | 0 | 125 | 75 | 118 | 0 | 25 | 222 | 0 | 0 | 0 |  | 6 | 48 | 0 | 35 | 11 | 29 | 10 | 28 | 0 | 0 | 0 | 280 | 240 | 165 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 23 | 0 | 13 | 10 | 25 | 17 | 146 | 66 | 0 | 16 | 0 | 44 | 39 | 44 | 42 | 112 | 0 | 58 | 84 | 0 | 181 | 0 | 0 | 10 | 310 | 24 | 3 | 0 | 105 | 0 | 0 | 160 | 0 | 118 | 0 | 50 | 103 | 21 | 366 | 84 | 88 | 34 | 0 | 289 | 17 | 56 | 34 | 27 | 25 | 350 | 66 | 0 | 108 | 34 | 0 | 17 | 0 | 102 | 17 | 230 | 36 | 0 | 0 | 7 | 0 |  | 907 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 36 | 50 | 8 | 130 | 29 | 110 | 0 | 0 | 0 | 35 | 13 | 92 | 0 | 0 | 26 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 352 | 17 | 0 | 35 | 50 | 56 | 0 | 0 | 55 | 1200 | 220 | 0 | 150 | 0 | 0 | 75 | 50 | 0 | 501 | 0 | 0 | 1363 | 0 | 0 |  | 7484 | 5958 | 13442 | 3711 | 907 | 2059 | 0 | 2661 | 3244 | 200 | 50 | 457 | 146 | 0 | 7 | 628.39 | 102.89
19:30 | 0 | 0 | 140 | 180 | 0 | 0 | 0 | 35 | 327 |  | 0 | 450 | 0 | 74 | 34 | 15 | 323 | 0 | 175 | 80 | 102 | 98 | 22 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 24 | 33 | 33 | 25 | 0 | 125 | 75 | 117 | 0 | 25 | 226 | 0 | 0 | 0 |  | 6 | 49 | 0 | 35 | 12 | 31 | 10 | 28 | 0 | 0 | 0 | 280 | 240 | 172 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 23 | 0 | 16 | 10 | 25 | 17 | 140 | 68 | 0 | 16 | 0 | 43 | 39 | 47 | 42 | 112 | 0 | 62 | 84 | 0 | 181 | 0 | 0 | 10 | 250 | 24 | 3 | 0 | 145 | 0 | 0 | 161 | 0 | 135 | 0 | 50 | 103 | 31 | 367 | 84 | 88 | 34 | 0 | 277 | 17 | 56 | 34 | 28 | 25 | 320 | 72 | 0 | 108 | 34 | 0 | 17 | 0 | 114 | 17 | 230 | 36 | 0 | 0 | 6 | 0 |  | 779 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 45 | 55 | 8 | 124 | 29 | 110 | 0 | 0 | 0 | 35 | 14 | 92 | 0 | 0 | 35 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 406 | 17 | 0 | 35 | 50 | 56 | 0 | 0 | 55 | 1200 | 221 | 0 | 150 | 0 | 0 | 75 | 233 | 0 | 500 | 0 | 0 | 1354 | 0 | 0 |  | 7616 | 6106 | 13722 | 3726 | 779 | 2057 | 0 | 2841 | 3234 | 200 | 233 | 506 | 140 | 0 | 6 | 742.99 | 0
20:00 | 0 | 0 | 140 | 180 | 0 | 0 | 0 | 53 | 327 |  | 0 | 450 | 0 | 74 | 34 | 15 | 290 | 0 | 135 | 65 | 102 | 98 | 22 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 24 | 33 | 33 | 25 | 0 | 126 | 75 | 120 | 0 | 25 | 223 | 0 | 0 | 0 |  | 6 | 49 | 0 | 35 | 12 | 35 | 10 | 21 | 0 | 0 | 0 | 280 | 240 | 172 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 23 | 0 | 16 | 10 | 25 | 17 | 144 | 66 | 0 | 16 | 0 | 43 | 39 | 47 | 42 | 112 | 0 | 56 | 84 | 0 | 181 | 0 | 0 | 10 | 265 | 24 | 3 | 0 | 148 | 0 | 0 | 163 | 0 | 135 | 0 | 50 | 103 | 30 | 366 | 84 | 88 | 34 | 0 | 284 | 17 | 56 | 34 | 28 | 50 | 350 | 70 | 0 | 108 | 34 | 0 | 17 | 0 | 114 | 17 | 230 | 53 | 0 | 0 | 12 | 0 |  | 779 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 34 | 52 | 8 | 130 | 27 | 110 | 0 | 0 | 0 | 35 | 15 | 92 | 0 | 0 | 39 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 414 | 17 | 0 | 40 | 50 | 56 | 0 | 0 | 55 | 1220 | 223 | 0 | 150 | 0 | 0 | 75 | 233 | 0 | 500 | 0 | 0 | 1361 | 0 | 0 |  | 7641 | 6146 | 13787 | 3699 | 779 | 2073 | 0 | 2871 | 3261 | 201 | 233 | 514 | 144 | 0 | 12 | 614.065 | 102.88
21:00 | 0 | 0 | 140 | 180 | 0 | 0 | 0 | 60 | 337 |  | 0 | 450 | 0 | 74 | 34 | 15 | 327 | 0 | 175 | 88 | 102 | 98 | 22 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 24 | 33 | 33 | 25 | 0 | 126 | 75 | 117 | 0 | 25 | 224 | 0 | 0 | 0 |  | 6 | 49 | 0 | 35 | 12 | 39 | 10 | 24 | 0 | 0 | 0 | 280 | 240 | 177 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 23 | 0 | 16 | 10 | 25 | 17 | 140 | 78 | 0 | 16 | 0 | 43 | 40 | 47 | 42 | 112 | 0 | 53 | 84 | 0 | 181 | 0 | 0 | 10 | 290 | 24 | 3 | 0 | 148 | 0 | 0 | 163 | 0 | 135 | 0 | 50 | 103 | 33 | 366 | 74 | 88 | 34 | 0 | 285 | 17 | 60 | 34 | 29 | 50 | 350 | 71 | 0 | 108 | 34 | 0 | 17 | 0 | 100 | 17 | 230 | 143 | 0 | 0 | 2 | 0 |  | 779 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 26 | 52 | 8 | 124 | 30 | 110 | 0 | 0 | 0 | 28 | 17 | 92 | 0 | 0 | 39 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 414 | 17 | 0 | 50 | 50 | 56 | 0 | 0 | 55 | 1244 | 222 | 0 | 150 | 0 | 0 | 75 | 234 | 0 | 500 | 0 | 0 | 1365 | 0 | 0 |  | 7865 | 6171 | 14036 | 3793 | 779 | 2113 | 0 | 2894 | 3289 | 201 | 234 | 591 | 140 | 0 | 2 | 634.12 | 102.89
22:00 | 0 | 0 | 140 | 180 | 0 | 0 | 0 | 70 | 337 |  | 0 | 450 | 0 | 46 | 34 | 15 | 324 | 0 | 125 | 88 | 102 | 98 | 22 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 24 | 33 | 33 | 25 | 0 | 125 | 75 | 118 | 0 | 25 | 220 | 0 | 0 | 0 |  | 6 | 50 | 0 | 35 | 12 | 45 | 10 | 36 | 0 | 0 | 0 | 305 | 240 | 169 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 23 | 0 | 16 | 10 | 25 | 17 | 146 | 80 | 0 | 16 | 0 | 43 | 40 | 47 | 42 | 113 | 0 | 55 | 81 | 0 | 181 | 0 | 0 | 10 | 305 | 24 | 3 | 0 | 148 | 0 | 0 | 163 | 0 | 133 | 0 | 50 | 103 | 31 | 406 | 74 | 88 | 17 | 0 | 142 | 17 | 55 | 34 | 28 | 50 | 350 | 71 | 0 | 108 | 34 | 0 | 17 | 0 | 109 | 17 | 230 | 143 | 0 | 0 | 5 | 0 |  | 779 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 21 | 43 | 8 | 130 | 32 | 110 | 0 | 0 | 0 | 28 | 15 | 92 | 0 | 0 | 39 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 414 | 17 | 0 | 50 | 50 | 56 | 0 | 0 | 35 | 1244 | 222 | 0 | 150 | 0 | 0 | 75 | 235 | 0 | 501 | 0 | 0 | 1359 | 0 | 0 |  | 7731 | 6147 | 13878 | 3822 | 779 | 2140 | 0 | 2691 | 3284 | 200 | 235 | 576 | 146 | 0 | 5 | 0 | 102.9
23:00 | 0 | 0 | 140 | 180 | 0 | 0 | 0 | 244 | 332 |  | 0 | 450 | 0 | 40 | 34 | 15 | 324 | 0 | 125 | 88 | 50 | 32 | 22 | 0 | 0 | 0 | 17 | 0 | 35 | 19 | 19 | 17 | 33 | 33 | 25 | 0 | 125 | 75 | 118 | 0 | 25 | 224 | 0 | 0 | 0 |  | 6 | 51 | 0 | 35 | 0 | 45 | 10 | 40 | 0 | 0 | 0 | 280 | 240 | 175 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 23 | 0 | 16 | 10 | 25 | 17 | 152 | 81 | 0 | 16 | 0 | 43 | 40 | 47 | 43 | 112 | 0 | 51 | 81 | 0 | 180 | 0 | 0 | 10 | 315 | 24 | 3 | 0 | 145 | 0 | 0 | 68 | 0 | 104 | 0 | 25 | 103 | 13 | 372 | 17 | 88 | 17 | 0 | 104 | 17 | 55 | 34 | 15 | 25 | 350 | 71 | 0 | 90 | 34 | 0 | 17 | 0 | 114 | 17 | 230 | 17 | 0 | 0 | 3 | 0 |  | 798 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 21 | 35 | 8 | 132 | 29 | 110 | 0 | 0 | 0 | 28 | 15 | 92 | 0 | 0 | 39 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 414 | 17 | 0 | 35 | 50 | 34 | 0 | 0 | 35 | 1244 | 222 | 0 | 150 | 0 | 0 | 75 | 236 | 0 | 501 | 0 | 0 | 1358 | 0 | 0 |  | 7208 | 6122 | 13330 | 3940 | 798 | 2146 | 0 | 2195 | 3283 | 200 | 236 | 377 | 152 | 0 | 3 | 0 | 102.91
24:00 | 0 | 0 | 140 | 180 | 0 | 0 | 0 | 274 | 332 |  | 0 | 450 | 0 | 42 | 34 | 15 | 324 | 0 | 115 | 88 | 16 | 32 | 23 | 0 | 0 | 0 | 17 | 0 | 35 | 19 | 19 | 21 | 33 | 33 | 8 | 0 | 125 | 75 | 120 | 0 | 8 | 223 | 0 | 0 | 0 |  | 0 | 34 | 0 | 25 | 0 | 45 | 10 | 40 | 0 | 0 | 0 | 305 | 240 | 173 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 23 | 0 | 16 | 10 | 25 | 17 | 140 | 81 | 0 | 0 | 0 | 43 | 40 | 47 | 43 | 113 | 0 | 56 | 81 | 0 | 180 | 0 | 0 | 10 | 310 | 24 | 3 | 0 | 80 | 0 | 0 | 68 | 0 | 39 | 0 | 25 | 63 | 5 | 369 | 17 | 17 | 34 | 0 | 70 | 17 | 55 | 17 | 9 | 25 | 350 | 54 | 0 | 17 | 34 | 0 | 17 | 0 | 62 | 17 | 230 | 17 | 0 | 0 | 3 | 0 |  | 798 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 11 | 37 | 8 | 130 | 29 | 110 | 0 | 0 | 0 | 0 | 15 | 56 | 0 | 0 | 24 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 414 | 17 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 150 | 0 | 0 | 75 | 236 | 0 | 499 | 0 | 0 | 1359 | 0 | 0 |  | 6697 | 5941 | 12638 | 3973 | 798 | 2140 | 0 | 1617 | 3282 | 200 | 236 | 249 | 140 | 0 | 3 | 0 | 102.92
KWH | 0 | 0 | 3625250 | 4277700 | 0 | 213272 | 0 | 2222080 | 7966000 |  | 0 | 10253800 | 0 | 1218240 | 516409 | 350200 | 7748912 | 0 | 3139000 | 688234 | 1220832 | 847200 | 554089 | 0 | 0 | 0 | 390240 | 438853 | 444339 | 422208 | 456000 | 356760 | 738100 | 729400 | 270720 | 0 | 2934851 | 1716000 | 2700000 | 0 | 296652 | 5193807 | 0 | 0 | 0 |  | 125040 | 926208 | 261697 | 592920 | 88320 | 331680 | 238944 | 629760 | 0 | 0 | 0 | 7154200 | 5951000 | 4358000 | 0 | 0 | 0 | 0 | 0 | 1131260 | 0 | 341648 | 0 | 356040 | 248940 | 600700 | 413140 | 3458880 | 1849920 | 0 | 331488 | 11500 | 1022000 | 937200 | 1138800 | 980136 | 2581854 | 0 | 1349568 | 1866240 | 0 | 4695330 | 0 | 0 | 253080 | 7173500 | 534408 | 104960 | 0 | 1934509 | 0 | 0 | 2181600 | 0 | 1600560 | 131895 | 679680 | 1223040 | 240872 | 8854000 | 751200 | 914832 | 805415 | 35402 | 2411236 | 445397 | 1320610 | 1048800 | 330120 | 665280 | 8329300 | 1255680 | 307880 | 1160640 | 658636 | 0 | 441360 | 181655 | 1378560 | 432720 | 5829600 | 746036 | 0 | 0 | 262080 | 523636 |  | 21178181 | 0 | 1438560 | 0 | 953280 | 0 | 0 | 0 | 188640 | 753664 | 79875 | 2996000 | 592283 | 1150176 | 0 | 0 | 0 | 209184 | 78692 | 813080 | 0 | 0 | 202757 | 205517 | 115266 | 0 | 0 | 175320 | 0 | 0 | 4632300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3850318 | 0 | 9368945 | 719040 | 0 | 952224 | 656928 | 960384 | 0 | 51053 | 980448 | 31408200 | 5253409 | 0 | 1368000 | 34020 | 693281 | 539712 | 1171578 | 0 | 10378180 | 241641 | 0 | 30500727 | 1273200 | 0 |  | 161049740 | 136164063 | 297213803 | 93228153 | 21178181 | 49402339 | 0 | 37973099 | 77443043 | 4650851 | 1171578 | 5484072 | 3458880 | 2961527 | 262080 | 0
Fuel Cost | 0 | 0 | 5292865 | 6373773 | 0 | 283651.76 | 0 | 2333184 | 8603280 |  | 0 | 11176642 | 0 | 13619923.2 | 6842419.25 | 4640150 | 8678781.44 | 0 | 5493250 | 10061981.08 | 17177106.24 | 13733112 | 5108700.58 | 0 | 0 | 0 | 4963852.8 | 5924515.5 | 5958585.99 | 316656 | 342000 | 0 | 0 | 0 | 4604947.2 | 0 | 792409.77 | 463320 | 5103000 | 0 | 4850260.2 | 5401559.28 | 0 | 0 | 0 |  | 1631772 | 15449149.44 | 4454082.94 | 8010349.2 | 1119897.6 | 3837537.6 | 303458.88 | 2097100.8 | 0 | 0 | 0 | 7941162 | 6486590 | 5055280 | 0 | 0 | 0 | 0 | 0 | 1889204.2 | 0 | 5900260.96 | 0 | 487774.8 | 186705 | 1051225 | 309855 | 24834758.4 | 2016412.8 | 0 | 450823.68 | 183310 | 1400140 | 1237104 | 1981512 | 1695635.28 | 2969132.1 | 0 | 2618161.92 | 4255027.2 | 0 | 4742283.3 | 0 | 0 | 501098.4 | 7173500 | 400806 | 79769.6 | 0 | 26406047.85 | 0 | 0 | 29407968 | 0 | 22167756 | 1541852.55 | 7014297.6 | 16706726.4 | 3196371.44 | 8145680 | 9134592 | 13228470.72 | 10188499.75 | 0 | 28307910.64 | 4850373.33 | 14038084.3 | 14232216 | 4255246.8 | 7836998.4 | 7662956 | 16261056 | 4448866 | 14728521.6 | 7495277.68 | 0 | 5764161.6 | 2170777.25 | 20637043.2 | 5698922.4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 63534543 | 0 | 1611187.2 | 0 | 9923644.8 | 0 | 0 | 0 | 3397406.4 | 13565952 | 1147803.75 | 3355520 | 1149029.02 | 12536918.4 | 0 | 0 | 0 | 3508015.68 | 1376323.08 | 12716571.2 | 0 | 0 | 3428620.87 | 2801196.71 | 1944537.42 | 0 | 0 | 132717.24 | 0 | 0 | 24504867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4466368.88 | 0 | 9275255.55 | 9663897.6 | 0 | 11264809.92 | 9492609.6 | 12196876.8 | 0 | 564135.65 | 11902638.72 | 282987882 | 5358477.18 | 0 | 10123200 | 384766.2 | 8132186.13 | 8273784.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 586417479.9 | 544721742.96 | 1131139222.86 | 99477050.02 | 63534543 | 58408545.49 | 0 | 479235921.41 | 307492749 | 1255729.77 | 0 | 79474031.99 | 24834758.4 | 17425893.78 | 0 | 0
Yesterday Day Peak | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 0 | 327 |  | 0 | 450 | 0 | 42 | 17 | 0 | 324 | 0 | 121 | 0 | 33 | 32 | 22 | 0 | 0 | 0 | 17 | 35 | 5 | 19 | 19 | 23 | 33 | 24 | 8 | 0 | 127 | 75 | 118 | 0 | 8 | 220 | 0 | 0 | 0 |  | 6 | 24 | 17 | 25 | 0 | 6 | 10 | 11 | 0 | 0 | 0 | 270 | 240 | 181 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 11 | 0 | 12 | 10 | 25 | 17 | 156 | 59 | 0 | 16 | 2 | 43 | 40 | 47 | 38 | 112 | 0 | 60 | 75 | 0 | 181 | 0 | 0 | 10 | 290 | 16 | 5 | 0 | 65 | 0 | 0 | 96 | 0 | 70 | 20 | 25 | 51 | 5 | 367 | 28 | 35 | 34 | 5 | 70 | 17 | 47 | 106 | 9 | 25 | 350 | 50 | 51 | 54 | 34 | 0 | 17 | 35 | 73 | 17 | 240 | 17 | 0 | 0 | 11 | 181 |  | 909 | 0 | 95 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 130 | 22 | 32 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 414 | 36 | 0 | 35 | 15 | 29 | 0 | 7 | 35 | 1244 | 220 | 0 | 0 | 5 | 64 | 0 | 50 | 0 | 402 | 11 | 0 | 1256 | 154 | 0 |  | 12284 | DayPeak
Yesterday Evening Peak | 0 | 0 | 140 | 180 | 0 | 0 | 0 | 60 | 337 | 0 | 0 | 450 | 0 | 74 | 34 | 15 | 327 | 0 | 175 | 88 | 102 | 98 | 22 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 24 | 33 | 33 | 25 | 0 | 126 | 75 | 117 | 0 | 25 | 224 | 0 | 0 | 0 | 0 | 6 | 49 | 0 | 35 | 12 | 39 | 10 | 24 | 0 | 0 | 0 | 280 | 240 | 177 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 23 | 0 | 16 | 10 | 25 | 17 | 140 | 78 | 0 | 16 | 0 | 43 | 40 | 47 | 42 | 112 | 0 | 53 | 84 | 0 | 181 | 0 | 0 | 10 | 290 | 24 | 3 | 0 | 148 | 0 | 0 | 163 | 0 | 135 | 0 | 50 | 103 | 33 | 366 | 74 | 88 | 34 | 0 | 285 | 17 | 60 | 34 | 29 | 50 | 350 | 71 | 0 | 108 | 34 | 0 | 17 | 0 | 100 | 17 | 230 | 143 | 0 | 0 | 2 | 0 |  | 779 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 26 | 52 | 8 | 124 | 30 | 110 | 0 | 0 | 0 | 28 | 17 | 92 | 0 | 0 | 39 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 414 | 17 | 0 | 50 | 50 | 56 | 0 | 0 | 55 | 1244 | 222 | 0 | 150 | 0 | 0 | 75 | 234 | 0 | 500 | 0 | 0 | 1365 | 0 | 0 |  | 14036 | EvPeak
Forecast for Evening | 0 | 0 | 140 | 180 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 450 | 0 | 74 | 34 | 15 | 330 | 0 | 150 | 88 | 102 | 98 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 21 | 33 | 33 | 25 | 0 | 125 | 75 | 120 | 0 | 25 | 225 |  | 0 | 0 | 0 | 6 | 50 | 0 | 35 | 12 | 47 | 10 | 25 | 0 | 0 | 0 | 280 | 240 | 180 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 23 | 0 | 16 | 11 | 25 | 17 | 163 | 80 | 0 | 16 | 0 | 43 | 40 | 50 | 42 | 112 | 0 | 50 | 86 | 0 | 180 | 0 | 0 | 10 | 300 | 24 | 3 | 0 | 145 | 0 | 0 | 150 | 0 | 135 | 0 | 50 | 100 | 30 | 370 | 85 | 88 | 51 | 0 | 285 | 17 | 55 | 34 | 30 | 50 | 350 | 70 | 0 | 108 | 34 | 0 | 17 |  | 115 | 17 | 230 | 143 |  | 0 | 10 | 0 |  | 909 | 0 | 0 |  | 63 | 0 | 0 | 0 | 40 | 52 | 8 | 132 | 30 | 110 | 0 | 0 | 0 | 35 | 20 | 92 | 0 | 0 | 40 | 40 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 155 | 0 | 414 | 17 | 0 | 50 | 50 | 56 | 0 | 0 | 55 | 1244 | 220 |  | 150 |  |  | 75 | 230 |  | 500 |  | 0 | 1360 |  | 0
Forecast for Day | 0 | 0 | 140 | 180 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 450 | 0 | 34 | 17 | 15 | 330 | 0 | 130 | 60 | 25 | 16 | 22 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 19 | 21 | 25 | 33 | 8 | 0 | 125 | 75 | 120 | 0 | 8 | 225 |  | 0 | 0 | 0 | 6 | 34 | 0 | 35 | 0 | 6 | 10 | 10 | 0 | 0 | 0 | 270 | 240 | 170 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 23 | 0 | 16 | 11 | 25 | 17 | 146 | 70 | 0 | 16 | 1.6 | 43 | 40 | 50 | 42 | 112 | 0 | 50 | 86 | 0 | 180 | 0 | 0 | 10 | 300 | 24 | 3 | 0 | 65 | 0 | 0 | 95 | 0 | 70 | 20 | 25 | 51 | 6 | 350 | 68 | 35 | 34 | 5 | 70 | 17 | 55 | 17 | 9 | 25 | 350 | 34 | 50 | 54 | 34 | 0 | 17 | 35 | 72 | 17 | 230 | 17 |  | 0 | 10 | 0 |  | 909 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 40 | 8 | 130 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 30 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 414 | 17 | 0 | 35 | 15 | 35 | 0 | 8 | 35 | 1244 | 220 |  | 17 | 6 | 100 | 0 | 0 |  | 400 | 30 | 0 | 1200 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 140 | 180 | 0 | 0 | 0 | 281 | 332 | 0 | 0 | 450 | 0 | 45 | 17 | 15 | 320 | 0 | 125 | 50 | 16 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 7 | 33 | 33 | 8 | 0 | 100 | 40 | 118 | 0 | 8 | 224 | 0 | 0 | 0 | 0 | 6 | 26 | 0 | 25 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 325 | 240 | 165 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 16 | 10 | 25 | 17 | 126 | 33 | 0 | 16 | 1 | 43 | 40 | 47 | 43 | 112 | 0 | 58 | 75 | 0 | 181 | 0 | 0 | 10 | 310 | 24 | 8 | 0 | 65 | 0 | 0 | 68 | 0 | 35 | 5 | 25 | 17 | 5 | 401 | 19 | 17 | 34 | 2 | 69 | 17 | 55 | 15 | 9 | 25 | 350 | 50 | 19 | 17 | 17 | 0 | 17 | 11 | 18 | 17 | 230 | 17 | 0 | 0 | 0 | 0 | 0 | 905 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 10 | 18 | 0 | 126 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 414 | 17 | 0 | 35 | 15 | 34 | 0 | 1 | 35 | 1100 | 222 | 0 | 17 | 1 | 49 | 0 | 235 | 0 | 402 | 5 | 0 | 1310 | 49 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
292.3904
| Minimum Generation |  | 11068 | 7:00
| Highest Generation |  | 14036 | 21:00
| Day Peak Generation |  | 12284 | 12:00
| Evening Peak Generation |  | 14036 | 21:00
| HVDC Max Flow |  | 909 | 6:00
| HVDC EvPeak Flow |  | 779 | 21:00
| Load factor L.F |  | 88.23% | [164 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-08-20
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-08-19 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 12284 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 11660
Evening Peak Generation : |  |  | 14036 | MW Hour : | 21:00 | Available Max Generation : |  | 14191
E.P. Demand (at gen end) : |  |  | 14700 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 15200
Maximum Generation : |  |  | 14036 | MW Hour : | 21:00 | Reserve(Generation end) |  | -
Total Gen. (MKWH) : |  |  | 297.2138 | System Load Factor : | 88.23% | Load Shed : |  | 950
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 890 | MW at | 2:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-08-20
Actual : |  | 102.98 | Ft.(MSL) , | Rule curve : | 95.08 | Ft.( MSL )
Gas Consumed : |  | Total = | 1112.72 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 157885595.51
: |  |  | Coal : | 307492749 | Oil : | 558709953.4 | Total : | 1024088297.91
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 10 | 240:00 | 4986.8826 |  |  | 200 | 4.011%
Chittagong Area |  | 77 | 1848:00 | 1372.8008 |  |  | 110 | 8.013%
Khulna Area |  | 164 | 3936:00 | 1923.7853 |  |  | 130 | 6.758%
Rajshahi Area |  | 82 | 1968:00 | 1672.8176 |  |  | 130 | 7.771%
Cumilla Area |  | 55 | 1320:00 | 1376.0741 |  |  | 110 | 7.994%
Mymensingh Area |  | 90 | 2160:00 | 1023.8281 |  |  | 90 | 8.791%
Sylhet Area |  | 0 | 0:00 | 573.4853 |  |  | 50 | 8.719%
Barisal Area |  | 0 | 0:00 | 478.2986 |  |  | 40 | 8.363%
Rangpur Area |  | 156 | 3744:00 | 935.4597 |  |  | 90 | 9.621%
Total |  | 634 |  | 14343.4322 |  |  | 950
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
| 08:17 | Bogura 230/132kV S/S T-01 LT is restored.
| 08:17 | Bogura 230/132kV S/S T-01 HT is restored.
08:26 | 14:40 | Gopalganj 132/33kV S/S T1 LT Scheduled S/D Due to Due to high side R & B phage bushing top maintenance of
Transformer-1 by energyp
08:27 | 14:39 | Gopalganj 132/33kV S/S T1 HT Scheduled S/D
08:27 | 14:39 | Gopalganj 132/33kV S/S T1 HT Scheduled S/D
08:44 | 16:41 | Madunaghat-Sikalbaha 132kV Ckt-2 Scheduled S/D from Madunaghat 132/33kV end Due to Line inspection and
maintenance work.
08:45 | 16:42 | Shikalbaha 230/132kV S/S Modunaghat Ckt-1 Forced S/D Due to Line maintenance
| 09:19 | Bakulia 132/33kV S/S T-3 (422T) HT is restored.
| 09:22 | Mymensingh 132/33kV S/S Transformer-3 (424T) HT is restored.
| 09:23 | Mymensingh 132/33kV S/S Transformer-3 (424T) LT is restored.
| 09:24 | Bakulia 132/33kV S/S T-3 (422T) LT is restored.
| 09:30 | Mahasthangarh 132/33kV S/S 416T MTR 2 HT is restored.
| 09:31 | Mahasthangarh 132/33kV S/S 416T MTR 2 LT is restored.
09:48 | 11:50 | Barguna 132/33kV S/S Transformer-1 HT Scheduled S/D Due to 33 KV BREB-2 Feeder D/S load
side Redhot Maintenance.
10:05 | 12:40 | Shikalbaha 230/132kV S/S Interconnection-2 Forced S/D Due to Bay maintenance at Shikalbahab132KV end.
10:20 |  | Matarbari 2*600 MW (CPGCL) unit-1 was sync.
10:45 | 11:40 | Kabirpur -Tongi 132kV Ckt-1 Forced S/D from Tongi 230/132/33kV end Due to For Kabirpur end Side Works
11:07 | 16:05 | Kulaura 132/33kV S/S TR-1 HT Scheduled S/D Due to 33KV bus maintenance by PBS. |  |  |  |  | 25.0MW load interruption.
11:07 | 16:07 | Kulaura 132/33kV S/S TR-1 LT Scheduled S/D Due to 33KV bus maintenance by PBS.
11:29 | 13:37 | Shahjadpur 132/33kV S/S T-4(435T) HT Forced S/D Due to Red-hot maintanace 33 kv R phase DS for T-4 Transformer.
11:29 | 13:37 | Shahjadpur 132/33kV S/S T-4(435T) HT Forced S/D Due to Red-hot maintanace 33 kv R phase DS for T-4 Transformer.
11:29 |  | Khulna 330 MW CCPP GT was sync.
12:00 |  | Day peak generation is 12284MW
12:00 |  | Day peak generation: 12284 MW.
12:50 |  | Khulna 330 MW CCPP GT was forced shutdown |  |  |  |  | 50 MW generation interruption
14:58 | 16:40 | Ashuganj-Brahmanbaria 132kV Ckt-2 Forced S/D from Brahmanbaria 132/33kV end Due to Emergency maintenance
Ashugonj sub-station and from Ashuganj 230/132/33kV end Due to R-phase CB oil filling
15:10 |  | Matarbari 2*600 MW (CPGCL) unit-1 was shutdown due to safety valve leakage. |  |  |  |  | 180 MW generation interruption
| 15:49 | Haripur 230/132kV S/S EGCB 412MW is restored.
15:51 |  | Bheramara 410MW was shutdown due to gas shortage. |  |  |  |  | 50 MW generation interruption
18:24 |  | Haripur 412MW CCPP GT was sync.
| 19:45 | Bogura 132/33kV S/S 132KV Bus-B is restored.
20:33 | 22:16 | Bogura 230/132kV S/S T-02 LT Forced S/D Due to Red hot maintenance
20:33 | 22:16 | Bogura 230/132kV S/S T-02 HT Forced S/D Due to red Hot maintenance
21:00 |  | Evening Peak Gen. 14036 MW
| 21:18 | APR-Hasnabad 230kV Ckt-2 is restored.
| 22:40 | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-2 is restored.
23:25 | 02:29 | Jamalpur 132/33kV S/S T-2 LT Forced S/D Due to 33 kv t2 extantion bus DS Red hot work |  |  |  |  | 40.0MW load interruption.
23:25 | 02:29 | Jamalpur 132/33kV S/S T-2 HT Forced S/D Due to 33 kv t2 extantion bud DS Redhot work
07:00 |  | Minimum Generation is 11661 MW

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-08-19 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 140 | 3625250
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4277700
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 213272 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 60 | 2222080 | Machine problem
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 337 | 7966000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10253800
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 74 | 1218240 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Under maint.
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 34 | 516409 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 350200 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 22 | 554089 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 422208 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 175 | 3139000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 88 | 688234 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 327 | 7748912 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1220832
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 390240 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 98 | 847200 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 438853 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 444339
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 43 | 812760 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 738100
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 729400
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 270720 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 148 | 1934509 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Contract Expired
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 135 | 1600560 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 914832 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 71 | 1255680 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 1160640 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 181655
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 432720 | Fuel shortage
| Dhaka area Total |  |  |  | 5722 | 2947 | 56568434
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 117 | 2700000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 296652
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 131895
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 39 | 331680 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 201 | 4650851
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 224 | 5193807
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 34 | 805415 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 49 | 926208 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 261697 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 35 | 592920 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 679680 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 10 | 238944 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 24 | 629760
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 12 | 88320 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 35402
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 285 | 2411236 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 445397 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 60 | 1320610 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 665280 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 34 | 658636 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 143 | 746036 | Engine problem
| SS Power I |  | SS Power | 0 | 0 | 0 | 0 | On test.
| Cox's Bazar Wind |  | IPP | 66 | 0 | 2 | 262080 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 0 | 523636 | On test.
| Chattogram area Total |  |  |  | 2545 | 1411 | 24596142
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 177 | 4358000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7154200 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 240 | 5951000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 230 | 5829600 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 0 | 0 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1131260
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 33 | 240872 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 23 | 341648 | Fuel shortage
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 103 | 1223040 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 356040 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 248940
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 140 | 3458880
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 600700 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 17 | 413140 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 1048800 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 29 | 330120 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 441360 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 100 | 1378560 | Engine problem
| Cumilla Area Total |  |  |  | 2896 | 1525 | 34506160
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 78 | 1849920 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 331488 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11500
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 163 | 2181600 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 74 | 751200 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 307880
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 125040 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 337 | 5558628
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1022000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 937200 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2581854 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 1138800
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 42 | 980136 | Engine problem
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 3 | 104960 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 53 | 1349568
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1866240
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 181 | 4695330 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Machine problem
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 534408
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7173500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 366 | 8854000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 253080
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 350 | 8329300
| Sylhet Area Total |  |  |  | 2427 | 1645 | 39820376
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 779 | 21178181
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 63 | 953280
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 26 | 188640
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 52 | 753664
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 1438560 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 79875 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 719040 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 50 | 656928 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 693281
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 220 | 234 | 1171578
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 500 | 10378180 | Coal shortage.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 3121 | 1729 | 38211207
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1150176
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 30 | 592283 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 124 | 2996000 | ST Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 31408200
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 222 | 5253409
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1368000
| Barisal 307 MW |  | IPP | 307*1 | 307 | 0 | 0 | Coal shortage.
| Barisal Area Total |  |  |  | 2265 | 1880 | 42768068
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 28 | 209184 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 17 | 78692 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Fuel shortage
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 39 | 202757 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage.
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 151 | 3850318 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 9368945
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 115266 | Fuel shortage
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 175320 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 205517 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 813080 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 952224 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 55 | 980448 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 34020
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1365 | 30500727
| Rajshahi Area Total |  |  |  | 3631 | 2251 | 47486498
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 180 | 4632300 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 56 | 960384 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 51053
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 75 | 539712 | Fuel shortage
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 241641
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1273200
| Rangpur Area Total |  |  |  | 950 | 311 | 7698290
| Total |  |  |  | 24171 | 14036 | 297213803
| Eastern Grid Total |  |  |  | 14204 | 7865 | 161049740
| Western Grid Total |  |  |  | 9967 | 6171 | 136164063
| National Grid Total |  |  |  | 24171 | 14036 | 297213803
*Data collected from respective power station over telephone.
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-08-19
| (a) ENTIRE EASTERN GRID : |  | 9140.91 | MW | (b) ENTIRE WESTERN GRID : |  | 4158.6 | MW
| i) Dhaka area |  | 4850.51 | MW | i) Khulna area |  | 1562.9 | MW
| ii) Chittagong area |  | 1291.4 | MW | ii) Rajshahi area |  | 1290 | MW
| iii) Comilla area |  | 1265 | MW | iii) Barisal area |  | 463.7 | MW
| iv) Mymensingh area |  | 1114 | MW | iv) Rangpur area |  | 842 | MW
| v) Sylhet area |  | 620 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 13299.51 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 34 | 22:00 | Kamrangirchar | 45 | 00:00 | Natore | 132 | 13:00 | Sholosohor | 41 | 09:00
2 | AKSML | 101 | 05:00 | Chowmuhani | 232 | 20:00 | Kaptai | N/A | N/A | Nawabganj | 48.4 | 22:00 | Shyampur | 164 | 11:00
3 | Aftabnagar | 52 | 13:00 | Chuadanga | 119 | 19:30 | Kazla | 89 | 14:00 | Netrakona | 125 | 20:00 | Siddhirganj | 118 | 15:00
4 | Agargaon | 84 | 19:00 | Coxsbazar | 113 | 18:30 | Keranigonj | 76 | 19:30 | New | 70.2 | 12:00 | Sirajganj | 108 | 00:00
5 | Agrabad | 74 | 19:30 | Cumilla(N) | 164 | 21:00 | Khagrachori | 36 | 19:00 | Niamatpur | 84 | 21:00 | Sonargaon | 88 | 21:00
6 | Amnura | 57 | 00:00 | Cumilla(S) | 158 | 00:00 | Khulna | 96 | 13:00 | Noapara | 48 | 22:00 | Sreemongol | 76 | 21:00
7 | Ashuganj | 74 | 00:00 | Daudkandi | 140 | 20:00 | Khulshi | 188 | 19:30 | PHP | 3 | 00:00 | Sreepur | 80 | 16:00
8 | BIPTC | N/A | N/A | Dhaka | 34 | 12:00 | Kishoreganj | 136 | 16:00 | Pabna | 120 | 19:00 | Srinagar | 47.3 | 22:00
9 | BSRM | 170 | 02:00 | Dhamrai | 132 | 19:30 | Kodda | 272 | 21:00 | Palashbari | 152 | 21:00 | Sunamganj | 53 | 20:00
10 | Bagerhat | 89 | 22:00 | Dhanmondi | 141 | 13:00 | Kulaura | 56 | 21:00 | Panchagarh | 48 | 18:30 | Sylhet | 171 | 19:00
11 | Bakulia | 102 | 19:00 | Dohazari | 88 | 18:30 | Kurigram | 60 | 07:00 | Patuakhali | 108.5 | 22:00 | TK | 0 | 00:00
12 | Banani | 52 | 12:00 | Faridpur | 158 | 22:00 | Kushtia | 156 | 19:30 | Payra | 25.4 | 22:00 | Tangail | 231 | 21:00
13 | Bangabhaban | 7 | 10:00 | Fatullah | 62 | 11:00 | Lalbag | 76 | 13:00 | Postogola | 58 | 13:00 | Thakurgaon | 84 | 22:00
14 | Barapukuria | 60 | 19:30 | Fenchuganj | 50 | 18:30 | Lalmonirhat | 52 | 19:00 | Purbachal | 18 | 19:00 | Tongi | 123 | 16:00
15 | Barguna | 20 | 02:00 | Feni | 124 | 19:00 | Madanganj | 34 | 00:00 | Purbasadipur | 119 | 12:00 | Ullon | 50 | 00:00
16 | Barishal | 104 | 21:00 | GPH | 12 | 10:00 | Madaripur | 110 | 22:00 | Rahim | 42 | 08:00 | Uttara | 70 | 19:30
17 | Barishal-230 | 102 | 21:00 | Ghorashal | 74 | 21:00 | Madartek | 87.07 | 00:00 | Rajbari | 72 | 19:00 | UttaraNew | 67 | 23:00
18 | Baroaulia | 64 | 00:00 | Goalpara | 36 | 00:00 | Madunaghat | 55 | 19:00 | Rajendrapur | 108 | 19:30 | Zigatola | 74 | 19:00
19 | Baroirhat | 69 | 20:00 | Gollamari | 50 | 13:00 | Magura | 64 | 22:00 | Rajshahi | 163 | 19:30
20 | Bashundhara | 146 | 15:00 | Gopalganj | 101.6 | 22:00 | Mahasthangarh | 78 | 19:00 | Rajshahi-230 | 36 | 00:00
21 | BashundharaCement | 6 | 09:00 | Gulshan | 62 | 12:00 | Manikganj | 115 | 21:00 | Ramganj | 112 | 19:00
22 | Beanibazar | 80 | 20:00 | Halishahar | 72.5 | 19:30 | Maniknagar | 73 | 13:00 | Rampur | 30 | 19:30
23 | Benapole | 66 | 22:00 | HaripurSBU | 153 | 16:00 | Matarbari | 50 | 19:00 | Rangamati | 18 | 20:00
24 | Bhaluka | 150 | 10:00 | Hasnabad | 90 | 19:00 | Matuail | 73 | 12:00 | Rangpur | 135 | 19:30
25 | Bhandaria | 52 | 22:00 | Hathazari | 79 | 19:00 | Millgate | 102 | 16:00 | Ruppur | 3.8 | 08:00
26 | Bhangura | 35 | 19:00 | Ishurdi | 69 | 13:00 | Mirpur | 132 | 19:00 | SSM | 0 | 00:00
27 | Bheramara(GK) | 65 | 22:00 | Jaldhaka | 72 | 19:00 | Mirsorai | 0 | 00:00 | Saidpur | 111 | 10:00
28 | Bhulta | 246 | 19:30 | Jamalpur | 175 | 20:00 | Mithapukur | 42 | 19:00 | Satkhira | 118 | 22:00
29 | Bog-Sherpur | 64 | 19:00 | Jashore | 129 | 22:00 | Modern | 0 | 00:00 | Satmasjid | 111 | 19:00
30 | Bogura | 147 | 00:00 | Jhenaidah | 127 | 22:00 | Mogbazar | 121.3 | 15:00 | Savar | 190 | 19:30
31 | Borhanuddin | 67 | 22:00 | Joydebpur | 176 | 19:30 | Mongla | 28 | 11:00 | Shahjadpur | 95 | 22:00
32 | Brahmanbaria | 168 | 20:00 | Joypurhat | 62 | 00:00 | Motijheel | 37 | 20:00 | Shahjibazar | 129 | 21:00
33 | Cantonment | 138 | 13:00 | Juldah | 28 | 13:00 | Munshiganj | 101 | 23:00 | Shahmirpur | 49.1 | 00:00
34 | Chandpur | 70 | 20:00 | KSRM | 24.5 | 21:00 | Mymensingh | 221 | 23:00 | Shariatpur | 86 | 22:00
35 | Chandraghona | 32 | 20:00 | Kabirpur | 285 | 09:00 | Naogaon | 128 | 00:00 | Sherpur | 164 | 19:00
36 | Chapai | 67 | 20:00 | Kachua | 85 | 19:00 | Narail | 57 | 22:00 | Shikalbaha | 40 | 21:00
37 | Charsaidpur | 44 | 00:00 | Kallyanpur | 108 | 00:00 | Narinda | 68 | 17:00 | Shikalbaha-230 | N/A | N/A
38 | Chauddagram | 60 | 20:00 | Kalurghat | 33 | 12:00 | Narshingdi | 182 | 19:30 | Shitalakhya | 100.1 | 16:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-08-19 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 398 | 03:00 | 386 | 16:00 | Gopalganj | 404 | 00:00 | 395 | 16:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 379 | 19:30 | 365 | 15:00
| Bhulta | 396 | 03:00 | 384 | 16:00 | Madunaghat_I | 388 | 00:00 | 382 | 12:00
| Bibiana | 403 | 09:00 | 394 | 15:00 | Payra | 412 | 03:00 | 406 | 13:00
| BIPTC | 398 | 06:00 | 390 | 13:00 | Rahanpur | N/A | N/A | N/A | N/A
| Bogura | N/A | N/A | N/A | N/A | Rampal | 405 | 09:00 | 398 | 13:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 232 | 00:00 | 224 | 13:00 | Hasnabad | 232 | 00:00 | 223 | 13:00
| AKSML | 233 | 20:00 | 231 | 19:30 | Hathazari | 236 | 21:00 | 229 | 08:00
| Aminbazar | 235 | 01:00 | 226 | 15:00 | Ishurdi | 233 | 20:00 | 224 | 16:00
| Ashuganj | 233 | 07:00 | 226 | 15:00 | Jhenaidah | 224 | 07:00 | 214 | 22:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 233 | 19:30 | 223 | 15:00
| Baghabari | 227 | 00:00 | 220 | 21:00 | Keranigonj | 231 | 00:00 | 223 | 13:00
| Barapukuria | 220 | 16:00 | 207 | 05:00 | Khulna(S) | 234 | 00:00 | 224 | 22:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | 232 | 07:00 | 230 | 05:00
| Barishal | 238 | 07:00 | 233 | 05:00 | Maniknagar | 232 | 03:00 | 224 | 13:00
| Bheramara | 233 | 19:30 | 222 | 16:00 | Meghnaghat | 236 | 00:00 | 229 | 15:00
| Bhulta | 234 | 01:00 | 226 | 15:00 | Mirsorai | 233 | 22:00 | 225 | 00:00
| Bibiana | 232 | 09:00 | 227 | 08:00 | Rajshahi | 228 | 20:00 | 218 | 16:00
| BIPTC | 233 | 19:30 | 221 | 16:00 | Rampal | 233 | 07:00 | 224 | 22:00
| Bogura | 226 | 07:00 | 218 | 01:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 242 | 17:00 | 239 | 01:00 | Rampura | 232 | 00:00 | 224 | 16:00
| BSRM | 235 | 19:30 | 225 | 18:00 | Shikalbaha | 234 | 19:30 | 227 | 04:00
| Cumilla(N) | 230 | 19:30 | 224 | 15:00 | Shyampur | 231 | 00:00 | 223 | 13:00
| Fenchuganj | 235 | 19:30 | 230 | 19:00 | Siddhirganj | 233 | 00:00 | 226 | 14:00
| Ghorashal | 235 | 00:00 | 235 | 00:00 | Sirajgonj | 235 | 07:00 | 230 | 13:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 228 | 07:00 | 223 | 13:00
| GPH | 239 | 07:00 | 226 | 18:00 | Tongi | 232 | 04:00 | 220 | 15:00
| Haripur | 230 | 00:00 | 224 | 15:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 136 | 06:00 | 129 | 15:00 | Lalbag | 136 | 03:00 | 130 | 13:00
| Agargaon | 133 | 00:00 | 127 | 13:00 | Lalmonirhat | 130 | 09:00 | 115 | 03:00
| Agrabad | 134 | 19:30 | 129 | 18:30 | Madanganj | 134 | 00:00 | 127 | 12:00
| AKS | 133 | 19:30 | 129 | 23:00 | Madaripur | 130 | 03:00 | 127 | 22:00
| Aminbazar | 136 | 19:30 | 125 | 16:00 | Madartek | 136 | 03:00 | 128 | 16:00
| Amnura | 140 | 20:00 | 123 | 00:00 | Madunaghat | 135 | 19:30 | 131 | 13:00
| Ashuganj | 139 | 08:00 | 134 | 16:00 | Magura | 134 | 07:00 | 123 | 22:00
| Bagerhat | 133 | 07:00 | 121 | 22:00 | Mahasthangarh | 133 | 09:00 | 125 | 02:00
| Bakulia | 138 | 19:30 | 131 | 18:00 | Manikganj | 134 | 19:00 | 126 | 11:00
| Banani | 135 | 00:00 | 129 | 13:00 | Maniknagar | 135 | 00:00 | 128 | 13:00
| Bangabhaban | 135 | 00:00 | 129 | 13:00 | Matarbari | 129 | 00:00 | 112 | 18:30
| Barapukuria | 137 | 16:00 | 125 | 05:00 | Matuail | 134 | 00:00 | 126.4 | 13:00
| Barguna | 138 | 18:30 | 132 | 01:00 | Millgate | 137 | 04:00 | 126 | 15:00
| Barishal | 139 | 19:30 | 130 | 00:00 | Mirpur | 134 | 00:00 | 127 | 13:00
| Barishal-230 | 137 | 18:30 | 133 | 04:00 | Mithapukur | 131 | 09:00 | 117 | 05:00
| Baroaulia | 136 | 19:30 | 130 | 18:30 | Modern | 135 | 21:00 | 128 | 18:00
| Baroirhat | 134 | 19:30 | 123 | 03:00 | Mogbazar | 137 | 05:00 | 130 | 12:00
| Bashundhara | 135 | 01:00 | 126 | 13:00 | Mongla | 132 | 00:00 | 122 | 22:00
| BashundharaCement | 134 | 00:00 | 127 | 12:00 | Motijheel | 135 | 00:00 | 129 | 13:00
| Beanibazar | 130 | 02:00 | 121 | 20:00 | Munshiganj | 135 | 00:00 | 127 | 13:00
| Benapole | 133 | 09:00 | 122 | 22:00 | Mymensingh | 134 | 19:30 | 115 | 18:30
| Bhaluka | 122 | 00:00 | 116 | 16:00 | Naogaon | 129 | 07:00 | 121 | 01:00
| Bhandaria | 135 | 19:30 | 125 | 02:00 | Narail | 134 | 09:00 | 121 | 22:00
| Bhangura | 134 | 19:30 | 130 | 16:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 133 | 01:00 | 126 | 22:00 | Narshingdi | 128 | 00:00 | 120 | 11:00
| Bheramara(GK) | 133 | 03:00 | 126 | 16:00 | Natore | 133 | 07:00 | 122 | 22:00
| Bhulta | 125 | 00:00 | 118 | 15:00 | Nawabganj | 136 | 07:00 | 130 | 13:00
| Bog-Sherpur | 127 | 00:00 | 123 | 15:00 | Netrakona | 132 | 19:30 | 116 | 23:00
| Bogura | 135 | 09:00 | 112 | 22:00 | New | 136 | 06:00 | 126 | 15:00
| Bogura-230 | 136 | 09:00 | 129 | 01:00 | Niamatpur | 128 | 07:00 | 116 | 23:00
| Brahmanbaria | 127 | 08:00 | 120 | 20:00 | Noapara | 134 | 07:00 | 125 | 22:00
| Cantonment | 133 | 03:00 | 126 | 13:00 | Pabna | 131 | 00:00 | 126 | 22:00
| Chandpur | 137 | 19:30 | 116 | 05:00 | Palashbari | 130 | 09:00 | 121 | 19:00
| Chandraghona | 137 | 19:30 | 132 | 18:00 | Panchagarh | 136 | 00:00 | 108 | 05:00
| Chapai | 130 | 07:00 | 123 | 19:00 | Patuakhali | 140 | 19:00 | 132 | 07:00
| Charsaidpur | 135 | 00:00 | 128 | 12:00 | Payra | 139 | 03:00 | 136 | 02:00
| Chauddagram | 130 | 10:00 | 122 | 06:00 | PHP | 132 | 19:30 | 120 | 20:00
| Chhatak | 128 | 06:00 | 123 | 19:30 | Postogola | 135 | 00:00 | 130 | 12:00
| Chowmuhani | 128 | 19:00 | 117 | 20:00 | Purbachal | 136 | 02:00 | 126 | 13:00
| Chuadanga | 132 | 09:00 | 116 | 22:00 | Purbasadipur | 132 | 00:00 | 110 | 05:00
| Coxsbazar | 128 | 00:00 | 114 | 18:30 | Rahanpur | N/A | N/A | N/A | N/A
| Cumilla(N) | 132 | 10:00 | 128 | 21:00 | Rahim | 134 | 00:00 | 128 | 12:00
| Cumilla(S) | 133 | 19:00 | 124 | 15:00 | Rajbari | 129 | 07:00 | 121 | 22:00
| Daudkandi | 132 | 19:30 | 126 | 06:00 | Rajendrapur | 134 | 19:00 | 124 | 16:00
| Dhaka | 136 | 04:00 | 130 | 12:00 | Rajshahi | 135 | 20:00 | 126 | 22:00
| Dhamrai | 135 | 00:00 | 128 | 13:00 | Rajshahi-230 | 136 | 19:30 | 121 | 23:00
| Dhanmondi | 134.5 | 00:00 | 126 | 13:00 | Ramganj | 131 | 19:30 | 115 | 04:00
| Dohazari | 134 | 19:30 | 127 | 18:30 | Rampur | 134 | 09:00 | 129 | 12:00
| Faridpur | 128 | 07:00 | 123 | 22:00 | Rampura | 135 | 00:00 | 129 | 13:00
| Fatullah | 130 | 00:00 | 124 | 13:00 | Rangamati | 136 | 19:30 | 131 | 18:00
| Fenchuganj | 134 | 07:00 | 130 | 19:00 | Rangpur | 130 | 17:00 | 114 | 05:00
| Feni | 133 | 19:30 | 122 | 20:00 | Ruppur | 134 | 07:00 | 128 | 22:00
| Ghorashal | 138 | 05:00 | 134 | 12:00 | Saidpur | 131 | 00:00 | 114 | 05:00
| Goalpara | 136 | 00:00 | 127 | 22:00 | Satkhira | 132 | 08:00 | 121 | 22:00
| Gollamari | 135 | 00:00 | 128 | 22:00 | Satmasjid | 133 | 00:00 | 127 | 13:00
| Gopalganj | 132 | 07:00 | 127 | 13:00 | Savar | 134 | 00:00 | 128 | 08:00
| Gopalganj-400 | 130 | 19:30 | 127 | 10:00 | Shahjadpur | 136 | 00:00 | 134 | 10:00
| Gulshan | 135 | 04:00 | 128 | 15:00 | Shahjibazar | 128 | 14:00 | 123 | 20:00
| Halishahar | 136 | 19:30 | 130 | 18:00 | Shahmirpur | 136 | 03:00 | 131 | 12:00
| Haripur | 134 | 00:00 | 128 | 12:00 | Shariatpur | 131 | 08:00 | 125 | 22:00
| HaripurSBU | 134 | 00:00 | 128 | 12:00 | Sherpur | 135 | 19:30 | 112 | 16:00
| Hasnabad | 136 | 00:00 | 130 | 11:00 | Shikalbaha | 126 | 20:00 | 120 | 18:00
| Hathazari | 137 | 21:00 | 133 | 08:00 | Shikalbaha-230 | 137 | 21:00 | 131 | 18:30
| Ishurdi | 134 | 00:00 | 128 | 16:00 | Shitalakhya | 135 | 00:00 | 128 | 13:00
| Jaldhaka | 131 | 16:00 | 110 | 06:00 | Sholosohor | 134 | 00:00 | 130 | 18:00
| Jamalpur | 136 | 19:30 | 116 | 16:00 | Shyampur | 131 | 02:00 | 124 | 13:00
| Jashore | 132 | 00:00 | 124 | 22:00 | Shyampur-230 | 130 | 03:00 | 124 | 13:00
| Jhenaidah | 136 | 08:00 | 127 | 21:00 | Siddhirganj | 134 | 00:00 | 128 | 12:00
| Jhenaidah-230 | 137 | 09:00 | 127 | 22:00 | Sirajganj | 130 | 19:30 | 125 | 15:00
| Joydebpur | 135 | 00:00 | 129 | 12:00 | Sonargaon | 131 | 19:30 | 128 | 08:00
| Joypurhat | 128 | 07:00 | 119 | 23:00 | Sreemongol | 129 | 07:00 | 124 | 20:00
| Juldah | 137 | 21:00 | 132 | 12:00 | Sreepur | 124 | 06:00 | 121 | 13:00
| Kabirpur | 137 | 19:00 | 124 | 10:00 | Srinagar | 136 | 01:00 | 130 | 15:00
| Kachua | 135 | 19:30 | 120 | 06:00 | SSM | 140 | 15:00 | 135 | 03:00
| Kaliakoir | 138 | 19:30 | 130 | 15:00 | Sunamganj | 126 | 07:00 | 120 | 18:30
| Kallyanpur | 129 | 02:00 | 124 | 13:00 | Sylhet | 131 | 07:00 | 127 | 18:30
| Kalurghat | 136 | 19:30 | 131 | 18:00 | Tangail | 133 | 19:30 | 124 | 16:00
| Kamrangirchar | 136 | 00:00 | 122 | 13:00 | Thakurgaon | 134 | 00:00 | 105 | 05:00
| Kaptai | N/A | N/A | N/A | N/A | TK | 136 | 09:00 | 130 | 15:00
| Kazla | 135 | 00:00 | 128 | 13:00 | Tongi | 137 | 04:00 | 130 | 04:00
| Keranigonj | 136 | 00:00 | 131 | 13:00 | Ullon | 136 | 07:00 | 129 | 13:00
| Khagrachori | 135 | 14:00 | 130 | 18:00 | Uttara | 134 | 21:00 | 128 | 11:00
| Khulna | 134 | 00:00 | 126 | 22:00 | UttaraNew | 134 | 19:30 | 128 | 11:00
| Khulna(S) | 134 | 00:00 | 128 | 22:00 | Zigatola | 136 | 03:00 | 131 | 13:00
| Khulshi | 134 | 19:30 | 128 | 18:00
| Kishoreganj | 130 | 07:00 | 123 | 16:00
| Kodda | 136 | 19:30 | 120 | 04:00
| KSRM | 136 | 19:30 | 131 | 13:00
| Kulaura | 132 | 11:00 | 128 | 21:00
| Kurigram | 130 | 16:00 | 113 | 02:00
| Kushtia | 133 | 03:00 | 124 | 22:00

## L-Curve
Date | 2023-08-19
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1086 | 6697 | 5941 | 12638 |  |  |  | QF-LDC-11
0:30 | 993 | 6712 | 5665 | 12377 | Date: | 2023-08-19
1:00 | 900 | 6727 | 5389 | 12116
1:30 | 895 | 6709.5 | 5378 | 12087.5
2:00 | 890 | 6692 | 5367 | 12059
2:30 | 905 | 6673.5 | 5360 | 12033.5 | [5 empty] | Gen. at Eve. Peak | 14036 | 14036 MW (21:00 )
3:00 | 920 | 6655 | 5353 | 12008 | [6 empty] | 21:00
3:30 | 940 | 6557.5 | 5426 | 11983.5 | [5 empty] | Gen. at Day Peak | 12284 | 12284 MW (12:00 )
4:00 | 960 | 6460 | 5499 | 11959 | [6 empty] | 12:00
4:30 | 975 | 6354 | 5490 | 11844 | [5 empty] | Highest Generation | 14036
5:00 | 990 | 6248 | 5481 | 11729 | [6 empty] | 21:00
5:30 | 965 | 6252.5 | 5300 | 11552.5
6:00 | 940 | 6257 | 5119 | 11376
6:30 | 975 | 6135.5 | 5086.5 | 11222
7:00 | 1010 | 6014 | 5054 | 11068
7:30 | 1095 | 5987.5 | 5090 | 11077.5
8:00 | 1180 | 5961 | 5126 | 11087
8:30 | 1195 | 5988.5 | 5202 | 11190.5
9:00 | 1210 | 6016 | 5278 | 11294
9:30 | 1300 | 6162 | 5380 | 11542
10:00 | 1390 | 6308 | 5482 | 11790
10:30 | 1385 | 6420.5 | 5483 | 11903.5
11:00 | 1380 | 6533 | 5484 | 12017
11:30 | 1332 | 6612.5 | 5538 | 12150.5
12:00 | 1284 | 6692 | 5592 | 12284
12:30 | 1282 | 6739.5 | 5600 | 12339.5
13:00 | 1280 | 6787 | 5608 | 12395
13:30 | 1280 | 6782.5 | 5560 | 12342.5
14:00 | 1280 | 6778 | 5512 | 12290
14:30 | 1348 | 6674 | 5513.5 | 12187.5
15:00 | 1416 | 6570 | 5515 | 12085
15:30 | 1418 | 6489.5 | 5482 | 11971.5
16:00 | 1420 | 6409 | 5449 | 11858
16:30 | 1385 | 6402.5 | 5437 | 11839.5
17:00 | 1350 | 6396 | 5425 | 11821
17:30 | 1325 | 6429.5 | 5456 | 11885.5
18:00 | 1300 | 6463 | 5487 | 11950
18:30 | 1203 | 6973.5 | 5722.5 | 12696
19:00 | 1106 | 7484 | 5958 | 13442
19:30 | 1060 | 7616 | 6106 | 13722
20:00 | 1110 | 7641 | 6146 | 13787 |  |  |  | Executive Engineer
20:30 | 1060 | 7753 | 6158.5 | 13911.5 |  |  |  | Network Operation Division
21:00 | 1010 | 7865 | 6171 | 14036
21:30 | 960 | 7798 | 6159 | 13957
22:00 | 910 | 7731 | 6147 | 13878 |  |  |  |  | Page 6 of 7
22:30 | 950 | 7469.5 | 6134.5 | 13604
23:00 | 990 | 7208 | 6122 | 13330
23:30 | 1038 | 6952.5 | 6031.5 | 12984
24:00 | 1086 | 6697 | 5941 | 12638
14036 MW (21:00 )
12284 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-08-19 |  | Energy |  | 297213803
QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3973 | 798 | 2140 | 0 | 1617 | 3282 | 200 | 236 | 249 | 140 | 0 | 3 | 0
0:30 | 4066.5 | 828.5 | 2140.5 | 0 | 1446 | 3211 | 200 | 118 | 211.5 | 146 | 0 | 9 | 660.86 |  | Date: | 43695
1:00 | 4160 | 859 | 2141 | 0 | 1275 | 3140 | 200 | 0 | 174 | 152 | 0 | 15 | 1321.72
1:30 | 4178 | 858.5 | 2132 | 0 | 1257.5 | 3141.5 | 200 | 0 | 158 | 150 | 0 | 12 | 1253.4375 | [8 empty] | Total Energy | 297.2138 | 297.2138 | Total Energy Gen 297.214 MKWHr Energy Not Served 13.640 MKWHr Energy Requirement 310.854 MKWHr
2:00 | 4196 | 858 | 2123 | 0 | 1240 | 3143 | 200 | 0 | 142 | 148 | 0 | 9 | 1185.155 | [8 empty] | Energy not Served | 13.6402 | 13.6402
2:30 | 4195 | 858.5 | 2105.5 | 0 | 1235 | 3141 | 200 | 0 | 141.5 | 147 | 0 | 10 | 1137.8825 | [8 empty] | Energy Requirement | 310.854 | 310.854
3:00 | 4194 | 859 | 2088 | 0 | 1230 | 3139 | 200 | 0 | 141 | 146 | 0 | 11 | 1090.61
3:30 | 4142 | 883.5 | 2098.5 | 0 | 1222.5 | 3138.5 | 200 | 0 | 141 | 144 | 0 | 13.5 | 1042.3825 | [7 empty] | Shortage
4:00 | 4090 | 908 | 2109 | 0 | 1215 | 3138 | 200 | 0 | 141 | 142 | 0 | 16 | 994.155
4:30 | 3990 | 907.5 | 2115 | 0 | 1194.5 | 3141.5 | 200 | 0 | 141 | 142 | 0 | 12.5 | 1008.48
5:00 | 3890 | 907 | 2121 | 0 | 1174 | 3145 | 200 | 0 | 141 | 142 | 0 | 9 | 1022.805
5:30 | 3920 | 908 | 2120 | 0 | 1095.5 | 3022 | 200 | 0 | 133 | 137 | 5.5 | 11.5 | 1000.3625
6:00 | 3950 | 909 | 2119 | 0 | 1017 | 2899 | 200 | 0 | 125 | 132 | 11 | 14 | 977.92
6:30 | 3911 | 908.5 | 2101 | 0 | 999 | 2846 | 160 | 0 | 123 | 125 | 36.5 | 12 | 957.865 | [6 empty] | Coal
7:00 | 3872 | 908 | 2083 | 0 | 981 | 2793 | 120 | 0 | 121 | 118 | 62 | 10 | 937.81
7:30 | 3797.5 | 908 | 2090.5 | 0 | 983.5 | 2812.5 | 120 | 0 | 111.5 | 121 | 123.5 | 9.5 | 833.2375 | [5 empty] | Oil
8:00 | 3723 | 908 | 2098 | 0 | 986 | 2832 | 120 | 0 | 102 | 124 | 185 | 9 | 728.665
8:30 | 3712.5 | 907.5 | 2007.5 | 0 | 1006.5 | 2895 | 161 | 0 | 101.5 | 127 | 259.5 | 12.5 | 725.3225
9:00 | 3702 | 907 | 1917 | 0 | 1027 | 2958 | 202 | 0 | 101 | 130 | 334 | 16 | 721.98
9:30 | 3743 | 908 | 1992 | 0 | 1094 | 2962.5 | 202 | 0 | 101 | 138 | 384 | 17.5 | 457.9225
10:00 | 3784 | 909 | 2067 | 0 | 1161 | 2967 | 202 | 0 | 101 | 146 | 434 | 19 | 193.865
10:30 | 3761 | 908.5 | 2035 | 0 | 1251.5 | 3089.5 | 202 | 0 | 98 | 145 | 396.5 | 16.5 | 142.295
11:00 | 3738 | 908 | 2003 | 0 | 1342 | 3212 | 202 | 0 | 95 | 144 | 359 | 14 | 90.725
11:30 | 3736 | 908.5 | 2041 | 0 | 1350 | 3257.5 | 202 | 25 | 111.5 | 150 | 356.5 | 12.5 | 84.04
12:00 | 3734 | 909 | 2079 | 0 | 1358 | 3303 | 202 | 50 | 128 | 156 | 354 | 11 | 77.355
12:30 | 3758.5 | 908 | 2058.5 | 0 | 1393.5 | 3332.5 | 202 | 25 | 160.5 | 152 | 340 | 9 | 210.5775
13:00 | 3783 | 907 | 2038 | 0 | 1429 | 3362 | 202 | 0 | 193 | 148 | 326 | 7 | 343.8
13:30 | 3783 | 907 | 2038 | 0 | 1429 | 3362 | 202 | 0 | 193 | 148 | 326 | 7 | 343.8
14:00 | 3783 | 907 | 2038 | 0 | 1429 | 3362 | 202 | 0 | 193 | 148 | 326 | 7 | 343.8
14:30 | 3735 | 906.5 | 2020 | 0 | 1434.5 | 3268 | 200.5 | 0 | 191.5 | 154 | 320.5 | 9.5 | 513.3125
15:00 | 3687 | 906 | 2002 | 0 | 1440 | 3174 | 199 | 0 | 190 | 160 | 315 | 12 | 682.825
15:30 | 3646 | 906.5 | 2021.5 | 0 | 1413 | 3179.5 | 199 | 0 | 193.5 | 157 | 241.5 | 14 | 695.7175
16:00 | 3605 | 907 | 2041 | 0 | 1386 | 3185 | 199 | 0 | 197 | 154 | 168 | 16 | 708.61
16:30 | 3599 | 906.5 | 2038 | 0 | 1428.5 | 3164.5 | 199 | 0 | 196 | 152 | 136 | 20 | 678.5275
17:00 | 3593 | 906 | 2035 | 0 | 1471 | 3144 | 199 | 0 | 195 | 150 | 104 | 24 | 648.445
17:30 | 3585.5 | 906.5 | 2006 | 0 | 1548.5 | 3176.5 | 199 | 0 | 237.5 | 149 | 62 | 15 | 455.0575
18:00 | 3578 | 907 | 1977 | 0 | 1626 | 3209 | 199 | 0 | 280 | 148 | 20 | 6 | 261.67
18:30 | 3644.5 | 907 | 2018 | 0 | 2143.5 | 3226.5 | 199.5 | 25 | 368.5 | 147 | 10 | 6.5 | 445.03
19:00 | 3711 | 907 | 2059 | 0 | 2661 | 3244 | 200 | 50 | 457 | 146 | 0 | 7 | 628.39
19:30 | 3726 | 779 | 2057 | 0 | 2841 | 3234 | 200 | 233 | 506 | 140 | 0 | 6 | 621.2275
20:00 | 3699 | 779 | 2073 | 0 | 2871 | 3261 | 201 | 233 | 514 | 144 | 0 | 12 | 614.065
20:30 | 3746 | 779 | 2093 | 0 | 2882.5 | 3275 | 201 | 233.5 | 552.5 | 142 | 0 | 7 | 624.0925
21:00 | 3793 | 779 | 2113 | 0 | 2894 | 3289 | 201 | 234 | 591 | 140 | 0 | 2 | 634.12
21:30 | 3807.5 | 779 | 2126.5 | 0 | 2792.5 | 3286.5 | 200.5 | 234.5 | 583.5 | 143 | 0 | 3.5 | 317.06
22:00 | 3822 | 779 | 2140 | 0 | 2691 | 3284 | 200 | 235 | 576 | 146 | 0 | 5 | 0
22:30 | 3881 | 788.5 | 2143 | 0 | 2443 | 3283.5 | 200 | 235.5 | 476.5 | 149 | 0 | 4 | 0
23:00 | 3940 | 798 | 2146 | 0 | 2195 | 3283 | 200 | 236 | 377 | 152 | 0 | 3 | 0
23:30 | 3956.5 | 798 | 2143 | 0 | 1906 | 3282.5 | 200 | 236 | 313 | 146 | 0 | 3 | 0 |  | Max Temp. in Dhaka |  | 32.6° C
24:00 | 3973 | 798 | 2140 | 0 | 1617 | 3282 | 200 | 236 | 249 | 140 | 0 | 3 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 297.214 MKWHr Energy Not Served 13.640 MKWHr Energy Requirement 310.854 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-08-19
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 125 | 125 | 125 | 125 | 125 | 125 | 80 | 80 | 127 | 127 | 127 | 127 | 127 | 126 | 124 | 124 | 124 | 124 |  | 125 | 125 | 126 | 126 | 125 | 125 | 125 | 2934851
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 40 | 40 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1716000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 123 | 120 | 121 | 120 | 123 | 119 | 118 | 122 | 120 | 118 | 118 | 118 | 120 |  | 118 | 117 | 120 | 117 | 118 | 118 | 120 | 2700000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 19 | 23 |  | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 296652
| Teknaf 20MW PP (Solartech) |  |  |  |  | 0 | 1 | 3 | 4 | 12 | 17 | 20 | 20 | 5 | 19 | 15 | 9 | 4 | 0 | [8 empty] | 131895
6 | Sikalbaha 225MW CCPP (Gas) | 225 | 226 | 227 | 226 | 227 | 225 | 226 | 223 | 223 | 223 | 223 | 220 | 215 | 221 | 219 | 219 | 222 | 221 |  | 222 | 226 | 223 | 224 | 220 | 224 | 223 | 5193807
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 16 | 16 | 16 | 16 | [9 empty] | 0 | 261697
12 | Hathazari 100 MW peaking PP | 33 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 24 | 24 | 41 | 41 | 41 | 41 | 41 | 66 |  | 48 | 49 | 49 | 49 | 50 | 51 | 34 | 926208
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 17 | 17 | 34 | 805415
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 24 | 13 | 16 | 16 | 16 | 0 | [5 empty] | 11 | 15 | 15 | 15 | 19 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 341648
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 61 | 92 | 89 | 96 | 160 | 131 | 97 | 101 | 100 | 134 | 133 | 121 | 160 | 136 | 156 | 155 | 129 | 102 |  | 192 | 175 | 135 | 175 | 125 | 125 | 115 | 3139000
17 | Siddhirganj 335 MW CCPP | 326 | 328 | 327 | 327 | 330 | 328 | 330 | 300 | 300 | 322 | 320 | 324 | 327 | 325 | 324 | 321 | 320 | 321 |  | 324 | 323 | 290 | 327 | 324 | 324 | 324 | 7748912
18 | Kodda 300 MW PP Unit-2 (Summit) | 62 | 64 | 65 | 65 | 65 | 65 | 65 | 64 | 65 | 57 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 |  | 105 | 145 | 148 | 148 | 148 | 145 | 80 | 1934509
19 | Ashuganj 195 MW PP (APSCL-United) | [25 empty] | 0 | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 130 | 130 | 130 | 150 | 150 | 150 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3625250
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4277700
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP
33 | Ashuganj 225 MW CCPP | 202 | 206 | 206 | 206 | 206 | 187 | 148 | 149 | 173 | 186 | 184 | 181 | 183 | 177 | 166 | 161 | 162 | 168 |  | 165 | 172 | 172 | 177 | 169 | 175 | 173 | 4358000
34 | Ashuganj 450 MW CCPP(South) | 240 | 240 | 240 | 240 | 240 | 240 | 265 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 5951000
| Ashuganj 450 MW CCPP(North) | 270 | 270 | 270 | 270 | 270 | 320 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 280 | 280 | 295 | 280 | 280 |  | 280 | 280 | 280 | 280 | 305 | 280 | 305 | 7154200
| Ashuganj 420 MW CCPP(East) | 230 | 230 | 230 | 230 | 230 | 230 | 300 | 230 | 230 | 235 | 240 | 240 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5829600
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 393 | 392 | 392 | 272 | 0 | [9 empty] | 0 |  |  | 0 |  | 14 | 35 | 53 | 60 | 70 | 244 | 274 | 2222080
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 10253800
41 | Haripur 360 MW CCPP(HPL) | 337 | 336 | 337 | 340 | 336 | 339 | 339 | 340 | 327 | 327 | 327 | 327 | 327 | 327 | 333 | 333 | 333 | 306 |  | 327 | 327 | 327 | 337 | 337 | 332 | 332 | 7966000
42 | RPCL 210MW CCPP | 106 | 106 | 108 | 107 | 105 | 108 | 107 | 104 | 65 | 64 | 63 | 59 | 59 | 58 | 58 | 59 | 60 | 61 |  | 66 | 68 | 66 | 78 | 80 | 81 | 81 | 1849920
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 2 | 6 | 40 | 51 | 52 | 51 | 19 | 18 | 44 | 7 | 8 | 2 | [8 empty] | 307880
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 |  | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 1022000
45 | Fenchugonj CCPP Phase-2 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 39 | 39 | 39 | 39 | 39 | 39 |  | 39 | 39 | 39 | 40 | 40 | 40 | 40 | 937200
46 | Shajibazar 330 MW CCPP | [21 empty] | 0
47 | Shahjibazar GTPP Unit- 8 & 9 | 50 | 50 | 51 | 51 | 51 | 51 | 59 | 58 | 60 | 60 | 60 | 60 | 55 | 60 | 60 | 59 | 60 | 60 |  | 58 | 62 | 56 | 53 | 55 | 51 | 56 | 1349568
48 | Shahjibazar 86 MW PP (Shahjibazar) | 78 | 78 | 78 | 78 | 75 | 75 | 75 | 75 | 72 | 72 | 75 | 75 | 75 | 75 | 75 | 81 | 84 | 84 |  | 84 | 84 | 84 | 84 | 81 | 81 | 81 | 1866240
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 179 | 180 | 180 | 180 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 |  | 181 | 181 | 181 | 181 | 181 | 180 | 180 | 4695330
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 253080
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 104960
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 47 | 47 | 47 | 44 | 44 | 44 | 44 | 44 |  | 44 | 47 | 47 | 47 | 47 | 47 | 47 | 1138800
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 19 | 16 | 16 | 16 | 16 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 534408
57 | Bibiana-II 341 MW CCPP (Summit) | 295 | 275 | 260 | 270 | 290 | 285 | 290 | 290 | 290 | 285 | 280 | 290 | 310 | 300 | 290 | 315 | 290 | 280 |  | 310 | 250 | 265 | 290 | 305 | 315 | 310 | 7173500
| Bibiyana South 400 MW | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 |  | 350 | 320 | 350 | 350 | 350 | 350 | 350 | 8329300
58 | Nababganj 55 MW PP (Southern power ) | [11 empty] | 5 | 17 | 17 | 17 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 444339
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 2 | 0 | 1 | 3 |  | 6 | 6 | 6 | 6 | 6 | 6 | 0 | 125040
60 | Barabkunda 22 MW PP (Regent) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 238944
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 422208
62 | Tangail 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 14 | 14 | 14 | 14 | 14 |  | 16 | 16 | 16 | 16 | 16 | 16 |  | 331488
63 | Impoprt (Tripura) | 152 | 148 | 146 | 142 | 142 | 132 | 118 | 124 | 130 | 146 | 144 | 156 | 148 | 144 | 160 | 154 | 150 | 148 |  | 146 | 140 | 144 | 140 | 146 | 152 | 140 | 3458880
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 39 | 39 | 39 | 42 | 4 | 12 | 7 | 5 | 6 | 11 | 14 | 11 | 8 | 12 | 20 | 24 |  | 28 | 28 | 21 | 24 | 36 | 40 | 40 | 629760
65 | Feni 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 13 | 13 | 13 | 12 | 12 | 14 | 14 | 15 | 15 | 14 | 13 |  | 13 | 16 | 16 | 16 | 16 | 16 | 16 | 356040
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 248940
67 | Jangalia 33 MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600700
68 | Cumilla 25 MW PP (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 14 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 413140
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456000
70 | Summit Madhabdi | 21 | 21 | 21 | 21 | 21 | 21 | 0 | 0 | 0 | 14 | 21 | 23 | 18 | 18 |  | 0 | 24 | 24 |  | 0 | 24 | 24 | 24 | 24 | 17 | 21 | 356760
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 738100
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 31 | 24 | 24 | 24 | 26 | 30 | 16 | 32 | 32 |  | 32 | 33 | 33 | 33 | 33 | 33 | 33 | 729400
73 | Ghorashal 108 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | [8 empty] | 0 | 213272
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 90 | 106 | 106 | 106 | 106 | 106 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 17 | 1048800
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 18 | 14 | 9 | 9 | 9 | 9 | 9 | 12 | 24 |  | 27 | 28 | 28 | 29 | 28 | 15 | 9 | 330120
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 108 | 108 | 108 | 108 | 108 | 90 | 17 | 1160640
77 | Siddhirganj 100 PP(Dutch Bangla) | 52 | 41 | 41 | 41 | 41 | 41 | [7 empty] | 2 | 8 | 9 | 9 | 9 |  | 14 | 80 | 65 | 88 | 88 | 88 | 88 | 688234
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 270720
79 | Kodda 150 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 22 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 98 | 98 | 98 | 98 | 98 | 32 | 32 | 847200
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [26 empty] | 0
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 22 | 35 | 52 | 52 | 35 | 35 | 35 | 35 |  | 88 | 88 | 88 | 88 | 88 | 88 | 17 | 914832
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 4 | 5 | 5 | 5 | 5 | 4 | 3 | 1 | 1 | [9 empty] | 35402
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 445397
| Karnaphuli Power Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 47 | 55 | 55 | 55 | 55 | 55 | 54 |  | 56 | 56 | 56 | 60 | 55 | 55 | 55 | 1320610
82 | Madanganj 102 PP(Summit) | 51 | 38 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 22 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 516409
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 22 | 22 | 22 | 22 | 22 | 15 | 20 | 22 | 22 | 23 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 23 | 554089
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 92 | 83 | 82 | 48 | 43 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 48 |  | 57 | 74 | 74 | 74 | 46 | 40 | 42 | 1218240
| Meghnaghat 104 MW PP (OPCL) | 36 | 36 | 35 | 49 | 52 | 35 | 35 | 38 | 52 | 55 | 48 | 50 | 52 | 53 | 53 | 52 | 52 | 52 |  | 66 | 72 | 70 | 71 | 71 | 71 | 54 | 1255680
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 25 | 592920
92 | Fenchuganj 44 MW (Energyprima) | 39 | 42 | 39 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 38 | 38 | 38 | 38 | 38 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 43 | 43 | 980136
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1131260
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 102 | 102 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 85 | 102 | 102 | 102 | 102 | 50 | 16 | 1220832
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 29 | 31 | 35 | 39 | 45 | 45 | 45 | 331680
96 | Chattogram 108 MW PP (ECPV) | [15 empty] | 10 | 13 | 12 |  | 11 | 12 | 12 | 12 | 12 |  | 0 | 88320
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  |  | 9 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 350200
100 | Manikganj 55 MW PP (Northern) | [9 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 |  | 0 | 438853
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 80 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 113 |  | 112 | 112 | 112 | 112 | 113 | 112 | 113 | 2581854
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | 0 | [8 empty] | 11500
103 | Kamalaghat 54 MW PP(Banco Energy) | [9 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 390240
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 67 | 67 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 96 | 96 | 115 | 115 | 115 | 68 | 68 | 68 |  | 160 | 161 | 163 | 163 | 163 | 68 | 68 | 2181600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 62 | 71 | 70 | 70 | 70 | 70 | 58 | 53 | 52 | 64 |  | 118 | 135 | 135 | 135 | 133 | 104 | 39 | 1600560
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 50 | 50 | 50 | 50 | 50 | 25 | 25 | 679680
116 | Chandpur 200 MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 28 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 81 |  | 103 | 103 | 103 | 103 | 103 | 103 | 63 | 1223040
117 | Ashuganj 150 MW PP (Midland) | 6 | 5 | 6 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 5 | 6 | 5 | 5 | 6 | 5 | 6 |  | 21 | 31 | 30 | 33 | 31 | 13 | 5 | 240872
118 | Bibiyana-III 400 MW CCPP | 368 | 368 | 368 | 368 | 366 | 412 | 368 | 405 | 368 | 367 | 363 | 367 | 405 | 367 | 343 | 335 | 319 | 319 |  | 366 | 367 | 366 | 366 | 406 | 372 | 369 | 8854000
| Jamalpur 115 MW PP (United) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 24 | 28 | 28 | 37 | 37 | 37 | 18 | 18 | 18 |  | 84 | 84 | 84 | 74 | 74 | 17 | 17 | 751200
| Anwara 300 MW PP (United) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 68 | 69 | 70 | 120 |  | 289 | 277 | 284 | 285 | 142 | 104 | 70 | 2411236
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 50 | 50 | 50 | 25 | 25 | 665280
| Anlima Energy Ltd. | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 658636
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 441360
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 7 | 20 | 26 | 29 | 37 | 35 | 3 | 22 | 27 | 18 | 5 | 2 | [8 empty] | 181655
| Chandpur 115(Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 18 | 17 | 29 | 68 | 73 | 72 | 72 | 72 | 72 | 72 | 80 |  | 102 | 114 | 114 | 100 | 109 | 114 | 62 | 1378560
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 432720
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 36 | 36 | 53 | 143 | 143 | 17 | 17 | 746036
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 15 | 9 | 11 | 16 | 9 | 14 | 10 | 9 | 16 | 19 | 14 | 11 | 7 | 11 | 12 | 16 | 24 | 6 |  | 7 | 6 | 12 | 2 | 5 | 3 | 3 | 262080
| Matarbari 2*600 MW (CPGCL) | [10 empty] | 72 | 181 | 175 | 185 | 0 | 0 | 0 | [8 empty] | 0 | 523636
120 | Eastern Zone Total | 6727 | 6692 | 6655 | 6460 | 6248 | 6257 | 6014 | 5961 | 6016 | 6308 | 6533 | 6692 | 6787 | 6778 | 6570 | 6409 | 6396 | 6463 | 0 | 7484 | 7616 | 7641 | 7865 | 7731 | 7208 | 6697 | 161049740
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 80 | 80 | 80 | 80 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 31 | 32 | 32 |  | 59 | 61 | 63 | 63 | 63 | 63 | 32 | 953280
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL) | [11 empty] | 50 | [7 empty] | 50 | 233 | 233 | 234 | 235 | 236 | 236 | 1171578
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [14 empty] | 5 | 9 | 14 | 30 |  | 36 | 45 | 34 | 26 | 21 | 21 | 11 | 188640
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 719040
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 2 | 20 | 51 | 61 | 106 | 47 | 64 | 50 | 84 | 77 | 63 | 35 | 5 | [8 empty] | 693281
131 | Rampal 1320 MW (BIFPCL) | 407 | 408 | 407 | 407 | 407 | 408 | 408 | 408 | 403 | 402 | 403 | 402 | 401 | 401 | 401 | 402 | 402 | 505 |  | 501 | 500 | 500 | 500 | 501 | 501 | 499 | 10378180
132 | United Payra Power Ltd. |  | 0 | 42 | 116 | 150 | 17 | 17 | 17 | 17 |  |  |  |  | 2 | 17 | 17 | 17 | 17 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 1368000
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 222 | 220 | 221 | 200 |  | 220 | 221 | 223 | 222 | 222 | 222 | 220 | 5253409
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 48 | 48 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 32 | 32 | 32 | 48 | 48 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1150176
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 130 | 128 | 124 | 124 | 130 | 123 | 130 | 80 | 124 | 132 | 124 | 130 | 126 | 126 | 130 | 128 | 128 | 130 |  | 130 | 124 | 130 | 124 | 130 | 132 | 130 | 2996000
140 | Bhola 33 MW PP (Venture) | 31 | 31 | 30 | 29 | 28 | 25 | 22 | 20 | 17 | 20 | 21 | 22 | 20 | 9 | 25 | 23 | 21 | 20 |  | 29 | 29 | 27 | 30 | 32 | 29 | 29 | 592283
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [15 empty] | 16 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 79875
143 | Gopalganj 100 MW Peaking PP | 46 | 46 | 42 | 42 | 42 | 42 | 38 | 19 | 18 | 18 | 16 | 16 | 25 | 17 | 17 | 16 | 15 | 25 |  | 50 | 55 | 52 | 52 | 43 | 35 | 37 | 753664
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 53 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 15 | 656928
146 | Bheramara HVDC | 859 | 858 | 859 | 908 | 907 | 909 | 908 | 908 | 907 | 909 | 908 | 909 | 907 | 907 | 906 | 907 | 906 | 907 |  | 907 | 779 | 779 | 779 | 779 | 798 | 798 | 21178181
147 | Bheramara 410 MW CCPP | 80 | 80 | 80 | 90 | 90 | 105 | 105 | 105 | 110 | 115 | 110 | 95 | 70 | 55 | 50 | [10 empty] | 0 | 1438560
148 | Payra 1320 MW | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1232 | 1210 | 1210 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1200 |  | 1200 | 1200 | 1220 | 1244 | 1244 | 1244 | 1244 | 31408200
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4632300
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [16 empty] | 6 | 35 |  | 35 | 35 | 35 | 28 | 28 | 28 | 0 | 209184
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 3 | 5 | 4 | 5 | 5 | 5 | 4 | 3 | 0 | 1 | [8 empty] | 34020
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 149 | 149 | 151 | 152 | 153 | 155 | 156 | 157 | 153 | 153 | 149 | 148 | 144 | 142 | 141 | 140 | 140 | 141 |  | 143 | 147 | 148 | 151 | 159 | 161 | 162 | 3850318
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 414 | 400 | 414 | 414 | 414 | 414 | 414 | 300 | 414 | 350 | 414 | 352 | 371 | 332 | 340 | 345 | 353 |  | 352 | 406 | 414 | 414 | 414 | 414 | 414 | 9368945
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 5 |  | 13 | 14 | 15 | 17 | 15 | 15 | 15 | 78692
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 175320
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP | 22 | 0 | [17 empty] | 26 | 35 | 39 | 39 | 39 | 39 | 24 | 202757
168 | Santahar 50 MW Peaking PP | [20 empty] | 24 | 24 | 24 | 24 | 24 | 0 | 115266
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 205517
170 | Chapainawabganj 100 MW Peaking PP | [11 empty] | 11 | 47 | 47 | 47 | 47 | 47 | 47 |  | 92 | 92 | 92 | 92 | 92 | 92 | 56 | 813080
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 40 | 50 | 50 | 35 | 35 | 952224
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 |  | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 980448
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 29 | 33 | 34 | 34 | 34 | 55 | 55 |  | 56 | 56 | 56 | 56 | 56 | 34 | 34 | 960384
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 5 | 7 | 7 | 7 | 7 | 4 | 5 | 2 | 2 | 1 | [8 empty] | 51053
178 | Energypac Power Venture Thakurgaon Ltd. | [15 empty] | 35 | 36 | 36 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 539712
| Intraco Solar 30 MW |  |  |  |  | 0 | 1 | 7 | 13 | 18 | 32 | 35 | 11 | 36 | 11 | 23 | 19 | 10 | 2 |  | 0 | [6 empty] | 241641
| Adani Power Jharkhanda Ltd | 1309 | 1311 | 1308 | 1307 | 1314 | 1067 | 961 | 1000 | 1143 | 1175 | 1307 | 1256 | 1322 | 1304 | 1309 | 1319 | 1318 | 1324 |  | 1363 | 1354 | 1361 | 1365 | 1359 | 1358 | 1359 | 30500727
178 | Teesta Solar Limited |  |  |  |  | 0 | 5 | 21 | 85 | 164 | 181 | 150 | 154 | 194 | 124 | 116 | 45 | 39 | 7 | [8 empty] | 1273200