## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-09-06 | Wednesday
|  | Date (day): | 2023-09-06 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13126.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15445 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-09-05 | 2023-09-06 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 110 | 180 | 180
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 170 | 170 | 0 | 0
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 40 | 40 | 68 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 403 | 407 | 412 | 412
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 320 | 326 | 330 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 48 | 48 | 50 | 50 | 50 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 10 | 330
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 95 | 80 | 95 | 95 |  | 7 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 24 | 15 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 34 | 56 | 55 | 55 | 20 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 18 | 19 |  |  | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 116 | 184 | 150 | 180 | 30 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 33 | 33 | 32 | 40 |  | 60 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 308 | 317 | 330 | 330
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 50 | 42 | 32 | 64 | 38 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 35 | 17 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 82 | 147 | 48 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 19 | 37 | 37 | 37 |  | 43 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 26 | 29 | 30 | 30 | 3 |  | Gas shortage
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 25 | 8 | 25 | 27 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 135 | 97 | 80 | 130 | 170 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
33 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
34 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 105 | 105 | 17 | 149
35 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 88 | 70 | 100 |  | 5 | Engine problem
36 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 35 | 53 | 34 | 53 | 51 |  | Fuel shortage
37 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 108 | 72 | 54 | 108 | 54 |  | Fuel shortage
38 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 34 | 0 | 35 | 0
39 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 15 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 6063 | 5722 | 2918 | 3085 | 2749 | 3547 | 814 | 875
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 115 | 115 | 115 |  | 65
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
41 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 17 | 8 | 17 | 8 |  | Fuel shortage
42 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 16 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 45 | 50 | 50
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 205 | 205 | 203 | 203
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 107 | 224 | 220 | 220
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 51 | 51 | 51 | 54 |  | Fuel shortage
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 37 | 72 | 40 | 70 | 28 |  | Fuel shortage
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 17 | 17 | 17 | 85 |  | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 11 | 13 | 14 | 14 | 8 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 33 | 25 | 35
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 12 | 0 | 12 | 96 |  | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 105 | 264 | 70 | 265
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 54 | 17 | 54
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 55 | 63 | 55 | 55 | 55 |  | Fuel shortage
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 34 | 51 | 34 | 51 | 65 |  | Fuel shortage
60 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 53 | 159 | 17 | 150 | 13
| SS Power I |  | Coal | SS Power | 0 | 0 | 0 | 626 | 0 | 0 | 0 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 0 | 3 | 10 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 2605 | 2545 | 1538 | 1473 | 1046 | 1464 | 637 | 395
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 194 | 203 | 200 | 200 | 21 |  | Gas shortage
62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 0 | 0 | 0 |  | 360 | Under maint
63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 240 | 305 | 280 | 300 |  |  | FGMO
64 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 240 | 401 | 400 | 400
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 25 | 25 | 25 | 20 |  | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 16 | 16 | 80 | 115 |  | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
69 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 5 | 35 | 6 | 30 | 120 |  | Fuel shortage
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 |  |  | Under Maint.
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
72 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 72 | 48 | 17 | 34 | 166 |  | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 17 | 16 | 16 |  | 6 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 110 | 120 | 149 | 165
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 32 | 33 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 32 | 34 | 43 | 43 |  | 9 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 11 | 11 | 11 |  | 14 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 105 | 17 | 106 |  | 8 | Engine problem
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 59 | 57 | 26 | 65 | 48 |  | Fuel shortage
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 0 | 0 |  |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2896 | 1376 | 1489 | 1318 | 1587 | 490 | 597
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 25 | 75 | 35 | 85 | 117 |  | Gas shortage
83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 16 | 16 | 16 |  | 6 | Engine problem
84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 114 | 160 | 115 | 145 | 55 |  | Fuel shortage
87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 36 | 84 | 37 | 95 | 20 |  | Fuel shortage
88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 50 | 0 | 50 | 0
89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 249 | 341 | 260.6 | 347 | 117 | 6
90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 24 | 0 | 0 | 0 |  | 70 | Machine problem.
91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 30 | 30 | 30 |  | 60 | Machine problem
92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 112 | 112 |  | 51 | ST Under maint.
93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 45 | 50 | 50 | 50
95 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 36 | 41 | 40 | 40 |  | 10 | Engine problem
96 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 5 | 11 | 11
97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 49 | 56 | 60 | 60
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 86 | 86 | 86
99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 181 | 178 | 180 | 181 |  | 50 | Machine problem
101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 16 | 17 | 17 | 17
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 16 | 16 | 16 | 9 |  | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 270 | 290 | 300 | 300 |  |  | FGMO
104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 366 | 368 | 400 | 400 |  |  | FGMO
105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 252 | 256 | 255 | 255 |  | 128 | ST Under maint.
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1457 | 1515 | 1567 | 1568 | 9 | 799
107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 927 | 804 | 943 | 943
108 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 61 | 80 | 66 | 98 |  | 17 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 9 | 25 | 25 | 40 |  | 14 | Engine problem
110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 16 | 40 | 50 | 59 |  | Fuel shortage
112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
113 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 32 | 40 | 40 | 40
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
114 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 17 | 17 | 17 | 88 |  | Fuel shortage
115 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 48 | 0 | 100 | 0
117 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 220 | 220 | 361 | 355 | 330 | 330
118 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 521 | 571 | 520 | 570 | 47
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3125 | 3121 | 1976 | 1908 | 2081 | 2088 | 955 | 31
119 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 48 | 96 | 110
120 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 22 | 34 | 23 | 33 |  | 7 | Engine problem
121 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 124 | 126 | 132 | 132 |  | 62 | ST under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
122 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244
123 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
124 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 35 | 150 | 35 | 150
125 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 | 307 |  | Coal shortage
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1661 | 1822 | 1750 | 1889 | 307 | 69
126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 35 | 0 | 35 | 17 |  | Fuel shortage
128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 11 | 0 | 21 |  | 50 | Engine problem
129 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 28 | 28 | 28 | 28
130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 8 | 42 | 34 | 42 | 8 |  | Fuel shortage
131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 39 | 30 | 40 | 10 |  | Fuel shortage
132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 148 | 158 | 160 | 160 | 50 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 125 | 134 | 180 | 180 | 40 |  | Gas shortage
135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 253 | 312 | 414 | 414
136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 24 | 0 | 24 | 26 |  | Fuel shortage
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 8 | 52
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 46 | 91 | 50 | 91 | 13 |  | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 68 | 35 | 70 | 43 |  | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 75 | 35 | 75 | 38 |  | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1361 | 1462 | 950 | 1400
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 2060 | 2539 | 1938 | 2640 | 836 | 53
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 180 | 180 | 180 | 180 |  | 94 | Machine problem
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 39 | 62 | 34 | 60 | 53 |  | Fuel shortage
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 36 | 75 | 35 | 75 | 40 |  | Fuel shortage
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 178 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 476 | 317 | 417 | 315 | 218 | 179
| Total |  |  |  |  | 24911 | 24171 | 13711 | 14489 | 13126.6 | 15445 | 4383 | 3004
A. |  | 2023-09-05 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 14489 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 12081 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 15350 | MW
3 | Day peak Generation : |  |  | 13711 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14499.86 | MW
4 | Evening peak Generation : |  |  | 14489 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 822 | MW
5 | Total Energy Generation : |  | 314.2412 | MKWHr | By Solar | 2.9336 | MKWHr
| By Gas : | 139.0437 | MKWHr |  | By Oil: | 55.1248 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 87.906 | MKWHr |  | By Hydro: | 4.8099 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.05136 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4383 | MW | Dhaka | 5116.56 | 5074.56 |  | 42 |  | 18:00 |  | 526.205
|  |  | For Plants S/D or M/C prob = |  |  | 3004 | MW | Chittagong | 1315.5 | 1130.5 |  | 185 |  | 19:00 |  | 811.75
|  |  | Total = |  |  | 7387 | MW | Khulna | 1787 | 1675 |  | 112 |  | 19:30 |  | 883.375
7 | Total Gas Supplied : |  |  | 1114.73 | MMCFD |  |  | Rajshahi | 1647 | 1617 |  | 30 |  | 20:00 |  | 802.2
8 | Fuel Cost : | i) Gas : | Taka | 153331059.68 | ii) Oil : | Taka | 590194032.02 | Comilla | 1298 | 1179 |  | 119 |  | 21:00 |  | 822.255
|  | iii) Coal : | Taka | 698591292.1 | Total | Taka | 1442116383.8 | Mymensingh | 1229 | 1084 |  | 145 |  | 22:00 |  | 921.575
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 619 | 554 |  | 65 |  | 23:00 |  | 1109.71
| ii) During Peak Demand : |  |  | 920 | MW (E to W) at | 21:00 | hrs | Barisal | 486.8 | 486.8 |  | 0 |  | 24:00 |  | 1423.905
| iii) Maximum : |  |  | 920 | MW at | 21:00 | hrs | Rangpur | 1001 | 877 |  | 124
10 | Maximum Temperature in Dhaka was |  |  |  | 37.3°C |  |  | Total | 14499.86 | 13677.86 |  | 822
B. |  | 2023-09-06 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 37.3°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 14500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15445 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 12500 | MW
4 | Reserve(Generation end) |  |  |  | 945 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 314.4798 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11652 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.6407 | MKWHr. | ii) HVDC Flow at Peak Time |  | 804 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.7312 | MKWHr. | iii) Maximum HVDC Flow : |  | 927 | MW at | 5:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 106.07 |  | (b) Today: | 106.11 |  | (c) Rule Curve: |  | 100.15
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-09-05 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 403 | 284 |  | 0 | 450 | 0 | 30 | 95 | 15 | 322 | 0 | 144 | 9 | 24 | 16 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 18 | 33 | 31 | 8 | 0 | 129 | 75 | 110 | 0 | 8 | 150 | 0 | 0 | 0 |  | 6 | 32 | 17 | 25 | 0 | 6 | 13 | 38 | 0 | 0 | 0 | 270 | 240 | 199 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 16 | 15 | 11 | 32 | 11 | 122 | 68 | 0 | 16 | 0 | 43 | 0 | 50 | 42 | 112 | 0 | 55 | 81 | 0 | 180 | 17 | 0 | 10 | 310 | 16 | 5 | 0 | 35 | 0 | 0 | 67 | 0 | 17 | 0 | 25 | 17 | 6 | 367 | 19 | 17 | 51 | 0 | 68 | 17 | 55 | 104 | 9 | 25 | 190 | 17 | 0 | 17 | 19 | 0 | 17 | 0 | 0 | 17 | 240 | 17 | 0 | 215 | 6 | 0 | 0 |  | 923 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 17 | 40 | 128 | 33 | 16 | 0 | 0 | 0 | 0 | 0 | 84 | 28 | 34 | 23 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 128 | 0 | 265 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 35 | 0 | 0 | 0 | 356 | 0 | 518 | 0 | 0 | 1464 | 0 | 0 |  | 6491 | 6079 | 12570 | 3933 | 923 | 1946 | 0 | 1243 | 3621 | 204 | 356 | 216 | 122 | 0 | 6 | 1365.65 | 106.03
2:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 382 | 272 |  | 0 | 450 | 0 | 32 | 95 | 15 | 324 | 0 | 101 | 9 | 24 | 16 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 18 | 33 | 31 | 8 | 0 | 129 | 75 | 114 | 0 | 8 | 150 | 0 | 0 | 0 |  | 6 | 32 | 17 | 25 | 0 | 6 | 13 | 39 | 0 | 0 | 0 | 270 | 240 | 200 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 16 | 15 | 11 | 25 | 11 | 118 | 69 | 0 | 16 | 0 | 43 | 0 | 50 | 42 | 112 | 0 | 55 | 81 | 0 | 180 | 17 | 0 | 10 | 290 | 16 | 5 | 0 | 30 | 0 | 0 | 67 | 0 | 17 | 0 | 25 | 17 | 6 | 367 | 19 | 17 | 51 | 0 | 70 | 17 | 55 | 104 | 9 | 25 | 170 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 0 | 17 | 240 | 17 | 0 | 260 | 2 | 0 | 0 |  | 924 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 10 | 17 | 40 | 130 | 32 | 16 | 0 | 0 | 0 | 0 | 0 | 84 | 28 | 34 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 275 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 35 | 0 | 0 | 0 | 356 | 0 | 519 | 0 | 0 | 1471 | 0 | 0 |  | 6411 | 6083 | 12494 | 3857 | 924 | 1924 | 0 | 1242 | 3674 | 204 | 356 | 193 | 118 | 0 | 2 | 1247.23 | 106.04
3:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 402 | 332 |  | 0 | 450 | 0 | 33 | 95 | 15 | 322 | 0 | 176 | 9 | 24 | 16 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 18 | 33 | 32 | 8 | 0 | 129 | 75 | 115 | 0 | 8 | 150 | 0 | 0 | 0 |  | 6 | 32 | 17 | 25 | 0 | 6 | 13 | 39 | 0 | 0 | 0 | 270 | 240 | 200 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 16 | 15 | 11 | 25 | 11 | 122 | 68 | 0 | 16 | 0 | 43 | 0 | 50 | 42 | 112 | 0 | 56 | 81 | 0 | 180 | 17 | 0 | 10 | 300 | 16 | 5 | 0 | 30 | 0 | 0 | 67 | 0 | 17 | 0 | 25 | 17 | 5 | 370 | 19 | 17 | 51 | 0 | 70 | 17 | 44 | 104 | 9 | 25 | 30 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 0 | 17 | 240 | 17 | 0 | 306 | 7 | 0 | 0 |  | 925 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 10 | 17 | 40 | 130 | 32 | 16 | 0 | 0 | 0 | 0 | 0 | 84 | 28 | 34 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 286 | 17 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1244 | 220 | 0 | 35 | 0 | 0 | 0 | 352 | 0 | 521 | 0 | 0 | 1454 | 0 | 0 |  | 6484 | 6009 | 12493 | 3818 | 925 | 2005 | 0 | 1162 | 3705 | 204 | 352 | 193 | 122 | 0 | 7 | 1152.685 | 106.05
4:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 408 | 327 |  | 0 | 450 | 0 | 33 | 95 | 15 | 316 | 0 | 175 | 9 | 24 | 16 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 18 | 33 | 32 | 8 | 0 | 129 | 75 | 112 | 0 | 8 | 150 | 0 | 0 | 0 |  | 6 | 32 | 17 | 25 | 0 | 6 | 13 | 39 | 0 | 0 | 0 | 270 | 240 | 202 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 16 | 15 | 11 | 25 | 11 | 124 | 68 | 0 | 16 | 0 | 43 | 0 | 50 | 42 | 112 | 0 | 56 | 81 | 0 | 180 | 17 | 0 | 10 | 290 | 16 | 5 | 0 | 30 | 0 | 0 | 66 | 0 | 17 | 0 | 25 | 17 | 6 | 367 | 19 | 17 | 51 | 0 | 70 | 0 | 54 | 104 | 9 | 25 | 30 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 0 | 17 | 240 | 17 | 0 | 300 | 1 | 0 | 0 |  | 925 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 10 | 17 | 40 | 110 | 31 | 16 | 0 | 0 | 0 | 0 | 0 | 48 | 28 | 34 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 296 | 17 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1244 | 220 | 0 | 35 | 0 | 0 | 0 | 355 | 0 | 521 | 0 | 0 | 1446 | 0 | 0 |  | 6434 | 5958 | 12392 | 3794 | 925 | 1999 | 0 | 1142 | 3691 | 204 | 355 | 157 | 124 | 0 | 1 | 1058.14 | 106.06
5:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 411 | 332 |  | 0 | 450 | 0 | 32 | 95 | 15 | 324 | 0 | 175 | 9 | 24 | 16 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 18 | 33 | 32 | 8 | 0 | 128 | 75 | 115 | 0 | 8 | 128 | 0 | 0 | 0 |  | 6 | 32 | 17 | 25 | 0 | 6 | 13 | 40 | 0 | 0 | 0 | 270 | 240 | 203 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 16 | 15 | 11 | 25 | 11 | 126 | 68 | 0 | 16 | 0 | 43 | 0 | 47 | 42 | 112 | 0 | 56 | 78 | 0 | 180 | 17 | 0 | 10 | 270 | 16 | 5 | 0 | 32 | 0 | 0 | 66 | 0 | 17 | 0 | 12 | 17 | 5 | 367 | 19 | 17 | 34 | 0 | 70 | 0 | 55 | 104 | 9 | 25 | 100 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 0 | 17 | 250 | 17 | 0 | 300 | 0 | 0 | 0 |  | 927 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 10 | 17 | 40 | 130 | 31 | 16 | 0 | 0 | 0 | 0 | 0 | 48 | 28 | 34 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 308 | 17 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1244 | 220 | 0 | 35 | 0 | 0 | 0 | 356 | 0 | 521 | 0 | 0 | 1412 | 0 | 0 |  | 6460 | 5964 | 12424 | 3892 | 927 | 1991 | 0 | 1115 | 3657 | 203 | 356 | 157 | 126 | 0 | 0 | 836.58 | 106.07
6:00 | 0 | 0 | 107 | 170 | 0 | 0 | 0 | 385 | 272 |  | 0 | 450 | 0 | 33 | 95 | 15 | 290 | 0 | 121 | 9 | 24 | 16 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 18 | 33 | 32 | 8 | 0 | 128 | 75 | 117 | 0 | 8 | 34 | 0 | 0 | 0 |  | 6 | 32 | 17 | 25 | 0 | 6 | 13 | 40 | 0 | 0 | 0 | 295 | 310 | 177 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 16 | 15 | 11 | 25 | 0 | 114 | 68 | 0 | 16 | 0 | 43 | 0 | 47 | 42 | 112 | 0 | 56 | 78 | 0 | 180 | 17 | 0 | 10 | 275 | 16 | 5 | 0 | 32 | 0 | 0 | 67 | 0 | 17 | 1 | 12 | 17 | 5 | 367 | 19 | 17 | 34 | 0 | 70 | 3 | 55 | 104 | 9 | 25 | 0 | 17 | 1 | 17 | 17 | 0 | 17 | 0 | 0 | 17 | 240 | 17 | 0 | 305 | 0 | 0 | 0 |  | 926 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 10 | 17 | 40 | 130 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 48 | 28 | 34 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 314 | 17 | 0 | 3 | 0 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 35 | 0 | 0 | 0 | 353 | 0 | 520 | 0 | 0 | 1363 | 3 | 0 |  | 6139 | 5943 | 12082 | 3633 | 926 | 1936 | 0 | 1153 | 3602 | 203 | 353 | 157 | 114 | 5 | 0 | 494.69 | 106.07
7:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 386 | 332 |  | 0 | 400 | 0 | 32 | 95 | 15 | 290 | 0 | 121 | 20 | 24 | 16 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 18 | 33 | 30 | 8 | 0 | 127 | 75 | 116 | 0 | 8 | 30 | 0 | 0 | 0 |  | 6 | 32 | 17 | 25 | 0 | 6 | 13 | 36 | 0 | 0 | 0 | 270 | 240 | 196 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 16 | 15 | 11 | 25 | 11 | 110 | 32 | 0 | 17 | 0 | 43 | 0 | 47 | 42 | 112 | 0 | 59 | 78 | 0 | 180 | 17 | 0 | 10 | 290 | 16 | 11 | 0 | 32 | 0 | 0 | 67 | 0 | 17 | 4 | 23 | 17 | 5 | 367 | 19 | 17 | 34 | 1 | 70 | 17 | 55 | 104 | 9 | 25 | 0 | 17 | 11 | 17 | 17 | 0 | 17 | 7 | 0 | 17 | 240 | 17 | 0 | 310 | 0 | 0 | 0 |  | 889 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 10 | 17 | 40 | 130 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 48 | 28 | 34 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 303 | 17 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 1244 | 220 | 0 | 35 | 0 | 1 | 0 | 364 | 0 | 521 | 6 | 0 | 1358 | 33 | 0 |  | 6124 | 5957 | 12081 | 3540 | 889 | 1928 | 0 | 1224 | 3603 | 202 | 364 | 157 | 110 | 64 | 0 | 400.145 | 106.09
8:00 | 0 | 0 | 110 | 180 | 0 | 0 | 0 | 411 | 332 |  | 0 | 370 | 0 | 32 | 95 | 15 | 290 | 0 | 101 | 32 | 24 | 16 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 19 | 18 | 33 | 30 | 8 | 0 | 128 | 75 | 117 | 0 | 8 | 34 | 0 | 0 | 0 |  | 6 | 32 | 17 | 25 | 0 | 6 | 13 | 9 | 0 | 0 | 0 | 270 | 240 | 194 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 16 | 15 | 5 | 29 | 0 | 116 | 28 | 0 | 16 | 1 | 43 | 0 | 47 | 39 | 112 | 0 | 58 | 78 | 0 | 181 | 17 | 0 | 0 | 270 | 8 | 11 | 0 | 30 | 0 | 0 | 67 | 0 | 19 | 6 | 25 | 17 | 6 | 368 | 19 | 17 | 34 | 2 | 70 | 17 | 55 | 17 | 9 | 25 | 160 | 17 | 26 | 17 | 17 | 0 | 17 | 16 | 0 | 17 | 240 | 17 | 0 | 311 | 0 | 0 | 0 |  | 889 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 10 | 13 | 40 | 130 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 47 | 28 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 299 | 17 | 0 | 35 | 0 | 34 | 0 | 3 | 35 | 1244 | 220 | 0 | 35 | 2 | 7 | 0 | 364 | 0 | 520 | 15 | 0 | 1366 | 82 | 0 |  | 6137 | 5989 | 12126 | 3686 | 889 | 1846 | 0 | 1099 | 3611 | 203 | 364 | 152 | 116 | 160 | 0 | 452.67 | 106.08
9:00 | 0 | 0 | 110 | 180 | 0 | 0 | 0 | 405 | 327 |  | 0 | 450 | 0 | 33 | 95 | 15 | 314 | 0 | 128 | 33 | 24 | 16 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 19 | 18 | 33 | 28 | 8 | 0 | 128 | 75 | 116 | 0 | 8 | 32 | 0 | 0 | 0 |  | 6 | 32 | 17 | 25 | 0 | 6 | 13 | 3 | 0 | 0 | 0 | 270 | 240 | 197 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 34 | 15 | 5 | 25 | 11 | 100 | 28 | 0 | 16 | 2 | 40 | 0 | 47 | 42 | 80 | 0 | 54 | 78 | 0 | 183 | 17 | 0 | 10 | 290 | 8 | 11 | 0 | 32 | 0 | 0 | 67 | 0 | 94 | 9 | 25 | 17 | 5 | 378 | 19 | 17 | 34 | 2 | 70 | 17 | 55 | 17 | 9 | 25 | 250 | 17 | 39 | 17 | 17 | 0 | 17 | 25 | 0 | 17 | 240 | 17 | 0 | 326 | 0 | 0 | 0 |  | 889 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 10 | 12 | 40 | 130 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 47 | 28 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 129 | 0 | 275 | 17 | 0 | 35 | 0 | 34 | 0 | 5 | 35 | 1230 | 220 | 0 | 35 | 4 | 15 | 0 | 362 | 0 | 520 | 24 | 0 | 1362 | 123 | 0 |  | 6464 | 6006 | 12470 | 3822 | 889 | 1891 | 0 | 1186 | 3618 | 203 | 362 | 151 | 100 | 248 | 0 | 410.65 | 106.08
10:00 | 0 | 0 | 110 | 180 | 0 | 0 | 0 | 405 | 327 |  | 0 | 450 | 0 | 38 | 95 | 15 | 274 | 0 | 75 | 33 | 25 | 48 | 32 | 0 | 0 | 0 | 17 | 17 | 0 | 16 | 19 | 16 | 33 | 26 | 8 | 0 | 129 | 75 | 116 | 0 | 8 | 51 | 0 | 0 | 0 |  | 6 | 38 | 17 | 25 | 0 | 6 | 11 | 2 | 0 | 0 | 0 | 270 | 240 | 197 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 34 | 15 | 5 | 27 | 0 | 96 | 26 | 0 | 16 | 2 | 43 | 0 | 45 | 42 | 80 | 0 | 40 | 78 | 0 | 181 | 17 | 0 | 10 | 275 | 8 | 11 | 0 | 52 | 0 | 0 | 66 | 0 | 105 | 19 | 25 | 17 | 5 | 318 | 19 | 17 | 37 | 4 | 70 | 17 | 55 | 17 | 17 | 25 | 252 | 17 | 47 | 17 | 20 | 0 | 17 | 29 | 0 | 17 | 240 | 21 | 0 | 516 | 0 | 0 | 0 |  | 927 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 10 | 12 | 40 | 80 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 47 | 28 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 128 | 0 | 276 | 17 | 0 | 35 | 0 | 35 | 0 | 6 | 35 | 1200 | 180 | 0 | 35 | 5 | 38 | 18 | 362 | 0 | 523 | 30 | 0 | 1359 | 158 | 0 |  | 6622 | 6018 | 12640 | 3604 | 927 | 1825 | 0 | 1313 | 3778 | 204 | 362 | 193 | 96 | 338 | 0 | 343.8 | 106.08
11:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 404 | 327 |  | 0 | 450 | 0 | 46 | 95 | 14 | 270 | 0 | 71 | 33 | 42 | 64 | 33 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 19 | 16 | 33 | 26 | 8 | 0 | 129 | 75 | 115 | 0 | 8 | 69 | 0 | 0 | 0 |  | 6 | 38 | 17 | 25 | 0 | 6 | 11 | 2 | 0 | 0 | 0 | 270 | 240 | 195 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 34 | 15 | 11 | 32 | 0 | 98 | 26 | 0 | 17 | 2 | 43 | 0 | 45 | 39 | 80 | 0 | 54 | 77 | 0 | 181 | 17 | 0 | 10 | 270 | 8 | 11 | 0 | 140 | 0 | 0 | 113 | 0 | 105 | 11 | 25 | 32 | 6 | 292 | 37 | 50 | 51 | 2 | 103 | 17 | 55 | 17 | 27 | 25 | 254 | 35 | 51 | 108 | 34 | 0 | 17 | 33 | 0 | 17 | 240 | 53 | 0 | 616 | 0 | 0 | 0 |  | 926 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 13 | 12 | 32 | 76 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 46 | 28 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 126 | 0 | 265 | 17 | 0 | 35 | 0 | 35 | 0 | 6 | 35 | 1200 | 180 | 0 | 35 | 5 | 66 | 35 | 363 | 0 | 521 | 35 | 0 | 1364 | 176 | 0 |  | 7219 | 6067 | 13286 | 3595 | 926 | 1808 | 0 | 1781 | 3881 | 204 | 363 | 243 | 98 | 387 | 0 | 252.12 | 106.09
12:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 403 | 320 |  | 0 | 450 | 0 | 48 | 95 | 24 | 308 | 0 | 116 | 33 | 50 | 82 | 34 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 19 | 0 | 33 | 26 | 8 | 0 | 130 | 75 | 110 | 0 | 8 | 107 | 0 | 0 | 0 |  | 6 | 37 | 17 | 25 | 0 | 6 | 11 | 3 | 0 | 0 | 0 | 270 | 240 | 194 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 32 | 15 | 11 | 32 | 11 | 110 | 25 | 0 | 16 | 2 | 24 | 0 | 45 | 36 | 112 | 0 | 49 | 77 | 0 | 181 | 16 | 0 | 10 | 270 | 8 | 11 | 0 | 135 | 0 | 0 | 114 | 0 | 105 | 16 | 25 | 72 | 5 | 366 | 36 | 70 | 51 | 2 | 105 | 17 | 55 | 17 | 59 | 25 | 252 | 35 | 50 | 108 | 34 | 0 | 17 | 34 | 0 | 15 | 240 | 53 | 0 | 626 | 0 | 0 | 0 |  | 927 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 9 | 0 | 32 | 124 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 46 | 28 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 253 | 17 | 0 | 35 | 0 | 39 | 0 | 7 | 35 | 1244 | 220 | 0 | 35 | 5 | 48 | 36 | 361 | 0 | 521 | 36 | 0 | 1361 | 178 | 0 |  | 7538 | 6173 | 13711 | 3779 | 927 | 1869 | 0 | 1906 | 3932 | 205 | 361 | 244 | 110 | 378 | 0 | 180.495 | 106.09
13:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 401 | 322 |  | 0 | 450 | 0 | 48 | 85 | 55 | 306 | 0 | 149 | 33 | 50 | 82 | 34 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 19 | 10 | 33 | 26 | 8 | 0 | 130 | 75 | 115 | 0 | 8 | 218 | 0 | 0 | 0 |  | 6 | 36 | 17 | 0 | 0 | 6 | 11 | 9 | 0 | 0 | 0 | 270 | 240 | 187 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 32 | 15 | 11 | 32 | 11 | 124 | 25 | 0 | 16 | 2 | 35 | 0 | 47 | 36 | 80 | 0 | 49 | 75 | 0 | 181 | 16 | 0 | 9 | 275 | 8 | 11 | 0 | 143 | 0 | 0 | 114 | 0 | 103 | 19 | 25 | 105 | 5 | 343 | 36 | 70 | 51 | 3 | 107 | 17 | 55 | 17 | 66 | 25 | 205 | 35 | 50 | 108 | 34 | 0 | 17 | 32 | 0 | 17 | 240 | 53 | 0 | 620 | 0 | 0 | 0 |  | 927 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 9 | 0 | 40 | 124 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 46 | 28 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 248 | 17 | 0 | 35 | 0 | 34 | 0 | 5 | 35 | 1244 | 220 | 0 | 35 | 5 | 86 | 36 | 349 | 0 | 520 | 35 | 0 | 1359 | 174 | 0 |  | 7678 | 6188 | 13866 | 3884 | 927 | 1845 | 0 | 1955 | 3923 | 205 | 349 | 243 | 124 | 411 | 0 | 223.47 | 106.09
14:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 400 | 317 |  | 0 | 450 | 0 | 55 | 67 | 15 | 303 | 0 | 149 | 33 | 50 | 82 | 33 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 19 | 0 | 33 | 26 | 8 | 0 | 130 | 75 | 115 | 0 | 8 | 217 | 0 | 0 | 0 |  | 6 | 36 | 17 | 25 | 0 | 6 | 11 | 6 | 0 | 0 | 0 | 270 | 240 | 180 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 16 | 15 | 11 | 32 | 11 | 124 | 25 | 0 | 16 | 2 | 34 | 0 | 47 | 34 | 80 | 0 | 49 | 74 | 0 | 177 | 17 | 0 | 10 | 290 | 8 | 11 | 0 | 60 | 0 | 0 | 114 | 0 | 37 | 18 | 25 | 78 | 5 | 344 | 36 | 82 | 51 | 2 | 106 | 17 | 55 | 17 | 61 | 25 | 205 | 42 | 46 | 54 | 34 | 0 | 17 | 28 | 0 | 17 | 240 | 53 | 0 | 617 | 3 | 0 | 0 |  | 926 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 9 | 0 | 32 | 124 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 46 | 28 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 229 | 17 | 0 | 35 | 0 | 34 | 0 | 7 | 35 | 1244 | 220 | 0 | 35 | 5 | 83 | 36 | 350 | 0 | 519 | 32 | 0 | 1365 | 159 | 0 |  | 7388 | 6148 | 13536 | 3858 | 926 | 1832 | 0 | 1688 | 3925 | 205 | 350 | 243 | 124 | 382 | 3 | 443.12 | 106.09
15:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 393 | 308 |  | 0 | 450 | 0 | 52 | 62 | 15 | 303 | 0 | 152 | 33 | 50 | 82 | 34 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 19 | 0 | 33 | 13 | 8 | 0 | 130 | 75 | 112 | 0 | 8 | 217 | 0 | 0 | 0 |  | 6 | 35 | 17 | 25 | 0 | 6 | 13 | 3 | 0 | 0 | 0 | 150 | 340 | 180 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 20 | 15 | 11 | 31 | 11 | 120 | 25 | 0 | 16 | 2 | 0 | 0 | 42 | 32 | 112 | 0 | 54 | 74 | 0 | 177 | 17 | 0 | 8 | 295 | 8 | 11 | 0 | 48 | 0 | 0 | 113 | 0 | 15 | 4 | 25 | 17 | 5 | 368 | 35 | 52 | 51 | 2 | 106 | 17 | 61 | 17 | 57 | 25 | 245 | 54 | 37 | 54 | 34 | 0 | 17 | 25 | 0 | 17 | 280 | 53 | 0 | 582 | 2 | 0 | 0 |  | 923 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 9 | 0 | 32 | 126 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 46 | 28 | 25 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 223 | 17 | 0 | 35 | 0 | 20 | 0 | 5 | 35 | 1244 | 220 | 0 | 35 | 4 | 69 | 36 | 345 | 0 | 518 | 20 | 0 | 1362 | 127 | 0 |  | 7241 | 6058 | 13299 | 3879 | 923 | 1843 | 0 | 1559 | 3886 | 205 | 345 | 242 | 120 | 295 | 2 | 812.705 | 106.1
16:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 396 | 311 |  | 0 | 450 | 0 | 48 | 62 | 15 | 310 | 0 | 152 | 33 | 50 | 82 | 44 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 19 | 16 | 33 | 26 | 8 | 0 | 130 | 75 | 113 | 0 | 8 | 217 | 0 | 0 | 0 |  | 6 | 35 | 17 | 25 | 6 | 10 | 13 | 5 | 0 | 0 | 0 | 0 | 350 | 203 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 33 | 16 | 8 | 31 | 11 | 120 | 28 | 0 | 16 | 1 | 0 | 0 | 45 | 36 | 112 | 0 | 54 | 82 | 0 | 177 | 17 | 0 | 8 | 270 | 8 | 11 | 0 | 48 | 0 | 0 | 67 | 0 | 17 | 12 | 12 | 17 | 5 | 370 | 18 | 52 | 51 | 1 | 69 | 17 | 61 | 17 | 57 | 25 | 245 | 55 | 25 | 54 | 34 | 0 | 0 | 2 | 0 | 17 | 360 | 53 | 0 | 0 | 3 | 0 | 0 |  | 924 | 0 | 0 | 0 | 77 | 0 | 0 | 0 | 9 | 0 | 32 | 126 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 53 | 28 | 34 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 242 | 17 | 0 | 35 | 0 | 30 | 0 | 4 | 50 | 1244 | 220 | 0 | 35 | 2 | 39 | 36 | 349 | 0 | 520 | 16 | 0 | 1360 | 82 | 0 |  | 6534 | 6071 | 12605 | 3884 | 924 | 1857 | 0 | 1526 | 3304 | 205 | 349 | 249 | 120 | 184 | 3 | 1188.975 | 106.1
17:00 | 0 | 0 | 102 | 170 | 0 | 0 | 0 | 402 | 317 |  | 0 | 450 | 0 | 48 | 80 | 15 | 308 | 0 | 151 | 33 | 50 | 82 | 54 | 0 | 0 | 0 | 35 | 35 | 35 | 15 | 19 | 16 | 33 | 15 | 8 | 0 | 129 | 75 | 112 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 52 | 17 | 25 | 12 | 40 | 13 | 16 | 0 | 0 | 0 | 0 | 355 | 202 | 8 | 0 | 10 | 0 | 0 | 51 | 0 | 0 | 33 | 16 | 11 | 31 | 11 | 96 | 32 | 0 | 16 | 0 | 0 | 20 | 46 | 35 | 112 | 0 | 60 | 84 | 0 | 177 | 17 | 0 | 9 | 275 | 8 | 11 | 0 | 47 | 0 | 0 | 67 | 0 | 15 | 1 | 25 | 17 | 6 | 367 | 18 | 52 | 51 | 0 | 69 | 17 | 70 | 17 | 57 | 25 | 245 | 53 | 10 | 54 | 34 | 0 | 6 | 2 | 0 | 17 | 401 | 53 | 0 | 0 | 0 | 0 | 0 |  | 921 | 0 | 0 | 0 | 77 | 0 | 0 | 0 | 13 | 0 | 32 | 100 | 24 | 32 | 0 | 0 | 0 | 0 | 4 | 46 | 28 | 42 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 257 | 17 | 0 | 39 | 0 | 39 | 0 | 2 | 55 | 1210 | 220 | 0 | 35 | 1 | 24 | 36 | 330 | 0 | 518 | 6 | 0 | 1361 | 45 | 0 |  | 6726 | 5981 | 12707 | 3951 | 921 | 1904 | 0 | 1674 | 3269 | 204 | 330 | 267 | 96 | 91 | 0 | 661.815 | 106.1
18:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 383 | 330 |  | 0 | 400 | 0 | 48 | 80 | 15 | 270 | 0 | 126 | 33 | 42 | 82 | 56 | 0 | 0 | 0 | 35 | 35 | 35 | 16 | 19 | 16 | 33 | 27 | 8 | 0 | 128 | 75 | 110 | 0 | 10 | 220 | 0 | 0 | 0 |  | 6 | 60 | 17 | 25 | 12 | 47 | 13 | 16 | 0 | 0 | 0 | 0 | 330 | 196 | 8 | 0 | 10 | 0 | 0 | 51 | 0 | 0 | 34 | 17 | 11 | 31 | 11 | 104 | 32 | 0 | 16 | 0 | 0 | 20 | 47 | 34 | 80 | 0 | 56 | 86 | 0 | 180 | 17 | 0 | 9 | 280 | 16 | 11 | 0 | 48 | 0 | 0 | 67 | 0 | 17 | 0 | 25 | 29 | 15 | 381 | 28 | 52 | 51 | 0 | 102 | 17 | 69 | 17 | 57 | 25 | 245 | 53 | 1 | 54 | 36 | 0 | 17 | 0 | 0 | 17 | 350 | 53 | 0 | 0 | 0 | 0 | 0 |  | 922 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 36 | 0 | 32 | 124 | 22 | 32 | 0 | 0 | 0 | 0 | 11 | 46 | 28 | 42 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 129 | 0 | 261 | 17 | 0 | 50 | 0 | 54 | 0 | 1 | 55 | 1140 | 213 | 0 | 35 | 0 | 2 | 36 | 349 | 0 | 548 | 1 | 0 | 1311 | 8 | 0 |  | 6621 | 5928 | 12549 | 3852 | 922 | 1837 | 0 | 1785 | 3179 | 203 | 349 | 305 | 104 | 13 | 0 | 526.205 | 106.1
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 397 | 327 |  | 0 | 450 | 0 | 48 | 80 | 15 | 318 | 0 | 191 | 33 | 42 | 130 | 55 | 0 | 0 | 0 | 35 | 35 | 55 | 18 | 19 | 16 | 33 | 26 | 25 | 0 | 129 | 75 | 112 | 0 | 17 | 226 | 0 | 0 | 0 |  | 6 | 64 | 17 | 25 | 12 | 47 | 13 | 15 | 0 | 0 | 0 | 0 | 355 | 203 | 8 | 0 | 25 | 0 | 0 | 51 | 0 | 0 | 40 | 17 | 11 | 31 | 11 | 116 | 45 | 0 | 16 | 0 | 0 | 30 | 47 | 37 | 112 | 0 | 56 | 86 | 0 | 180 | 17 | 0 | 9 | 305 | 16 | 5 | 0 | 80 | 0 | 0 | 160 | 0 | 43 | 0 | 25 | 34 | 13 | 367 | 83 | 88 | 51 | 0 | 256 | 24 | 61 | 104 | 57 | 25 | 248 | 53 | 0 | 54 | 51 | 0 | 17 | 0 | 0 | 17 | 401 | 87 | 0 | 0 | 0 | 0 | 0 |  | 919 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 47 | 12 | 40 | 126 | 30 | 48 | 0 | 0 | 0 | 35 | 11 | 63 | 28 | 42 | 26 | 52 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 129 | 0 | 295 | 17 | 0 | 50 | 0 | 64 | 0 | 0 | 55 | 1190 | 216 | 0 | 136 | 0 | 0 | 70 | 345 | 0 | 568 | 0 | 0 | 1411 | 0 | 0 |  | 7614 | 6486 | 14100 | 4099 | 919 | 1988 | 0 | 2564 | 3349 | 204 | 345 | 516 | 116 | 0 | 0 | 811.75 | 106.11
19:30 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 409 | 327 |  | 0 | 450 | 0 | 48 | 80 | 15 | 319 | 0 | 156 | 33 | 42 | 145 | 55 | 0 | 0 | 0 | 35 | 35 | 55 | 18 | 19 | 17 | 33 | 26 | 25 | 0 | 129 | 75 | 112 | 0 | 17 | 222 | 0 | 0 | 0 |  | 6 | 68 | 17 | 25 | 12 | 50 | 13 | 20 | 0 | 0 | 0 | 0 | 305 | 200 | 16 | 0 | 25 | 0 | 0 | 51 | 0 | 0 | 43 | 17 | 11 | 31 | 11 | 114 | 47 | 0 | 16 | 0 | 0 | 30 | 47 | 39 | 112 | 0 | 56 | 86 | 0 | 180 | 17 | 0 | 9 | 300 | 16 | 5 | 0 | 95 | 0 | 0 | 160 | 0 | 106 | 0 | 25 | 34 | 32 | 368 | 84 | 88 | 51 | 0 | 256 | 54 | 61 | 104 | 57 | 25 | 255 | 53 | 0 | 72 | 51 | 0 | 17 | 0 | 0 | 17 | 380 | 123 | 0 | 0 | 0 | 0 | 0 |  | 919 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 28 | 20 | 40 | 126 | 30 | 48 | 0 | 0 | 0 | 35 | 11 | 90 | 28 | 42 | 31 | 52 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 304 | 17 | 0 | 50 | 0 | 61 | 0 | 0 | 55 | 1244 | 217 | 0 | 150 | 0 | 0 | 75 | 352 | 0 | 568 | 0 | 0 | 1413 | 0 | 0 |  | 7740 | 6585 | 14325 | 4015 | 919 | 2008 | 0 | 2716 | 3405 | 204 | 352 | 592 | 114 | 0 | 0 | 883.375 | 0
20:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 407 | 327 |  | 0 | 450 | 0 | 46 | 80 | 15 | 317 | 0 | 153 | 33 | 42 | 147 | 56 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 18 | 33 | 26 | 25 | 0 | 129 | 75 | 116 | 0 | 17 | 221 | 0 | 0 | 0 |  | 6 | 72 | 17 | 25 | 12 | 0 | 13 | 30 | 0 | 0 | 0 | 0 | 330 | 198 | 16 | 0 | 25 | 0 | 0 | 51 | 0 | 0 | 40 | 17 | 11 | 33 | 11 | 114 | 50 | 0 | 16 | 0 | 0 | 30 | 47 | 41 | 112 | 0 | 55 | 86 | 0 | 180 | 17 | 0 | 10 | 280 | 16 | 5 | 0 | 97 | 0 | 0 | 160 | 0 | 105 | 0 | 25 | 34 | 31 | 404 | 84 | 88 | 51 | 0 | 260 | 54 | 69 | 105 | 57 | 25 | 250 | 53 | 0 | 72 | 51 | 0 | 17 | 0 | 0 | 17 | 380 | 159 | 0 | 0 | 2 | 0 | 0 |  | 804 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 25 | 35 | 40 | 126 | 29 | 48 | 0 | 0 | 0 | 35 | 11 | 90 | 28 | 42 | 39 | 52 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 304 | 17 | 0 | 50 | 0 | 62 | 0 | 0 | 70 | 1244 | 217 | 0 | 150 | 0 | 0 | 75 | 354 | 0 | 571 | 0 | 0 | 1421 | 0 | 0 |  | 7792 | 6518 | 14310 | 4071 | 804 | 2000 | 0 | 2691 | 3416 | 204 | 354 | 654 | 114 | 0 | 2 | 802.2 | 106.11
21:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 407 | 326 |  | 0 | 450 | 0 | 48 | 80 | 15 | 317 | 0 | 184 | 33 | 42 | 147 | 56 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 18 | 33 | 29 | 25 | 0 | 130 | 75 | 115 | 0 | 17 | 224 | 0 | 0 | 0 |  | 6 | 72 | 17 | 25 | 12 | 45 | 13 | 33 | 0 | 0 | 0 | 0 | 305 | 203 | 16 | 0 | 25 | 0 | 0 | 51 | 0 | 0 | 34 | 17 | 11 | 33 | 11 | 120 | 75 | 0 | 16 | 0 | 0 | 30 | 50 | 41 | 112 | 0 | 56 | 86 | 0 | 178 | 17 | 0 | 10 | 290 | 16 | 5 | 0 | 97 | 0 | 0 | 160 | 0 | 105 | 0 | 25 | 48 | 35 | 368 | 84 | 88 | 51 | 0 | 264 | 54 | 63 | 105 | 57 | 25 | 256 | 53 | 0 | 72 | 51 | 0 | 17 | 0 | 0 | 17 | 401 | 159 | 0 | 0 | 3 | 0 | 0 |  | 804 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 25 | 16 | 40 | 126 | 34 | 48 | 0 | 0 | 0 | 35 | 11 | 91 | 28 | 42 | 39 | 52 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 312 | 17 | 0 | 68 | 0 | 62 | 0 | 0 | 75 | 1244 | 220 | 0 | 150 | 0 | 0 | 75 | 355 | 0 | 571 | 0 | 0 | 1462 | 0 | 0 |  | 7903 | 6586 | 14489 | 4107 | 804 | 2031 | 0 | 2771 | 3457 | 205 | 355 | 636 | 120 | 0 | 3 | 822.255 | 106.11
22:00 | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 405 | 327 |  | 0 | 450 | 0 | 43 | 80 | 15 | 316 | 0 | 173 | 33 | 16 | 148 | 56 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 18 | 33 | 30 | 25 | 0 | 130 | 75 | 115 | 0 | 17 | 223 | 0 | 0 | 0 |  | 0 | 72 | 17 | 25 | 12 | 50 | 13 | 35 | 0 | 0 | 0 | 0 | 305 | 202 | 16 | 0 | 25 | 0 | 0 | 51 | 0 | 0 | 42 | 17 | 11 | 33 | 11 | 114 | 78 | 0 | 17 | 0 | 0 | 30 | 50 | 41 | 112 | 0 | 56 | 84 | 0 | 178 | 17 | 0 | 10 | 295 | 16 | 5 | 0 | 97 | 0 | 0 | 160 | 0 | 105 | 0 | 25 | 54 | 30 | 366 | 84 | 88 | 51 | 0 | 88 | 17 | 65 | 105 | 68 | 25 | 260 | 53 | 0 | 72 | 51 | 0 | 17 | 0 | 0 | 17 | 401 | 159 | 0 | 0 | 15 | 0 | 0 |  | 803 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 25 | 15 | 40 | 126 | 35 | 48 | 0 | 0 | 0 | 35 | 11 | 91 | 28 | 42 | 39 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 324 | 17 | 0 | 70 | 0 | 63 | 0 | 0 | 75 | 1244 | 220 | 0 | 150 | 0 | 0 | 75 | 354 | 0 | 572 | 0 | 0 | 1456 | 0 | 0 |  | 7684 | 6551 | 14235 | 4099 | 803 | 2050 | 0 | 2507 | 3452 | 205 | 354 | 636 | 114 | 0 | 15 | 921.575 | 106.11
23:00 | 0 | 0 | 140 | 170 | 0 | 0 | 0 | 409 | 327 |  | 0 | 450 | 0 | 36 | 80 | 15 | 317 | 0 | 178 | 18 | 16 | 32 | 56 | 0 | 0 | 0 | 35 | 0 | 35 | 19 | 19 | 19 | 33 | 31 | 25 | 0 | 130 | 75 | 120 | 0 | 8 | 226 | 0 | 0 | 0 |  | 3 | 70 | 17 | 25 | 0 | 50 | 13 | 38 | 0 | 0 | 0 | 0 | 305 | 201 | 16 | 0 | 25 | 0 | 0 | 51 | 0 | 0 | 42 | 17 | 11 | 33 | 11 | 118 | 78 | 0 | 16 | 0 | 0 | 30 | 50 | 42 | 112 | 0 | 56 | 84 | 0 | 178 | 17 | 0 | 10 | 290 | 16 | 5 | 0 | 95 | 0 | 0 | 66 | 0 | 50 | 0 | 25 | 52 | 20 | 371 | 18 | 88 | 51 | 0 | 87 | 17 | 74 | 105 | 68 | 25 | 260 | 53 | 0 | 72 | 51 | 0 | 17 | 0 | 0 | 17 | 401 | 159 | 0 | 0 | 2 | 0 | 0 |  | 804 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 25 | 15 | 40 | 130 | 34 | 48 | 0 | 0 | 0 | 35 | 11 | 91 | 28 | 42 | 39 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 325 | 17 | 0 | 70 | 0 | 34 | 0 | 0 | 75 | 1244 | 220 | 0 | 150 | 0 | 0 | 0 | 355 | 0 | 572 | 0 | 0 | 1449 | 0 | 0 |  | 7293 | 6445 | 13738 | 4155 | 804 | 2049 | 0 | 2087 | 3445 | 205 | 355 | 518 | 118 | 0 | 2 | 1109.71 | 106.11
24:00 | 0 | 0 | 131 | 170 | 0 | 0 | 0 | 401 | 327 |  | 0 | 450 | 10 | 33 | 80 | 15 | 320 | 0 | 131 | 16 | 16 | 32 | 43 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 19 | 19 | 33 | 32 | 8 | 0 | 130 | 75 | 118 | 0 | 8 | 224 | 0 | 0 | 0 |  | 6 | 70 | 17 | 25 | 0 | 50 | 13 | 38 | 0 | 0 | 0 | 0 | 305 | 202 | 16 | 0 | 25 | 0 | 0 | 51 | 0 | 0 | 42 | 17 | 11 | 33 | 11 | 120 | 50 | 0 | 16 | 0 | 0 | 30 | 50 | 42 | 80 | 0 | 56 | 84 | 0 | 178 | 17 | 0 | 10 | 290 | 16 | 5 | 0 | 72 | 0 | 0 | 65 | 0 | 24 | 0 | 25 | 32 | 12 | 368 | 18 | 17 | 51 | 0 | 88 | 17 | 66 | 105 | 28 | 25 | 260 | 17 | 0 | 17 | 51 | 0 | 17 | 0 | 0 | 17 | 401 | 17 | 0 | 0 | 4 | 0 | 0 |  | 804 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 16 | 16 | 40 | 128 | 34 | 48 | 0 | 0 | 0 | 0 | 11 | 91 | 28 | 42 | 38 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 329 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 150 | 0 | 0 | 0 | 357 | 0 | 570 | 0 | 0 | 1405 | 0 | 0 |  | 6648 | 6261 | 12909 | 4041 | 804 | 2031 | 0 | 1640 | 3399 | 205 | 357 | 308 | 120 | 0 | 4 | 1423.905 | 106.11
KWH | 0 | 0 | 2671656 | 3984750 | 0 | 0 | 0 | 9703420 | 7670000 |  | 0 | 10167000 | 2676 | 963840 | 1957633 | 416663 | 7417503 | 0 | 3577000 | 573120 | 792720 | 1426560 | 1114363 | 0 | 0 | 0 | 389520 | 444402 | 517248 | 359316 | 456000 | 371520 | 731200 | 643300 | 270720 | 0 | 3005890 | 1804000 | 2700000 | 0 | 231877 | 3655711 | 0 | 0 | 0 |  | 144240 | 1041312 | 407983 | 510840 | 83520 | 415200 | 309072 | 493440 | 0 | 0 | 0 | 4341800 | 6734000 | 4756000 | 117091 | 0 | 160704 | 0 | 0 | 1140372 | 0 | 0 | 682920 | 369544 | 238860 | 730800 | 216900 | 2731200 | 1084800 | 0 | 363204 | 15050 | 594000 | 216000 | 1138800 | 939744 | 2436955 | 0 | 1313472 | 1913280 | 0 | 3666710 | 394000 | 0 | 235440 | 7020000 | 279048 | 192168 | 0 | 1560654 | 0 | 0 | 2212800 | 0 | 1203120 | 116775 | 558720 | 804480 | 252581 | 8786000 | 810000 | 1105920 | 1156690 | 24000 | 2448873 | 462458 | 1442720 | 1521900 | 881160 | 606720 | 4569400 | 804480 | 394630 | 1162080 | 779073 | 0 | 424800 | 225204 | 0 | 430200 | 7280400 | 1333163 | 0 | 6049090 | 51360 | 0 | 0 |  | 21640727 | 0 | 0 | 0 | 1387200 | 0 | 0 | 0 | 336000 | 270336 | 903750 | 2901000 | 635236 | 612384 | 0 | 0 | 0 | 180320 | 74007 | 1436624 | 661500 | 667251 | 201995 | 299496 | 109152 | 0 | 0 | 184680 | 0 | 0 | 4314000 | 0 | 0 | 3903882 | 0 | 0 | 0 | 0 | 0 | 3369364 | 0 | 6707636 | 420480 | 0 | 934944 | 0 | 952521 | 0 | 52901 | 967104 | 31424000 | 5198836 | 0 | 1507200 | 40560 | 461520 | 633062 | 8222207 | 0 | 12727270 | 256861 | 0 | 33391636 | 1346060 | 0 |  | 164907528 | 149333702 | 314241230 | 93227184 | 21640727 | 45816506 | 0 | 40085147 | 87905996 | 4809890 | 8222207 | 6817452 | 2731200 | 2933561 | 51360 | 0
Fuel Cost | 0 | 0 | 3900617.76 | 5937277.5 | 0 | 0 | 0 | 10188591 | 8283600 |  | 0 | 11082030 | 2970.36 | 10775731.2 | 25938637.25 | 5520784.75 | 8307603.36 | 0 | 6259750 | 8379014.4 | 11153570.4 | 23124537.6 | 10274426.86 | 0 | 0 | 0 | 4954694.4 | 5999427 | 6936295.68 | 269487 | 342000 | 0 | 0 | 0 | 4604947.2 | 0 | 811590.3 | 487080 | 5103000 | 0 | 3791188.95 | 3801939.44 | 0 | 0 | 0 |  | 1882332 | 17369084.16 | 6943870.66 | 6901448.4 | 1059033.6 | 4803864 | 392521.44 | 1643155.2 | 0 | 0 | 0 | 4819398 | 7340060 | 5516960 | 151047.39 | 0 | 181595.52 | 0 | 0 | 1904421.24 | 0 | 0 | 9185274 | 506275.28 | 179145 | 1278900 | 162675 | 19610016 | 1182432 | 0 | 493957.44 | 239897 | 813780 | 285120 | 1981512 | 1625757.12 | 2802498.25 | 0 | 2548135.68 | 4362278.4 | 0 | 3703377.1 | 847100 | 0 | 466171.2 | 7020000 | 209286 | 146047.68 | 0 | 21302927.1 | 0 | 0 | 29828544 | 0 | 16663212 | 1365099.75 | 5765990.4 | 10989196.8 | 3351749.87 | 8083120 | 9849600 | 15991603.2 | 14632128.5 | 373440 | 28749769.02 | 5036167.62 | 15336113.6 | 20652183 | 11358152.4 | 7147161.6 | 4203848 | 10418016 | 5702403.5 | 14746795.2 | 8865850.74 | 0 | 5547888 | 2691187.8 | 0 | 5665734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 64922181 | 0 | 0 | 0 | 14440752 | 0 | 0 | 0 | 6051360 | 4866048 | 12986887.5 | 3249120 | 1232357.84 | 6674985.6 | 0 | 0 | 0 | 3023966.4 | 1294382.43 | 22468799.36 | 5093550 | 11049676.56 | 3415735.45 | 4082130.48 | 1841394.24 | 0 | 0 | 139802.76 | 0 | 0 | 36582720 | 0 | 0 | 4528503.12 | 0 | 0 | 0 | 0 | 0 | 3908462.24 | 0 | 6640559.64 | 5651251.2 | 0 | 11060387.52 | 0 | 12097016.7 | 0 | 584556.05 | 11740642.56 | 260819200 | 5302812.72 | 0 | 11153280 | 458733.6 | 5413629.6 | 9704840.46 | 0 | 0 | 115690884.3 | 0 | 0 | 285498487.8 | 0 | 0 |  | 591107101.27 | 953669097.13 | 1544776198.4 | 98829888.32 | 64922181 | 54501171.36 | 0 | 499794853.72 | 698591292.1 | 1298670.3 | 0 | 90399178.3 | 19610016 | 16828947.3 | 0 | 0
Yesterday Day Peak | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 403 | 320 |  | 0 | 450 | 0 | 48 | 95 | 24 | 308 | 0 | 116 | 33 | 50 | 82 | 34 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 19 | 0 | 33 | 26 | 8 | 0 | 130 | 75 | 110 | 0 | 8 | 107 | 0 | 0 | 0 |  | 6 | 37 | 17 | 25 | 0 | 6 | 11 | 3 | 0 | 0 | 0 | 270 | 240 | 194 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 32 | 15 | 11 | 32 | 11 | 110 | 25 | 0 | 16 | 2 | 24 | 0 | 45 | 36 | 112 | 0 | 49 | 77 | 0 | 181 | 16 | 0 | 10 | 270 | 8 | 11 | 0 | 135 | 0 | 0 | 114 | 0 | 105 | 16 | 25 | 72 | 5 | 366 | 36 | 70 | 51 | 2 | 105 | 17 | 55 | 17 | 59 | 25 | 252 | 35 | 50 | 108 | 34 | 0 | 17 | 34 | 0 | 15 | 240 | 53 | 0 | 626 | 0 | 0 | 0 |  | 927 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 9 | 0 | 32 | 124 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 46 | 28 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 253 | 17 | 0 | 35 | 0 | 39 | 0 | 7 | 35 | 1244 | 220 | 0 | 35 | 5 | 48 | 36 | 361 | 0 | 521 | 36 | 0 | 1361 | 178 | 0 |  | 13711 | DayPeak
Yesterday Evening Peak | 0 | 0 | 110 | 170 | 0 | 0 | 0 | 407 | 326 |  | 0 | 450 | 0 | 48 | 80 | 15 | 317 | 0 | 184 | 33 | 42 | 147 | 56 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 18 | 33 | 29 | 25 | 0 | 130 | 75 | 115 | 0 | 17 | 224 | 0 | 0 | 0 | 0 | 6 | 72 | 17 | 25 | 12 | 45 | 13 | 33 | 0 | 0 | 0 | 0 | 305 | 203 | 16 | 0 | 25 | 0 | 0 | 51 | 0 | 0 | 34 | 17 | 11 | 33 | 11 | 120 | 75 | 0 | 16 | 0 | 0 | 30 | 50 | 41 | 112 | 0 | 56 | 86 | 0 | 178 | 17 | 0 | 10 | 290 | 16 | 5 | 0 | 97 | 0 | 0 | 160 | 0 | 105 | 0 | 25 | 48 | 35 | 368 | 84 | 88 | 51 | 0 | 264 | 54 | 63 | 105 | 57 | 25 | 256 | 53 | 0 | 72 | 51 | 0 | 17 | 0 | 0 | 17 | 401 | 159 | 0 | 0 | 3 | 0 | 0 |  | 804 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 25 | 16 | 40 | 126 | 34 | 48 | 0 | 0 | 0 | 35 | 11 | 91 | 28 | 42 | 39 | 52 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 312 | 17 | 0 | 68 | 0 | 62 | 0 | 0 | 75 | 1244 | 220 | 0 | 150 | 0 | 0 | 75 | 355 | 0 | 571 | 0 | 0 | 1462 | 0 | 0 |  | 14489 | EvPeak
Forecast for Evening | 0 | 0 | 180 | 0 | 0 | 40 | 0 | 412 | 330 | 0 | 0 | 450 | 330 | 50 | 95 | 15 | 330 | 0 | 180 | 40 | 64 | 150 | 55 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 18 | 33 | 30 | 25 | 0 | 128 | 75 | 115 | 0 | 17 | 220 |  | 0 | 0 | 0 | 6 | 70 | 17 | 25 | 12 | 50 | 14 | 35 | 0 | 0 | 0 | 0 | 300 | 200 | 80 | 0 | 25 | 0 | 0 | 51 | 0 | 0 | 43 | 16 | 11 | 33 | 11 | 165 | 85 | 0 | 16 | 0 | 0 | 30 | 50 | 40 | 112 | 0 | 60 | 86 | 0 | 181 | 17 | 0 | 10 | 300 | 16 | 11 | 0 | 130 | 0 | 0 | 145 | 0 | 149 | 0 | 25 | 34 | 30 | 400 | 95 | 100 | 51 | 0 | 265 | 54 | 55 | 106 | 65 | 25 | 255 | 53 | 0 | 108 | 51 | 0 | 17 |  | 0 | 17 | 400 | 150 |  | 0 | 10 | 0 |  |  | 943 | 0 | 0 |  | 98 | 0 | 0 | 0 | 40 | 50 | 40 | 132 | 33 | 110 | 0 | 0 | 0 | 35 | 21 | 91 | 28 | 42 | 40 | 52 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 160 |  | 0 | 0 | 0 | 0 | 180 | 0 | 414 | 17 | 0 | 70 | 0 | 60 | 0 | 0 | 75 | 1244 | 220 |  | 150 |  |  | 75 | 330 |  | 570 |  | 0 | 1400 |  | 0
Forecast for Day | 0 | 0 | 180 | 0 | 0 | 40 | 0 | 412 | 330 | 0 | 0 | 450 | 10 | 50 | 95 | 15 | 330 | 0 | 150 | 32 | 32 | 48 | 55 | 0 | 0 | 0 | 17 | 35 | 35 | 18 | 19 | 18 | 33 | 30 | 8 | 0 | 128 | 75 | 115 | 0 | 8 | 220 |  | 0 | 0 | 0 | 6 | 40 | 17 | 25 | 0 | 50 | 14 | 25 | 0 | 0 | 0 | 0 | 280 | 200 | 16 | 0 | 25 | 0 | 0 | 51 | 0 | 0 | 43 | 16 | 11 | 33 | 11 | 149 | 35 | 0 | 16 | 1.6 | 0 | 30 | 50 | 40 | 112 | 0 | 60 | 86 | 0 | 180 | 17 | 0 | 10 | 300 | 16 | 11 | 0 | 80 | 0 | 0 | 115 | 0 | 17 | 20 | 25 | 17 | 6 | 400 | 37 | 70 | 51 | 5 | 70 | 17 | 55 | 17 | 26 | 25 | 255 | 34 | 50 | 54 | 34 | 0 | 17 | 35 | 0 | 17 | 400 | 17 |  | 0 | 10 | 0 |  |  | 943 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 25 | 40 | 40 | 132 | 23 | 96 | 0 | 0 | 0 | 0 | 0 | 50 | 28 | 34 | 30 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 414 | 17 | 0 | 35 | 0 | 34 | 0 | 8 | 35 | 1244 | 220 |  | 35 | 6 | 100 | 35 | 330 |  | 520 | 30 | 0 | 950 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 200 | 0 | 0 | 36 | 0 | 405 | 328 | 0 | 0 | 450 | 10 | 32 | 80 | 15 | 322 | 0 | 146 | 15 | 16 | 16 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 19 | 19 | 33 | 32 | 8 | 0 | 75 | 40 | 110 | 0 | 8 | 223 | 0 | 0 | 0 | 0 | 6 | 24 | 17 | 25 | 0 | 6 | 13 | 15 | 0 | 0 | 0 | 0 | 275 | 200 | 0 | 0 | 25 | 0 | 0 | 51 | 0 | 0 | 16 | 17 | 11 | 14 | 11 | 112 | 30 | 0 | 17 | 1 | 0 | 30 | 47 | 42 | 80 | 0 | 60 | 75 | 0 | 179 | 17 | 0 | 10 | 290 | 16 | 5 | 0 | 47 | 0 | 0 | 67 | 0 | 17 | 8 | 25 | 17 | 1 | 368 | 19 | 17 | 17 | 1 | 70 | 17 | 55 | 17 | 9 | 25 | 260 | 17 | 11 | 17 | 17 | 0 | 17 | 13 | 0 | 17 | 401 | 17 | 0 | 0 | 11 | 0 | 0 | 0 | 925 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 10 | 0 | 40 | 130 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 340 | 17 | 0 | 35 | 0 | 34 | 0 | 3 | 35 | 1244 | 220 | 0 | 35 | 1 | 5 | 0 | 354 | 0 | 522 | 15 | 0 | 975 | 83 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
292.3904
| Minimum Generation |  | 12081 | 7:00 | [201 empty] | 139043690
| Highest Generation |  | 14489 | 21:00 | [201 empty] | 139.0437 |  |  |  |  | 2.9336
| Day Peak Generation |  | 13711 | 12:00 | [201 empty] | 55124806
| Evening Peak Generation |  | 14489 | 21:00 | [201 empty] | 55.1248 |  |  | 45816506 |  | 4.8099
| HVDC Max Flow |  | 927 | 5:00 | [201 empty] | 21.6407 |  |  |  |  | 0.05136
| HVDC EvPeak Flow |  | 804 | 21:00 | [199 empty] | 314241230 |  | 2.7312 |  | 87.906
| Load factor L.F |  | 90.37% | [165 empty] | 1275.5 | [36 empty] | 314.2412

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-09-06
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-09-05 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 13711 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 11652
Evening Peak Generation : |  |  | 14489 | MW Hour : | 21:00 | Available Max Generation : |  | 15445
E.P. Demand (at gen end) : |  |  | 15350 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14500
Maximum Generation : |  |  | 14489 | MW Hour : | 21:00 | Reserve(Generation end) |  | 945
Total Gen. (MKWH) : |  |  | 314.2412 | System Load Factor : | 90.37% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 920 | MW at | 21:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-09-06
Actual : |  | 106.11 | Ft.(MSL) , | Rule curve : | 100.15 | Ft.( MSL )
Gas Consumed : |  | Total = | 1114.73 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 153331059.68
: |  |  | Coal : | 698591292.1 | Oil : | 590194032.02 | Total : | 1442116383.8
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 42 | 1008:00 | 4857.5703 |  |  | 0 | 0%
Chittagong Area |  | 185 | 4440:00 | 1336.484 |  |  | 0 | 0%
Khulna Area |  | 112 | 2688:00 | 1872.677 |  |  | 0 | 0%
Rajshahi Area |  | 30 | 720:00 | 1628.1782 |  |  | 0 | 0%
Cumilla Area |  | 119 | 2856:00 | 1339.4547 |  |  | 0 | 0%
Mymensingh Area |  | 145 | 3480:00 | 996.477 |  |  | 0 | 0%
Sylhet Area |  | 65 | 1560:00 | 558.2777 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 465.5121 |  |  | 0 | 0%
Rangpur Area |  | 124 | 2976:00 | 910.4541 |  |  | 0 | 0%
Total |  | 822 |  | 13965.0851 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
8:02 | 13:08 | Dhanmondi 132/33kV T-3 was shut down for yearly maintenance.
- | 8:06 | Bagerhat-Bhandaria 132 kV Ckt-1 is restored.
8:11 | 9:25 | Sylhet 132/33kV S/S T4 LT Tripped showing 51/50 (O/C) relays Due to O/L.
9:25 | 20:04 | Gopalganj(N)-Madaripur 132kV Ckt-3 Project Work S/D from Gopalganj 400/132kV end. and from Madaripur 132/33kVend.
9:59 | 12:02 | Uttara 132/33kV S/S GT-01 LT Scheduled S/D Due to OTI damage.
9:59 | 12:02 | Uttara 132/33kV S/S GT-01 LT Scheduled S/D Due to OTI Damage. |  |  |  |  | 19.0MW load interrup.
10:00 | 12:01 | Uttara 132/33kV S/S GT-01 HT Scheduled S/D Due to OTI damage.
10:00 | 12:01 | Uttara 132/33kV S/S GT-01 HT Scheduled S/D Due to OTI damage.
10:14 | 17:50 | Baghabari-Ishurdi 230 kV Ckt-2 Scheduled S/D from Ishurdi 230/132kV end Due to request of Bogra ALDC and from
Baghabari 230/132kV end Due to Busbar Stability test.
- | 10:42 | Sikalbaha 225MW ST was sync.
10:47 | - | Dhaka University GT-1 was S/D.
12:00 | - | Day peak generation: 13711 MW.
12:26 | 12:48 | Halishahar-Julda 132kV Ckt-1 Tripped from Juldah 132/33kV end showing Distance Relay relays Due to Line Trip.
12:34 | 12:44 | Bashundhara-Rampura 132 kV Ckt-1 Tripped from Rampura 230/132kV end showing Distance Realy (21/1): B-N,Z1 Trip. Master
Trip 86T2 & 86T4. Tee point: High Impedance Diffential 87Tee2(FDR) A,B,C relays Due to Unknown.
12:50 | 12:59 | Jashore 132/33kV S/S T-1 LT Tripped showing E/F inst relays Due to 33 kv Narail west zone feeder fault. |  |  |  |  | 53.0MW load interrup.
12:50 | 12:59 | Jashore 132/33kV S/S T-1 LT Tripped showing E/F inst relays Due to 33 kv Narail west zone feeder fault.
13:15 | - | Chandpur 132/33kV S/S 115MW CPGL Power Plant Incomer (L5) Scheduled S/D Due to Maintenance work.
- | 13:47 | Jashore 132/33kV S/S T-3 HT is restored.
13:59 | 15:48 | Bhulta 132/33kV S/S GT2 LT Forced S/D Due to Red hot maintenance. |  |  |  |  | 50.0MW load interrup.
14:00 | 15:44 | Bhulta 132/33kV S/S GT2 HT Forced S/D Due to None. |  |  |  |  | 50.0MW load interrup.
- | 14:06 | Jashore 132/33kV S/S T-3 LT is restored.
14:25 | 15:40 | Sylhet 132/33kV S/S T4 LT Tripped showing 51/50 relays Due to Over load.
14:51 | - | Meghnaghat-Bashkhali 400kV ckt tripped.
14:56 | 15:12 | Narshingdi 132/33kV S/S T-2 HT Tripped showing O/C relays Due to Over Current. |  |  |  |  | 40.0MW load interrup.
15:03 | - | Bashkhali SS Power 600 MW (Unit-2) tripped.
15:21 | - | Ashugonj (North) 360 MW was Forced shutdown.
15:21 | 17:40 | Rampal 400/230kV S/S ICT-2 LT Project Work S/D Due to Relay Check.
15:22 | 17:41 | Rampal 400/230kV S/S ICT-2 HT Project Work S/D Due to Relay Check.
15:47 | 16:58 | Srinagar 132/33kV S/S Tr-01 LT Scheduled S/D Due to Due to red hot maintenance at 4 no feeder bus side of pbs. |  |  |  |  | 25.0MW load interrup.
15:48 | 16:57 | Srinagar 132/33kV S/S Tr-01 HT Forced S/D Due to Due to red hot maintenance at 4 no feeder bus side of pbs. |  |  |  |  | 25.0MW load interrup.
17:57 | - | Ramura -Gulshan 132Kv UG ckt was charged from Rampura end.
18:17 | 19:28 | Sylhet 132/33kV S/S T4 LT Tripped showing OC relays Due to Over load.
18:28 | - | Meghnaghat-Bashkhali 400kV Ckt was switched on.
21:00 | - | Today's Evening peak generation is 14489 MW.
21:59 | - | Keranigonj 230/132/33kV S/S Hasnabad Forced S/D Due to As there is spark in the line conductor, the circuit breaker is opened
under the direction of the officer-in-charge.
- | 23:26 | Meghnaghat Summit CCPP 305MW GT1 was sync.
23:33 | - | Ghorashal Unit 5 shutdown for emergency maintenance. |  |  |  |  | 140MW generation interrup.
- | 5:27 | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-1 is restored.
- | 5:29 | Sirajganj 132/33kV S/S Sherpur-2 is restored.
5:30 | - | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-1 Forced S/D from Bog-Sherpur 132/33kV end Due to With the permission of ALDC Bogura.
5:31 | - | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-2 Forced S/D from Bog-Sherpur 132/33kV end Due to With the permission of ALDC Bogura.
5:57 | - | Barapukuria-Bogura 230 kV Ckt-1 Scheduled S/D from Bogura 230/132kV end Due to isolator replacement.
6:00 | - | Minimum Generation during the Shift : 11652 MW
6:22 | - | Bogura 230/132kV S/S 230KV Main 2 Forced S/D Due to Isolator replacement.
7:10 | - | Gulsan-Rampura 132kV Ckt-2 Scheduled S/D from Rampura 230/132kV end.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-09-05 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 110 | 2671656 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 170 | 3984750 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 407 | 9703420
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 326 | 7670000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10167000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 48 | 963840 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 2676 | Under maint.
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 80 | 1957633 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 416663 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 56 | 1114363 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 359316
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 184 | 3577000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 33 | 573120 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 317 | 7417503
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 42 | 792720 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 389520 | Engine problem
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 147 | 1426560
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 444402 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 517248
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 37 | 827520 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 731200
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 29 | 643300
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 270720 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 97 | 1560654 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Contract Expired
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 105 | 1203120 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1105920 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 53 | 804480 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 1162080 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 225204
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 430200 | Fuel shortage
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0
| Dhaka area Total |  |  |  | 5722 | 3085 | 63113788
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2700000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 231877 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 116775
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 45 | 415200
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 205 | 4809890
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 224 | 3655711
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 1156690 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 72 | 1041312 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 407983 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 25 | 510840 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 558720 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 13 | 309072 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 33 | 493440
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 12 | 83520 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 24000
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 264 | 2448873 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 462458
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 63 | 1442720 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 606720 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 51 | 779073 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 159 | 1333163 | Fuel shortage
| SS Power I |  | SS Power | 0 | 0 | 0 | 6049090 | On test.
| Cox's Bazar Wind |  | IPP | 66 | 0 | 3 | 51360 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2545 | 1473 | 29688487
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 203 | 4756000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 4341800 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 6734000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 401 | 7280400 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 25 | 160704 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 16 | 117091 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1140372
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 35 | 252581 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Fuel shortage
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 48 | 804480 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 369544 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 238860
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 120 | 2731200
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 730800
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 34 | 682920 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 11 | 216900 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 105 | 1521900 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 57 | 881160 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 424800 | Fuel shortage
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | Fuel shortage
| Cumilla Area Total |  |  |  | 2896 | 1489 | 33385512
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 75 | 1084800 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 363204 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15050
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 160 | 2212800 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 84 | 810000 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 394630
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 144240 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 341 | 5024724
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 594000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 216000 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2436955 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1138800 | Engine problem
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 41 | 939744 | Engine problem
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 192168 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 56 | 1313472
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1913280
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 178 | 3666710 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 394000 | Machine problem
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 279048 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7020000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 368 | 8786000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 235440
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 256 | 4569400 | ST Under maint.
| Sylhet Area Total |  |  |  | 2427 | 1515 | 33695017
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 804 | 21640727
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 80 | 1387200 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 25 | 336000 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserved
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 16 | 270336 | Fuel shortage
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 40 | 903750
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 420480 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 461520
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 220 | 355 | 8222207
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 571 | 12727270
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 3121 | 1908 | 46369490
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 612384 | Fuel shortage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 34 | 635236 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 126 | 2901000 | ST Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 31424000
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5198836
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1507200
| Barisal 307 MW |  | IPP | 307*1 | 307 | 0 | 0 | Coal shortage.
| Barisal Area Total |  |  |  | 2265 | 1822 | 42278656
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 35 | 180320 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 11 | 74007 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 28 | 661500
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 667251 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 39 | 201995 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 158 | 3903882 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 134 | 3369364 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 312 | 6707636 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 109152 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 184680 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 299496
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 91 | 1436624 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 68 | 934944 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 75 | 967104 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 40560
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1462 | 33391636
| Rajshahi Area Total |  |  |  | 3631 | 2539 | 53130151
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 180 | 4314000 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 62 | 952521 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 52901
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 75 | 633062 | Fuel shortage
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 256861
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1346060
| Rangpur Area Total |  |  |  | 950 | 317 | 7555405
| Total |  |  |  | 24171 | 14489 | 314241230
| Eastern Grid Total |  |  |  | 14204 | 7903 | 164907528
| Western Grid Total |  |  |  | 9967 | 6586 | 149333702
| National Grid Total |  |  |  | 24171 | 14489 | 314241230
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-09-05
| (a) ENTIRE EASTERN GRID : |  | 9022.06 | MW | (b) ENTIRE WESTERN GRID : |  | 4655.8 | MW
| i) Dhaka area |  | 5074.56 | MW | i) Khulna area |  | 1675 | MW
| ii) Chittagong area |  | 1130.5 | MW | ii) Rajshahi area |  | 1617 | MW
| iii) Comilla area |  | 1179 | MW | iii) Barisal area |  | 486.8 | MW
| iv) Mymensingh area |  | 1084 | MW | iv) Rangpur area |  | 877 | MW
| v) Sylhet area |  | 554 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 13677.86 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 5 | 09:00 | Chhatak | 37 | 18:30 | Kamrangirchar | 70.14 | 13:00 | Natore | 171 | 21:00 | Sholosohor | 38 | 19:00
2 | AKSML | 98 | 12:00 | Chowmuhani | 191 | 22:00 | Kaptai | N/A | N/A | Nawabganj | 48.1 | 22:00 | Shyampur | 154 | 09:00
3 | Aftabnagar | 66 | 13:00 | Chuadanga | 115 | 21:00 | Kazla | 112 | 18:30 | Netrakona | 128 | 19:30 | Siddhirganj | 126 | 12:00
4 | Agargaon | 105 | 13:00 | Coxsbazar | 125 | 19:00 | Keranigonj | 82 | 19:00 | New | 83 | 13:00 | Sirajganj | 120 | 19:00
5 | Agrabad | 78 | 12:00 | Cumilla(N) | 189 | 12:00 | Khagrachori | 32 | 19:30 | Niamatpur | 92 | 22:00 | Sonargaon | 81 | 21:00
6 | Amnura | 60 | 21:00 | Cumilla(S) | 126 | 05:00 | Khulna | 91 | 20:00 | Noapara | 51 | 21:00 | Sreemongol | 68 | 18:30
7 | Ashuganj | 82 | 23:00 | Daudkandi | 126 | 22:00 | Khulshi | 192 | 11:00 | PHP | 2 | 22:00 | Sreepur | 79.86 | 18:30
8 | BIPTC | N/A | N/A | Dhaka | 37 | 12:00 | Kishoreganj | 118 | 00:00 | Pabna | 129 | 21:00 | Srinagar | 49.68 | 22:00
9 | BSRM | 160 | 02:00 | Dhamrai | 126 | 09:00 | Kodda | 284 | 21:00 | Palashbari | 132 | 07:00 | Sunamganj | 54 | 18:30
10 | Bagerhat | 86 | 21:00 | Dhanmondi | 126 | 13:00 | Kulaura | 54 | 18:30 | Panchagarh | 73 | 19:00 | Sylhet | 177 | 18:30
11 | Bakulia | 104 | 18:30 | Dohazari | 92 | 19:30 | Kurigram | 58 | 07:00 | Patuakhali | 108 | 23:00 | TK | 30.5 | 20:00
12 | Banani | 74 | 13:00 | Faridpur | 153 | 21:00 | Kushtia | 130 | 17:00 | Payra | 23.8 | 21:00 | Tangail | 252 | 21:00
13 | Bangabhaban | 19 | 10:00 | Fatullah | 69 | 11:00 | Lalbag | 101 | 13:00 | Postogola | 63 | 23:00 | Thakurgaon | 92 | 22:00
14 | Barapukuria | 65 | 14:00 | Fenchuganj | 48 | 18:30 | Lalmonirhat | 55 | 18:30 | Purbachal | 22 | 15:00 | Tongi | 119 | 10:00
15 | Barguna | 20 | 19:00 | Feni | 141 | 22:00 | Madanganj | 40 | 20:00 | Purbasadipur | 122 | 13:00 | Ullon | 44 | 00:00
16 | Barishal | 111 | 22:00 | GPH | 77 | 07:00 | Madaripur | 101 | 04:00 | Rahim | 41 | 12:00 | Uttara | 86 | 13:00
17 | Barishal-230 | 112 | 21:00 | Ghorashal | 77 | 23:00 | Madartek | 93 | 23:00 | Rajbari | 68 | 20:00 | UttaraNew | 72 | 15:00
18 | Baroaulia | 71 | 01:00 | Goalpara | 36 | 13:00 | Madunaghat | 58 | 19:00 | Rajendrapur | 104 | 19:30 | Zigatola | 75 | 13:00
19 | Baroirhat | 70 | 18:30 | Gollamari | 57 | 13:00 | Magura | 60 | 05:00 | Rajshahi | 174 | 20:00
20 | Bashundhara | 174 | 15:00 | Gopalganj | 109 | 22:00 | Mahasthangarh | 86 | 23:00 | Rajshahi-230 | 42 | 23:00
21 | BashundharaCement | 12 | 12:00 | Gulshan | 80 | 12:00 | Manikganj | 122 | 19:00 | Ramganj | 94 | 20:00
22 | Beanibazar | 84 | 18:30 | Halishahar | 72.5 | 11:00 | Maniknagar | 104 | 12:00 | Rampur | 30 | 18:30
23 | Benapole | 62 | 21:00 | HaripurSBU | 148 | 12:00 | Matarbari | 40 | 19:30 | Rangamati | 18 | 18:30
24 | Bhaluka | 114 | 18:30 | Hasnabad | 89 | 22:00 | Matuail | 74 | 12:00 | Rangpur | 146 | 12:00
25 | Bhandaria | 52 | 20:00 | Hathazari | 76 | 19:30 | Millgate | 108 | 15:00 | Ruppur | 6.6 | 15:00
26 | Bhangura | 40 | 19:00 | Ishurdi | 83 | 21:00 | Mirpur | 140 | 12:00 | SSM | 0 | 00:00
27 | Bheramara(GK) | 62 | 18:30 | Jaldhaka | 80 | 18:30 | Mirsorai | 3 | 00:00 | Saidpur | 107 | 08:00
28 | Bhulta | 247 | 23:00 | Jamalpur | 174 | 19:00 | Mithapukur | 54 | 18:30 | Satkhira | 127 | 21:00
29 | Bog-Sherpur | 70 | 19:30 | Jashore | 129 | 23:00 | Modern | 0 | 00:00 | Satmasjid | 115 | 13:00
30 | Bogura | 193 | 19:30 | Jhenaidah | 132 | 22:00 | Mogbazar | 152.2 | 15:00 | Savar | 194 | 19:00
31 | Borhanuddin | 68 | 21:00 | Joydebpur | 183 | 19:30 | Mongla | 24 | 00:00 | Shahjadpur | 101 | 19:30
32 | Brahmanbaria | 163 | 19:30 | Joypurhat | 68 | 19:30 | Motijheel | 48 | 12:00 | Shahjibazar | 125 | 15:00
33 | Cantonment | 168 | 14:00 | Juldah | 23 | 03:00 | Munshiganj | 112 | 00:00 | Shahmirpur | 49.3 | 00:00
34 | Chandpur | 66 | 22:00 | KSRM | 35 | 17:00 | Mymensingh | 224 | 06:00 | Shariatpur | 72 | 21:00
35 | Chandraghona | 33 | 19:00 | Kabirpur | 284 | 20:00 | Naogaon | 151 | 21:00 | Sherpur | 140 | 19:00
36 | Chapai | 72 | 22:00 | Kachua | 72 | 12:00 | Narail | 53 | 05:00 | Shikalbaha | 27 | 19:00
37 | Charsaidpur | 61 | 23:00 | Kallyanpur | 111 | 00:00 | Narinda | 85 | 13:00 | Shikalbaha-230 | N/A | N/A
38 | Chauddagram | 57 | 19:30 | Kalurghat | 34 | 10:00 | Narshingdi | 180 | 19:30 | Shitalakhya | 111.1 | 12:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-09-05 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 409 | 13:00 | 383 | 15:00 | Gopalganj | 401 | 06:00 | 393 | 13:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 374 | 18:30 | 366 | 16:00
| Bhulta | 390 | 07:00 | 377 | 16:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 401 | 05:00 | 390 | 14:00 | Payra | 410 | 05:00 | 406 | 14:00
| BIPTC | 399 | 08:00 | 393 | 01:00 | Rahanpur | 392 | 18:00 | 379 | 02:00
| Bogura | N/A | N/A | N/A | N/A | Rampal | 403 | 19:00 | 399 | 14:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 229 | 04:00 | 220 | 13:00 | Hasnabad | 227 | 21:00 | 220 | 13:00
| AKSML | 232 | 00:00 | 224 | 12:00 | Hathazari | 234 | 21:00 | 225 | 09:00
| Aminbazar | 238 | 22:00 | 221 | 11:00 | Ishurdi | 235 | 19:00 | 225 | 12:00
| Ashuganj | 229 | 06:00 | 224 | 13:00 | Jhenaidah | 227 | 16:00 | 220 | 12:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 228 | 03:00 | 222 | 12:00
| Baghabari | 228 | 18:30 | 220 | 12:00 | Keranigonj | 228 | 04:00 | 219 | 13:00
| Barapukuria | 215 | 17:00 | 203 | 04:00 | Khulna(S) | 235 | 06:00 | 230 | 21:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 236 | 19:00 | 232 | 14:00 | Maniknagar | 229 | 04:00 | 218 | 13:00
| Bheramara | 235 | 19:00 | 225 | 12:00 | Meghnaghat | 230 | 00:00 | 226 | 13:00
| Bhulta | 229 | 01:00 | 223 | 12:00 | Mirsorai | 237 | 21:00 | 223 | 09:00
| Bibiana | 229 | 01:00 | 223 | 17:00 | Rajshahi | 235 | 19:00 | 224 | 12:00
| BIPTC | 235 | 19:00 | 224 | 12:00 | Rampal | 233 | 19:00 | 228 | 14:00
| Bogura | 221 | 17:00 | 211 | 05:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 241 | 01:00 | 238 | 08:00 | Rampura | 228 | 04:00 | 218 | 12:00
| BSRM | 237 | 21:00 | 224 | 09:00 | Shikalbaha | 235 | 21:00 | 223 | 13:00
| Cumilla(N) | 225 | 01:00 | 220 | 09:00 | Shyampur | 227 | 06:00 | 219 | 13:00
| Fenchuganj | 233 | 01:00 | 227 | 18:30 | Siddhirganj | 229 | 04:00 | 222 | 12:00
| Ghorashal | 230 | 00:00 | 230 | 00:00 | Sirajgonj | 232 | 19:00 | 228 | 05:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 223 | 00:00 | 220 | 09:00
| GPH | 235 | 21:00 | 222 | 13:00 | Tongi | 225 | 04:00 | 215 | 13:00
| Haripur | 227 | 18:00 | 221 | 14:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 134 | 04:00 | 125 | 12:00 | Lalbag | 134 | 06:00 | 126 | 13:00
| Agargaon | 131 | 03:00 | 124 | 11:00 | Lalmonirhat | 124 | 09:00 | 116 | 05:00
| Agrabad | 135 | 22:00 | 129 | 09:00 | Madanganj | 132 | 06:00 | 128 | 13:00
| AKS | 133 | 21:00 | 126 | 13:00 | Madaripur | 130 | 03:00 | 127 | 14:00
| Aminbazar | 132 | 00:00 | 121 | 12:00 | Madartek | 134 | 04:00 | 125 | 13:00
| Amnura | 140 | 23:00 | 33 | 06:00 | Madunaghat | 137 | 21:00 | 130 | 09:00
| Ashuganj | 136 | 00:00 | 135 | 08:00 | Magura | 136 | 15:00 | 128 | 21:00
| Bagerhat | 136 | 06:00 | 128 | 00:00 | Mahasthangarh | 130 | 17:00 | 119 | 05:00
| Bakulia | 137 | 21:00 | 130 | 09:00 | Manikganj | 133 | 22:00 | 123 | 19:00
| Banani | 134 | 04:00 | 126 | 12:00 | Maniknagar | 131 | 02:00 | 124 | 13:00
| Bangabhaban | 132 | 02:00 | 123 | 13:00 | Matarbari | 129 | 21:00 | 113 | 19:00
| Barapukuria | 133 | 00:00 | 123 | 05:00 | Matuail | 133 | 06:00 | 129 | 10:00
| Barguna | 139 | 04:00 | 133 | 15:00 | Millgate | 131 | 06:00 | 124 | 09:00
| Barishal | 139 | 05:00 | 132 | 00:00 | Mirpur | 131 | 03:00 | 12 | 00:00
| Barishal-230 | 135 | 07:00 | 132 | 14:00 | Mithapukur | 129 | 19:00 | 117 | 03:00
| Baroaulia | 137 | 21:00 | 130 | 09:00 | Modern | 135 | 21:00 | 128 | 09:00
| Baroirhat | 129 | 21:00 | 122 | 08:00 | Mogbazar | 135 | 04:00 | 125 | 13:00
| Bashundhara | 134 | 07:00 | 123 | 13:00 | Mongla | 133 | 10:00 | 127 | 20:00
| BashundharaCement | 132 | 01:00 | 128 | 13:00 | Motijheel | 132 | 02:00 | 123 | 13:00
| Beanibazar | 125 | 07:00 | 120 | 18:30 | Munshiganj | 132 | 01:00 | 129 | 10:00
| Benapole | 136 | 07:00 | 129 | 00:00 | Mymensingh | 137 | 18:30 | 114 | 09:00
| Bhaluka | 119 | 01:00 | 117 | 09:00 | Naogaon | 125 | 18:00 | 111 | 21:00
| Bhandaria | 137 | 05:00 | 125 | 21:00 | Narail | 134 | 15:00 | 127 | 13:00
| Bhangura | 134 | 19:00 | 130 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 132 | 19:00 | 127 | 12:00 | Narshingdi | 125 | 14:00 | 120 | 12:00
| Bheramara(GK) | 133 | 15:00 | 127 | 12:00 | Natore | 128 | 19:00 | 121 | 14:00
| Bhulta | 125 | 02:00 | 120 | 09:00 | Nawabganj | 133 | 04:00 | 127 | 13:00
| Bog-Sherpur | 132 | 16:00 | 122 | 03:00 | Netrakona | 136 | 18:30 | 117 | 19:00
| Bogura | 133 | 18:00 | 111 | 13:00 | New | 131 | 06:00 | 125 | 09:00
| Bogura-230 | 134 | 17:00 | 120 | 05:00 | Niamatpur | 125 | 18:00 | 107 | 21:00
| Brahmanbaria | 124 | 07:00 | 119 | 13:00 | Noapara | 136 | 07:00 | 131 | 20:00
| Cantonment | 131 | 04:00 | 123 | 13:00 | Pabna | 132 | 19:00 | 125 | 12:00
| Chandpur | 124 | 18:30 | 117 | 07:00 | Palashbari | 125 | 17:00 | 115 | 05:00
| Chandraghona | 136 | 00:00 | 131 | 13:00 | Panchagarh | 129 | 00:00 | 108 | 08:00
| Chapai | 126 | 10:00 | 119 | 22:00 | Patuakhali | 138 | 00:00 | 135 | 03:00
| Charsaidpur | 134 | 04:00 | 90 | 00:00 | Payra | 138 | 00:00 | 137 | 02:00
| Chauddagram | 127 | 18:30 | 121 | 09:00 | PHP | 129 | 21:00 | 120 | 09:00
| Chhatak | 127 | 03:00 | 123 | 11:00 | Postogola | 133 | 02:00 | 129 | 10:00
| Chowmuhani | 125 | 21:00 | 115 | 09:00 | Purbachal | 134 | 03:00 | 123 | 09:00
| Chuadanga | 131 | 16:00 | 122 | 21:00 | Purbasadipur | 127 | 19:00 | 108 | 05:00
| Coxsbazar | 128 | 21:00 | 112 | 19:00 | Rahanpur | 129 | 16:00 | 124 | 21:00
| Cumilla(N) | 129 | 18:30 | 124 | 12:00 | Rahim | 133 | 03:00 | 130 | 09:00
| Cumilla(S) | 132 | 00:00 | 124 | 09:00 | Rajbari | 128 | 16:00 | 122 | 13:00
| Daudkandi | 127 | 00:00 | 122 | 13:00 | Rajendrapur | 134 | 19:00 | 126 | 18:00
| Dhaka | 134 | 04:00 | 125 | 13:00 | Rajshahi | 132 | 19:00 | 121 | 18:00
| Dhamrai | 132 | 01:00 | 126 | 09:00 | Rajshahi-230 | 132 | 18:30 | 116 | 22:00
| Dhanmondi | 134 | 03:00 | 127 | 13:00 | Ramganj | 121 | 18:30 | 112 | 09:00
| Dohazari | 133 | 21:00 | 126 | 19:00 | Rampur | 135 | 18:00 | 128 | 13:00
| Faridpur | 128 | 16:00 | 124 | 12:00 | Rampura | 134 | 06:00 | 124 | 12:00
| Fatullah | 128 | 05:00 | 123 | 13:00 | Rangamati | 136 | 21:00 | 130 | 19:00
| Fenchuganj | 132 | 01:00 | 128 | 13:00 | Rangpur | 128 | 19:00 | 115 | 03:00
| Feni | 128 | 00:00 | 122 | 08:00 | Ruppur | 136 | 18:30 | 128 | 14:00
| Ghorashal | 136 | 00:00 | 132 | 16:00 | Saidpur | 125 | 12:00 | 113 | 08:00
| Goalpara | 136 | 10:00 | 132 | 19:30 | Satkhira | 135 | 17:00 | 126 | 20:00
| Gollamari | 136 | 06:00 | 131 | 15:00 | Satmasjid | 131 | 04:00 | 124 | 13:00
| Gopalganj | 130 | 06:00 | 127 | 01:00 | Savar | 132 | 22:00 | 126 | 18:00
| Gopalganj-400 | 128 | 05:00 | 126 | 13:00 | Shahjadpur | 137 | 19:00 | 133 | 14:00
| Gulshan | 133 | 03:00 | 125 | 12:00 | Shahjibazar | 126 | 16:00 | 122 | 13:00
| Halishahar | 136 | 22:00 | 129 | 09:00 | Shahmirpur | 136 | 22:00 | 129 | 09:00
| Haripur | 133 | 01:00 | 130 | 09:00 | Shariatpur | 129 | 07:00 | 125 | 14:00
| HaripurSBU | 133 | 03:00 | 130 | 09:00 | Sherpur | 136 | 18:30 | 115 | 17:00
| Hasnabad | 132 | 01:00 | 129 | 10:00 | Shikalbaha | 125 | 18:00 | 118 | 10:00
| Hathazari | 137 | 12:00 | 133 | 02:00 | Shikalbaha-230 | 136 | 00:00 | 129 | 13:00
| Ishurdi | 134 | 19:00 | 128 | 12:00 | Shitalakhya | 133 | 04:00 | 128.5 | 13:00
| Jaldhaka | 125 | 16:00 | 113 | 07:00 | Sholosohor | 136 | 21:00 | 128 | 13:00
| Jamalpur | 138 | 18:30 | 116 | 16:00 | Shyampur | 127 | 02:00 | 123 | 09:00
| Jashore | 135 | 16:00 | 130 | 14:00 | Shyampur-230 | 128 | 04:00 | 122 | 13:00
| Jhenaidah | 138 | 15:00 | 129 | 20:00 | Siddhirganj | 133 | 04:00 | 129 | 13:00
| Jhenaidah-230 | 138 | 16:00 | 132 | 14:00 | Sirajganj | 131 | 06:00 | 124 | 13:00
| Joydebpur | 134 | 18:30 | 127 | 15:00 | Sonargaon | 131 | 01:00 | 128 | 12:00
| Joypurhat | 123 | 18:00 | 108 | 21:00 | Sreemongol | 127 | 07:00 | 123 | 12:00
| Juldah | 137 | 21:00 | 130 | 13:00 | Sreepur | 122 | 04:00 | 119 | 09:00
| Kabirpur | 135 | 22:00 | 121 | 09:00 | Srinagar | 140 | 23:00 | 128 | 13:00
| Kachua | 124 | 21:00 | 118 | 08:00 | SSM | 139 | 00:00 | 132 | 10:00
| Kaliakoir | 137 | 18:30 | 130 | 19:00 | Sunamganj | 123 | 01:00 | 117 | 18:30
| Kallyanpur | 127 | 02:00 | 122 | 13:00 | Sylhet | 128 | 00:00 | 125 | 18:30
| Kalurghat | 137 | 21:00 | 130 | 10:00 | Tangail | 132 | 18:30 | 122 | 19:00
| Kamrangirchar | 134 | 06:00 | 118 | 13:00 | Thakurgaon | 128 | 00:00 | 105 | 08:00
| Kaptai | N/A | N/A | N/A | N/A | TK | 136 | 21:00 | 0.6 | 19:00
| Kazla | 131 | 05:00 | 123 | 13:00 | Tongi | 132 | 04:00 | 126 | 13:00
| Keranigonj | 134 | 04:00 | 128 | 13:00 | Ullon | 134 | 06:00 | 125 | 13:00
| Khagrachori | 136 | 19:30 | 129 | 13:00 | Uttara | 131 | 04:00 | 126 | 14:00
| Khulna | 136 | 07:00 | 131 | 14:00 | UttaraNew | 131 | 04:00 | 126 | 09:00
| Khulna(S) | 137 | 06:00 | 131 | 20:00 | Zigatola | 134 | 05:00 | 127 | 13:00
| Khulshi | 134 | 21:00 | 128 | 09:00
| Kishoreganj | 126 | 01:00 | 123 | 09:00
| Kodda | 135 | 22:00 | 125 | 09:00
| KSRM | 136 | 21:00 | 129 | 09:00
| Kulaura | 130 | 01:00 | 127 | 13:00
| Kurigram | 127 | 19:00 | 107 | 07:00
| Kushtia | 133 | 16:00 | 127 | 12:00

## L-Curve
Date | 2023-09-05
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1460 | 6648 | 6261 | 12909 |  |  |  | QF-LDC-11
0:30 | 1330 | 6569.5 | 6170 | 12739.5 | Date: | 2023-09-05
1:00 | 1200 | 6491 | 6079 | 12570
1:30 | 1205 | 6451 | 6081 | 12532
2:00 | 1210 | 6411 | 6083 | 12494
2:30 | 1210 | 6447.5 | 6046 | 12493.5 | [5 empty] | Gen. at Eve. Peak | 14489 | 14489 MW (21:00 )
3:00 | 1210 | 6484 | 6009 | 12493 | [6 empty] | 21:00
3:30 | 1155 | 6459 | 5983.5 | 12442.5 | [5 empty] | Gen. at Day Peak | 13711 | 13711 MW (12:00 )
4:00 | 1100 | 6434 | 5958 | 12392 | [6 empty] | 12:00
4:30 | 1065 | 6447 | 5961 | 12408 | [5 empty] | Highest Generation | 14489
5:00 | 1030 | 6460 | 5964 | 12424 | [6 empty] | 21:00
5:30 | 1055 | 6299.5 | 5953.5 | 12253
6:00 | 1080 | 6139 | 5943 | 12082
6:30 | 1125 | 6131.5 | 5950 | 12081.5
7:00 | 1170 | 6124 | 5957 | 12081
7:30 | 1210 | 6130.5 | 5973 | 12103.5
8:00 | 1250 | 6137 | 5989 | 12126
8:30 | 1340 | 6300.5 | 5997.5 | 12298
9:00 | 1430 | 6464 | 6006 | 12470
9:30 | 1430 | 6543 | 6012 | 12555
10:00 | 1430 | 6622 | 6018 | 12640
10:30 | 1405 | 6920.5 | 6042.5 | 12963
11:00 | 1380 | 7219 | 6067 | 13286
11:30 | 1335 | 7378.5 | 6120 | 13498.5
12:00 | 1290 | 7538 | 6173 | 13711
12:30 | 1255 | 7608 | 6180.5 | 13788.5
13:00 | 1220 | 7678 | 6188 | 13866
13:30 | 1170 | 7533 | 6168 | 13701
14:00 | 1120 | 7388 | 6148 | 13536
14:30 | 1200 | 7314.5 | 6103 | 13417.5
15:00 | 1280 | 7241 | 6058 | 13299
15:30 | 1335 | 6887.5 | 6064.5 | 12952
16:00 | 1390 | 6534 | 6071 | 12605
16:30 | 1340 | 6630 | 6026 | 12656
17:00 | 1290 | 6726 | 5981 | 12707
17:30 | 1310 | 6673.5 | 5954.5 | 12628
18:00 | 1330 | 6621 | 5928 | 12549
18:30 | 1275 | 7117.5 | 6207 | 13324.5
19:00 | 1220 | 7614 | 6486 | 14100
19:30 | 1260 | 7740 | 6585 | 14325
20:00 | 990 | 7792 | 6518 | 14310 |  |  |  | Executive Engineer
20:30 | 955 | 7847.5 | 6552 | 14399.5 |  |  |  | Network Operation Division
21:00 | 920 | 7903 | 6586 | 14489
21:30 | 925 | 7793.5 | 6568.5 | 14362
22:00 | 930 | 7684 | 6551 | 14235 |  |  |  |  | Page 6 of 7
22:30 | 1115 | 7488.5 | 6498 | 13986.5
23:00 | 1300 | 7293 | 6445 | 13738
23:30 | 1380 | 6970.5 | 6353 | 13323.5
24:00 | 1460 | 6648 | 6261 | 12909
14489 MW (21:00 )
13711 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-09-05 |  | Energy |  | 314241230
QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 4041 | 804 | 2031 | 0 | 1640 | 3399 | 205 | 357 | 308 | 120 | 0 | 4 | 1423.905
0:30 | 3987 | 863.5 | 1988.5 | 0 | 1441.5 | 3510 | 204.5 | 356.5 | 262 | 121 | 0 | 5 | 1394.7775 |  | Date: | 43712
1:00 | 3933 | 923 | 1946 | 0 | 1243 | 3621 | 204 | 356 | 216 | 122 | 0 | 6 | 1365.65
1:30 | 3895 | 923.5 | 1935 | 0 | 1242.5 | 3647.5 | 204 | 356 | 204.5 | 120 | 0 | 4 | 1306.44 | [7 empty] | Total Energy | 314.2412 | 314.2412 | Total Energy Gen 314.241 MKWHr Energy Not Served 18.119 MKWHr Energy Requirement 332.360 MKWHr
2:00 | 3857 | 924 | 1924 | 0 | 1242 | 3674 | 204 | 356 | 193 | 118 | 0 | 2 | 1247.23 | [7 empty] | Energy not Served | 18.1192 | 18.1192
2:30 | 3837.5 | 924.5 | 1964.5 | 0 | 1202 | 3689.5 | 204 | 354 | 193 | 120 | 0 | 4.5 | 1199.9575 | [7 empty] | Energy Requirement | 332.3604 | 332.3604
3:00 | 3818 | 925 | 2005 | 0 | 1162 | 3705 | 204 | 352 | 193 | 122 | 0 | 7 | 1152.685
3:30 | 3806 | 925 | 2002 | 0 | 1152 | 3698 | 204 | 353.5 | 175 | 123 | 0 | 4 | 1105.4125
4:00 | 3794 | 925 | 1999 | 0 | 1142 | 3691 | 204 | 355 | 157 | 124 | 0 | 1 | 1058.14
4:30 | 3843 | 926 | 1995 | 0 | 1128.5 | 3674 | 203.5 | 355.5 | 157 | 125 | 0 | 0.5 | 947.36
5:00 | 3892 | 927 | 1991 | 0 | 1115 | 3657 | 203 | 356 | 157 | 126 | 0 | 0 | 836.58
5:30 | 3762.5 | 926.5 | 1963.5 | 0 | 1134 | 3629.5 | 203 | 354.5 | 157 | 120 | 2.5 | 0 | 665.635
6:00 | 3633 | 926 | 1936 | 0 | 1153 | 3602 | 203 | 353 | 157 | 114 | 5 | 0 | 494.69
6:30 | 3586.5 | 907.5 | 1932 | 0 | 1188.5 | 3602.5 | 202.5 | 358.5 | 157 | 112 | 34.5 | 0 | 447.4175 | [6 empty] | Coal
7:00 | 3540 | 889 | 1928 | 0 | 1224 | 3603 | 202 | 364 | 157 | 110 | 64 | 0 | 400.145
7:30 | 3613 | 889 | 1887 | 0 | 1161.5 | 3607 | 202.5 | 364 | 154.5 | 113 | 112 | 0 | 426.4075 | [5 empty] | Oil
8:00 | 3686 | 889 | 1846 | 0 | 1099 | 3611 | 203 | 364 | 152 | 116 | 160 | 0 | 452.67
8:30 | 3754 | 889 | 1868.5 | 0 | 1142.5 | 3614.5 | 203 | 363 | 151.5 | 108 | 204 | 0 | 431.66
9:00 | 3822 | 889 | 1891 | 0 | 1186 | 3618 | 203 | 362 | 151 | 100 | 248 | 0 | 410.65
9:30 | 3713 | 908 | 1858 | 0 | 1249.5 | 3698 | 203.5 | 362 | 172 | 98 | 293 | 0 | 377.225
10:00 | 3604 | 927 | 1825 | 0 | 1313 | 3778 | 204 | 362 | 193 | 96 | 338 | 0 | 343.8
10:30 | 3599.5 | 926.5 | 1816.5 | 0 | 1547 | 3829.5 | 204 | 362.5 | 218 | 97 | 362.5 | 0 | 297.96
11:00 | 3595 | 926 | 1808 | 0 | 1781 | 3881 | 204 | 363 | 243 | 98 | 387 | 0 | 252.12
11:30 | 3687 | 926.5 | 1838.5 | 0 | 1843.5 | 3906.5 | 204.5 | 362 | 243.5 | 104 | 382.5 | 0 | 216.3075
12:00 | 3779 | 927 | 1869 | 0 | 1906 | 3932 | 205 | 361 | 244 | 110 | 378 | 0 | 180.495
12:30 | 3831.5 | 927 | 1857 | 0 | 1930.5 | 3927.5 | 205 | 355 | 243.5 | 117 | 394.5 | 0 | 311.8075
13:00 | 3884 | 927 | 1845 | 0 | 1955 | 3923 | 205 | 349 | 243 | 124 | 411 | 0 | 443.12
13:30 | 3884 | 927 | 1845 | 0 | 1955 | 3923 | 205 | 349 | 243 | 124 | 411 | 0 | 443.12
14:00 | 3884 | 927 | 1845 | 0 | 1955 | 3923 | 205 | 349 | 243 | 124 | 411 | 0 | 443.12
14:30 | 3881.5 | 925 | 1844 | 0 | 1757 | 3904.5 | 205 | 347 | 242.5 | 122 | 353 | 1 | 627.9125
15:00 | 3879 | 923 | 1843 | 0 | 1559 | 3886 | 205 | 345 | 242 | 120 | 295 | 2 | 812.705
15:30 | 3881.5 | 923.5 | 1850 | 0 | 1542.5 | 3595 | 205 | 347 | 245.5 | 120 | 239.5 | 2.5 | 1000.84
16:00 | 3884 | 924 | 1857 | 0 | 1526 | 3304 | 205 | 349 | 249 | 120 | 184 | 3 | 1188.975
16:30 | 3917.5 | 922.5 | 1880.5 | 0 | 1600 | 3286.5 | 204.5 | 339.5 | 258 | 108 | 137.5 | 1.5 | 925.395
17:00 | 3951 | 921 | 1904 | 0 | 1674 | 3269 | 204 | 330 | 267 | 96 | 91 | 0 | 661.815
17:30 | 3901.5 | 921.5 | 1870.5 | 0 | 1729.5 | 3224 | 203.5 | 339.5 | 286 | 100 | 52 | 0 | 594.01
18:00 | 3852 | 922 | 1837 | 0 | 1785 | 3179 | 203 | 349 | 305 | 104 | 13 | 0 | 526.205
18:30 | 3975.5 | 920.5 | 1912.5 | 0 | 2174.5 | 3264 | 203.5 | 347 | 410.5 | 110 | 6.5 | 0 | 668.9775
19:00 | 4099 | 919 | 1988 | 0 | 2564 | 3349 | 204 | 345 | 516 | 116 | 0 | 0 | 811.75
19:30 | 4015 | 919 | 2008 | 0 | 2716 | 3405 | 204 | 352 | 592 | 114 | 0 | 0 | 806.975
20:00 | 4071 | 804 | 2000 | 0 | 2691 | 3416 | 204 | 354 | 654 | 114 | 0 | 2 | 802.2
20:30 | 4089 | 804 | 2015.5 | 0 | 2731 | 3436.5 | 204.5 | 354.5 | 645 | 117 | 0 | 2.5 | 812.2275
21:00 | 4107 | 804 | 2031 | 0 | 2771 | 3457 | 205 | 355 | 636 | 120 | 0 | 3 | 822.255
21:30 | 4103 | 803.5 | 2040.5 | 0 | 2639 | 3454.5 | 205 | 354.5 | 636 | 117 | 0 | 9 | 871.915
22:00 | 4099 | 803 | 2050 | 0 | 2507 | 3452 | 205 | 354 | 636 | 114 | 0 | 15 | 921.575
22:30 | 4127 | 803.5 | 2049.5 | 0 | 2297 | 3448.5 | 205 | 354.5 | 577 | 116 | 0 | 8.5 | 1015.6425
23:00 | 4155 | 804 | 2049 | 0 | 2087 | 3445 | 205 | 355 | 518 | 118 | 0 | 2 | 1109.71
23:30 | 4098 | 804 | 2040 | 0 | 1863.5 | 3422 | 205 | 356 | 413 | 119 | 0 | 3 | 1266.8075 |  | Max Temp. in Dhaka |  | 37.3°C
24:00 | 4041 | 804 | 2031 | 0 | 1640 | 3399 | 205 | 357 | 308 | 120 | 0 | 4 | 1423.905
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 314.241 MKWHr Energy Not Served 18.119 MKWHr Energy Requirement 332.360 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-09-05
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 129 | 129 | 129 | 129 | 128 | 128 | 127 | 128 | 128 | 129 | 129 | 130 | 130 | 130 | 130 | 130 | 129 | 128 |  | 129 | 129 | 129 | 130 | 130 | 130 | 130 | 3005890
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1804000
3 | Chattogram TPP-1 | 110 | 114 | 115 | 112 | 115 | 117 | 116 | 117 | 116 | 116 | 115 | 110 | 115 | 115 | 112 | 113 | 112 | 110 |  | 112 | 112 | 116 | 115 | 115 | 120 | 118 | 2700000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 |  | 17 | 17 | 17 | 17 | 17 | 8 | 8 | 231877
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 4 | 6 | 9 | 19 | 11 | 16 | 19 | 18 | 4 | 12 | 1 | 0 | [8 empty] | 116775
6 | Sikalbaha 225MW CCPP (Gas) | 150 | 150 | 150 | 150 | 128 | 34 | 30 | 34 | 32 | 51 | 69 | 107 | 218 | 217 | 217 | 217 | 226 | 220 |  | 226 | 222 | 221 | 224 | 223 | 226 | 224 | 3655711
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 407983
12 | Hathazari 100 MW peaking PP | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 38 | 38 | 37 | 36 | 36 | 35 | 35 | 52 | 60 |  | 64 | 68 | 72 | 72 | 72 | 70 | 70 | 1041312
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 51 | 51 | 51 | 51 | 34 | 34 | 34 | 34 | 34 | 37 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1156690
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [25 empty] | 0 | 0
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 144 | 101 | 176 | 175 | 175 | 121 | 121 | 101 | 128 | 75 | 71 | 116 | 149 | 149 | 152 | 152 | 151 | 126 |  | 191 | 156 | 153 | 184 | 173 | 178 | 131 | 3577000
17 | Siddhirganj 335 MW CCPP | 322 | 324 | 322 | 316 | 324 | 290 | 290 | 290 | 314 | 274 | 270 | 308 | 306 | 303 | 303 | 310 | 308 | 270 |  | 318 | 319 | 317 | 317 | 316 | 317 | 320 | 7417503
18 | Kodda 300 MW PP Unit-2 (Summit) | 35 | 30 | 30 | 30 | 32 | 32 | 32 | 30 | 32 | 52 | 140 | 135 | 143 | 60 | 48 | 48 | 47 | 48 |  | 80 | 95 | 97 | 97 | 97 | 95 | 72 | 1560654
19 | Ashuganj 195 MW PP (APSCL-United) | [16 empty] | 8 | 8 |  | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 117091
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 110 | 110 | 110 | 110 | 110 | 107 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 102 | 110 |  | 110 | 110 | 110 | 110 | 110 | 140 | 131 | 2671656
23 | Ghorasal TPP Unit-5 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 180 | 180 | 180 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 3984750
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 215 | 260 | 306 | 300 | 300 | 305 | 310 | 311 | 326 | 516 | 616 | 626 | 620 | 617 | 582 | [10 empty] | 0 | 6049090
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | [16 empty] | 10 | 10 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 160704
33 | Ashuganj 225 MW CCPP | 199 | 200 | 200 | 202 | 203 | 177 | 196 | 194 | 197 | 197 | 195 | 194 | 187 | 180 | 180 | 203 | 202 | 196 |  | 203 | 200 | 198 | 203 | 202 | 201 | 202 | 4756000
34 | Ashuganj 450 MW CCPP(South) | 240 | 240 | 240 | 240 | 240 | 310 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 340 | 350 | 355 | 330 |  | 355 | 305 | 330 | 305 | 305 | 305 | 305 | 6734000
| Ashuganj 450 MW CCPP(North) | 270 | 270 | 270 | 270 | 270 | 295 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 150 | [10 empty] | 0 | 4341800
| Ashuganj 420 MW CCPP(East) | 240 | 240 | 240 | 240 | 250 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 280 | 360 | 401 | 350 |  | 401 | 380 | 380 | 401 | 401 | 401 | 401 | 7280400
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 403 | 382 | 402 | 408 | 411 | 385 | 386 | 411 | 405 | 405 | 404 | 403 | 401 | 400 | 393 | 396 | 402 | 383 |  | 397 | 409 | 407 | 407 | 405 | 409 | 401 | 9703420
Meghnaghat Unique power
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 400 | 370 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 400 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 10167000
41 | Haripur 360 MW CCPP(HPL) | 284 | 272 | 332 | 327 | 332 | 272 | 332 | 332 | 327 | 327 | 327 | 320 | 322 | 317 | 308 | 311 | 317 | 330 |  | 327 | 327 | 327 | 326 | 327 | 327 | 327 | 7670000
42 | RPCL 210MW CCPP | 68 | 69 | 68 | 68 | 68 | 68 | 32 | 28 | 28 | 26 | 26 | 25 | 25 | 25 | 25 | 28 | 32 | 32 |  | 45 | 47 | 50 | 75 | 78 | 78 | 50 | 1084800
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 11 | 26 | 39 | 47 | 51 | 50 | 50 | 46 | 37 | 25 | 10 | 1 | [8 empty] | 394630
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 40 | 43 | 43 | 24 | 35 | 34 | [12 empty] | 594000
45 | Fenchugonj CCPP Phase-2 | [16 empty] | 20 | 20 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 216000
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 55 | 55 | 56 | 56 | 56 | 56 | 59 | 58 | 54 | 40 | 54 | 49 | 49 | 49 | 54 | 54 | 60 | 56 |  | 56 | 56 | 55 | 56 | 56 | 56 | 56 | 1313472
48 | Shahjibazar 86 MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 78 | 78 | 78 | 78 | 78 | 78 | 77 | 77 | 75 | 74 | 74 | 82 | 84 | 86 |  | 86 | 86 | 86 | 86 | 84 | 84 | 84 | 1913280
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 181 | 183 | 181 | 181 | 181 | 181 | 177 | 177 | 177 | 177 | 180 |  | 180 | 180 | 180 | 178 | 178 | 178 | 178 | 3666710
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 394000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 9 | 10 | 8 | 8 | 9 | 9 |  | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 235440
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 192168
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 47 | 47 | 47 | 47 | 47 | 45 | 45 | 45 | 47 | 47 | 42 | 45 | 46 | 47 |  | 47 | 47 | 47 | 50 | 50 | 50 | 50 | 1138800
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 279048
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 290 | 300 | 290 | 270 | 275 | 290 | 270 | 290 | 275 | 270 | 270 | 275 | 290 | 295 | 270 | 275 | 280 |  | 305 | 300 | 280 | 290 | 295 | 290 | 290 | 7020000
| Bibiyana South 400 MW | 190 | 170 | 30 | 30 | 100 | 0 |  | 160 | 250 | 252 | 254 | 252 | 205 | 205 | 245 | 245 | 245 | 245 |  | 248 | 255 | 250 | 256 | 260 | 260 | 260 | 4569400
58 | Nababganj 55 MW PP (Southern power ) | [10 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 35 | 0 | 517248
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 0 | 3 | 6 | 144240
60 | Barabkunda 22 MW PP (Regent) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 11 | 11 | 11 | 11 | 11 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 309072
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 |  | 16 | 16 |  |  | 15 | 16 |  | 18 | 18 | 19 | 19 | 19 | 19 | 0 | 359316
62 | Tangail 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 16 | 16 | 16 | 17 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 17 | 16 | 16 | 363204
63 | Impoprt (Tripura) | 122 | 118 | 122 | 124 | 126 | 114 | 110 | 116 | 100 | 96 | 98 | 110 | 124 | 124 | 120 | 120 | 96 | 104 |  | 116 | 114 | 114 | 120 | 114 | 118 | 120 | 2731200
64 | Malancha, Ctg. EPZ (United) | 38 | 39 | 39 | 39 | 40 | 40 | 36 | 9 | 3 | 2 | 2 | 3 | 9 | 6 | 3 | 5 | 16 | 16 |  | 15 | 20 | 30 | 33 | 35 | 38 | 38 | 493440
65 | Feni 22 MW PP (Doreen) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 16 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 369544
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 5 | 5 | 11 | 11 | 11 | 11 | 11 | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 238860
67 | Jangalia 33 MW PP (Summit) | 32 | 25 | 25 | 25 | 25 | 25 | 25 | 29 | 25 | 27 | 32 | 32 | 32 | 32 | 31 | 31 | 31 | 31 |  | 31 | 31 | 33 | 33 | 33 | 33 | 33 | 730800
68 | Cumilla 25 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 0 | 11 |  | 11 |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 216900
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456000
70 | Summit Madhabdi | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 16 | 16 |  | 10 |  | 0 | 16 | 16 | 16 |  | 16 | 17 | 18 | 18 | 18 | 19 | 19 | 371520
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 731200
72 | Rupganj 33 MW PP(Summit) | 31 | 31 | 32 | 32 | 32 | 32 | 30 | 30 | 28 | 26 | 26 | 26 | 26 | 26 | 13 | 26 | 15 | 27 |  | 26 | 26 | 26 | 29 | 30 | 31 | 32 | 643300
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 104 | 104 | 105 | 105 | 105 | 105 | 105 | 1521900
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 17 | 27 | 59 | 66 | 61 | 57 | 57 | 57 | 57 |  | 57 | 57 | 57 | 57 | 68 | 68 | 28 | 881160
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 108 | 108 | 108 | 54 | 54 | 54 | 54 | 54 |  | 54 | 72 | 72 | 72 | 72 | 72 | 17 | 1162080
77 | Siddhirganj 100 PP(Dutch Bangla) | 9 | 9 | 9 | 9 | 9 | 9 | 20 | 32 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 18 | 16 | 573120
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 270720
79 | Kodda 150 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 48 | 64 | 82 | 82 | 82 | 82 | 82 | 82 | 82 |  | 130 | 145 | 147 | 147 | 148 | 32 | 32 | 1426560
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 34 | 34 | 34 | 32 | 32 | 16 | 20 | 33 | 33 | 34 |  | 40 | 43 | 40 | 34 | 42 | 42 | 42 | 682920
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 50 | 70 | 70 | 82 | 52 | 52 | 52 | 52 |  | 88 | 88 | 88 | 88 | 88 | 88 | 17 | 1105920
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 2 | 4 | 2 | 2 | 3 | 2 | 2 | 1 | 0 | [9 empty] | 24000
| Jodiac Power | 17 | 17 | 17 |  |  | 3 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 24 | 54 | 54 | 54 | 17 | 17 | 17 | 462458
| Karnaphuli Power Ltd. | 55 | 55 | 44 | 54 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 61 | 61 | 70 | 69 |  | 61 | 61 | 69 | 63 | 65 | 74 | 66 | 1442720
82 | Madanganj 102 PP(Summit) | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 85 | 67 | 62 | 62 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1957633
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 56 | 56 | 57 | 44 | 46 | 41 | 43 | 32 | 23 | 32 | 33 | 34 | 34 | 33 | 34 | 44 | 54 | 56 |  | 55 | 55 | 56 | 56 | 56 | 56 | 43 | 1114363
86 | Meghnaghat CCPP ( Summit) | [25 empty] | 10 | 2676
87 | Meghnaghat 100 MW(IEL) | 30 | 32 | 33 | 33 | 32 | 33 | 32 | 32 | 33 | 38 | 46 | 48 | 48 | 55 | 52 | 48 | 48 | 48 |  | 48 | 48 | 46 | 48 | 43 | 36 | 33 | 963840
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 42 | 54 | 55 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 17 | 804480
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 510840
92 | Fenchuganj 44 MW (Energyprima) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 39 | 42 | 42 | 39 | 36 | 36 | 34 | 32 | 36 | 35 | 34 |  | 37 | 39 | 41 | 41 | 41 | 42 | 42 | 939744
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1140372
94 | Gagnagar 102 MW PP (Digital Power) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 42 | 50 | 50 | 50 | 50 | 50 | 50 | 42 |  | 42 | 42 | 42 | 42 | 16 | 16 | 16 | 792720
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 10 | 40 | 47 |  | 47 | 50 |  | 45 | 50 | 50 | 50 | 415200
96 | Chattogram 108 MW PP (ECPV) | [15 empty] | 6 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 |  | 0 | 83520
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 14 | 24 | 55 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 416663
100 | Manikganj 55 MW PP (Northern) | [9 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 |  | 0 | 444402
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 80 | 80 | 80 | 112 | 80 | 80 | 112 | 112 | 112 | 80 |  | 112 | 112 | 112 | 112 | 112 | 112 | 80 | 2436955
102 | Sarishabari 3 MW Solar Plant | [7 empty] | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 15050
103 | Kamalaghat 54 MW PP(Banco Energy) | [9 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 389520
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 67 | 67 | 67 | 66 | 66 | 67 | 67 | 67 | 67 | 66 | 113 | 114 | 114 | 114 | 113 | 67 | 67 | 67 |  | 160 | 160 | 160 | 160 | 160 | 66 | 65 | 2212800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 19 | 94 | 105 | 105 | 105 | 103 | 37 | 15 | 17 | 15 | 17 |  | 43 | 106 | 105 | 105 | 105 | 50 | 24 | 1203120
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 12 | 12 | 23 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 12 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 558720
116 | Chandpur 200 MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 32 | 72 | 105 | 78 | 17 | 17 | 17 | 29 |  | 34 | 34 | 34 | 48 | 54 | 52 | 32 | 804480
117 | Ashuganj 150 MW PP (Midland) | 6 | 6 | 5 | 6 | 5 | 5 | 5 | 6 | 5 | 5 | 6 | 5 | 5 | 5 | 5 | 5 | 6 | 15 |  | 13 | 32 | 31 | 35 | 30 | 20 | 12 | 252581
118 | Bibiyana-III 400 MW CCPP | 367 | 367 | 370 | 367 | 367 | 367 | 367 | 368 | 378 | 318 | 292 | 366 | 343 | 344 | 368 | 370 | 367 | 381 |  | 367 | 368 | 404 | 368 | 366 | 371 | 368 | 8786000
| Jamalpur 115 MW PP (United) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 37 | 36 | 36 | 36 | 35 | 18 | 18 | 28 |  | 83 | 84 | 84 | 84 | 84 | 18 | 18 | 810000
| Anwara 300 MW PP (United) | 68 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 103 | 105 | 107 | 106 | 106 | 69 | 69 | 102 |  | 256 | 256 | 260 | 264 | 88 | 87 | 88 | 2448873
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 606720
| Anlima Energy Ltd. | 19 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 36 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 779073
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 6 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 424800
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 7 | 16 | 25 | 29 | 33 | 34 | 32 | 28 | 25 | 2 | 2 | 0 | [8 empty] | 225204
| Chandpur 115(Doreen) | [25 empty] | 0 | 0
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 15 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 430200
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 21 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 87 | 123 | 159 | 159 | 159 | 159 | 17 | 1333163
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 6 | 2 | 7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 3 | [5 empty] | 2 | 3 | 15 | 2 | 4 | 51360
Matarbari 2*600 MW (CPGCL)
120 | Eastern Zone Total | 6491 | 6411 | 6484 | 6434 | 6460 | 6139 | 6124 | 6137 | 6464 | 6622 | 7219 | 7538 | 7678 | 7388 | 7241 | 6534 | 6726 | 6621 |  | 7614 | 7740 | 7792 | 7903 | 7684 | 7293 | 6648 | 164907528
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 44 | 46 | 46 | 46 | 46 | 46 | 48 | 32 | 32 | 47 | 46 | 61 | 61 | 62 | 46 | 77 | 77 | 79 |  | 96 | 80 | 80 | 80 | 80 | 80 | 80 | 1387200
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL) | 356 | 356 | 352 | 355 | 356 | 353 | 364 | 364 | 362 | 362 | 363 | 361 | 349 | 350 | 345 | 349 | 330 | 349 |  | 345 | 352 | 354 | 355 | 354 | 355 | 357 | 8222207
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 13 | 9 | 9 | 9 | 9 | 9 | 13 | 36 |  | 47 | 28 | 25 | 25 | 25 | 25 | 16 | 336000
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 420480
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 1 | 7 | 15 | 38 | 66 | 48 | 86 | 83 | 69 | 39 | 24 | 2 | [8 empty] | 461520
131 | Rampal 1320 MW (BIFPCL) | 518 | 519 | 521 | 521 | 521 | 520 | 521 | 520 | 520 | 523 | 521 | 521 | 520 | 519 | 518 | 520 | 518 | 548 |  | 568 | 568 | 571 | 571 | 572 | 572 | 570 | 12727270
132 | United Payra Power Ltd. | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 136 | 150 | 150 | 150 | 150 | 150 | 150 | 1507200
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 220 | 220 | 220 | 220 | 220 | 220 | 213 |  | 216 | 217 | 217 | 220 | 220 | 220 | 220 | 5198836
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 32 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 612384
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 128 | 130 | 130 | 110 | 130 | 130 | 130 | 130 | 130 | 80 | 76 | 124 | 124 | 124 | 126 | 126 | 100 | 124 |  | 126 | 126 | 126 | 126 | 126 | 130 | 128 | 2901000
140 | Bhola 33 MW PP (Venture) | 33 | 32 | 32 | 31 | 31 | 25 | 7 | 19 | 18 | 17 | 20 | 22 | 23 | 24 | 25 | 25 | 24 | 22 |  | 30 | 30 | 29 | 34 | 35 | 34 | 34 | 635236
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 32 | 32 | 40 | 32 | 32 | 32 | 32 | 32 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 903750
143 | Gopalganj 100 MW Peaking PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 13 | 12 | 12 | 12 | [8 empty] | 12 | 20 | 35 | 16 | 15 | 15 | 16 | 270336
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 923 | 924 | 925 | 925 | 927 | 926 | 889 | 889 | 889 | 927 | 926 | 927 | 927 | 926 | 923 | 924 | 921 | 922 |  | 919 | 919 | 804 | 804 | 803 | 804 | 804 | 21640727
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1230 | 1200 | 1200 | 1244 | 1244 | 1244 | 1244 | 1244 | 1210 | 1140 |  | 1190 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 31424000
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 180 | 180 | 180 | 180 | 180 | 170 | 170 | 170 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4314000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 0 | 180320
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 4 | 5 | 5 | 5 | 5 | 5 | 4 | 2 | 1 | 0 | [8 empty] | 40560
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 152 | 154 | 157 | 158 | 159 | 160 | 161 | 159 | 155 | 150 | 149 | 148 | 149 | 147 | 147 | 147 | 148 | 148 |  | 153 | 156 | 156 | 158 | 158 | 157 | 158 | 3903882
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 128 | 131 | 131 | 131 | 135 | 136 | 136 | 134 | 129 | 128 | 126 | 125 | 124 | 125 | 124 | 123 | 123 | 129 |  | 129 | 131 | 131 | 134 | 135 | 135 | 135 | 3369364
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 265 | 275 | 286 | 296 | 308 | 314 | 303 | 299 | 275 | 276 | 265 | 253 | 248 | 229 | 223 | 242 | 257 | 261 |  | 295 | 304 | 304 | 312 | 324 | 325 | 329 | 6707636
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 4 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 74007
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 184680
165 | Amnura 50 MW PP(Sinha) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 661500
166 | Katakhali 50 MW PP (Northern) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 25 | 34 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 667251
167 | Katakhali 50 MW Peaking PP | 23 | 0 | [17 empty] | 26 | 31 | 39 | 39 | 39 | 39 | 38 | 201995
168 | Santahar 50 MW Peaking PP | [19 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 109152
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 52 | 52 | 52 | 52 | 8 | 8 | 8 | 299496
170 | Chapainawabganj 100 MW Peaking PP | 84 | 84 | 84 | 48 | 48 | 48 | 48 | 47 | 47 | 47 | 46 | 46 | 46 | 46 | 46 | 53 | 46 | 46 |  | 63 | 90 | 90 | 91 | 91 | 91 | 91 | 1436624
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 |  |  |  | 3 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 39 | 50 |  | 50 | 50 | 50 | 68 | 70 | 70 | 35 | 934944
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 |  |  |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 50 | 55 | 55 |  | 55 | 55 | 70 | 75 | 75 | 75 | 35 | 967104
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 35 | 35 | 39 | 34 | 34 | 20 | 30 | 39 | 54 |  | 64 | 61 | 62 | 62 | 63 | 34 | 34 | 952521
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 3 | 5 | 6 | 6 | 7 | 5 | 7 | 5 | 4 | 2 | 1 | [8 empty] | 52901
178 | Energypac Power Venture Thakurgaon Ltd. | [9 empty] | 18 | 35 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 70 | 75 | 75 | 75 | 75 |  | 0 | 633062
| Intraco Solar 30 MW | [5 empty] | 0 | 6 | 15 | 24 | 30 | 35 | 36 | 35 | 32 | 20 | 16 | 6 | 1 | [8 empty] | 256861
| Adani Power Jharkhanda Ltd | 1464 | 1471 | 1454 | 1446 | 1412 | 1363 | 1358 | 1366 | 1362 | 1359 | 1364 | 1361 | 1359 | 1365 | 1362 | 1360 | 1361 | 1311 |  | 1411 | 1413 | 1421 | 1462 | 1456 | 1449 | 1405 | 33391636
178 | Teesta Solar Limited | [5 empty] | 3 | 33 | 82 | 123 | 158 | 176 | 178 | 174 | 159 | 127 | 82 | 45 | 8 | [8 empty] | 1346060