## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-09-09 | Saturday
|  | Date (day): | 2023-09-09 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12817.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14857 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-09-08 | 2023-09-09 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 130 | 200 | 200 | 200
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  |  | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 80 | 77 | 75 | 77 | 31 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 323 | 396 | 412 | 412
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 290 | 343 | 330 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 370 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 66 | 32 | 33 | 67 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 5 | 0 | 0 |  | 335 | Under maint.
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 17 | 26 | 80 | 80 |  | 22 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 15 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 20 | 40 | 45 | 30 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 16 | 19 | 19
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 39 | 97 | 100 | 100 |  | 110 | GT-2 Under S/D
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 9 | 20 | 16 | 20 |  | 80 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 322 | 328 | 330 | 330
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 8 | 8 | 16 | 86 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 82 | 64 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 55 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 29 | 38 | 38 | 38 |  | 42 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 32 | 32 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 25 | 8 | 25 | 27 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 15 | 63 | 84 | 130 | 170 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
33 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
34 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 145 | 17 | 149
35 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 70 | 70 | 105
36 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 17 | 17 | 87 |  | Fuel shortage
37 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 54 | 54 | 108 | 54 |  | Fuel shortage
38 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 12 | 0 | 35 | 0
39 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 6063 | 5722 | 1934 | 2759 | 2676 | 3049 | 855 | 1357
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 105 | 110 | 110 |  | 70
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
41 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 17 | 8 | 17 | 8 |  | Fuel shortage
42 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 2 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 6 | 6 | 50
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 202 | 199 | 195 | 199
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 224 | 225 | 225 | 225
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 17 | 17 | 88 |  | Fuel shortage
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 30 | 49 | 32 | 60 | 38 |  | Fuel shortage
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 | 102 |  | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 13 | 12 | 12 | 12 | 10 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 32 | 42 | 10 | 30
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 30 | 264 | 70 | 265 | 35 |  | Fuel shortage
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 54 | 17 | 54
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 55 | 66 | 55 | 55 | 55 |  | Fuel shortage
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 34 | 34 | 34 | 34 | 82 |  | Fuel shortage
60 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 160 | 17 | 158 | 5
| SS Power I |  | Coal | SS Power | 0 | 0 | 0 | 557 | 0 | 0 | 0 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 1 | 4 | 10 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 2605 | 2545 | 1409 | 1329 | 918 | 1371 | 756 | 400
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 197 | 204 | 200 | 200 | 21 |  | Gas shortage
62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 165 | 320 | 360
63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 305 | 300 | 300 |  |  | FGMO
64 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 45 | 49 | 49 | 49
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 158 | 197 | 190 | 195
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
69 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 20 | 150 | 13 | 150
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 |  | 52 | Under Maint.
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
72 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 72 | 104 | 68 | 100 | 100 |  | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 18 | 16 | 18 |  | 4 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 128 | 160 | 149 | 165
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 46 | 51 | 51
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 17 | 34 | 70 |  | 8 | Engine problem
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 27 | 78 | 28 | 75 | 38 |  | Fuel shortage
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 0 | 0 | 115 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2896 | 1106 | 1617 | 1542 | 1857 | 274 | 677
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 35 | 99 | 70 | 100 | 102 |  | Gas shortage
83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 16 | 16 | 16 |  | 6 | Engine problem
84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 87 | 163 | 115 | 150 | 50 |  | Fuel shortage
87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 0 | 85 | 37 | 95 | 20 |  | Fuel shortage
88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 36 | 0 | 50 | 0
89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 181 | 369 | 295.6 | 367 | 102 | 6
90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 40 | 40 |  | 50 | Machine problem
92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 80 | 112 | 112 | 112 |  | 51 | ST Under maint.
93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 22 | 50 | 50 | 50
95 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 42 | 40 | 40 | 40 |  | 10 | Engine problem
96 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 5 | 11 | 11
97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 59 | 60 | 60
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 86 | 86 | 86
99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 185 | 184 | 185 | 185 |  | 46 | Machine problem
101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 16 | 17 | 17 | 17
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 9 |  | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 290 | 300 | 300 |  |  | FGMO
104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 317 | 369 | 400 | 400 |  |  | FGMO
105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 50 | 143 | 50 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1237 | 1451 | 1407 | 1757 | 9 | 627
107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 920 | 778 | 938 | 938
108 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 16 | 66 | 98
109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 10 | 25 | 40 |  | 14 | Engine problem
110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 10 | 40 | 50 | 59 |  | Fuel shortage
112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
113 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 24 | 40
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
114 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 35 | 17 | 51 | 54 |  | Fuel shortage
115 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 33 | 0 | 100 | 0
117 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 220 | 220 | 128 | 122 | 120 | 120
118 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 517 | 402 | 400 | 450 | 167
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3125 | 3121 | 1614 | 1381 | 1730 | 1787 | 1041 | 14
119 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 16 | 48
120 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 19 | 27 | 23 | 30 |  | 10 | Engine problem
121 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 80 | 130 | 132 | 132 |  | 62 | ST under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
122 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1000 | 1244 | 1244 | 1244
123 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 180 | 110 | 110 | 110
124 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 72 | 35 | 150
125 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 | 307 |  | Coal shortage
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1296 | 1583 | 1560 | 1714 | 307 | 72
126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 35 | 0 | 35 | 17 |  | Fuel shortage
128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 21 | 0 | 21 |  | 50 | Engine problem
129 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 28 | 28
130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 8 | 34 | 42 | 8 |  | Fuel shortage
131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 30 | 40 | 10 |  | Fuel shortage
132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 161 | 164 | 160 | 160 | 50 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 156 | 140 | 160 | 80 |  | Gas shortage
135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 300 | 387 | 414 | 414
136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 24 | 24 | 24 | 26 |  | Fuel shortage
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 52
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 34 | 50 | 91 | 13 |  | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 70 | 35 | 70 | 43 |  | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 75 | 35 | 75 | 38 |  | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 0 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 919 | 1362 | 1300 | 1400
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 1598 | 2383 | 2272 | 2620 | 876 | 53
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 180 | 180 | 180 | 180 |  | 94 | Machine problem
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 94 | 34 | 80 | 33 |  | Fuel shortage
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 113 | 35 | 75 | 40 |  | Fuel shortage
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 11 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 15 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 210 | 387 | 417 | 335 | 198 | 179
| Total |  |  |  |  | 24911 | 24171 | 10585 | 13259 | 12817.6 | 14857 | 4418 | 3385
A. |  | 2023-09-08 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 13259 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 10221 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13300 | MW
3 | Day peak Generation : |  |  | 10585 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12680.49 | MW
4 | Evening peak Generation : |  |  | 13259 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 39 | MW
5 | Total Energy Generation : |  | 278.0544 | MKWHr | By Solar | 1.2068 | MKWHr
| By Gas : | 130.8026 | MKWHr |  | By Oil: | 37.5379 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 78.8857 | MKWHr |  | By Hydro: | 4.3615 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.15024 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4418 | MW | Dhaka | 4265.49 | 4265.49 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3385 | MW | Chittagong | 1295.2 | 1295.2 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 7803 | MW | Khulna | 1581.4 | 1581.4 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 1070.15 | MMCFD |  |  | Rajshahi | 1323.2 | 1323.2 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 152840130.566 | ii) Oil : | Taka | 441214558.28 | Comilla | 1253 | 1253 |  | 0 |  | 21:00 |  | 39
|  | iii) Coal : | Taka | 619316584.35 | Total | Taka | 1213371273.196 | Mymensingh | 1143 | 1104 |  | 39 |  | 22:00 |  | 53.48
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 549 | 549 |  | 0 |  | 23:00 |  | 251.165
| ii) During Peak Demand : |  |  | 1130 | MW (E to W) at | 21:00 | hrs | Barisal | 397.2 | 397.2 |  | 0 |  | 24:00 |  | 419.245
| iii) Maximum : |  |  | 1030 | MW at | 20:00 | hrs | Rangpur | 873 | 873 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 32.5°C |  |  | Total | 12680.49 | 12641.49 |  | 39
B. |  | 2023-09-09 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 32.5°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 14300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14857 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 12000 | MW
4 | Reserve(Generation end) |  |  |  | 557 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 299.8852 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10895 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.8764 | MKWHr. | ii) HVDC Flow at Peak Time |  | 778 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.2333 | MKWHr. | iii) Maximum HVDC Flow : |  | 922 | MW at | 7:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 106.17 |  | (b) Today: | 106.36 |  | (c) Rule Curve: |  | 100.84
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-09-08 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 180 | 0 | 0 | 74 | 0 | 410 | 332 |  | 0 | 450 | 27 | 8 | 82 | 15 | 326 | 0 | 93 | 9 | 16 | 16 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 33 | 32 | 8 | 0 | 129 | 75 | 110 | 0 | 8 | 222 | 0 | 0 | 0 |  | 6 | 42 | 0 | 25 | 0 | 6 | 13 | 38 | 0 | 0 | 0 | 0 | 330 | 194 | 199 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 52 | 16 | 0 | 33 | 12 | 152 | 81 | 0 | 16 | 0 | 30 | 39 | 50 | 43 | 112 | 0 | 61 | 78 | 0 | 182 | 17 | 0 | 10 | 305 | 16 | 5 | 0 | 45 | 0 | 0 | 68 | 0 | 17 | 0 | 25 | 34 | 35 | 385 | 18 | 35 | 17 | 0 | 69 | 17 | 48 | 17 | 15 | 25 | 15 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 155 | 12 | 0 | 0 |  | 921 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 19 | 20 | 24 | 130 | 31 | 16 | 0 | 0 | 0 | 35 | 0 | 0 | 28 | 42 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 352 | 53 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 1244 | 221 | 0 | 35 | 0 | 0 | 0 | 120 | 0 | 521 | 0 | 0 | 1407 | 0 | 0 |  | 6164 | 5894 | 12058 | 3389 | 921 | 2373 | 0 | 1231 | 3507 | 204 | 120 | 149 | 152 | 0 | 12 | 1377.11 | 106.15
2:00 | 0 | 0 | 180 | 0 | 0 | 75 | 0 | 410 | 332 |  | 0 | 450 | 27 | 8 | 82 | 15 | 327 | 0 | 94 | 9 | 16 | 16 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 25 | 32 | 8 | 0 | 129 | 75 | 113 | 0 | 8 | 222 | 0 | 0 | 0 |  | 6 | 42 | 0 | 25 | 0 | 6 | 13 | 38 | 0 | 0 | 0 | 0 | 320 | 182 | 199 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 52 | 16 | 11 | 33 | 12 | 148 | 80 | 0 | 16 | 0 | 30 | 39 | 47 | 43 | 112 | 0 | 61 | 78 | 0 | 184 | 17 | 0 | 10 | 300 | 16 | 5 | 0 | 45 | 0 | 0 | 67 | 0 | 17 | 0 | 25 | 34 | 26 | 370 | 18 | 35 | 17 | 0 | 69 | 17 | 48 | 17 | 9 | 25 | 25 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 232 | 11 | 0 | 0 |  | 921 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 10 | 0 | 24 | 130 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 42 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 361 | 53 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 1244 | 222 | 0 | 35 | 0 | 0 | 0 | 120 | 0 | 524 | 0 | 0 | 1382 | 0 | 0 |  | 6193 | 5813 | 12006 | 3370 | 921 | 2372 | 0 | 1213 | 3562 | 204 | 120 | 85 | 148 | 0 | 11 | 1235.77 | 106.15
3:00 | 0 | 0 | 210 | 0 | 0 | 76 | 0 | 411 | 332 |  | 0 | 450 | 44 | 8 | 82 | 15 | 328 | 0 | 94 | 9 | 16 | 16 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 25 | 32 | 8 | 0 | 130 | 75 | 105 | 0 | 8 | 224 | 0 | 0 | 0 |  | 6 | 42 | 0 | 25 | 0 | 6 | 13 | 38 | 0 | 0 | 0 | 0 | 305 | 180 | 199 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 51 | 16 | 11 | 33 | 12 | 142 | 80 | 0 | 16 | 0 | 30 | 39 | 47 | 43 | 112 | 0 | 61 | 78 | 0 | 184 | 17 | 0 | 10 | 300 | 16 | 5 | 0 | 45 | 0 | 0 | 68 | 0 | 17 | 0 | 25 | 34 | 26 | 368 | 18 | 35 | 17 | 0 | 69 | 0 | 44 | 17 | 9 | 25 | 40 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 280 | 11 | 0 | 0 |  | 921 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 10 | 0 | 24 | 130 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 42 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 370 | 53 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1244 | 222 | 0 | 35 | 0 | 0 | 0 | 121 | 0 | 524 | 0 | 0 | 1272 | 0 | 0 |  | 6255 | 5638 | 11893 | 3393 | 921 | 2395 | 0 | 1120 | 3500 | 205 | 121 | 85 | 142 | 0 | 11 | 1152.685 | 106.16
4:00 | 0 | 0 | 209 | 0 | 0 | 76 | 0 | 414 | 332 |  | 0 | 450 | 43 | 8 | 82 | 15 | 327 | 0 | 95 | 9 | 16 | 16 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 25 | 32 | 8 | 0 | 130 | 75 | 105 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 42 | 0 | 25 | 0 | 6 | 13 | 38 | 0 | 0 | 0 | 0 | 305 | 177 | 197 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 51 | 16 | 11 | 33 | 12 | 130 | 79 | 0 | 16 | 0 | 30 | 39 | 47 | 43 | 112 | 0 | 61 | 78 | 0 | 184 | 17 | 0 | 10 | 280 | 16 | 5 | 0 | 45 | 0 | 0 | 68 | 0 | 17 | 0 | 25 | 34 | 25 | 368 | 19 | 35 | 17 | 0 | 69 | 0 | 55 | 17 | 9 | 25 | 50 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 370 | 8 | 0 | 0 |  | 920 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 10 | 0 | 24 | 130 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 42 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 376 | 53 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1244 | 223 | 0 | 35 | 0 | 0 | 0 | 122 | 0 | 522 | 0 | 0 | 1053 | 0 | 0 |  | 6329 | 5429 | 11758 | 3406 | 920 | 2380 | 0 | 1133 | 3369 | 205 | 122 | 85 | 130 | 0 | 8 | 995.11 | 106.16
5:00 | 0 | 0 | 210 | 0 | 0 | 77 | 0 | 411 | 332 |  | 0 | 450 | 3 | 8 | 82 | 15 | 327 | 0 | 93 | 9 | 16 | 16 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 25 | 32 | 8 | 0 | 130 | 75 | 107 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 42 | 0 | 25 | 0 | 6 | 13 | 40 | 0 | 0 | 0 | 0 | 325 | 193 | 197 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 51 | 16 | 11 | 33 | 12 | 126 | 82 | 0 | 16 | 0 | 30 | 39 | 47 | 43 | 112 | 0 | 61 | 75 | 0 | 184 | 17 | 0 | 10 | 300 | 16 | 5 | 0 | 45 | 0 | 0 | 68 | 0 | 17 | 0 | 25 | 34 | 26 | 382 | 19 | 35 | 17 | 0 | 69 | 0 | 55 | 17 | 9 | 25 | 50 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 385 | 27 | 0 | 0 |  | 921 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 10 | 0 | 24 | 130 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 388 | 53 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1244 | 220 | 0 | 35 | 0 | 0 | 0 | 122 | 0 | 522 | 0 | 0 | 911 | 0 | 0 |  | 6391 | 5291 | 11682 | 3458 | 921 | 2369 | 0 | 1127 | 3242 | 205 | 122 | 85 | 126 | 0 | 27 | 781.19 | 106.17
6:00 | 0 | 0 | 130 | 0 | 0 | 75 | 0 | 413 | 302 |  | 0 | 450 | 0 | 8 | 82 | 15 | 305 | 0 | 95 | 9 | 16 | 16 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 25 | 31 | 8 | 0 | 129 | 75 | 111 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 42 | 0 | 25 | 0 | 6 | 13 | 42 | 0 | 0 | 0 | 0 | 275 | 177 | 197 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 51 | 16 | 11 | 33 | 12 | 100 | 83 | 0 | 16 | 0 | 30 | 39 | 44 | 43 | 80 | 0 | 60 | 75 | 0 | 184 | 17 | 0 | 10 | 270 | 16 | 5 | 0 | 45 | 0 | 0 | 68 | 0 | 17 | 0 | 25 | 34 | 26 | 319 | 19 | 35 | 17 | 0 | 69 | 1 | 55 | 17 | 8 | 25 | 50 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 480 | 11 | 0 | 0 |  | 920 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 10 | 0 | 24 | 70 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 340 | 53 | 0 | 27 | 0 | 34 | 0 | 0 | 35 | 1200 | 222 | 0 | 35 | 0 | 0 | 0 | 113 | 0 | 522 | 0 | 0 | 922 | 0 | 0 |  | 6121 | 5204 | 11325 | 3176 | 920 | 2223 | 0 | 1189 | 3304 | 204 | 113 | 85 | 100 | 0 | 11 | 358.125 | 106.17
7:00 | 0 | 0 | 130 | 0 | 0 | 75 | 0 | 345 | 302 |  | 0 | 400 | 0 | 9 | 80 | 15 | 280 | 0 | 95 | 9 | 16 | 16 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 25 | 32 | 8 | 0 | 73 | 0 | 113 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 42 | 0 | 25 | 0 | 6 | 13 | 38 | 0 | 0 | 0 | 0 | 275 | 177 | 158 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 51 | 16 | 11 | 33 | 12 | 112 | 35 | 0 | 16 | 0 | 30 | 39 | 44 | 43 | 80 | 0 | 61 | 75 | 0 | 184 | 17 | 0 | 10 | 280 | 16 | 11 | 0 | 45 | 0 | 0 | 68 | 0 | 17 | 0 | 25 | 34 | 26 | 319 | 19 | 35 | 17 | 1 | 69 | 17 | 55 | 17 | 9 | 25 | 50 | 17 | 1 | 17 | 17 | 0 | 17 | 5 | 0 | 17 | 0 | 17 | 0 | 600 | 5 | 0 | 0 |  | 922 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 8 | 80 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 340 | 17 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 1050 | 222 | 0 | 35 | 0 | 3 | 0 | 122 | 0 | 522 | 3 | 0 | 918 | 12 | 0 |  | 5920 | 4943 | 10863 | 3056 | 922 | 2137 | 0 | 1066 | 3270 | 73 | 122 | 75 | 112 | 25 | 5 | 188.135 | 106.18
8:00 | 0 | 0 | 130 | 0 | 0 | 75 | 0 | 344 | 302 |  | 0 | 400 | 0 | 8 | 30 | 15 | 280 | 0 | 97 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 25 | 33 | 8 | 0 | 70 | 0 | 113 | 0 | 0 | 226 | 0 | 0 | 0 |  | 6 | 32 | 0 | 25 | 0 | 6 | 13 | 38 | 0 | 0 | 0 | 0 | 275 | 177 | 160 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 51 | 13 | 11 | 33 | 12 | 96 | 35 | 0 | 16 | 0 | 30 | 39 | 44 | 43 | 80 | 0 | 61 | 75 | 0 | 185 | 17 | 0 | 10 | 280 | 16 | 11 | 0 | 15 | 0 | 0 | 68 | 0 | 17 | 0 | 25 | 34 | 25 | 319 | 19 | 35 | 17 | 1 | 70 | 17 | 55 | 17 | 9 | 25 | 50 | 17 | 13 | 17 | 17 | 0 | 17 | 7 | 0 | 17 | 0 | 0 | 0 | 490 | 0 | 0 | 0 |  | 921 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 80 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 340 | 17 | 0 | 35 | 0 | 0 | 0 | 1 | 35 | 1050 | 180 | 0 | 17 | 0 | 6 | 0 | 124 | 0 | 524 | 4 | 0 | 917 | 32 | 0 |  | 5649 | 4816 | 10465 | 3058 | 921 | 2096 | 0 | 827 | 3161 | 70 | 124 | 48 | 96 | 64 | 0 | 100.275 | 106.19
9:00 | 0 | 0 | 130 | 0 | 0 | 72 | 0 | 344 | 304 |  | 0 | 360 | 0 | 8 | 17 | 15 | 280 | 0 | 62 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 25 | 33 | 8 | 0 | 70 | 0 | 109 | 0 | 0 | 226 | 0 | 0 | 0 |  | 6 | 33 | 0 | 25 | 0 | 6 | 13 | 38 | 0 | 0 | 0 | 0 | 275 | 177 | 160 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 24 | 13 | 11 | 33 | 12 | 96 | 34 | 0 | 16 | 1 | 30 | 40 | 44 | 40 | 80 | 0 | 61 | 75 | 0 | 185 | 17 | 0 | 10 | 285 | 16 | 11 | 0 | 15 | 0 | 0 | 67 | 0 | 17 | 1 | 25 | 34 | 26 | 319 | 19 | 17 | 17 | 1 | 70 | 17 | 55 | 17 | 9 | 25 | 50 | 17 | 7 | 17 | 17 | 0 | 17 | 6 | 0 | 17 | 0 | 0 | 0 | 365 | 0 | 0 | 0 |  | 922 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 340 | 0 | 0 | 35 | 0 | 0 | 0 | 1 | 35 | 1040 | 180 | 0 | 17 | 0 | 18 | 0 | 124 | 0 | 521 | 18 | 0 | 916 | 65 | 0 |  | 5384 | 4837 | 10221 | 3019 | 922 | 2057 | 0 | 744 | 3022 | 70 | 124 | 49 | 96 | 118 | 0 | 71.625 | 106.2
10:00 | 0 | 0 | 130 | 0 | 0 | 75 | 0 | 344 | 303 |  | 0 | 360 | 0 | 9 | 17 | 15 | 280 | 0 | 60 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 19 | 19 | 18 | 25 | 33 | 8 | 0 | 122 | 75 | 113 | 0 | 0 | 228 | 0 | 0 | 0 |  | 6 | 33 | 0 | 25 | 0 | 6 | 13 | 37 | 0 | 0 | 0 | 0 | 275 | 177 | 160 | 0 | 45 | 0 | 0 | 51 | 0 | 0 | 24 | 0 | 11 | 33 | 12 | 114 | 34 | 0 | 16 | 1 | 30 | 40 | 44 | 40 | 80 | 0 | 61 | 75 | 0 | 185 | 17 | 0 | 10 | 280 | 16 | 11 | 0 | 15 | 0 | 0 | 68 | 0 | 17 | 3 | 25 | 52 | 21 | 319 | 19 | 17 | 17 | 2 | 70 | 17 | 55 | 17 | 9 | 25 | 50 | 17 | 10 | 17 | 18 | 0 | 17 | 11 | 0 | 17 | 0 | 0 | 0 | 264 | 12 | 0 | 0 |  | 921 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 340 | 0 | 0 | 35 | 0 | 0 | 0 | 3 | 35 | 1040 | 180 | 0 | 17 | 0 | 23 | 0 | 124 | 0 | 523 | 15 | 0 | 910 | 60 | 0 |  | 5515 | 4820 | 10335 | 2994 | 921 | 2053 | 0 | 794 | 2917 | 197 | 124 | 81 | 114 | 128 | 12 | 0 | 106.21
11:00 | 0 | 0 | 130 | 0 | 0 | 76 | 0 | 344 | 273 |  | 0 | 360 | 0 | 8 | 17 | 15 | 280 | 0 | 60 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 5 | 19 | 19 | 18 | 25 | 32 | 8 | 0 | 127 | 75 | 113 | 0 | 0 | 226 | 0 | 0 | 0 |  | 6 | 24 | 0 | 25 | 0 | 6 | 13 | 32 | 0 | 0 | 0 | 0 | 275 | 177 | 158 | 0 | 45 | 0 | 0 | 51 | 0 | 0 | 8 | 0 | 11 | 33 | 12 | 124 | 34 | 0 | 16 | 1 | 30 | 40 | 22 | 39 | 80 | 0 | 61 | 78 | 0 | 185 | 16 | 0 | 10 | 275 | 16 | 11 | 0 | 15 | 0 | 0 | 86 | 0 | 17 | 12 | 25 | 70 | 18 | 319 | 0 | 17 | 17 | 3 | 30 | 17 | 55 | 17 | 17 | 25 | 50 | 17 | 20 | 17 | 34 | 0 | 17 | 19 | 0 | 17 | 0 | 0 | 0 | 426 | 2 | 0 | 0 |  | 921 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 300 | 0 | 0 | 35 | 0 | 0 | 0 | 4 | 35 | 1020 | 180 | 0 | 17 | 0 | 23 | 0 | 122 | 0 | 520 | 11 | 0 | 912 | 86 | 0 |  | 5640 | 4790 | 10430 | 3000 | 921 | 1952 | 0 | 798 | 3058 | 202 | 122 | 72 | 124 | 179 | 2 | 0 | 106.22
12:00 | 0 | 0 | 130 | 0 | 0 | 80 | 0 | 323 | 290 |  | 0 | 370 | 0 | 8 | 17 | 15 | 322 | 0 | 39 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 19 | 10 | 25 | 32 | 8 | 0 | 127 | 75 | 110 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 30 | 0 | 25 | 0 | 6 | 13 | 32 | 0 | 0 | 0 | 0 | 310 | 197 | 158 | 0 | 45 | 0 | 0 | 51 | 0 | 0 | 8 | 0 | 11 | 33 | 12 | 128 | 35 | 0 | 16 | 1 | 30 | 40 | 22 | 42 | 80 | 0 | 60 | 78 | 0 | 185 | 16 | 0 | 10 | 280 | 16 | 11 | 0 | 15 | 0 | 0 | 87 | 0 | 17 | 2 | 25 | 72 | 20 | 317 | 0 | 17 | 17 | 4 | 30 | 17 | 55 | 17 | 27 | 25 | 50 | 17 | 36 | 17 | 34 | 0 | 17 | 12 | 0 | 17 | 0 | 0 | 0 | 557 | 1 | 0 | 0 |  | 920 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 300 | 0 | 0 | 35 | 0 | 0 | 0 | 4 | 35 | 1000 | 180 | 0 | 17 | 0 | 33 | 0 | 128 | 0 | 517 | 11 | 0 | 919 | 15 | 0 |  | 5867 | 4718 | 10585 | 3020 | 920 | 1992 | 0 | 825 | 3173 | 202 | 128 | 78 | 128 | 118 | 1 | 0 | 106.23
13:00 | 0 | 0 | 130 | 0 | 0 | 80 | 0 | 400 | 332 |  | 0 | 420 | 0 | 9 | 17 | 15 | 321 | 0 | 94 | 12 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 15 | 19 | 6 | 25 | 32 | 8 | 0 | 122 | 75 | 110 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 32 | 0 | 25 | 0 | 6 | 13 | 34 | 0 | 0 | 0 | 38 | 305 | 183 | 158 | 0 | 47 | 0 | 0 | 51 | 0 | 0 | 8 | 0 | 11 | 33 | 12 | 138 | 33 | 0 | 16 | 1 | 30 | 40 | 49 | 42 | 112 | 0 | 60 | 78 | 0 | 185 | 17 | 0 | 10 | 310 | 8 | 11 | 0 | 15 | 0 | 0 | 87 | 0 | 17 | 3 | 25 | 75 | 18 | 367 | 0 | 17 | 17 | 2 | 30 | 17 | 55 | 17 | 30 | 25 | 50 | 17 | 22 | 17 | 34 | 0 | 17 | 16 | 0 | 17 | 0 | 0 | 0 | 554 | 0 | 0 | 0 |  | 921 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 346 | 0 | 0 | 35 | 0 | 0 | 0 | 5 | 35 | 1040 | 110 | 0 | 17 | 1 | 31 | 0 | 121 | 0 | 519 | 16 | 0 | 1022 | 118 | 0 |  | 6254 | 4937 | 11191 | 3220 | 921 | 2151 | 0 | 833 | 3315 | 197 | 121 | 80 | 138 | 215 | 0 | 0 | 106.24
14:00 | 0 | 0 | 130 | 0 | 0 | 80 | 0 | 406 | 302 |  | 0 | 370 | 0 | 8 | 17 | 15 | 260 | 0 | 38 | 17 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 16 | 19 | 6 | 25 | 32 | 8 | 0 | 124 | 75 | 113 | 0 | 0 | 226 | 0 | 0 | 0 |  | 6 | 32 | 0 | 25 | 0 | 6 | 13 | 42 | 0 | 0 | 0 | 10 | 270 | 176 | 158 | 0 | 46 | 0 | 0 | 51 | 0 | 0 | 8 | 0 | 11 | 33 | 12 | 124 | 33 | 0 | 16 | 0 | 30 | 40 | 50 | 42 | 80 | 0 | 61 | 78 | 0 | 185 | 17 | 0 | 10 | 220 | 16 | 11 | 0 | 15 | 0 | 0 | 88 | 0 | 17 | 3 | 25 | 78 | 20 | 368 | 0 | 17 | 17 | 1 | 30 | 17 | 55 | 17 | 28 | 25 | 40 | 17 | 23 | 17 | 34 | 0 | 17 | 8 | 0 | 17 | 0 | 0 | 0 | 557 | 0 | 0 | 0 |  | 920 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 300 | 0 | 0 | 35 | 0 | 0 | 0 | 5 | 35 | 1030 | 110 | 0 | 17 | 2 | 26 | 0 | 123 | 0 | 514 | 13 | 0 | 1024 | 125 | 0 |  | 5875 | 4878 | 10753 | 3042 | 920 | 1913 | 0 | 841 | 3305 | 199 | 123 | 80 | 124 | 206 | 0 | 0 | 106.22
15:00 | 0 | 0 | 130 | 0 | 0 | 77 | 0 | 377 | 281 |  | 0 | 370 | 0 | 8 | 17 | 15 | 260 | 0 | 38 | 17 | 25 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 16 | 19 | 6 | 25 | 32 | 8 | 0 | 124 | 75 | 105 | 0 | 1 | 226 | 0 | 0 | 0 |  | 6 | 31 | 10 | 25 | 0 | 6 | 13 | 33 | 0 | 0 | 0 | 10 | 275 | 173 | 158 | 0 | 47 | 0 | 0 | 51 | 0 | 0 | 9 | 8 | 0 | 33 | 12 | 132 | 34 | 0 | 16 | 0 | 30 | 40 | 50 | 42 | 80 | 0 | 61 | 78 | 0 | 185 | 17 | 0 | 10 | 295 | 16 | 11 | 0 | 17 | 0 | 0 | 87 | 0 | 17 | 4 | 25 | 77 | 18 | 317 | 0 | 35 | 17 | 2 | 66 | 17 | 55 | 17 | 29 | 25 | 42 | 17 | 27 | 24 | 34 | 0 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 612 | 4 | 0 | 0 |  | 921 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 250 | 0 | 0 | 35 | 0 | 0 | 0 | 3 | 35 | 1050 | 110 | 0 | 17 | 1 | 17 | 0 | 121 | 0 | 399 | 13 | 0 | 1090 | 95 | 0 |  | 6002 | 4762 | 10764 | 2960 | 921 | 1903 | 0 | 925 | 3331 | 199 | 121 | 106 | 132 | 162 | 4 | 0 | 106.26
16:00 | 0 | 0 | 130 | 0 | 0 | 75 | 0 | 374 | 282 |  | 0 | 400 | 0 | 40 | 28 | 15 | 300 | 0 | 62 | 17 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 16 | 19 | 6 | 25 | 16 | 8 | 0 | 124 | 75 | 108 | 0 | 8 | 223 | 0 | 0 | 0 |  | 6 | 31 | 0 | 25 | 0 | 6 | 13 | 33 | 0 | 0 | 0 | 10 | 275 | 150 | 158 | 0 | 48 | 0 | 0 | 51 | 0 | 0 | 24 | 16 | 0 | 33 | 12 | 130 | 34 | 0 | 16 | 0 | 30 | 40 | 50 | 43 | 80 | 0 | 60 | 81 | 0 | 186 | 17 | 0 | 10 | 295 | 16 | 11 | 0 | 35 | 0 | 0 | 87 | 0 | 17 | 2 | 25 | 72 | 20 | 322 | 0 | 35 | 17 | 1 | 66 | 17 | 55 | 17 | 29 | 25 | 50 | 17 | 11 | 54 | 34 | 0 | 17 | 9 | 0 | 17 | 0 | 0 | 0 | 0 | 4 | 0 | 0 |  | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1200 | 110 | 0 | 17 | 1 | 12 | 0 | 121 | 0 | 411 | 5 | 0 | 1110 | 85 | 0 |  | 5539 | 4884 | 10423 | 3009 | 920 | 1986 | 0 | 945 | 2901 | 199 | 121 | 79 | 130 | 129 | 4 | 0 | 106.27
17:00 | 0 | 0 | 130 | 0 | 0 | 75 | 0 | 375 | 282 |  | 0 | 400 | 0 | 12 | 17 | 15 | 300 | 0 | 61 | 17 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 16 | 19 | 6 | 25 | 32 | 8 | 0 | 124 | 75 | 109 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 48 | 0 | 25 | 0 | 6 | 12 | 42 | 0 | 0 | 0 | 10 | 275 | 150 | 158 | 0 | 48 | 0 | 0 | 51 | 0 | 0 | 21 | 16 | 0 | 33 | 12 | 130 | 34 | 0 | 17 | 0 | 30 | 40 | 50 | 43 | 112 | 0 | 61 | 86 | 0 | 183 | 17 | 0 | 10 | 300 | 16 | 11 | 0 | 15 | 0 | 0 | 87 | 0 | 17 | 1 | 25 | 70 | 28 | 363 | 0 | 28 | 17 | 0 | 69 | 17 | 55 | 17 | 34 | 25 | 85 | 17 | 2 | 17 | 34 | 0 | 17 | 3 | 0 | 17 | 0 | 0 | 0 | 0 | 6 | 0 | 0 |  | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1200 | 110 | 0 | 17 | 0 | 6 | 0 | 121 | 0 | 406 | 3 | 0 | 1105 | 17 | 0 |  | 5576 | 4796 | 10372 | 3104 | 922 | 2035 | 0 | 835 | 2891 | 199 | 121 | 96 | 130 | 33 | 6 | 0 | 106.28
18:00 | 0 | 0 | 130 | 0 | 0 | 79 | 0 | 357 | 292 |  | 0 | 330 | 0 | 8 | 17 | 15 | 270 | 0 | 39 | 17 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 16 | 19 | 6 | 25 | 32 | 8 | 0 | 124 | 75 | 114 | 0 | 8 | 222 | 0 | 0 | 0 |  | 6 | 64 | 0 | 25 | 0 | 6 | 12 | 42 | 0 | 0 | 0 | 40 | 310 | 150 | 158 | 0 | 48 | 0 | 0 | 51 | 0 | 0 | 26 | 16 | 0 | 33 | 12 | 130 | 45 | 0 | 16 | 0 | 30 | 40 | 50 | 43 | 80 | 0 | 60 | 86 | 0 | 183 | 17 | 0 | 10 | 280 | 16 | 11 | 0 | 15 | 0 | 0 | 87 | 0 | 17 | 0 | 25 | 68 | 42 | 404 | 0 | 35 | 17 | 0 | 65 | 17 | 55 | 17 | 36 | 25 | 100 | 17 | 0 | 17 | 34 | 0 | 17 | 0 | 0 | 17 | 0 | 7 | 0 | 0 | 1 | 0 | 0 |  | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 110 | 0 | 17 | 0 | 1 | 0 | 123 | 0 | 403 | 0 | 0 | 1114 | 0 | 0 |  | 5559 | 4753 | 10312 | 3168 | 921 | 1900 | 0 | 853 | 2897 | 199 | 123 | 119 | 130 | 1 | 1 | 0 | 106.29
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 200 | 0 | 0 | 79 | 0 | 390 | 271 |  | 0 | 450 | 5 | 28 | 42 | 15 | 280 | 0 | 36 | 18 | 50 | 149 | 17 | 0 | 0 | 0 | 35 | 35 | 35 | 16 | 19 | 6 | 25 | 32 | 18 | 0 | 124 | 75 | 108 | 0 | 17 | 227 | 0 | 0 | 0 |  | 6 | 66 | 0 | 25 | 0 | 6 | 12 | 42 | 0 | 0 | 0 | 90 | 300 | 205 | 197 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 47 | 16 | 11 | 33 | 12 | 152 | 58 | 0 | 16 | 0 | 30 | 40 | 50 | 43 | 80 | 0 | 61 | 86 | 0 | 184 | 17 | 0 | 10 | 300 | 16 | 8 | 0 | 85 | 0 | 0 | 142 | 0 | 92 | 0 | 25 | 84 | 77 | 319 | 94 | 63 | 17 | 0 | 255 | 22 | 55 | 17 | 68 | 25 | 111 | 17 | 0 | 80 | 34 | 0 | 17 | 0 | 0 | 17 | 0 | 88 | 0 | 0 | 1 | 0 | 0 |  | 921 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 45 | 11 | 32 | 130 | 25 | 32 | 0 | 0 | 0 | 35 | 5 | 35 | 0 | 42 | 32 | 52 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 300 | 5 | 0 | 22 | 0 | 72 | 0 | 0 | 70 | 1244 | 110 | 0 | 72 | 0 | 0 | 31 | 121 | 0 | 402 | 0 | 0 | 1324 | 0 | 0 |  | 6926 | 5741 | 12667 | 3377 | 921 | 2099 | 0 | 2157 | 3150 | 199 | 121 | 490 | 152 | 0 | 1 | 0 | 106.32
19:30 | 0 | 0 | 200 | 0 | 0 | 76 | 0 | 327 | 252 |  | 0 | 360 | 5 | 66 | 82 | 15 | 260 | 0 | 36 | 24 | 50 | 149 | 45 | 0 | 0 | 0 | 54 | 35 | 35 | 16 | 19 | 19 | 25 | 32 | 25 | 0 | 124 | 75 | 105 | 0 | 17 | 226 | 0 | 0 | 0 |  | 6 | 58 | 0 | 25 | 0 | 6 | 12 | 42 | 0 | 0 | 0 | 95 | 280 | 204 | 197 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 51 | 16 | 11 | 33 | 12 | 150 | 58 | 0 | 16 | 0 | 30 | 40 | 50 | 40 | 80 | 0 | 61 | 86 | 0 | 184 | 17 | 0 | 10 | 275 | 16 | 8 | 0 | 130 | 0 | 0 | 150 | 0 | 135 | 0 | 25 | 102 | 140 | 319 | 85 | 88 | 17 | 0 | 257 | 54 | 55 | 17 | 68 | 25 | 122 | 17 | 0 | 126 | 34 | 0 | 17 | 0 | 0 | 17 | 0 | 88 | 0 | 0 | 4 | 0 | 0 |  | 921 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 39 | 11 | 32 | 130 | 25 | 32 | 0 | 0 | 0 | 35 | 10 | 70 | 0 | 8 | 32 | 52 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 260 | 29 | 0 | 70 | 0 | 73 | 0 | 0 | 70 | 1244 | 110 | 0 | 135 | 0 | 0 | 72 | 123 | 0 | 403 | 0 | 0 | 1314 | 0 | 0 |  | 7115 | 5894 | 13009 | 3303 | 921 | 1919 | 0 | 2733 | 3141 | 199 | 123 | 516 | 150 | 0 | 4 | 0 | 0
20:00 | 0 | 0 | 200 | 0 | 0 | 76 | 0 | 326 | 264 |  | 0 | 360 | 4 | 61 | 82 | 15 | 260 | 0 | 40 | 25 | 25 | 98 | 33 | 0 | 0 | 0 | 54 | 35 | 35 | 16 | 19 | 19 | 25 | 32 | 25 | 0 | 124 | 75 | 108 | 0 | 17 | 225 | 0 | 0 | 0 |  | 6 | 49 | 0 | 25 | 0 | 6 | 12 | 42 | 0 | 0 | 0 | 115 | 295 | 202 | 197 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 51 | 16 | 11 | 33 | 12 | 160 | 57 | 0 | 17 | 0 | 30 | 40 | 50 | 40 | 80 | 0 | 60 | 86 | 0 | 184 | 17 | 0 | 10 | 270 | 16 | 8 | 0 | 130 | 0 | 0 | 162 | 0 | 135 | 0 | 25 | 104 | 130 | 324 | 85 | 105 | 17 | 0 | 264 | 54 | 64 | 17 | 76 | 25 | 126 | 17 | 0 | 126 | 34 | 0 | 17 | 0 | 0 | 17 | 0 | 160 | 0 | 0 | 6 | 0 | 0 |  | 920 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 10 | 11 | 32 | 130 | 26 | 0 | 0 | 0 | 0 | 35 | 14 | 63 | 0 | 8 | 32 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 270 | 40 | 0 | 65 | 0 | 88 | 0 | 0 | 75 | 1244 | 110 | 0 | 135 | 0 | 0 | 80 | 122 | 0 | 402 | 0 | 0 | 1312 | 0 | 0 |  | 7195 | 5792 | 12987 | 3348 | 920 | 1936 | 0 | 2662 | 3138 | 199 | 122 | 496 | 160 | 0 | 6 | 0 | 106.31
21:00 | 0 | 0 | 200 | 0 | 0 | 77 | 0 | 396 | 343 |  | 0 | 450 | 5 | 66 | 26 | 15 | 328 | 0 | 97 | 20 | 8 | 82 | 20 | 0 | 0 | 0 | 54 | 35 | 35 | 16 | 19 | 19 | 25 | 32 | 25 | 0 | 124 | 75 | 105 | 0 | 17 | 225 | 0 | 0 | 0 |  | 6 | 49 | 0 | 25 | 0 | 6 | 12 | 42 | 0 | 0 | 0 | 165 | 305 | 204 | 197 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 46 | 18 | 11 | 33 | 12 | 160 | 99 | 0 | 16 | 0 | 30 | 40 | 50 | 40 | 112 | 0 | 59 | 86 | 0 | 184 | 17 | 0 | 10 | 290 | 16 | 5 | 0 | 63 | 0 | 0 | 163 | 0 | 145 | 0 | 25 | 104 | 150 | 369 | 85 | 70 | 17 | 0 | 264 | 54 | 66 | 17 | 78 | 25 | 143 | 17 | 0 | 54 | 34 | 0 | 17 | 0 | 0 | 17 | 0 | 160 | 0 | 0 | 4 | 0 | 0 |  | 778 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 10 | 10 | 8 | 130 | 27 | 0 | 0 | 0 | 0 | 35 | 21 | 34 | 0 | 8 | 31 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 387 | 35 | 0 | 70 | 0 | 94 | 0 | 0 | 75 | 1244 | 110 | 0 | 72 | 0 | 0 | 113 | 122 | 0 | 402 | 0 | 0 | 1362 | 0 | 0 |  | 7525 | 5734 | 13259 | 3707 | 778 | 2277 | 0 | 2368 | 3188 | 199 | 122 | 456 | 160 | 0 | 4 | 39 | 106.32
22:00 | 0 | 0 | 200 | 0 | 0 | 77 | 0 | 414 | 332 |  | 0 | 450 | 18 | 61 | 17 | 15 | 331 | 0 | 96 | 8 | 8 | 82 | 25 | 0 | 0 | 0 | 54 | 35 | 55 | 16 | 19 | 19 | 25 | 32 | 25 | 0 | 124 | 75 | 111 | 0 | 17 | 224 | 0 | 0 | 0 |  | 6 | 49 | 0 | 25 | 0 | 6 | 12 | 42 | 0 | 0 | 0 | 255 | 310 | 204 | 197 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 51 | 18 | 11 | 33 | 12 | 158 | 95 | 0 | 16 | 0 | 30 | 40 | 50 | 43 | 112 | 0 | 59 | 84 | 0 | 184 | 17 | 0 | 10 | 290 | 16 | 5 | 0 | 60 | 0 | 0 | 164 | 0 | 149 | 0 | 25 | 103 | 150 | 366 | 85 | 70 | 17 | 0 | 124 | 17 | 60 | 17 | 78 | 25 | 150 | 17 | 0 | 54 | 34 | 0 | 17 | 0 | 0 | 17 | 0 | 160 | 0 | 0 | 5 | 0 | 0 |  | 777 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 10 | 10 | 8 | 130 | 28 | 0 | 0 | 0 | 0 | 35 | 19 | 34 | 0 | 8 | 31 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 414 | 35 | 0 | 70 | 0 | 95 | 0 | 0 | 75 | 1244 | 110 | 0 | 54 | 0 | 0 | 114 | 122 | 0 | 402 | 0 | 0 | 1366 | 0 | 0 |  | 7469 | 5755 | 13224 | 3835 | 777 | 2308 | 0 | 2174 | 3192 | 199 | 122 | 454 | 158 | 0 | 5 | 53.48 | 106.33
23:00 | 0 | 0 | 200 | 0 | 0 | 77 | 0 | 418 | 292 |  | 0 | 450 | 28 | 54 | 28 | 15 | 330 | 0 | 37 | 8 | 58 | 32 | 33 | 0 | 0 | 0 | 35 | 17 | 55 | 16 | 19 | 19 | 25 | 32 | 25 | 0 | 122 | 75 | 110 | 0 | 8 | 227 | 0 | 0 | 0 |  | 6 | 49 | 0 | 25 | 0 | 6 | 12 | 42 | 0 | 0 | 0 | 360 | 275 | 178 | 197 | 0 | 48 | 0 | 0 | 51 | 0 | 0 | 51 | 18 | 11 | 33 | 12 | 148 | 93 | 0 | 16 | 0 | 30 | 40 | 50 | 40 | 80 | 0 | 59 | 84 | 0 | 184 | 17 | 0 | 10 | 270 | 16 | 5 | 0 | 60 | 0 | 0 | 67 | 0 | 75 | 0 | 25 | 103 | 150 | 368 | 19 | 70 | 17 | 0 | 87 | 17 | 55 | 17 | 78 | 25 | 205 | 17 | 0 | 54 | 34 | 0 | 17 | 0 | 0 | 17 | 0 | 160 | 0 | 67 | 3 | 0 | 0 |  | 806 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 10 | 10 | 8 | 130 | 30 | 32 | 0 | 0 | 0 | 35 | 19 | 34 | 0 | 8 | 31 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 380 | 35 | 0 | 70 | 0 | 95 | 0 | 0 | 75 | 1244 | 110 | 0 | 54 | 0 | 0 | 114 | 121 | 0 | 402 | 0 | 0 | 1361 | 0 | 0 |  | 7168 | 5779 | 12947 | 3880 | 806 | 2191 | 0 | 1943 | 3254 | 197 | 121 | 404 | 148 | 0 | 3 | 251.165 | 106.34
24:00 | 0 | 0 | 200 | 0 | 0 | 77 | 0 | 414 | 332 |  | 0 | 450 | 28 | 49 | 64 | 15 | 330 | 0 | 97 | 8 | 58 | 32 | 34 | 0 | 0 | 0 | 0 | 0 | 55 | 18 | 19 | 19 | 25 | 16 | 8 | 0 | 122 | 75 | 108 | 0 | 8 | 227 | 0 | 0 | 0 |  | 6 | 41 | 0 | 25 | 0 | 6 | 12 | 42 | 0 | 0 | 0 | 305 | 305 | 178 | 197 | 0 | 46 | 0 | 0 | 51 | 0 | 0 | 51 | 18 | 11 | 33 | 12 | 156 | 96 | 0 | 16 | 0 | 30 | 40 | 50 | 43 | 112 | 0 | 59 | 84 | 0 | 184 | 17 | 0 | 10 | 290 | 16 | 5 | 0 | 57 | 0 | 0 | 68 | 0 | 17 | 0 | 25 | 72 | 45 | 368 | 19 | 35 | 17 | 0 | 87 | 17 | 55 | 17 | 24 | 25 | 300 | 17 | 0 | 54 | 34 | 0 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 200 | 2 | 0 | 0 |  | 807 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 10 | 10 | 32 | 123 | 30 | 32 | 0 | 0 | 0 | 35 | 19 | 34 | 0 | 42 | 31 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 380 | 37 | 0 | 35 | 0 | 95 | 0 | 0 | 35 | 1244 | 110 | 0 | 100 | 0 | 0 | 0 | 121 | 0 | 403 | 0 | 0 | 1363 | 0 | 0 |  | 7041 | 5700 | 12741 | 3984 | 807 | 2286 | 0 | 1569 | 3390 | 197 | 121 | 229 | 156 | 0 | 2 | 419.245 | 106.35
KWH | 0 | 0 | 3895500 | 0 | 0 | 1796090 | 0 | 9291770 | 7436000 |  | 0 | 9600800 | 252247 | 486720 | 952339 | 376124 | 7359585 | 0 | 1898000 | 271680 | 433296 | 1097280 | 414224 | 0 | 0 | 0 | 395280 | 446305 | 394968 | 412452 | 456000 | 358920 | 616100 | 747100 | 284640 | 0 | 2805491 | 1556000 | 2500000 | 0 | 175111 | 5289429 | 0 | 0 | 0 |  | 149040 | 953424 | 7463 | 523800 | 0 | 152160 | 297552 | 963360 | 0 | 0 | 0 | 1390700 | 7176000 | 4454000 | 4282182 | 0 | 1146456 | 0 | 0 | 1199048 | 0 | 0 | 880954 | 285768 | 204660 | 818900 | 287500 | 3233280 | 1312320 | 0 | 365292 | 6300 | 717000 | 917640 | 1096200 | 1009152 | 2363564 | 0 | 1451424 | 1894080 | 0 | 3758140 | 405000 | 0 | 252720 | 7000000 | 371112 | 195360 | 0 | 1093964 | 0 | 0 | 2136000 | 0 | 935568 | 36045 | 583680 | 1535520 | 1160872 | 8406000 | 549600 | 1032000 | 428218 | 17043 | 2100109 | 463187 | 1318100 | 425220 | 734160 | 614400 | 1829300 | 418560 | 183220 | 874080 | 667418 | 0 | 442800 | 101025 | 0 | 433080 | 0 | 824654 | 0 | 6267272 | 150240 | 0 | 0 |  | 21876363 | 0 | 0 | 0 | 883200 | 0 | 0 | 0 | 146400 | 84224 | 300000 | 2452000 | 527296 | 206400 | 0 | 0 | 0 | 235103 | 79429 | 269424 | 166960 | 373286 | 157328 | 150960 | 108545 | 0 | 0 | 193878 | 0 | 0 | 4395800 | 0 | 0 | 4059564 | 0 | 0 | 0 | 0 | 0 | 3701000 | 0 | 8293381 | 573120 | 0 | 841344 | 0 | 712022 | 0 | 35270 | 838944 | 29717200 | 3815073 | 0 | 1016400 | 7740 | 0 | 523200 | 2705636 | 0 | 11418180 | 109302 | 0 | 27087273 | 710810 | 0 |  | 149282337 | 128772055 | 278054392 | 79021422 | 21876363 | 51781193 | 0 | 30869013 | 78885725 | 4361491 | 2705636 | 3963274 | 3233280 | 1206755 | 150240 | 0
Fuel Cost | 0 | 0 | 5687430 | 0 | 0 | 2388799.7 | 0 | 9756358.5 | 8030880 |  | 0 | 10464872 | 279994.17 | 5441529.6 | 12618491.75 | 4983643 | 8242735.2 | 0 | 3321500 | 3971961.6 | 6096474.72 | 17786908.8 | 3819145.28 | 0 | 0 | 0 | 5027961.6 | 6025117.5 | 5296520.88 | 309339 | 342000 | 0 | 0 | 0 | 4841726.4 | 0 | 757482.57 | 420120 | 4725000 | 0 | 2863064.85 | 5501006.16 | 0 | 0 | 0 |  | 1944972 | 15903112.32 | 127020.26 | 7076538 | 0 | 1760491.2 | 377891.04 | 3207988.8 | 0 | 0 | 0 | 1543677 | 7821840 | 5166640 | 5524014.78 | 0 | 1295495.28 | 0 | 0 | 2002410.16 | 0 | 0 | 11848831.3 | 391502.16 | 153495 | 1433075 | 215625 | 23214950.4 | 1430428.8 | 0 | 496797.12 | 100422 | 982290 | 1211284.8 | 1907388 | 1745832.96 | 2718098.6 | 0 | 2815762.56 | 4318502.4 | 0 | 3795721.4 | 870750 | 0 | 500385.6 | 7000000 | 278334 | 148473.6 | 0 | 14932608.6 | 0 | 0 | 28793280 | 0 | 12957616.8 | 421366.05 | 6023577.6 | 20975203.2 | 15404771.44 | 7733520 | 6683136 | 14922720 | 5416957.7 | 265189.08 | 24655279.66 | 5044106.43 | 14011403 | 5770235.4 | 9463322.4 | 7237632 | 1682956 | 5420352 | 2647529 | 11092075.2 | 7595216.84 | 0 | 5782968 | 1207248.75 | 0 | 5703663.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 65629089 | 0 | 0 | 0 | 9194112 | 0 | 0 | 0 | 2636664 | 1516032 | 4311000 | 2746240 | 1022954.24 | 2249760 | 0 | 0 | 0 | 3942677.31 | 1389213.21 | 4213791.36 | 1285592 | 6181616.16 | 2660416.48 | 2057584.8 | 1831154.15 | 0 | 0 | 146765.646 | 0 | 0 | 37276384 | 0 | 0 | 4709094.24 | 0 | 0 | 0 | 0 | 0 | 4293160 | 0 | 8210447.19 | 7702732.8 | 0 | 9953099.52 | 0 | 9042679.4 | 0 | 389733.5 | 10184780.16 | 246652760 | 3891374.46 | 0 | 7521360 | 87539.4 | 0 | 8020656 | 0 | 0 | 103791256.2 | 0 | 0 | 231596184.15 | 0 | 0 |  | 502174039.57 | 806337903.376 | 1308511942.946 | 89626187.506 | 65629089 | 63213943.06 | 0 | 389207568.39 | 619316584.35 | 1177602.57 | 0 | 52006989.89 | 23214950.4 | 5119027.78 | 0 | 0
Yesterday Day Peak | 0 | 0 | 130 | 0 | 0 | 80 | 0 | 323 | 290 |  | 0 | 370 | 0 | 8 | 17 | 15 | 322 | 0 | 39 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 19 | 10 | 25 | 32 | 8 | 0 | 127 | 75 | 110 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 30 | 0 | 25 | 0 | 6 | 13 | 32 | 0 | 0 | 0 | 0 | 310 | 197 | 158 | 0 | 45 | 0 | 0 | 51 | 0 | 0 | 8 | 0 | 11 | 33 | 12 | 128 | 35 | 0 | 16 | 1 | 30 | 40 | 22 | 42 | 80 | 0 | 60 | 78 | 0 | 185 | 16 | 0 | 10 | 280 | 16 | 11 | 0 | 15 | 0 | 0 | 87 | 0 | 17 | 2 | 25 | 72 | 20 | 317 | 0 | 17 | 17 | 4 | 30 | 17 | 55 | 17 | 27 | 25 | 50 | 17 | 36 | 17 | 34 | 0 | 17 | 12 | 0 | 17 | 0 | 0 | 0 | 557 | 1 | 0 | 0 |  | 920 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 300 | 0 | 0 | 35 | 0 | 0 | 0 | 4 | 35 | 1000 | 180 | 0 | 17 | 0 | 33 | 0 | 128 | 0 | 517 | 11 | 0 | 919 | 15 | 0 |  | 10585 | DayPeak
Yesterday Evening Peak | 0 | 0 | 200 | 0 | 0 | 77 | 0 | 396 | 343 |  | 0 | 450 | 5 | 66 | 26 | 15 | 328 | 0 | 97 | 20 | 8 | 82 | 20 | 0 | 0 | 0 | 54 | 35 | 35 | 16 | 19 | 19 | 25 | 32 | 25 | 0 | 124 | 75 | 105 | 0 | 17 | 225 | 0 | 0 | 0 | 0 | 6 | 49 | 0 | 25 | 0 | 6 | 12 | 42 | 0 | 0 | 0 | 165 | 305 | 204 | 197 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 46 | 18 | 11 | 33 | 12 | 160 | 99 | 0 | 16 | 0 | 30 | 40 | 50 | 40 | 112 | 0 | 59 | 86 | 0 | 184 | 17 | 0 | 10 | 290 | 16 | 5 | 0 | 63 | 0 | 0 | 163 | 0 | 145 | 0 | 25 | 104 | 150 | 369 | 85 | 70 | 17 | 0 | 264 | 54 | 66 | 17 | 78 | 25 | 143 | 17 | 0 | 54 | 34 | 0 | 17 | 0 | 0 | 17 | 0 | 160 | 0 | 0 | 4 | 0 | 0 |  | 778 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 10 | 10 | 8 | 130 | 27 | 0 | 0 | 0 | 0 | 35 | 21 | 34 | 0 | 8 | 31 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 387 | 35 | 0 | 70 | 0 | 94 | 0 | 0 | 75 | 1244 | 110 | 0 | 72 | 0 | 0 | 113 | 122 | 0 | 402 | 0 | 0 | 1362 | 0 | 0 |  | 13259 | EvPeak
Forecast for Evening | 0 | 0 | 200 | 0 | 0 | 77 | 0 | 412 | 330 | 0 | 0 | 450 | 0 | 33 | 80 | 15 | 330 | 0 | 100 | 20 | 16 | 150 | 45 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 19 | 25 | 33 | 25 | 0 | 124 | 75 | 110 | 0 | 17 | 225 |  | 0 | 0 | 0 | 6 | 60 | 0 | 25 | 0 | 50 | 12 | 30 | 0 | 0 | 0 | 360 | 300 | 200 | 195 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 51 | 18 | 11 | 33 | 12 | 165 | 100 | 0 | 16 | 0 | 30 | 40 | 50 | 40 | 112 | 0 | 60 | 86 | 0 | 185 | 17 | 0 | 10 | 300 | 16 | 11 | 0 | 130 | 0 | 0 | 150 | 0 | 149 | 0 | 25 | 100 | 150 | 400 | 95 | 105 | 17 | 0 | 265 | 54 | 55 | 70 | 75 | 25 | 400 | 17 | 0 | 108 | 34 | 0 | 17 |  | 0 | 17 | 0 | 158 |  | 0 | 10 | 0 |  |  | 938 | 0 | 0 |  | 98 | 0 | 0 | 0 | 40 | 50 | 40 | 132 | 30 | 48 | 0 | 0 | 0 | 35 | 21 | 91 | 28 | 42 | 40 | 52 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 160 |  | 0 | 0 | 0 | 0 | 160 | 0 | 414 | 51 | 0 | 70 | 0 | 80 | 0 | 0 | 75 | 1244 | 110 |  | 150 |  |  | 75 | 120 |  | 450 |  | 0 | 1400 |  | 0
Forecast for Day | 0 | 0 | 200 | 0 | 0 | 75 | 0 | 412 | 330 | 0 | 0 | 450 | 0 | 32 | 80 | 15 | 330 | 0 | 100 | 16 | 8 | 64 | 40 | 0 | 0 | 0 | 17 | 35 | 55 | 19 | 19 | 19 | 25 | 33 | 8 | 0 | 120 | 75 | 110 | 0 | 8 | 225 |  | 0 | 0 | 0 | 6 | 32 | 0 | 25 | 0 | 6 | 12 | 10 | 0 | 0 | 0 | 320 | 300 | 200 | 190 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 51 | 16 | 11 | 33 | 12 | 149 | 70 | 0 | 16 | 1.6 | 30 | 40 | 50 | 40 | 112 | 0 | 60 | 86 | 0 | 185 | 17 | 0 | 10 | 300 | 16 | 11 | 0 | 84 | 0 | 0 | 115 | 0 | 17 | 20 | 25 | 68 | 13 | 400 | 37 | 70 | 17 | 5 | 70 | 17 | 55 | 34 | 28 | 25 | 50 | 17 | 50 | 54 | 34 | 0 | 17 | 35 | 0 | 17 | 0 | 17 |  | 0 | 10 | 0 |  |  | 938 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 25 | 40 | 24 | 132 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 28 | 34 | 30 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 414 | 17 | 0 | 35 | 0 | 34 | 0 | 8 | 35 | 1244 | 110 |  | 35 | 6 | 100 | 35 | 120 |  | 400 | 30 | 0 | 1300 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 150 | 0 | 0 | 71 | 0 | 368 | 261 | 0 | 0 | 350 | 0 | 9 | 0 | 15 | 260 | 0 | 38 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 19 | 25 | 32 | 8 | 0 | 124 | 75 | 111 | 0 | 8 | 224 | 0 | 0 | 0 | 0 | 6 | 33 | 0 | 25 | 0 | 0 | 12 | 7 | 0 | 0 | 0 | 310 | 300 | 158 | 158 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 51 | 16 | 11 | 33 | 12 | 138 | 72 | 0 | 16 | 1 | 30 | 40 | 47 | 43 | 80 | 0 | 40 | 78 | 0 | 185 | 17 | 0 | 10 | 280 | 8 | 5 | 0 | 0 | 0 | 0 | 68 | 0 | 17 | 11 | 25 | 34 | 0 | 329 | 19 | 35 | 17 | 3 | 70 | 17 | 55 | 17 | 9 | 25 | 215 | 17 | 14 | 17 | 17 | 0 | 17 | 8 | 0 | 0 | 0 | 17 | 0 | 457 | 0 | 0 | 200 | 0 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 350 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 880 | 110 | 0 | 0 | 1 | 23 | 0 | 121 | 0 | 403 | 8 | 0 | 1215 | 20 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
292.3904
| Minimum Generation |  | 10221 | 9:00 | [201 empty] | 130802615
| Highest Generation |  | 13259 | 21:00 | [201 empty] | 130.8026 |  |  |  |  | 1.2068
| Day Peak Generation |  | 10585 | 12:00 | [201 empty] | 37537923
| Evening Peak Generation |  | 13259 | 21:00 | [201 empty] | 37.5379 |  |  | 51781193 |  | 4.3615
| HVDC Max Flow |  | 922 | 7:00 | [201 empty] | 21.8764 |  |  |  |  | 0.15024
| HVDC EvPeak Flow |  | 778 | 21:00 | [199 empty] | 278054392 |  | 3.2333 |  | 78.8857
| Load factor L.F |  | 87.38% | [165 empty] | 1275.5 | [36 empty] | 278.0544

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-09-09
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-09-08 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 10585 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 10895
Evening Peak Generation : |  |  | 13259 | MW Hour : | 21:00 | Available Max Generation : |  | 14857
E.P. Demand (at gen end) : |  |  | 13300 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14300
Maximum Generation : |  |  | 13259 | MW Hour : | 21:00 | Reserve(Generation end) |  | 557
Total Gen. (MKWH) : |  |  | 278.0544 | System Load Factor : | 87.38% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 1030 | MW at | 20:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-09-09
Actual : |  | 106.36 | Ft.(MSL) , | Rule curve : | 10084 | Ft.( MSL )
Gas Consumed : |  | Total = | 1070.15 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 152840130.566
: |  |  | Coal : | 619316584.35 | Oil : | 441214558.28 | Total : | 1213371273.196
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 5019.2107 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1381.88 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1936.5624 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1683.9775 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1385.229 |  |  | 0 | 0%
Mymensingh Area |  | 39 | 936:00 | 1030.6659 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 577.2872 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 481.4952 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 941.7111 |  |  | 0 | 0%
Total |  | 39 |  | 14438.019 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
| 08:16 | Cox'sbazar-Dohazari 132 kV Ckt-1 is restored.
08:18 | 09:52 | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to None |  |  |  |  | 30.0MW load interruption
08:18 | 09:50 | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to D/S 189A Y phase Riser Hotspot Maintenece work
| 08:26 | Kushtia 132/33kV S/S T2 HT is restored.
| 08:27 | Kushtia 132/33kV S/S T2 LT is restored.
09:10 | 11:10 | Mithapukur-Palashbari 132kV Ckt-1 Forced S/D from Palashbari 132/33kV end Due to CB open
09:12 | 10:06 | Bakulia 132/33kV S/S Bus-A Project Work S/D Due to None
09:12 | 11:09 | Mithapukur-Palashbari 132kV Ckt-2 Forced S/D from Mithapukur 132/33kV end Due to Only CB open
09:34 | 09:46 | Dohazari 132/33kV S/S Power Transformer -T-1 HT Forced S/D Due to For Station Supply fuse cut. |  |  |  |  | 12.0MW load interruption
| 09:42 | Gulshan 132/33kV S/S MT-1 HT is restored.
09:59 | 11:13 | Dohazari 132/33kV S/S Power Transformer -T-2 HT Scheduled S/D Due to Fir 33KV PBS keranihut redhot maintenance |  |  |  |  | 30.0MW load interruption
| 10:47 | Bogura 230/132kV S/S 230KV Main 2 is restored.
11:11 | 11:47 | Mahasthangar-Palashbari 132kV Ckt-1 Forced S/D from Palashbari 132/33kV end.
11:11 | 11:47 | Mahasthangar-Palashbari 132kV Ckt-2 Forced S/D from Palashbari 132/33kV end Due to None
| 11:42 | Barapukuria-Bogura 230 kV Ckt-2 is restored.
12:00 |  | Day peak Gen : 10585 MW , No shed
12:18 |  | Ashuganj North GT was sync.
12:44 |  | Bhola Natun Biddyut GT-2 was shutdown.
12:45 | 17:28 | Rahanpur 400/132kV S/S Rahanpur-Chapainawabganj 132 KV Line Ckt-02 Scheduled S/D Due to Gas leakage in GIL.
15:01 |  | SS Power unit-2 was forced shutdown due to load rejection test. |  |  |  |  | 600.0MW generation interruption
15:41 | 15:55 | Tongi 230/132/33kV S/S Tongi-Uttara 3rd Phase Ckt Tripped showing ABB,RED670 relays Due to General
15:41 | 15:55 | Tongi 230/132/33kV S/S Tongi-Uttara 3rd Phase Ckt Tripped showing ABB,RED670 relays Due to General
15:50 | 17:23 | Magura 132/33kV S/S T-2 (415T) HT Tripped showing Oil temp. Trip. relays Due to Water entered in oil temp. Meter.
16:29 |  | Bibiyana South 400 MW ST was sync.
| 17:32 | Rahanpur 400/132kV S/S LV 132 KV BUS is restored.
| 17:45 | Sirajganj 132/33kV S/S Sherpur-1 is restored.
17:52 |  | Ashugonj North 360MW ST was sync.
18:01 |  | Meghnaghat Summit CCPP 305MW GT1 was sync.
18:56 |  | SS Power - Matarbari 400 kv line - 1 & 2 tripped from SS Power end showing high voltage.
18:56 |  | Madunaghat 400/230 kv Tr. tripped operating differential relay.
19:21 |  | Sirajganj - Sherpur 132 KV ckt-1 is charged from Sirajganj 132/33kV S/S side.
20:00 |  | SS Power - Matarbari 400 kv line-1 was switched on.
20:30 |  | Madunaghat 400/230KV auto transformer was switched on
20:38 |  | SS Power - Matarbari 400 kv line - 2 was switched on.
21:00 |  | Evening Peak Gen. 13260 MW
22:45 |  | Bashkhali SS Power Unit-2 was sync.
| 23:40 | Haripur-Meghnaghat 230kV Ckt-1 is restored.
23:42 | 23:49 | Haripur-Meghnaghat 230kV Ckt-1 Tripped from Haripur 230/132kV end showing Circulating
Current Protection (CC2): Y phase, Tripping Relay (86T1). relays.
23:50 |  | Haripur-Meghnaghat 230kV Ckt-1 Tripped from Haripur 230/132kV end showing Circulating
Current Protection (CC1): B phase, Tripping Relay (86T1). relays.
00:38 |  | Meghnaghat Summit CCPP 305MW GT1 was shutdown
00:53 |  | Bibiyana South 400 MW ST was force shutdown. |  |  |  |  | 136.0MW generation interruption
02:10 |  | Meghnaghat Unique 584 MW PP Unit transformar breaker was switched on
02:10 |  | Meghnaghat Unique 584 MW PP Unit transformar breaker was switched on
04:24 |  | Sirajganj-3 225 MW PP ST tripped |  |  |  |  | 73MW generation interruption
06:33 |  | Rampur 230/132/33 S/S TR-1 LT Forced S/D Due to RED HOT MAINTENANCE
06:34 |  | Rampur 230/132/33 S/S TR-1 HT Forced S/D Due to RED HOT AT LT SIDE B-PHASE
06:36 |  | Meghnaghat Unique 584 MW PP GT was sync
07:00 |  | Minimum Generation is 10895 MW
07:16 |  | Barishal-Patuakhali(Barguna T at Bakergonj) 132 kV Ckt Scheduled S/D from Patuakhali 132/33kV end Due to
Maintenance work for Main Bus
07:21 |  | Patuakhali 132/33kV S/S UPPL (150MW) 132kV LINE Scheduled S/D Due to Maintenance for Main bus
07:27 |  | Patuakhali-Payra 132kV Ckt-1 Forced S/D from Payra 400/132/33kV end Due to Bus maintenance at Patuakhali |  |  |  |  | 53.0MW load interruption
Substation. and from Patuakhali 132/33kV end Due to Maintenance for Main Bus Shutdown
07:28 |  | Patuakhali-Payra 132kV Ckt-2 Forced S/D from Payra 400/132/33kV end Due to Bus maintenance at Patuakhali
substation and from Patuakhali 132/33kV end Due to Maintenance for Main Bus
07:44 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) LT Scheduled S/D Due to Redhot Maintenance.
07:48 |  | Sirajganj 132/33kV S/S Sherpur-2 Scheduled S/D Due to OPGW Wire Stringing.
07:49 |  | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-2 Project Work S/D from Bog-Sherpur 132/33kV end Due to According to ALDC's
instructions.
07:50 |  | Hathazari 230/132/33kV S/S T-01 LT Scheduled S/D Due to 33kv side new DS commissioning by REB. |  |  |  |  | 35.0MW load interruption
07:50 |  | Hathazari 230/132/33kV S/S T-01 HT Scheduled S/D Due to 33kv side new DS commissioning by REB.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-09-08 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 200 | 3895500
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 77 | 1796090 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 396 | 9291770
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 343 | 7436000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9600800
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 66 | 486720 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 5 | 252247 | Start up process
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 26 | 952339 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 376124 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 20 | 414224 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 16 | 412452 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 97 | 1898000 | GT-2 Under maint
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 20 | 271680 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 328 | 7359585
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 433296 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 395280
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 82 | 1097280
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 446305 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 394968 | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 38 | 814920 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 616100 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 32 | 747100
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 284640 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 63 | 1093964 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Contract Expired
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 145 | 935568 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1032000 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 418560 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 874080 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 101025
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 433080 | Fuel shortage
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0
| Dhaka area Total |  |  |  | 5722 | 2759 | 54561697
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 105 | 2500000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 175111 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 36045
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 6 | 152160 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 199 | 4361491
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 225 | 5289429
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 428218 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 49 | 953424 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 7463 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 25 | 523800 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 583680 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 12 | 297552 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 963360
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 17043
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 264 | 2100109 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 463187
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 66 | 1318100 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 614400 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 34 | 667418 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 160 | 824654 | Fuel shortage
| SS Power I |  | SS Power | 0 | 0 | 0 | 6267272 | On test.
| Cox's Bazar Wind |  | IPP | 66 | 0 | 4 | 150240 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2545 | 1329 | 28694156
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 204 | 4454000 | Under maint.
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 165 | 1390700 | Under maint.
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7176000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 49 | 1146456
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 197 | 4282182
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1199048
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 150 | 1160872
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Fuel shortage
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 104 | 1535520 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 285768 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 204660
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 160 | 3233280
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 818900
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 46 | 880954
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 12 | 287500 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 425220 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 78 | 734160 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 442800 | Fuel shortage
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | Fuel shortage
| Cumilla Area Total |  |  |  | 2896 | 1617 | 29658020
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 99 | 1312320 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 365292 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 6300
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 163 | 2136000 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 85 | 549600 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 183220
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 149040 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 369 | 4701772
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 717000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 917640 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2363564 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1096200
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 40 | 1009152 | Engine problem
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 195360 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 59 | 1451424
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1894080
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 184 | 3758140 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 405000 | Machine problem
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 371112 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7000000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 369 | 8406000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 252720
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 143 | 1829300 | ST Under maint.
| Sylhet Area Total |  |  |  | 2427 | 1451 | 31666692
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 778 | 21876363
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 883200 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 10 | 146400 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserved
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 10 | 84224 | Fuel shortage
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 300000
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 573120 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 0
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 220 | 122 | 2705636 | Low demand
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 402 | 11418180 | Low demand
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 3121 | 1381 | 37987123
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 206400 | Fuel shortage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 27 | 527296 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 130 | 2452000 | ST Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 29717200
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 110 | 3815073 | Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 72 | 1016400
| Barisal 307 MW |  | IPP | 307*1 | 307 | 0 | 0 | Coal shortage.
| Barisal Area Total |  |  |  | 2265 | 1583 | 37734369
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 35 | 235103 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 21 | 79429 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 166960 | Fuel shortage
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 373286 | Fuel shortage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 157328 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 164 | 4059564 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 156 | 3701000 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 387 | 8293381 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 108545 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 193878 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 150960
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 34 | 269424 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 841344 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 75 | 838944 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 7740
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1362 | 27087273
| Rajshahi Area Total |  |  |  | 3631 | 2383 | 46564159
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 180 | 4395800 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 94 | 712022 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 35270
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 113 | 523200 | Fuel shortage
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 109302
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 710810
| Rangpur Area Total |  |  |  | 950 | 387 | 6486404
| Total |  |  |  | 24171 | 13259 | 278054392
| Eastern Grid Total |  |  |  | 14204 | 7525 | 149282337
| Western Grid Total |  |  |  | 9967 | 5734 | 128772055
| National Grid Total |  |  |  | 24171 | 13259 | 278054392
*Data collected from respective power station over telephone.
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-09-08
| (a) ENTIRE EASTERN GRID : |  | 8466.69 | MW | (b) ENTIRE WESTERN GRID : |  | 4174.8 | MW
| i) Dhaka area |  | 4265.49 | MW | i) Khulna area |  | 1581.4 | MW
| ii) Chittagong area |  | 1295.2 | MW | ii) Rajshahi area |  | 1323.2 | MW
| iii) Comilla area |  | 1253 | MW | iii) Barisal area |  | 397.2 | MW
| iv) Mymensingh area |  | 1104 | MW | iv) Rangpur area |  | 873 | MW
| v) Sylhet area |  | 549 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 12641.49 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 32 | 23:00 | Kamrangirchar | 60 | 00:00 | Natore | 128 | 20:00 | Sholosohor | 27 | 19:30
2 | AKSML | 122 | 09:00 | Chowmuhani | 188 | 19:00 | Kaptai | N/A | N/A | Nawabganj | 46 | 22:00 | Shyampur | 158 | 00:00
3 | Aftabnagar | 48 | 00:00 | Chuadanga | 109 | 00:00 | Kazla | 88 | 00:00 | Netrakona | 137 | 21:00 | Siddhirganj | 106 | 00:00
4 | Agargaon | 78 | 18:30 | Coxsbazar | 112 | 18:30 | Keranigonj | 72 | 00:00 | New | 67 | 00:00 | Sirajganj | 103 | 00:00
5 | Agrabad | 58 | 22:00 | Cumilla(N) | 154 | 22:00 | Khagrachori | 28 | 19:00 | Niamatpur | 74 | 21:00 | Sonargaon | 79 | 00:00
6 | Amnura | 50 | 00:00 | Cumilla(S) | 160 | 20:00 | Khulna | 85 | 18:30 | Noapara | 35 | 00:00 | Sreemongol | 62 | 22:00
7 | Ashuganj | 70 | 23:00 | Daudkandi | 124 | 21:00 | Khulshi | 166 | 23:00 | PHP | 1 | 00:00 | Sreepur | 64 | 01:00
8 | BIPTC | N/A | N/A | Dhaka | 12 | 00:00 | Kishoreganj | 166 | 22:00 | Pabna | 108 | 21:00 | Srinagar | 43.9 | 22:00
9 | BSRM | 187 | 18:00 | Dhamrai | 96 | 06:00 | Kodda | 219 | 21:00 | Palashbari | 120 | 21:00 | Sunamganj | 56 | 21:00
10 | Bagerhat | 82 | 19:30 | Dhanmondi | 101.3 | 18:30 | Kulaura | 44 | 23:00 | Panchagarh | 57 | 19:00 | Sylhet | 141 | 13:00
11 | Bakulia | 91 | 03:00 | Dohazari | 80 | 19:00 | Kurigram | 64 | 18:30 | Patuakhali | 92 | 00:00 | TK | 25 | 03:00
12 | Banani | 44 | 14:00 | Faridpur | 147 | 22:00 | Kushtia | 138 | 18:30 | Payra | 22 | 22:00 | Tangail | 221 | 20:00
13 | Bangabhaban | 4 | 00:00 | Fatullah | 60 | 00:00 | Lalbag | 76 | 00:00 | Postogola | 57 | 00:00 | Thakurgaon | 92 | 19:30
14 | Barapukuria | 63 | 00:00 | Fenchuganj | 46 | 22:00 | Lalmonirhat | 49 | 19:00 | Purbachal | 21 | 00:00 | Tongi | 106 | 00:00
15 | Barguna | 18 | 19:30 | Feni | 103 | 19:00 | Madanganj | 32 | 00:00 | Purbasadipur | 118 | 00:00 | Ullon | 40 | 00:00
16 | Barishal | 92 | 00:00 | GPH | 91 | 17:00 | Madaripur | 99 | 22:00 | Rahim | 38 | 00:00 | Uttara | 68 | 18:30
17 | Barishal-230 | 90 | 22:00 | Ghorashal | 60 | 19:00 | Madartek | 84.14 | 00:00 | Rajbari | 66 | 21:00 | UttaraNew | 65 | 00:00
18 | Baroaulia | 66 | 01:00 | Goalpara | 32 | 22:00 | Madunaghat | 47 | 21:00 | Rajendrapur | 88 | 22:00 | Zigatola | 66 | 00:00
19 | Baroirhat | 53 | 19:00 | Gollamari | 46 | 00:00 | Magura | 59.5 | 19:00 | Rajshahi | 155 | 00:00
20 | Bashundhara | 140 | 00:00 | Gopalganj | 95 | 19:30 | Mahasthangarh | 68 | 19:30 | Rajshahi-230 | 37 | 00:00
21 | BashundharaCement | 1 | 10:00 | Gulshan | 90 | 18:30 | Manikganj | 105 | 21:00 | Ramganj | 120 | 21:00
22 | Beanibazar | 70 | 21:00 | Halishahar | 57.5 | 19:00 | Maniknagar | 76 | 00:00 | Rampur | 27 | 00:00
23 | Benapole | 56 | 19:00 | HaripurSBU | 131 | 00:00 | Matarbari | 38 | 21:00 | Rangamati | 18 | 19:00
24 | Bhaluka | 116 | 19:30 | Hasnabad | 82 | 00:00 | Matuail | 65 | 00:00 | Rangpur | 136 | 20:00
25 | Bhandaria | 50 | 22:00 | Hathazari | 67 | 21:00 | Millgate | 85 | 00:00 | Ruppur | 5.2 | 10:00
26 | Bhangura | 32 | 01:00 | Ishurdi | 68 | 21:00 | Mirpur | 123 | 18:30 | SSM | 0 | 00:00
27 | Bheramara(GK) | 60 | 21:00 | Jaldhaka | 80 | 21:00 | Mirsorai | 5 | 00:00 | Saidpur | 88 | 19:30
28 | Bhulta | 220 | 00:00 | Jamalpur | 162 | 19:30 | Mithapukur | 40 | 20:00 | Satkhira | 112 | 20:00
29 | Bog-Sherpur | 60 | 19:00 | Jashore | 128 | 00:00 | Modern | 0 | 00:00 | Satmasjid | 103 | 00:00
30 | Bogura | 153 | 22:00 | Jhenaidah | 125 | 19:00 | Mogbazar | 104.2 | 19:00 | Savar | 148 | 01:00
31 | Borhanuddin | 54 | 21:00 | Joydebpur | 142 | 22:00 | Mongla | 24 | 00:00 | Shahjadpur | 95 | 20:00
32 | Brahmanbaria | 168 | 22:00 | Joypurhat | 53 | 00:00 | Motijheel | 33 | 00:00 | Shahjibazar | 112 | 19:30
33 | Cantonment | 132 | 19:00 | Juldah | 20 | 18:00 | Munshiganj | 100 | 00:00 | Shahmirpur | 36 | 00:00
34 | Chandpur | 70 | 20:00 | KSRM | 26 | 14:00 | Mymensingh | 212 | 01:00 | Shariatpur | 77 | 22:00
35 | Chandraghona | 28 | 19:30 | Kabirpur | 218 | 00:00 | Naogaon | 120 | 00:00 | Sherpur | 140 | 22:00
36 | Chapai | 60 | 00:00 | Kachua | 77 | 22:00 | Narail | 52 | 21:00 | Shikalbaha | 23 | 19:30
37 | Charsaidpur | 39 | 11:00 | Kallyanpur | 111 | 00:00 | Narinda | 54 | 00:00 | Shikalbaha-230 | N/A | N/A
38 | Chauddagram | 55 | 22:00 | Kalurghat | 22 | 04:00 | Narshingdi | 169 | 21:00 | Shitalakhya | 78.4 | 01:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-09-08 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 400 | 18:30 | 397 | 12:00 | Gopalganj | 406 | 19:00 | 395 | 22:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 382 | 18:30 | 369 | 00:00
| Bhulta | 394 | 22:00 | 378 | 00:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 402 | 10:00 | 394 | 13:00 | Payra | 413 | 06:00 | 407 | 21:00
| BIPTC | 400 | 06:00 | 395 | 01:00 | Rahanpur | 407 | 09:00 | 386 | 01:00
| Bogura | N/A | N/A | N/A | N/A | Rampal | 408 | 06:00 | 396 | 22:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 232 | 19:00 | 224 | 01:00 | Hasnabad | 233 | 19:30 | 224 | 00:00
| AKSML | 227 | 00:00 | 221 | 02:00 | Hathazari | 228 | 21:00 | 223 | 12:00
| Aminbazar | 232 | 18:30 | 228 | 00:00 | Ishurdi | 235 | 06:00 | 224 | 20:00
| Ashuganj | 235 | 19:00 | 228 | 01:00 | Jhenaidah | 229 | 06:00 | 215 | 22:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 235 | 22:00 | 226 | 00:00
| Baghabari | 231 | 06:00 | 223 | 01:00 | Keranigonj | 231 | 19:00 | 224 | 01:00
| Barapukuria | 222 | 14:00 | 208 | 02:00 | Khulna(S) | 237 | 10:00 | 227 | 21:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 237 | 07:00 | 230 | 22:00 | Maniknagar | 231 | 19:30 | 224 | 00:00
| Bheramara | 233 | 04:00 | 223 | 20:00 | Meghnaghat | 239 | 21:00 | 230 | 07:00
| Bhulta | 234 | 19:30 | 226 | 00:00 | Mirsorai | 231 | 19:00 | 221 | 07:00
| Bibiana | 231 | 11:00 | 226 | 03:00 | Rajshahi | 235 | 06:00 | 220 | 21:00
| BIPTC | 235 | 06:00 | 221 | 20:00 | Rampal | 235 | 06:00 | 226 | 22:00
| Bogura | 229 | 06:00 | 215 | 03:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 241 | 08:00 | 235 | 22:00 | Rampura | 231 | 19:00 | 224 | 00:00
| BSRM | 232 | 20:00 | 221 | 09:00 | Shikalbaha | 228 | 20:00 | 222 | 13:00
| Cumilla(N) | 230 | 20:00 | 222 | 02:00 | Shyampur | 232 | 19:30 | 224 | 01:00
| Fenchuganj | 234 | 06:00 | 230 | 02:00 | Siddhirganj | 233 | 19:30 | 227 | 00:00
| Ghorashal | 235 | 22:00 | 230 | 00:00 | Sirajgonj | 237 | 11:00 | 231 | 02:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 231 | 08:00 | 224 | 01:00
| GPH | 228 | 21:00 | 221 | 05:00 | Tongi | 234 | 19:00 | 223 | 00:00
| Haripur | 231 | 22:00 | 225 | 00:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 134 | 19:00 | 130 | 01:00 | Lalbag | 136 | 19:30 | 132 | 00:00
| Agargaon | 133 | 19:00 | 128 | 01:00 | Lalmonirhat | 130 | 11:00 | 120 | 00:00
| Agrabad | 133 | 00:00 | 128 | 12:00 | Madanganj | 136 | 19:30 | 131 | 01:00
| AKS | 130 | 10:00 | 127 | 08:00 | Madaripur | 132 | 18:00 | 126 | 22:00
| Aminbazar | 134 | 18:30 | 130 | 00:00 | Madartek | 133 | 07:00 | 129 | 12:00
| Amnura | 135 | 00:00 | 120 | 00:00 | Madunaghat | 134 | 00:00 | 130 | 09:00
| Ashuganj | 138 | 19:30 | 135 | 00:00 | Magura | 136 | 06:00 | 126 | 22:00
| Bagerhat | 135 | 06:00 | 124 | 23:00 | Mahasthangarh | 141 | 11:00 | 124 | 03:00
| Bakulia | 133 | 10:00 | 128 | 07:00 | Manikganj | 134 | 18:00 | 125 | 01:00
| Banani | 134 | 21:00 | 129 | 12:00 | Maniknagar | 134 | 19:30 | 130 | 00:00
| Bangabhaban | 134 | 19:30 | 129 | 01:00 | Matarbari | 127 | 08:00 | 116 | 07:00
| Barapukuria | 138 | 14:00 | 127 | 02:00 | Matuail | 136 | 19:30 | 131 | 00:00
| Barguna | 139 | 06:00 | 133 | 23:00 | Millgate | 136 | 19:00 | 129 | 00:00
| Barishal | 139 | 08:00 | 130 | 21:00 | Mirpur | 133 | 19:00 | 128 | 13:00
| Barishal-230 | 138 | 10:00 | 131 | 21:00 | Mithapukur | 132 | 14:00 | 120 | 03:00
| Baroaulia | 133 | 00:00 | 129 | 13:00 | Modern | 133 | 10:00 | 129 | 05:00
| Baroirhat | 129 | 17:00 | 121 | 02:00 | Mogbazar | 135 | 21:00 | 131 | 00:00
| Bashundhara | 135 | 19:30 | 129 | 01:00 | Mongla | 134 | 06:00 | 125 | 22:00
| BashundharaCement | 136 | 19:30 | 130 | 01:00 | Motijheel | 134 | 19:30 | 129 | 01:00
| Beanibazar | 127 | 08:00 | 124 | 22:00 | Munshiganj | 135 | 19:30 | 131 | 00:00
| Benapole | 136 | 06:00 | 126 | 22:00 | Mymensingh | 133 | 19:00 | 115 | 01:00
| Bhaluka | 125 | 09:00 | 118 | 01:00 | Naogaon | 133 | 06:00 | 120 | 02:00
| Bhandaria | 138 | 07:00 | 128 | 22:00 | Narail | 136 | 06:00 | 124 | 22:00
| Bhangura | 137 | 05:00 | 132 | 20:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 133 | 06:00 | 126 | 20:00 | Narshingdi | 130 | 14:00 | 124 | 01:00
| Bheramara(GK) | 134 | 06:00 | 125 | 22:00 | Natore | 131 | 06:00 | 122 | 20:00
| Bhulta | 128 | 19:00 | 123 | 00:00 | Nawabganj | 136 | 19:00 | 131 | 00:00
| Bog-Sherpur | 138 | 10:00 | 127 | 01:00 | Netrakona | 132 | 19:00 | 124 | 10:00
| Bogura | 140 | 09:00 | 113 | 00:00 | New | 137 | 19:30 | 130 | 00:00
| Bogura-230 | 141 | 11:00 | 128 | 03:00 | Niamatpur | 132 | 11:00 | 122 | 00:00
| Brahmanbaria | 130 | 09:00 | 122 | 04:00 | Noapara | 138 | 06:00 | 128 | 21:00
| Cantonment | 132 | 06:00 | 128 | 00:00 | Pabna | 134 | 06:00 | 126 | 22:00
| Chandpur | 126 | 08:00 | 118 | 02:00 | Palashbari | 134 | 10:00 | 120 | 02:00
| Chandraghona | 136 | 17:00 | 131 | 07:00 | Panchagarh | 129 | 19:30 | 115 | 01:00
| Chapai | 133 | 08:00 | 123 | 00:00 | Patuakhali | 139 | 06:00 | 135 | 20:00
| Charsaidpur | 137 | 19:30 | 131 | 00:00 | Payra | 140 | 07:00 | 137 | 02:00
| Chauddagram | 128 | 10:00 | 123 | 01:00 | PHP | 127 | 10:00 | 120 | 03:00
| Chhatak | 129 | 17:00 | 124 | 21:00 | Postogola | 137 | 19:00 | 131 | 01:00
| Chowmuhani | 125 | 17:00 | 119 | 22:00 | Purbachal | 136 | 19:30 | 128 | 00:00
| Chuadanga | 133 | 06:00 | 119 | 21:00 | Purbasadipur | 129 | 14:00 | 118 | 04:00
| Coxsbazar | 126 | 15:00 | 110 | 08:00 | Rahanpur | 134 | 08:00 | 128 | 01:00
| Cumilla(N) | 133 | 23:00 | 126 | 02:00 | Rahim | 137 | 19:30 | 132 | 00:00
| Cumilla(S) | 133 | 06:00 | 126 | 01:00 | Rajbari | 128 | 06:00 | 121 | 22:00
| Daudkandi | 130 | 10:00 | 125 | 01:00 | Rajendrapur | 137 | 19:00 | 125 | 08:00
| Dhaka | 134 | 19:30 | 130 | 12:00 | Rajshahi | 132 | 04:00 | 124 | 21:00
| Dhamrai | 136 | 19:00 | 131 | 00:00 | Rajshahi-230 | 133 | 06:00 | 120 | 00:00
| Dhanmondi | 136.5 | 19:30 | 131.5 | 01:00 | Ramganj | 124 | 10:00 | 112 | 02:00
| Dohazari | 131 | 10:00 | 123 | 07:00 | Rampur | 132 | 17:00 | 129 | 06:00
| Faridpur | 129 | 06:00 | 122 | 22:00 | Rampura | 133 | 19:00 | 130 | 00:00
| Fatullah | 138 | 19:00 | 132 | 01:00 | Rangamati | 134 | 00:00 | 129 | 07:00
| Fenchuganj | 133 | 09:00 | 130 | 00:00 | Rangpur | 132 | 14:00 | 118 | 01:00
| Feni | 128 | 10:00 | 122 | 01:00 | Ruppur | 134 | 05:00 | 127 | 21:00
| Ghorashal | 137 | 01:00 | 135 | 10:00 | Saidpur | 131 | 15:00 | 117 | 02:00
| Goalpara | 138 | 06:00 | 129 | 23:00 | Satkhira | 135 | 06:00 | 124 | 23:00
| Gollamari | 136 | 06:00 | 129 | 22:00 | Satmasjid | 132 | 19:00 | 128 | 00:00
| Gopalganj | 131 | 06:00 | 125 | 23:00 | Savar | 134 | 19:00 | 128 | 00:00
| Gopalganj-400 | 130 | 06:00 | 125 | 22:00 | Shahjadpur | 141 | 06:00 | 135 | 00:00
| Gulshan | 133 | 06:00 | 130 | 00:00 | Shahjibazar | 130 | 09:00 | 124 | 00:00
| Halishahar | 132 | 10:00 | 129 | 06:00 | Shahmirpur | 133 | 16:00 | 129 | 00:00
| Haripur | 137 | 19:30 | 132 | 00:00 | Shariatpur | 131 | 08:00 | 124 | 22:00
| HaripurSBU | 137 | 19:30 | 132 | 00:00 | Sherpur | 130 | 19:00 | 119 | 10:00
| Hasnabad | 137 | 18:30 | 131 | 00:00 | Shikalbaha | 123 | 00:00 | 118 | 07:00
| Hathazari | 135 | 00:00 | 132 | 12:00 | Shikalbaha-230 | 133 | 00:00 | 130 | 08:00
| Ishurdi | 135 | 06:00 | 128 | 20:00 | Shitalakhya | 137.1 | 19:30 | 130.6 | 01:00
| Jaldhaka | 131 | 14:00 | 112 | 01:00 | Sholosohor | 132 | 00:00 | 129 | 03:00
| Jamalpur | 134 | 19:00 | 120 | 10:00 | Shyampur | 137 | 21:00 | 133 | 00:00
| Jashore | 137 | 06:00 | 126 | 21:00 | Shyampur-230 | 138 | 19:30 | 132 | 00:00
| Jhenaidah | 139 | 05:00 | 128 | 22:00 | Siddhirganj | 135 | 18:30 | 132 | 00:00
| Jhenaidah-230 | 139 | 06:00 | 129 | 22:00 | Sirajganj | 134 | 04:00 | 128 | 21:00
| Joydebpur | 138 | 19:30 | 132 | 02:00 | Sonargaon | 132 | 00:00 | 129 | 01:00
| Joypurhat | 133 | 11:00 | 120 | 01:00 | Sreemongol | 130 | 09:00 | 126 | 00:00
| Juldah | 134 | 00:00 | 130 | 12:00 | Sreepur | 128 | 17:00 | 122 | 01:00
| Kabirpur | 137 | 18:30 | 127 | 00:00 | Srinagar | 136 | 18:30 | 132 | 00:00
| Kachua | 127 | 23:00 | 116 | 02:00 | SSM | 138 | 19:00 | 132 | 13:00
| Kaliakoir | 138 | 18:30 | 131 | 01:00 | Sunamganj | 127 | 10:00 | 121 | 19:30
| Kallyanpur | 134 | 19:00 | 130 | 00:00 | Sylhet | 130 | 09:00 | 128 | 00:00
| Kalurghat | 134 | 00:00 | 129 | 07:00 | Tangail | 134 | 18:30 | 125 | 08:00
| Kamrangirchar | 136 | 19:00 | 128 | 23:00 | Thakurgaon | 129 | 20:00 | 108 | 01:00
| Kaptai | N/A | N/A | N/A | N/A | TK | 133 | 00:00 | 129 | 07:00
| Kazla | 133 | 20:00 | 129 | 00:00 | Tongi | 150 | 17:00 | 122 | 17:00
| Keranigonj | 136 | 19:00 | 132 | 00:00 | Ullon | 134 | 19:30 | 130 | 01:00
| Khagrachori | 134 | 00:00 | 128 | 07:00 | Uttara | 133 | 19:00 | 129 | 00:00
| Khulna | 137 | 06:00 | 128 | 22:00 | UttaraNew | 134 | 19:00 | 127 | 00:00
| Khulna(S) | 137 | 06:00 | 130 | 21:00 | Zigatola | 136 | 19:00 | 131 | 00:00
| Khulshi | 132 | 00:00 | 127 | 07:00
| Kishoreganj | 131 | 17:00 | 123 | 01:00
| Kodda | 138 | 18:30 | 126 | 01:00
| KSRM | 134 | 17:00 | 128 | 03:00
| Kulaura | 131 | 09:00 | 129 | 00:00
| Kurigram | 128 | 06:00 | 114 | 01:00
| Kushtia | 133 | 06:00 | 125 | 21:00

## L-Curve
Date | 2023-09-08
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1290 | 7041 | 5700 | 12741 |  |  |  | QF-LDC-11
0:30 | 1278 | 6602.5 | 5797 | 12399.5 | Date: | 2023-09-08
1:00 | 1266 | 6164 | 5894 | 12058
1:30 | 1268 | 6178.5 | 5853.5 | 12032
2:00 | 1270 | 6193 | 5813 | 12006
2:30 | 1255 | 6224 | 5725.5 | 11949.5 | [5 empty] | Gen. at Eve. Peak | 13259 | 13259 MW (21:00 )
3:00 | 1240 | 6255 | 5638 | 11893 | [6 empty] | 21:00
3:30 | 1185 | 6292 | 5533.5 | 11825.5 | [5 empty] | Gen. at Day Peak | 10585 | 10585 MW (12:00 )
4:00 | 1130 | 6329 | 5429 | 11758 | [6 empty] | 12:00
4:30 | 1125 | 6360 | 5360 | 11720 | [5 empty] | Highest Generation | 13259
5:00 | 1120 | 6391 | 5291 | 11682 | [6 empty] | 21:00
5:30 | 1115 | 6256 | 5247.5 | 11503.5
6:00 | 1110 | 6121 | 5204 | 11325
6:30 | 1137 | 6020.5 | 5073.5 | 11094
7:00 | 1164 | 5920 | 4943 | 10863
7:30 | 1187 | 5784.5 | 4879.5 | 10664
8:00 | 1210 | 5649 | 4816 | 10465
8:30 | 1265 | 5516.5 | 4826.5 | 10343
9:00 | 1320 | 5384 | 4837 | 10221
9:30 | 1330 | 5449.5 | 4828.5 | 10278
10:00 | 1340 | 5515 | 4820 | 10335
10:30 | 1290 | 5577.5 | 4805 | 10382.5
11:00 | 1240 | 5640 | 4790 | 10430
11:30 | 1155 | 5753.5 | 4754 | 10507.5
12:00 | 1070 | 5867 | 4718 | 10585
12:30 | 1197 | 6060.5 | 4827.5 | 10888
13:00 | 1324 | 6254 | 4937 | 11191
13:30 | 1412 | 6064.5 | 4907.5 | 10972
14:00 | 1500 | 5875 | 4878 | 10753
14:30 | 1469 | 5938.5 | 4820 | 10758.5
15:00 | 1438 | 6002 | 4762 | 10764
15:30 | 1434 | 5770.5 | 4823 | 10593.5
16:00 | 1430 | 5539 | 4884 | 10423
16:30 | 1405 | 5557.5 | 4840 | 10397.5
17:00 | 1380 | 5576 | 4796 | 10372
17:30 | 1285 | 5567.5 | 4774.5 | 10342
18:00 | 1190 | 5559 | 4753 | 10312
18:30 | 1215 | 6242.5 | 5247 | 11489.5
19:00 | 1240 | 6926 | 5741 | 12667
19:30 | 1220 | 7115 | 5894 | 13009
20:00 | 1030 | 7195 | 5792 | 12987 |  |  |  | Executive Engineer
20:30 | 1080 | 7360 | 5763 | 13123 |  |  |  | Network Operation Division
21:00 | 1130 | 7525 | 5734 | 13259
21:30 | 1140 | 7497 | 5744.5 | 13241.5
22:00 | 1150 | 7469 | 5755 | 13224 |  |  |  |  | Page 6 of 7
22:30 | 1200 | 7318.5 | 5767 | 13085.5
23:00 | 1250 | 7168 | 5779 | 12947
23:30 | 1270 | 7104.5 | 5739.5 | 12844
24:00 | 1290 | 7041 | 5700 | 12741
13259 MW (21:00 )
10585 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-09-08 |  | Energy |  | 278054392
QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3984 | 807 | 2286 | 0 | 1569 | 3390 | 197 | 121 | 229 | 156 | 0 | 2 | 419.245
0:30 | 3686.5 | 864 | 2329.5 | 0 | 1400 | 3448.5 | 200.5 | 120.5 | 189 | 154 | 0 | 7 | 898.1775 |  | Date: | 43715
1:00 | 3389 | 921 | 2373 | 0 | 1231 | 3507 | 204 | 120 | 149 | 152 | 0 | 12 | 1377.11
1:30 | 3379.5 | 921 | 2372.5 | 0 | 1222 | 3534.5 | 204 | 120 | 117 | 150 | 0 | 11.5 | 1306.44 | [8 empty] | Total Energy | 278.0544 | 278.0544 | Total Energy Gen 278.054 MKWHr Energy Not Served 6.943 MKWHr Energy Requirement 284.998 MKWHr
2:00 | 3370 | 921 | 2372 | 0 | 1213 | 3562 | 204 | 120 | 85 | 148 | 0 | 11 | 1235.77 | [8 empty] | Energy not Served | 6.9432 | 6.9432
2:30 | 3381.5 | 921 | 2383.5 | 0 | 1166.5 | 3531 | 204.5 | 120.5 | 85 | 145 | 0 | 11 | 1194.2275 | [8 empty] | Energy Requirement | 284.9976 | 284.9976
3:00 | 3393 | 921 | 2395 | 0 | 1120 | 3500 | 205 | 121 | 85 | 142 | 0 | 11 | 1152.685
3:30 | 3399.5 | 920.5 | 2387.5 | 0 | 1126.5 | 3434.5 | 205 | 121.5 | 85 | 136 | 0 | 9.5 | 1073.8975 | [7 empty] | Shortage
4:00 | 3406 | 920 | 2380 | 0 | 1133 | 3369 | 205 | 122 | 85 | 130 | 0 | 8 | 995.11
4:30 | 3432 | 920.5 | 2374.5 | 0 | 1130 | 3305.5 | 205 | 122 | 85 | 128 | 0 | 17.5 | 888.15
5:00 | 3458 | 921 | 2369 | 0 | 1127 | 3242 | 205 | 122 | 85 | 126 | 0 | 27 | 781.19
5:30 | 3317 | 920.5 | 2296 | 0 | 1158 | 3273 | 204.5 | 117.5 | 85 | 113 | 0 | 19 | 569.6575
6:00 | 3176 | 920 | 2223 | 0 | 1189 | 3304 | 204 | 113 | 85 | 100 | 0 | 11 | 358.125
6:30 | 3116 | 921 | 2180 | 0 | 1127.5 | 3287 | 138.5 | 117.5 | 80 | 106 | 12.5 | 8 | 273.13 | [6 empty] | Coal
7:00 | 3056 | 922 | 2137 | 0 | 1066 | 3270 | 73 | 122 | 75 | 112 | 25 | 5 | 188.135
7:30 | 3057 | 921.5 | 2116.5 | 0 | 946.5 | 3215.5 | 71.5 | 123 | 61.5 | 104 | 44.5 | 2.5 | 144.205 | [5 empty] | Oil
8:00 | 3058 | 921 | 2096 | 0 | 827 | 3161 | 70 | 124 | 48 | 96 | 64 | 0 | 100.275
8:30 | 3038.5 | 921.5 | 2076.5 | 0 | 785.5 | 3091.5 | 70 | 124 | 48.5 | 96 | 91 | 0 | 85.95
9:00 | 3019 | 922 | 2057 | 0 | 744 | 3022 | 70 | 124 | 49 | 96 | 118 | 0 | 71.625
9:30 | 3006.5 | 921.5 | 2055 | 0 | 769 | 2969.5 | 133.5 | 124 | 65 | 105 | 123 | 6 | 35.8125
10:00 | 2994 | 921 | 2053 | 0 | 794 | 2917 | 197 | 124 | 81 | 114 | 128 | 12 | 0
10:30 | 2997 | 921 | 2002.5 | 0 | 796 | 2987.5 | 199.5 | 123 | 76.5 | 119 | 153.5 | 7 | 0
11:00 | 3000 | 921 | 1952 | 0 | 798 | 3058 | 202 | 122 | 72 | 124 | 179 | 2 | 0
11:30 | 3010 | 920.5 | 1972 | 0 | 811.5 | 3115.5 | 202 | 125 | 75 | 126 | 148.5 | 1.5 | 0
12:00 | 3020 | 920 | 1992 | 0 | 825 | 3173 | 202 | 128 | 78 | 128 | 118 | 1 | 0
12:30 | 3120 | 920.5 | 2071.5 | 0 | 829 | 3244 | 199.5 | 124.5 | 79 | 133 | 166.5 | 0.5 | 0
13:00 | 3220 | 921 | 2151 | 0 | 833 | 3315 | 197 | 121 | 80 | 138 | 215 | 0 | 0
13:30 | 3220 | 921 | 2151 | 0 | 833 | 3315 | 197 | 121 | 80 | 138 | 215 | 0 | 0
14:00 | 3220 | 921 | 2151 | 0 | 833 | 3315 | 197 | 121 | 80 | 138 | 215 | 0 | 0
14:30 | 3090 | 921 | 2027 | 0 | 879 | 3323 | 198 | 121 | 93 | 135 | 188.5 | 2 | 0
15:00 | 2960 | 921 | 1903 | 0 | 925 | 3331 | 199 | 121 | 106 | 132 | 162 | 4 | 0
15:30 | 2984.5 | 920.5 | 1944.5 | 0 | 935 | 3116 | 199 | 121 | 92.5 | 131 | 145.5 | 4 | 0
16:00 | 3009 | 920 | 1986 | 0 | 945 | 2901 | 199 | 121 | 79 | 130 | 129 | 4 | 0
16:30 | 3056.5 | 921 | 2010.5 | 0 | 890 | 2896 | 199 | 121 | 87.5 | 130 | 81 | 5 | 0
17:00 | 3104 | 922 | 2035 | 0 | 835 | 2891 | 199 | 121 | 96 | 130 | 33 | 6 | 0
17:30 | 3136 | 921.5 | 1967.5 | 0 | 844 | 2894 | 199 | 122 | 107.5 | 130 | 17 | 3.5 | 0
18:00 | 3168 | 921 | 1900 | 0 | 853 | 2897 | 199 | 123 | 119 | 130 | 1 | 1 | 0
18:30 | 3272.5 | 921 | 1999.5 | 0 | 1505 | 3023.5 | 199 | 122 | 304.5 | 141 | 0.5 | 1 | 0
19:00 | 3377 | 921 | 2099 | 0 | 2157 | 3150 | 199 | 121 | 490 | 152 | 0 | 1 | 0
19:30 | 3303 | 921 | 1919 | 0 | 2733 | 3141 | 199 | 123 | 516 | 150 | 0 | 4 | 0
20:00 | 3348 | 920 | 1936 | 0 | 2662 | 3138 | 199 | 122 | 496 | 160 | 0 | 6 | 0
20:30 | 3527.5 | 849 | 2106.5 | 0 | 2515 | 3163 | 199 | 122 | 476 | 160 | 0 | 5 | 19.5
21:00 | 3707 | 778 | 2277 | 0 | 2368 | 3188 | 199 | 122 | 456 | 160 | 0 | 4 | 39
21:30 | 3771 | 777.5 | 2292.5 | 0 | 2271 | 3190 | 199 | 122 | 455 | 159 | 0 | 4.5 | 46.24
22:00 | 3835 | 777 | 2308 | 0 | 2174 | 3192 | 199 | 122 | 454 | 158 | 0 | 5 | 53.48
22:30 | 3857.5 | 791.5 | 2249.5 | 0 | 2058.5 | 3223 | 198 | 121.5 | 429 | 153 | 0 | 4 | 152.3225
23:00 | 3880 | 806 | 2191 | 0 | 1943 | 3254 | 197 | 121 | 404 | 148 | 0 | 3 | 251.165
23:30 | 3932 | 806.5 | 2238.5 | 0 | 1756 | 3322 | 197 | 121 | 316.5 | 152 | 0 | 2.5 | 335.205 |  | Max Temp. in Dhaka |  | 32.5°C
24:00 | 3984 | 807 | 2286 | 0 | 1569 | 3390 | 197 | 121 | 229 | 156 | 0 | 2 | 419.245
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 278.054 MKWHr Energy Not Served 6.943 MKWHr Energy Requirement 284.998 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-09-08
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 129 | 129 | 130 | 130 | 130 | 129 | 73 | 70 | 70 | 122 | 127 | 127 | 122 | 124 | 124 | 124 | 124 | 124 |  | 124 | 124 | 124 | 124 | 124 | 122 | 122 | 2805491
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 0 |  |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1556000
3 | Chattogram TPP-1 | 110 | 113 | 105 | 105 | 107 | 111 | 113 | 113 | 109 | 113 | 113 | 110 | 110 | 113 | 105 | 108 | 109 | 114 |  | 108 | 105 | 108 | 105 | 111 | 110 | 108 | 2500000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [7 empty] | 1 | 8 | 8 | 8 |  | 17 | 17 | 17 | 17 | 17 | 8 | 8 | 175111
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 0 | 0 | 1 | 3 | 12 | 2 | 3 | 3 | 4 | 2 | 1 | [9 empty] | 36045
6 | Sikalbaha 225MW CCPP (Gas) | 222 | 222 | 224 | 226 | 226 | 226 | 226 | 226 | 226 | 228 | 226 | 224 | 224 | 226 | 226 | 223 | 226 | 222 |  | 227 | 226 | 225 | 225 | 224 | 227 | 227 | 5289429
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [14 empty] | 10 | [11 empty] | 7463
12 | Hathazari 100 MW peaking PP | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 32 | 33 | 33 | 24 | 30 | 32 | 32 | 31 | 31 | 48 | 64 |  | 66 | 58 | 49 | 49 | 49 | 49 | 41 | 953424
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 428218
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 93 | 94 | 94 | 95 | 93 | 95 | 95 | 97 | 62 | 60 | 60 | 39 | 94 | 38 | 38 | 62 | 61 | 39 |  | 36 | 36 | 40 | 97 | 96 | 37 | 97 | 1898000
17 | Siddhirganj 335 MW CCPP | 326 | 327 | 328 | 327 | 327 | 305 | 280 | 280 | 280 | 280 | 280 | 322 | 321 | 260 | 260 | 300 | 300 | 270 |  | 280 | 260 | 260 | 328 | 331 | 330 | 330 | 7359585
18 | Kodda 300 MW PP Unit-2 (Summit) | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 17 | 35 | 15 | 15 |  | 85 | 130 | 130 | 63 | 60 | 60 | 57 | 1093964
19 | Ashuganj 195 MW PP (APSCL-United) | 199 | 199 | 199 | 197 | 197 | 197 | 158 | 160 | 160 | 160 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 |  | 197 | 197 | 197 | 197 | 197 | 197 | 197 | 4282182
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 180 | 180 | 210 | 209 | 210 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 3895500
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 155 | 232 | 280 | 370 | 385 | 480 | 600 | 490 | 365 | 264 | 426 | 557 | 554 | 557 | 612 | [9 empty] | 67 | 200 | 6267272
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 45 | 45 | 45 | 47 | 46 | 47 | 48 | 48 | 48 |  | 49 | 49 | 49 | 49 | 49 | 48 | 46 | 1146456
33 | Ashuganj 225 MW CCPP | 194 | 182 | 180 | 177 | 193 | 177 | 177 | 177 | 177 | 177 | 177 | 197 | 183 | 176 | 173 | 150 | 150 | 150 |  | 205 | 204 | 202 | 204 | 204 | 178 | 178 | 4454000
34 | Ashuganj 450 MW CCPP(South) | 330 | 320 | 305 | 305 | 325 | 275 | 275 | 275 | 275 | 275 | 275 | 310 | 305 | 270 | 275 | 275 | 275 | 310 |  | 300 | 280 | 295 | 305 | 310 | 275 | 305 | 7176000
| Ashuganj 450 MW CCPP(North) | [12 empty] | 38 | 10 | 10 | 10 | 10 | 40 |  | 90 | 95 | 115 | 165 | 255 | 360 | 305 | 1390700
| Ashuganj 420 MW CCPP(East) | [25 empty] | 0 | 0
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 410 | 410 | 411 | 414 | 411 | 413 | 345 | 344 | 344 | 344 | 344 | 323 | 400 | 406 | 377 | 374 | 375 | 357 |  | 390 | 327 | 326 | 396 | 414 | 418 | 414 | 9291770
Meghnaghat Unique power
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 400 | 400 | 360 | 360 | 360 | 370 | 420 | 370 | 370 | 400 | 400 | 330 |  | 450 | 360 | 360 | 450 | 450 | 450 | 450 | 9600800
41 | Haripur 360 MW CCPP(HPL) | 332 | 332 | 332 | 332 | 332 | 302 | 302 | 302 | 304 | 303 | 273 | 290 | 332 | 302 | 281 | 282 | 282 | 292 |  | 271 | 252 | 264 | 343 | 332 | 292 | 332 | 7436000
42 | RPCL 210MW CCPP | 81 | 80 | 80 | 79 | 82 | 83 | 35 | 35 | 34 | 34 | 34 | 35 | 33 | 33 | 34 | 34 | 34 | 45 |  | 58 | 58 | 57 | 99 | 95 | 93 | 96 | 1312320
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 1 | 13 | 7 | 10 | 20 | 36 | 22 | 23 | 27 | 11 | 2 | 0 | [8 empty] | 183220
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 717000
45 | Fenchugonj CCPP Phase-2 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 917640
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 61 | 61 | 61 | 61 | 61 | 60 | 61 | 61 | 61 | 61 | 61 | 60 | 60 | 61 | 61 | 60 | 61 | 60 |  | 61 | 61 | 60 | 59 | 59 | 59 | 59 | 1451424
48 | Shahjibazar 86 MW PP (Shahjibazar) | 78 | 78 | 78 | 78 | 75 | 75 | 75 | 75 | 75 | 75 | 78 | 78 | 78 | 78 | 78 | 81 | 86 | 86 |  | 86 | 86 | 86 | 86 | 84 | 84 | 84 | 1894080
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 182 | 184 | 184 | 184 | 184 | 184 | 184 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 186 | 183 | 183 |  | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 3758140
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 405000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 252720
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 195360
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 47 | 47 | 47 | 47 | 44 | 44 | 44 | 44 | 44 | 22 | 22 | 49 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1096200
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 371112
57 | Bibiana-II 341 MW CCPP (Summit) | 305 | 300 | 300 | 280 | 300 | 270 | 280 | 280 | 285 | 280 | 275 | 280 | 310 | 220 | 295 | 295 | 300 | 280 |  | 300 | 275 | 270 | 290 | 290 | 270 | 290 | 7000000
| Bibiyana South 400 MW | 15 | 25 | 40 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 40 | 42 | 50 | 85 | 100 |  | 111 | 122 | 126 | 143 | 150 | 205 | 300 | 1829300
58 | Nababganj 55 MW PP (Southern power ) | [10 empty] | 5 | 17 | 17 | 17 | 17 | 35 | 17 | 17 |  | 35 | 35 | 35 | 35 | 55 | 55 | 55 | 394968
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 149040
60 | Barabkunda 22 MW PP (Regent) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 297552
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 15 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 18 | 412452
62 | Tangail 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 16 |  | 16 | 16 | 17 | 16 | 16 | 16 | 16 | 365292
63 | Impoprt (Tripura) | 152 | 148 | 142 | 130 | 126 | 100 | 112 | 96 | 96 | 114 | 124 | 128 | 138 | 124 | 132 | 130 | 130 | 130 |  | 152 | 150 | 160 | 160 | 158 | 148 | 156 | 3233280
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 38 | 38 | 40 | 42 | 38 | 38 | 38 | 37 | 32 | 32 | 34 | 42 | 33 | 33 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 963360
65 | Feni 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 13 | 13 | [5 empty] | 8 | 16 | 16 | 16 |  | 16 | 16 | 16 | 18 | 18 | 18 | 18 | 285768
66 | Feni 11 MW PP (Doreen) | 0 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | [5 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 204660
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 818900
68 | Cumilla 25 MW PP (Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 287500
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456000
70 | Summit Madhabdi | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 10 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 19 | 19 | 19 | 19 | 19 | 19 | 358920
71 | Maona 33 MW PP(Summit) | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 616100
72 | Rupganj 33 MW PP(Summit) | 32 | 32 | 32 | 32 | 32 | 31 | 32 | 33 | 33 | 33 | 32 | 32 | 32 | 32 | 32 | 16 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 747100
73 | Ghorashal 108 MW PP (Regent) | 74 | 75 | 76 | 76 | 77 | 75 | 75 | 75 | 72 | 75 | 76 | 80 | 80 | 80 | 77 | 75 | 75 | 79 |  | 79 | 76 | 76 | 77 | 77 | 77 | 77 | 1796090
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 425220
| Chowmuhani 113 MW | 15 | 9 | 9 | 9 | 9 | 8 | 9 | 9 | 9 | 9 | 17 | 27 | 30 | 28 | 29 | 29 | 34 | 36 |  | 68 | 68 | 76 | 78 | 78 | 78 | 24 | 734160
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 24 | 54 | 17 | 17 |  | 80 | 126 | 126 | 54 | 54 | 54 | 54 | 874080
77 | Siddhirganj 100 PP(Dutch Bangla) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 17 | 17 | 17 | 17 | 17 |  | 18 | 24 | 25 | 20 | 8 | 8 | 8 | 271680
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 18 | 25 | 25 | 25 | 25 | 25 | 8 | 284640
79 | Kodda 150 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 |  | 149 | 149 | 98 | 82 | 82 | 32 | 32 | 1097280
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 51 | 51 | 51 | 51 | 51 | 51 | 24 | 24 | 8 | 8 | 8 | 8 | 9 | 24 | 21 | 26 |  | 47 | 51 | 51 | 46 | 51 | 51 | 51 | 880954
| Gazipur 100 MW PP | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 28 | 35 |  | 63 | 88 | 105 | 70 | 70 | 70 | 35 | 1032000
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 1 | 1 | 2 | 3 | 4 | 2 | 1 | 2 | 1 | 0 | [9 empty] | 17043
| Jodiac Power | 17 | 17 |  |  |  | 1 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 22 | 54 | 54 | 54 | 17 | 17 | 17 | 463187
| Karnaphuli Power Ltd. | 48 | 48 | 44 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 64 | 66 | 60 | 55 | 55 | 1318100
82 | Madanganj 102 PP(Summit) | 82 | 82 | 82 | 82 | 82 | 82 | 80 | 30 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 28 | 17 | 17 |  | 42 | 82 | 82 | 26 | 17 | 28 | 64 | 952339
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 35 | 33 | 33 | 34 | 34 | 34 | 29 | [12 empty] | 17 | 45 | 33 | 20 | 25 | 33 | 34 | 414224
86 | Meghnaghat CCPP ( Summit) | 27 | 27 | 44 | 43 | 3 | 0 | [13 empty] | 5 | 5 | 4 | 5 | 18 | 28 | 28 | 252247
87 | Meghnaghat 100 MW(IEL) | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 8 | 8 | 9 | 8 | 8 | 9 | 8 | 8 | 40 | 12 | 8 |  | 28 | 66 | 61 | 66 | 61 | 54 | 49 | 486720
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 418560
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 523800
92 | Fenchuganj 44 MW (Energyprima) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 40 | 40 | 39 | 42 | 42 | 42 | 42 | 43 | 43 | 43 |  | 43 | 40 | 40 | 40 | 43 | 40 | 43 | 1009152
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1199048
94 | Gagnagar 102 MW PP (Digital Power) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 25 | 8 | 8 | 8 |  | 50 | 50 | 25 | 8 | 8 | 58 | 58 | 433296
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 152160
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 376124
100 | Manikganj 55 MW PP (Northern) | [9 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 17 | 0 | 446305
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 112 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 112 | 80 | 80 | 80 | 112 | 80 |  | 80 | 80 | 80 | 112 | 112 | 80 | 112 | 2363564
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 |  | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 6300
103 | Kamalaghat 54 MW PP(Banco Energy) | [9 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 35 | 54 | 54 | 54 | 54 | 35 | 0 | 395280
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 68 | 67 | 68 | 68 | 68 | 68 | 68 | 68 | 67 | 68 | 86 | 87 | 87 | 88 | 87 | 87 | 87 | 87 |  | 142 | 150 | 162 | 163 | 164 | 67 | 68 | 2136000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 92 | 135 | 135 | 145 | 149 | 75 | 17 | 935568
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 583680
116 | Chandpur 200 MW (Desh energy) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 52 | 70 | 72 | 75 | 78 | 77 | 72 | 70 | 68 |  | 84 | 102 | 104 | 104 | 103 | 103 | 72 | 1535520
117 | Ashuganj 150 MW PP (Midland) | 35 | 26 | 26 | 25 | 26 | 26 | 26 | 25 | 26 | 21 | 18 | 20 | 18 | 20 | 18 | 20 | 28 | 42 |  | 77 | 140 | 130 | 150 | 150 | 150 | 45 | 1160872
118 | Bibiyana-III 400 MW CCPP | 385 | 370 | 368 | 368 | 382 | 319 | 319 | 319 | 319 | 319 | 319 | 317 | 367 | 368 | 317 | 322 | 363 | 404 |  | 319 | 319 | 324 | 369 | 366 | 368 | 368 | 8406000
| Jamalpur 115 MW PP (United) | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | [9 empty] | 94 | 85 | 85 | 85 | 85 | 19 | 19 | 549600
| Anwara 300 MW PP (United) | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 70 | 70 | 70 | 30 | 30 | 30 | 30 | 66 | 66 | 69 | 65 |  | 255 | 257 | 264 | 264 | 124 | 87 | 87 | 2100109
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 614400
| Anlima Energy Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 667418
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 442800
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 5 | 7 | 6 | 11 | 19 | 12 | 16 | 8 |  | 9 | 3 | [9 empty] | 101025
| Chandpur 115(Doreen) | [25 empty] | 0 | 0
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 433080
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [7 empty] | 17 |  |  | 7 |  | 88 | 88 | 160 | 160 | 160 | 160 | 17 | 824654
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 12 | 11 | 11 | 8 | 27 | 11 | 5 |  | 0 | 12 | 2 | 1 | 0 | 0 | 4 | 4 | 6 | 1 |  | 1 | 4 | 6 | 4 | 5 | 3 | 2 | 150240
Matarbari 2*600 MW (CPGCL)
120 | Eastern Zone Total | 6164 | 6193 | 6255 | 6329 | 6391 | 6121 | 5920 | 5649 | 5384 | 5515 | 5640 | 5867 | 6254 | 5875 | 6002 | 5539 | 5576 | 5559 |  | 6926 | 7115 | 7195 | 7525 | 7469 | 7168 | 7041 | 149282337
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 81 | 81 | 79 | 80 | 80 | 80 | 79 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 |  |  |  |  | 47 | 65 | 32 | 16 | 16 | 16 | 47 | 883200
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL) | 120 | 120 | 121 | 122 | 122 | 113 | 122 | 124 | 124 | 124 | 122 | 128 | 121 | 123 | 121 | 121 | 121 | 123 |  | 121 | 123 | 122 | 122 | 122 | 121 | 121 | 2705636
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 19 | 10 | 10 | 10 | 10 | 10 | [13 empty] | 45 | 39 | 10 | 10 | 10 | 10 | 10 | 146400
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 53 | 53 | 53 | 53 | 53 | 53 | 17 | 17 | [11 empty] | 5 | 29 | 40 | 35 | 35 | 35 | 37 | 573120
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 0 | 3 | 6 | 18 | 23 | 23 | 33 | 31 | 26 | 17 | 12 | 6 | 1
131 | Rampal 1320 MW (BIFPCL) | 521 | 524 | 524 | 522 | 522 | 522 | 522 | 524 | 521 | 523 | 520 | 517 | 519 | 514 | 399 | 411 | 406 | 403 |  | 402 | 403 | 402 | 402 | 402 | 402 | 403 | 11418180
132 | United Payra Power Ltd. | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 72 | 135 | 135 | 72 | 54 | 54 | 100 | 1016400
133 | Bhola Nutan Biddut BD LTD (GAS) | 221 | 222 | 222 | 223 | 220 | 222 | 222 | 180 | 180 | 180 | 180 | 180 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 3815073
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [12 empty] | 32 | 32 |  |  |  | 32 | 32 | 206400
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 130 | 130 | 130 | 130 | 130 | 70 | 80 | 80 | 80 | 70 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 130 | 130 | 130 | 130 | 130 | 130 | 123 | 2452000
140 | Bhola 33 MW PP (Venture) | 31 | 27 | 23 | 24 | 24 | 22 | 19 | 18 | 18 | 18 | 18 | 19 | 19 | 20 | 18 | 18 | 16 | 19 |  | 25 | 25 | 26 | 27 | 28 | 30 | 30 | 527296
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 24 | 24 | 24 | 24 | 24 | 24 | 8 | 8 | [11 empty] | 32 | 32 | 32 | 8 | 8 | 8 | 32 | 300000
143 | Gopalganj 100 MW Peaking PP | 20 | [18 empty] | 11 | 11 | 11 | 10 | 10 | 10 | 10 | 84224
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 921 | 921 | 921 | 920 | 921 | 920 | 922 | 921 | 922 | 921 | 921 | 920 | 921 | 920 | 921 | 920 | 922 | 921 |  | 921 | 921 | 920 | 778 | 777 | 806 | 807 | 21876363
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 1244 | 1244 | 1244 | 1244 | 1244 | 1200 | 1050 | 1050 | 1040 | 1040 | 1020 | 1000 | 1040 | 1030 | 1050 | 1200 | 1200 | 1200 |  | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 29717200
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4395800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 35 | [18 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 235103
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 1 | 1 | 0 | 0 | [8 empty] | 7740
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 156 | 156 | 156 | 156 | 156 | 158 | 160 | 160 | 160 | 160 | 161 | 161 | 160 | 160 | 161 | 161 | 160 | 160 |  | 164 | 165 | 164 | 164 | 164 | 164 | 164 | 4059564
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 138 | 137 | 138 | 141 | 142 | 142 | 141 | 143 | 143 | 142 | 141 | 140 | 137 | 135 | 137 | 142 | 144 | 147 |  | 148 | 152 | 152 | 156 | 164 | 165 | 165 | 3701000
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 352 | 361 | 370 | 376 | 388 | 340 | 340 | 340 | 340 | 340 | 300 | 300 | 346 | 300 | 250 | 300 | 300 | 270 |  | 300 | 260 | 270 | 387 | 414 | 380 | 380 | 8293381
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [19 empty] | 5 | 10 | 14 | 21 | 19 | 19 | 19 | 79429
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 193878
165 | Amnura 50 MW PP(Sinha) | 28 | 28 | 28 | 28 | 21 | 21 | [19 empty] | 0 | 166960
166 | Katakhali 50 MW PP (Northern) | 42 | 42 | 42 | 42 | 42 | 42 | 8 | [12 empty] | 42 | 8 | 8 | 8 | 8 | 8 | 42 | 373286
167 | Katakhali 50 MW Peaking PP | [19 empty] | 32 | 32 | 32 | 31 | 31 | 31 | 31 | 157328
168 | Santahar 50 MW Peaking PP | [19 empty] | 24 | 24 | 24 | 24 | 24 | 24 |  | 108545
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [12 empty] | 52 | 52 | 8 | 8 | 8 | 8 | 8 | 150960
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 35 | 70 | 63 | 34 | 34 | 34 | 34 | 269424
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 |  |  |  | 27 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  |  |  | 22 | 70 | 65 | 70 | 70 | 70 | 35 | 841344
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 |  |  |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  |  |  | 70 | 70 | 75 | 75 | 75 | 75 | 35 | 838944
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 | 34 | 34 | [13 empty] | 72 | 73 | 88 | 94 | 95 | 95 | 95 | 712022
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 1 | 3 | 4 | 4 | 5 | 5 | 3 | 3 | 1 | 0 | [8 empty] | 35270
178 | Energypac Power Venture Thakurgaon Ltd. | [19 empty] | 31 | 72 | 80 | 113 | 114 | 114 | 0 | 523200
| Intraco Solar 30 MW | [5 empty] | 0 | 3 | 4 | 18 | 15 | 11 | 11 | 16 | 13 | 13 | 5 | 3 | 0 | [8 empty] | 109302
| Adani Power Jharkhanda Ltd | 1407 | 1382 | 1272 | 1053 | 911 | 922 | 918 | 917 | 916 | 910 | 912 | 919 | 1022 | 1024 | 1090 | 1110 | 1105 | 1114 |  | 1324 | 1314 | 1312 | 1362 | 1366 | 1361 | 1363 | 27087273
178 | Teesta Solar Limited | [6 empty] | 12 | 32 | 65 | 60 | 86 | 15 | 118 | 125 | 95 | 85 | 17 | 0 |  | 0 | [6 empty] | 710810