## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-09-16 | Saturday
|  | Date (day): | 2023-09-16 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13411.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15335 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-09-15 | 2023-09-16 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 170 | 210 | 200 | 200
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  |  | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 76 | 83 | 82 | 85 | 23 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 353 | 409 | 0 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 272 | 332 | 330 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 48 | 72 | 72 | 28 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 286 | 285 | 300 | 300 | 35 |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 83 | 85 | 85 | 17 |  | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 15 | 15 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 55 | 55 | 20 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 185 | 74 |  | 136 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 40 | 92 | 92
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 320 | 330 | 330
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 25 | 91 | 50 | 92 |  | 10 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 54 | 17 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 82 | 32 | 48 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 35 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 19 | 38 | 38 | 38 |  | 42 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 30 | 24 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 8 | 8 | 25 | 27 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 20 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 130 | 80 | 130 | 170 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
33 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
34 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 149 | 17 | 149
35 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 105 | 35 | 105
36 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 72 | 53 | 72 | 32 |  | Fuel shortage
37 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 4 | 162 | 54 | 108 | 54 |  | Fuel shortage
38 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 14 | 0 | 35 | 0
39 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 6063 | 5722 | 2216 | 3291 | 2815 | 3615 | 669 | 956
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
41 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 15 | 8 | 17 | 8 |  | Fuel shortage
42 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 6 | 6 | 50
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 199 | 199 | 202 | 203
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 222 | 225 | 225
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 17 | 17 | 88 |  | Fuel shortage
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 63 | 32 | 52 | 46 |  | Fuel shortage
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 | 102 |  | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 10 | 10 | 10 | 10 | 90 |  | Fuel shortage
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 12 | 11 | 12 | 12 | 10 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 39 | 10 | 25
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 12 | 96 |  | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 66 | 175 | 70 | 280 | 20 |  | Fuel shortage
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 54 | 17 | 54
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 41 | 55 | 55 | 55 | 55 |  | Fuel shortage
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 10 | 10 | 10 | 10 | 90 |  | Fuel shortage
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 7 | 34 | 34 | 51 | 65 |  | Fuel shortage
60 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 35 | 54 | 160
| SS Power I |  | Coal | SS Power | 0 | 0 | 0 | 612 | 620 | 612 | 612 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 3 | 0 | 10 | 25 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 2605 | 2545 | 1238 | 1577 | 1421 | 1882 | 758 | 510
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 206 | 208 | 200 | 200 | 21 |  | Gas shortage
62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 310 | 310 | 310 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 270 | 305 | 305 |  |  | FGMO
64 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 46 | 48 | 43 | 48
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 145 | 78 | 108 | 108 | 87 |  | Gas shortae
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
69 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 10 | 20 | 145 |  | 5 | Engine problem
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 10 | 0 | 0 |  | 52 | Under Maint.
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
72 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 66 | 104 | 68 | 100 | 100 |  | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 18 | 16 | 17 |  | 5 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 116 | 154 | 149 | 165
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 25 | 52
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 52 | 98 | 105 | 105 |  | 9 | Engine problem
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 76 | 28 | 75 | 38 |  | Fuel shortage
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 21 | 17 | 17 |  | 37 | Engine problem
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 0 | 0 | 115 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2896 | 1382 | 1563 | 1500 | 1753 | 361 | 684
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 25 | 82 | 32 | 50 | 152 |  | Gas shortage
83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 115 | 153 | 115 | 160 | 40 |  | Fuel shortage
87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 37 | 94 | 47 | 85 | 30 |  | Fuel shortage
88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 33 | 0 | 50 | 0
89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 236 | 353 | 269.6 | 319 | 152 | 4
90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 40 | 43 | 42 | 43 |  | 27 | Machine problem.
91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 39 | 39 | 40 | 40 |  | 50 | Machine problem
92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 112 | 112 |  | 51 | ST Under maint.
93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 50 | 50
95 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 38 | 39 | 40 | 42 |  | 8 | Engine problem
96 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 5 | 11 | 11
97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 66 |  | Gas shortage
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 84 | 86 | 86
99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 187 | 181 | 185 | 185 |  | 46 | Machine problem
101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 16 | 17 | 17 | 17
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 9 |  | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 290 | 280 | 280 |  |  | FGMO
104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 405 | 368 | 400 | 400 |  |  | FGMO
105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 380 | 390 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1669 | 1644 | 1689 | 1692 | 75 | 612
107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 924 | 800 | 938 | 938
108 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 49 | 49 | 49 | 66 |  | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 40 | 25 | 40 |  | 14 | Engine problem
110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 37 | 0 | 40 | 69 |  | Fuel shortage
112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
113 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 16 | 0 | 0
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
114 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 72 | 54 | 70 | 35 |  | Fuel shortage
115 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 67 | 100 | 100 | 5 |  | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 33 | 0 | 100 | 0
117 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
118 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0 |  | 617 | Under maint
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3125 | 3121 | 957 | 1081 | 1266 | 1237 | 1051 | 631
119 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 64 | 16 | 64
120 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 21 | 29 | 23 | 31 |  | 9 | Engine problem
121 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 130 | 130 | 130 | 130 |  | 64 | ST under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
122 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1120 | 1244 | 1244 | 1244
123 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 222 | 10 | 220 | 220
124 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 135 | 35 | 150
125 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 | 307 |  | Coal shortage
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1493 | 1612 | 1668 | 1839 | 307 | 73
126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 37 | 0 | 35 | 17 |  | Fuel shortage
128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 21 |  | 50 | Engine problem
129 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 28 | 28
130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 8 | 34 | 42 | 8 |  | Fuel shortage
131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 30 | 40 | 10 |  | Fuel shortage
132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 198 | 189 | 180 | 185 | 25 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 205 | 211 | 170 | 190 | 30 |  | Gas shortage
135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 240 | 414 | 380 | 414
136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 24 | 24 | 32 | 18 |  | Fuel shortage
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 8 | 44 |  | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 93 | 50 | 91 | 13 |  | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 35 | 75 | 38 |  | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113
143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 0 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1254 | 1362 | 1300 | 1400
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 1905 | 2464 | 2366 | 2682 | 794 | 53
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 180 | 180 | 180 | 180 |  | 94 | Machine problem
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 10 | 86 | 34 | 64 | 49 |  | Fuel shortage
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 75 | 35 | 72 | 43 |  | Fuel shortage
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 132 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 359 | 341 | 417 | 316 | 217 | 179
| Total |  |  |  |  | 24911 | 24171 | 11455 | 13926 | 13411.6 | 15335 | 4384 | 3702
A. |  | 2023-09-15 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 13974 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 10711 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14050 | MW
3 | Day peak Generation : |  |  | 11455 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13463.16 | MW
4 | Evening peak Generation : |  |  | 13926 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 118 | MW
5 | Total Energy Generation : |  | 295.6935 | MKWHr | By Solar | 1.3645 | MKWHr
| By Gas : | 147.8175 | MKWHr |  | By Oil: | 36.5214 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 80.493 | MKWHr |  | By Hydro: | 4.3247 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.10704 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4384 | MW | Dhaka | 4425.56 | 4425.56 |  | 0 |  | 18:00 |  | 95.5
|  |  | For Plants S/D or M/C prob = |  |  | 3702 | MW | Chittagong | 1287 | 1287 |  | 0 |  | 19:00 |  | 164.26
|  |  | Total = |  |  | 8086 | MW | Khulna | 1656 | 1656 |  | 0 |  | 19:30 |  | 160.44
7 | Total Gas Supplied : |  |  | 1094.66 | MMCFD |  |  | Rajshahi | 1465.6 | 1465.6 |  | 0 |  | 20:00 |  | 105.05
8 | Fuel Cost : | i) Gas : | Taka | 165278274.302 | ii) Oil : | Taka | 458459905.91 | Comilla | 1380 | 1350 |  | 30 |  | 21:00 |  | 118
|  | iii) Coal : | Taka | 552748002.1 | Total | Taka | 1176486182.312 | Mymensingh | 1234 | 1186 |  | 48 |  | 22:00 |  | 168.08
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 620 | 580 |  | 40 |  | 23:00 |  | 325.655
| ii) During Peak Demand : |  |  | 890 | MW (E to W) at | 21:00 | hrs | Barisal | 440 | 440 |  | 0 |  | 24:00 |  | 549.125
| iii) Maximum : |  |  | 760 | MW at | 19:00 | hrs | Rangpur | 955 | 955 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 35°C |  |  | Total | 13463.16 | 13345.16 |  | 118
B. |  | 2023-09-16 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 35°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 14500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15335 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 12800 | MW
4 | Reserve(Generation end) |  |  |  | 835 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 306.8238 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11548 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.5884 | MKWHr. | ii) HVDC Flow at Peak Time |  | 800 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.4771 | MKWHr. | iii) Maximum HVDC Flow : |  | 925 | MW at | 6:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 107.79 |  | (b) Today: | 107.89 |  | (c) Rule Curve: |  | 102.45
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-09-15 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 210 | 0 | 0 | 82 | 0 | 413 | 337 |  | 0 | 450 | 269 | 72 | 75 | 15 | 327 | 0 | 0 | 88 | 91 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 18 | 30 | 28 | 8 | 0 | 123 | 75 | 0 | 0 | 8 | 225 | 0 | 0 | 0 |  | 6 | 23 | 0 | 12 | 0 | 6 | 12 | 39 | 0 | 0 | 0 | 280 | 305 | 195 | 108 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 158 | 47 | 0 | 16 | 0 | 43 | 40 | 47 | 43 | 112 | 0 | 0 | 81 | 0 | 185 | 17 | 0 | 10 | 300 | 16 | 5 | 0 | 47 | 0 | 0 | 68 | 0 | 17 | 0 | 10 | 34 | 115 | 403 | 18 | 17 | 17 | 0 | 70 | 17 | 59 | 17 | 9 | 10 | 400 | 45 | 0 | 17 | 19 | 0 | 17 | 0 | 0 | 17 | 0 | 53 | 0 | 622 | 12 | 0 | 0 | 0 |  | 924 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 11 | 36 | 8 | 126 | 30 | 48 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 414 | 72 | 0 | 35 | 67 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 17 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 1413 | 0 | 0 |  | 7475 | 5525 | 13000 | 3886 | 924 | 2593 | 0 | 1470 | 3459 | 198 | 120 | 180 | 158 | 0 | 12 | 719.115 | 107.76
2:00 | 0 | 0 | 210 | 0 | 0 | 82 | 0 | 419 | 337 |  | 0 | 450 | 295 | 69 | 85 | 15 | 328 | 0 | 0 | 87 | 91 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 18 | 25 | 28 | 8 | 0 | 122 | 75 | 0 | 0 | 8 | 225 | 0 | 0 | 0 |  | 6 | 23 | 0 | 12 | 0 | 6 | 12 | 39 | 0 | 0 | 0 | 280 | 305 | 209 | 108 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 160 | 46 | 0 | 17 | 0 | 43 | 40 | 47 | 43 | 112 | 0 | 0 | 81 | 0 | 185 | 17 | 0 | 10 | 265 | 16 | 5 | 0 | 47 | 0 | 0 | 68 | 0 | 17 | 0 | 10 | 34 | 102 | 403 | 18 | 17 | 17 | 0 | 70 | 17 | 64 | 17 | 9 | 10 | 400 | 35 | 0 | 17 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 621 | 6 | 0 | 0 | 0 |  | 876 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 11 | 0 | 8 | 130 | 29 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 370 | 72 | 0 | 35 | 67 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 17 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 1412 | 0 | 0 |  | 7413 | 5376 | 12789 | 3906 | 876 | 2539 | 0 | 1456 | 3457 | 197 | 122 | 70 | 160 | 0 | 6 | 652.265 | 107.77
3:00 | 0 | 0 | 210 | 0 | 0 | 82 | 0 | 416 | 337 |  | 0 | 450 | 270 | 33 | 85 | 15 | 326 | 0 | 0 | 87 | 91 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 18 | 25 | 30 | 8 | 0 | 122 | 75 | 0 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 23 | 0 | 12 | 0 | 6 | 12 | 39 | 0 | 0 | 0 | 280 | 305 | 212 | 108 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 158 | 47 | 0 | 17 | 0 | 43 | 40 | 47 | 40 | 112 | 0 | 0 | 81 | 0 | 185 | 17 | 0 | 10 | 275 | 16 | 5 | 0 | 47 | 0 | 0 | 68 | 0 | 17 | 0 | 10 | 34 | 18 | 403 | 18 | 17 | 17 | 0 | 70 | 0 | 55 | 17 | 9 | 10 | 400 | 35 | 0 | 17 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 621 | 9 | 0 | 0 | 0 |  | 923 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 11 | 0 | 8 | 122 | 28 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 370 | 72 | 0 | 0 | 67 | 34 | 0 | 0 | 0 | 1244 | 220 | 0 | 17 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 1346 | 0 | 0 |  | 7249 | 5280 | 12529 | 3902 | 923 | 2520 | 0 | 1240 | 3391 | 197 | 122 | 67 | 158 | 0 | 9 | 548.17 | 107.78
4:00 | 0 | 0 | 210 | 0 | 0 | 82 | 0 | 420 | 337 |  | 0 | 450 | 282 | 0 | 75 | 15 | 327 | 0 | 0 | 73 | 91 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 25 | 30 | 8 | 0 | 122 | 75 | 0 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 6 | 12 | 39 | 0 | 0 | 0 | 280 | 305 | 210 | 108 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 164 | 47 | 0 | 17 | 0 | 43 | 40 | 47 | 40 | 112 | 0 | 0 | 81 | 0 | 185 | 17 | 0 | 10 | 260 | 16 | 5 | 0 | 47 | 0 | 0 | 68 | 0 | 17 | 0 | 10 | 34 | 18 | 403 | 18 | 17 | 17 | 0 | 70 | 0 | 55 | 17 | 9 | 10 | 400 | 35 | 0 | 17 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 5 | 0 | 622 | 11 | 0 | 0 | 0 |  | 924 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 370 | 72 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1244 | 180 | 0 | 17 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 0 | 1359 | 0 | 0 |  | 7167 | 5116 | 12283 | 3905 | 924 | 2475 | 0 | 1060 | 3405 | 197 | 121 | 21 | 164 | 0 | 11 | 487.05 | 107.78
5:00 | 0 | 0 | 210 | 0 | 0 | 79 | 0 | 419 | 337 |  | 0 | 450 | 282 | 0 | 28 | 15 | 329 | 0 | 0 | 16 | 74 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 25 | 30 | 8 | 0 | 122 | 75 | 0 | 0 | 8 | 227 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 6 | 12 | 42 | 0 | 0 | 0 | 280 | 305 | 210 | 108 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 160 | 47 | 0 | 16 | 0 | 43 | 40 | 47 | 37 | 112 | 0 | 0 | 78 | 0 | 185 | 17 | 0 | 10 | 265 | 16 | 5 | 0 | 15 | 0 | 0 | 68 | 0 | 17 | 0 | 10 | 34 | 18 | 403 | 18 | 17 | 17 | 0 | 70 | 0 | 55 | 17 | 9 | 10 | 400 | 35 | 0 | 17 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 624 | 5 | 0 | 0 | 0 |  | 923 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 300 | 72 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1244 | 180 | 0 | 17 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 0 | 1370 | 0 | 0 |  | 7001 | 5010 | 12011 | 3919 | 923 | 2404 | 0 | 848 | 3418 | 197 | 121 | 16 | 160 | 0 | 5 | 422.11 | 107.79
6:00 | 0 | 0 | 210 | 0 | 0 | 79 | 0 | 404 | 301 |  | 0 | 400 | 280 | 0 | 17 | 15 | 329 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 25 | 30 | 8 | 0 | 122 | 75 | 0 | 0 | 8 | 225 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 6 | 12 | 33 | 0 | 0 | 0 | 280 | 270 | 210 | 108 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 140 | 46 | 0 | 17 | 0 | 43 | 40 | 47 | 38 | 80 | 0 | 0 | 78 | 0 | 184 | 17 | 0 | 10 | 270 | 16 | 5 | 0 | 15 | 0 | 0 | 68 | 0 | 17 | 1 | 10 | 34 | 18 | 402 | 18 | 17 | 17 | 0 | 70 | 1 | 55 | 17 | 9 | 10 | 400 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 621 | 5 | 0 | 0 | 0 |  | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 300 | 35 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1200 | 180 | 0 | 0 | 0 | 1 | 0 | 121 | 0 | 0 | 0 | 0 | 1283 | 1 | 0 |  | 6709 | 4774 | 11483 | 3836 | 925 | 2277 | 0 | 679 | 3284 | 197 | 121 | 16 | 140 | 3 | 5 | 382 | 107.79
7:00 | 0 | 0 | 210 | 0 | 0 | 82 | 0 | 351 | 287 |  | 0 | 360 | 276 | 0 | 17 | 15 | 326 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 25 | 30 | 8 | 0 | 65 | 0 | 0 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 6 | 12 | 37 | 0 | 0 | 0 | 280 | 270 | 211 | 108 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 128 | 32 | 0 | 18 | 0 | 43 | 40 | 47 | 37 | 80 | 0 | 0 | 78 | 0 | 185 | 17 | 0 | 10 | 270 | 16 | 5 | 0 | 15 | 0 | 0 | 68 | 0 | 17 | 3 | 10 | 34 | 18 | 402 | 18 | 17 | 17 | 0 | 70 | 17 | 55 | 17 | 8 | 10 | 398 | 17 | 15 | 17 | 17 | 0 | 17 | 5 | 0 | 17 | 0 | 0 | 0 | 625 | 6 | 0 | 0 | 0 |  | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 270 | 35 | 0 | 0 | 0 | 34 | 0 | 1 | 0 | 1000 | 180 | 0 | 0 | 0 | 15 | 0 | 121 | 0 | 0 | 6 | 0 | 1261 | 36 | 0 |  | 6478 | 4539 | 11017 | 3734 | 924 | 2191 | 0 | 685 | 3066 | 65 | 121 | 16 | 128 | 81 | 6 | 222.515 | 107.8
8:00 | 0 | 0 | 210 | 0 | 0 | 82 | 0 | 351 | 272 |  | 0 | 320 | 285 | 0 | 17 | 15 | 280 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 25 | 30 | 8 | 0 | 65 | 0 | 0 | 0 | 8 | 220 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 6 | 12 | 38 | 0 | 0 | 0 | 275 | 265 | 208 | 108 | 0 | 48 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 25 | 12 | 124 | 27 | 0 | 18 | 1 | 43 | 40 | 47 | 40 | 80 | 0 | 0 | 78 | 0 | 185 | 17 | 0 | 10 | 270 | 8 | 5 | 0 | 15 | 0 | 0 | 68 | 0 | 17 | 8 | 10 | 34 | 18 | 354 | 18 | 17 | 17 | 2 | 69 | 17 | 55 | 17 | 9 | 10 | 370 | 17 | 28 | 17 | 17 | 0 | 17 | 18 | 0 | 17 | 0 | 0 | 0 | 612 | 2 | 0 | 0 | 0 |  | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 240 | 17 | 0 | 0 | 0 | 34 | 0 | 2 | 0 | 940 | 183 | 0 | 0 | 0 | 44 | 0 | 122 | 0 | 0 | 16 | 0 | 1260 | 90 | 0 |  | 6278 | 4517 | 10795 | 3561 | 923 | 2122 | 0 | 659 | 2992 | 65 | 122 | 16 | 124 | 209 | 2 | 148.025 | 107.81
9:00 | 0 | 0 | 170 | 0 | 0 | 79 | 0 | 351 | 271 |  | 0 | 320 | 302 | 0 | 14 | 15 | 280 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 25 | 30 | 8 | 0 | 65 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 6 | 12 | 25 | 0 | 0 | 0 | 350 | 240 | 209 | 108 | 0 | 48 | 0 | 0 | 51 | 0 | 0 | 25 | 18 | 10 | 25 | 12 | 126 | 27 | 0 | 18 | 1 | 43 | 40 | 47 | 39 | 80 | 0 | 0 | 40 | 0 | 185 | 17 | 0 | 10 | 275 | 8 | 5 | 0 | 0 | 0 | 0 | 68 | 0 | 17 | 13 | 10 | 34 | 13 | 354 | 18 | 17 | 17 | 3 | 32 | 17 | 55 | 17 | 9 | 10 | 370 | 0 | 35 | 17 | 17 | 0 | 17 | 30 | 0 | 17 | 0 | 0 | 0 | 612 | 2 | 0 | 0 | 0 |  | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 240 | 0 | 0 | 0 | 0 | 10 | 0 | 3 | 0 | 940 | 182 | 0 | 0 | 0 | 59 | 0 | 121 | 0 | 0 | 24 | 0 | 1270 | 129 | 0 |  | 6172 | 4539 | 10711 | 3564 | 924 | 2088 | 0 | 506 | 3002 | 65 | 121 | 16 | 126 | 297 | 2 | 84.995 | 107.82
10:00 | 0 | 0 | 170 | 0 | 0 | 79 | 0 | 352 | 272 |  | 0 | 320 | 296 | 0 | 0 | 15 | 280 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 25 | 30 | 8 | 0 | 124 | 75 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 6 | 12 | 13 | 0 | 0 | 0 | 275 | 265 | 205 | 107 | 0 | 47 | 0 | 0 | 51 | 0 | 0 | 25 | 18 | 10 | 25 | 12 | 116 | 27 | 0 | 18 | 2 | 42 | 40 | 47 | 39 | 112 | 0 | 0 | 40 | 0 | 187 | 17 | 0 | 10 | 290 | 8 | 5 | 0 | 0 | 0 | 0 | 68 | 0 | 17 | 20 | 10 | 34 | 0 | 355 | 19 | 17 | 17 | 5 | 32 | 17 | 55 | 17 | 9 | 10 | 380 | 0 | 23 | 17 | 17 | 0 | 17 | 34 | 0 | 17 | 0 | 0 | 0 | 612 | 4 | 0 | 0 | 0 |  | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 940 | 184 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 17 | 0 | 1269 | 145 | 0 |  | 6292 | 4371 | 10663 | 3521 | 924 | 2119 | 0 | 470 | 3001 | 199 | 0 | 48 | 116 | 261 | 4 | 35.335 | 107.83
11:00 | 0 | 0 | 170 | 0 | 0 | 78 | 0 | 353 | 272 |  | 0 | 370 | 285 | 0 | 0 | 15 | 280 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 19 | 0 | 25 | 30 | 8 | 20 | 124 | 75 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 6 | 12 | 2 | 0 | 0 | 0 | 275 | 265 | 205 | 108 | 0 | 44 | 0 | 0 | 51 | 0 | 0 | 27 | 18 | 10 | 25 | 12 | 126 | 26 | 0 | 18 | 2 | 42 | 40 | 47 | 38 | 112 | 0 | 0 | 78 | 0 | 187 | 17 | 0 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 113 | 0 | 17 | 20 | 10 | 36 | 0 | 405 | 37 | 17 | 17 | 4 | 0 | 0 | 34 | 21 | 9 | 10 | 380 | 0 | 47 | 0 | 0 | 0 | 17 | 10 | 0 | 17 | 0 | 0 | 0 | 612 | 1 | 0 | 0 | 0 |  | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 960 | 184 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 22 | 0 | 1262 | 206 | 0 |  | 6418 | 4509 | 10927 | 3618 | 924 | 2192 | 0 | 454 | 3014 | 199 | 0 | 48 | 126 | 351 | 1 | 0 | 107.84
12:00 | 0 | 0 | 170 | 0 | 0 | 76 | 0 | 353 | 272 |  | 0 | 450 | 286 | 0 | 0 | 15 | 280 | 0 | 0 | 0 | 25 | 82 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 19 | 0 | 25 | 30 | 8 | 20 | 124 | 75 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 6 | 12 | 2 | 0 | 0 | 0 | 280 | 270 | 206 | 145 | 0 | 46 | 0 | 0 | 51 | 0 | 0 | 52 | 17 | 10 | 33 | 12 | 116 | 25 | 0 | 18 | 2 | 40 | 39 | 47 | 38 | 112 | 0 | 0 | 78 | 0 | 187 | 16 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 115 | 0 | 17 | 20 | 10 | 66 | 0 | 405 | 37 | 17 | 17 | 5 | 66 | 0 | 41 | 52 | 9 | 10 | 380 | 0 | 33 | 4 | 7 | 0 | 17 | 14 | 0 | 17 | 0 | 0 | 0 | 612 | 3 | 0 | 0 | 0 |  | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 240 | 0 | 0 | 0 | 0 | 10 | 0 | 6 | 0 | 1120 | 222 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 31 | 0 | 1254 | 132 | 0 |  | 6741 | 4714 | 11455 | 3696 | 924 | 2340 | 0 | 653 | 3166 | 199 | 0 | 82 | 116 | 276 | 3 | 0 | 107.85
13:00 | 0 | 0 | 210 | 0 | 0 | 76 | 0 | 387 | 330 |  | 0 | 450 | 277 | 8 | 6 | 20 | 310 | 0 | 0 | 12 | 25 | 82 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 19 | 10 | 25 | 30 | 8 | 0 | 122 | 75 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 6 | 12 | 2 | 0 | 0 | 0 | 305 | 305 | 206 | 145 | 0 | 46 | 0 | 0 | 51 | 0 | 0 | 49 | 18 | 10 | 32 | 12 | 136 | 25 | 0 | 18 | 0 | 40 | 39 | 47 | 38 | 112 | 0 | 0 | 78 | 0 | 182 | 17 | 0 | 10 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 125 | 0 | 48 | 16 | 10 | 97 | 5 | 357 | 38 | 17 | 17 | 4 | 68 | 11 | 55 | 52 | 27 | 10 | 350 | 23 | 21 | 54 | 34 | 0 | 17 | 36 | 0 | 17 | 0 | 0 | 0 | 612 | 7 | 0 | 0 | 0 |  | 924 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 350 | 10 | 0 | 0 | 0 | 33 | 0 | 6 | 0 | 1244 | 223 | 0 | 0 | 4 | 17 | 0 | 0 | 0 | 0 | 25 | 0 | 1260 | 151 | 0 |  | 7182 | 4930 | 12112 | 3689 | 924 | 2491 | 0 | 1010 | 3296 | 197 | 0 | 82 | 136 | 280 | 7 | 0 | 107.85
14:00 | 0 | 0 | 150 | 0 | 0 | 76 | 0 | 408 | 282 |  | 0 | 370 | 299 | 12 | 17 | 25 | 270 | 0 | 0 | 13 | 25 | 82 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 19 | 10 | 25 | 30 | 8 | 0 | 122 | 75 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 6 | 12 | 2 | 0 | 0 | 0 | 305 | 310 | 202 | 145 | 0 | 43 | 0 | 0 | 51 | 0 | 0 | 34 | 18 | 10 | 31 | 12 | 142 | 29 | 0 | 18 | 1 | 40 | 40 | 44 | 35 | 112 | 0 | 0 | 77 | 0 | 183 | 17 | 0 | 10 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 125 | 0 | 53 | 17 | 10 | 100 | 10 | 376 | 37 | 17 | 17 | 4 | 69 | 17 | 55 | 52 | 27 | 10 | 350 | 17 | 46 | 17 | 34 | 0 | 17 | 31 | 0 | 17 | 0 | 0 | 0 | 612 | 6 | 0 | 0 | 0 |  | 924 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 300 | 35 | 0 | 0 | 0 | 35 | 0 | 6 | 0 | 1160 | 220 | 0 | 3 | 5 | 8 | 0 | 0 | 0 | 0 | 31 | 0 | 1250 | 178 | 0 |  | 7018 | 4807 | 11825 | 3587 | 924 | 2325 | 0 | 1033 | 3202 | 197 | 0 | 82 | 142 | 327 | 6 | 0 | 107.84
15:00 | 0 | 0 | 180 | 0 | 0 | 73 | 0 | 402 | 332 |  | 0 | 420 | 282 | 9 | 17 | 25 | 312 | 0 | 0 | 9 | 25 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 19 | 10 | 25 | 30 | 8 | 0 | 120 | 75 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 305 | 305 | 203 | 173 | 0 | 41 | 0 | 0 | 51 | 0 | 0 | 32 | 18 | 10 | 32 | 12 | 150 | 30 | 0 | 18 | 1 | 40 | 39 | 44 | 35 | 112 | 0 | 0 | 77 | 0 | 180 | 17 | 0 | 10 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 116 | 0 | 22 | 18 | 10 | 76 | 10 | 403 | 37 | 17 | 17 | 3 | 70 | 17 | 55 | 52 | 28 | 10 | 350 | 22 | 19 | 35 | 34 | 0 | 17 | 23 | 0 | 17 | 0 | 0 | 0 | 612 | 6 | 0 | 0 | 0 |  | 924 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 414 | 35 | 0 | 0 | 0 | 34 | 0 | 4 | 0 | 1170 | 220 | 0 | 17 | 4 | 14 | 0 | 0 | 0 | 0 | 26 | 0 | 1258 | 136 | 0 |  | 7147 | 4879 | 12026 | 3643 | 924 | 2578 | 0 | 998 | 3220 | 195 | 0 | 64 | 150 | 248 | 6 | 0 | 107.86
16:00 | 0 | 0 | 180 | 0 | 0 | 73 | 0 | 409 | 328 |  | 0 | 420 | 274 | 8 | 17 | 25 | 270 | 0 | 0 | 9 | 25 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 19 | 10 | 25 | 30 | 8 | 0 | 120 | 75 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 6 | 11 | 19 | 0 | 0 | 0 | 310 | 305 | 204 | 173 | 0 | 42 | 0 | 0 | 15 | 0 | 0 | 32 | 18 | 10 | 32 | 12 | 144 | 32 | 0 | 18 | 1 | 40 | 39 | 44 | 35 | 112 | 0 | 0 | 83 | 0 | 180 | 17 | 0 | 10 | 275 | 16 | 11 | 0 | 0 | 0 | 0 | 67 | 0 | 17 | 3 | 10 | 68 | 10 | 329 | 19 | 17 | 17 | 2 | 70 | 17 | 44 | 52 | 28 | 0 | 350 | 28 | 7 | 35 | 34 | 0 | 17 | 16 | 0 | 17 | 0 | 0 | 0 | 612 | 6 | 0 | 0 | 0 |  | 925 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 370 | 43 | 0 | 0 | 0 | 34 | 0 | 3 | 0 | 1200 | 40 | 0 | 17 | 2 | 18 | 0 | 0 | 0 | 0 | 15 | 0 | 1266 | 91 | 0 |  | 6872 | 4658 | 11530 | 3547 | 925 | 2291 | 0 | 942 | 3258 | 195 | 0 | 64 | 144 | 158 | 6 | 100.275 | 107.87
17:00 | 0 | 0 | 140 | 0 | 0 | 76 | 0 | 410 | 328 |  | 0 | 420 | 261 | 8 | 17 | 25 | 270 | 0 | 0 | 9 | 25 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 19 | 10 | 25 | 30 | 8 | 0 | 120 | 75 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 6 | 11 | 21 | 0 | 0 | 0 | 310 | 305 | 200 | 175 | 0 | 46 | 0 | 0 | 15 | 0 | 0 | 32 | 18 | 10 | 33 | 12 | 140 | 32 | 0 | 17 | 0 | 43 | 39 | 46 | 32 | 112 | 0 | 0 | 85 | 0 | 181 | 17 | 0 | 10 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 67 | 0 | 17 | 2 | 10 | 68 | 10 | 330 | 19 | 17 | 17 | 1 | 70 | 17 | 55 | 34 | 28 | 10 | 340 | 17 | 8 | 17 | 34 | 0 | 17 | 6 | 0 | 17 | 0 | 0 | 0 | 612 | 4 | 0 | 0 | 0 |  | 923 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 370 | 17 | 0 | 0 | 0 | 34 | 0 | 1 | 0 | 1140 | 0 | 0 | 17 | 0 | 10 | 0 | 0 | 0 | 0 | 6 | 0 | 1263 | 34 | 0 |  | 6786 | 4467 | 11253 | 3555 | 923 | 2249 | 0 | 860 | 3195 | 195 | 0 | 64 | 140 | 68 | 4 | 92.635 | 107.87
18:00 | 0 | 0 | 170 | 0 | 0 | 79 | 0 | 382 | 330 |  | 0 | 370 | 303 | 8 | 17 | 25 | 240 | 0 | 0 | 9 | 32 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 19 | 19 | 10 | 25 | 24 | 8 | 0 | 121 | 75 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 6 | 11 | 26 | 0 | 0 | 0 | 320 | 305 | 171 | 177 | 0 | 47 | 0 | 0 | 15 | 0 | 0 | 16 | 18 | 10 | 33 | 12 | 152 | 32 | 0 | 18 | 0 | 43 | 39 | 28 | 39 | 80 | 0 | 0 | 65 | 0 | 182 | 17 | 0 | 10 | 275 | 16 | 11 | 0 | 0 | 0 | 0 | 76 | 0 | 40 | 0 | 10 | 51 | 10 | 340 | 19 | 17 | 17 | 0 | 60 | 17 | 55 | 17 | 28 | 10 | 350 | 17 | 0 | 17 | 34 | 0 | 27 | 0 | 0 | 17 | 0 | 5 | 0 | 624 | 0 | 0 | 0 | 0 |  | 923 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 370 | 35 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 1030 | 0 | 0 | 17 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1219 | 1 | 0 |  | 6669 | 4281 | 10950 | 3519 | 923 | 2188 | 0 | 848 | 3053 | 196 | 0 | 69 | 152 | 2 | 0 | 95.5 | 107.87
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 205 | 0 | 0 | 80 | 0 | 393 | 282 |  | 0 | 450 | 237 | 27 | 26 | 55 | 270 | 0 | 0 | 28 | 91 | 147 | 4 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 19 | 13 | 25 | 30 | 25 | 0 | 124 | 75 | 0 | 0 | 10 | 223 | 0 | 0 | 0 |  | 6 | 56 | 0 | 12 | 0 | 6 | 11 | 33 | 0 | 0 | 0 | 310 | 305 | 170 | 108 | 0 | 47 | 0 | 0 | 33 | 0 | 0 | 24 | 18 | 10 | 33 | 12 | 152 | 44 | 0 | 18 | 0 | 43 | 39 | 50 | 39 | 80 | 0 | 0 | 86 | 0 | 181 | 17 | 0 | 10 | 280 | 16 | 11 | 0 | 85 | 0 | 0 | 153 | 0 | 149 | 0 | 10 | 85 | 30 | 368 | 94 | 105 | 17 | 0 | 270 | 30 | 55 | 106 | 76 | 10 | 335 | 46 | 0 | 125 | 34 | 0 | 35 | 0 | 0 | 17 | 0 | 87 | 0 | 612 | 1 | 0 | 0 | 0 |  | 801 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 41 | 33 | 16 | 128 | 28 | 64 | 0 | 0 | 0 | 37 | 5 | 92 | 0 | 34 | 39 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 370 | 53 | 0 | 35 | 67 | 83 | 0 | 0 | 50 | 1160 | 0 | 0 | 135 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 1315 | 0 | 0 |  | 8197 | 5281 | 13478 | 3677 | 801 | 2166 | 0 | 2654 | 3267 | 199 | 0 | 561 | 152 | 0 | 1 | 164.26 | 107.89
19:30 | 0 | 0 | 210 | 0 | 0 | 81 | 0 | 408 | 282 |  | 0 | 450 | 277 | 48 | 78 | 55 | 270 | 0 | 0 | 40 | 91 | 98 | 21 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 19 | 19 | 25 | 24 | 8 | 0 | 124 | 75 | 0 | 0 | 17 | 222 | 0 | 0 | 0 |  | 6 | 63 | 0 | 12 | 0 | 6 | 11 | 33 | 0 | 0 | 0 | 310 | 270 | 204 | 78 | 0 | 48 | 0 | 0 | 43 | 0 | 0 | 51 | 18 | 10 | 33 | 12 | 154 | 45 | 0 | 18 | 0 | 43 | 39 | 50 | 39 | 80 | 0 | 0 | 86 | 0 | 181 | 17 | 0 | 10 | 270 | 16 | 8 | 0 | 115 | 0 | 0 | 153 | 0 | 149 | 0 | 10 | 100 | 70 | 368 | 95 | 105 | 17 | 0 | 175 | 54 | 55 | 106 | 76 | 10 | 350 | 72 | 0 | 162 | 34 | 0 | 17 | 0 | 0 | 17 | 0 | 87 | 0 | 620 | 3 | 0 | 0 | 0 |  | 801 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 35 | 36 | 16 | 128 | 28 | 64 | 0 | 0 | 0 | 37 | 5 | 93 | 0 | 16 | 40 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 370 | 72 | 0 | 70 | 67 | 77 | 0 | 0 | 35 | 1160 | 0 | 0 | 135 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 1324 | 0 | 0 |  | 8389 | 5343 | 13732 | 3748 | 801 | 2177 | 0 | 2848 | 3284 | 199 | 0 | 518 | 154 | 0 | 3 | 160.44 | 0
20:00 | 0 | 0 | 210 | 0 | 0 | 82 | 0 | 408 | 331 |  | 0 | 450 | 304 | 47 | 78 | 55 | 300 | 0 | 0 | 40 | 91 | 64 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 19 | 19 | 25 | 24 | 8 | 0 | 124 | 75 | 0 | 0 | 17 | 221 | 0 | 0 | 0 |  | 6 | 63 | 0 | 12 | 0 | 6 | 11 | 33 | 0 | 0 | 0 | 310 | 270 | 206 | 78 | 0 | 48 | 0 | 0 | 43 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 146 | 52 | 0 | 18 | 0 | 43 | 39 | 50 | 39 | 80 | 0 | 0 | 86 | 0 | 181 | 17 | 0 | 10 | 265 | 16 | 5 | 0 | 122 | 0 | 0 | 153 | 0 | 149 | 0 | 10 | 104 | 10 | 367 | 94 | 105 | 17 | 0 | 175 | 54 | 55 | 106 | 76 | 10 | 375 | 72 | 0 | 162 | 34 | 0 | 20 | 0 | 0 | 17 | 0 | 35 | 0 | 612 | 0 | 0 | 0 | 0 |  | 801 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 34 | 36 | 16 | 130 | 29 | 64 | 0 | 0 | 0 | 37 | 0 | 93 | 0 | 8 | 40 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 370 | 72 | 0 | 70 | 67 | 84 | 0 | 0 | 35 | 1180 | 0 | 0 | 135 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 1360 | 0 | 0 |  | 8347 | 5393 | 13740 | 3804 | 801 | 2250 | 0 | 2782 | 3332 | 199 | 0 | 426 | 146 | 0 | 0 | 105.05 | 107.88
21:00 | 0 | 0 | 210 | 0 | 0 | 83 | 0 | 409 | 332 |  | 0 | 450 | 285 | 48 | 83 | 15 | 320 | 0 | 0 | 40 | 91 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 19 | 19 | 25 | 24 | 8 | 0 | 124 | 75 | 0 | 0 | 15 | 222 | 0 | 0 | 0 |  | 6 | 63 | 0 | 12 | 0 | 6 | 11 | 39 | 0 | 0 | 0 | 310 | 270 | 208 | 78 | 0 | 48 | 0 | 0 | 51 | 0 | 10 | 52 | 18 | 10 | 33 | 12 | 154 | 82 | 0 | 18 | 0 | 43 | 39 | 50 | 39 | 112 | 0 | 0 | 84 | 0 | 181 | 17 | 0 | 10 | 290 | 16 | 5 | 0 | 130 | 0 | 0 | 153 | 0 | 149 | 0 | 10 | 104 | 10 | 368 | 94 | 105 | 17 | 0 | 175 | 54 | 55 | 98 | 76 | 10 | 390 | 72 | 0 | 162 | 34 | 0 | 21 | 0 | 0 | 17 | 0 | 35 | 0 | 620 | 0 | 0 | 0 | 0 |  | 800 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 40 | 37 | 16 | 130 | 29 | 64 | 0 | 0 | 0 | 37 | 0 | 93 | 0 | 8 | 40 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 414 | 72 | 0 | 35 | 67 | 86 | 0 | 0 | 35 | 1244 | 10 | 0 | 135 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 1362 | 0 | 0 |  | 8428 | 5498 | 13926 | 3884 | 800 | 2356 | 0 | 2716 | 3406 | 199 | 0 | 411 | 154 | 0 | 0 | 118 | 107.89
22:00 | 0 | 0 | 210 | 0 | 0 | 83 | 0 | 409 | 332 |  | 0 | 450 | 301 | 48 | 85 | 15 | 322 | 0 | 0 | 40 | 91 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 19 | 19 | 25 | 24 | 8 | 0 | 125 | 75 | 0 | 0 | 17 | 222 | 0 | 0 | 0 |  | 6 | 56 | 0 | 12 | 0 | 8 | 11 | 39 | 0 | 0 | 0 | 310 | 265 | 208 | 78 | 0 | 48 | 0 | 0 | 43 | 0 | 23 | 43 | 18 | 10 | 33 | 12 | 150 | 82 | 0 | 16 | 0 | 43 | 40 | 50 | 39 | 112 | 0 | 0 | 84 | 0 | 181 | 17 | 0 | 10 | 295 | 0 | 5 | 0 | 130 | 0 | 0 | 153 | 0 | 149 | 0 | 10 | 104 | 10 | 368 | 94 | 105 | 17 | 0 | 225 | 17 | 55 | 105 | 78 | 10 | 390 | 72 | 0 | 162 | 34 | 0 | 17 | 0 | 0 | 17 | 0 | 35 | 0 | 612 | 1 | 0 | 0 | 0 |  | 800 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 37 | 37 | 16 | 130 | 32 | 64 | 0 | 0 | 0 | 37 | 0 | 93 | 0 | 8 | 40 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 414 | 72 | 0 | 35 | 67 | 86 | 0 | 0 | 35 | 1244 | 10 | 0 | 135 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 1350 | 0 | 0 |  | 8432 | 5542 | 13974 | 3881 | 800 | 2372 | 0 | 2770 | 3386 | 200 | 0 | 414 | 150 | 0 | 1 | 168.08 | 107.89
23:00 | 0 | 0 | 210 | 0 | 0 | 83 | 0 | 409 | 332 |  | 0 | 450 | 313 | 48 | 85 | 15 | 322 | 0 | 0 | 40 | 91 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 19 | 19 | 25 | 31 | 8 | 0 | 126 | 75 | 0 | 0 | 8 | 222 | 0 | 0 | 0 |  | 6 | 56 | 0 | 12 | 0 | 6 | 11 | 39 | 0 | 0 | 0 | 330 | 325 | 206 | 90 | 0 | 48 | 0 | 0 | 43 | 0 | 23 | 43 | 18 | 10 | 33 | 12 | 164 | 81 | 0 | 16 | 0 | 43 | 41 | 50 | 39 | 112 | 0 | 0 | 84 | 0 | 182 | 17 | 0 | 10 | 295 | 16 | 5 | 0 | 130 | 0 | 0 | 68 | 0 | 86 | 0 | 10 | 104 | 11 | 388 | 28 | 105 | 17 | 0 | 230 | 17 | 55 | 105 | 77 | 10 | 390 | 72 | 0 | 108 | 34 | 0 | 17 | 0 | 0 | 17 | 0 | 35 | 0 | 620 | 0 | 0 | 0 | 0 |  | 820 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 37 | 37 | 16 | 130 | 32 | 64 | 0 | 0 | 0 | 37 | 0 | 57 | 0 | 8 | 40 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 209 | 0 | 414 | 72 | 0 | 37 | 67 | 56 | 0 | 0 | 60 | 1244 | 50 | 0 | 135 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 1372 | 0 | 0 |  | 8326 | 5583 | 13909 | 4000 | 820 | 2436 | 0 | 2494 | 3416 | 201 | 0 | 378 | 164 | 0 | 0 | 325.655 | 107.89
24:00 | 0 | 0 | 210 | 0 | 0 | 83 | 0 | 409 | 332 |  | 0 | 450 | 283 | 51 | 85 | 15 | 325 | 0 | 0 | 75 | 74 | 48 | 8 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 19 | 19 | 25 | 30 | 8 | 0 | 126 | 75 | 0 | 0 | 8 | 223 | 0 | 0 | 0 |  | 6 | 30 | 0 | 12 | 0 | 6 | 11 | 42 | 0 | 0 | 0 | 310 | 305 | 210 | 123 | 0 | 49 | 0 | 0 | 51 | 0 | 23 | 43 | 18 | 10 | 33 | 12 | 168 | 80 | 0 | 16 | 0 | 43 | 40 | 50 | 39 | 112 | 0 | 0 | 84 | 0 | 182 | 17 | 0 | 10 | 290 | 16 | 5 | 0 | 70 | 0 | 0 | 67 | 0 | 17 | 0 | 10 | 46 | 35 | 368 | 18 | 35 | 17 | 0 | 230 | 17 | 55 | 105 | 35 | 10 | 397 | 72 | 0 | 17 | 34 | 0 | 17 | 0 | 0 | 17 | 0 | 53 | 0 | 622 | 0 | 0 | 0 | 0 |  | 820 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 22 | 37 | 16 | 130 | 32 | 110 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 34 | 22 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 414 | 72 | 0 | 50 | 85 | 34 | 0 | 0 | 113 | 1244 | 50 | 0 | 135 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 1411 | 0 | 0 |  | 7915 | 5660 | 13575 | 3950 | 820 | 2445 | 0 | 2242 | 3457 | 201 | 0 | 292 | 168 | 0 | 0 | 549.125 | 107.89
KWH | 0 | 0 | 4638313 | 0 | 0 | 1872409 | 0 | 9572360 | 7510000 |  | 0 | 9733500 | 6860858 | 499200 | 858129 | 510705 | 7310867 | 0 | 0 | 657600 | 1224288 | 1106400 | 22498 | 0 | 0 | 0 | 388800 | 440555 | 442944 | 444420 | 456000 | 347760 | 593800 | 699700 | 209760 | 38196 | 2772698 | 1552000 | 0 | 0 | 151745 | 5329680 | 0 | 0 | 0 |  | 148800 | 372912 | 0 | 265080 | 0 | 153120 | 266496 | 669600 | 0 | 0 | 0 | 7499100 | 7083000 | 4923000 | 2877091 | 0 | 1117368 | 0 | 0 | 1078580 | 0 | 67568 | 1012512 | 429336 | 250200 | 756200 | 280100 | 3477120 | 969600 | 0 | 394776 | 10400 | 1002000 | 913200 | 1122600 | 911736 | 2474590 | 0 | 0 | 1820160 | 0 | 4736670 | 395000 | 0 | 251460 | 6891000 | 354072 | 172080 | 0 | 963491 | 0 | 0 | 2200800 | 0 | 1123488 | 131085 | 253440 | 1470720 | 557018 | 9123000 | 837600 | 856320 | 431563 | 30359 | 2338473 | 450398 | 1338180 | 1144560 | 676200 | 251520 | 9106000 | 809280 | 301440 | 1166400 | 612218 | 0 | 473760 | 186433 | 0 | 433080 | 0 | 404800 | 0 | 14939998 | 107040 | 0 | 0 | 0 |  | 21588363 | 0 | 0 | 0 | 805440 | 0 | 0 | 0 | 229440 | 254848 | 108750 | 2883000 | 579184 | 588768 | 0 | 0 | 0 | 200786 | 7318 | 481936 | 0 | 105017 | 205284 | 76267 | 106607 | 0 | 0 | 193806 | 0 | 0 | 4381700 | 0 | 0 | 4709345 | 0 | 0 | 0 | 0 | 0 | 4455664 | 0 | 8382872 | 1106880 | 0 | 370560 | 629424 | 948326 | 0 | 43476 | 383808 | 29693100 | 3337718 | 0 | 992400 | 16860 | 277920 | 494016 | 1099567 | 0 | 0 | 234668 | 0 | 31478182 | 131855 | 0 |  | 174110376 | 121583155 | 295693531 | 91444109 | 21588363 | 56373358 | 0 | 31983901 | 80492980 | 4324698 | 1099567 | 3437899 | 3477120 | 1364496 | 107040 | 0
Fuel Cost | 0 | 0 | 6771936.98 | 0 | 0 | 2490303.97 | 0 | 10050978 | 8110800 |  | 0 | 10609515 | 7615552.38 | 5581056 | 11370209.25 | 6766841.25 | 8188171.04 | 0 | 0 | 9614112 | 17225732.16 | 17934744 | 207431.56 | 0 | 0 | 0 | 4945536 | 5947492.5 | 5939879.04 | 333315 | 342000 | 0 | 0 | 0 | 3568017.6 | 93198.24 | 748628.46 | 419040 | 0 | 0 | 2481030.75 | 5542867.2 | 0 | 0 | 0 |  | 1941840 | 6220172.16 | 0 | 3581230.8 | 0 | 1771598.4 | 338449.92 | 2229768 | 0 | 0 | 0 | 8324001 | 7720470 | 5710680 | 3711447.39 | 0 | 1262625.84 | 0 | 0 | 1801228.6 | 0 | 1166899.36 | 13618286.4 | 588190.32 | 187650 | 1323350 | 210075 | 24965721.6 | 1056864 | 0 | 536895.36 | 165776 | 1372740 | 1205424 | 1953324 | 1577303.28 | 2845778.5 | 0 | 0 | 4149964.8 | 0 | 4784036.7 | 849250 | 0 | 497890.8 | 6891000 | 265554 | 130780.8 | 0 | 13151652.15 | 0 | 0 | 29666784 | 0 | 15560308.8 | 1532383.65 | 2615500.8 | 20090035.2 | 7391628.86 | 8393160 | 10185216 | 12382387.2 | 5459271.95 | 472386.04 | 27453673.02 | 4904834.22 | 14224853.4 | 15531679.2 | 8716218 | 2962905.6 | 8377520 | 10480176 | 4355808 | 14801616 | 6967040.84 | 0 | 6187305.6 | 2227874.35 | 0 | 5703663.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 64765089 | 0 | 0 | 0 | 8384630.4 | 0 | 0 | 0 | 4132214.4 | 4587264 | 1562737.5 | 3228960 | 1123616.96 | 6417571.2 | 0 | 0 | 0 | 3367181.22 | 127991.82 | 7537479.04 | 0 | 1739081.52 | 3471352.44 | 1039519.21 | 1798460.09 | 0 | 0 | 146711.142 | 0 | 0 | 37156816 | 0 | 0 | 5462840.2 | 0 | 0 | 0 | 0 | 0 | 5168570.24 | 0 | 8299043.28 | 14876467.2 | 0 | 4383724.8 | 9095176.8 | 12043740.2 | 0 | 480409.8 | 4659429.12 | 246452730 | 3404472.36 | 0 | 7343760 | 190686.6 | 3260001.6 | 7573265.28 | 0 | 0 | 0 | 0 | 0 | 269138456.1 | 0 | 0 |  | 527650537.89 | 752419449.522 | 1280069987.412 | 97967264.982 | 64765089 | 67311009.32 | 0 | 408116147.38 | 552748002.1 | 1167668.46 | 0 | 50343758.53 | 24965721.6 | 12685326.04 | 0 | 0
Yesterday Day Peak | 0 | 0 | 170 | 0 | 0 | 76 | 0 | 353 | 272 |  | 0 | 450 | 286 | 0 | 0 | 15 | 280 | 0 | 0 | 0 | 25 | 82 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 19 | 0 | 25 | 30 | 8 | 20 | 124 | 75 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 6 | 12 | 2 | 0 | 0 | 0 | 280 | 270 | 206 | 145 | 0 | 46 | 0 | 0 | 51 | 0 | 0 | 52 | 17 | 10 | 33 | 12 | 116 | 25 | 0 | 18 | 2 | 40 | 39 | 47 | 38 | 112 | 0 | 0 | 78 | 0 | 187 | 16 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 115 | 0 | 17 | 20 | 10 | 66 | 0 | 405 | 37 | 17 | 17 | 5 | 66 | 0 | 41 | 52 | 9 | 10 | 380 | 0 | 33 | 4 | 7 | 0 | 17 | 14 | 0 | 17 | 0 | 0 | 0 | 612 | 3 | 0 | 0 | 0 |  | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 240 | 0 | 0 | 0 | 0 | 10 | 0 | 6 | 0 | 1120 | 222 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 31 | 0 | 1254 | 132 | 0 |  | 11455 | DayPeak
Yesterday Evening Peak | 0 | 0 | 210 | 0 | 0 | 83 | 0 | 409 | 332 |  | 0 | 450 | 285 | 48 | 83 | 15 | 320 | 0 | 0 | 40 | 91 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 19 | 19 | 25 | 24 | 8 | 0 | 124 | 75 | 0 | 0 | 15 | 222 | 0 | 0 | 0 | 0 | 6 | 63 | 0 | 12 | 0 | 6 | 11 | 39 | 0 | 0 | 0 | 310 | 270 | 208 | 78 | 0 | 48 | 0 | 0 | 51 | 0 | 10 | 52 | 18 | 10 | 33 | 12 | 154 | 82 | 0 | 18 | 0 | 43 | 39 | 50 | 39 | 112 | 0 | 0 | 84 | 0 | 181 | 17 | 0 | 10 | 290 | 16 | 5 | 0 | 130 | 0 | 0 | 153 | 0 | 149 | 0 | 10 | 104 | 10 | 368 | 94 | 105 | 17 | 0 | 175 | 54 | 55 | 98 | 76 | 10 | 390 | 72 | 0 | 162 | 34 | 0 | 21 | 0 | 0 | 17 | 0 | 35 | 0 | 620 | 0 | 0 | 0 | 0 |  | 800 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 40 | 37 | 16 | 130 | 29 | 64 | 0 | 0 | 0 | 37 | 0 | 93 | 0 | 8 | 40 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 414 | 72 | 0 | 35 | 67 | 86 | 0 | 0 | 35 | 1244 | 10 | 0 | 135 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 1362 | 0 | 0 |  | 13926 | EvPeak
Forecast for Evening | 0 | 0 | 200 | 0 | 0 | 85 | 0 | 400 | 330 | 0 | 0 | 450 | 300 | 72 | 85 | 55 | 330 | 0 | 74 | 92 | 92 | 149 | 55 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 19 | 25 | 33 | 25 | 0 | 128 | 75 | 0 | 0 | 17 | 225 |  | 0 | 0 | 0 | 6 | 52 | 0 | 12 | 12 | 50 | 12 | 25 | 0 | 0 | 0 | 310 | 305 | 200 | 108 | 0 | 48 | 0 | 0 | 51 | 0 | 0 | 52 | 17 | 10 | 33 | 12 | 165 | 50 | 0 | 18 | 0 | 43 | 40 | 50 | 42 | 112 | 0 | 0 | 86 | 0 | 185 | 17 | 0 | 10 | 280 | 16 | 11 | 0 | 130 | 0 | 0 | 160 | 0 | 149 | 0 | 10 | 100 | 145 | 400 | 85 | 105 | 17 | 0 | 280 | 54 | 55 | 105 | 75 | 10 | 400 | 72 | 0 | 108 | 51 | 0 | 17 |  | 0 | 17 | 0 | 160 |  | 612 | 25 | 0 | 0 |  |  | 938 | 0 | 0 |  | 49 | 0 | 0 | 0 | 40 | 40 | 0 | 130 | 31 | 64 | 0 | 0 | 0 | 35 | 21 | 91 | 28 | 42 | 40 | 8 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 185 |  | 0 | 0 | 0 | 0 | 190 | 0 | 414 | 70 | 0 | 75 | 100 | 64 | 0 | 0 | 113 | 1244 | 220 |  | 150 |  |  | 72 | 0 |  | 0 |  | 0 | 1400 |  | 0
Forecast for Day | 0 | 0 | 200 | 0 | 0 | 82 | 0 | 0 | 330 | 0 | 0 | 450 | 300 | 72 | 85 | 15 | 330 | 0 | 185 | 92 | 50 | 48 | 55 | 0 | 0 | 0 | 17 | 35 | 55 | 19 | 19 | 19 | 25 | 33 | 8 | 0 | 127 | 75 | 0 | 0 | 8 | 225 |  | 0 | 0 | 0 | 6 | 32 | 0 | 12 | 0 | 6 | 12 | 10 | 0 | 0 | 0 | 310 | 305 | 200 | 108 | 0 | 43 | 0 | 0 | 51 | 0 | 0 | 25 | 16 | 10 | 33 | 12 | 149 | 32 | 0 | 18 | 1.6 | 42 | 40 | 50 | 40 | 112 | 0 | 0 | 86 | 0 | 185 | 17 | 0 | 10 | 280 | 16 | 11 | 0 | 80 | 0 | 0 | 115 | 0 | 17 | 20 | 10 | 68 | 20 | 400 | 47 | 35 | 17 | 5 | 70 | 17 | 55 | 105 | 28 | 10 | 400 | 53 | 50 | 54 | 34 | 0 | 17 | 35 | 0 | 17 | 0 | 54 |  | 612 | 10 | 0 | 0 |  |  | 938 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 25 | 0 | 0 | 130 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 28 | 34 | 30 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 380 | 54 | 0 | 35 | 100 | 34 | 0 | 8 | 113 | 1244 | 220 |  | 35 | 6 | 100 | 35 | 0 |  | 0 | 30 | 0 | 1300 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 170 | 0 | 0 | 74 | 0 | 0 | 337 | 0 | 0 | 400 | 285 | 0 | 22 | 15 | 240 | 0 | 74 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 25 | 31 | 8 | 0 | 126 | 75 | 0 | 0 | 8 | 223 | 0 | 0 | 0 | 0 | 6 | 24 | 0 | 12 | 0 | 6 | 11 | 10 | 0 | 0 | 0 | 305 | 305 | 209 | 127 | 0 | 43 | 0 | 0 | 51 | 0 | 0 | 25 | 18 | 10 | 26 | 12 | 150 | 32 | 0 | 16 | 1 | 43 | 40 | 50 | 40 | 112 | 0 | 0 | 75 | 0 | 183 | 17 | 0 | 10 | 285 | 16 | 11 | 0 | 25 | 0 | 0 | 68 | 0 | 17 | 5 | 10 | 34 | 20 | 368 | 18 | 17 | 17 | 2 | 70 | 17 | 55 | 17 | 9 | 10 | 400 | 44 | 27 | 17 | 17 | 0 | 17 | 16 | 0 | 17 | 0 | 17 | 0 | 622 | 0 | 0 | 0 | 0 | 0 | 926 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 380 | 54 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 1200 | 221 | 0 | 17 | 1 | 45 | 0 | 0 | 0 | 0 | 16 | 0 | 1317 | 92 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
292.3904
| Minimum Generation |  | 10711 | 9:00 | [202 empty] | 147817467
| Highest Generation |  | 13974 | 22:00 | [202 empty] | 147.8175 |  |  |  |  | 1.3645
| Day Peak Generation |  | 11455 | 12:00 | [202 empty] | 36521367
| Evening Peak Generation |  | 13926 | 21:00 | [202 empty] | 36.5214 |  |  | 56373358 |  | 4.3247
| HVDC Max Flow |  | 925 | 6:00 | [202 empty] | 21.5884 |  |  |  |  | 0.10704
| HVDC EvPeak Flow |  | 800 | 21:00 | [200 empty] | 295693531 |  | 3.4771 |  | 80.493
| Load factor L.F |  | 88.17% | [166 empty] | 1275.5 | [36 empty] | 295.6935

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-09-16
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-09-15 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 11455 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 11548
Evening Peak Generation : |  |  | 13926 | MW Hour : | 21:00 | Available Max Generation : |  | 15335
E.P. Demand (at gen end) : |  |  | 14050 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14500
Maximum Generation : |  |  | 13974 | MW Hour : | 22:00 | Reserve(Generation end) |  | 835
Total Gen. (MKWH) : |  |  | 295.6935 | System Load Factor : | 88.17% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 760 | MW at | 19:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-09-16
Actual : |  | 107.89 | Ft.(MSL) , | Rule curve : | 102.45 | Ft.( MSL )
Gas Consumed : |  | Total = | 1094.66 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 165278274.302
: |  |  | Coal : | 552748002.1 | Oil : | 458459905.91 | Total : | 1176486182.312
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4857.5703 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1336.484 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1872.677 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1628.1782 |  |  | 0 | 0%
Cumilla Area |  | 30 | 720:00 | 1339.4547 |  |  | 0 | 0%
Mymensingh Area |  | 48 | 1152:00 | 996.477 |  |  | 0 | 0%
Sylhet Area |  | 40 | 960:00 | 558.2777 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 465.5121 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 910.4541 |  |  | 0 | 0%
Total |  | 118 |  | 13965.0851 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
8:40 | 15:29 | Shahjibazar 132/33kV S/S BPDB 60 MW Scheduled S/D Due to 952 Brekar Bus D/S connecting Rod Change.
8:40 | 15:29 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Scheduled S/D from Shahjibazar 132/33kV end Due to 952 Brekar Bus D/S connecting
Rod Change and from Brahmanbaria 132/33kV end Due to S/D taken by NLDC.
8:43 | 11:20 | Goalpara 132/33kV S/S Goalpara-NWPGCL Forced S/D Due to Redhot Remove.
- | 8:46 | Aminbazar 400/230/132kV S/S 132 kv Bus 01 is restored.
- | 8:55 | Thakurgaon 132/33kV S/S T-2(412T) LT is restored.
330MW generation interrup.
- | 8:55 | Thakurgaon 132/33kV S/S T-2(412T) HT is restored.
8.0MW load interrup.
- | 9:29 | Shahjadpur-Sirajganj 132kV Ckt-1 is restored.
- | 9:29 | Sirajganj 132/33kV S/S Main Bus is restored.
- | 9:34 | Sirajganj 132/33kV S/S T2-(425) HT is restored.
- | 9:35 | Sirajganj 132/33kV S/S T2-(425) LT is restored.
9:47 | - | Khulna 330 MW PP was shutdown due to fuel shortage.
- | 9:48 | Baghabari-Sirajganj 132 kV Ckt-1 is restored.
10:04 | 14:38 | GPH 230/33kV S/S Transformer -2 (D07) HT Scheduled S/D Due to winding.
- | 10:12 | Tongi 80 MW PP was sync. |  |  |  |  | 80MW generation interrup.
- | 10:18 | Aminbazar-Kallyanpur 132kV Ckt-2 is restored.
10:21 | 17:35 | Aminbazar-Kallyanpur 132kV Ckt-1 Scheduled S/D from Kallyanpur 132/33kV end Due to For loop changing work.
10:31 | - | Rampal 400/230kV S/S Generator Transformer-1 (GT-1) HT Project Work S/D Due to For maintenance.
10:31 | - | Rampal 400/230kV S/S Generator Transformer-1 (GT-1) LT Project Work S/D Due to For maintenance.
- | 10:58 | Siddhirganj 132/33kV S/S T-1 HT is restored.
- | 10:59 | Siddhirganj 132/33kV S/S T-1 LT is restored.
35.0MW load interrup.
- | 11:02 | Sirajganj 132/33kV S/S T4-(445) HT is restored.
35.0MW load interrup.
- | 11:02 | Sirajganj 132/33kV S/S T4-(445) LT is restored.
35.0MW load interrup.
- | 11:12 | Sirajganj 132/33kV S/S T1-(415) LT is restored.
- | 11:12 | Sirajganj 132/33kV S/S T1-(415) HT is restored.
11:31 | - | Bheramara(GK) 132/33kV S/S TR-4 LT Scheduled S/D Due to Oil centrifuge.
11:32 | - | Bheramara(GK) 132/33kV S/S TR-4 HT Scheduled S/D Due to Oil Centrifuge.
12:00 | - | Day Peak Gen. 11455 MW
12:15 | - | Tongi 80 MW PP was shutdown due to gas shortage.
15:43 | - | Bhola Nutan Bidyut CCPP ST tripped.
15:56 | - | Bhola Nutan Bidyut CCPP GT12 tripped.
16:18 | - | Bhola Nutan Bidyut CCPP GT11 tripped.
- | 20:49 | Bhola Nutan Bidyut CCPP GT11 was sync.
21:00 | - | Evening Peak Generation : 13926 MW
21:51 | 0:45 | Sylhet 132/33kV S/S T4 LT Tripped showing (50/51) O/C. relays.
- | 1:24 | Bhola Nutan Bidyut CCPP ST was sync.
- | 1:24 | Bhola Nutan Bidyut CCPP ST was sync.
5:37 | - | Haripur 412 MW CCPP was shutdown due to control oil supply filter maintenance.
5:37 | - | Haripur 412 MW CCPP S/D due to fuel control system problem.
6:00 | - | minimum generation 11548 MW
- | 6:21 | Madanganj 132/33kV S/S Madanganj-Fatullah 132KV Ckt is restored.
6:53 | - | Srinagar 132/33kV S/S Tr-01 HT Scheduled S/D Due to ৩১ কেভি বাস কাপলার আইসোলেটর রেডহট এর সংরক্ষণ কাজ মুন্সিগঞ্জ
পল্লিবিদ্যুৎ কর্তৃক বাস্তবায়ন।
6:53 | - | Srinagar 132/33kV S/S Tr-01 LT Scheduled S/D Due to ৩৩ কেভি বাস কাপলার আইসোলেটর রেডহট এর সংরক্ষণ কাজ মুন্সিগঞ্জ
পল্লিবিদ্যুৎ কর্তৃক বাস্তবায়ন।
6:53 | - | Srinagar 132/33kV S/S 33 kV bus Scheduled S/D Due to ৩১ কেভি বাস কাপলার আইসোলেটর রেডহট এর সংরক্ষণ কাজ মুন্সিগঞ্জ
পল্লিবিদ্যুৎ কর্তৃক বাস্তবায়ন।
6:54 | - | Srinagar 132/33kV S/S Tr-02 HT Scheduled S/D Due to ৩৩ কেভি বাস কাপলার আইসোলেটর রেডহট এর সংরক্ষণ কাজ মুন্সিগঞ্জ
পল্লিবিদ্যুৎ কর্তৃক বাস্তবায়ন।
6:54 | - | Srinagar 132/33kV S/S Tr-02 LT Scheduled S/D Due to ৩৩ কেভি বাস কাপলার আইসোলেটর রেডহট এর সংরক্ষণ কাজ মুন্সিগঞ্জ
পল্লিবিদ্যুৎ কর্তৃক বাস্তবায়ন।
6:58 | - | Haripur-Meghnaghat 230kV Ckt-2 Scheduled S/D from Haripur 230/132kV end Due to two conductor change of tension tower to
gentry at Meghnaghat sub-station.
7:25 | - | Faridpur 132/33kV S/S Transformer-2 HT Scheduled S/D Due to 33 kv Bus Redhot Problem. |  |  |  |  | 50.0MW load interrup.
7:25 | - | Faridpur 132/33kV S/S Transformer-2 LT Scheduled S/D Due to 33 kv Bus Redhot Problem. |  |  |  |  | 50.0MW load interrup.
7:35 | - | Full power interruption (60 MW) occurring under Beanibazar 132/33 kV S/S due to the scheduled shutdown of Fenchuganj-Sylhet |  |  |  |  | 60MW load interrup.
132 kV ckt-2.
7:35 | - | Fenchuganj -Sylhet 132kV Ckt-1 Project Work S/D from Sylhet 132/33kV end Due to Due to South Surma Line Connection.
7:36 | - | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Project Work S/D from Fenchuganj 230/132/33kV end Due to Project work.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-09-15 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 210 | 4638313
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 83 | 1872409 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 409 | 9572360
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 332 | 7510000 | Frequency Control
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9733500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 48 | 499200 | Low Demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 285 | 6860858 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 83 | 858129 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 510705 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 22498 | Reserved
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 444420 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 40 | 657600 | High voltage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 320 | 7310867 | Frequency Control
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 91 | 1224288 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 388800
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 1106400 | Low Demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 440555 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 442944
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 38 | 803760 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 593800 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 24 | 699700 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 209760 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 38196 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 130 | 963491 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Contract Expired
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1123488
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 856320
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 72 | 809280 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1166400
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 186433
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 433080 | Fuel shortage
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0
| Dhaka area Total |  |  |  | 5722 | 3291 | 61977554
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 15 | 151745 | High voltage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 131085
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 6 | 153120 | Low Demand
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 199 | 4324698
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 222 | 5329680
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 431563 | Low Demand
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 63 | 372912 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 12 | 265080 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 10 | 253440 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 11 | 266496 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 39 | 669600
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30359
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 175 | 2338473 | Low Demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 450398
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 55 | 1338180 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 10 | 251520 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 34 | 612218 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 35 | 404800 | Low Demand
| SS Power I |  | SS Power | 0 | 0 | 620 | 14939998 | On test.
| Cox's Bazar Wind |  | IPP | 66 | 0 | 0 | 107040 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2545 | 1577 | 32822405
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 208 | 4923000 | 0
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7499100
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 7083000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 48 | 1117368
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 78 | 2877091 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1078580
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 10 | 557018 | Low Demand
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 10 | 67568 | Machine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 104 | 1470720 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 429336 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 250200
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 154 | 3477120
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 756200
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 1012512
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 12 | 280100 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 98 | 1144560 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 76 | 676200 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 21 | 473760 | Fuel shortage
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | Machine problem
| Cumilla Area Total |  |  |  | 2896 | 1563 | 35173433
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 82 | 969600 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 394776 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10400
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 153 | 2200800 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 94 | 837600 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 301440
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 148800 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 353 | 4863416
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1002000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 39 | 913200 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2474590 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1122600
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 39 | 911736 | Engine problem
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 172080 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under maint.
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1820160
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 181 | 4736670 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 395000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 354072 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 6891000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 368 | 9123000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 251460
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 390 | 9106000
| Sylhet Area Total |  |  |  | 2427 | 1644 | 39273568
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 800 | 21588363
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 49 | 805440 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 40 | 229440 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserved
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 37 | 254848 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 16 | 108750 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 72 | 1106880 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 67 | 629424 | Low Demand
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 277920
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 220 | 0 | 1099567 | Fuel shortage
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | Machine problem
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3121 | 1081 | 26100632
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 64 | 588768 | Low Demand
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 29 | 579184 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 130 | 2883000 | ST Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 29693100
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 10 | 3337718 | Engine problem
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 135 | 992400 | Machine problem
| Barisal 307 MW |  | IPP | 307*1 | 307 | 0 | 0 | Coal shortage.
| Barisal Area Total |  |  |  | 2265 | 1612 | 38074170
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 37 | 200786 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 7318 | Reserved
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserved
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 105017 | Low Demand
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 205284 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 189 | 4709345 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 211 | 4455664
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 8382872
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 106607 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 193806 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 76267 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 93 | 481936 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 370560 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 383808 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 16860
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1362 | 31478182
| Rajshahi Area Total |  |  |  | 3631 | 2464 | 51174312
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 180 | 4381700 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 86 | 948326 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 43476
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 75 | 494016 | Fuel shortage
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 234668
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 131855
| Rangpur Area Total |  |  |  | 950 | 341 | 6234041
| Total |  |  |  | 24171 | 13926 | 295693531
| Eastern Grid Total |  |  |  | 14204 | 8428 | 174110376
| Western Grid Total |  |  |  | 9967 | 5498 | 121583155
| National Grid Total |  |  |  | 24171 | 13926 | 295693531
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-09-15
| (a) ENTIRE EASTERN GRID : |  | 8828.56 | MW | (b) ENTIRE WESTERN GRID : |  | 4516.6 | MW
| i) Dhaka area |  | 4425.56 | MW | i) Khulna area |  | 1656 | MW
| ii) Chittagong area |  | 1287 | MW | ii) Rajshahi area |  | 1465.6 | MW
| iii) Comilla area |  | 1350 | MW | iii) Barisal area |  | 440 | MW
| iv) Mymensingh area |  | 1186 | MW | iv) Rangpur area |  | 955 | MW
| v) Sylhet area |  | 580 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 13345.16 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 39 | 02:00 | Kamrangirchar | 57 | 00:00 | Natore | 148 | 19:00 | Sholosohor | 32 | 19:00
2 | AKSML | 105 | 03:00 | Chowmuhani | 230 | 21:00 | Kaptai | N/A | N/A | Nawabganj | 47.4 | 22:00 | Shyampur | 132 | 00:00
3 | Aftabnagar | 50 | 19:00 | Chuadanga | 112 | 19:00 | Kazla | 96 | 00:00 | Netrakona | 146 | 20:00 | Siddhirganj | 102 | 23:00
4 | Agargaon | 96 | 18:30 | Coxsbazar | 125 | 19:30 | Keranigonj | 72 | 00:00 | New | 62 | 00:00 | Sirajganj | 118 | 19:00
5 | Agrabad | 54 | 18:30 | Cumilla(N) | 173 | 22:00 | Khagrachori | 26 | 18:30 | Niamatpur | 84 | 00:00 | Sonargaon | 85 | 00:00
6 | Amnura | 55 | 23:00 | Cumilla(S) | 164 | 04:00 | Khulna | 85 | 19:30 | Noapara | 41 | 00:00 | Sreemongol | 69 | 18:30
7 | Ashuganj | 79 | 19:00 | Daudkandi | 138 | 00:00 | Khulshi | 160 | 23:00 | PHP | 7 | 17:00 | Sreepur | 70 | 01:00
8 | BIPTC | N/A | N/A | Dhaka | 14 | 18:00 | Kishoreganj | 148 | 03:00 | Pabna | 117 | 19:30 | Srinagar | 46.3 | 22:00
9 | BSRM | 186 | 21:00 | Dhamrai | 122 | 00:00 | Kodda | 231 | 12:00 | Palashbari | 136 | 20:00 | Sunamganj | 58 | 21:00
10 | Bagerhat | 86 | 19:00 | Dhanmondi | 124 | 18:30 | Kulaura | 50 | 18:30 | Panchagarh | 64 | 19:00 | Sylhet | 156 | 21:00
11 | Bakulia | 87 | 20:00 | Dohazari | 100 | 22:00 | Kurigram | 71 | 19:00 | Patuakhali | 107 | 22:00 | TK | 30.5 | 21:00
12 | Banani | 50 | 18:30 | Faridpur | 155 | 21:00 | Kushtia | 144 | 19:00 | Payra | 24 | 22:00 | Tangail | 233 | 21:00
13 | Bangabhaban | 4 | 00:00 | Fatullah | 59 | 01:00 | Lalbag | 73 | 00:00 | Postogola | 55 | 00:00 | Thakurgaon | 102 | 19:00
14 | Barapukuria | 70 | 08:00 | Fenchuganj | 47 | 18:30 | Lalmonirhat | 57 | 19:00 | Purbachal | 21 | 13:00 | Tongi | 102 | 00:00
15 | Barguna | 20 | 00:00 | Feni | 117 | 22:00 | Madanganj | 26 | 00:00 | Purbasadipur | 128 | 23:00 | Ullon | 42 | 22:00
16 | Barishal | 94 | 00:00 | GPH | 10 | 18:30 | Madaripur | 105 | 22:00 | Rahim | 34 | 01:00 | Uttara | 66 | 18:30
17 | Barishal-230 | 98 | 23:00 | Ghorashal | 72 | 00:00 | Madartek | 87.25 | 23:00 | Rajbari | 72 | 19:00 | UttaraNew | 64 | 23:00
18 | Baroaulia | 70 | 00:00 | Goalpara | 36 | 13:00 | Madunaghat | 51 | 19:00 | Rajendrapur | 90 | 19:00 | Zigatola | 62 | 18:30
19 | Baroirhat | 57 | 18:30 | Gollamari | 50 | 00:00 | Magura | 66 | 19:00 | Rajshahi | 154 | 00:00
20 | Bashundhara | 142 | 18:30 | Gopalganj | 103 | 21:00 | Mahasthangarh | 80 | 23:00 | Rajshahi-230 | 36 | 00:00
21 | BashundharaCement | 0 | 00:00 | Gulshan | 50 | 12:00 | Manikganj | 112 | 19:00 | Ramganj | 114 | 21:00
22 | Beanibazar | 80 | 22:00 | Halishahar | 65 | 12:00 | Maniknagar | 74 | 13:00 | Rampur | 29 | 00:00
23 | Benapole | 58 | 19:00 | HaripurSBU | 143 | 00:00 | Matarbari | 46 | 21:00 | Rangamati | 20 | 18:30
24 | Bhaluka | 116 | 18:30 | Hasnabad | 84 | 22:00 | Matuail | 59 | 00:00 | Rangpur | 145 | 18:30
25 | Bhandaria | 50 | 00:00 | Hathazari | 76 | 19:00 | Millgate | 80 | 00:00 | Ruppur | 5.8 | 11:00
26 | Bhangura | 36 | 20:00 | Ishurdi | 72 | 19:00 | Mirpur | 133 | 12:00 | SSM | 0 | 00:00
27 | Bheramara(GK) | 63 | 00:00 | Jaldhaka | 85 | 19:00 | Mirsorai | 4 | 18:30 | Saidpur | 106 | 00:00
28 | Bhulta | 238 | 04:00 | Jamalpur | 174 | 20:00 | Mithapukur | 48 | 19:00 | Satkhira | 119 | 19:00
29 | Bog-Sherpur | 74 | 04:00 | Jashore | 122 | 19:00 | Modern | 0 | 00:00 | Satmasjid | 99 | 18:30
30 | Bogura | 175 | 22:00 | Jhenaidah | 127 | 19:00 | Mogbazar | 107.9 | 18:30 | Savar | 170 | 12:00
31 | Borhanuddin | 63 | 22:00 | Joydebpur | 150 | 01:00 | Mongla | 18 | 00:00 | Shahjadpur | 102 | 19:30
32 | Brahmanbaria | 172 | 19:30 | Joypurhat | 62 | 20:00 | Motijheel | 32 | 00:00 | Shahjibazar | 107 | 16:00
33 | Cantonment | 133 | 13:00 | Juldah | 22 | 00:00 | Munshiganj | 106 | 00:00 | Shahmirpur | 41 | 23:00
34 | Chandpur | 74 | 21:00 | KSRM | 22 | 19:00 | Mymensingh | 234 | 22:00 | Shariatpur | 82 | 22:00
35 | Chandraghona | 30 | 18:30 | Kabirpur | 230 | 00:00 | Naogaon | 136 | 23:00 | Sherpur | 158 | 19:30
36 | Chapai | 65 | 00:00 | Kachua | 83 | 21:00 | Narail | 57 | 19:00 | Shikalbaha | 16 | 19:30
37 | Charsaidpur | 24 | 08:00 | Kallyanpur | 93 | 20:00 | Narinda | 58 | 13:00 | Shikalbaha-230 | N/A | N/A
38 | Chauddagram | 65 | 23:00 | Kalurghat | 26 | 00:00 | Narshingdi | 191 | 21:00 | Shitalakhya | 79.2 | 00:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-09-15 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 400 | 17:00 | 391 | 11:00 | Gopalganj | 408 | 07:00 | 396 | 12:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 383 | 18:30 | 371 | 11:00
| Bhulta | 402 | 17:00 | 390 | 12:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 404 | 17:00 | 395 | 11:00 | Payra | 415 | 17:00 | 408 | 13:00
| BIPTC | 399 | 05:00 | 393 | 15:00 | Rahanpur | 399 | 17:00 | 384 | 00:00
| Bogura | N/A | N/A | N/A | N/A | Rampal | 411 | 07:00 | 398 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 234 | 18:30 | 227 | 12:00 | Hasnabad | 235 | 17:00 | 228 | 12:00
| AKSML | 231 | 19:00 | 220 | 14:00 | Hathazari | 232 | 19:00 | 224 | 11:00
| Aminbazar | 235 | 16:00 | 230 | 00:00 | Ishurdi | 235 | 16:00 | 223 | 01:00
| Ashuganj | 238 | 18:30 | 231 | 12:00 | Jhenaidah | 229 | 16:00 | 215 | 12:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 236 | 19:00 | 228 | 12:00
| Baghabari | 231 | 07:00 | 221 | 12:00 | Keranigonj | 235 | 19:00 | 227 | 12:00
| Barapukuria | 217 | 17:00 | 205 | 01:00 | Khulna(S) | 237 | 16:00 | 224 | 12:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 238 | 03:00 | 226 | 23:00 | Maniknagar | 235 | 19:00 | 228 | 12:00
| Bheramara | 236 | 16:00 | 224 | 01:00 | Meghnaghat | 244 | 18:00 | 237 | 02:00
| Bhulta | 238 | 19:00 | 231 | 12:00 | Mirsorai | 235 | 19:00 | 221 | 11:00
| Bibiana | 234 | 19:00 | 226 | 22:00 | Rajshahi | 233 | 06:00 | 218 | 12:00
| BIPTC | 236 | 17:00 | 221 | 12:00 | Rampal | 236 | 17:00 | 225 | 12:00
| Bogura | 225 | 17:00 | 214 | 04:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 242 | 08:00 | 230 | 18:00 | Rampura | 236 | 19:30 | 229 | 12:00
| BSRM | 234 | 19:00 | 222 | 11:00 | Shikalbaha | 230 | 19:30 | 223 | 11:00
| Cumilla(N) | 233 | 19:00 | 227 | 02:00 | Shyampur | 236 | 19:00 | 229 | 01:00
| Fenchuganj | 238 | 19:00 | 230 | 05:00 | Siddhirganj | 238 | 19:00 | 231 | 12:00
| Ghorashal | 240 | 18:00 | 235 | 00:00 | Sirajgonj | 236 | 07:00 | 231 | 04:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 233 | 17:00 | 227 | 01:00
| GPH | 232 | 19:00 | 220 | 11:00 | Tongi | 233 | 18:30 | 223 | 12:00
| Haripur | 234 | 19:00 | 229 | 12:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 138 | 06:00 | 134 | 11:00 | Lalbag | 137 | 08:00 | 133 | 00:00
| Agargaon | 153 | 18:00 | 132 | 18:00 | Lalmonirhat | 126 | 17:00 | 115 | 00:00
| Agrabad | 133 | 19:00 | 128 | 12:00 | Madanganj | 138 | 19:00 | 131 | 11:00
| AKS | 137 | 09:00 | 126 | 14:00 | Madaripur | 132 | 17:00 | 128 | 12:00
| Aminbazar | 135 | 16:00 | 131 | 00:00 | Madartek | 137 | 07:00 | 132 | 12:00
| Amnura | 137 | 19:30 | 119 | 22:00 | Madunaghat | 134 | 19:00 | 129 | 11:00
| Ashuganj | 140 | 17:00 | 137 | 00:00 | Magura | 137 | 09:00 | 127 | 21:00
| Bagerhat | 136 | 16:00 | 125 | 12:00 | Mahasthangarh | 131 | 10:00 | 122 | 21:00
| Bakulia | 132 | 00:00 | 128 | 11:00 | Manikganj | 134 | 18:00 | 133 | 18:00
| Banani | 138 | 19:00 | 134 | 10:00 | Maniknagar | 136 | 19:00 | 132 | 11:00
| Bangabhaban | 136 | 19:00 | 132 | 12:00 | Matarbari | 123 | 09:00 | 111 | 20:00
| Barapukuria | 134 | 16:00 | 125 | 01:00 | Matuail | 137.5 | 19:00 | 132.5 | 12:00
| Barguna | 137 | 17:00 | 133 | 03:00 | Millgate | 138 | 19:00 | 130 | 04:00
| Barishal | 137 | 20:00 | 130 | 23:00 | Mirpur | 134 | 19:00 | 129 | 11:00
| Barishal-230 | 138 | 07:00 | 131 | 22:00 | Mithapukur | 128 | 16:00 | 118 | 22:00
| Baroaulia | 133 | 19:00 | 129 | 11:00 | Modern | 133 | 07:00 | 129 | 02:00
| Baroirhat | 129 | 00:00 | 122 | 15:00 | Mogbazar | 140 | 07:00 | 135 | 10:00
| Bashundhara | 138 | 08:00 | 132 | 00:00 | Mongla | 136 | 16:00 | 129 | 02:00
| BashundharaCement | 138 | 19:00 | 131 | 11:00 | Motijheel | 136 | 19:00 | 132 | 12:00
| Beanibazar | 126 | 07:00 | 121 | 22:00 | Munshiganj | 139 | 19:00 | 132 | 11:00
| Benapole | 137 | 16:00 | 127 | 18:30 | Mymensingh | 132 | 18:30 | 115 | 22:00
| Bhaluka | 124 | 08:00 | 119 | 21:00 | Naogaon | 129 | 17:00 | 115 | 22:00
| Bhandaria | 137 | 20:00 | 126 | 01:00 | Narail | 137 | 17:00 | 126 | 01:00
| Bhangura | 139 | 06:00 | 130 | 01:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 135 | 16:00 | 128 | 01:00 | Narshingdi | 131 | 16:00 | 126 | 00:00
| Bheramara(GK) | 136 | 17:00 | 128 | 01:00 | Natore | 132 | 17:00 | 122 | 22:00
| Bhulta | 129 | 13:00 | 123 | 03:00 | Nawabganj | 138 | 18:00 | 132 | 21:00
| Bog-Sherpur | 133 | 06:00 | 118 | 18:30 | Netrakona | 131 | 18:00 | 119 | 12:00
| Bogura | 135 | 17:00 | 114 | 22:00 | New | 137 | 18:30 | 132 | 12:00
| Bogura-230 | 136 | 17:00 | 126 | 04:00 | Niamatpur | 127 | 17:00 | 111 | 22:00
| Brahmanbaria | 127 | 17:00 | 121 | 02:00 | Noapara | 138 | 17:00 | 128 | 12:00
| Cantonment | 134 | 07:00 | 129 | 11:00 | Pabna | 137 | 06:00 | 125 | 23:00
| Chandpur | 127 | 19:00 | 120 | 03:00 | Palashbari | 127 | 16:00 | 116 | 21:00
| Chandraghona | 135 | 19:00 | 131 | 10:00 | Panchagarh | 124 | 17:00 | 110 | 05:00
| Chapai | 127 | 09:00 | 120 | 00:00 | Patuakhali | 137 | 00:00 | 134 | 01:00
| Charsaidpur | 140 | 19:00 | 132 | 11:00 | Payra | 140 | 19:00 | 137 | 01:00
| Chauddagram | 130 | 19:00 | 123 | 02:00 | PHP | 128 | 00:00 | 122 | 01:00
| Chhatak | 127 | 06:00 | 123 | 04:00 | Postogola | 139 | 19:00 | 133 | 12:00
| Chowmuhani | 122 | 00:00 | 115 | 05:00 | Purbachal | 138 | 07:00 | 130 | 12:00
| Chuadanga | 134 | 17:00 | 120 | 18:30 | Purbasadipur | 124 | 16:00 | 110 | 01:00
| Coxsbazar | 123 | 17:00 | 113 | 23:00 | Rahanpur | 132 | 17:00 | 126 | 00:00
| Cumilla(N) | 134 | 17:00 | 130 | 01:00 | Rahim | 138 | 19:00 | 133 | 12:00
| Cumilla(S) | 134 | 19:00 | 125 | 13:00 | Rajbari | 130 | 06:00 | 124 | 00:00
| Daudkandi | 129 | 17:00 | 122 | 02:00 | Rajendrapur | 138 | 19:00 | 127 | 00:00
| Dhaka | 138 | 19:00 | 134 | 11:00 | Rajshahi | 133 | 17:00 | 125 | 12:00
| Dhamrai | 136 | 19:00 | 131 | 00:00 | Rajshahi-230 | 135 | 06:00 | 118 | 01:00
| Dhanmondi | 137 | 19:00 | 132 | 12:00 | Ramganj | 121 | 00:00 | 114 | 02:00
| Dohazari | 128 | 10:00 | 123 | 01:00 | Rampur | 133 | 22:00 | 123 | 11:00
| Faridpur | 131 | 17:00 | 126 | 00:00 | Rampura | 137 | 17:00 | 133 | 12:00
| Fatullah | 141 | 19:00 | 129 | 21:00 | Rangamati | 134 | 19:00 | 130 | 02:00
| Fenchuganj | 132 | 00:00 | 130 | 05:00 | Rangpur | 127 | 17:00 | 116 | 00:00
| Feni | 130 | 19:00 | 122 | 03:00 | Ruppur | 138 | 17:00 | 130 | 01:00
| Ghorashal | 141 | 19:00 | 136 | 00:00 | Saidpur | 129 | 17:00 | 113 | 01:00
| Goalpara | 139 | 17:00 | 129 | 12:00 | Satkhira | 134 | 16:00 | 125 | 18:30
| Gollamari | 137 | 16:00 | 130 | 12:00 | Satmasjid | 134 | 07:00 | 129 | 12:00
| Gopalganj | 134 | 19:00 | 126 | 12:00 | Savar | 135 | 19:00 | 128 | 12:00
| Gopalganj-400 | 131 | 07:00 | 127 | 12:00 | Shahjadpur | 142 | 07:00 | 132 | 00:00
| Gulshan | 137 | 06:00 | 133 | 12:00 | Shahjibazar | 129 | 08:00 | 125 | 00:00
| Halishahar | 133 | 19:00 | 128 | 11:00 | Shahmirpur | 132 | 07:00 | 128 | 11:00
| Haripur | 138 | 19:00 | 133 | 12:00 | Shariatpur | 131 | 07:00 | 126 | 18:30
| HaripurSBU | 138 | 19:00 | 133 | 12:00 | Sherpur | 125 | 18:30 | 108 | 10:00
| Hasnabad | 138 | 19:00 | 133 | 12:00 | Shikalbaha | 122 | 06:00 | 118 | 11:00
| Hathazari | 136 | 19:00 | 131 | 11:00 | Shikalbaha-230 | 133 | 08:00 | 129 | 11:00
| Ishurdi | 138 | 17:00 | 130 | 00:00 | Shitalakhya | 139.6 | 19:00 | 132.2 | 12:00
| Jaldhaka | 126 | 17:00 | 112 | 18:30 | Sholosohor | 133 | 19:00 | 127 | 11:00
| Jamalpur | 131 | 18:30 | 114 | 10:00 | Shyampur | 138 | 18:00 | 134 | 11:00
| Jashore | 138 | 17:00 | 128 | 12:00 | Shyampur-230 | 140 | 19:00 | 126 | 13:00
| Jhenaidah | 140 | 17:00 | 129 | 18:30 | Siddhirganj | 138 | 19:00 | 132 | 12:00
| Jhenaidah-230 | 140 | 17:00 | 130 | 18:30 | Sirajganj | 134 | 10:00 | 122 | 00:00
| Joydebpur | 140 | 19:00 | 132 | 00:00 | Sonargaon | 134 | 19:00 | 130 | 07:00
| Joypurhat | 127 | 17:00 | 113 | 22:00 | Sreemongol | 129 | 08:00 | 125 | 18:30
| Juldah | 133 | 16:00 | 128 | 09:00 | Sreepur | 128 | 18:00 | 123 | 01:00
| Kabirpur | 138 | 19:00 | 129 | 11:00 | Srinagar | 137 | 18:30 | 133 | 21:00
| Kachua | 128 | 17:00 | 119 | 02:00 | SSM | 137 | 00:00 | 130 | 11:00
| Kaliakoir | 138 | 18:30 | 132 | 02:00 | Sunamganj | 124 | 08:00 | 118 | 22:00
| Kallyanpur | 136 | 19:00 | 130 | 12:00 | Sylhet | 129 | 05:00 | 127 | 21:00
| Kalurghat | 132 | 07:00 | 129 | 01:00 | Tangail | 130 | 03:00 | 124 | 15:00
| Kamrangirchar | 138 | 18:30 | 129 | 00:00 | Thakurgaon | 122 | 17:00 | 108 | 03:00
| Kaptai | N/A | N/A | N/A | N/A | TK | 133 | 17:00 | 130 | 02:00
| Kazla | 136 | 18:30 | 132 | 12:00 | Tongi | 138 | 18:30 | 133 | 00:00
| Keranigonj | 137 | 06:00 | 133 | 12:00 | Ullon | 137 | 07:00 | 133 | 12:00
| Khagrachori | 132 | 03:00 | 129 | 11:00 | Uttara | 135 | 19:00 | 129 | 13:00
| Khulna | 137 | 17:00 | 128 | 12:00 | UttaraNew | 134 | 19:30 | 128 | 12:00
| Khulna(S) | 138 | 17:00 | 128 | 12:00 | Zigatola | 137 | 07:00 | 132 | 12:00
| Khulshi | 132 | 19:00 | 127 | 11:00
| Kishoreganj | 131 | 19:00 | 125 | 18:30
| Kodda | 139 | 18:30 | 126 | 02:00
| KSRM | 135 | 19:00 | 129 | 02:00
| Kulaura | 130 | 00:00 | 128 | 18:30
| Kurigram | 126 | 16:00 | 112 | 18:30
| Kushtia | 136 | 17:00 | 126 | 18:30

## L-Curve
Date | 2023-09-15
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1056 | 7915 | 5660 | 13575 |  |  |  | QF-LDC-11
0:30 | 1053 | 7695 | 5592.5 | 13287.5 | Date: | 2023-09-15
1:00 | 1050 | 7475 | 5525 | 13000
1:30 | 1060 | 7444 | 5450.5 | 12894.5
2:00 | 1070 | 7413 | 5376 | 12789
2:30 | 1045 | 7331 | 5328 | 12659 | [5 empty] | Gen. at Eve. Peak | 13926 | 13926 MW (21:00 )
3:00 | 1020 | 7249 | 5280 | 12529 | [6 empty] | 21:00
3:30 | 1035 | 7208 | 5198 | 12406 | [5 empty] | Gen. at Day Peak | 11455 | 11455 MW (12:00 )
4:00 | 1050 | 7167 | 5116 | 12283 | [6 empty] | 12:00
4:30 | 1060 | 7084 | 5063 | 12147 | [5 empty] | Highest Generation | 13974
5:00 | 1070 | 7001 | 5010 | 12011 | [6 empty] | 22:00
5:30 | 1090 | 6855 | 4892 | 11747
6:00 | 1110 | 6709 | 4774 | 11483
6:30 | 1115 | 6593.5 | 4656.5 | 11250
7:00 | 1120 | 6478 | 4539 | 11017
7:30 | 1165 | 6378 | 4528 | 10906
8:00 | 1210 | 6278 | 4517 | 10795
8:30 | 1250 | 6225 | 4528 | 10753
9:00 | 1290 | 6172 | 4539 | 10711
9:30 | 1325 | 6232 | 4455 | 10687
10:00 | 1360 | 6292 | 4371 | 10663
10:30 | 1365 | 6355 | 4440 | 10795
11:00 | 1370 | 6418 | 4509 | 10927
11:30 | 1300 | 6579.5 | 4611.5 | 11191
12:00 | 1230 | 6741 | 4714 | 11455
12:30 | 1195 | 6961.5 | 4822 | 11783.5
13:00 | 1160 | 7182 | 4930 | 12112
13:30 | 1125 | 7100 | 4868.5 | 11968.5
14:00 | 1090 | 7018 | 4807 | 11825
14:30 | 1165 | 7082.5 | 4843 | 11925.5
15:00 | 1240 | 7147 | 4879 | 12026
15:30 | 1240 | 7009.5 | 4768.5 | 11778
16:00 | 1240 | 6872 | 4658 | 11530
16:30 | 1195 | 6829 | 4562.5 | 11391.5
17:00 | 1150 | 6786 | 4467 | 11253
17:30 | 1125 | 6727.5 | 4374 | 11101.5
18:00 | 1100 | 6669 | 4281 | 10950
18:30 | 930 | 7433 | 4781 | 12214
19:00 | 760 | 8197 | 5281 | 13478
19:30 | 820 | 8389 | 5343 | 13732
20:00 | 860 | 8347 | 5393 | 13740 |  |  |  | Executive Engineer
20:30 | 875 | 8387.5 | 5445.5 | 13833 |  |  |  | Network Operation Division
21:00 | 890 | 8428 | 5498 | 13926
21:30 | 910 | 8430 | 5520 | 13950
22:00 | 930 | 8432 | 5542 | 13974 |  |  |  |  | Page 6 of 7
22:30 | 973 | 8379 | 5562.5 | 13941.5
23:00 | 1016 | 8326 | 5583 | 13909
23:30 | 1036 | 8120.5 | 5621.5 | 13742
24:00 | 1056 | 7915 | 5660 | 13575
13926 MW (21:00 )
11455 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-09-15 |  | Energy |  | 295693531
QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3950 | 820 | 2445 | 0 | 2242 | 3457 | 201 | 0 | 292 | 168 | 0 | 0 | 549.125
0:30 | 3918 | 872 | 2519 | 0 | 1856 | 3458 | 199.5 | 60 | 236 | 163 | 0 | 6 | 634.12 |  | Date: | 43722
1:00 | 3886 | 924 | 2593 | 0 | 1470 | 3459 | 198 | 120 | 180 | 158 | 0 | 12 | 719.115
1:30 | 3896 | 900 | 2566 | 0 | 1463 | 3458 | 197.5 | 121 | 125 | 159 | 0 | 9 | 685.69 | [7 empty] | Total Energy | 295.6935 | 295.6935 | Total Energy Gen 295.694 MKWHr Energy Not Served 5.467 MKWHr Energy Requirement 301.160 MKWHr
2:00 | 3906 | 876 | 2539 | 0 | 1456 | 3457 | 197 | 122 | 70 | 160 | 0 | 6 | 652.265 | [7 empty] | Energy not Served | 5.4669 | 5.4669
2:30 | 3904 | 899.5 | 2529.5 | 0 | 1348 | 3424 | 197 | 122 | 68.5 | 159 | 0 | 7.5 | 600.2175 | [7 empty] | Energy Requirement | 301.1605 | 301.1605
3:00 | 3902 | 923 | 2520 | 0 | 1240 | 3391 | 197 | 122 | 67 | 158 | 0 | 9 | 548.17
3:30 | 3903.5 | 923.5 | 2497.5 | 0 | 1150 | 3398 | 197 | 121.5 | 44 | 161 | 0 | 10 | 517.61
4:00 | 3905 | 924 | 2475 | 0 | 1060 | 3405 | 197 | 121 | 21 | 164 | 0 | 11 | 487.05
4:30 | 3912 | 923.5 | 2439.5 | 0 | 954 | 3411.5 | 197 | 121 | 18.5 | 162 | 0 | 8 | 454.58
5:00 | 3919 | 923 | 2404 | 0 | 848 | 3418 | 197 | 121 | 16 | 160 | 0 | 5 | 422.11
5:30 | 3877.5 | 924 | 2340.5 | 0 | 763.5 | 3351 | 197 | 121 | 16 | 150 | 1.5 | 5 | 402.055
6:00 | 3836 | 925 | 2277 | 0 | 679 | 3284 | 197 | 121 | 16 | 140 | 3 | 5 | 382
6:30 | 3785 | 924.5 | 2234 | 0 | 682 | 3175 | 131 | 121 | 16 | 134 | 42 | 5.5 | 302.2575 | [6 empty] | Coal
7:00 | 3734 | 924 | 2191 | 0 | 685 | 3066 | 65 | 121 | 16 | 128 | 81 | 6 | 222.515
7:30 | 3647.5 | 923.5 | 2156.5 | 0 | 672 | 3029 | 65 | 121.5 | 16 | 126 | 145 | 4 | 185.27 | [5 empty] | Oil
8:00 | 3561 | 923 | 2122 | 0 | 659 | 2992 | 65 | 122 | 16 | 124 | 209 | 2 | 148.025
8:30 | 3562.5 | 923.5 | 2105 | 0 | 582.5 | 2997 | 65 | 121.5 | 16 | 125 | 253 | 2 | 116.51
9:00 | 3564 | 924 | 2088 | 0 | 506 | 3002 | 65 | 121 | 16 | 126 | 297 | 2 | 84.995
9:30 | 3542.5 | 924 | 2103.5 | 0 | 488 | 3001.5 | 132 | 60.5 | 32 | 121 | 279 | 3 | 60.165
10:00 | 3521 | 924 | 2119 | 0 | 470 | 3001 | 199 | 0 | 48 | 116 | 261 | 4 | 35.335
10:30 | 3569.5 | 924 | 2155.5 | 0 | 462 | 3007.5 | 199 | 0 | 48 | 121 | 306 | 2.5 | 17.6675
11:00 | 3618 | 924 | 2192 | 0 | 454 | 3014 | 199 | 0 | 48 | 126 | 351 | 1 | 0
11:30 | 3657 | 924 | 2266 | 0 | 553.5 | 3090 | 199 | 0 | 65 | 121 | 313.5 | 2 | 0
12:00 | 3696 | 924 | 2340 | 0 | 653 | 3166 | 199 | 0 | 82 | 116 | 276 | 3 | 0
12:30 | 3692.5 | 924 | 2415.5 | 0 | 831.5 | 3231 | 198 | 0 | 82 | 126 | 278 | 5 | 0
13:00 | 3689 | 924 | 2491 | 0 | 1010 | 3296 | 197 | 0 | 82 | 136 | 280 | 7 | 0
13:30 | 3689 | 924 | 2491 | 0 | 1010 | 3296 | 197 | 0 | 82 | 136 | 280 | 7 | 0
14:00 | 3689 | 924 | 2491 | 0 | 1010 | 3296 | 197 | 0 | 82 | 136 | 280 | 7 | 0
14:30 | 3666 | 924 | 2534.5 | 0 | 1004 | 3258 | 196 | 0 | 73 | 143 | 264 | 6.5 | 0
15:00 | 3643 | 924 | 2578 | 0 | 998 | 3220 | 195 | 0 | 64 | 150 | 248 | 6 | 0
15:30 | 3595 | 924.5 | 2434.5 | 0 | 970 | 3239 | 195 | 0 | 64 | 147 | 203 | 6 | 50.1375
16:00 | 3547 | 925 | 2291 | 0 | 942 | 3258 | 195 | 0 | 64 | 144 | 158 | 6 | 100.275
16:30 | 3551 | 924 | 2270 | 0 | 901 | 3226.5 | 195 | 0 | 64 | 142 | 113 | 5 | 96.455
17:00 | 3555 | 923 | 2249 | 0 | 860 | 3195 | 195 | 0 | 64 | 140 | 68 | 4 | 92.635
17:30 | 3537 | 923 | 2218.5 | 0 | 854 | 3124 | 195.5 | 0 | 66.5 | 146 | 35 | 2 | 94.0675
18:00 | 3519 | 923 | 2188 | 0 | 848 | 3053 | 196 | 0 | 69 | 152 | 2 | 0 | 95.5
18:30 | 3598 | 862 | 2177 | 0 | 1751 | 3160 | 197.5 | 0 | 315 | 152 | 1 | 0.5 | 129.88
19:00 | 3677 | 801 | 2166 | 0 | 2654 | 3267 | 199 | 0 | 561 | 152 | 0 | 1 | 164.26
19:30 | 3748 | 801 | 2177 | 0 | 2848 | 3284 | 199 | 0 | 518 | 154 | 0 | 3 | 134.655
20:00 | 3804 | 801 | 2250 | 0 | 2782 | 3332 | 199 | 0 | 426 | 146 | 0 | 0 | 105.05
20:30 | 3844 | 800.5 | 2303 | 0 | 2749 | 3369 | 199 | 0 | 418.5 | 150 | 0 | 0 | 111.525
21:00 | 3884 | 800 | 2356 | 0 | 2716 | 3406 | 199 | 0 | 411 | 154 | 0 | 0 | 118
21:30 | 3882.5 | 800 | 2364 | 0 | 2743 | 3396 | 199.5 | 0 | 412.5 | 152 | 0 | 0.5 | 143.04
22:00 | 3881 | 800 | 2372 | 0 | 2770 | 3386 | 200 | 0 | 414 | 150 | 0 | 1 | 168.08
22:30 | 3940.5 | 810 | 2404 | 0 | 2632 | 3401 | 200.5 | 0 | 396 | 157 | 0 | 0.5 | 246.8675
23:00 | 4000 | 820 | 2436 | 0 | 2494 | 3416 | 201 | 0 | 378 | 164 | 0 | 0 | 325.655
23:30 | 3975 | 820 | 2440.5 | 0 | 2368 | 3436.5 | 201 | 0 | 335 | 166 | 0 | 0 | 437.39 |  | Max Temp. in Dhaka |  | 35°C
24:00 | 3950 | 820 | 2445 | 0 | 2242 | 3457 | 201 | 0 | 292 | 168 | 0 | 0 | 549.125
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 295.694 MKWHr Energy Not Served 5.467 MKWHr Energy Requirement 301.160 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-09-15
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 123 | 122 | 122 | 122 | 122 | 122 | 65 | 65 | 65 | 124 | 124 | 124 | 122 | 122 | 120 | 120 | 120 | 121 |  | 124 | 124 | 124 | 124 | 125 | 126 | 126 | 2772698
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 0 | 0 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1552000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | [10 empty] | 10 | 17 | 17 | 15 | 17 | 8 | 8 | 151745
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 3 | 8 | 13 | 20 | 20 | 20 | 16 | 17 | 18 | 3 | 2 | [9 empty] | 131085
6 | Sikalbaha 225MW CCPP (Gas) | 225 | 225 | 226 | 226 | 227 | 225 | 226 | 220 | 222 | 221 | 220 | 216 | 218 | 215 | 218 | 221 | 223 | 219 |  | 223 | 222 | 221 | 222 | 222 | 222 | 223 | 5329680
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [25 empty] | 0 | 0
12 | Hathazari 100 MW peaking PP | 23 | 23 | 23 | [16 empty] | 56 | 63 | 63 | 63 | 56 | 56 | 30 | 372912
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 431563
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [22 empty] | 10 | 23 | 23 | 23 | 67568
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 327 | 328 | 326 | 327 | 329 | 329 | 326 | 280 | 280 | 280 | 280 | 280 | 310 | 270 | 312 | 270 | 270 | 240 |  | 270 | 270 | 300 | 320 | 322 | 322 | 325 | 7310867
18 | Kodda 300 MW PP Unit-2 (Summit) | 47 | 47 | 47 | 47 | 15 | 15 | 15 | 15 | 0 | [10 empty] | 85 | 115 | 122 | 130 | 130 | 130 | 70 | 963491
19 | Ashuganj 195 MW PP (APSCL-United) | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 107 | 108 | 145 | 145 | 145 | 173 | 173 | 175 | 177 |  | 108 | 78 | 78 | 78 | 78 | 90 | 123 | 2877091
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 170 | 170 | 170 | 170 | 210 | 150 | 180 | 180 | 140 | 170 |  | 205 | 210 | 210 | 210 | 210 | 210 | 210 | 4638313
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 622 | 621 | 621 | 622 | 624 | 621 | 625 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 624 |  | 612 | 620 | 612 | 620 | 612 | 620 | 622 | 14939998
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 48 | 48 | 47 | 44 | 46 | 46 | 43 | 41 | 42 | 46 | 47 |  | 47 | 48 | 48 | 48 | 48 | 48 | 49 | 1117368
33 | Ashuganj 225 MW CCPP | 195 | 209 | 212 | 210 | 210 | 210 | 211 | 208 | 209 | 205 | 205 | 206 | 206 | 202 | 203 | 204 | 200 | 171 |  | 170 | 204 | 206 | 208 | 208 | 206 | 210 | 4923000
34 | Ashuganj 450 MW CCPP(South) | 305 | 305 | 305 | 305 | 305 | 270 | 270 | 265 | 240 | 265 | 265 | 270 | 305 | 310 | 305 | 305 | 305 | 305 |  | 305 | 270 | 270 | 270 | 265 | 325 | 305 | 7083000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 275 | 350 | 275 | 275 | 280 | 305 | 305 | 305 | 310 | 310 | 320 |  | 310 | 310 | 310 | 310 | 310 | 330 | 310 | 7499100
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP | [9 empty] | 0 | 20 | 20 | 0 | [13 empty] | 38196
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 413 | 419 | 416 | 420 | 419 | 404 | 351 | 351 | 351 | 352 | 353 | 353 | 387 | 408 | 402 | 409 | 410 | 382 |  | 393 | 408 | 408 | 409 | 409 | 409 | 409 | 9572360
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 400 | 360 | 320 | 320 | 320 | 370 | 450 | 450 | 370 | 420 | 420 | 420 | 370 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 9733500
41 | Haripur 360 MW CCPP(HPL) | 337 | 337 | 337 | 337 | 337 | 301 | 287 | 272 | 271 | 272 | 272 | 272 | 330 | 282 | 332 | 328 | 328 | 330 |  | 282 | 282 | 331 | 332 | 332 | 332 | 332 | 7510000
42 | RPCL 210MW CCPP | 47 | 46 | 47 | 47 | 47 | 46 | 32 | 27 | 27 | 27 | 26 | 25 | 25 | 29 | 30 | 32 | 32 | 32 |  | 44 | 45 | 52 | 82 | 82 | 81 | 80 | 969600
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 15 | 28 | 35 | 23 | 47 | 33 | 21 | 46 | 19 | 7 | 8 | 0 | [8 empty] | 301440
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 40 | 40 | 40 | 40 | 40 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1002000
45 | Fenchugonj CCPP Phase-2 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 39 | 39 | 40 | 39 | 39 | 39 | 39 |  | 39 | 39 | 39 | 39 | 40 | 41 | 40 | 913200
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86 MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 78 | 78 | 78 | 78 | 40 | 40 | 78 | 78 | 78 | 77 | 77 | 83 | 85 | 65 |  | 86 | 86 | 86 | 84 | 84 | 84 | 84 | 1820160
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 185 | 185 | 185 | 185 | 185 | 184 | 185 | 185 | 185 | 187 | 187 | 187 | 182 | 183 | 180 | 180 | 181 | 182 |  | 181 | 181 | 181 | 181 | 181 | 182 | 182 | 4736670
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 395000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 251460
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 8 | 5 | 5 | 5 | 5 | 5 | 172080
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 44 | 44 | 46 | 28 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1122600
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 0 | 16 | 16 | 354072
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 265 | 275 | 260 | 265 | 270 | 270 | 270 | 275 | 290 | 300 | 290 | 280 | 280 | 310 | 275 | 280 | 275 |  | 280 | 270 | 265 | 290 | 295 | 295 | 290 | 6891000
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 400 | 398 | 370 | 370 | 380 | 380 | 380 | 350 | 350 | 350 | 350 | 340 | 350 |  | 335 | 350 | 375 | 390 | 390 | 390 | 397 | 9106000
58 | Nababganj 55 MW PP (Southern power ) | [12 empty] | 17 | 17 | 17 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 442944
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 148800
60 | Barabkunda 22 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 10 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 266496
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 444420
62 | Tangail 22 MW PP (Doreen) | 16 | 17 | 17 | 17 | 16 | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 18 |  | 18 | 18 | 18 | 18 | 16 | 16 | 16 | 394776
63 | Impoprt (Tripura) | 158 | 160 | 158 | 164 | 160 | 140 | 128 | 124 | 126 | 116 | 126 | 116 | 136 | 142 | 150 | 144 | 140 | 152 |  | 152 | 154 | 146 | 154 | 150 | 164 | 168 | 3477120
64 | Malancha, Ctg. EPZ (United) | 39 | 39 | 39 | 39 | 42 | 33 | 37 | 38 | 25 | 13 | 2 | 2 | 2 | 2 | 2 | 19 | 21 | 26 |  | 33 | 33 | 33 | 39 | 39 | 39 | 42 | 669600
65 | Feni 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 429336
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 250200
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 33 | 32 | 31 | 32 | 32 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 756200
68 | Cumilla 25 MW PP (Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 280100
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456000
70 | Summit Madhabdi | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 0 | 10 | 10 | 10 | 10 | 10 | 10 |  | 13 | 19 | 19 | 19 | 19 | 19 | 19 | 347760
71 | Maona 33 MW PP(Summit) | 30 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 593800
72 | Rupganj 33 MW PP(Summit) | 28 | 28 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 |  | 30 | 24 | 24 | 24 | 24 | 31 | 30 | 699700
73 | Ghorashal 108 MW PP (Regent) | 82 | 82 | 82 | 82 | 79 | 79 | 82 | 82 | 79 | 79 | 78 | 76 | 76 | 76 | 73 | 73 | 76 | 79 |  | 80 | 81 | 82 | 83 | 83 | 83 | 83 | 1872409
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 21 | 52 | 52 | 52 | 52 | 52 | 34 | 17 |  | 106 | 106 | 106 | 98 | 105 | 105 | 105 | 1144560
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 9 | 9 | 9 | 9 | 9 | 27 | 27 | 28 | 28 | 28 | 28 |  | 76 | 76 | 76 | 76 | 78 | 77 | 35 | 676200
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 4 | 54 | 17 | 35 | 35 | 17 | 17 |  | 125 | 162 | 162 | 162 | 162 | 108 | 17 | 1166400
77 | Siddhirganj 100 PP(Dutch Bangla) | 88 | 87 | 87 | 73 | 16 | 0 | [6 empty] | 12 | 13 | 9 | 9 | 9 | 9 |  | 28 | 40 | 40 | 40 | 40 | 40 | 75 | 657600
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 209760
79 | Kodda 150 MW PP | 32 | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 48 | 48 | 82 | 82 | 82 | 64 | 64 | 64 | 64 |  | 147 | 98 | 64 | 32 | 32 | 32 | 48 | 1106400
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 25 | 25 | 27 | 52 | 49 | 34 | 32 | 32 | 32 | 16 |  | 24 | 51 | 52 | 52 | 43 | 43 | 43 | 1012512
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 105 | 105 | 105 | 105 | 105 | 105 | 35 | 856320
| Kaptai 7 MW Solar PP | [7 empty] | 2 | 3 | 5 | 4 | 5 | 4 | 4 | 3 | 2 | 1 | [9 empty] | 30359
| Jodiac Power | 17 | 17 |  |  |  | 1 | 17 | 17 | 17 | 17 | 0 |  | 11 | 17 | 17 | 17 | 17 | 17 |  | 30 | 54 | 54 | 54 | 17 | 17 | 17 | 450398
| Karnaphuli Power Ltd. | 59 | 64 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 34 | 41 | 55 | 55 | 55 | 44 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1338180
82 | Madanganj 102 PP(Summit) | 75 | 85 | 85 | 75 | 28 | 17 | 17 | 17 | 14 | 0 |  |  | 6 | 17 | 17 | 17 | 17 | 17 |  | 26 | 78 | 78 | 83 | 85 | 85 | 85 | 858129
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 4 | 21 | 0 |  |  |  | 8 | 22498
86 | Meghnaghat CCPP ( Summit) | 269 | 295 | 270 | 282 | 282 | 280 | 276 | 285 | 302 | 296 | 285 | 286 | 277 | 299 | 282 | 274 | 261 | 303 |  | 237 | 277 | 304 | 285 | 301 | 313 | 283 | 6860858
87 | Meghnaghat 100 MW(IEL) | 72 | 69 | 33 | [9 empty] | 8 | 12 | 9 | 8 | 8 | 8 |  | 27 | 48 | 47 | 48 | 48 | 48 | 51 | 499200
| Meghnaghat 104 MW PP (OPCL) | 45 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 0 |  |  |  | 23 | 17 | 22 | 28 | 17 | 17 |  | 46 | 72 | 72 | 72 | 72 | 72 | 72 | 809280
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 265080
92 | Fenchuganj 44 MW (Energyprima) | 43 | 43 | 40 | 40 | 37 | 38 | 37 | 40 | 39 | 39 | 38 | 38 | 38 | 35 | 35 | 35 | 32 | 39 |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 911736
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 15 | 15 | 15 |  | 33 | 43 | 43 | 51 | 43 | 43 | 51 | 1078580
94 | Gagnagar 102 MW PP (Digital Power) | 91 | 91 | 91 | 91 | 74 | 25 | 16 | 8 | 8 | 8 | 8 | 25 | 25 | 25 | 25 | 25 | 25 | 32 |  | 91 | 91 | 91 | 91 | 91 | 91 | 74 | 1224288
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 8 | 6 | 6 | 153120
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 | [14 empty] | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 25 | 25 | 25 | 25 | 25 |  | 55 | 55 | 55 | 15 | 15 | 15 | 15 | 510705
100 | Manikganj 55 MW PP (Northern) | [10 empty] | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 440555
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 112 | 80 | 80 | 80 | 80 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 80 |  | 80 | 80 | 80 | 112 | 112 | 112 | 112 | 2474590
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 0 | 1 | 1 | 1 | 0 | [9 empty] | 10400
103 | Kamalaghat 54 MW PP(Banco Energy) | [6 empty] | 0 | 0 |  |  |  |  | 17 | 17 | 17 | 17 | 17 | 0 |  | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 388800
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 113 | 115 | 125 | 125 | 116 | 67 | 67 | 76 |  | 153 | 153 | 153 | 153 | 153 | 68 | 67 | 2200800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 48 | 53 | 22 | 17 | 17 | 40 |  | 149 | 149 | 149 | 149 | 149 | 86 | 17 | 1123488
115 | Juldah 100 MW PP Unit-3 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 253440
116 | Chandpur 200 MW (Desh energy) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 36 | 66 | 97 | 100 | 76 | 68 | 68 | 51 |  | 85 | 100 | 104 | 104 | 104 | 104 | 46 | 1470720
117 | Ashuganj 150 MW PP (Midland) | 115 | 102 | 18 | 18 | 18 | 18 | 18 | 18 | 13 | 0 |  |  | 5 | 10 | 10 | 10 | 10 | 10 |  | 30 | 70 | 10 | 10 | 10 | 11 | 35 | 557018
118 | Bibiyana-III 400 MW CCPP | 403 | 403 | 403 | 403 | 403 | 402 | 402 | 354 | 354 | 355 | 405 | 405 | 357 | 376 | 403 | 329 | 330 | 340 |  | 368 | 368 | 367 | 368 | 368 | 388 | 368 | 9123000
| Jamalpur 115 MW PP (United) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 37 | 37 | 38 | 37 | 37 | 19 | 19 | 19 |  | 94 | 95 | 94 | 94 | 94 | 28 | 18 | 837600
| Anwara 300 MW PP (United) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 69 | 32 | 32 | 0 | 66 | 68 | 69 | 70 | 70 | 70 | 60 |  | 270 | 175 | 175 | 175 | 225 | 230 | 230 | 2338473
| Juldah unit-2 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 251520
| Anlima Energy Ltd. | 19 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 7 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 612218
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 27 |  | 35 | 17 | 20 | 21 | 17 | 17 | 17 | 473760
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 5 | 18 | 30 | 34 | 10 | 14 | 36 | 31 | 23 | 16 | 6 | 0 | [8 empty] | 186433
| Chandpur 115(Doreen) | [25 empty] | 0 | 0
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 433080
| Mirsharai 150 MW (Oil) | 53 | 17 | 17 | 5 | 0 | [12 empty] | 5 |  | 87 | 87 | 35 | 35 | 35 | 35 | 53 | 404800
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 12 | 6 | 9 | 11 | 5 | 5 | 6 | 2 | 2 | 4 | 1 | 3 | 7 | 6 | 6 | 6 | 4 | 0 |  | 1 | 3 | 0 | 0 | 1 | 0 | 0 | 107040
Matarbari 2*600 MW (CPGCL)
120 | Eastern Zone Total | 7475 | 7413 | 7249 | 7167 | 7001 | 6709 | 6478 | 6278 | 6172 | 6292 | 6418 | 6741 | 7182 | 7018 | 7147 | 6872 | 6786 | 6669 |  | 8197 | 8389 | 8347 | 8428 | 8432 | 8326 | 7915 | 174110376
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 65 | 65 | 65 | 65 | 22 | 0 | [6 empty] | 21 | 32 | 32 | 46 | 16 | 16 |  | 47 | 47 | 47 | 49 | 68 | 69 | 70 | 805440
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL) | 120 | 122 | 122 | 121 | 121 | 121 | 121 | 122 | 121 | 0 | [15 empty] | 0 | 1099567
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 11 | 11 | 11 | 0 | [15 empty] | 41 | 35 | 34 | 40 | 37 | 37 | 22 | 229440
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 72 | 72 | 72 | 72 | 72 | 35 | 35 | 17 | 0 |  |  |  | 10 | 35 | 35 | 43 | 17 | 35 |  | 53 | 72 | 72 | 72 | 72 | 72 | 72 | 1106880
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 1 | 15 | 44 | 59 | 11 | 36 | 33 | 17 | 8 | 14 | 18 | 10 | 1 | [8 empty] | 277920
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 0 | [7 empty] | 3 | 17 | 17 | 17 | 17 |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 992400
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 180 | 180 | 180 | 180 | 183 | 182 | 184 | 184 | 222 | 223 | 220 | 220 | 40 | 0 | [5 empty] | 10 | 10 | 50 | 50 | 3337718
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 48 | 48 | 48 | 16 | 0 | [14 empty] | 64 | 64 | 64 | 64 | 64 | 64 | 110 | 588768
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 126 | 130 | 122 | 122 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 72 | 80 | 80 | 80 | 130 | 128 |  | 128 | 128 | 130 | 130 | 130 | 130 | 130 | 2883000
140 | Bhola 33 MW PP (Venture) | 30 | 29 | 28 | 26 | 26 | 22 | 18 | 18 | 19 | 19 | 17 | 21 | 22 | 22 | 23 | 20 | 18 | 21 |  | 28 | 28 | 29 | 29 | 32 | 32 | 32 | 579184
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | 0 | [15 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 108750
143 | Gopalganj 100 MW Peaking PP | 36 | 0 | [17 empty] | 33 | 36 | 36 | 37 | 37 | 37 | 37 | 254848
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 67 | 67 | 67 | 0 | [15 empty] | 67 | 67 | 67 | 67 | 67 | 67 | 85 | 629424
146 | Bheramara HVDC | 924 | 876 | 923 | 924 | 923 | 925 | 924 | 923 | 924 | 924 | 924 | 924 | 924 | 924 | 924 | 925 | 923 | 923 |  | 801 | 801 | 801 | 800 | 800 | 820 | 820 | 21588363
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 1244 | 1244 | 1244 | 1244 | 1244 | 1200 | 1000 | 940 | 940 | 940 | 960 | 1120 | 1244 | 1160 | 1170 | 1200 | 1140 | 1030 |  | 1160 | 1160 | 1180 | 1244 | 1244 | 1244 | 1244 | 29693100
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4381700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 37 | 37 | 37 | 37 | 37 | 37 | 0 | 200786
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 4 | 2 | 0 | 0 | [8 empty] | 16860
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 201 | 200 | 202 | 201 | 203 | 204 | 170 | 170 | 170 | 170 | 170 | 198 | 180 | 160 | 160 | 160 | 160 | 160 |  | 180 | 180 | 180 | 189 | 205 | 205 | 205 | 4709345
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 176 | 177 | 177 | 177 | 180 | 150 | 150 | 140 | 130 | 130 | 166 | 205 | 200 | 170 | 140 | 140 | 140 | 140 |  | 176 | 215 | 210 | 211 | 212 | 209 | 206 | 4455664
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 370 | 370 | 370 | 300 | 300 | 270 | 240 | 240 | 240 | 240 | 240 | 350 | 300 | 414 | 370 | 370 | 370 |  | 370 | 370 | 370 | 414 | 414 | 414 | 414 | 8382872
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [19 empty] | 5 | 5 | 0 |  |  |  |  | 7318
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 193806
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern) | 8 | 8 | 8 | 0 | [15 empty] | 34 | 16 | 8 | 8 | 8 | 8 | 34 | 105017
167 | Katakhali 50 MW Peaking PP | [19 empty] | 39 | 40 | 40 | 40 | 40 | 40 | 22 | 205284
168 | Santahar 50 MW Peaking PP | [19 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 106607
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 0 | [15 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 76267
170 | Chapainawabganj 100 MW Peaking PP | 25 | 0 | [17 empty] | 92 | 93 | 93 | 93 | 93 | 57 | 57 | 481936
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 0 | [16 empty] | 35 | 70 | 70 | 35 | 35 | 37 | 50 | 370560
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 0 | [16 empty] | 50 | 35 | 35 | 35 | 35 | 60 | 113 | 383808
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 10 | 0 |  | 10 | 33 | 35 | 34 | 34 | 34 | 32 |  | 83 | 77 | 84 | 86 | 86 | 56 | 34 | 948326
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 6 | 6 | 6 | 4 | 3 | 1 | 0 | [8 empty] | 43476
178 | Energypac Power Venture Thakurgaon Ltd. | [19 empty] | 72 | 72 | 75 | 75 | 95 | 95 | 95 | 494016
| Intraco Solar 30 MW | [5 empty] | 0 | 6 | 16 | 24 | 17 | 22 | 31 | 25 | 31 | 26 | 15 | 6 | 0 | [8 empty] | 234668
| Adani Power Jharkhanda Ltd | 1413 | 1412 | 1346 | 1359 | 1370 | 1283 | 1261 | 1260 | 1270 | 1269 | 1262 | 1254 | 1260 | 1250 | 1258 | 1266 | 1263 | 1219 |  | 1315 | 1324 | 1360 | 1362 | 1350 | 1372 | 1411 | 31478182
178 | Teesta Solar Limited | [5 empty] | 1 | 36 | 90 | 129 | 145 | 206 | 132 | 151 | 178 | 136 | 91 | 34 | 1 | [8 empty] | 131855