## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-09-22 | Friday
|  | Date (day): | 2023-09-22 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14345.6 | MW |  |  | (b) At Evening Peak Hour : |  | 16072 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-09-21 | 2023-09-22 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 170 | 130 | 160 | 160
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  |  | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 52 | 51 | 78 | 85 | 23 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 398 | 360 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 323 | 285 | 330 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 72 | 72 | 28 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 306 | 275 | 300 | 300 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 85 | 85 |  | 17 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 15 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 55 | 55 | 20 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 18 | 18 | 19 | 19
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 8 | 92 | 92 |  | 8 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 317 | 280 | 200 | 200 |  |  | ST Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 32 | 25 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 25 | 17 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 82 | 16 | 135
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 35 | 35 | 38 | 38 |  | 42 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 23 | 30 | 31 | 31 |  | 2 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 25 | 8 | 25 | 27 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 32 | 145 | 145 | 155 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
33 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
34 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 107 | 100 | 108 | 100 | 49
35 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 70 | 35 | 105
36 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 54 | 72 | 32 |  | Fuel shortage
37 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 54 | 54 | 108 | 54 |  | Fuel shortage
38 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 0 | 0 | 35 | 0
39 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 34 | 54 | 17 | 54
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 6063 | 5722 | 2487 | 2521 | 3031 | 3368 | 823 | 837
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 105 | 105 | 75 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
41 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 17 | 8 | 17 | 8 |  | Fuel shortage
42 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 19 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 10 | 42 | 6 | 50
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 157 | 157 | 200 | 200
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 217 | 222 | 225 | 225
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 21 | 34 | 51 | 51 | 54 |  | Fuel shortage
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 40 | 70 | 28 |  | Fuel shortage
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 | 102 |  | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 12 | 35 | 50 | 50 |  | Fuel shortage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 50 | 25 | 50 | 50 |  | Fuel shortage
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 11 | 9 | 11 | 11 | 11 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 7 | 29 | 41 | 25
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 85 | 120 | 285 |  | 15 | Engine problem
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 17 | 17 | 54
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 110 | 55 | 55 | 55 | 55 |  | Fuel shortage
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 50 | 25 | 50 | 50 |  | Fuel shortage
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 3 | 17 | 34 | 51 | 65 |  | Fuel shortage
60 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 0 | 54 | 160
| SS Power I |  | Coal | SS Power | 0 | 0 | 0 | 570 | 612 | 600 | 600 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 12 | 7 | 10 | 20 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 2605 | 2545 | 1254 | 1515 | 1687 | 2129 | 656 | 345
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 205 | 179 | 200 | 200 | 21 |  | Gas shortage
62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 335 | 280 | 330 | 330 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 335 | 275 | 330 | 330 |  |  | FGMO
64 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 43 | 50 | 50 | 50
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 108 | 147 | 140 | 140 | 55 |  | Gas shortae
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 10 | 50 |  |  | Gas shortage
69 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 5 | 6 | 50 | 145 |  | 5 | Engine problem
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 15 | 25 |  | 27 | Machine problem
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
72 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 68 | 100 | 68 | 100 | 100 |  | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 10 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 142 | 142 | 149 | 165
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 25 | 52
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 17 | 105 | 105 |  | 9 | Engine problem
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 36 | 95 | 26 | 78 | 35 |  | Fuel shortage
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 35 | 17 | 34 |  | 20 | Engine problem
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 0 | 0
| Cumilla Area Total |  |  |  |  | 2959 | 2896 | 1433 | 1502 | 1588 | 1877 | 211 | 641
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 28 | 32 | 30 | 50 | 152 |  | Gas shortage
83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 18 | 19 | 19 |  | 3 | Engine problem
84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 65 | 115 | 142 | 58 |  | Fuel shortage
87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 56 | 97 | 37 | 104 | 11 |  | Fuel shortage
88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 30 | 0 | 50 | 0
89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 18 | 14 | 18 | 4 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 207 | 230 | 266.6 | 333 | 152 | 3
90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 30 | 40 | 40 |  | 50 | Machine problem
92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 112 | 112 |  | 51 | ST Under maint.
93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 45 | 47 | 50 | 50
95 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 43 | 43 | 40 | 40 |  | 10 | Engine problem
96 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 66 |  | Gas shortage
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 75 | 81 | 85 | 86
99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 185 | 184 | 185 | 185 |  | 46 | Machine problem
101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 16 | 17 | 17 | 17
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 0 | 8 | 8 | 17 |  | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 270 | 300 | 300 |  |  | FGMO
104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 398 | 401 | 400 | 400 |  |  | FGMO
105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 385 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1672 | 1649 | 1701 | 1702 | 83 | 614
107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 905 | 776 | 938 | 938
108 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 10 | 16 | 32 | 66 | 49 |  | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 40 |  | 14 | Engine problem
110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 120 | 120 | 110 |  | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 | 69 |  | Fuel shortage
112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
113 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 0 | 16
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
114 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 5 | 17 | 54 | 72 | 33 |  | Fuel shortage
115 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 0 | 0 | 105 |  | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 11 | 0 | 100 | 0
117 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
118 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 520 | 571 | 520 | 565
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3125 | 3121 | 1451 | 1403 | 1789 | 1857 | 1012 | 14
119 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 16 | 110
120 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 19 | 28 | 23 | 25 |  | 15 | Engine problem
121 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 130 | 124 | 130 | 130 |  | 64 | ST under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
122 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1020 | 1244 | 1244 | 1244
123 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 109 | 109 | 110 | 110 |  | 110 | GT-1 under maint
124 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 35 | 150
125 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 | 307 |  | Coal shortage
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1278 | 1538 | 1558 | 1769 | 307 | 189
126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 30 | 22 |  | Fuel shortage
128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 20 |  | 51 | Engine problem
129 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 28 | 28
130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 34 | 42 | 8 |  | Fuel shortage
131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 40 | 10 |  | Fuel shortage
132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 140 | 202 | 180 | 200 | 10 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 211 | 170 | 200 | 20 |  | Gas shortage
135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 300 | 414 | 380 | 414
136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 24 | 32 | 18 |  | Fuel shortage
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 8 | 44 |  | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 50 | 91 | 13 |  | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 35 | 70 | 43 |  | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 55 | 75 | 38 |  | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1101 | 1311 | 1300 | 1400
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 1692 | 2213 | 2300 | 2658 | 817 | 54
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 180 | 180 | 180 | 180 |  | 94 | Machine problem
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 75 | 42 | 84 | 29 |  | Fuel shortage
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 35 | 35 | 115
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 1 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 40 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 222 | 290 | 425 | 379 | 154 | 179
| Total |  |  |  |  | 24911 | 24171 | 11696 | 12861 | 14345.6 | 16072 | 4215 | 2876
A. |  | 2023-09-21 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 12861 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 10455 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12861 | MW
3 | Day peak Generation : |  |  | 11696 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12340.75 | MW
4 | Evening peak Generation : |  |  | 12861 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 280.9538 | MKWHr | By Solar | 1.1866 | MKWHr
| By Gas : | 142.3727 | MKWHr |  | By Oil: | 22.1257 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 86.3869 | MKWHr |  | By Hydro: | 4.1072 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.30048 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4215 | MW | Dhaka | 4705.35 | 4705.35 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2876 | MW | Chittagong | 1262.5 | 1262.5 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 7091 | MW | Khulna | 1484.5 | 1484.5 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 1066.13 | MMCFD |  |  | Rajshahi | 1218.4 | 1218.4 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 160758088.838 | ii) Oil : | Taka | 287650723.19 | Comilla | 1170 | 1170 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 622289828.55 | Total | Taka | 1070698640.578 | Mymensingh | 905 | 905 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 511 | 511 |  | 0 |  | 23:00 |  | 114.6
| ii) During Peak Demand : |  |  | 1110 | MW (E to W) at | 19:30 | hrs | Barisal | 408 | 408 |  | 0 |  | 24:00 |  | 94.545
| iii) Maximum : |  |  | 920 | MW at | 22:00 | hrs | Rangpur | 676 | 676 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 32.8°C |  |  | Total | 12340.75 | 12340.75 |  | 0
B. |  | 2023-09-22 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 32.8°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 13000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 16072 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 11000 | MW
4 | Reserve(Generation end) |  |  |  | 3072 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 283.9903 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9824 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.1113 | MKWHr. | ii) HVDC Flow at Peak Time |  | 776 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.3629 | MKWHr. | iii) Maximum HVDC Flow : |  | 906 | MW at | 4:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 108.61 |  | (b) Today: | 108.5 |  | (c) Rule Curve: |  | 103.84
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-09-21 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 160 | 0 | 0 | 52 | 0 | 394 | 337 |  | 0 | 450 | 290 | 0 | 0 | 15 | 59 | 0 | 0 | 0 | 40 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 18 | 25 | 30 | 8 | 0 | 128 | 75 | 103 | 0 | 8 | 225 | 0 | 0 | 0 |  | 12 | 0 | 0 | 12 | 0 | 40 | 11 | 38 | 0 | 0 | 0 | 310 | 275 | 211 | 137 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 25 | 18 | 8 | 33 | 12 | 152 | 72 | 0 | 19 | 0 | 43 | 40 | 45 | 44 | 80 | 0 | 0 | 81 | 0 | 185 | 17 | 0 | 10 | 280 | 8 | 8 | 0 | 15 | 0 | 0 | 68 | 0 | 85 | 0 | 12 | 34 | 6 | 368 | 19 | 17 | 51 | 0 | 70 | 17 | 55 | 105 | 9 | 12 | 400 | 0 | 0 | 17 | 17 | 0 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 612 | 11 | 0 | 0 | 0 |  | 905 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 350 | 54 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1200 | 109 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 516 | 0 | 0 | 1256 | 0 | 0 |  | 6865 | 5125 | 11990 | 3580 | 905 | 2382 | 0 | 961 | 3764 | 203 | 0 | 32 | 152 | 0 | 11 | 143.25 | 108.63
2:00 | 0 | 0 | 160 | 0 | 0 | 52 | 0 | 394 | 337 |  | 0 | 450 | 276 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 18 | 25 | 30 | 0 | 0 | 128 | 75 | 101 | 0 | 0 | 223 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 9 | 11 | 38 | 0 | 0 | 0 | 310 | 275 | 212 | 137 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 25 | 18 | 8 | 33 | 12 | 148 | 72 | 0 | 19 | 0 | 43 | 40 | 45 | 44 | 80 | 0 | 0 | 81 | 0 | 184 | 17 | 0 | 10 | 290 | 8 | 8 | 0 | 0 | 0 | 0 | 68 | 0 | 17 | 0 | 12 | 34 | 0 | 368 | 19 | 17 | 51 | 0 | 68 | 17 | 61 | 105 | 9 | 12 | 400 | 0 | 0 | 0 | 17 | 0 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 612 | 10 | 0 | 0 | 0 |  | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 350 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1200 | 109 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 522 | 0 | 0 | 1262 | 0 | 0 |  | 6599 | 5042 | 11641 | 3549 | 905 | 2378 | 0 | 656 | 3776 | 203 | 0 | 16 | 148 | 0 | 10 | 142.295 | 108.63
3:00 | 0 | 0 | 160 | 0 | 0 | 52 | 0 | 394 | 337 |  | 0 | 450 | 277 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 18 | 25 | 30 | 0 | 0 | 128 | 75 | 105 | 0 | 0 | 224 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 6 | 9 | 38 | 0 | 0 | 0 | 310 | 275 | 211 | 137 | 0 | 50 | 0 | 0 | 10 | 0 | 0 | 25 | 18 | 8 | 33 | 12 | 144 | 72 | 0 | 19 | 0 | 43 | 40 | 45 | 44 | 80 | 0 | 0 | 81 | 0 | 184 | 17 | 0 | 10 | 290 | 8 | 11 | 0 | 0 | 0 | 0 | 68 | 0 | 17 | 0 | 12 | 34 | 0 | 367 | 19 | 17 | 51 | 0 | 68 | 0 | 55 | 105 | 9 | 0 | 400 | 0 | 0 | 0 | 17 | 0 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 612 | 13 | 0 | 0 | 0 |  | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1040 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 524 | 0 | 0 | 1258 | 0 | 0 |  | 6527 | 4769 | 11296 | 3499 | 905 | 2335 | 0 | 567 | 3614 | 203 | 0 | 16 | 144 | 0 | 13 | 147.07 | 108.62
4:00 | 0 | 0 | 130 | 0 | 0 | 52 | 0 | 362 | 302 |  | 0 | 400 | 266 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 18 | 25 | 30 | 0 | 0 | 128 | 75 | 107 | 0 | 0 | 226 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 6 | 9 | 38 | 0 | 0 | 0 | 280 | 270 | 211 | 108 | 0 | 50 | 0 | 0 | 10 | 0 | 0 | 25 | 18 | 8 | 33 | 12 | 142 | 72 | 0 | 19 | 0 | 43 | 40 | 45 | 44 | 80 | 0 | 0 | 81 | 0 | 186 | 17 | 0 | 10 | 300 | 8 | 11 | 0 | 0 | 0 | 0 | 68 | 0 | 17 | 0 | 12 | 34 | 0 | 367 | 19 | 0 | 51 | 0 | 69 | 0 | 55 | 105 | 9 | 0 | 365 | 0 | 0 | 0 | 17 | 0 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 612 | 12 | 0 | 0 | 0 |  | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1030 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 522 | 0 | 0 | 1263 | 0 | 0 |  | 6476 | 4763 | 11239 | 3582 | 906 | 2220 | 0 | 551 | 3607 | 203 | 0 | 16 | 142 | 0 | 12 | 134.655 | 108.62
5:00 | 0 | 0 | 130 | 0 | 0 | 52 | 0 | 350 | 303 |  | 0 | 370 | 268 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 18 | 25 | 30 | 0 | 0 | 128 | 75 | 105 | 0 | 0 | 226 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 6 | 9 | 39 | 0 | 0 | 0 | 280 | 275 | 211 | 108 | 0 | 50 | 0 | 0 | 10 | 0 | 0 | 25 | 18 | 8 | 33 | 12 | 140 | 72 | 0 | 19 | 0 | 43 | 40 | 45 | 44 | 80 | 0 | 0 | 81 | 0 | 184 | 17 | 0 | 10 | 275 | 8 | 11 | 0 | 0 | 0 | 0 | 68 | 0 | 17 | 0 | 12 | 34 | 0 | 320 | 19 | 0 | 17 | 0 | 15 | 0 | 55 | 105 | 9 | 0 | 365 | 0 | 0 | 0 | 17 | 0 | 20 | 0 | 0 | 17 | 0 | 0 | 0 | 612 | 15 | 0 | 0 | 0 |  | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1010 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 525 | 0 | 0 | 1210 | 0 | 0 |  | 6346 | 4642 | 10988 | 3605 | 906 | 2118 | 0 | 448 | 3537 | 203 | 0 | 16 | 140 | 0 | 15 | 106.96 | 108.62
6:00 | 0 | 0 | 130 | 0 | 0 | 52 | 0 | 345 | 272 |  | 0 | 370 | 278 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 19 | 25 | 30 | 0 | 0 | 128 | 75 | 101 | 0 | 0 | 224 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 6 | 9 | 38 | 0 | 0 | 0 | 280 | 275 | 210 | 108 | 0 | 47 | 0 | 0 | 10 | 0 | 0 | 25 | 18 | 8 | 33 | 12 | 130 | 72 | 0 | 19 | 0 | 43 | 40 | 45 | 44 | 80 | 0 | 0 | 81 | 0 | 184 | 17 | 0 | 10 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 68 | 0 | 17 | 0 | 12 | 34 | 0 | 320 | 19 | 0 | 17 | 0 | 15 | 0 | 55 | 34 | 9 | 0 | 365 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 580 | 13 | 0 | 0 | 0 |  | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 960 | 109 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 526 | 0 | 0 | 1124 | 0 | 0 |  | 6148 | 4505 | 10653 | 3532 | 905 | 2109 | 0 | 374 | 3370 | 203 | 0 | 16 | 130 | 1 | 13 | 111.735 | 108.61
7:00 | 0 | 0 | 130 | 0 | 0 | 52 | 0 | 301 | 273 |  | 0 | 370 | 285 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 19 | 25 | 30 | 0 | 0 | 128 | 75 | 106 | 0 | 0 | 223 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 6 | 9 | 36 | 0 | 0 | 0 | 290 | 330 | 210 | 108 | 0 | 47 | 0 | 0 | 10 | 0 | 0 | 25 | 18 | 8 | 33 | 12 | 118 | 29 | 0 | 16 | 0 | 43 | 40 | 45 | 44 | 80 | 0 | 0 | 81 | 0 | 184 | 17 | 0 | 9 | 310 | 0 | 11 | 0 | 0 | 0 | 0 | 68 | 0 | 17 | 2 | 0 | 29 | 0 | 320 | 19 | 0 | 0 | 1 | 0 | 0 | 78 | 17 | 8 | 0 | 365 | 0 | 1 | 0 | 0 | 0 | 17 | 5 | 0 | 17 | 0 | 0 | 0 | 500 | 8 | 0 | 0 | 0 |  | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 109 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 525 | 0 | 0 | 1110 | 2 | 0 |  | 6003 | 4452 | 10455 | 3511 | 900 | 2134 | 0 | 313 | 3215 | 203 | 0 | 16 | 118 | 37 | 8 | 109.825 | 108.59
8:00 | 0 | 0 | 130 | 0 | 0 | 52 | 0 | 301 | 272 |  | 0 | 370 | 290 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 19 | 25 | 30 | 0 | 0 | 128 | 75 | 103 | 0 | 0 | 223 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 6 | 0 | 7 | 0 | 0 | 0 | 335 | 335 | 210 | 108 | 0 | 47 | 0 | 0 | 10 | 0 | 0 | 25 | 18 | 8 | 33 | 12 | 116 | 29 | 0 | 16 | 0 | 43 | 40 | 45 | 44 | 80 | 0 | 0 | 81 | 0 | 184 | 17 | 0 | 10 | 300 | 0 | 11 | 0 | 0 | 0 | 0 | 68 | 0 | 20 | 4 | 0 | 17 | 0 | 320 | 19 | 0 | 0 | 2 | 0 | 0 | 110 | 17 | 9 | 0 | 365 | 0 | 5 | 0 | 0 | 0 | 17 | 16 | 0 | 17 | 0 | 0 | 0 | 500 | 7 | 0 | 0 | 0 |  | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 900 | 109 | 0 | 0 | 3 | 26 | 0 | 0 | 0 | 524 | 3 | 0 | 1108 | 23 | 0 |  | 6046 | 4480 | 10526 | 3549 | 905 | 2098 | 0 | 337 | 3212 | 203 | 0 | 16 | 116 | 83 | 7 | 108.87 | 108.57
9:00 | 0 | 0 | 130 | 0 | 0 | 52 | 0 | 380 | 330 |  | 0 | 400 | 278 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 18 | 19 | 19 | 25 | 23 | 6 | 0 | 82 | 75 | 108 | 0 | 0 | 223 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 6 | 9 | 5 | 0 | 0 | 0 | 310 | 310 | 213 | 108 | 0 | 47 | 0 | 0 | 24 | 0 | 0 | 25 | 18 | 8 | 33 | 12 | 124 | 30 | 0 | 16 | 1 | 43 | 40 | 45 | 44 | 112 | 0 | 0 | 81 | 0 | 184 | 17 | 0 | 9 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 68 | 0 | 82 | 9 | 0 | 21 | 1 | 368 | 19 | 1 | 0 | 3 | 0 | 0 | 110 | 17 | 9 | 0 | 400 | 2 | 15 | 17 | 0 | 0 | 8 | 21 | 0 | 17 | 0 | 0 | 0 | 502 | 18 | 0 | 0 | 0 |  | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 940 | 109 | 0 | 0 | 3 | 36 | 0 | 0 | 0 | 525 | 3 | 0 | 1101 | 4 | 0 |  | 6441 | 4543 | 10984 | 3713 | 905 | 2255 | 0 | 452 | 3248 | 157 | 0 | 16 | 124 | 96 | 18 | 139.43 | 108.55
10:00 | 0 | 0 | 130 | 0 | 0 | 52 | 0 | 398 | 330 |  | 0 | 400 | 298 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 18 | 19 | 17 | 25 | 23 | 8 | 0 | 82 | 75 | 110 | 0 | 0 | 220 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 6 | 11 | 6 | 0 | 0 | 0 | 275 | 280 | 210 | 108 | 0 | 47 | 0 | 0 | 43 | 0 | 0 | 25 | 18 | 8 | 33 | 12 | 136 | 28 | 0 | 16 | 2 | 43 | 40 | 45 | 44 | 80 | 0 | 0 | 81 | 0 | 187 | 17 | 0 | 9 | 270 | 0 | 11 | 0 | 0 | 0 | 0 | 68 | 0 | 107 | 0 | 0 | 68 | 3 | 368 | 19 | 52 | 5 | 4 | 0 | 0 | 110 | 17 | 15 | 0 | 400 | 14 | 16 | 17 | 0 | 0 | 0 | 18 | 0 | 32 | 0 | 0 | 0 | 500 | 18 | 0 | 0 | 0 |  | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 940 | 109 | 0 | 0 | 2 | 75 | 0 | 0 | 0 | 521 | 6 | 0 | 1091 | 90 | 0 |  | 6584 | 4665 | 11249 | 3670 | 905 | 2243 | 0 | 627 | 3232 | 157 | 0 | 48 | 136 | 213 | 18 | 39 | 108.54
11:00 | 0 | 0 | 130 | 0 | 0 | 52 | 0 | 396 | 330 |  | 0 | 400 | 314 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 18 | 19 | 16 | 25 | 23 | 8 | 0 | 82 | 75 | 111 | 0 | 0 | 218 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 6 | 11 | 6 | 0 | 0 | 0 | 325 | 310 | 205 | 108 | 0 | 47 | 0 | 0 | 51 | 0 | 0 | 16 | 18 | 8 | 25 | 12 | 136 | 28 | 0 | 16 | 1 | 43 | 40 | 45 | 43 | 80 | 0 | 0 | 75 | 0 | 185 | 17 | 0 | 9 | 300 | 0 | 11 | 0 | 0 | 0 | 0 | 58 | 0 | 107 | 0 | 0 | 68 | 6 | 400 | 56 | 52 | 17 | 5 | 0 | 0 | 110 | 17 | 36 | 0 | 390 | 17 | 31 | 17 | 0 | 0 | 12 | 21 | 0 | 34 | 0 | 0 | 0 | 532 | 16 | 0 | 0 | 0 |  | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 960 | 109 | 0 | 0 | 5 | 22 | 0 | 0 | 0 | 523 | 1 | 0 | 1104 | 42 | 0 |  | 6827 | 4602 | 11429 | 3746 | 906 | 2293 | 0 | 715 | 3299 | 157 | 0 | 32 | 136 | 129 | 16 | 0 | 108.53
12:00 | 0 | 0 | 170 | 0 | 0 | 52 | 0 | 398 | 323 |  | 0 | 450 | 306 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 32 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 18 | 19 | 16 | 25 | 23 | 8 | 0 | 82 | 75 | 100 | 0 | 0 | 217 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 10 | 11 | 7 | 0 | 0 | 0 | 335 | 335 | 205 | 108 | 0 | 43 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 8 | 25 | 12 | 142 | 28 | 0 | 16 | 1 | 43 | 40 | 45 | 43 | 112 | 0 | 0 | 75 | 0 | 185 | 16 | 0 | 9 | 310 | 0 | 11 | 0 | 0 | 0 | 0 | 58 | 0 | 107 | 19 | 0 | 68 | 5 | 398 | 56 | 52 | 21 | 2 | 15 | 0 | 110 | 17 | 36 | 0 | 385 | 17 | 30 | 35 | 3 | 0 | 17 | 0 | 0 | 34 | 0 | 0 | 0 | 570 | 12 | 0 | 0 | 0 |  | 905 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 300 | 5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1020 | 109 | 0 | 0 | 3 | 11 | 0 | 0 | 0 | 520 | 1 | 0 | 1101 | 40 | 0 |  | 7053 | 4643 | 11696 | 3835 | 905 | 2319 | 0 | 811 | 3391 | 157 | 0 | 16 | 142 | 108 | 12 | 0 | 108.52
13:00 | 0 | 0 | 160 | 0 | 0 | 52 | 0 | 399 | 313 |  | 0 | 450 | 262 | 0 | 0 | 10 | 310 | 0 | 0 | 0 | 74 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 18 | 19 | 15 | 25 | 23 | 8 | 0 | 82 | 75 | 97 | 0 | 0 | 220 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 15 | 11 | 10 | 0 | 0 | 0 | 310 | 310 | 213 | 107 | 0 | 45 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 8 | 32 | 12 | 152 | 12 | 0 | 16 | 1 | 43 | 30 | 45 | 42 | 112 | 0 | 0 | 77 | 0 | 184 | 17 | 0 | 9 | 290 | 0 | 11 | 0 | 42 | 0 | 0 | 58 | 0 | 106 | 11 | 0 | 68 | 28 | 368 | 59 | 52 | 51 | 3 | 60 | 0 | 110 | 17 | 38 | 0 | 365 | 34 | 46 | 54 | 17 | 0 | 17 | 18 | 0 | 34 | 0 | 0 | 0 | 600 | 13 | 0 | 0 | 0 |  | 905 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 330 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1050 | 109 | 0 | 0 | 2 | 27 | 0 | 0 | 0 | 520 | 9 | 0 | 1106 | 135 | 0 |  | 7175 | 4835 | 12010 | 3699 | 905 | 2279 | 0 | 1080 | 3456 | 157 | 0 | 16 | 152 | 253 | 13 | 0 | 108.51
14:00 | 0 | 0 | 130 | 0 | 0 | 52 | 0 | 328 | 280 |  | 0 | 330 | 282 | 0 | 10 | 15 | 270 | 0 | 0 | 0 | 99 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 18 | 19 | 15 | 25 | 28 | 8 | 0 | 82 | 75 | 106 | 0 | 0 | 222 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 11 | 9 | 0 | 0 | 0 | 280 | 295 | 180 | 107 | 0 | 46 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 8 | 33 | 12 | 142 | 16 | 0 | 18 | 2 | 43 | 30 | 47 | 42 | 80 | 0 | 0 | 77 | 0 | 183 | 17 | 0 | 9 | 260 | 0 | 11 | 0 | 15 | 0 | 0 | 95 | 0 | 54 | 13 | 0 | 68 | 50 | 319 | 59 | 52 | 51 | 1 | 60 | 0 | 110 | 17 | 37 | 0 | 385 | 68 | 17 | 54 | 17 | 0 | 6 | 0 | 0 | 34 | 0 | 0 | 0 | 544 | 25 | 0 | 0 | 0 |  | 906 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 330 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1050 | 109 | 0 | 0 | 3 | 11 | 0 | 0 | 0 | 520 | 16 | 0 | 1120 | 134 | 0 |  | 6715 | 4841 | 11556 | 3474 | 906 | 2085 | 0 | 1107 | 3414 | 157 | 0 | 48 | 142 | 198 | 25 | 0 | 108.53
15:00 | 0 | 0 | 130 | 0 | 0 | 52 | 0 | 321 | 255 |  | 0 | 330 | 314 | 0 | 17 | 15 | 240 | 0 | 0 | 0 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 16 | 19 | 15 | 25 | 28 | 8 | 0 | 81 | 75 | 100 | 0 | 0 | 222 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 11 | 6 | 0 | 0 | 0 | 280 | 275 | 208 | 107 | 0 | 46 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 33 | 12 | 130 | 16 | 0 | 18 | 2 | 40 | 30 | 22 | 42 | 80 | 0 | 0 | 77 | 0 | 183 | 17 | 0 | 9 | 280 | 0 | 11 | 0 | 15 | 0 | 0 | 95 | 0 | 17 | 5 | 0 | 17 | 53 | 316 | 59 | 35 | 51 | 1 | 30 | 0 | 110 | 0 | 38 | 0 | 397 | 35 | 41 | 17 | 17 | 0 | 0 | 2 | 0 | 34 | 0 | 0 | 0 | 450 | 13 | 0 | 0 | 0 |  | 905 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 280 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 900 | 109 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 523 | 6 | 0 | 1113 | 11 | 0 |  | 6241 | 4459 | 10700 | 3387 | 905 | 2034 | 0 | 774 | 3166 | 156 | 0 | 48 | 130 | 87 | 13 | 0 | 108.51
16:00 | 0 | 0 | 130 | 0 | 0 | 52 | 0 | 321 | 277 |  | 0 | 330 | 304 | 0 | 17 | 15 | 240 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 15 | 0 | 28 | 8 | 0 | 82 | 75 | 100 | 0 | 0 | 222 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 11 | 10 | 0 | 0 | 0 | 290 | 285 | 210 | 108 | 0 | 47 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 0 | 25 | 12 | 142 | 17 | 0 | 18 | 0 | 41 | 30 | 42 | 43 | 112 | 0 | 0 | 80 | 0 | 184 | 17 | 0 | 9 | 300 | 0 | 11 | 0 | 15 | 0 | 0 | 27 | 0 | 17 | 5 | 0 | 18 | 56 | 325 | 68 | 35 | 34 | 0 | 30 | 0 | 108 | 0 | 39 | 0 | 394 | 25 | 12 | 17 | 17 | 0 | 9 | 2 | 0 | 34 | 0 | 0 | 0 | 510 | 6 | 0 | 0 | 0 |  | 906 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 320 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 900 | 109 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 522 | 0 | 0 | 1115 | 3 | 0 |  | 6260 | 4485 | 10745 | 3378 | 906 | 2165 | 0 | 683 | 3227 | 157 | 0 | 48 | 142 | 33 | 6 | 0 | 108.51
17:00 | 0 | 0 | 130 | 0 | 0 | 52 | 0 | 321 | 277 |  | 0 | 330 | 275 | 0 | 17 | 15 | 240 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 15 | 25 | 30 | 8 | 0 | 82 | 75 | 100 | 0 | 0 | 223 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 11 | 19 | 0 | 0 | 0 | 280 | 280 | 180 | 108 | 0 | 48 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 25 | 12 | 132 | 20 | 0 | 18 | 0 | 43 | 30 | 49 | 43 | 112 | 0 | 0 | 81 | 0 | 184 | 17 | 0 | 10 | 290 | 0 | 11 | 0 | 15 | 0 | 0 | 19 | 0 | 17 | 2 | 0 | 51 | 58 | 320 | 68 | 35 | 34 | 0 | 30 | 0 | 64 | 0 | 38 | 0 | 400 | 17 | 0 | 17 | 17 | 0 | 17 | 1 | 0 | 34 | 0 | 0 | 0 | 541 | 2 | 0 | 0 | 0 |  | 905 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 320 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 900 | 109 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 522 | 1 | 0 | 1110 | 10 | 0 |  | 6238 | 4486 | 10724 | 3378 | 905 | 2146 | 0 | 665 | 3253 | 157 | 0 | 64 | 132 | 22 | 2 | 0 | 108.52
18:00 | 0 | 0 | 130 | 0 | 0 | 51 | 0 | 322 | 320 |  | 0 | 450 | 308 | 0 | 17 | 15 | 240 | 0 | 0 | 5 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 12 | 17 | 19 | 15 | 25 | 30 | 8 | 0 | 82 | 75 | 105 | 0 | 0 | 224 | 0 | 0 | 0 |  | 18 | 0 | 0 | 12 | 0 | 0 | 9 | 10 | 0 | 0 | 0 | 280 | 280 | 186 | 108 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 4 | 18 | 10 | 32 | 12 | 146 | 20 | 0 | 18 | 0 | 43 | 30 | 47 | 43 | 80 | 0 | 0 | 81 | 0 | 184 | 17 | 0 | 10 | 290 | 0 | 11 | 0 | 15 | 0 | 0 | 28 | 0 | 24 | 0 | 12 | 60 | 6 | 364 | 55 | 35 | 34 | 0 | 60 | 12 | 55 | 17 | 76 | 12 | 400 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 0 | 54 | 0 | 0 | 0 | 580 | 9 | 0 | 0 | 0 |  | 905 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 80 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 320 | 17 | 0 | 0 | 15 | 32 | 0 | 0 | 0 | 940 | 109 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 568 | 0 | 0 | 1241 | 0 | 0 |  | 6653 | 4762 | 11415 | 3461 | 905 | 2302 | 0 | 857 | 3509 | 157 | 0 | 69 | 146 | 0 | 9 | 0 | 108.52
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 130 | 0 | 0 | 51 | 0 | 386 | 280 |  | 0 | 450 | 265 | 0 | 13 | 0 | 280 | 0 | 0 | 8 | 25 | 98 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 18 | 19 | 15 | 25 | 30 | 25 | 0 | 82 | 75 | 103 | 0 | 10 | 226 | 0 | 0 | 0 |  | 18 | 0 | 0 | 12 | 0 | 17 | 9 | 29 | 0 | 0 | 0 | 280 | 275 | 180 | 147 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 45 | 18 | 10 | 33 | 12 | 144 | 30 | 0 | 19 | 0 | 43 | 30 | 47 | 43 | 112 | 0 | 0 | 81 | 0 | 185 | 17 | 0 | 10 | 270 | 0 | 11 | 0 | 28 | 0 | 0 | 65 | 0 | 100 | 0 | 20 | 100 | 6 | 401 | 93 | 70 | 34 | 0 | 100 | 17 | 55 | 52 | 95 | 45 | 400 | 17 | 0 | 38 | 17 | 0 | 20 | 0 | 0 | 54 | 0 | 0 | 0 | 612 | 17 | 0 | 0 | 0 |  | 892 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 124 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 414 | 17 | 0 | 18 | 15 | 60 | 0 | 0 | 0 | 1200 | 109 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 573 | 0 | 0 | 1309 | 0 | 0 |  | 7388 | 5445 | 12833 | 3742 | 892 | 2386 | 0 | 1491 | 3874 | 157 | 0 | 130 | 144 | 0 | 17 | 0 | 108.53
19:30 | 0 | 0 | 130 | 0 | 0 | 51 | 0 | 360 | 285 |  | 0 | 450 | 275 | 0 | 0 | 0 | 280 | 0 | 0 | 8 | 25 | 82 | 0 | 0 | 0 | 0 | 25 | 35 | 55 | 18 | 19 | 16 | 25 | 30 | 25 | 0 | 82 | 75 | 100 | 0 | 17 | 222 | 0 | 0 | 0 |  | 18 | 0 | 0 | 12 | 0 | 42 | 9 | 29 | 0 | 0 | 0 | 280 | 275 | 179 | 147 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 142 | 32 | 0 | 18 | 0 | 43 | 30 | 47 | 43 | 112 | 0 | 0 | 81 | 0 | 184 | 17 | 0 | 10 | 270 | 0 | 11 | 0 | 32 | 0 | 0 | 65 | 0 | 100 | 0 | 50 | 100 | 6 | 401 | 97 | 70 | 34 | 0 | 85 | 17 | 55 | 17 | 95 | 50 | 400 | 17 | 0 | 54 | 17 | 0 | 35 | 0 | 0 | 54 | 0 | 0 | 0 | 612 | 7 | 0 | 0 | 0 |  | 776 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 124 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 414 | 17 | 0 | 35 | 15 | 75 | 0 | 0 | 0 | 1244 | 109 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 571 | 0 | 0 | 1311 | 0 | 0 |  | 7417 | 5444 | 12861 | 3747 | 776 | 2402 | 0 | 1598 | 3918 | 157 | 0 | 114 | 142 | 0 | 7 | 0 | 0
20:00 | 0 | 0 | 130 | 0 | 0 | 51 | 0 | 360 | 285 |  | 0 | 450 | 300 | 0 | 0 | 0 | 280 | 0 | 0 | 8 | 8 | 64 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 18 | 19 | 16 | 25 | 30 | 25 | 0 | 81 | 75 | 100 | 0 | 17 | 224 | 0 | 0 | 0 |  | 18 | 0 | 0 | 12 | 0 | 49 | 9 | 42 | 0 | 0 | 0 | 280 | 275 | 181 | 147 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 152 | 32 | 0 | 16 | 0 | 43 | 30 | 50 | 43 | 112 | 0 | 0 | 81 | 0 | 185 | 17 | 0 | 10 | 275 | 0 | 11 | 0 | 42 | 0 | 0 | 65 | 0 | 106 | 0 | 50 | 100 | 6 | 402 | 98 | 70 | 34 | 0 | 65 | 17 | 55 | 17 | 95 | 50 | 400 | 17 | 0 | 17 | 17 | 0 | 35 | 0 | 0 | 54 | 0 | 0 | 0 | 612 | 8 | 0 | 0 | 0 |  | 776 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 130 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 360 | 17 | 0 | 35 | 15 | 85 | 0 | 0 | 0 | 1244 | 109 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 571 | 0 | 0 | 1312 | 0 | 0 |  | 7438 | 5396 | 12834 | 3746 | 776 | 2394 | 0 | 1587 | 3919 | 156 | 0 | 96 | 152 | 0 | 8 | 0 | 108.53
21:00 | 0 | 0 | 130 | 0 | 0 | 51 | 0 | 361 | 287 |  | 0 | 450 | 272 | 0 | 0 | 0 | 280 | 0 | 0 | 8 | 8 | 64 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 18 | 19 | 17 | 25 | 32 | 25 | 0 | 82 | 75 | 103 | 0 | 17 | 226 | 0 | 0 | 0 |  | 18 | 0 | 0 | 12 | 0 | 50 | 9 | 42 | 0 | 0 | 0 | 280 | 275 | 180 | 147 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 152 | 0 | 0 | 16 | 0 | 43 | 30 | 50 | 43 | 112 | 0 | 0 | 81 | 0 | 184 | 17 | 0 | 10 | 270 | 0 | 11 | 0 | 45 | 0 | 0 | 65 | 0 | 107 | 0 | 50 | 104 | 6 | 368 | 99 | 70 | 34 | 0 | 65 | 17 | 55 | 17 | 95 | 50 | 400 | 17 | 0 | 17 | 17 | 0 | 35 | 0 | 0 | 54 | 0 | 0 | 0 | 612 | 13 | 0 | 0 | 0 |  | 775 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 360 | 17 | 0 | 35 | 4 | 85 | 0 | 0 | 0 | 1244 | 109 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 571 | 0 | 0 | 1317 | 0 | 0 |  | 7364 | 5334 | 12698 | 3639 | 775 | 2364 | 0 | 1578 | 3924 | 157 | 0 | 96 | 152 | 0 | 13 | 0 | 108.53
22:00 | 0 | 0 | 130 | 0 | 0 | 51 | 0 | 332 | 257 |  | 0 | 450 | 274 | 0 | 0 | 0 | 250 | 0 | 0 | 8 | 8 | 64 | 0 | 0 | 0 | 0 | 54 | 35 | 17 | 18 | 19 | 18 | 25 | 32 | 25 | 0 | 82 | 75 | 101 | 0 | 17 | 225 | 0 | 0 | 0 |  | 18 | 0 | 0 | 12 | 0 | 50 | 9 | 42 | 0 | 0 | 0 | 280 | 275 | 181 | 147 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 154 | 44 | 0 | 18 | 0 | 43 | 30 | 50 | 43 | 112 | 0 | 0 | 81 | 0 | 184 | 17 | 0 | 10 | 280 | 8 | 11 | 0 | 45 | 0 | 0 | 65 | 0 | 107 | 0 | 50 | 104 | 5 | 368 | 100 | 51 | 34 | 0 | 65 | 17 | 55 | 17 | 96 | 50 | 400 | 17 | 0 | 17 | 17 | 0 | 35 | 0 | 0 | 54 | 0 | 0 | 0 | 612 | 5 | 0 | 0 | 0 |  | 776 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 320 | 17 | 0 | 35 | 0 | 85 | 0 | 0 | 0 | 1244 | 109 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 572 | 0 | 0 | 1326 | 0 | 0 |  | 7278 | 5226 | 12504 | 3573 | 776 | 2307 | 0 | 1502 | 3934 | 157 | 0 | 96 | 154 | 0 | 5 | 0 | 108.53
23:00 | 0 | 0 | 130 | 0 | 0 | 51 | 0 | 326 | 257 |  | 0 | 450 | 301 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 18 | 19 | 18 | 25 | 32 | 25 | 0 | 82 | 75 | 104 | 0 | 8 | 225 | 0 | 0 | 0 |  | 18 | 0 | 0 | 12 | 0 | 0 | 9 | 42 | 0 | 0 | 0 | 285 | 280 | 182 | 148 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 156 | 49 | 0 | 18 | 0 | 43 | 30 | 47 | 46 | 112 | 0 | 0 | 81 | 0 | 184 | 17 | 0 | 10 | 285 | 8 | 11 | 0 | 15 | 0 | 0 | 20 | 0 | 58 | 0 | 50 | 104 | 6 | 368 | 71 | 51 | 34 | 0 | 65 | 17 | 55 | 82 | 69 | 50 | 400 | 17 | 0 | 17 | 17 | 0 | 35 | 0 | 0 | 54 | 0 | 0 | 0 | 612 | 10 | 0 | 0 | 0 |  | 802 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 320 | 18 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1244 | 109 | 0 | 17 | 0 | 0 | 36 | 0 | 0 | 572 | 0 | 0 | 1310 | 0 | 0 |  | 7066 | 5164 | 12230 | 3597 | 802 | 2341 | 0 | 1185 | 3918 | 157 | 0 | 64 | 156 | 0 | 10 | 114.6 | 108.54
24:00 | 0 | 0 | 130 | 0 | 0 | 51 | 0 | 326 | 277 |  | 0 | 450 | 304 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 18 | 19 | 18 | 25 | 32 | 8 | 0 | 82 | 75 | 104 | 0 | 0 | 224 | 0 | 0 | 0 |  | 12 | 0 | 0 | 12 | 0 | 0 | 9 | 42 | 0 | 0 | 0 | 285 | 280 | 188 | 148 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 152 | 35 | 0 | 18 | 0 | 43 | 30 | 47 | 46 | 112 | 0 | 0 | 81 | 0 | 184 | 17 | 0 | 10 | 305 | 8 | 11 | 0 | 0 | 0 | 0 | 18 | 0 | 24 | 0 | 25 | 73 | 5 | 378 | 69 | 17 | 34 | 0 | 65 | 17 | 55 | 106 | 16 | 50 | 398 | 17 | 0 | 17 | 17 | 0 | 35 | 0 | 0 | 17 | 0 | 0 | 0 | 612 | 10 | 0 | 0 | 0 |  | 802 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 320 | 35 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1244 | 109 | 0 | 17 | 0 | 0 | 37 | 0 | 0 | 571 | 0 | 0 | 1263 | 0 | 0 |  | 6844 | 5117 | 11961 | 3613 | 802 | 2382 | 0 | 943 | 3870 | 157 | 0 | 32 | 152 | 0 | 10 | 94.545 | 108.54
KWH | 0 | 0 | 3303250 | 0 | 0 | 1245136 | 0 | 8663040 | 7146000 |  | 0 | 9564500 | 6909033 | 0 | 81086 | 125774 | 6102948 | 0 | 0 | 37440 | 409968 | 882240 | 0 | 0 | 0 | 0 | 309600 | 500425 | 238019 | 392436 | 456000 | 405720 | 590500 | 679100 | 232800 | 0 | 2295212 | 1812000 | 2500000 | 0 | 87751 | 5213077 | 0 | 0 | 0 |  | 395280 | 0 | 0 | 88080 | 0 | 318240 | 218448 | 653280 | 0 | 0 | 0 | 7506100 | 7075000 | 4873000 | 2927273 | 0 | 1142208 | 0 | 0 | 979768 | 0 | 0 | 620486 | 432360 | 197640 | 747400 | 279100 | 3362880 | 851520 | 0 | 399312 | 10300 | 1014000 | 820920 | 1080000 | 1036728 | 2367327 | 0 | 0 | 1914240 | 0 | 4764500 | 410000 | 0 | 238320 | 7048000 | 73056 | 257856 | 0 | 398945 | 0 | 0 | 1447200 | 0 | 1366128 | 73035 | 339840 | 1372800 | 347927 | 8572000 | 1171200 | 812160 | 797054 | 25563 | 1156691 | 174774 | 1907740 | 988380 | 884520 | 307200 | 9355700 | 372480 | 185470 | 457920 | 327436 | 0 | 553320 | 87072 | 0 | 790560 | 0 | 0 | 0 | 13581817 | 300480 | 0 | 0 | 0 |  | 21111272 | 0 | 0 | 0 | 219840 | 0 | 0 | 0 | 0 | 0 | 26625 | 2477000 | 565127 | 44352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154910 | 0 | 0 | 172044 | 0 | 0 | 4344500 | 0 | 0 | 3957518 | 0 | 0 | 0 | 0 | 0 | 3907482 | 0 | 8275818 | 301440 | 0 | 153312 | 52704 | 456892 | 0 | 8349 | 0 | 27346000 | 2611964 | 0 | 116400 | 23400 | 303840 | 297792 | 0 | 0 | 12865450 | 46142 | 0 | 28249091 | 423410 | 0 |  | 162441089 | 118512674 | 280953763 | 87810235 | 21111272 | 54562514 | 0 | 21088581 | 86386858 | 4107212 | 0 | 1037150 | 3362880 | 1186581 | 300480 | 0
Fuel Cost | 0 | 0 | 4822745 | 0 | 0 | 1656030.88 | 0 | 9096192 | 7717680 |  | 0 | 10425305 | 7669026.63 | 0 | 1074389.5 | 1666505.5 | 6835301.76 | 0 | 0 | 547372.8 | 5768249.76 | 14301110.4 | 0 | 0 | 0 | 0 | 3938112 | 6755737.5 | 3191834.79 | 294327 | 342000 | 0 | 0 | 0 | 3959928 | 0 | 619707.24 | 489240 | 4725000 | 0 | 1434728.85 | 5421600.08 | 0 | 0 | 0 |  | 5158404 | 0 | 0 | 1189960.8 | 0 | 3682036.8 | 277428.96 | 2175422.4 | 0 | 0 | 0 | 8331771 | 7711750 | 5652680 | 3776182.17 | 0 | 1290695.04 | 0 | 0 | 1636212.56 | 0 | 0 | 8345536.7 | 592333.2 | 148230 | 1307950 | 209325 | 24145478.4 | 928156.8 | 0 | 543064.32 | 164182 | 1389180 | 1083614.4 | 1879200 | 1793539.44 | 2722426.05 | 0 | 0 | 4364467.2 | 0 | 4812145 | 881500 | 0 | 471873.6 | 7048000 | 54792 | 195970.56 | 0 | 5445599.25 | 0 | 0 | 19508256 | 0 | 18920872.8 | 853779.15 | 3507148.8 | 18752448 | 4616991.29 | 7886240 | 14241792 | 11743833.6 | 10082733.1 | 397760.28 | 13579552.34 | 1903288.86 | 20279276.2 | 13412316.6 | 11401462.8 | 3618816 | 8607244 | 4823616 | 2680041.5 | 5811004.8 | 3726221.68 | 0 | 7226359.2 | 1040510.4 | 0 | 10411675.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 63333816 | 0 | 0 | 0 | 2288534.4 | 0 | 0 | 0 | 0 | 0 | 382601.25 | 2774240 | 1096346.38 | 483436.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2613331.7 | 0 | 0 | 130237.308 | 0 | 0 | 36841360 | 0 | 0 | 4590720.88 | 0 | 0 | 0 | 0 | 0 | 4532679.12 | 0 | 8193059.82 | 4051353.6 | 0 | 1813680.96 | 761572.8 | 5802528.4 | 0 | 92256.45 | 0 | 226971800 | 2664203.28 | 0 | 861360 | 264654 | 3564043.2 | 4565151.36 | 0 | 0 | 116946940.5 | 0 | 0 | 241529728.05 | 0 | 0 |  | 431194472.94 | 737149636.258 | 1168344109.198 | 95469113.428 | 63333816 | 65288975.41 | 0 | 270736281.09 | 622289828.55 | 1108947.24 | 0 | 16914442.1 | 24145478.4 | 9057226.98 | 0 | 0
Yesterday Day Peak | 0 | 0 | 170 | 0 | 0 | 52 | 0 | 398 | 323 |  | 0 | 450 | 306 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 32 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 18 | 19 | 16 | 25 | 23 | 8 | 0 | 82 | 75 | 100 | 0 | 0 | 217 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 10 | 11 | 7 | 0 | 0 | 0 | 335 | 335 | 205 | 108 | 0 | 43 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 8 | 25 | 12 | 142 | 28 | 0 | 16 | 1 | 43 | 40 | 45 | 43 | 112 | 0 | 0 | 75 | 0 | 185 | 16 | 0 | 9 | 310 | 0 | 11 | 0 | 0 | 0 | 0 | 58 | 0 | 107 | 19 | 0 | 68 | 5 | 398 | 56 | 52 | 21 | 2 | 15 | 0 | 110 | 17 | 36 | 0 | 385 | 17 | 30 | 35 | 3 | 0 | 17 | 0 | 0 | 34 | 0 | 0 | 0 | 570 | 12 | 0 | 0 | 0 |  | 905 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 300 | 5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1020 | 109 | 0 | 0 | 3 | 11 | 0 | 0 | 0 | 520 | 1 | 0 | 1101 | 40 | 0 |  | 11696 | DayPeak
Yesterday Evening Peak | 0 | 0 | 130 | 0 | 0 | 51 | 0 | 360 | 285 |  | 0 | 450 | 275 | 0 | 0 | 0 | 280 | 0 | 0 | 8 | 25 | 82 | 0 | 0 | 0 | 0 | 25 | 35 | 55 | 18 | 19 | 16 | 25 | 30 | 25 | 0 | 82 | 75 | 100 | 0 | 17 | 222 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 12 | 0 | 42 | 9 | 29 | 0 | 0 | 0 | 280 | 275 | 179 | 147 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 142 | 32 | 0 | 18 | 0 | 43 | 30 | 47 | 43 | 112 | 0 | 0 | 81 | 0 | 184 | 17 | 0 | 10 | 270 | 0 | 11 | 0 | 32 | 0 | 0 | 65 | 0 | 100 | 0 | 50 | 100 | 6 | 401 | 97 | 70 | 34 | 0 | 85 | 17 | 55 | 17 | 95 | 50 | 400 | 17 | 0 | 54 | 17 | 0 | 35 | 0 | 0 | 54 | 0 | 0 | 0 | 612 | 7 | 0 | 0 | 0 |  | 776 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 124 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 414 | 17 | 0 | 35 | 15 | 75 | 0 | 0 | 0 | 1244 | 109 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 571 | 0 | 0 | 1311 | 0 | 0 |  | 12861 | EvPeak
Forecast for Evening | 0 | 0 | 160 | 0 | 0 | 85 | 0 | 400 | 330 | 0 | 0 | 450 | 300 | 72 | 85 | 55 | 200 | 0 | 0 | 92 | 102 | 135 | 55 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 19 | 25 | 31 | 25 | 0 | 125 | 75 | 105 | 0 | 17 | 225 |  | 0 | 0 | 0 | 18 | 70 | 0 | 50 | 0 | 50 | 11 | 25 | 0 | 0 | 0 | 330 | 330 | 200 | 140 | 0 | 50 | 0 | 0 | 50 | 0 | 25 | 52 | 18 | 10 | 33 | 12 | 165 | 50 | 0 | 19 | 0 | 43 | 40 | 50 | 40 | 112 | 0 | 0 | 86 | 0 | 185 | 17 | 0 | 10 | 300 | 8 | 11 | 0 | 145 | 0 | 0 | 142 | 0 | 100 | 0 | 50 | 100 | 145 | 400 | 104 | 105 | 51 | 0 | 285 | 54 | 55 | 105 | 78 | 50 | 400 | 72 | 0 | 108 | 51 | 0 | 34 |  | 0 | 54 | 0 | 160 |  | 600 | 20 | 0 | 0 |  |  | 938 | 0 | 0 |  | 66 | 120 | 0 | 0 | 40 | 40 | 16 | 130 | 25 | 110 | 0 | 0 | 0 | 30 | 20 | 91 | 28 | 42 | 40 | 8 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 200 |  | 0 | 0 | 0 | 0 | 200 | 0 | 414 | 72 | 0 | 70 | 0 | 84 | 0 | 0 | 75 | 1244 | 110 |  | 150 |  |  | 115 | 0 |  | 565 |  | 0 | 1400 |  | 0
Forecast for Day | 0 | 0 | 160 | 0 | 0 | 78 | 0 | 400 | 330 | 0 | 0 | 450 | 300 | 72 | 85 | 15 | 200 | 0 | 0 | 92 | 102 | 16 | 55 | 0 | 0 | 0 | 17 | 35 | 55 | 19 | 19 | 19 | 25 | 31 | 8 | 0 | 125 | 75 | 105 | 0 | 8 | 225 |  | 0 | 0 | 0 | 14 | 40 | 0 | 35 | 0 | 6 | 11 | 41 | 0 | 0 | 0 | 330 | 330 | 200 | 140 | 0 | 50 | 0 | 0 | 10 | 0 | 15 | 25 | 18 | 10 | 33 | 12 | 149 | 30 | 0 | 19 | 1.6 | 43 | 40 | 50 | 40 | 112 | 0 | 0 | 85 | 0 | 185 | 17 | 0 | 10 | 300 | 8 | 11 | 0 | 145 | 0 | 0 | 115 | 0 | 108 | 20 | 25 | 68 | 50 | 400 | 37 | 35 | 51 | 5 | 120 | 17 | 55 | 105 | 26 | 25 | 400 | 54 | 50 | 54 | 34 | 0 | 17 | 35 | 0 | 17 | 0 | 54 |  | 600 | 10 | 0 | 0 |  |  | 938 | 0 | 0 | 0 | 32 | 120 | 0 | 0 | 25 | 0 | 0 | 130 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 28 | 34 | 30 | 0 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 380 | 54 | 0 | 35 | 0 | 42 | 0 | 8 | 55 | 1244 | 110 |  | 35 | 6 | 100 | 35 | 0 |  | 520 | 30 | 0 | 1300 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 130 | 0 | 0 | 52 | 0 | 351 | 262 | 0 | 0 | 330 | 266 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 18 | 17 | 24 | 0 | 0 | 80 | 75 | 108 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 9 | 41 | 0 | 0 | 0 | 280 | 275 | 181 | 78 | 0 | 50 | 0 | 0 | 10 | 0 | 0 | 25 | 18 | 10 | 33 | 12 | 110 | 33 | 0 | 18 | 0 | 43 | 30 | 11 | 20 | 80 | 0 | 0 | 20 | 0 | 184 | 0 | 0 | 10 | 280 | 8 | 11 | 0 | 0 | 0 | 0 | 19 | 0 | 17 | 0 | 12 | 34 | 0 | 377 | 70 | 0 | 17 | 2 | 15 | 0 | 34 | 17 | 0 | 12 | 365 | 0 | 11 | 0 | 17 | 0 | 17 | 11 | 0 | 17 | 0 | 0 | 0 | 474 | 10 | 0 | 0 | 0 | 0 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 109 | 0 | 0 | 1 | 46 | 0 | 0 | 0 | 523 | 1 | 0 | 965 | 31 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
292.3904
| Minimum Generation |  | 10455 | 7:00 | [202 empty] | 142372749
| Highest Generation |  | 12861 | 19:30 | [202 empty] | 142.3727 |  |  |  |  | 1.1866
| Day Peak Generation |  | 11696 | 12:00 | [202 empty] | 22125731
| Evening Peak Generation |  | 12861 | 19:30 | [202 empty] | 22.1257 |  |  | 54562514 |  | 4.1072
| HVDC Max Flow |  | 906 | 4:00 | [202 empty] | 21.1113 |  |  |  |  | 0.30048
| HVDC EvPeak Flow |  | 776 | 19:30 | [200 empty] | 280953763 |  | 3.3629 |  | 86.3869
| Load factor L.F |  | 91.02% | [166 empty] | 1275.5 | [36 empty] | 280.9538

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-09-22
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-09-21 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 11696 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9824
Evening Peak Generation : |  |  | 12861 | MW Hour : | 19:30 | Available Max Generation : |  | 16072
E.P. Demand (at gen end) : |  |  | 12861 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 13000
Maximum Generation : |  |  | 12861 | MW Hour : | 19:30 | Reserve(Generation end) |  | 3072
Total Gen. (MKWH) : |  |  | 280.9538 | System Load Factor : | 91.02% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 920 | MW at | 22:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-09-22
Actual : |  | 108.5 | Ft.(MSL) , | Rule curve : | 103.84 | Ft.( MSL )
Gas Consumed : |  | Total = | 1066.13 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 160758088.838
: |  |  | Coal : | 622289828.55 | Oil : | 287650723.19 | Total : | 1070698640.578
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4857.5703 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1336.484 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1872.677 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1628.1782 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1339.4547 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 996.477 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 558.2777 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 465.5121 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 910.4541 |  |  | 0 | 0%
Total |  | 0 |  | 13965.0851 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
10:33 | 13:42 | Savar 132/33kV S/S Bus-B Scheduled S/D Due to PBS Shutdown.
14:08 | 14:43 | Keranigonj 230/132/33kV S/S Hasnabad Tripped showing 86.1 relays
15:22 | 17:50 | Madaripur 132/33kV S/S T3-426T LT Scheduled S/D
15:47 | 17:40 | Jamalpur 132/33kV S/S T-4 HT Scheduled S/D Due to sw-2 feeder d/s red hot problem. |  |  |  |  | 7 MW load interrup.
16:37 | 17:01 | Chandraghona 132/33kV S/S TR-01(406T) HT Project Work S/D |  |  |  |  | 18 MW load interrup.
16:37 | 17:01 | Chandraghona 132/33kV S/S MAIN BUS-1 Project Work S/D
17:55 | 20:51 | Cumilla(N) 230/132/33kV S/S 132KV T-04 LT Forced S/D Due to Red hot Remove. |  |  |  |  | 5 MW load interrup.
01:05 |  | Siddirganj CCPP 335MW ST was forced shutdown
05:29 |  | BIPTC S/S 20DF24 Tripped showing Distance relay. relays Due to Trip by impedance 21R.
05:57 |  | Bogura-----Gadda 400 KV ckt -1 S/D
06:14 |  | Joypurhat 132/33kV S/S Transformer T-3 HT S/D Due to Development Work implementation by Joypurhat PBS. |  |  |  |  | 9 MW load interrup.
06:15 |  | Joypurhat 132/33kV S/S Transformer T-4 (437 T) HT S/D Due to Development Work implementation by Joypurhat PBS
06:31 |  | Chowmuhani 132/33kV S/S HFPL line Project Work S/D Due to ESPNERP Project work
06:58 |  | Aminbazar 400/230/132kV S/S 132 kv Bus 01 Scheduled S/D Due to DS maintanence
07:04 |  | Aminbazar 400/230/132kV S/S ATR-02 LT Scheduled S/D Due to DS maintanence
07:11 | 07:30 | Sylhet 132/33kV S/S T1 LT Tripped showing O/C relays. |  |  |  |  | 25 MW load interrup.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-09-21 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 130 | 3303250
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 51 | 1245136 | Frequency control
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 360 | 8663040 | Frequency control
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 285 | 7146000 | Frequency control
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9564500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 275 | 6909033 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 81086 | High voltage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 0 | 125774 | High voltage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 18 | 392436 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 8 | 37440 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 6102948 | Frequency control
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 25 | 409968 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 25 | 309600 | High voltage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 82 | 882240 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 500425
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 238019
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 35 | 861720 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 590500 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 30 | 679100
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 232800 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 32 | 398945 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Contract Expired
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 100 | 1366128 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 812160 | High voltage
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 372480 | High voltage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 457920 | High voltage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 87072
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 790560
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5722 | 2521 | 52560280
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2500000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 87751 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 73035
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 42 | 318240 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 157 | 4107212
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 222 | 5213077
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 34 | 797054 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Low demand
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 12 | 88080 | Low demand
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 339840 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 9 | 218448 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 29 | 653280
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25563
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 85 | 1156691 | Low demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 174774 | Low demand
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 55 | 1907740 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 307200 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 327436 | Low demand
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 0 | 0 | Reserve
| SS Power I |  | SS Power | 0 | 0 | 612 | 13581817
| Cox's Bazar Wind |  | IPP | 66 | 0 | 7 | 300480 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2545 | 1515 | 32177718
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 179 | 4873000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7506100 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 275 | 7075000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 50 | 1142208
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 147 | 2927273 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 979768
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 6 | 347927 | Low demand
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Low demand
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 100 | 1372800 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 432360 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 197640
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 142 | 3362880
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 747400
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 620486
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 12 | 279100 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 988380 | High voltage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 95 | 884520 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 553320 | Machine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | Fuel shortage
| Cumilla Area Total |  |  |  | 2896 | 1502 | 34290162
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 32 | 851520 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 399312 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10300
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 65 | 1447200 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 97 | 1171200 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 185470
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 395280 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 230 | 4460282
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1014000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 820920 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2367327 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 1080000 | Engine problem
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 43 | 1036728 | Engine problem
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 257856 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under maint.
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1914240
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 184 | 4764500 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 410000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 0 | 73056 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 7048000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 401 | 8572000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 238320
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9355700
| Sylhet Area Total |  |  |  | 2427 | 1649 | 38952647
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 776 | 21111272
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 219840 | High voltage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Low demand
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Low demand
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 26625 | Low demand
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 301440 | High voltage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 52704 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 303840
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 220 | 0 | 0 | Fuel shortage
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 571 | 12865450
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3121 | 1403 | 34881171
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 44352 | Low demand
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 28 | 565127 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 124 | 2477000 | ST Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 27346000
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 109 | 2611964 | GT-1 under maint
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 116400 | Low demand
| Barisal 307 MW |  | IPP | 307*1 | 307 | 0 | 0 | Coal shortage.
| Barisal Area Total |  |  |  | 2265 | 1538 | 33160843
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Low demand
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Low demand
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 202 | 3957518
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 211 | 3907482
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 8275818
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 154910 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 172044 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | High voltage
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 153312 | High voltage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | High voltage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 23400
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1311 | 28249091
| Rajshahi Area Total |  |  |  | 3631 | 2213 | 44893575
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 180 | 4344500 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 75 | 456892 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 8349
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 35 | 297792 | Low demand
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 46142
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 423410
| Rangpur Area Total |  |  |  | 950 | 290 | 5577085
| Total |  |  |  | 24171 | 12861 | 280953763
| Eastern Grid Total |  |  |  | 14204 | 7417 | 162441089
| Western Grid Total |  |  |  | 9967 | 5444 | 118512674
| National Grid Total |  |  |  | 24171 | 12861 | 280953763
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-09-21
| (a) ENTIRE EASTERN GRID : |  | 8553.85 | MW | (b) ENTIRE WESTERN GRID : |  | 3786.9 | MW
| i) Dhaka area |  | 4705.35 | MW | i) Khulna area |  | 1484.5 | MW
| ii) Chittagong area |  | 1262.5 | MW | ii) Rajshahi area |  | 1218.4 | MW
| iii) Comilla area |  | 1170 | MW | iii) Barisal area |  | 408 | MW
| iv) Mymensingh area |  | 905 | MW | iv) Rangpur area |  | 676 | MW
| v) Sylhet area |  | 511 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 12340.75 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 32 | 23:00 | Kamrangirchar | 64.8 | 13:00 | Narshingdi | 186 | 21:00 | Shikalbaha-230 | N/A | N/A
2 | AKSML | 103 | 08:00 | Chowmuhani | 212 | 20:00 | Kaptai | N/A | N/A | Natore | 126 | 21:00 | Shitalakhya | 123.4 | 12:00
3 | Aftabnagar | 34 | 19:00 | Chuadanga | 97 | 19:00 | Kazla | 92 | 13:00 | Nawabganj | 42.6 | 21:00 | Sholosohor | 39 | 15:00
4 | Agargaon | 88 | 13:00 | Coxsbazar | 118 | 18:30 | Keranigonj | 74 | 19:00 | Netrakona | 113 | 22:00 | Shyampur | 144 | 12:00
5 | Agrabad | 74 | 14:00 | Cumilla(N) | 138 | 22:00 | Khagrachori | 26 | 21:00 | New | 78.7 | 12:00 | Siddhirganj | 102 | 12:00
6 | Amnura | 45 | 21:00 | Cumilla(S) | 154 | 00:00 | Khulna | 82 | 19:00 | Niamatpur | 68 | 21:00 | Sirajganj | 98 | 19:30
7 | Ashuganj | 66 | 00:00 | Daudkandi | 128 | 21:00 | Khulshi | 171 | 18:00 | Noapara | 44 | 19:00 | Sonargaon | 85 | 23:00
8 | BIPTC | N/A | N/A | Dhaka | 34 | 12:00 | Kishoreganj | 152 | 20:00 | PHP | 9 | 08:00 | Sreemongol | 59 | 18:30
9 | BSRM | 173 | 18:00 | Dhamrai | 126 | 12:00 | Kodda | 281 | 19:00 | Pabna | 108 | 18:30 | Sreepur | 72 | 15:00
10 | Bagerhat | 84 | 19:30 | Dhanmondi | 112 | 13:00 | Kulaura | 40 | 19:00 | Palashbari | 98 | 00:00 | Srinagar | 41 | 18:30
11 | Bakulia | 98 | 19:00 | Dohazari | 92 | 20:00 | Kurigram | 56 | 23:00 | Panchagarh | 44 | 18:30 | Sunamganj | 48 | 22:00
12 | Banani | 32 | 13:00 | Faridpur | 144 | 20:00 | Kushtia | 128 | 18:30 | Patuakhali | 100.5 | 21:00 | Sylhet | 145 | 13:00
13 | Bangabhaban | 17 | 10:00 | Fatullah | 64 | 15:00 | Lalbag | 102 | 13:00 | Payra | 22 | 14:00 | TK | 29.5 | 19:00
14 | Barapukuria | 51 | 02:00 | Fenchuganj | 42 | 19:00 | Lalmonirhat | 36 | 00:00 | Postogola | 57 | 13:00 | Tangail | 200 | 22:00
15 | Barguna | 20 | 23:00 | Feni | 104 | 21:00 | MI_Cement | 19.2 | 13:00 | Purbachal | 20 | 14:00 | Thakurgaon | 72 | 00:00
16 | Barishal | 97 | 13:00 | GPH | 19 | 16:00 | Madanganj | 22 | 21:00 | Purbasadipur | 100 | 00:00 | Tongi | 113 | 12:00
17 | Barishal-230 | 90 | 21:00 | Ghorashal | 73 | 18:00 | Madaripur | 88 | 21:00 | Rahim | 41 | 10:00 | Ullon | 38 | 18:00
18 | Baroaulia | 64 | 17:00 | Goalpara | 34 | 13:00 | Madartek | 76.7 | 18:30 | Rajbari | 70 | 19:00 | Uttara | 85 | 11:00
19 | Baroirhat | 58 | 18:30 | Gollamari | 51 | 13:00 | Madunaghat | 53 | 19:00 | Rajendrapur | 94 | 18:30 | UttaraNew | 64 | 14:00
20 | Bashundhara | 148 | 13:00 | Gopalganj | 97.4 | 19:00 | Magura | 57 | 19:00 | Rajshahi | 135 | 19:00 | Zigatola | 64 | 13:00
21 | BashundharaCement | 6 | 11:00 | Gulshan | 124 | 13:00 | Mahasthangarh | 64 | 00:00 | Rajshahi-230 | 31 | 00:00
22 | Beanibazar | 65 | 21:00 | Halishahar | 77 | 21:00 | Manikganj | 119 | 22:00 | Ramganj | 106 | 00:00
23 | Benapole | 54 | 18:30 | HaripurSBU | 142 | 01:00 | Maniknagar | 90 | 13:00 | Rampur | 29 | 00:00
24 | Bhaluka | 134 | 15:00 | Hasnabad | 82 | 19:00 | Matarbari | 44 | 21:00 | Rangamati | 16 | 11:00
25 | Bhandaria | 46 | 19:00 | Hathazari | 71 | 21:00 | Matuail | 64 | 12:00 | Rangpur | 114 | 19:00
26 | Bhangura | 30 | 19:00 | Ishurdi | 65 | 19:30 | Millgate | 96 | 12:00 | Ruppur | 5.8 | 09:00
27 | Bheramara(GK) | 54 | 19:00 | Jaldhaka | 52 | 00:00 | Mirpur | 129 | 13:00 | SSM | 0 | 00:00
28 | Bhulta | 253 | 12:00 | Jamalpur | 134 | 00:00 | Mirsorai | 2 | 09:00 | Saidpur | 86 | 09:00
29 | Bog-Sherpur | 50 | 01:00 | Jashore | 116 | 19:00 | Mithapukur | 40 | 00:00 | Satkhira | 110 | 19:00
30 | Bogura | 143 | 19:00 | Jhenaidah | 111 | 20:00 | Modern | 0 | 00:00 | Satmasjid | 110 | 13:00
31 | Borhanuddin | 62 | 21:00 | Joydebpur | 173 | 18:30 | Mogbazar | 142.3 | 13:00 | Savar | 180 | 16:00
32 | Brahmanbaria | 157 | 22:00 | Joypurhat | 48 | 19:30 | Mongla | 30 | 09:00 | ShahCement | 31 | 11:00
33 | Cantonment | 150 | 13:00 | Juldah | 19 | 13:00 | Motijheel | 39 | 13:00 | Shahjadpur | 92 | 21:00
34 | Chandpur | 67 | 22:00 | KSRM | 27 | 18:00 | Munshiganj | 95 | 19:30 | Shahjibazar | 120 | 00:00
35 | Chandraghona | 29 | 18:30 | Kabirpur | 285 | 11:00 | Mymensingh | 204 | 22:00 | Shahmirpur | 49.6 | 00:00
36 | Chapai | 55 | 22:00 | Kachua | 72 | 22:00 | Naogaon | 115 | 21:00 | Shariatpur | 72 | 22:00
37 | Charsaidpur | 49 | 10:00 | Kallyanpur | 99 | 13:00 | Narail | 50 | 18:30 | Sherpur | 96 | 01:00
38 | Chauddagram | 53 | 22:00 | Kalurghat | 36 | 12:00 | Narinda | 78 | 13:00 | Shikalbaha | 37 | 10:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-09-21 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 399 | 00:00 | 385 | 12:00 | Gopalganj | 403 | 06:00 | 395 | 18:30
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 376 | 05:00 | 367 | 12:00
| Bhulta | 395 | 06:00 | 383 | 12:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 402 | 19:00 | 393 | 14:00 | Payra | 411 | 06:00 | 406 | 00:00
| BIPTC | 402 | 06:00 | 395 | 16:00 | Rahanpur | 404 | 14:00 | 394 | 01:00
| Bogura | N/A | N/A | N/A | N/A | Rampal | 407 | 06:00 | 397 | 18:30
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 231 | 22:00 | 222 | 12:00 | Hasnabad | 232 | 05:00 | 226 | 16:00
| AKSML | 232 | 21:00 | 223 | 11:00 | Hathazari | 231 | 22:00 | 223 | 19:00
| Aminbazar | 233 | 04:00 | 226 | 11:00 | Ishurdi | 234 | 06:00 | 223 | 18:30
| Ashuganj | 235 | 08:00 | 228 | 11:00 | Jhenaidah | 229 | 09:00 | 214 | 18:30
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 231 | 04:00 | 224 | 11:00
| Baghabari | 231 | 06:00 | 221 | 18:30 | Keranigonj | 230 | 05:00 | 222 | 12:00
| Barapukuria | 222 | 10:00 | 214 | 00:00 | Khulna(S) | 235 | 09:00 | 226 | 18:30
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 236 | 07:00 | 230 | 00:00 | Maniknagar | 231 | 21:00 | 223 | 12:00
| Bheramara | 235 | 06:00 | 224 | 18:30 | Meghnaghat | 239 | 21:00 | 232 | 11:00
| Bhulta | 234 | 04:00 | 226 | 12:00 | Mirsorai | 228 | 01:00 | 222 | 11:00
| Bibiana | 231 | 09:00 | 226 | 12:00 | Rajshahi | 231 | 09:00 | 216 | 18:30
| BIPTC | 235 | 06:00 | 221 | 18:30 | Rampal | 234 | 14:00 | 226 | 18:30
| Bogura | 229 | 09:00 | 221 | 00:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 240 | 07:00 | 234 | 00:00 | Rampura | 233 | 05:00 | 225 | 11:00
| BSRM | 230 | 07:00 | 223 | 11:00 | Shikalbaha | 230 | 00:00 | 224 | 12:00
| Cumilla(N) | 231 | 22:00 | 224 | 12:00 | Shyampur | 231 | 06:00 | 223 | 12:00
| Fenchuganj | 235 | 22:00 | 231 | 02:00 | Siddhirganj | 233 | 21:00 | 226 | 12:00
| Ghorashal | 230 | 00:00 | 230 | 00:00 | Sirajgonj | 237 | 09:00 | 232 | 12:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 233 | 07:00 | 227 | 11:00
| GPH | 228 | 00:00 | 222 | 11:00 | Tongi | 228 | 04:00 | 220 | 11:00
| Haripur | 232 | 03:00 | 224 | 11:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 137 | 06:00 | 129 | 11:00 | Lalbag | 132 | 22:00 | 124 | 12:00
| Agargaon | 133 | 22:00 | 126 | 12:00 | Lalmonirhat | 131 | 10:00 | 123 | 00:00
| Agrabad | 132 | 00:00 | 127 | 11:00 | Madanganj | 133 | 06:00 | 128 | 11:00
| AKS | 130 | 00:00 | 123 | 05:00 | Madaripur | 131 | 06:00 | 127 | 21:00
| Aminbazar | 132 | 03:00 | 128 | 11:00 | Madartek | 136 | 04:00 | 123 | 09:00
| Amnura | 133 | 09:00 | 124 | 18:30 | Madunaghat | 133 | 00:00 | 128 | 12:00
| Ashuganj | 139 | 07:00 | 136 | 11:00 | Magura | 138 | 04:00 | 127 | 18:30
| Bagerhat | 131 | 12:00 | 120 | 18:30 | Mahasthangarh | 135 | 09:00 | 129 | 01:00
| Bakulia | 133 | 00:00 | 128 | 11:00 | Manikganj | 132 | 01:00 | 125 | 14:00
| Banani | 137 | 06:00 | 128 | 12:00 | Maniknagar | 134 | 04:00 | 127 | 12:00
| Bangabhaban | 134 | 07:00 | 127 | 12:00 | Matarbari | 124 | 14:00 | 113 | 18:30
| Barapukuria | 138 | 05:00 | 132 | 00:00 | Matuail | 134 | 21:00 | 128.4 | 12:00
| Barguna | 136 | 09:00 | 130 | 00:00 | Millgate | 135 | 22:00 | 126 | 11:00
| Barishal | 136 | 13:00 | 128 | 23:00 | Mirpur | 131 | 06:00 | 126 | 11:00
| Barishal-230 | 136 | 07:00 | 130 | 22:00 | Mithapukur | 133 | 15:00 | 126 | 00:00
| Baroaulia | 133 | 06:00 | 129 | 10:00 | MI_Cement | 134.6 | 22:00 | 128 | 12:00
| Baroirhat | 130 | 14:00 | 123 | 12:00 | Modern | 132 | 00:00 | 128 | 11:00
| Bashundhara | 137 | 04:00 | 125 | 12:00 | Mogbazar | 137 | 03:00 | 130 | 11:00
| BashundharaCement | 133 | 06:00 | 128 | 11:00 | Mongla | 131 | 13:00 | 122 | 21:00
| Beanibazar | 128 | 17:00 | 124 | 00:00 | Motijheel | 134 | 06:00 | 127 | 12:00
| Benapole | 135 | 15:00 | 126 | 18:30 | Munshiganj | 134 | 22:00 | 128 | 12:00
| Bhaluka | 128 | 17:00 | 120 | 00:00 | Mymensingh | 134 | 16:00 | 118 | 00:00
| Bhandaria | 135 | 08:00 | 124 | 22:00 | Naogaon | 131 | 06:00 | 125 | 00:00
| Bhangura | 138 | 06:00 | 132 | 12:00 | Narail | 138 | 05:00 | 126 | 18:30
| Bheramara | 135 | 06:00 | 128 | 18:30 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara(GK) | 135 | 14:00 | 127 | 18:30 | Narshingdi | 128 | 18:00 | 122 | 12:00
| Bhulta | 128 | 22:00 | 121 | 00:00 | Natore | 131 | 06:00 | 122 | 18:30
| Bog-Sherpur | 133 | 06:00 | 125 | 12:00 | Nawabganj | 131 | 04:00 | 125 | 12:00
| Bogura | 138 | 06:00 | 115 | 18:30 | Netrakona | 133 | 02:00 | 122 | 21:00
| Bogura-230 | 139 | 09:00 | 132 | 00:00 | New | 136 | 21:00 | 126 | 11:00
| Brahmanbaria | 132 | 15:00 | 120 | 00:00 | Niamatpur | 132 | 16:00 | 123 | 00:00
| Cantonment | 132 | 04:00 | 124 | 12:00 | Noapara | 135 | 17:00 | 126 | 18:30
| Chandpur | 134 | 14:00 | 119 | 00:00 | Pabna | 135 | 09:00 | 125 | 18:30
| Chandraghona | 134 | 14:00 | 131 | 11:00 | Palashbari | 132 | 10:00 | 125 | 00:00
| Chapai | 131 | 17:00 | 126 | 00:00 | Panchagarh | 135 | 11:00 | 125 | 00:00
| Charsaidpur | 135 | 22:00 | 129 | 11:00 | Patuakhali | 136 | 07:00 | 132 | 00:00
| Chauddagram | 131 | 13:00 | 124 | 12:00 | Payra | 139 | 00:00 | 136 | 00:00
| Chhatak | 129 | 17:00 | 124 | 00:00 | PHP | 129 | 13:00 | 122 | 23:00
| Chowmuhani | 130 | 14:00 | 117 | 00:00 | Postogola | 136 | 22:00 | 130 | 11:00
| Chuadanga | 135 | 09:00 | 122 | 18:30 | Purbachal | 137 | 03:00 | 125 | 12:00
| Coxsbazar | 122 | 09:00 | 113 | 18:30 | Purbasadipur | 132 | 11:00 | 122 | 00:00
| Cumilla(N) | 134 | 14:00 | 129 | 10:00 | Rahanpur | 139 | 23:00 | 130 | 00:00
| Cumilla(S) | 134 | 14:00 | 129 | 09:00 | Rahim | 134 | 02:00 | 127 | 19:00
| Daudkandi | 126 | 15:00 | 120 | 00:00 | Rajbari | 132 | 14:00 | 123 | 18:30
| Dhaka | 137 | 04:00 | 129 | 12:00 | Rajendrapur | 134 | 19:00 | 126 | 13:00
| Dhamrai | 134 | 06:00 | 127 | 12:00 | Rajshahi | 132 | 07:00 | 123 | 18:30
| Dhanmondi | 134.5 | 21:00 | 128 | 12:00 | Rajshahi-230 | 134 | 06:00 | 123 | 01:00
| Dohazari | 130 | 15:00 | 125 | 11:00 | Ramganj | 133 | 14:00 | 115 | 00:00
| Faridpur | 130 | 06:00 | 125 | 18:00 | Rampur | 132 | 00:00 | 127 | 11:00
| Fatullah | 136 | 21:00 | 130 | 12:00 | Rampura | 137 | 05:00 | 129 | 11:00
| Fenchuganj | 133 | 16:00 | 130 | 00:00 | Rangamati | 133 | 00:00 | 129 | 12:00
| Feni | 131 | 14:00 | 124 | 00:00 | Rangpur | 133 | 10:00 | 124 | 03:00
| Ghorashal | 138 | 01:00 | 133 | 12:00 | Ruppur | 137 | 17:00 | 131 | 00:00
| Goalpara | 134 | 13:00 | 126 | 18:30 | Saidpur | 134 | 11:00 | 125 | 00:00
| Gollamari | 133 | 15:00 | 127 | 18:30 | Satkhira | 132 | 14:00 | 121 | 18:30
| Gopalganj | 130 | 13:00 | 124 | 18:30 | Satmasjid | 133 | 22:00 | 125 | 12:00
| Gopalganj-400 | 130 | 07:00 | 126 | 18:30 | Savar | 132 | 22:00 | 127 | 11:00
| Gulshan | 136 | 04:00 | 128 | 12:00 | ShahCement | 135 | 22:00 | 129 | 11:00
| Halishahar | 133 | 19:30 | 127 | 11:00 | Shahjadpur | 140 | 15:00 | 136 | 00:00
| Haripur | 134 | 02:00 | 130 | 11:00 | Shahjibazar | 131 | 07:00 | 122 | 00:00
| HaripurSBU | 134 | 02:00 | 130 | 11:00 | Shahmirpur | 133 | 19:00 | 127 | 11:00
| Hasnabad | 135 | 04:00 | 130 | 11:00 | Shariatpur | 131 | 16:00 | 125 | 00:00
| Hathazari | 135 | 03:00 | 131 | 11:00 | Sherpur | 139 | 17:00 | 115 | 00:00
| Ishurdi | 137 | 06:00 | 130 | 18:30 | Shikalbaha | 122 | 00:00 | 117 | 11:00
| Jaldhaka | 134 | 11:00 | 125 | 00:00 | Shikalbaha-230 | 135 | 14:00 | 129 | 12:00
| Jamalpur | 138 | 17:00 | 120 | 00:00 | Shitalakhya | 134.6 | 22:00 | 128 | 12:00
| Jashore | 135 | 09:00 | 126 | 18:30 | Sholosohor | 132 | 01:00 | 128 | 11:00
| Jhenaidah | 139 | 17:00 | 129 | 18:30 | Shyampur | 136 | 05:00 | 128 | 11:00
| Jhenaidah-230 | 140 | 09:00 | 129 | 18:30 | Shyampur-230 | 136 | 22:00 | 130 | 12:00
| Joydebpur | 137 | 15:00 | 129 | 12:00 | Siddhirganj | 134 | 06:00 | 129 | 12:00
| Joypurhat | 131 | 08:00 | 125 | 00:00 | Sirajganj | 136 | 15:00 | 127 | 12:00
| Juldah | 134 | 19:30 | 128 | 11:00 | Sonargaon | 130 | 00:00 | 127 | 06:00
| Kabirpur | 136 | 19:00 | 123 | 11:00 | Sreemongol | 131 | 17:00 | 124 | 00:00
| Kachua | 131 | 14:00 | 119 | 00:00 | Sreepur | 128 | 07:00 | 124 | 00:00
| Kaliakoir | 136 | 15:00 | 132 | 08:00 | Srinagar | 132 | 21:00 | 125 | 12:00
| Kallyanpur | 132 | 06:00 | 128 | 11:00 | SSM | 138 | 19:00 | 130 | 11:00
| Kalurghat | 133 | 01:00 | 128 | 12:00 | Sunamganj | 126 | 17:00 | 121 | 01:00
| Kamrangirchar | 133 | 22:00 | 126 | 11:00 | Sylhet | 130 | 17:00 | 127 | 00:00
| Kaptai | N/A | N/A | N/A | N/A | Tangail | 136 | 15:00 | 126 | 21:00
| Kazla | 134 | 05:00 | 127 | 12:00 | Thakurgaon | 134 | 11:00 | 123 | 18:30
| Keranigonj | 132 | 05:00 | 126 | 12:00 | TK | 133 | 18:30 | 123 | 19:00
| Khagrachori | 133 | 06:00 | 129 | 12:00 | Tongi | 136 | 21:00 | 129 | 12:00
| Khulna | 133 | 14:00 | 125 | 18:30 | Ullon | 137 | 06:00 | 128 | 12:00
| Khulna(S) | 133 | 09:00 | 127 | 18:30 | Uttara | 131 | 06:00 | 126 | 12:00
| Khulshi | 131 | 00:00 | 126 | 11:00 | UttaraNew | 131 | 04:00 | 125 | 12:00
| Kishoreganj | 133 | 17:00 | 125 | 00:00 | Zigatola | 132 | 06:00 | 126 | 12:00
| Kodda | 135 | 19:00 | 125 | 08:00
| KSRM | 133 | 19:00 | 128 | 12:00
| Kulaura | 132 | 16:00 | 129 | 00:00
| Kurigram | 131 | 06:00 | 124 | 00:00
| Kushtia | 135 | 06:00 | 126 | 18:30

## L-Curve
Date | 2023-09-21
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1004 | 6844 | 5117 | 11961 |  |  |  | QF-LDC-11
0:30 | 1042 | 6854.5 | 5121 | 11975.5 | Date: | 2023-09-21
1:00 | 1080 | 6865 | 5125 | 11990
1:30 | 1110 | 6732 | 5083.5 | 11815.5
2:00 | 1140 | 6599 | 5042 | 11641
2:30 | 1108 | 6563 | 4905.5 | 11468.5 | [5 empty] | Gen. at Eve. Peak | 12861 | 12861 MW (19:30 )
3:00 | 1076 | 6527 | 4769 | 11296 | [6 empty] | 19:30
3:30 | 1063 | 6501.5 | 4766 | 11267.5 | [5 empty] | Gen. at Day Peak | 11696 | 11696 MW (12:00 )
4:00 | 1050 | 6476 | 4763 | 11239 | [6 empty] | 12:00
4:30 | 1065 | 6411 | 4702.5 | 11113.5 | [5 empty] | Highest Generation | 12861
5:00 | 1080 | 6346 | 4642 | 10988 | [6 empty] | 19:30
5:30 | 1075 | 6247 | 4573.5 | 10820.5
6:00 | 1070 | 6148 | 4505 | 10653
6:30 | 1045 | 6075.5 | 4478.5 | 10554
7:00 | 1020 | 6003 | 4452 | 10455
7:30 | 1020 | 6024.5 | 4466 | 10490.5
8:00 | 1020 | 6046 | 4480 | 10526
8:30 | 1110 | 6243.5 | 4511.5 | 10755
9:00 | 1200 | 6441 | 4543 | 10984
9:30 | 1290 | 6512.5 | 4604 | 11116.5
10:00 | 1380 | 6584 | 4665 | 11249
10:30 | 1400 | 6705.5 | 4633.5 | 11339
11:00 | 1420 | 6827 | 4602 | 11429
11:30 | 1430 | 6940 | 4622.5 | 11562.5
12:00 | 1440 | 7053 | 4643 | 11696
12:30 | 1455 | 7114 | 4739 | 11853
13:00 | 1470 | 7175 | 4835 | 12010
13:30 | 1538 | 6945 | 4838 | 11783
14:00 | 1606 | 6715 | 4841 | 11556
14:30 | 1497 | 6478 | 4650 | 11128
15:00 | 1388 | 6241 | 4459 | 10700
15:30 | 1444 | 6250.5 | 4472 | 10722.5
16:00 | 1500 | 6260 | 4485 | 10745
16:30 | 1455 | 6249 | 4485.5 | 10734.5
17:00 | 1410 | 6238 | 4486 | 10724
17:30 | 1280 | 6445.5 | 4624 | 11069.5
18:00 | 1150 | 6653 | 4762 | 11415
18:30 | 1160 | 7020.5 | 5103.5 | 12124
19:00 | 1170 | 7388 | 5445 | 12833
19:30 | 1110 | 7417 | 5444 | 12861
20:00 | 990 | 7438 | 5396 | 12834 |  |  |  | Executive Engineer
20:30 | 975 | 7401 | 5365 | 12766 |  |  |  | Network Operation Division
21:00 | 960 | 7364 | 5334 | 12698
21:30 | 940 | 7321 | 5280 | 12601
22:00 | 920 | 7278 | 5226 | 12504 |  |  |  |  | Page 6 of 7
22:30 | 968 | 7172 | 5195 | 12367
23:00 | 1016 | 7066 | 5164 | 12230
23:30 | 1010 | 6955 | 5140.5 | 12095.5
24:00 | 1004 | 6844 | 5117 | 11961
12861 MW (19:30 )
11696 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-09-21 |  | Energy |  | 280953763
[15 empty] | 43728 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3613 | 802 | 2382 | 0 | 943 | 3870 | 157 | 0 | 32 | 152 | 0 | 10 | 94.545
0:30 | 3596.5 | 853.5 | 2382 | 0 | 952 | 3817 | 180 | 0 | 32 | 152 | 0 | 10.5 | 118.8975 |  |  | Date: | 43728
1:00 | 3580 | 905 | 2382 | 0 | 961 | 3764 | 203 | 0 | 32 | 152 | 0 | 11 | 143.25
1:30 | 3564.5 | 905 | 2380 | 0 | 808.5 | 3770 | 203 | 0 | 24 | 150 | 0 | 10.5 | 142.7725 | [9 empty] | Total Energy | 280.9538 | 280.9538 | Total Energy Gen 280.954 MKWHr Energy Not Served 1.382 MKWHr Energy Requirement 282.336 MKWHr
2:00 | 3549 | 905 | 2378 | 0 | 656 | 3776 | 203 | 0 | 16 | 148 | 0 | 10 | 142.295 | [9 empty] | Energy not Served | 1.3819 | 1.3819
2:30 | 3524 | 905 | 2356.5 | 0 | 611.5 | 3695 | 203 | 0 | 16 | 146 | 0 | 11.5 | 144.6825 | [9 empty] | Energy Requirement | 282.3357 | 282.3357
3:00 | 3499 | 905 | 2335 | 0 | 567 | 3614 | 203 | 0 | 16 | 144 | 0 | 13 | 147.07
3:30 | 3540.5 | 905.5 | 2277.5 | 0 | 559 | 3610.5 | 203 | 0 | 16 | 143 | 0 | 12.5 | 140.8625 | [8 empty] | Shortage
4:00 | 3582 | 906 | 2220 | 0 | 551 | 3607 | 203 | 0 | 16 | 142 | 0 | 12 | 134.655
4:30 | 3593.5 | 906 | 2169 | 0 | 499.5 | 3572 | 203 | 0 | 16 | 141 | 0 | 13.5 | 120.8075
5:00 | 3605 | 906 | 2118 | 0 | 448 | 3537 | 203 | 0 | 16 | 140 | 0 | 15 | 106.96
5:30 | 3568.5 | 905.5 | 2113.5 | 0 | 411 | 3453.5 | 203 | 0 | 16 | 135 | 0.5 | 14 | 109.3475
6:00 | 3532 | 905 | 2109 | 0 | 374 | 3370 | 203 | 0 | 16 | 130 | 1 | 13 | 111.735
6:30 | 3521.5 | 902.5 | 2121.5 | 0 | 343.5 | 3292.5 | 203 | 0 | 16 | 124 | 19 | 10.5 | 110.78 | [7 empty] | Coal
7:00 | 3511 | 900 | 2134 | 0 | 313 | 3215 | 203 | 0 | 16 | 118 | 37 | 8 | 109.825
7:30 | 3530 | 902.5 | 2116 | 0 | 325 | 3213.5 | 203 | 0 | 16 | 117 | 60 | 7.5 | 109.3475 | [6 empty] | Oil
8:00 | 3549 | 905 | 2098 | 0 | 337 | 3212 | 203 | 0 | 16 | 116 | 83 | 7 | 108.87
8:30 | 3631 | 905 | 2176.5 | 0 | 394.5 | 3230 | 180 | 0 | 16 | 120 | 89.5 | 12.5 | 124.15
9:00 | 3713 | 905 | 2255 | 0 | 452 | 3248 | 157 | 0 | 16 | 124 | 96 | 18 | 139.43
9:30 | 3691.5 | 905 | 2249 | 0 | 539.5 | 3240 | 157 | 0 | 32 | 130 | 154.5 | 18 | 89.215
10:00 | 3670 | 905 | 2243 | 0 | 627 | 3232 | 157 | 0 | 48 | 136 | 213 | 18 | 39
10:30 | 3708 | 905.5 | 2268 | 0 | 671 | 3265.5 | 157 | 0 | 40 | 136 | 171 | 17 | 19.5
11:00 | 3746 | 906 | 2293 | 0 | 715 | 3299 | 157 | 0 | 32 | 136 | 129 | 16 | 0
11:30 | 3790.5 | 905.5 | 2306 | 0 | 763 | 3345 | 157 | 0 | 24 | 139 | 118.5 | 14 | 0
12:00 | 3835 | 905 | 2319 | 0 | 811 | 3391 | 157 | 0 | 16 | 142 | 108 | 12 | 0
12:30 | 3767 | 905 | 2299 | 0 | 945.5 | 3423.5 | 157 | 0 | 16 | 147 | 180.5 | 12.5 | 0
13:00 | 3699 | 905 | 2279 | 0 | 1080 | 3456 | 157 | 0 | 16 | 152 | 253 | 13 | 0
13:30 | 3699 | 905 | 2279 | 0 | 1080 | 3456 | 157 | 0 | 16 | 152 | 253 | 13 | 0
14:00 | 3699 | 905 | 2279 | 0 | 1080 | 3456 | 157 | 0 | 16 | 152 | 253 | 13 | 0
14:30 | 3543 | 905 | 2156.5 | 0 | 927 | 3311 | 156.5 | 0 | 32 | 141 | 170 | 13 | 0
15:00 | 3387 | 905 | 2034 | 0 | 774 | 3166 | 156 | 0 | 48 | 130 | 87 | 13 | 0
15:30 | 3382.5 | 905.5 | 2099.5 | 0 | 728.5 | 3196.5 | 156.5 | 0 | 48 | 136 | 60 | 9.5 | 0
16:00 | 3378 | 906 | 2165 | 0 | 683 | 3227 | 157 | 0 | 48 | 142 | 33 | 6 | 0
16:30 | 3378 | 905.5 | 2155.5 | 0 | 674 | 3240 | 157 | 0 | 56 | 137 | 27.5 | 4 | 0
17:00 | 3378 | 905 | 2146 | 0 | 665 | 3253 | 157 | 0 | 64 | 132 | 22 | 2 | 0
17:30 | 3419.5 | 905 | 2224 | 0 | 761 | 3381 | 157 | 0 | 66.5 | 139 | 11 | 5.5 | 0
18:00 | 3461 | 905 | 2302 | 0 | 857 | 3509 | 157 | 0 | 69 | 146 | 0 | 9 | 0
18:30 | 3601.5 | 898.5 | 2344 | 0 | 1174 | 3691.5 | 157 | 0 | 99.5 | 145 | 0 | 13 | 0
19:00 | 3742 | 892 | 2386 | 0 | 1491 | 3874 | 157 | 0 | 130 | 144 | 0 | 17 | 0
19:30 | 3747 | 776 | 2402 | 0 | 1598 | 3918 | 157 | 0 | 114 | 142 | 0 | 7 | 0
20:00 | 3746 | 776 | 2394 | 0 | 1587 | 3919 | 156 | 0 | 96 | 152 | 0 | 8 | 0
20:30 | 3692.5 | 775.5 | 2379 | 0 | 1582.5 | 3921.5 | 156.5 | 0 | 96 | 152 | 0 | 10.5 | 0
21:00 | 3639 | 775 | 2364 | 0 | 1578 | 3924 | 157 | 0 | 96 | 152 | 0 | 13 | 0
21:30 | 3606 | 775.5 | 2335.5 | 0 | 1540 | 3929 | 157 | 0 | 96 | 153 | 0 | 9 | 0
22:00 | 3573 | 776 | 2307 | 0 | 1502 | 3934 | 157 | 0 | 96 | 154 | 0 | 5 | 0
22:30 | 3585 | 789 | 2324 | 0 | 1343.5 | 3926 | 157 | 0 | 80 | 155 | 0 | 7.5 | 57.3
23:00 | 3597 | 802 | 2341 | 0 | 1185 | 3918 | 157 | 0 | 64 | 156 | 0 | 10 | 114.6
23:30 | 3605 | 802 | 2361.5 | 0 | 1064 | 3894 | 157 | 0 | 48 | 154 | 0 | 10 | 104.5725 |  |  | Max Temp. in Dhaka |  | 32.8°C
24:00 | 3613 | 802 | 2382 | 0 | 943 | 3870 | 157 | 0 | 32 | 152 | 0 | 10 | 94.545
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 280.954 MKWHr Energy Not Served 1.382 MKWHr Energy Requirement 282.336 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-09-21
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 82 | 82 | 82 | 82 | 82 | 82 | 81 | 82 | 82 | 82 |  | 82 | 82 | 81 | 82 | 82 | 82 | 82 | 2295212
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1812000
3 | Chattogram TPP-1 | 103 | 101 | 105 | 107 | 105 | 101 | 106 | 103 | 108 | 110 | 111 | 100 | 97 | 106 | 100 | 100 | 100 | 105 |  | 103 | 100 | 100 | 103 | 101 | 104 | 104 | 2500000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 0 | [17 empty] | 10 | 17 | 17 | 17 | 17 | 8 | 0 | 87751
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 2 | 4 | 9 |  |  | 19 | 11 | 13 | 5 | 5 | 2 | [9 empty] | 73035
6 | Sikalbaha 225MW CCPP (Gas) | 225 | 223 | 224 | 226 | 226 | 224 | 223 | 223 | 223 | 220 | 218 | 217 | 220 | 222 | 222 | 222 | 223 | 224 |  | 226 | 222 | 224 | 226 | 225 | 225 | 224 | 5213077
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
Dohazari -Kalaish 100 MW Peaking
12 | Hathazari 100 MW peaking PP | [26 empty] | 0
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 51 | 51 | 51 | 51 | 17 | 17 |  |  |  | 5 | 17 | 21 | 51 | 51 | 51 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 797054
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 59 | 38 | 41 | 250 | 331 | 280 | 280 | 280 | 331 | 328 | 321 | 317 | 310 | 270 | 240 | 240 | 240 | 240 |  | 280 | 280 | 280 | 280 | 250 | 250 | 250 | 6102948
18 | Kodda 300 MW PP Unit-2 (Summit) | 15 | 0 | [10 empty] | 42 | 15 | 15 | 15 | 15 | 15 |  | 28 | 32 | 42 | 45 | 45 | 15 | 0 | 398945
19 | Ashuganj 195 MW PP (APSCL-United) | 137 | 137 | 137 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 107 | 107 | 107 | 108 | 108 | 108 |  | 147 | 147 | 147 | 147 | 147 | 148 | 148 | 2927273
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 160 | 160 | 160 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 170 | 160 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3303250
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 612 | 612 | 612 | 612 | 612 | 580 | 500 | 500 | 502 | 500 | 532 | 570 | 600 | 544 | 450 | 510 | 541 | 580 |  | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 13581817
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 47 | 47 | 47 | 47 | 43 | 45 | 46 | 46 | 47 | 48 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1142208
33 | Ashuganj 225 MW CCPP | 211 | 212 | 211 | 211 | 211 | 210 | 210 | 210 | 213 | 210 | 205 | 205 | 213 | 180 | 208 | 210 | 180 | 186 |  | 180 | 179 | 181 | 180 | 181 | 182 | 188 | 4873000
34 | Ashuganj 450 MW CCPP(South) | 275 | 275 | 275 | 270 | 275 | 275 | 330 | 335 | 310 | 280 | 310 | 335 | 310 | 295 | 275 | 285 | 280 | 280 |  | 275 | 275 | 275 | 275 | 275 | 280 | 280 | 7075000
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 310 | 280 | 280 | 280 | 290 | 335 | 310 | 275 | 325 | 335 | 310 | 280 | 280 | 290 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 285 | 285 | 7506100
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 394 | 394 | 394 | 362 | 350 | 345 | 301 | 301 | 380 | 398 | 396 | 398 | 399 | 328 | 321 | 321 | 321 | 322 |  | 386 | 360 | 360 | 361 | 332 | 326 | 326 | 8663040
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 400 | 370 | 370 | 370 | 370 | 400 | 400 | 400 | 450 | 450 | 330 | 330 | 330 | 330 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 9564500
41 | Haripur 360 MW CCPP(HPL) | 337 | 337 | 337 | 302 | 303 | 272 | 273 | 272 | 330 | 330 | 330 | 323 | 313 | 280 | 255 | 277 | 277 | 320 |  | 280 | 285 | 285 | 287 | 257 | 257 | 277 | 7146000
42 | RPCL 210MW CCPP | 72 | 72 | 72 | 72 | 72 | 72 | 29 | 29 | 30 | 28 | 28 | 28 | 12 | 16 | 16 | 17 | 20 | 20 |  | 30 | 32 | 32 | 0 | 44 | 49 | 35 | 851520
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 1 | 5 | 15 | 16 | 31 | 30 | 46 | 17 | 41 | 12 | 0 | [9 empty] | 185470
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 40 | 41 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1014000
45 | Fenchugonj CCPP Phase-2 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 820920
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86 MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 75 | 75 | 77 | 77 | 77 | 80 | 81 | 81 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1914240
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 185 | 184 | 184 | 186 | 184 | 184 | 184 | 184 | 184 | 187 | 185 | 185 | 184 | 183 | 183 | 184 | 184 | 184 |  | 185 | 184 | 185 | 184 | 184 | 184 | 184 | 4764500
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 410000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 238320
54 | Hobiganj 11 MW PP Cofidence-E | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 257856
55 | Fenchugonj 51 MW PP (Barakatullah) | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 47 | 22 | 42 | 49 | 47 |  | 47 | 47 | 50 | 50 | 50 | 47 | 47 | 1080000
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 0 | [17 empty] | 8 | 8 | 8 | 73056
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 290 | 290 | 300 | 275 | 290 | 310 | 300 | 290 | 270 | 300 | 310 | 290 | 260 | 280 | 300 | 290 | 290 |  | 270 | 270 | 275 | 270 | 280 | 285 | 305 | 7048000
| Bibiyana South 400 MW | 400 | 400 | 400 | 365 | 365 | 365 | 365 | 365 | 400 | 400 | 390 | 385 | 365 | 385 | 397 | 394 | 400 | 400 |  | 400 | 400 | 400 | 400 | 400 | 400 | 398 | 9355700
58 | Nababganj 55 MW PP (Southern power ) | [11 empty] | 17 | 17 | 17 |  |  |  | 12 |  | 55 | 55 | 55 | 55 | 17 | 0 | 0 | 238019
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 12 | 395280
60 | Barabkunda 22 MW PP (Regent) | 11 | 11 | 9 | 9 | 9 | 9 | 9 |  | 9 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 218448
61 | Narshingdi 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 16 |  |  | 17 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 392436
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 18 | 18 | 18 | 18 | 18 |  | 19 | 18 | 16 | 16 | 18 | 18 | 18 | 399312
63 | Impoprt (Tripura) | 152 | 148 | 144 | 142 | 140 | 130 | 118 | 116 | 124 | 136 | 136 | 142 | 152 | 142 | 130 | 142 | 132 | 146 |  | 144 | 142 | 152 | 152 | 154 | 156 | 152 | 3362880
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 38 | 38 | 39 | 38 | 36 | 7 | 5 | 6 | 6 | 7 | 10 | 9 | 6 | 10 | 19 | 10 |  | 29 | 29 | 42 | 42 | 42 | 42 | 42 | 653280
65 | Feni 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 432360
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 197640
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 32 | 33 | 33 | 25 | 25 | 32 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 747400
68 | Cumilla 25 MW PP (Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 279100
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456000
70 | Summit Madhabdi | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 17 | 16 | 16 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 16 | 16 | 17 | 18 | 18 | 18 | 405720
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 590500
72 | Rupganj 33 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 23 | 23 | 23 | 23 | 23 | 28 | 28 | 28 | 30 | 30 |  | 30 | 30 | 30 | 32 | 32 | 32 | 32 | 679100
73 | Ghorashal 108 MW PP (Regent) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1245136
| Feni Lanka Power | 105 | 105 | 105 | 105 | 105 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 17 |  | 52 | 17 | 17 | 17 | 17 | 82 | 106 | 988380
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 9 | 9 | 15 | 36 | 36 | 38 | 37 | 38 | 39 | 38 | 76 |  | 95 | 95 | 95 | 95 | 96 | 69 | 16 | 884520
| Manikgonj 162MW PP(MPGL) | 17 | 0 | [6 empty] | 17 | 17 | 17 | 35 | 54 | 54 | 17 | 17 | 17 | 17 |  | 38 | 54 | 17 | 17 | 17 | 17 | 17 | 457920
77 | Siddhirganj 100 PP(Dutch Bangla) | [17 empty] | 5 |  | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 37440
78 | Gazipur 52 MW PP | 8 | 0 | [6 empty] | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 232800
79 | Kodda 150 MW PP | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 48 | 32 | 16 | 16 | 48 | 48 | 48 | 64 | 64 |  | 98 | 82 | 64 | 64 | 64 | 32 | 32 | 882240
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 8 | 8 | 8 |  |  |  | 4 |  | 45 | 52 | 52 | 52 | 52 | 52 | 52 | 620486
| Gazipur 100 MW PP | 17 | 17 | 17 | 0 |  |  |  |  | 1 | 52 | 52 | 52 | 52 | 52 | 35 | 35 | 35 | 35 |  | 70 | 70 | 70 | 70 | 51 | 51 | 17 | 812160
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 2 | 3 | 1 | 1 | 0 | 0 | [9 empty] | 25563
| Jodiac Power | 17 | 17 | 0 | [14 empty] | 12 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 174774
| Karnaphuli Power Ltd. | 55 | 61 | 55 | 55 | 55 | 55 | 78 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 108 | 64 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1907740
82 | Madanganj 102 PP(Summit) | [13 empty] | 10 | 17 | 17 | 17 | 17 |  | 13 | [5 empty] | 0 | 81086
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 290 | 276 | 277 | 266 | 268 | 278 | 285 | 290 | 278 | 298 | 314 | 306 | 262 | 282 | 314 | 304 | 275 | 308 |  | 265 | 275 | 300 | 272 | 274 | 301 | 304 | 6909033
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [8 empty] | 2 | 14 | 17 | 17 | 34 | 68 | 35 | 25 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 372480
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 12 | 0 | [15 empty] | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 88080
92 | Fenchuganj 44 MW (Energyprima) | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 42 | 42 | 42 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 46 | 46 | 1036728
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 10 | 10 | 10 | 10 | 10 | 10 | 24 | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 979768
94 | Gagnagar 102 MW PP (Digital Power) | 40 | 0 | [6 empty] | 8 | 8 | 8 | 32 | 74 | 99 | 25 | 8 | 8 | 8 |  | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 409968
95 | Patenga 50MW PP (Baraka) | 40 | 9 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 10 | 15 | [6 empty] | 17 | 42 | 49 | 50 | 50 | 0 | 0 | 318240
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 0 | [10 empty] | 10 | 15 | 15 | 15 | 15 | 15 | [7 empty] | 0 | 125774
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 0 |  | 500425
101 | Kushiara 163 MW CCPP (KP) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 112 | 80 | 80 | 112 | 112 | 80 | 80 | 112 | 112 | 80 |  | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 2367327
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 2 | 1 | 1 | 1 | 2 | 2 | [11 empty] | 10300
103 | Kamalaghat 54 MW PP(Banco Energy) | [10 empty] | 17 | 17 | 17 | 17 | [6 empty] | 25 | 54 | 54 | 54 | 54 | 35 | 309600
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 58 | 58 | 58 | 95 | 95 | 27 | 19 | 28 |  | 65 | 65 | 65 | 65 | 65 | 20 | 18 | 1447200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 85 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 82 | 107 | 107 | 107 | 106 | 54 | 17 | 17 | 17 | 24 |  | 100 | 100 | 106 | 107 | 107 | 58 | 24 | 1366128
115 | Juldah 100 MW PP Unit-3 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | [11 empty] | 12 |  | 20 | 50 | 50 | 50 | 50 | 50 | 25 | 339840
116 | Chandpur 200 MW (Desh energy) | 34 | 34 | 34 | 34 | 34 | 34 | 29 | 17 | 21 | 68 | 68 | 68 | 68 | 68 | 17 | 18 | 51 | 60 |  | 100 | 100 | 100 | 104 | 104 | 104 | 73 | 1372800
117 | Ashuganj 150 MW PP (Midland) | 6 | 0 | [6 empty] | 1 | 3 | 6 | 5 | 28 | 50 | 53 | 56 | 58 | 6 |  | 6 | 6 | 6 | 6 | 5 | 6 | 5 | 347927
118 | Bibiyana-III 400 MW CCPP | 368 | 368 | 367 | 367 | 320 | 320 | 320 | 320 | 368 | 368 | 400 | 398 | 368 | 319 | 316 | 325 | 320 | 364 |  | 401 | 401 | 402 | 368 | 368 | 368 | 378 | 8572000
| Jamalpur 115 MW PP (United) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 56 | 56 | 59 | 59 | 59 | 68 | 68 | 55 |  | 93 | 97 | 98 | 99 | 100 | 71 | 69 | 1171200
| Anwara 300 MW PP (United) | 70 | 68 | 68 | 69 | 15 | 15 | [5 empty] | 15 | 60 | 60 | 30 | 30 | 30 | 60 |  | 100 | 85 | 65 | 65 | 65 | 65 | 65 | 1156691
| Juldah unit-2 (Acorn) | 12 | 12 | 0 | [14 empty] | 12 |  | 45 | 50 | 50 | 50 | 50 | 50 | 50 | 307200
| Anlima Energy Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | [5 empty] | 3 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 327436
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 20 | 17 | 17 | 17 | 8 |  | 12 | 17 | 17 | 6 |  | 9 | 17 | 17 |  | 20 | 35 | 35 | 35 | 35 | 35 | 35 | 553320
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 5 | 16 | 21 | 18 | 21 |  | 18 | 0 | 2 | 2 | 1 | [9 empty] | 87072
| Chandpur 115(Doreen) | [25 empty] | 0 | 0
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 32 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 17 | 790560
Mirsharai 150 MW (Oil)
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 11 | 10 | 13 | 12 | 15 | 13 | 8 | 7 | 18 | 18 | 16 | 12 | 13 | 25 | 13 | 6 | 2 | 9 |  | 17 | 7 | 8 | 13 | 5 | 10 | 10 | 300480
Matarbari 2*600 MW (CPGCL)
120 | Eastern Zone Total | 6865 | 6599 | 6527 | 6476 | 6346 | 6148 | 6003 | 6046 | 6441 | 6584 | 6827 | 7053 | 7175 | 6715 | 6241 | 6260 | 6238 | 6653 |  | 7388 | 7417 | 7438 | 7364 | 7278 | 7066 | 6844 | 162441089
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 0 | [9 empty] | 10 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 219840
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 54 | 0 | [9 empty] | 5 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 18 | 35 | 301440
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 1 | 26 | 26 | 36 | 75 | 22 | 11 | 27 | 11 | 18 | 10 | 7 | [9 empty] | 303840
131 | Rampal 1320 MW (BIFPCL) | 516 | 522 | 524 | 522 | 525 | 526 | 525 | 524 | 525 | 521 | 523 | 520 | 520 | 520 | 523 | 522 | 522 | 568 |  | 573 | 571 | 571 | 571 | 572 | 572 | 571 | 12865450
132 | United Payra Power Ltd. | [17 empty] | 6 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 116400
133 | Bhola Nutan Biddut BD LTD (GAS) | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 |  | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 2611964
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [19 empty] | 16 | 16 | 16 | 16 | 0 |  | 0 | 44352
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 90 | 84 | 90 | 90 | 90 | 90 | 90 | 90 | 80 | 90 | 90 | 130 | 120 | 120 | 80 | 80 | 80 | 80 |  | 124 | 124 | 130 | 124 | 124 | 130 | 132 | 2477000
140 | Bhola 33 MW PP (Venture) | 28 | 28 | 25 | 25 | 24 | 22 | 22 | 20 | 18 | 18 | 21 | 19 | 20 | 20 | 20 | 18 | 20 | 24 |  | 27 | 28 | 28 | 29 | 30 | 31 | 29 | 565127
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 8 |  | 8 | 8 | 8 |  |  |  | 0 | 26625
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [17 empty] | 15 |  | 15 | 15 | 15 | 4 | 0 |  | 0 | 52704
146 | Bheramara HVDC | 905 | 905 | 905 | 906 | 906 | 905 | 900 | 905 | 905 | 905 | 906 | 905 | 905 | 906 | 905 | 906 | 905 | 905 |  | 892 | 776 | 776 | 775 | 776 | 802 | 802 | 21111272
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 1200 | 1200 | 1040 | 1030 | 1010 | 960 | 900 | 900 | 940 | 940 | 960 | 1020 | 1050 | 1050 | 900 | 900 | 900 | 940 |  | 1200 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 27346000
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4344500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [26 empty] | 0
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 3 | 3 | 2 | 5 | 3 | 2 | 3 | 0 | 0 | 0 | [9 empty] | 23400
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 170 | 170 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 199 | 202 | 200 | 190 | 150 | 155 | 170 | 3957518
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 173 | 173 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 142 |  | 176 | 211 | 202 | 170 | 150 | 150 | 150 | 3907482
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 350 | 350 | 350 | 350 | 300 | 300 | 300 | 300 | 350 | 350 | 350 | 300 | 330 | 330 | 280 | 320 | 320 | 320 |  | 414 | 414 | 360 | 360 | 320 | 320 | 320 | 8275818
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 172044
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [17 empty] | 5 |  | 32 | 32 | 32 | 32 | 32 | 32 | 0 | 154910
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [19 empty] | 18 | 35 | 35 | 35 | 35 |  | 0 | 153312
172 | Confidence Power Bogura Unit-1 113 MW | [25 empty] | 0 | 0
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 0 | [14 empty] | 32 |  | 60 | 75 | 85 | 85 | 85 | 34 | 34 | 456892
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | [8 empty] | 8349
178 | Energypac Power Venture Thakurgaon Ltd. | 36 | 17 | 0 | [14 empty] | 6 |  | 35 | 35 | 35 | 35 | 35 | 36 | 37 | 297792
| Intraco Solar 30 MW | [5 empty] | 0 | 0 | 3 | 3 | 6 | 1 | 1 | 9 | 16 | 6 | 0 | 1 | 0 | [8 empty] | 46142
| Adani Power Jharkhanda Ltd | 1256 | 1262 | 1258 | 1263 | 1210 | 1124 | 1110 | 1108 | 1101 | 1091 | 1104 | 1101 | 1106 | 1120 | 1113 | 1115 | 1110 | 1241 |  | 1309 | 1311 | 1312 | 1317 | 1326 | 1310 | 1263 | 28249091
178 | Teesta Solar Limited | [6 empty] | 2 | 23 | 4 | 90 | 42 | 40 | 135 | 134 | 11 | 3 | 10 | [9 empty] | 423410