## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-09-27 | Wednesday
|  | Date (day): | 2023-09-27 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 15114.6 | MW |  |  | (b) At Evening Peak Hour : |  | 17046 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-09-26 | 2023-09-27 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 150 | 155 | 155 | 25 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  |  | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 53 | 52 | 53 | 53 | 55 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 405 | 414 | 412 | 412
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 322 | 332 | 330 | 330 | 30
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 72 | 82 | 18 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 310 | 289 | 310 | 310 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 17 | 85 | 85 | 85 |  | 17 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 30 | 15 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 55 | 55 | 20 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 20 | 20 | 20
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 8 | 92 | 92 |  | 8 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 308 | 160 | 200 | 210
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 40 | 91 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 35 | 17 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 142 | 48 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 55 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 38 | 35 | 38 | 38 |  | 42 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 14 | 30 | 30
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 25 | 8 | 25 | 27 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 38 | 145 | 300 | 300
32 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
33 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
34 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 120 | 17 | 149
35 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 88 | 35 | 88
36 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 18 | 72 | 54 | 72 | 32 |  | Fuel shortage
37 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 90 | 54 | 108 | 54 |  | Fuel shortage
38 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 35 | 0 | 35 | 0
39 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 34 | 54 | 17 | 54
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 5763 | 5422 | 2571 | 2996 | 3119 | 3574 | 666 | 835
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 103 | 100 | 100 | 75 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
41 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 17 | 8 | 17 | 8 |  | Fuel shortage
42 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 13 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 40 | 6 | 40
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 200 | 202 | 196 | 196
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 225 | 225 | 225
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 24 | 51 | 51 | 51 | 54 |  | Fuel shortage
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 71 | 40 | 64 | 34 |  | Fuel shortage
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 | 102 |  | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 58 | 70 | 70 | 30 |  | Fuel shortage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 37 | 50 | 25 | 50 | 50 |  | Fuel shortage
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 9 | 11 | 11 | 11 | 11 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 14 | 7 | 25
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 60 | 282 | 120 | 285 |  | 15 | Engine problem
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 54 | 17 | 54
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 34 | 55 | 55 | 55 | 55 |  | Fuel shortage
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 50 | 38 | 63 | 37 |  | Fuel shortage
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 34 | 51 | 34 | 51 | 65 |  | Fuel shortage
60 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 0 | 54 | 150
| SS Power I |  | Coal | SS Power | 0 | 0 | 0 | 612 | 550 | 350 | 350 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 0 | 0 | 10 | 20 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 0 | 42 | 600 | 600 |  |  | On test.
| Chattogram area Total |  |  |  |  | 2605 | 2545 | 1363 | 1926 | 2042 | 2477 | 629 | 345
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 187 | 208 | 200 | 200 | 21 |  | Gas shortage
62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 290 | 330 | 330 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 270 | 330 | 330 |  |  | FGMO
64 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 47 | 48 | 50 | 50
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 86 | 145 | 78 | 145 | 50 |  | Gas shortae
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 50 |  |  | Gas shortage
69 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 2 | 107 | 50 | 150
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 31 |  | 21 | Machine problem
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
72 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 68 | 86 | 68 | 85 | 115 |  | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 0 | 18 | 18 |  | 4 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 154 | 152 | 149 | 165
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 52 | 52 | 52
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 105 | 105 | 105 |  | 9 | Engine problem
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 31 | 86 | 27 | 85 | 28 |  | Fuel shortage
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 35 | 17 | 34 |  | 20 | Engine problem
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 52 | 52 | 34 | 50 | 65 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2896 | 1438 | 1742 | 1614 | 1935 | 279 | 630
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 28 | 30 | 43 | 43 | 159 |  | Gas shortage
83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 18 | 18 |  | 4 | Engine problem
84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 98 | 153 | 115 | 159 | 41 |  | Fuel shortage
87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 56 | 94 | 37 | 104 | 11 |  | Fuel shortage
88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 24 | 0 | 50 | 0
89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 13 | 18 | 18 | 18 | 4 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 220 | 295 | 282.6 | 342 | 159 | 4
90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 40 | 43 | 43 | 43 |  | 27 | Machine problem.
91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 40 | 40 |  | 50 | Machine problem
92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 112 | 112 |  | 51 | ST Under maint.
93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 50 | 50
95 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 47 | 47 | 40 | 46 |  | 4 | Engine problem
96 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 5 | 11 | 11
97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 66 |  | Gas shortage
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 86 | 86 | 86
99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 184 | 182 | 185 | 185 |  | 46 | Machine problem
101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 16 | 17 | 17 | 17
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 | 17 |  | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 260 | 300 | 300 |  |  | FGMO
104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 403 | 409 | 400 | 400 |  |  | FGMO
105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 379 | 397 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1660 | 1656 | 1702 | 1708 | 83 | 608
107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 909 | 778 | 938 | 938
108 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 82 | 32 | 82 | 33 |  | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 40 |  | 14 | Engine problem
110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 | 69 |  | Fuel shortage
112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
113 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 0 | 16 | 24 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
114 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 6 | 41 | 54 | 72 | 33 |  | Fuel shortage
115 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 100 | 100
116 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 99 | 0 | 100 | 0
117 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
118 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 520 | 520 | 520 | 520
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3125 | 3121 | 1550 | 1444 | 1769 | 1808 | 1035 | 14
119 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 16 | 110
120 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 23 | 28 | 23 | 25 |  | 15 | Engine problem
121 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 66 | 62 | 65 | 65 |  | 129 | GT-2 & ST under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
122 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1040 | 1232 | 1244 | 1244
123 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 223 | 220 | 220 | 220
124 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 35 | 150
125 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 150 | 307 | 300 | 300
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1502 | 1882 | 1903 | 2114 | 0 | 144
126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 38 | 0 | 38 | 14 |  | Fuel shortage
128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 0 |  | 71 | Engine problem
129 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 28 | 28 |  |  | Fuel shortage
130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 34 | 42 | 8 |  | Fuel shortage
131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 30 | 40 | 10 |  | Fuel shortage
132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 140 | 181 | 150 | 180 | 30 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 130 | 186 | 150 | 180 | 40 |  | Gas shortage
135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 330 | 360 | 360 | 400
136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 24 | 32 | 18 |  | Fuel shortage
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 52 | 0 |  | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 40 | 50 | 91 |  | 13 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 90 | 90 | 90 | 23 |  | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 35 | 113 | 0 |  | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1164 | 1216 | 1300 | 1400
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 1777 | 2304 | 2265 | 2694 | 734 | 87
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 180 | 180 | 180 | 180 |  | 94 | Machine problem
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 99 | 35 | 99 | 14 |  | Fuel shortage
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 108 | 35 | 115
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 127 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 348 | 387 | 418 | 394 | 139 | 179
| Total |  |  |  |  | 24611 | 23871 | 12429 | 14632 | 15114.6 | 17046 | 3724 | 2846
A. |  | 2023-09-26 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 14632 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
2 | Minimum Generation : |  |  | 10877 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14750 | MW
3 | Day peak Generation : |  |  | 12429 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14133.93 | MW
4 | Evening peak Generation : |  |  | 14632 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 113 | MW
5 | Total Energy Generation : |  | 305.5378 | MKWHr | By Solar | 2.8132 | MKWHr
| By Gas : | 144.039 | MKWHr |  | By Oil: | 35.2953 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 93.6116 | MKWHr |  | By Hydro: | 4.6517 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.04656 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3724 | MW | Dhaka | 5017.33 | 4995.33 |  | 22 |  | 18:00 |  | 251
|  |  | For Plants S/D or M/C prob = |  |  | 2846 | MW | Chittagong | 1338.5 | 1338.5 |  | 0 |  | 19:00 |  | 229.2
|  |  | Total = |  |  | 6570 | MW | Khulna | 1743.7 | 1743.7 |  | 0 |  | 19:30 |  | 110.78
7 | Total Gas Supplied : |  |  | 1086.75 | MMCFD |  |  | Rajshahi | 1466.4 | 1466.4 |  | 0 |  | 20:00 |  | 112.69
8 | Fuel Cost : | i) Gas : | Taka | 162018203.998 | ii) Oil : | Taka | 465150961.03 | Comilla | 1373 | 1358 |  | 15 |  | 21:00 |  | 132.745
|  | iii) Coal : | Taka | 692978649.9 | Total | Taka | 1320147814.928 | Mymensingh | 1209 | 1161 |  | 48 |  | 22:00 |  | 185.27
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 619 | 591 |  | 28 |  | 23:00 |  | 372.45
| ii) During Peak Demand : |  |  | 1010 | MW (W to E) at | 20:00 | hrs | Barisal | 441 | 441 |  | 0 |  | 24:00 |  | 399.19
| iii) Maximum : |  |  | 1010 | MW at | 18:30 | hrs | Rangpur | 926 | 926 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 32.5°C |  |  | Total | 14133.93 | 14020.93 |  | 113
B. |  | 2023-09-27 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 32.5°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 15000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 17046 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 13000 | MW
4 | Reserve(Generation end) |  |  |  | 2046 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 313.2222 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11405 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.616 | MKWHr. | ii) HVDC Flow at Peak Time |  | 778 | MW at | 20:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.4646 | MKWHr. | iii) Maximum HVDC Flow : |  | 910 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 107.83 |  | (b) Today: | 107.77 |  | (c) Rule Curve: |  | 105.04
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-09-26 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 388 | 301 |  | 0 | 450 | 275 | 0 | 1 | 0 | 324 | 0 | 0 | 0 | 50 | 23 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 19 | 16 | 25 | 30 | 8 | 0 | 126 | 75 | 100 | 0 | 8 | 224 | 0 | 0 | 0 |  | 12 | 0 | 0 | 58 | 0 | 6 | 9 | 39 | 0 | 0 | 0 | 315 | 315 | 211 | 88 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 0 | 144 | 70 | 0 | 18 | 0 | 43 | 30 | 47 | 49 | 112 | 0 | 0 | 81 | 0 | 183 | 17 | 0 | 10 | 290 | 8 | 8 | 0 | 0 | 0 | 0 | 69 | 0 | 35 | 0 | 25 | 34 | 10 | 404 | 19 | 34 | 51 | 0 | 70 | 17 | 55 | 105 | 9 | 25 | 396 | 35 | 0 | 17 | 17 | 0 | 35 | 0 | 53 | 17 | 0 | 0 | 0 | 528 | 0 | 0 | 0 | 0 |  | 910 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 380 | 35 | 0 | 0 | 15 | 49 | 0 | 0 | 0 | 1100 | 180 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 521 | 0 | 260 | 1262 | 0 | 0 |  | 7118 | 5445 | 12563 | 3891 | 910 | 2435 | 0 | 1108 | 3851 | 201 | 0 | 23 | 144 | 0 | 0 | 274.085 | 107.85
2:00 | 0 | 0 | 130 | 0 | 0 | 12 | 0 | 405 | 303 |  | 0 | 450 | 283 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 18 | 25 | 30 | 8 | 0 | 126 | 75 | 90 | 0 | 8 | 224 | 0 | 0 | 0 |  | 12 | 0 | 0 | 58 | 0 | 6 | 9 | 34 | 0 | 0 | 0 | 280 | 280 | 210 | 68 | 0 | 50 | 0 | 0 | 10 | 0 | 0 | 52 | 18 | 10 | 33 | 0 | 142 | 70 | 0 | 18 | 0 | 43 | 30 | 47 | 49 | 112 | 0 | 0 | 81 | 0 | 183 | 17 | 0 | 10 | 275 | 8 | 8 | 0 | 0 | 0 | 0 | 69 | 0 | 35 | 0 | 25 | 34 | 0 | 403 | 19 | 17 | 51 | 0 | 70 | 17 | 55 | 105 | 9 | 25 | 397 | 17 | 0 | 17 | 17 | 0 | 35 | 0 | 53 | 17 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 0 |  | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 380 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 522 | 0 | 205 | 1264 | 0 | 0 |  | 6895 | 5152 | 12047 | 3698 | 910 | 2323 | 0 | 874 | 3883 | 201 | 0 | 16 | 142 | 0 | 0 | 241.615 | 107.85
3:00 | 0 | 0 | 130 | 0 | 0 | 12 | 0 | 406 | 302 |  | 0 | 450 | 277 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 25 | 31 | 8 | 0 | 126 | 75 | 100 | 0 | 8 | 224 | 0 | 0 | 0 |  | 12 | 0 | 0 | 58 | 0 | 6 | 9 | 40 | 0 | 0 | 0 | 280 | 280 | 180 | 68 | 0 | 50 | 0 | 0 | 10 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 140 | 69 | 0 | 18 | 0 | 43 | 30 | 47 | 49 | 80 | 0 | 0 | 81 | 0 | 183 | 17 | 0 | 10 | 280 | 8 | 8 | 0 | 0 | 0 | 0 | 69 | 0 | 35 | 0 | 25 | 34 | 0 | 403 | 19 | 17 | 40 | 0 | 70 | 0 | 55 | 105 | 9 | 25 | 398 | 22 | 0 | 17 | 17 | 0 | 35 | 0 | 50 | 17 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 0 |  | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 380 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 0 | 153 | 1213 | 0 | 0 |  | 6834 | 5046 | 11880 | 3693 | 910 | 2294 | 0 | 848 | 3778 | 201 | 0 | 16 | 140 | 0 | 0 | 210.1 | 107.84
4:00 | 0 | 0 | 130 | 0 | 0 | 12 | 0 | 405 | 302 |  | 0 | 400 | 299 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 25 | 32 | 8 | 0 | 0 | 75 | 100 | 0 | 8 | 222 | 0 | 0 | 0 |  | 12 | 0 | 0 | 58 | 0 | 6 | 9 | 40 | 0 | 0 | 0 | 290 | 285 | 187 | 68 | 0 | 50 | 0 | 0 | 10 | 0 | 0 | 25 | 18 | 10 | 33 | 12 | 138 | 35 | 0 | 18 | 0 | 43 | 30 | 47 | 49 | 80 | 0 | 0 | 81 | 0 | 183 | 17 | 0 | 10 | 285 | 8 | 8 | 0 | 0 | 0 | 0 | 69 | 0 | 35 | 0 | 25 | 34 | 0 | 403 | 19 | 0 | 40 | 0 | 70 | 0 | 55 | 105 | 9 | 25 | 395 | 34 | 0 | 0 | 17 | 0 | 35 | 0 | 54 | 17 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 0 |  | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 380 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1020 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 518 | 0 | 150 | 1216 | 0 | 0 |  | 6577 | 4944 | 11521 | 3632 | 909 | 2270 | 0 | 785 | 3696 | 75 | 0 | 16 | 138 | 0 | 0 | 170.945 | 107.84
5:00 | 0 | 0 | 130 | 0 | 0 | 12 | 0 | 395 | 302 |  | 0 | 340 | 286 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 25 | 32 | 8 | 0 | 92 | 75 | 100 | 0 | 8 | 223 | 0 | 0 | 0 |  | 12 | 0 | 0 | 58 | 0 | 6 | 9 | 40 | 0 | 0 | 0 | 280 | 280 | 180 | 68 | 0 | 50 | 0 | 0 | 10 | 0 | 0 | 25 | 18 | 10 | 33 | 12 | 136 | 34 | 0 | 18 | 0 | 43 | 30 | 47 | 49 | 80 | 0 | 0 | 78 | 0 | 183 | 17 | 0 | 10 | 280 | 8 | 8 | 0 | 0 | 0 | 0 | 69 | 0 | 35 | 0 | 25 | 34 | 0 | 403 | 19 | 0 | 51 | 0 | 70 | 0 | 55 | 105 | 9 | 25 | 360 | 34 | 0 | 0 | 17 | 0 | 35 | 0 | 53 | 17 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 0 |  | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 980 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 521 | 0 | 150 | 1217 | 0 | 0 |  | 6521 | 4821 | 11342 | 3536 | 909 | 2148 | 0 | 770 | 3660 | 167 | 0 | 16 | 136 | 0 | 0 | 122.24 | 107.83
6:00 | 0 | 0 | 130 | 0 | 0 | 12 | 0 | 350 | 262 |  | 0 | 320 | 291 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 0 | 32 | 8 | 0 | 92 | 75 | 110 | 0 | 0 | 222 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 5 | 9 | 40 | 0 | 0 | 0 | 280 | 280 | 180 | 68 | 0 | 50 | 0 | 0 | 10 | 0 | 0 | 25 | 18 | 10 | 33 | 12 | 128 | 34 | 0 | 18 | 0 | 43 | 30 | 47 | 49 | 80 | 0 | 0 | 78 | 0 | 183 | 17 | 0 | 10 | 290 | 8 | 8 | 0 | 0 | 0 | 0 | 69 | 0 | 35 | 0 | 25 | 34 | 0 | 351 | 19 | 0 | 51 | 0 | 15 | 1 | 55 | 78 | 9 | 12 | 360 | 34 | 0 | 0 | 17 | 0 | 35 | 0 | 54 | 17 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 0 |  | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 940 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 522 | 0 | 150 | 1202 | 2 | 0 |  | 6165 | 4727 | 10892 | 3393 | 909 | 2061 | 0 | 610 | 3606 | 167 | 0 | 16 | 128 | 2 | 0 | 103.14 | 107.83
7:00 | 0 | 0 | 130 | 0 | 0 | 12 | 0 | 306 | 262 |  | 0 | 320 | 281 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 17 | 30 | 8 | 0 | 92 | 75 | 100 | 0 | 0 | 225 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 9 | 38 | 0 | 0 | 0 | 320 | 335 | 180 | 68 | 0 | 50 | 0 | 0 | 10 | 0 | 0 | 25 | 18 | 10 | 33 | 12 | 120 | 34 | 0 | 16 | 0 | 43 | 30 | 47 | 49 | 80 | 0 | 0 | 78 | 0 | 183 | 17 | 0 | 10 | 280 | 8 | 8 | 0 | 0 | 0 | 0 | 69 | 0 | 35 | 2 | 25 | 34 | 0 | 352 | 19 | 17 | 17 | 1 | 15 | 17 | 55 | 52 | 9 | 0 | 360 | 17 | 9 | 0 | 17 | 0 | 35 | 3 | 53 | 26 | 0 | 0 | 0 | 612 | 2 | 0 | 0 | 0 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 930 | 180 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 523 | 0 | 150 | 1164 | 32 | 0 |  | 6157 | 4720 | 10877 | 3451 | 908 | 2037 | 0 | 557 | 3559 | 167 | 0 | 16 | 120 | 60 | 2 | 165.215 | 107.82
8:00 | 0 | 0 | 130 | 0 | 0 | 12 | 0 | 306 | 262 |  | 0 | 320 | 310 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 19 | 25 | 30 | 8 | 0 | 127 | 75 | 102 | 0 | 0 | 219 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 9 | 11 | 0 | 0 | 0 | 345 | 310 | 202 | 68 | 0 | 50 | 0 | 0 | 10 | 0 | 0 | 25 | 18 | 10 | 33 | 12 | 126 | 34 | 0 | 16 | 1 | 43 | 30 | 47 | 49 | 80 | 0 | 0 | 78 | 0 | 183 | 17 | 0 | 10 | 290 | 8 | 11 | 0 | 0 | 0 | 0 | 69 | 0 | 35 | 6 | 25 | 34 | 0 | 352 | 19 | 17 | 17 | 2 | 15 | 17 | 55 | 17 | 9 | 0 | 360 | 17 | 26 | 0 | 17 | 0 | 28 | 12 | 55 | 34 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 0 |  | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 940 | 185 | 0 | 0 | 2 | 36 | 0 | 0 | 0 | 523 | 1 | 150 | 1164 | 50 | 0 |  | 6237 | 4779 | 11016 | 3480 | 909 | 2052 | 0 | 525 | 3569 | 202 | 0 | 16 | 126 | 137 | 0 | 166.17 | 107.82
9:00 | 0 | 0 | 130 | 0 | 0 | 12 | 0 | 350 | 292 |  | 0 | 320 | 312 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 19 | 19 | 25 | 28 | 8 | 0 | 127 | 75 | 99 | 0 | 0 | 218 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 9 | 4 | 0 | 0 | 0 | 335 | 305 | 196 | 68 | 0 | 49 | 0 | 0 | 10 | 0 | 0 | 25 | 18 | 10 | 33 | 0 | 136 | 29 | 0 | 16 | 2 | 43 | 30 | 47 | 49 | 80 | 0 | 0 | 78 | 0 | 183 | 17 | 0 | 10 | 305 | 8 | 11 | 0 | 0 | 0 | 0 | 68 | 0 | 35 | 16 | 25 | 34 | 0 | 404 | 19 | 52 | 17 | 2 | 15 | 17 | 55 | 17 | 9 | 0 | 360 | 17 | 38 | 0 | 17 | 0 | 17 | 25 | 54 | 34 | 0 | 0 | 0 | 612 | 1 | 0 | 0 | 0 |  | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 940 | 185 | 0 | 0 | 4 | 67 | 0 | 0 | 0 | 521 | 1 | 150 | 1160 | 135 | 0 |  | 6420 | 4891 | 11311 | 3531 | 909 | 2091 | 0 | 570 | 3563 | 202 | 0 | 16 | 136 | 292 | 1 | 180.495 | 107.81
10:00 | 0 | 0 | 130 | 0 | 0 | 40 | 0 | 390 | 331 |  | 0 | 400 | 298 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 7 | 19 | 19 | 25 | 28 | 8 | 0 | 126 | 75 | 100 | 0 | 0 | 222 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 9 | 4 | 0 | 0 | 0 | 315 | 310 | 181 | 68 | 0 | 45 | 0 | 0 | 35 | 0 | 0 | 25 | 16 | 10 | 33 | 0 | 148 | 28 | 0 | 16 | 1 | 43 | 30 | 44 | 46 | 112 | 0 | 0 | 78 | 0 | 184 | 17 | 0 | 10 | 305 | 8 | 11 | 0 | 0 | 0 | 0 | 68 | 0 | 35 | 19 | 25 | 34 | 0 | 404 | 19 | 52 | 17 | 4 | 15 | 17 | 55 | 17 | 29 | 0 | 390 | 17 | 42 | 17 | 17 | 0 | 8 | 30 | 54 | 34 | 0 | 0 | 0 | 612 | 1 | 0 | 0 | 0 |  | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 940 | 220 | 0 | 0 | 2 | 83 | 0 | 0 | 0 | 521 | 6 | 150 | 1150 | 157 | 0 |  | 6808 | 4986 | 11794 | 3648 | 909 | 2310 | 0 | 632 | 3553 | 201 | 0 | 42 | 148 | 350 | 1 | 53.48 | 107.81
11:00 | 0 | 0 | 130 | 0 | 0 | 51 | 0 | 408 | 322 |  | 0 | 400 | 307 | 0 | 2 | 0 | 312 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 19 | 19 | 25 | 28 | 8 | 0 | 126 | 75 | 102 | 0 | 0 | 215 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 9 | 3 | 0 | 0 | 0 | 320 | 310 | 182 | 86 | 0 | 47 | 0 | 0 | 51 | 0 | 0 | 25 | 16 | 10 | 33 | 0 | 148 | 28 | 0 | 0 | 2 | 42 | 30 | 44 | 48 | 112 | 0 | 0 | 78 | 0 | 184 | 17 | 0 | 10 | 285 | 8 | 11 | 0 | 1 | 0 | 0 | 106 | 0 | 19 | 20 | 37 | 38 | 1 | 405 | 47 | 52 | 17 | 5 | 15 | 17 | 55 | 17 | 28 | 12 | 380 | 17 | 53 | 54 | 34 | 0 | 17 | 32 | 50 | 34 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 0 |  | 909 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 260 | 1 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 990 | 220 | 0 | 0 | 5 | 96 | 0 | 0 | 0 | 521 | 34 | 150 | 1158 | 176 | 0 |  | 7043 | 5088 | 12131 | 3653 | 909 | 2299 | 0 | 833 | 3611 | 201 | 0 | 48 | 148 | 429 | 0 | 0 | 107.8
12:00 | 0 | 0 | 150 | 0 | 0 | 53 | 0 | 405 | 322 |  | 0 | 450 | 310 | 0 | 17 | 15 | 308 | 0 | 0 | 0 | 40 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 19 | 19 | 25 | 28 | 8 | 0 | 125 | 75 | 100 | 0 | 0 | 214 | 0 | 0 | 0 |  | 13 | 0 | 0 | 0 | 0 | 0 | 9 | 5 | 0 | 0 | 0 | 320 | 310 | 187 | 86 | 0 | 47 | 0 | 0 | 51 | 0 | 0 | 25 | 16 | 10 | 33 | 12 | 154 | 28 | 0 | 0 | 1 | 40 | 30 | 47 | 47 | 112 | 0 | 0 | 78 | 0 | 184 | 16 | 0 | 10 | 295 | 8 | 11 | 0 | 38 | 0 | 0 | 98 | 0 | 17 | 13 | 37 | 68 | 2 | 403 | 56 | 52 | 24 | 4 | 60 | 17 | 34 | 17 | 31 | 0 | 379 | 18 | 24 | 54 | 34 | 0 | 17 | 35 | 52 | 34 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 0 |  | 909 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 330 | 6 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1040 | 223 | 0 | 0 | 5 | 99 | 0 | 0 | 0 | 520 | 34 | 150 | 1164 | 127 | 0 |  | 7252 | 5177 | 12429 | 3674 | 909 | 2442 | 0 | 987 | 3666 | 200 | 0 | 48 | 154 | 349 | 0 | 0 | 107.8
13:00 | 0 | 0 | 150 | 0 | 0 | 51 | 0 | 403 | 298 |  | 0 | 450 | 266 | 1 | 17 | 15 | 305 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 19 | 17 | 25 | 20 | 8 | 0 | 125 | 75 | 100 | 0 | 0 | 217 | 0 | 0 | 0 |  | 8 | 0 | 0 | 0 | 0 | 0 | 9 | 7 | 0 | 0 | 0 | 315 | 310 | 181 | 88 | 0 | 47 | 0 | 0 | 51 | 0 | 0 | 25 | 17 | 8 | 33 | 12 | 158 | 12 | 0 | 0 | 1 | 40 | 30 | 50 | 46 | 112 | 0 | 0 | 78 | 0 | 184 | 17 | 0 | 10 | 295 | 8 | 11 | 0 | 45 | 0 | 0 | 97 | 0 | 17 | 20 | 37 | 68 | 2 | 403 | 56 | 52 | 34 | 4 | 100 | 17 | 49 | 17 | 32 | 0 | 387 | 40 | 51 | 72 | 34 | 0 | 31 | 33 | 53 | 34 | 0 | 0 | 0 | 590 | 0 | 0 | 0 | 0 |  | 909 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 414 | 17 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1160 | 216 | 0 | 0 | 5 | 93 | 0 | 0 | 0 | 520 | 36 | 150 | 1171 | 153 | 0 |  | 7304 | 5450 | 12754 | 3679 | 909 | 2455 | 0 | 1121 | 3771 | 200 | 0 | 58 | 158 | 403 | 0 | 0 | 107.79
14:00 | 0 | 0 | 150 | 0 | 0 | 51 | 0 | 358 | 291 |  | 0 | 370 | 307 | 3 | 17 | 15 | 144 | 0 | 0 | 0 | 58 | 58 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 19 | 16 | 25 | 20 | 8 | 0 | 125 | 75 | 98 | 0 | 0 | 214 | 0 | 0 | 0 |  | 12 | 15 | 0 | 46 | 0 | 3 | 10 | 6 | 0 | 0 | 0 | 340 | 285 | 194 | 88 | 0 | 43 | 0 | 0 | 51 | 0 | 0 | 25 | 17 | 8 | 33 | 12 | 160 | 12 | 0 | 0 | 2 | 40 | 30 | 50 | 46 | 80 | 0 | 0 | 78 | 0 | 184 | 17 | 0 | 10 | 300 | 8 | 11 | 0 | 45 | 0 | 0 | 97 | 0 | 17 | 17 | 37 | 68 | 2 | 397 | 56 | 35 | 51 | 3 | 100 | 17 | 55 | 88 | 34 | 22 | 380 | 58 | 8 | 72 | 34 | 0 | 35 | 29 | 52 | 34 | 0 | 0 | 0 | 520 | 2 | 0 | 0 | 0 |  | 908 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 414 | 17 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1200 | 220 | 0 | 0 | 5 | 83 | 0 | 0 | 0 | 520 | 31 | 150 | 1159 | 177 | 0 |  | 7109 | 5495 | 12604 | 3468 | 908 | 2386 | 0 | 1316 | 3729 | 200 | 0 | 73 | 160 | 362 | 2 | 0 | 107.8
15:00 | 0 | 0 | 147 | 0 | 0 | 51 | 0 | 394 | 321 |  | 0 | 450 | 313 | 7 | 17 | 15 | 203 | 0 | 0 | 2 | 58 | 47 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 19 | 16 | 25 | 16 | 8 | 0 | 125 | 75 | 105 | 0 | 5 | 217 | 0 | 0 | 0 |  | 12 | 32 | 0 | 47 | 0 | 6 | 10 | 3 | 0 | 0 | 0 | 315 | 270 | 183 | 107 | 0 | 43 | 0 | 0 | 51 | 0 | 0 | 25 | 17 | 8 | 33 | 12 | 156 | 12 | 0 | 0 | 1 | 40 | 30 | 47 | 46 | 112 | 0 | 0 | 78 | 0 | 184 | 17 | 0 | 10 | 295 | 8 | 11 | 0 | 45 | 0 | 0 | 94 | 0 | 17 | 0 | 37 | 68 | 13 | 400 | 56 | 35 | 51 | 3 | 120 | 17 | 55 | 105 | 32 | 38 | 380 | 72 | 38 | 72 | 34 | 0 | 35 | 23 | 52 | 34 | 0 | 0 | 0 | 520 | 7 | 0 | 0 | 0 |  | 909 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 414 | 22 | 0 | 0 | 0 | 2 | 0 | 6 | 0 | 1244 | 220 | 0 | 0 | 4 | 65 | 0 | 0 | 0 | 515 | 7 | 180 | 1196 | 118 | 0 |  | 7416 | 5533 | 12949 | 3545 | 909 | 2543 | 0 | 1410 | 3835 | 200 | 0 | 79 | 156 | 265 | 7 | 48.705 | 107.78
16:00 | 0 | 0 | 146 | 0 | 0 | 52 | 0 | 408 | 327 |  | 0 | 450 | 255 | 8 | 51 | 15 | 204 | 0 | 0 | 24 | 58 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 19 | 16 | 25 | 14 | 8 | 0 | 125 | 75 | 100 | 0 | 8 | 219 | 0 | 0 | 0 |  | 12 | 32 | 0 | 47 | 0 | 6 | 11 | 3 | 0 | 0 | 0 | 290 | 270 | 181 | 107 | 0 | 43 | 0 | 0 | 51 | 0 | 0 | 25 | 17 | 8 | 33 | 12 | 158 | 12 | 0 | 0 | 1 | 40 | 30 | 47 | 40 | 112 | 0 | 0 | 84 | 0 | 183 | 17 | 0 | 10 | 300 | 8 | 11 | 0 | 45 | 0 | 0 | 68 | 0 | 17 | 0 | 37 | 68 | 38 | 405 | 19 | 35 | 51 | 1 | 120 | 17 | 55 | 105 | 35 | 38 | 390 | 69 | 21 | 90 | 30 | 0 | 35 | 15 | 53 | 34 | 0 | 0 | 0 | 550 | 7 | 0 | 0 | 0 |  | 909 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 340 | 35 | 0 | 0 | 0 | 70 | 0 | 3 | 0 | 1220 | 218 | 0 | 0 | 2 | 40 | 0 | 0 | 0 | 521 | 17 | 180 | 1211 | 76 | 0 |  | 7410 | 5489 | 12899 | 3559 | 909 | 2420 | 0 | 1528 | 3862 | 200 | 0 | 80 | 158 | 176 | 7 | 144.205 | 107.78
17:00 | 0 | 0 | 150 | 0 | 0 | 51 | 0 | 363 | 276 |  | 0 | 370 | 250 | 8 | 51 | 15 | 150 | 0 | 0 | 24 | 58 | 48 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 19 | 16 | 25 | 14 | 8 | 0 | 125 | 75 | 95 | 0 | 8 | 218 | 0 | 0 | 0 |  | 12 | 56 | 0 | 47 | 0 | 23 | 11 | 12 | 0 | 0 | 0 | 290 | 270 | 180 | 107 | 0 | 43 | 0 | 0 | 51 | 0 | 9 | 25 | 17 | 8 | 33 | 12 | 154 | 17 | 0 | 0 | 0 | 40 | 30 | 47 | 44 | 112 | 0 | 0 | 86 | 0 | 182 | 17 | 0 | 10 | 270 | 8 | 11 | 0 | 45 | 0 | 0 | 68 | 0 | 17 | 3 | 37 | 68 | 50 | 404 | 19 | 52 | 51 | 0 | 120 | 17 | 55 | 105 | 84 | 38 | 356 | 72 | 5 | 90 | 18 | 0 | 35 | 4 | 52 | 38 | 0 | 0 | 0 | 580 | 2 | 0 | 0 | 0 |  | 909 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 22 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 320 | 36 | 0 | 0 | 0 | 92 | 0 | 1 | 0 | 1200 | 180 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 521 | 4 | 150 | 1209 | 9 | 0 |  | 7260 | 5204 | 12464 | 3348 | 909 | 2208 | 0 | 1658 | 3840 | 200 | 0 | 117 | 154 | 28 | 2 | 177.63 | 107.77
18:00 | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 323 | 256 |  | 0 | 450 | 307 | 8 | 51 | 15 | 160 | 0 | 0 | 20 | 58 | 70 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 20 | 19 | 16 | 25 | 14 | 8 | 0 | 125 | 75 | 100 | 0 | 8 | 209 | 0 | 0 | 0 |  | 12 | 56 | 0 | 12 | 0 | 35 | 11 | 14 | 0 | 0 | 0 | 335 | 330 | 201 | 107 | 0 | 44 | 0 | 0 | 51 | 0 | 25 | 25 | 17 | 10 | 33 | 6 | 166 | 18 | 0 | 0 | 0 | 40 | 30 | 50 | 44 | 80 | 0 | 0 | 86 | 0 | 183 | 17 | 0 | 10 | 270 | 8 | 5 | 0 | 50 | 0 | 0 | 68 | 0 | 23 | 0 | 37 | 77 | 55 | 392 | 19 | 52 | 51 | 0 | 150 | 17 | 55 | 52 | 84 | 38 | 375 | 72 | 0 | 90 | 17 | 0 | 35 | 0 | 52 | 54 | 0 | 14 | 0 | 505 | 1 | 0 | 0 | 0 |  | 908 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 22 | 0 | 8 | 65 | 27 | 0 | 0 | 0 | 0 | 0 | 5 | 22 | 0 | 0 | 7 | 0 | 15 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 340 | 36 | 0 | 0 | 15 | 99 | 0 | 0 | 0 | 1120 | 220 | 0 | 11 | 0 | 0 | 35 | 0 | 0 | 516 | 0 | 150 | 1113 | 0 | 0 |  | 7410 | 5227 | 12637 | 3454 | 908 | 2364 | 0 | 1724 | 3584 | 200 | 0 | 236 | 166 | 0 | 1 | 251 | 107.77
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 397 | 332 |  | 0 | 450 | 273 | 8 | 55 | 15 | 160 | 0 | 0 | 8 | 91 | 118 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 19 | 3 | 25 | 14 | 25 | 0 | 125 | 75 | 104 | 0 | 17 | 221 | 0 | 0 | 0 |  | 9 | 71 | 0 | 47 | 0 | 39 | 11 | 20 | 0 | 0 | 0 | 315 | 295 | 210 | 145 | 0 | 48 | 0 | 0 | 51 | 0 | 0 | 49 | 18 | 10 | 33 | 6 | 148 | 22 | 0 | 0 | 0 | 43 | 30 | 50 | 44 | 112 | 0 | 0 | 86 | 0 | 181 | 17 | 0 | 10 | 290 | 8 | 5 | 0 | 133 | 0 | 0 | 142 | 0 | 100 | 0 | 50 | 87 | 80 | 403 | 94 | 88 | 51 | 0 | 276 | 22 | 55 | 52 | 84 | 45 | 380 | 71 | 0 | 90 | 31 | 0 | 35 | 0 | 52 | 34 | 0 | 0 | 0 | 550 | 0 | 16 | 0 | 0 |  | 908 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 41 | 0 | 8 | 62 | 29 | 16 | 0 | 0 | 0 | 10 | 5 | 40 | 0 | 0 | 38 | 0 | 25 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 414 | 41 | 0 | 55 | 15 | 99 | 0 | 0 | 90 | 1220 | 212 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 531 | 0 | 268 | 1208 | 0 | 0 |  | 8286 | 5974 | 14260 | 3562 | 908 | 2570 | 0 | 2551 | 3973 | 200 | 0 | 348 | 148 | 0 | 0 | 229.2 | 107.74
19:30 | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 414 | 332 |  | 0 | 450 | 290 | 0 | 85 | 40 | 160 | 0 | 0 | 8 | 91 | 136 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 11 | 19 | 16 | 25 | 14 | 25 | 0 | 125 | 75 | 100 | 0 | 17 | 220 | 0 | 0 | 0 |  | 18 | 71 | 0 | 47 | 0 | 39 | 11 | 27 | 0 | 0 | 0 | 290 | 280 | 207 | 145 | 0 | 48 | 0 | 0 | 51 | 0 | 0 | 52 | 0 | 10 | 33 | 12 | 152 | 29 | 0 | 0 | 0 | 43 | 30 | 50 | 46 | 112 | 0 | 0 | 86 | 0 | 181 | 17 | 0 | 10 | 265 | 8 | 5 | 0 | 145 | 0 | 0 | 153 | 0 | 110 | 0 | 50 | 87 | 110 | 409 | 94 | 88 | 51 | 0 | 278 | 54 | 55 | 52 | 84 | 50 | 396 | 72 | 0 | 90 | 51 | 0 | 35 | 0 | 53 | 54 | 0 | 0 | 0 | 550 | 0 | 16 | 0 | 0 |  | 777 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 8 | 65 | 31 | 16 | 0 | 0 | 0 | 38 | 0 | 40 | 0 | 0 | 39 | 0 | 25 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 360 | 39 | 0 | 90 | 15 | 99 | 0 | 0 | 113 | 1244 | 224 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 521 | 0 | 307 | 1220 | 0 | 0 |  | 8522 | 5962 | 14484 | 3579 | 777 | 2531 | 0 | 2858 | 4038 | 200 | 0 | 349 | 152 | 0 | 0 | 110.78 | 0
20:00 | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 414 | 332 |  | 0 | 450 | 289 | 0 | 85 | 30 | 160 | 0 | 0 | 8 | 91 | 142 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 20 | 19 | 16 | 25 | 14 | 25 | 0 | 127 | 75 | 103 | 0 | 17 | 225 | 0 | 0 | 0 |  | 18 | 71 | 0 | 58 | 0 | 40 | 11 | 14 | 0 | 0 | 0 | 290 | 270 | 208 | 145 | 0 | 48 | 0 | 0 | 51 | 0 | 0 | 52 | 0 | 10 | 33 | 12 | 152 | 30 | 0 | 0 | 0 | 43 | 30 | 50 | 47 | 112 | 0 | 0 | 86 | 0 | 182 | 17 | 0 | 10 | 260 | 8 | 5 | 0 | 145 | 0 | 0 | 153 | 0 | 120 | 0 | 50 | 86 | 107 | 409 | 94 | 88 | 51 | 0 | 282 | 54 | 55 | 105 | 86 | 50 | 397 | 72 | 0 | 90 | 51 | 0 | 35 | 0 | 52 | 54 | 0 | 0 | 0 | 550 | 0 | 42 | 0 | 0 |  | 778 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 8 | 62 | 28 | 16 | 0 | 0 | 0 | 38 | 0 | 40 | 0 | 0 | 40 | 0 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 360 | 41 | 0 | 90 | 15 | 99 | 0 | 0 | 113 | 1232 | 220 | 0 | 17 | 0 | 0 | 108 | 0 | 0 | 520 | 0 | 307 | 1216 | 0 | 0 |  | 8615 | 6017 | 14632 | 3586 | 778 | 2506 | 0 | 2998 | 4047 | 202 | 0 | 363 | 152 | 0 | 0 | 112.69 | 107.75
21:00 | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 360 | 281 |  | 0 | 450 | 292 | 0 | 55 | 40 | 160 | 0 | 0 | 8 | 91 | 144 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 20 | 19 | 16 | 25 | 14 | 25 | 0 | 127 | 75 | 105 | 0 | 17 | 221 | 0 | 0 | 0 |  | 18 | 71 | 0 | 58 | 0 | 39 | 11 | 33 | 0 | 0 | 0 | 290 | 270 | 208 | 145 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 46 | 14 | 10 | 33 | 12 | 154 | 42 | 0 | 16 | 0 | 43 | 30 | 50 | 48 | 112 | 0 | 0 | 86 | 0 | 183 | 17 | 0 | 10 | 270 | 8 | 5 | 0 | 45 | 0 | 0 | 153 | 0 | 124 | 0 | 50 | 86 | 95 | 405 | 94 | 88 | 51 | 0 | 282 | 51 | 55 | 105 | 87 | 50 | 395 | 72 | 0 | 90 | 51 | 0 | 35 | 0 | 53 | 54 | 0 | 0 | 0 | 550 | 26 | 175 | 0 | 0 |  | 778 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 8 | 66 | 31 | 16 | 0 | 0 | 0 | 31 | 0 | 40 | 0 | 0 | 40 | 0 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 320 | 44 | 0 | 94 | 15 | 99 | 0 | 0 | 113 | 1244 | 180 | 0 | 17 | 0 | 0 | 113 | 0 | 0 | 522 | 0 | 307 | 1208 | 0 | 0 |  | 8606 | 5930 | 14536 | 3580 | 778 | 2411 | 0 | 2841 | 4186 | 202 | 0 | 358 | 154 | 0 | 26 | 132.745 | 107.74
22:00 | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 351 | 282 |  | 0 | 450 | 250 | 0 | 34 | 15 | 160 | 0 | 0 | 8 | 91 | 144 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 20 | 19 | 16 | 25 | 14 | 25 | 0 | 126 | 75 | 101 | 0 | 17 | 220 | 0 | 0 | 0 |  | 18 | 71 | 0 | 58 | 0 | 39 | 11 | 35 | 0 | 0 | 0 | 290 | 270 | 210 | 145 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 146 | 71 | 0 | 16 | 0 | 43 | 30 | 50 | 48 | 112 | 0 | 0 | 84 | 0 | 183 | 17 | 0 | 10 | 285 | 8 | 5 | 0 | 45 | 0 | 0 | 153 | 0 | 124 | 0 | 50 | 86 | 60 | 405 | 94 | 88 | 51 | 0 | 69 | 17 | 55 | 105 | 87 | 50 | 380 | 72 | 0 | 90 | 51 | 0 | 35 | 0 | 52 | 54 | 0 | 0 | 0 | 550 | 0 | 207 | 0 | 0 |  | 892 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 8 | 62 | 33 | 16 | 0 | 0 | 0 | 31 | 0 | 40 | 0 | 0 | 40 | 0 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 320 | 46 | 0 | 94 | 15 | 99 | 0 | 0 | 113 | 1244 | 180 | 0 | 17 | 0 | 0 | 113 | 0 | 0 | 521 | 0 | 307 | 1301 | 0 | 0 |  | 8260 | 6146 | 14406 | 3595 | 892 | 2387 | 0 | 2517 | 4310 | 201 | 0 | 358 | 146 | 0 | 0 | 185.27 | 107.73
23:00 | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 324 | 282 |  | 0 | 450 | 297 | 0 | 34 | 15 | 160 | 0 | 0 | 8 | 91 | 56 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 20 | 19 | 16 | 25 | 14 | 25 | 0 | 126 | 75 | 100 | 0 | 8 | 223 | 0 | 0 | 0 |  | 18 | 64 | 0 | 46 | 0 | 39 | 11 | 35 | 0 | 0 | 0 | 300 | 280 | 207 | 145 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 156 | 72 | 0 | 16 | 0 | 43 | 30 | 50 | 48 | 112 | 0 | 0 | 84 | 0 | 183 | 17 | 0 | 10 | 270 | 8 | 5 | 0 | 45 | 0 | 0 | 68 | 0 | 59 | 0 | 50 | 86 | 10 | 405 | 18 | 88 | 51 | 0 | 69 | 17 | 55 | 105 | 52 | 50 | 388 | 72 | 0 | 90 | 51 | 0 | 35 | 0 | 53 | 54 | 0 | 0 | 0 | 450 | 0 | 267 | 0 | 0 |  | 892 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 8 | 66 | 33 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 207 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 320 | 60 | 0 | 94 | 15 | 99 | 0 | 0 | 70 | 1244 | 180 | 0 | 17 | 0 | 0 | 75 | 0 | 0 | 519 | 0 | 307 | 1318 | 0 | 0 |  | 7837 | 5993 | 13830 | 3596 | 892 | 2419 | 0 | 2121 | 4285 | 201 | 0 | 160 | 156 | 0 | 0 | 372.45 | 107.72
24:00 | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 393 | 331 |  | 0 | 450 | 294 | 0 | 34 | 15 | 180 | 0 | 0 | 8 | 91 | 32 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 20 | 19 | 18 | 25 | 32 | 8 | 0 | 125 | 75 | 100 | 0 | 8 | 225 | 0 | 0 | 0 |  | 12 | 57 | 0 | 46 | 0 | 11 | 9 | 40 | 0 | 0 | 0 | 290 | 310 | 207 | 147 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 156 | 71 | 0 | 18 | 0 | 43 | 30 | 50 | 48 | 112 | 0 | 0 | 84 | 0 | 183 | 17 | 0 | 10 | 290 | 8 | 5 | 0 | 45 | 0 | 0 | 67 | 0 | 44 | 0 | 25 | 48 | 10 | 405 | 18 | 34 | 51 | 0 | 70 | 17 | 55 | 105 | 19 | 50 | 392 | 72 | 0 | 72 | 51 | 0 | 35 | 0 | 53 | 17 | 0 | 0 | 0 | 400 | 1 | 267 | 0 | 0 |  | 891 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 8 | 66 | 33 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 360 | 71 | 0 | 94 | 15 | 70 | 0 | 0 | 70 | 1244 | 220 | 0 | 17 | 0 | 0 | 75 | 0 | 0 | 520 | 0 | 307 | 1370 | 0 | 0 |  | 7693 | 6059 | 13752 | 3723 | 891 | 2572 | 0 | 1832 | 4288 | 200 | 0 | 89 | 156 | 0 | 1 | 399.19 | 107.71
KWH | 0 | 0 | 3391469 | 0 | 0 | 928363 | 0 | 9132030 | 7248000 |  | 0 | 9538000 | 7000029 | 43200 | 453233 | 255387 | 5852457 | 0 | 0 | 109997 | 966816 | 1190400 | 0 | 0 | 0 | 0 | 383040 | 518765 | 513214 | 425124 | 456000 | 398880 | 574020 | 531000 | 288480 | 0 | 2839653 | 1812000 | 2400000 | 0 | 160614 | 5193818 | 0 | 0 | 0 |  | 337920 | 554928 | 0 | 781680 | 0 | 290400 | 235152 | 559680 | 0 | 0 | 0 | 7772800 | 7093000 | 4724000 | 2341818 | 0 | 1137744 | 0 | 0 | 932188 | 0 | 40784 | 837321 | 382320 | 228420 | 802200 | 223320 | 3464640 | 802560 | 0 | 229644 | 11850 | 1006000 | 696720 | 1158600 | 1127304 | 2401200 | 0 | 0 | 1921920 | 0 | 4736790 | 398000 | 0 | 247680 | 7025500 | 190080 | 209328 | 0 | 848073 | 0 | 0 | 2114400 | 0 | 1087632 | 122580 | 819840 | 1356000 | 558690 | 9543000 | 942000 | 1074240 | 1013673 | 29520 | 2318400 | 451268 | 1295522 | 1781820 | 829080 | 603840 | 9133300 | 1102080 | 325750 | 1166400 | 717600 | 0 | 787680 | 233995 | 1278720 | 831960 | 0 | 1673 | 0 | 13658180 | 46560 | 734545 | 0 | 0 |  | 21616000 | 0 | 0 | 0 | 501120 | 0 | 0 | 0 | 41760 | 0 | 49875 | 1444000 | 615362 | 85440 | 0 | 0 | 0 | 114892 | 10560 | 164272 | 0 | 0 | 197968 | 0 | 134581 | 0 | 0 | 191754 | 0 | 0 | 4379500 | 0 | 0 | 4155027 | 0 | 0 | 0 | 0 | 0 | 3982809 | 0 | 8419672 | 566880 | 0 | 528000 | 132336 | 852777 | 0 | 43805 | 580704 | 28528400 | 4900882 | 0 | 141600 | 36660 | 685440 | 485760 | 0 | 0 | 12509090 | 169628 | 4778200 | 29023636 | 1153940 | 0 |  | 174315501 | 131222330 | 305537831 | 87672766 | 21616000 | 56366198 | 0 | 32843477 | 93611551 | 4651653 | 0 | 2451818 | 3464640 | 2813168 | 46560 | 0
Fuel Cost | 0 | 0 | 4951544.74 | 0 | 0 | 1234722.79 | 0 | 9588631.5 | 7827840 |  | 0 | 10396420 | 7770032.19 | 482976 | 6005337.25 | 3383877.75 | 6554751.84 | 0 | 0 | 1608156.14 | 13603101.12 | 19296384 | 0 | 0 | 0 | 0 | 4872268.8 | 7003327.5 | 6882199.74 | 318843 | 342000 | 0 | 0 | 0 | 4907044.8 | 0 | 766706.31 | 489240 | 4536000 | 0 | 2626038.9 | 5401570.72 | 0 | 0 | 0 |  | 4409856 | 9256199.04 | 0 | 10560496.8 | 0 | 3359928 | 298643.04 | 1863734.4 | 0 | 0 | 0 | 8627808 | 7731370 | 5479840 | 3020945.22 | 0 | 1285650.72 | 0 | 0 | 1556753.96 | 0 | 704339.68 | 11261967.45 | 523778.4 | 171315 | 1403850 | 167490 | 24876115.2 | 874790.4 | 0 | 312315.84 | 188889 | 1378220 | 919670.4 | 2015964 | 1950235.92 | 2761380 | 0 | 0 | 4381977.6 | 0 | 4784157.9 | 855700 | 0 | 490406.4 | 7025500 | 142560 | 159089.28 | 0 | 11576196.45 | 0 | 0 | 28502112 | 0 | 15063703.2 | 1432960.2 | 8460748.8 | 18522960 | 7413816.3 | 8779560 | 11454720 | 15533510.4 | 12822963.45 | 459331.2 | 27218016 | 4914308.52 | 13771398.86 | 24179297.4 | 10686841.2 | 7113235.2 | 8402636 | 14271936 | 4707087.5 | 14801616 | 8166288 | 0 | 10287100.8 | 2796240.25 | 19142438.4 | 10956913.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 64848000 | 0 | 0 | 0 | 5216659.2 | 0 | 0 | 0 | 752097.6 | 0 | 716703.75 | 1617280 | 1193802.28 | 931296 | 0 | 0 | 0 | 1926738.84 | 184694.4 | 2569214.08 | 0 | 0 | 3347638.88 | 0 | 2270381.47 | 0 | 0 | 145157.778 | 0 | 0 | 37138160 | 0 | 0 | 4819831.32 | 0 | 0 | 0 | 0 | 0 | 4620058.44 | 0 | 8335475.28 | 7618867.2 | 0 | 6246240 | 1912255.2 | 10830267.9 | 0 | 484045.25 | 7049746.56 | 236785720 | 4998899.64 | 0 | 1047840 | 414624.6 | 8040211.2 | 7446700.8 | 0 | 0 | 113707628.1 | 0 | 57195054 | 248152087.8 | 0 | 0 |  | 577087888.07 | 852563377.568 | 1429651265.638 | 95194114.318 | 64848000 | 66824089.68 | 0 | 424843273.04 | 692978649.9 | 1255946.31 | 0 | 40307687.99 | 24876115.2 | 18523389.2 | 0 | 0
Yesterday Day Peak | 0 | 0 | 150 | 0 | 0 | 53 | 0 | 405 | 322 |  | 0 | 450 | 310 | 0 | 17 | 15 | 308 | 0 | 0 | 0 | 40 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 19 | 19 | 25 | 28 | 8 | 0 | 125 | 75 | 100 | 0 | 0 | 214 | 0 | 0 | 0 |  | 13 | 0 | 0 | 0 | 0 | 0 | 9 | 5 | 0 | 0 | 0 | 320 | 310 | 187 | 86 | 0 | 47 | 0 | 0 | 51 | 0 | 0 | 25 | 16 | 10 | 33 | 12 | 154 | 28 | 0 | 0 | 1 | 40 | 30 | 47 | 47 | 112 | 0 | 0 | 78 | 0 | 184 | 16 | 0 | 10 | 295 | 8 | 11 | 0 | 38 | 0 | 0 | 98 | 0 | 17 | 13 | 37 | 68 | 2 | 403 | 56 | 52 | 24 | 4 | 60 | 17 | 34 | 17 | 31 | 0 | 379 | 18 | 24 | 54 | 34 | 0 | 17 | 35 | 52 | 34 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 0 |  | 909 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 330 | 6 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1040 | 223 | 0 | 0 | 5 | 99 | 0 | 0 | 0 | 520 | 34 | 150 | 1164 | 127 | 0 |  | 12429 | DayPeak
Yesterday Evening Peak | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 414 | 332 |  | 0 | 450 | 289 | 0 | 85 | 30 | 160 | 0 | 0 | 8 | 91 | 142 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 20 | 19 | 16 | 25 | 14 | 25 | 0 | 127 | 75 | 103 | 0 | 17 | 225 | 0 | 0 | 0 | 0 | 18 | 71 | 0 | 58 | 0 | 40 | 11 | 14 | 0 | 0 | 0 | 290 | 270 | 208 | 145 | 0 | 48 | 0 | 0 | 51 | 0 | 0 | 52 | 0 | 10 | 33 | 12 | 152 | 30 | 0 | 0 | 0 | 43 | 30 | 50 | 47 | 112 | 0 | 0 | 86 | 0 | 182 | 17 | 0 | 10 | 260 | 8 | 5 | 0 | 145 | 0 | 0 | 153 | 0 | 120 | 0 | 50 | 86 | 107 | 409 | 94 | 88 | 51 | 0 | 282 | 54 | 55 | 105 | 86 | 50 | 397 | 72 | 0 | 90 | 51 | 0 | 35 | 0 | 52 | 54 | 0 | 0 | 0 | 550 | 0 | 42 | 0 | 0 |  | 778 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 8 | 62 | 28 | 16 | 0 | 0 | 0 | 38 | 0 | 40 | 0 | 0 | 40 | 0 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 360 | 41 | 0 | 90 | 15 | 99 | 0 | 0 | 113 | 1232 | 220 | 0 | 17 | 0 | 0 | 108 | 0 | 0 | 520 | 0 | 307 | 1216 | 0 | 0 |  | 14632 | EvPeak
Forecast for Evening | 0 | 0 | 155 | 0 | 0 | 53 | 0 | 412 | 330 | 0 | 0 | 450 | 310 | 82 | 85 | 55 | 210 | 0 | 0 | 92 | 102 | 149 | 55 | 0 | 0 | 0 | 35 | 35 | 55 | 20 | 19 | 19 | 25 | 30 | 25 | 0 | 121 | 75 | 100 | 0 | 17 | 225 |  | 0 | 0 | 0 | 18 | 64 | 0 | 70 | 0 | 40 | 11 | 25 | 0 | 0 | 0 | 330 | 330 | 200 | 145 | 0 | 50 | 0 | 0 | 50 | 0 | 31 | 52 | 18 | 10 | 33 | 12 | 165 | 43 | 0 | 18 | 0 | 43 | 40 | 50 | 46 | 112 | 0 | 0 | 86 | 0 | 185 | 17 | 0 | 10 | 300 | 8 | 11 | 0 | 300 | 0 | 0 | 159 | 0 | 149 | 0 | 50 | 85 | 150 | 400 | 104 | 88 | 51 | 0 | 285 | 54 | 55 | 105 | 85 | 63 | 400 | 72 | 0 | 108 | 51 | 0 | 34 |  | 50 | 54 | 0 | 150 |  | 350 | 20 | 600 | 0 |  |  | 938 | 0 | 0 |  | 82 | 0 | 0 | 0 | 40 | 40 | 16 | 65 | 25 | 110 | 0 | 0 | 0 | 38 | 0 | 91 | 28 | 42 | 40 | 52 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 180 |  | 0 | 0 | 0 | 0 | 180 | 0 | 400 | 72 | 0 | 90 | 100 | 99 | 0 | 0 | 113 | 1244 | 220 |  | 150 |  |  | 115 | 0 |  | 520 |  | 300 | 1400 |  | 0
Forecast for Day | 0 | 0 | 155 | 0 | 0 | 53 | 0 | 412 | 330 | 0 | 0 | 450 | 310 | 72 | 85 | 15 | 200 | 0 | 0 | 92 | 102 | 48 | 55 | 0 | 0 | 0 | 17 | 35 | 55 | 20 | 19 | 19 | 25 | 30 | 8 | 0 | 121 | 75 | 100 | 0 | 8 | 225 |  | 0 | 0 | 0 | 18 | 40 | 0 | 70 | 0 | 6 | 11 | 7 | 0 | 0 | 0 | 330 | 330 | 200 | 78 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 149 | 43 | 0 | 18 | 1.6 | 43 | 40 | 50 | 40 | 112 | 0 | 0 | 86 | 0 | 185 | 17 | 0 | 10 | 300 | 8 | 11 | 0 | 300 | 0 | 0 | 115 | 0 | 17 | 20 | 25 | 68 | 50 | 400 | 37 | 35 | 51 | 5 | 120 | 17 | 55 | 105 | 27 | 38 | 400 | 54 | 50 | 54 | 34 | 0 | 17 | 35 | 34 | 17 | 0 | 54 |  | 350 | 10 | 600 | 0 |  |  | 938 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 25 | 0 | 0 | 65 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 28 | 34 | 30 | 0 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 360 | 54 | 0 | 90 | 100 | 35 | 0 | 8 | 35 | 1244 | 220 |  | 35 | 6 | 100 | 35 | 0 |  | 520 | 30 | 300 | 1300 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 155 | 0 | 0 | 52 | 0 | 347 | 266 | 0 | 0 | 320 | 299 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 18 | 25 | 32 | 8 | 0 | 126 | 75 | 108 | 0 | 8 | 224 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 6 | 9 | 12 | 0 | 0 | 0 | 350 | 310 | 207 | 78 | 0 | 50 | 0 | 0 | 20 | 0 | 0 | 8 | 18 | 8 | 33 | 12 | 124 | 34 | 0 | 18 | 0 | 43 | 30 | 47 | 48 | 80 | 0 | 0 | 78 | 0 | 183 | 17 | 0 | 10 | 280 | 0 | 8 | 0 | 0 | 0 | 0 | 67 | 0 | 35 | 11 | 25 | 34 | 0 | 378 | 19 | 34 | 51 | 1 | 70 | 17 | 55 | 17 | 9 | 25 | 360 | 17 | 22 | 0 | 17 | 0 | 17 | 12 | 53 | 17 | 0 | 0 | 0 | 400 | 7 | 267 | 0 | 0 | 0 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 280 | 17 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1022 | 184 | 0 | 0 | 2 | 29 | 0 | 0 | 0 | 522 | 14 | 200 | 1169 | 85 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
[128 empty] | 399274 |  | 399226 | [74 empty] | 292.3904
| Minimum Generation |  | 10877 | 7:00 | [202 empty] | 144038964
| Highest Generation |  | 14632 | 20:00 | [202 empty] | 144.039 |  |  |  |  | 2.8132
| Day Peak Generation |  | 12429 | 12:00 | [202 empty] | 35295295
| Evening Peak Generation |  | 14632 | 20:00 | [202 empty] | 35.2953 |  |  | 56366198 |  | 4.6517
| HVDC Max Flow |  | 910 | 1:00 | [202 empty] | 21.616 |  |  |  |  | 0.04656
| HVDC EvPeak Flow |  | 778 | 20:00 | [200 empty] | 305537831 |  | 3.4646 |  | 93.6116
| Load factor L.F |  | 87.01% | [166 empty] | 1275.5 | [36 empty] | 305.5378

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-09-27
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-09-26 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 12429 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 11405
Evening Peak Generation : |  |  | 14632 | MW Hour : | 20:00 | Available Max Generation : |  | 17046
E.P. Demand (at gen end) : |  |  | 14750 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 15000
Maximum Generation : |  |  | 14632 | MW Hour : | 20:00 | Reserve(Generation end) |  | 2046
Total Gen. (MKWH) : |  |  | 305.5378 | System Load Factor : | 87.01% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 1010 | MW at | 18:30 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-09-27
Actual : |  | 107.77 | Ft.(MSL) , | Rule curve : | 105.04 | Ft.( MSL )
Gas Consumed : |  | Total = | 1086.75 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 162018203.998
: |  |  | Coal : | 692978649.9 | Oil : | 465150961.03 | Total : | 1320147814.928
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 22 | 528:00 | 4857.5703 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1336.484 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1872.677 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1628.1782 |  |  | 0 | 0%
Cumilla Area |  | 15 | 360:00 | 1339.4547 |  |  | 0 | 0%
Mymensingh Area |  | 48 | 1152:00 | 996.477 |  |  | 0 | 0%
Sylhet Area |  | 28 | 672:00 | 558.2777 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 465.5121 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 910.4541 |  |  | 0 | 0%
Total |  | 113 |  | 13965.0851 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:38 | 08:54 | Hasnabad 132/33kV T-2 LT Tripped showing Tripped relay Due to 33kV Zinzira-1 feeder fault. |  |  |  |  | 23 MW Power interrup.
08:53 | 14:12 | Meghnaghat 230/132kV S/S Bus-2 S/D Due to Busbar-2 shutdown for rectification of high temperature of ST bay Bus-2 DS(Y phase)
| 09:21 | Munshiganj 132/33kV S/S Transformer-2 HT is restored.
| 09:21 | Bhulta 132/33kV S/S GT2 HT is restored.
09:30 | 15:12 | BSRM-Mirsharai 230 kV Ckt-2 Scheduled S/D from Mirsorai 230/33kV end Due to Annual maintenance work and from BSRM
230/33kV end Due to Deadline Checking
10:03 | 17:16 | Magura 132/33kV S/S T-3 LT Scheduled S/D Due to Experimental testing of T-3
10:18 | 13:58 | Pabna- Shahjadpur 132kV Ckt-1 Forced S/D from Due to Baghabari 230/132kV T2 Transformer S/D.
10:29 |  | Banani 132/33 kV T-2 transformer shut down due to energy meter replacement.
10:32 | 12:08 | Baghabari 230/132kV S/S T-2 Bank LT Forced S/D Due to Red hot maintenance work bushing clamp connector(Y-Phase)
10:43 | 11:00 | Ashuganj-Cumilla(N) 230 kV Ckt-2 Tripped from Cumilla(N) end showing Secondary distance Protection operated -b phase -c phase.
Auto Reclosure Relay
10:57 | 17:59 | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-2 Forced S/D from Bog-Sherpur 132/33kV end Due to According to NLDC's instructions.
11:09 | 17:58 | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-1 Forced S/D from Bog-Sherpur 132/33kV end Due to According to NLDC's instructions.
11:21 |  | Banani 132/33 kV T-2 transformer switched ON
12:47 | 13:51 | Hathazari 230/132/33kV S/S MT-02 LT Tripped showing SIEMENS winding temperature relays Due to winding temperature high |  |  |  |  | 60 MW Power interrup.
13:04 | 13:35 | Hasnabad-Keraniganj 230kV Ckt-1 Tripped from Hasnabad end showing Distance relay relays Due to Unknown
13:48 |  | Siddirganj 335 MW CCPP ST forced shut down due to poor steam quality |  |  |  |  | 110 MW Generation interrup.
| 15:42 | Noapara 132/33kV S/S T-1 LT is restored.
17:56 | 01:15 | Sylhet 132/33kV S/S T4 LT Tripped showing 51 relays Due to Over Load
17:59 | 20:08 | Baghabari-Sirajganj 132 kV Ckt-1 Forced S/D from Sirajganj end Due to In Baghabari S/S T-01 has taken shutdown for this reason
ALDC,Bogura request to CB open
18:05 | 20:07 | Baghabari 230/132kV S/S T-1 LT Forced S/D Due to PDB 132 KV side maintanace work.
18:45 |  | Matarbari 2*600 MW (CPGCL) Unit-1 was sync.
20:09 |  | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-2 Forced S/D from Bog-Sherpur end Due to According to instructions of ALDC, Bogura.
20:09 |  | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-1 Forced S/D from Bog-Sherpur end Due to According to instructions of ALDC, Bogura.
22:10 | 23:25 | Bhulta 132/33kV S/S GT1 HT Forced S/D Due to To minimize Red hot of 132 KV Bus of B phase |  |  |  |  | 60 MW Power interrup.
05:05 | 05:27 | Baroirhat-Feni 132 kV Ckt-2 Tripped from Feni end showing Power swing A,CB 1 A/R Fail relays Due to Unknown and from Baroirhat end
showing Distance relay Due to Distance trip.
06:23 |  | Cumilla(N)-Daudkandi 132 kV Ckt-2 Forced S/D from Cumilla(N) end Due to Red hot remove.
06:56 |  | Natore 132/33kV S/S TR-3 (425 T) LT Scheduled S/D Due to Conductor loop change.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-09-26 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 150 | 3391469
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 52 | 928363 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 414 | 9132030
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 332 | 7248000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9538000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 0 | 43200 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 289 | 7000029 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 85 | 453233 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 30 | 255387 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Low demand
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 20 | 425124 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 8 | 109997 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 160 | 5852457 | Frequency control
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 91 | 966816 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 383040 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 142 | 1190400
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 518765 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 513214 | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 35 | 854880 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 574020 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 14 | 531000 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 288480 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 145 | 848073 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 120 | 1087632 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1074240 | Low demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 72 | 1102080 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 90 | 1166400 | Low demand
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 233995
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 831960
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5422 | 2996 | 56542284
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 103 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 160614 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 122580
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 40 | 290400 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 202 | 4651653
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 225 | 5193818
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 1013673 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 71 | 554928
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 58 | 781680 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 819840 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 11 | 235152 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 14 | 559680
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29520
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 282 | 2318400 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 451268
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 55 | 1295522 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 603840 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 51 | 717600 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 0 | 1673 | Low demand
| SS Power I |  | SS Power | 0 | 0 | 550 | 13658180
| Cox's Bazar Wind |  | IPP | 66 | 0 | 0 | 46560 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 42 | 734545 | On test.
| Chattogram area Total |  |  |  | 2545 | 1926 | 36641126
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 208 | 4724000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 290 | 7772800 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 7093000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 48 | 1137744
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 145 | 2341818 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 932188
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 107 | 558690 | Low demand
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 40784 | Reserve
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 86 | 1356000 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 382320 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 228420
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 152 | 3464640
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 802200
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 837321
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 12 | 223320 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 105 | 1781820 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 86 | 829080 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 787680 | Machine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 52 | 1278720 | Fuel shortage
| Cumilla Area Total |  |  |  | 2896 | 1742 | 36572545
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 30 | 802560 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 229644 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11850
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 153 | 2114400 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 94 | 942000 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 325750
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 337920 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 295 | 4764124
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1006000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 696720 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2401200 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1158600
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 47 | 1127304
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 209328
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under maint.
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1921920
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 182 | 4736790 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 398000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 190080 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 260 | 7025500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 409 | 9543000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 247680
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 397 | 9133300
| Sylhet Area Total |  |  |  | 2427 | 1656 | 39795422
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 778 | 21616000
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 82 | 501120
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 41760
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Low demand
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 49875 | Low demand
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 41 | 566880 | High Voltage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 132336 | Low demand
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 685440
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 220 | 0 | 0 | Reserve
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 520 | 12509090
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3121 | 1444 | 36102501
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 85440 | Low demand
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 28 | 615362 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 62 | 1444000 | ST Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1232 | 28528400
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4900882
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 141600 | Low demand
| Barisal 307 MW |  | IPP | 307*1 | 307 | 307 | 4778200
| Barisal Area Total |  |  |  | 2265 | 1882 | 40493884
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 38 | 114892
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 10560 | Reserve
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 197968
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 181 | 4155027 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 186 | 3982809 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 360 | 8419672 | Frequency control
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 134581 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 191754 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 40 | 164272 | Low demand
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 90 | 528000 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 580704
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 36660
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1216 | 29023636
| Rajshahi Area Total |  |  |  | 3631 | 2304 | 47540535
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 180 | 4379500 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 99 | 852777 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 43805
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 108 | 485760 | Engine problem
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 169628
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1153940
| Rangpur Area Total |  |  |  | 950 | 387 | 7085410
| Total |  |  |  | 23871 | 14632 | 305537831
| Eastern Grid Total |  |  |  | 13904 | 8615 | 174315501
| Western Grid Total |  |  |  | 9967 | 6017 | 131222330
| National Grid Total |  |  |  | 23871 | 14632 | 305537831
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-09-26
| (a) ENTIRE EASTERN GRID : |  | 9443.83 | MW | (b) ENTIRE WESTERN GRID : |  | 4577.1 | MW
| i) Dhaka area |  | 4995.33 | MW | i) Khulna area |  | 1743.7 | MW
| ii) Chittagong area |  | 1338.5 | MW | ii) Rajshahi area |  | 1466.4 | MW
| iii) Comilla area |  | 1358 | MW | iii) Barisal area |  | 441 | MW
| iv) Mymensingh area |  | 1161 | MW | iv) Rangpur area |  | 926 | MW
| v) Sylhet area |  | 591 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 14020.93 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 14 | 10:00 | Chhatak | 36 | 21:00 | Kamrangirchar | 82.2 | 13:00 | Narshingdi | 188 | 21:00 | Shikalbaha-230 | N/A | N/A
2 | AKSML | 87 | 15:00 | Chowmuhani | 232 | 22:00 | Kaptai | N/A | N/A | Natore | 148 | 20:00 | Shitalakhya | 102.5 | 16:00
3 | Aftabnagar | 36 | 18:30 | Chuadanga | 115 | 19:00 | Kazla | 94 | 13:00 | Nawabganj | 47.9 | 22:00 | Sholosohor | 44 | 14:00
4 | Agargaon | 95 | 13:00 | Coxsbazar | 135 | 18:00 | Keranigonj | 72 | 12:00 | Netrakona | 147 | 22:00 | Shyampur | 110 | 05:00
5 | Agrabad | 84 | 15:00 | Cumilla(N) | 188 | 20:00 | Khagrachori | 36 | 19:00 | New | 78 | 11:00 | Siddhirganj | 122 | 12:00
6 | Amnura | 51 | 21:00 | Cumilla(S) | 167 | 18:00 | Khulna | 99 | 19:00 | Niamatpur | 74 | 22:00 | Sirajganj | 127 | 19:30
7 | Ashuganj | 71 | 23:00 | Daudkandi | 150 | 21:00 | Khulshi | 167 | 15:00 | Noapara | 47 | 18:30 | Sonargaon | 88 | 00:00
8 | BIPTC | N/A | N/A | Dhaka | 34 | 11:00 | Kishoreganj | 150 | 19:30 | PHP | 5 | 10:00 | Sreemongol | 63 | 01:00
9 | BSRM | 139 | 06:00 | Dhamrai | 134 | 18:30 | Kodda | 289 | 21:00 | Pabna | 128 | 20:00 | Sreepur | 80.48 | 19:00
10 | Bagerhat | 90 | 21:00 | Dhanmondi | 116 | 14:00 | Kulaura | 52 | 18:30 | Palashbari | 126 | 20:00 | Srinagar | 47.1 | 22:00
11 | Bakulia | 109 | 19:00 | Dohazari | 86 | 21:00 | Kurigram | 70 | 19:30 | Panchagarh | 57 | 20:00 | Sunamganj | 56 | 21:00
12 | Banani | 34 | 13:00 | Faridpur | 159 | 19:30 | Kushtia | 144 | 19:00 | Patuakhali | 111 | 22:00 | Sylhet | 165 | 19:30
13 | Bangabhaban | 17 | 10:00 | Fatullah | 69 | 15:00 | Lalbag | 94 | 13:00 | Payra | 22 | 00:00 | TK | 33 | 20:00
14 | Barapukuria | 63 | 22:00 | Fenchuganj | 49 | 18:30 | Lalmonirhat | 50 | 18:30 | Postogola | 58 | 13:00 | Tangail | 244 | 19:30
15 | Barguna | 20 | 00:00 | Feni | 125 | 20:00 | MI_Cement | 19.7 | 17:00 | Purbachal | 21 | 18:30 | Thakurgaon | 93 | 20:00
16 | Barishal | 106 | 18:30 | GPH | 66 | 13:00 | Madanganj | 26 | 21:00 | Purbasadipur | 116 | 21:00 | Tongi | 112 | 20:00
17 | Barishal-230 | 98 | 21:00 | Ghorashal | 74 | 15:00 | Madaripur | 109 | 22:00 | Rahim | 38 | 07:00 | Ullon | 44 | 20:00
18 | Baroaulia | 69 | 13:00 | Goalpara | 34 | 00:00 | Madartek | 90.32 | 23:00 | Rajbari | 78 | 19:00 | Uttara | 74 | 12:00
19 | Baroirhat | 65 | 20:00 | Gollamari | 47 | 00:00 | Madunaghat | 60 | 18:30 | Rajendrapur | 84 | 15:00 | UttaraNew | 71 | 23:00
20 | Bashundhara | 153 | 18:30 | Gopalganj | 106 | 19:30 | Magura | 64 | 18:30 | Rajshahi | 153 | 19:30 | Zigatola | 64 | 18:00
21 | BashundharaCement | 5 | 07:00 | Gulshan | 128 | 13:00 | Mahasthangarh | 76 | 20:00 | Rajshahi-230 | 33 | 21:00
22 | Beanibazar | 82 | 18:30 | Halishahar | 84 | 15:00 | Manikganj | 124 | 20:00 | Ramganj | 118 | 22:00
23 | Benapole | 64 | 20:00 | HaripurSBU | 147 | 15:00 | Maniknagar | 92 | 11:00 | Rampur | 33 | 20:00
24 | Bhaluka | 126 | 18:30 | Hasnabad | 106 | 19:00 | Matarbari | 45 | 00:00 | Rangamati | 18 | 18:30
25 | Bhandaria | 50 | 22:00 | Hathazari | 83 | 14:00 | Matuail | 66 | 12:00 | Rangpur | 150 | 19:00
26 | Bhangura | 36 | 19:00 | Ishurdi | 77 | 20:00 | Millgate | 103 | 15:00 | Ruppur | 6.4 | 16:00
27 | Bheramara(GK) | 67 | 18:30 | Jaldhaka | 73 | 20:00 | Mirpur | 137 | 19:00 | SSM | 134 | 15:00
28 | Bhulta | 248 | 16:00 | Jamalpur | 170 | 22:00 | Mirsorai | 5 | 15:00 | Saidpur | 101 | 18:30
29 | Bog-Sherpur | 58 | 18:30 | Jashore | 134 | 20:00 | Mithapukur | 45 | 21:00 | Satkhira | 127 | 19:30
30 | Bogura | 164 | 21:00 | Jhenaidah | 132 | 19:00 | Modern | 0 | 00:00 | Satmasjid | 95 | 18:30
31 | Borhanuddin | 64 | 23:00 | Joydebpur | 180 | 18:30 | Mogbazar | 131.8 | 16:00 | Savar | 192 | 15:00
32 | Brahmanbaria | 155 | 02:00 | Joypurhat | 60 | 20:00 | Mongla | 32 | 11:00 | ShahCement | 27 | 23:00
33 | Cantonment | 156 | 13:00 | Juldah | 22 | 15:00 | Motijheel | 43 | 13:00 | Shahjadpur | 108 | 20:00
34 | Chandpur | 77 | 21:00 | KSRM | 28 | 10:00 | Munshiganj | 111 | 23:00 | Shahjibazar | 127 | 21:00
35 | Chandraghona | 33 | 18:30 | Kabirpur | 299 | 11:00 | Mymensingh | 223 | 22:00 | Shahmirpur | 53.7 | 01:00
36 | Chapai | 61 | 21:00 | Kachua | 77 | 21:00 | Naogaon | 124 | 21:00 | Shariatpur | 84 | 21:00
37 | Charsaidpur | 27 | 11:00 | Kallyanpur | 111 | 18:30 | Narail | 59 | 19:00 | Sherpur | 152 | 19:00
38 | Chauddagram | 65 | 21:00 | Kalurghat | 34 | 12:00 | Narinda | 85 | 13:00 | Shikalbaha | 29 | 00:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-09-26 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 395 | 07:00 | 382 | 12:00 | Gopalganj | 403 | 06:00 | 391 | 15:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 375 | 19:00 | 361 | 16:00
| Bhulta | 395 | 07:00 | 382 | 12:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 400 | 18:30 | 388 | 16:00 | Payra | 412 | 06:00 | 404 | 23:00
| BIPTC | 400 | 05:00 | 393 | 15:00 | Rahanpur | 405 | 06:00 | 393 | 18:30
| Bogura | N/A | N/A | N/A | N/A | Rampal | 404 | 07:00 | 392 | 23:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 231 | 07:00 | 221 | 12:00 | Hasnabad | 229 | 04:00 | 223 | 15:00
| AKSML | 234 | 19:30 | 224 | 01:00 | Hathazari | 236 | 21:00 | 225 | 10:00
| Aminbazar | 232 | 04:00 | 223 | 11:00 | Ishurdi | 234 | 06:00 | 224 | 13:00
| Ashuganj | 235 | 20:00 | 227 | 15:00 | Jhenaidah | 227 | 06:00 | 214 | 18:30
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 230 | 06:00 | 222 | 14:00
| Baghabari | 231 | 20:00 | 221 | 21:00 | Keranigonj | 231 | 07:00 | 221 | 12:00
| Barapukuria | 222 | 07:00 | 206 | 19:00 | Khulna(S) | 232 | 06:00 | 222 | 18:30
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 237 | 06:00 | 230 | 18:30 | Maniknagar | 231 | 04:00 | 222 | 12:00
| Bheramara | 236 | 20:00 | 224 | 14:00 | Meghnaghat | 239 | 07:00 | 230 | 13:00
| Bhulta | 234 | 07:00 | 225 | 12:00 | Mirsorai | 232 | 21:00 | 224 | 11:00
| Bibiana | 237 | 18:30 | 224 | 15:00 | Rajshahi | 232 | 19:30 | 219 | 23:00
| BIPTC | 234 | 06:00 | 222 | 13:00 | Rampal | 232 | 06:00 | 222 | 23:00
| Bogura | 229 | 06:00 | 220 | 19:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 242 | 08:00 | 237 | 00:00 | Rampura | 233 | 06:00 | 223 | 12:00
| BSRM | 233 | 20:00 | 225 | 02:00 | Shikalbaha | 236 | 21:00 | 224 | 11:00
| Cumilla(N) | 231 | 20:00 | 225 | 10:00 | Shyampur | 232 | 07:00 | 223 | 12:00
| Fenchuganj | 233 | 06:00 | 229 | 01:00 | Siddhirganj | 233 | 05:00 | 226 | 11:00
| Ghorashal | 230 | 00:00 | 230 | 00:00 | Sirajgonj | 237 | 06:00 | 232 | 14:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 230 | 07:00 | 223 | 15:00
| GPH | 232 | 21:00 | 224 | 11:00 | Tongi | 228 | 19:30 | 216 | 15:00
| Haripur | 230 | 01:00 | 223 | 16:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 136 | 04:00 | 128 | 10:00 | Lalbag | 131 | 05:00 | 124 | 12:00
| Agargaon | 133 | 06:00 | 125 | 12:00 | Lalmonirhat | 130 | 03:00 | 122 | 13:00
| Agrabad | 135 | 20:00 | 128 | 10:00 | Madanganj | 134 | 19:00 | 128 | 12:00
| AKS | 134 | 20:00 | 126 | 10:00 | Madaripur | 130 | 07:00 | 125 | 22:00
| Aminbazar | 131 | 04:00 | 126 | 11:00 | Madartek | 136 | 06:00 | 128 | 12:00
| Amnura | 138 | 20:00 | 124 | 23:00 | Madunaghat | 136 | 20:00 | 129 | 11:00
| Ashuganj | 139 | 07:00 | 135 | 15:00 | Magura | 137 | 07:00 | 126 | 18:30
| Bagerhat | 130 | 09:00 | 121 | 23:00 | Mahasthangarh | 135 | 06:00 | 126 | 19:00
| Bakulia | 136 | 21:00 | 128 | 10:00 | Manikganj | 132 | 18:00 | 124 | 15:00
| Banani | 136 | 03:00 | 128 | 11:00 | Maniknagar | 135 | 05:00 | 127 | 11:00
| Bangabhaban | 134 | 06:00 | 127 | 11:00 | Matarbari | 133 | 00:00 | 112 | 01:00
| Barapukuria | 138 | 07:00 | 123 | 19:00 | Matuail | 134.4 | 07:00 | 129 | 10:00
| Barguna | 135 | 17:00 | 128 | 22:00 | Millgate | 133 | 07:00 | 124 | 12:00
| Barishal | 135 | 05:00 | 126 | 22:00 | Mirpur | 130 | 03:00 | 124 | 10:00
| Barishal-230 | 137 | 06:00 | 132 | 19:30 | Mithapukur | 134 | 06:00 | 123 | 18:30
| Baroaulia | 136 | 21:00 | 128 | 10:00 | MI_Cement | 135.2 | 20:00 | 129.3 | 11:00
| Baroirhat | 132 | 17:00 | 124 | 09:00 | Modern | 136 | 21:00 | 128 | 11:00
| Bashundhara | 136 | 03:00 | 123 | 15:00 | Mogbazar | 136 | 02:00 | 130 | 10:00
| BashundharaCement | 134 | 19:00 | 128 | 12:00 | Mongla | 130 | 17:00 | 123 | 00:00
| Beanibazar | 127 | 07:00 | 120 | 18:00 | Motijheel | 134 | 06:00 | 127 | 11:00
| Benapole | 134 | 06:00 | 123 | 18:30 | Munshiganj | 135 | 20:00 | 129 | 11:00
| Bhaluka | 124 | 04:00 | 119 | 15:00 | Mymensingh | 133 | 18:00 | 116 | 22:00
| Bhandaria | 132 | 09:00 | 120 | 22:00 | Naogaon | 134 | 06:00 | 124 | 18:30
| Bhangura | 137 | 06:00 | 132 | 00:00 | Narail | 137 | 06:00 | 126 | 18:30
| Bheramara | 135 | 06:00 | 128 | 14:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara(GK) | 134 | 06:00 | 126 | 18:30 | Narshingdi | 130 | 07:00 | 121 | 11:00
| Bhulta | 129 | 23:00 | 120 | 11:00 | Natore | 130 | 06:00 | 122 | 18:30
| Bog-Sherpur | 137 | 17:00 | 125 | 11:00 | Nawabganj | 132 | 07:00 | 124 | 12:00
| Bogura | 139 | 07:00 | 114 | 18:00 | Netrakona | 134 | 18:30 | 120 | 16:00
| Bogura-230 | 139 | 06:00 | 130 | 19:00 | New | 134 | 06:00 | 125 | 12:00
| Brahmanbaria | 127 | 07:00 | 120 | 01:00 | Niamatpur | 133 | 07:00 | 120 | 19:00
| Cantonment | 132 | 05:00 | 124 | 12:00 | Noapara | 134 | 06:00 | 125 | 18:30
| Chandpur | 132 | 17:00 | 120 | 01:00 | Pabna | 135 | 06:00 | 127 | 18:30
| Chandraghona | 136 | 19:30 | 131 | 10:00 | Palashbari | 132 | 17:00 | 118 | 19:00
| Chapai | 132 | 17:00 | 127 | 00:00 | Panchagarh | 132 | 06:00 | 104 | 19:00
| Charsaidpur | 136 | 20:00 | 129 | 12:00 | Patuakhali | 135 | 06:00 | 131 | 02:00
| Chauddagram | 132 | 17:00 | 125 | 01:00 | Payra | 139 | 07:00 | 135 | 22:00
| Chhatak | 128 | 03:00 | 122 | 21:00 | PHP | 129 | 17:00 | 123 | 11:00
| Chowmuhani | 128 | 17:00 | 120 | 02:00 | Postogola | 135 | 20:00 | 130 | 10:00
| Chuadanga | 132 | 06:00 | 118 | 18:30 | Purbachal | 136 | 03:00 | 124 | 11:00
| Coxsbazar | 126 | 21:00 | 113 | 02:00 | Purbasadipur | 129 | 21:00 | 107 | 19:00
| Cumilla(N) | 134 | 17:00 | 129 | 01:00 | Rahanpur | 133 | 11:00 | 130 | 00:00
| Cumilla(S) | 132 | 17:00 | 122 | 12:00 | Rahim | 134 | 01:00 | 130 | 10:00
| Daudkandi | 126 | 17:00 | 117 | 12:00 | Rajbari | 130 | 06:00 | 122 | 22:00
| Dhaka | 137 | 06:00 | 128 | 12:00 | Rajendrapur | 135 | 18:30 | 123 | 15:00
| Dhamrai | 133 | 05:00 | 125 | 12:00 | Rajshahi | 133 | 06:00 | 124 | 23:00
| Dhanmondi | 135 | 07:00 | 129 | 12:00 | Rajshahi-230 | 134 | 17:00 | 123 | 23:00
| Dohazari | 133 | 20:00 | 122 | 01:00 | Ramganj | 122 | 11:00 | 117 | 02:00
| Faridpur | 130 | 05:00 | 122 | 23:00 | Rampur | 137 | 20:00 | 127 | 09:00
| Fatullah | 137 | 07:00 | 131 | 10:00 | Rampura | 137 | 06:00 | 128 | 11:00
| Fenchuganj | 136 | 19:00 | 129 | 02:00 | Rangamati | 135 | 20:00 | 130 | 11:00
| Feni | 131 | 17:00 | 124 | 02:00 | Rangpur | 130 | 06:00 | 118 | 19:00
| Ghorashal | 138 | 19:00 | 133 | 17:00 | Ruppur | 138 | 05:00 | 130 | 00:00
| Goalpara | 135 | 17:00 | 127 | 18:30 | Saidpur | 132 | 06:00 | 111 | 19:00
| Gollamari | 133 | 06:00 | 125 | 01:00 | Satkhira | 131 | 17:00 | 120 | 22:00
| Gopalganj | 130 | 06:00 | 124 | 18:30 | Satmasjid | 132 | 05:00 | 125 | 12:00
| Gopalganj-400 | 129 | 05:00 | 125 | 22:00 | Savar | 130 | 19:00 | 124 | 10:00
| Gulshan | 136 | 07:00 | 128 | 12:00 | ShahCement | 136 | 20:00 | 129 | 12:00
| Halishahar | 137 | 21:00 | 127 | 11:00 | Shahjadpur | 141 | 18:00 | 135 | 10:00
| Haripur | 134 | 01:00 | 130 | 10:00 | Shahjibazar | 128 | 08:00 | 122 | 15:00
| HaripurSBU | 138 | 16:00 | 130 | 10:00 | Shahmirpur | 137 | 21:00 | 128 | 11:00
| Hasnabad | 133 | 00:00 | 130 | 10:00 | Shariatpur | 130 | 07:00 | 123 | 23:00
| Hathazari | 139 | 21:00 | 131 | 11:00 | Sherpur | 129 | 11:00 | 116 | 16:00
| Ishurdi | 137 | 05:00 | 130 | 18:30 | Shikalbaha | 125 | 21:00 | 118 | 10:00
| Jaldhaka | 132 | 06:00 | 109 | 19:00 | Shikalbaha-230 | 137 | 21:00 | 129 | 11:00
| Jamalpur | 134 | 18:30 | 119 | 16:00 | Shitalakhya | 135.2 | 20:00 | 129.3 | 10:00
| Jashore | 134 | 05:00 | 125 | 18:30 | Sholosohor | 136 | 21:00 | 128 | 10:00
| Jhenaidah | 138 | 05:00 | 128 | 18:30 | Shyampur | 133 | 07:00 | 129 | 12:00
| Jhenaidah-230 | 138 | 06:00 | 129 | 18:30 | Shyampur-230 | 136 | 07:00 | 131 | 10:00
| Joydebpur | 136 | 20:00 | 127 | 12:00 | Siddhirganj | 135 | 06:00 | 129 | 12:00
| Joypurhat | 133 | 07:00 | 122 | 19:00 | Sirajganj | 133 | 06:00 | 122 | 19:00
| Juldah | 138 | 20:00 | 129 | 10:00 | Sonargaon | 132 | 17:00 | 127 | 02:00
| Kabirpur | 136 | 18:30 | 121 | 11:00 | Sreemongol | 128 | 08:00 | 124 | 23:00
| Kachua | 131 | 17:00 | 121 | 23:00 | Sreepur | 126 | 07:00 | 121 | 15:00
| Kaliakoir | 137 | 19:00 | 129 | 14:00 | Srinagar | 131 | 04:00 | 125 | 12:00
| Kallyanpur | 132 | 05:00 | 126 | 12:00 | SSM | 140 | 21:00 | 131 | 11:00
| Kalurghat | 134 | 19:30 | 129 | 10:00 | Sunamganj | 123 | 07:00 | 118 | 21:00
| Kamrangirchar | 132 | 07:00 | 123 | 10:00 | Sylhet | 129 | 07:00 | 126 | 15:00
| Kaptai | N/A | N/A | N/A | N/A | Tangail | 130 | 03:00 | 124 | 14:00
| Kazla | 134 | 05:00 | 126 | 13:00 | Thakurgaon | 130 | 06:00 | 102 | 19:00
| Keranigonj | 133 | 07:00 | 125 | 12:00 | TK | 138 | 20:00 | 129 | 11:00
| Khagrachori | 133 | 18:00 | 129 | 11:00 | Tongi | 136 | 07:00 | 127 | 11:00
| Khulna | 132 | 06:00 | 125 | 18:30 | Ullon | 136 | 06:00 | 128 | 12:00
| Khulna(S) | 133 | 06:00 | 127 | 22:00 | Uttara | 133 | 06:00 | 125 | 10:00
| Khulshi | 134 | 20:00 | 127 | 10:00 | UttaraNew | 130 | 03:00 | 124 | 11:00
| Kishoreganj | 131 | 07:00 | 124 | 23:00 | Zigatola | 132 | 07:00 | 125 | 12:00
| Kodda | 135 | 19:00 | 122 | 15:00
| KSRM | 136 | 19:00 | 128 | 10:00
| Kulaura | 130 | 06:00 | 128 | 16:00
| Kurigram | 130 | 06:00 | 112 | 19:00
| Kushtia | 134 | 06:00 | 126 | 18:30

## L-Curve
Date | 2023-09-26
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1140 | 7693 | 6059 | 13752 |  |  |  | QF-LDC-11
0:30 | 1240 | 7405.5 | 5752 | 13157.5 | Date: | 2023-09-26
1:00 | 1340 | 7118 | 5445 | 12563
1:30 | 1345 | 7006.5 | 5298.5 | 12305
2:00 | 1350 | 6895 | 5152 | 12047
2:30 | 1365 | 6864.5 | 5099 | 11963.5 | [5 empty] | Gen. at Eve. Peak | 14632 | 14632 MW (20:00 )
3:00 | 1380 | 6834 | 5046 | 11880 | [6 empty] | 20:00
3:30 | 1365 | 6705.5 | 4995 | 11700.5 | [5 empty] | Gen. at Day Peak | 12429 | 12429 MW (12:00 )
4:00 | 1350 | 6577 | 4944 | 11521 | [6 empty] | 12:00
4:30 | 1355 | 6549 | 4882.5 | 11431.5 | [5 empty] | Highest Generation | 14632
5:00 | 1360 | 6521 | 4821 | 11342 | [6 empty] | 20:00
5:30 | 1355 | 6343 | 4774 | 11117
6:00 | 1350 | 6165 | 4727 | 10892
6:30 | 1265 | 6161 | 4723.5 | 10884.5
7:00 | 1180 | 6157 | 4720 | 10877
7:30 | 1275 | 6197 | 4749.5 | 10946.5
8:00 | 1370 | 6237 | 4779 | 11016
8:30 | 1425 | 6328.5 | 4835 | 11163.5
9:00 | 1480 | 6420 | 4891 | 11311
9:30 | 1490 | 6614 | 4938.5 | 11552.5
10:00 | 1500 | 6808 | 4986 | 11794
10:30 | 1450 | 6925.5 | 5037 | 11962.5
11:00 | 1400 | 7043 | 5088 | 12131
11:30 | 1410 | 7147.5 | 5132.5 | 12280
12:00 | 1420 | 7252 | 5177 | 12429
12:30 | 1375 | 7278 | 5313.5 | 12591.5
13:00 | 1330 | 7304 | 5450 | 12754
13:30 | 1425 | 7206.5 | 5472.5 | 12679
14:00 | 1520 | 7109 | 5495 | 12604
14:30 | 1470 | 7262.5 | 5514 | 12776.5
15:00 | 1420 | 7416 | 5533 | 12949
15:30 | 1455 | 7413 | 5511 | 12924
16:00 | 1490 | 7410 | 5489 | 12899
16:30 | 1480 | 7335 | 5346.5 | 12681.5
17:00 | 1470 | 7260 | 5204 | 12464
17:30 | 1320 | 7335 | 5215.5 | 12550.5
18:00 | 1170 | 7410 | 5227 | 12637
18:30 | 1110 | 7848 | 5600.5 | 13448.5
19:00 | 1050 | 8286 | 5974 | 14260
19:30 | 1050 | 8522 | 5962 | 14484
20:00 | 1010 | 8615 | 6017 | 14632 |  |  |  | Executive Engineer
20:30 | 1050 | 8610.5 | 5973.5 | 14584 |  |  |  | Network Operation Division
21:00 | 1090 | 8606 | 5930 | 14536
21:30 | 1095 | 8433 | 6038 | 14471
22:00 | 1100 | 8260 | 6146 | 14406 |  |  |  |  | Page 6 of 7
22:30 | 1110 | 8048.5 | 6069.5 | 14118
23:00 | 1120 | 7837 | 5993 | 13830
23:30 | 1130 | 7765 | 6026 | 13791
24:00 | 1140 | 7693 | 6059 | 13752
14632 MW (20:00 )
12429 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-09-26 |  | Energy |  | 305537831
[15 empty] | 43733 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3723 | 891 | 2572 | 0 | 1832 | 4288 | 200 | 0 | 89 | 156 | 0 | 1 | 399.19
0:30 | 3807 | 900.5 | 2503.5 | 0 | 1470 | 4069.5 | 200.5 | 0 | 56 | 150 | 0 | 0.5 | 336.6375 |  |  | Date: | 43733
1:00 | 3891 | 910 | 2435 | 0 | 1108 | 3851 | 201 | 0 | 23 | 144 | 0 | 0 | 274.085
1:30 | 3794.5 | 910 | 2379 | 0 | 991 | 3867 | 201 | 0 | 19.5 | 143 | 0 | 0 | 257.85 | [9 empty] | Total Energy | 305.5378 | 305.5378 | Total Energy Gen 305.538 MKWHr Energy Not Served 3.783 MKWHr Energy Requirement 309.320 MKWHr
2:00 | 3698 | 910 | 2323 | 0 | 874 | 3883 | 201 | 0 | 16 | 142 | 0 | 0 | 241.615 | [9 empty] | Energy not Served | 3.7826 | 3.7826
2:30 | 3695.5 | 910 | 2308.5 | 0 | 861 | 3830.5 | 201 | 0 | 16 | 141 | 0 | 0 | 225.8575 | [9 empty] | Energy Requirement | 309.3204 | 309.3204
3:00 | 3693 | 910 | 2294 | 0 | 848 | 3778 | 201 | 0 | 16 | 140 | 0 | 0 | 210.1
3:30 | 3662.5 | 909.5 | 2282 | 0 | 816.5 | 3737 | 138 | 0 | 16 | 139 | 0 | 0 | 190.5225 | [8 empty] | Shortage
4:00 | 3632 | 909 | 2270 | 0 | 785 | 3696 | 75 | 0 | 16 | 138 | 0 | 0 | 170.945
4:30 | 3584 | 909 | 2209 | 0 | 777.5 | 3678 | 121 | 0 | 16 | 137 | 0 | 0 | 146.5925
5:00 | 3536 | 909 | 2148 | 0 | 770 | 3660 | 167 | 0 | 16 | 136 | 0 | 0 | 122.24
5:30 | 3464.5 | 909 | 2104.5 | 0 | 690 | 3633 | 167 | 0 | 16 | 132 | 1 | 0 | 112.69
6:00 | 3393 | 909 | 2061 | 0 | 610 | 3606 | 167 | 0 | 16 | 128 | 2 | 0 | 103.14
6:30 | 3422 | 908.5 | 2049 | 0 | 583.5 | 3582.5 | 167 | 0 | 16 | 124 | 31 | 1 | 134.1775 | [7 empty] | Coal
7:00 | 3451 | 908 | 2037 | 0 | 557 | 3559 | 167 | 0 | 16 | 120 | 60 | 2 | 165.215
7:30 | 3465.5 | 908.5 | 2044.5 | 0 | 541 | 3564 | 184.5 | 0 | 16 | 123 | 98.5 | 1 | 165.6925 | [6 empty] | Oil
8:00 | 3480 | 909 | 2052 | 0 | 525 | 3569 | 202 | 0 | 16 | 126 | 137 | 0 | 166.17
8:30 | 3505.5 | 909 | 2071.5 | 0 | 547.5 | 3566 | 202 | 0 | 16 | 131 | 214.5 | 0.5 | 173.3325
9:00 | 3531 | 909 | 2091 | 0 | 570 | 3563 | 202 | 0 | 16 | 136 | 292 | 1 | 180.495
9:30 | 3589.5 | 909 | 2200.5 | 0 | 601 | 3558 | 201.5 | 0 | 29 | 142 | 321 | 1 | 116.9875
10:00 | 3648 | 909 | 2310 | 0 | 632 | 3553 | 201 | 0 | 42 | 148 | 350 | 1 | 53.48
10:30 | 3650.5 | 909 | 2304.5 | 0 | 732.5 | 3582 | 201 | 0 | 45 | 148 | 389.5 | 0.5 | 26.74
11:00 | 3653 | 909 | 2299 | 0 | 833 | 3611 | 201 | 0 | 48 | 148 | 429 | 0 | 0
11:30 | 3663.5 | 909 | 2370.5 | 0 | 910 | 3638.5 | 200.5 | 0 | 48 | 151 | 389 | 0 | 0
12:00 | 3674 | 909 | 2442 | 0 | 987 | 3666 | 200 | 0 | 48 | 154 | 349 | 0 | 0
12:30 | 3676.5 | 909 | 2448.5 | 0 | 1054 | 3718.5 | 200 | 0 | 53 | 156 | 376 | 0 | 0
13:00 | 3679 | 909 | 2455 | 0 | 1121 | 3771 | 200 | 0 | 58 | 158 | 403 | 0 | 0
13:30 | 3679 | 909 | 2455 | 0 | 1121 | 3771 | 200 | 0 | 58 | 158 | 403 | 0 | 0
14:00 | 3679 | 909 | 2455 | 0 | 1121 | 3771 | 200 | 0 | 58 | 158 | 403 | 0 | 0
14:30 | 3612 | 909 | 2499 | 0 | 1265.5 | 3803 | 200 | 0 | 68.5 | 157 | 334 | 3.5 | 24.3525
15:00 | 3545 | 909 | 2543 | 0 | 1410 | 3835 | 200 | 0 | 79 | 156 | 265 | 7 | 48.705
15:30 | 3552 | 909 | 2481.5 | 0 | 1469 | 3848.5 | 200 | 0 | 79.5 | 157 | 220.5 | 7 | 96.455
16:00 | 3559 | 909 | 2420 | 0 | 1528 | 3862 | 200 | 0 | 80 | 158 | 176 | 7 | 144.205
16:30 | 3453.5 | 909 | 2314 | 0 | 1593 | 3851 | 200 | 0 | 98.5 | 156 | 102 | 4.5 | 160.9175
17:00 | 3348 | 909 | 2208 | 0 | 1658 | 3840 | 200 | 0 | 117 | 154 | 28 | 2 | 177.63
17:30 | 3401 | 908.5 | 2286 | 0 | 1691 | 3712 | 200 | 0 | 176.5 | 160 | 14 | 1.5 | 214.315
18:00 | 3454 | 908 | 2364 | 0 | 1724 | 3584 | 200 | 0 | 236 | 166 | 0 | 1 | 251
18:30 | 3508 | 908 | 2467 | 0 | 2137.5 | 3778.5 | 200 | 0 | 292 | 157 | 0 | 0.5 | 240.1
19:00 | 3562 | 908 | 2570 | 0 | 2551 | 3973 | 200 | 0 | 348 | 148 | 0 | 0 | 229.2
19:30 | 3579 | 777 | 2531 | 0 | 2858 | 4038 | 200 | 0 | 349 | 152 | 0 | 0 | 170.945
20:00 | 3586 | 778 | 2506 | 0 | 2998 | 4047 | 202 | 0 | 363 | 152 | 0 | 0 | 112.69
20:30 | 3583 | 778 | 2458.5 | 0 | 2919.5 | 4116.5 | 202 | 0 | 360.5 | 153 | 0 | 13 | 122.7175
21:00 | 3580 | 778 | 2411 | 0 | 2841 | 4186 | 202 | 0 | 358 | 154 | 0 | 26 | 132.745
21:30 | 3587.5 | 835 | 2399 | 0 | 2679 | 4248 | 201.5 | 0 | 358 | 150 | 0 | 13 | 159.0075
22:00 | 3595 | 892 | 2387 | 0 | 2517 | 4310 | 201 | 0 | 358 | 146 | 0 | 0 | 185.27
22:30 | 3595.5 | 892 | 2403 | 0 | 2319 | 4297.5 | 201 | 0 | 259 | 151 | 0 | 0 | 278.86
23:00 | 3596 | 892 | 2419 | 0 | 2121 | 4285 | 201 | 0 | 160 | 156 | 0 | 0 | 372.45
23:30 | 3659.5 | 891.5 | 2495.5 | 0 | 1976.5 | 4286.5 | 200.5 | 0 | 124.5 | 156 | 0 | 0.5 | 385.82 |  |  | Max Temp. in Dhaka |  | 32.5°C
24:00 | 3723 | 891 | 2572 | 0 | 1832 | 4288 | 200 | 0 | 89 | 156 | 0 | 1 | 399.19
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 305.538 MKWHr Energy Not Served 3.783 MKWHr Energy Requirement 309.320 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-09-26
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 126 | 126 | 126 | 0 | 92 | 92 | 92 | 127 | 127 | 126 | 126 | 125 | 125 | 125 | 125 | 125 | 125 | 125 |  | 125 | 125 | 127 | 127 | 126 | 126 | 125 | 2839653
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1812000
3 | Chattogram TPP-1 | 100 | 90 | 100 | 100 | 100 | 110 | 100 | 102 | 99 | 100 | 102 | 100 | 100 | 98 | 105 | 100 | 95 | 100 |  | 104 | 100 | 103 | 105 | 101 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 | 0 | [8 empty] | 5 | 8 | 8 | 8 |  | 17 | 17 | 17 | 17 | 17 | 8 | 8 | 160614
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 2 | 6 | 16 | 19 | 20 | 13 | 20 | 17 | 0 |  | 3 | [9 empty] | 122580
6 | Sikalbaha 225MW CCPP (Gas) | 224 | 224 | 224 | 222 | 223 | 222 | 225 | 219 | 218 | 222 | 215 | 214 | 217 | 214 | 217 | 219 | 218 | 209 |  | 221 | 220 | 225 | 221 | 220 | 223 | 225 | 5193818
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
Dohazari -Kalaish 100 MW Peaking
12 | Hathazari 100 MW peaking PP | [13 empty] | 15 | 32 | 32 | 56 | 56 |  | 71 | 71 | 71 | 71 | 71 | 64 | 57 | 554928
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 51 | 51 | 40 | 40 | 51 | 51 | 17 | 17 | 17 | 17 | 17 | 24 | 34 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1013673
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [16 empty] | 9 | 25 |  | 0 | [5 empty] | 0 | 40784
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 324 | 324 | 324 | 280 | 280 | 250 | 250 | 250 | 250 | 315 | 312 | 308 | 305 | 144 | 203 | 204 | 150 | 160 |  | 160 | 160 | 160 | 160 | 160 | 160 | 180 | 5852457
18 | Kodda 300 MW PP Unit-2 (Summit) | [10 empty] | 1 | 38 | 45 | 45 | 45 | 45 | 45 | 50 |  | 133 | 145 | 145 | 45 | 45 | 45 | 45 | 848073
19 | Ashuganj 195 MW PP (APSCL-United) | 88 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 86 | 86 | 88 | 88 | 107 | 107 | 107 | 107 |  | 145 | 145 | 145 | 145 | 145 | 145 | 147 | 2341818
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 150 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 150 | 150 | 150 | 147 | 146 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3391469
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 528 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 590 | 520 | 520 | 550 | 580 | 505 |  | 550 | 550 | 550 | 550 | 550 | 450 | 400 | 13658180
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 49 | 45 | 47 | 47 | 47 | 43 | 43 | 43 | 43 | 44 |  | 48 | 48 | 48 | 49 | 49 | 49 | 50 | 1137744
33 | Ashuganj 225 MW CCPP | 211 | 210 | 180 | 187 | 180 | 180 | 180 | 202 | 196 | 181 | 182 | 187 | 181 | 194 | 183 | 181 | 180 | 201 |  | 210 | 207 | 208 | 208 | 210 | 207 | 207 | 4724000
34 | Ashuganj 450 MW CCPP(South) | 315 | 280 | 280 | 285 | 280 | 280 | 335 | 310 | 305 | 310 | 310 | 310 | 310 | 285 | 270 | 270 | 270 | 330 |  | 295 | 280 | 270 | 270 | 270 | 280 | 310 | 7093000
| Ashuganj 450 MW CCPP(North) | 315 | 280 | 280 | 290 | 280 | 280 | 320 | 345 | 335 | 315 | 320 | 320 | 315 | 340 | 315 | 290 | 290 | 335 |  | 315 | 290 | 290 | 290 | 290 | 300 | 290 | 7772800
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 388 | 405 | 406 | 405 | 395 | 350 | 306 | 306 | 350 | 390 | 408 | 405 | 403 | 358 | 394 | 408 | 363 | 323 |  | 397 | 414 | 414 | 360 | 351 | 324 | 393 | 9132030
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 400 | 340 | 320 | 320 | 320 | 320 | 400 | 400 | 450 | 450 | 370 | 450 | 450 | 370 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 9538000
41 | Haripur 360 MW CCPP(HPL) | 301 | 303 | 302 | 302 | 302 | 262 | 262 | 262 | 292 | 331 | 322 | 322 | 298 | 291 | 321 | 327 | 276 | 256 |  | 332 | 332 | 332 | 281 | 282 | 282 | 331 | 7248000
42 | RPCL 210MW CCPP | 70 | 70 | 69 | 35 | 34 | 34 | 34 | 34 | 29 | 28 | 28 | 28 | 12 | 12 | 12 | 12 | 17 | 18 |  | 22 | 29 | 30 | 42 | 71 | 72 | 71 | 802560
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 9 | 26 | 38 | 42 | 53 | 24 | 51 | 8 | 38 | 21 | 5 | 0 | [8 empty] | 325750
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1006000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 696720
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86 MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 84 | 86 | 86 |  | 86 | 86 | 86 | 86 | 84 | 84 | 84 | 1921920
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 184 | 184 | 184 | 184 | 184 | 184 | 183 | 182 | 183 |  | 181 | 181 | 182 | 183 | 183 | 183 | 183 | 4736790
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 398000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 247680
54 | Hobiganj 11 MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 209328
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 44 | 47 | 50 | 50 | 47 | 47 | 47 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1158600
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 190080
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 275 | 280 | 285 | 280 | 290 | 280 | 290 | 305 | 305 | 285 | 295 | 295 | 300 | 295 | 300 | 270 | 270 |  | 290 | 265 | 260 | 270 | 285 | 270 | 290 | 7025500
| Bibiyana South 400 MW | 396 | 397 | 398 | 395 | 360 | 360 | 360 | 360 | 360 | 390 | 380 | 379 | 387 | 380 | 380 | 390 | 356 | 375 |  | 380 | 396 | 397 | 395 | 380 | 388 | 392 | 9133300
58 | Nababganj 55 MW PP (Southern power ) | [9 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 513214
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 18 | 18 | 18 | 13 | 8 | 12 | 12 | 12 | 12 | 12 |  | 9 | 18 | 18 | 18 | 18 | 18 | 12 | 337920
60 | Barabkunda 22 MW PP (Regent) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 10 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 9 | 235152
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 7 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 20 |  | 0 | 11 | 20 | 20 | 20 | 20 | 20 | 425124
62 | Tangail 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 16 | 16 | 16 | 16 | 0 | [11 empty] | 16 | 16 | 16 | 18 | 229644
63 | Impoprt (Tripura) | 144 | 142 | 140 | 138 | 136 | 128 | 120 | 126 | 136 | 148 | 148 | 154 | 158 | 160 | 156 | 158 | 154 | 166 |  | 148 | 152 | 152 | 154 | 146 | 156 | 156 | 3464640
64 | Malancha, Ctg. EPZ (United) | 39 | 34 | 40 | 40 | 40 | 40 | 38 | 11 | 4 | 4 | 3 | 5 | 7 | 6 | 3 | 3 | 12 | 14 |  | 20 | 27 | 14 | 33 | 35 | 35 | 40 | 559680
65 | Feni 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 16 | 16 | 16 | 17 | 17 | 17 | 17 | 17 | 17 |  | 18 | 0 |  | 14 | 18 | 18 | 18 | 382320
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 8 | 8 | 8 | 8 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 228420
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 802200
68 | Cumilla 25 MW PP (Summit) | 0 | 0 | 12 | 12 | 12 | 12 | 12 | 12 | 0 | 0 |  | 12 | 12 | 12 | 12 | 12 | 12 | 6 |  | 6 | 12 | 12 | 12 | 12 | 12 | 12 | 223320
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456000
70 | Summit Madhabdi | 16 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 17 | 16 | 16 | 16 | 16 | 16 |  | 3 | 16 | 16 | 16 | 16 | 16 | 18 | 398880
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 0 | 17 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 574020
72 | Rupganj 33 MW PP(Summit) | 30 | 30 | 31 | 32 | 32 | 32 | 30 | 30 | 28 | 28 | 28 | 28 | 20 | 20 | 16 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 32 | 531000
73 | Ghorashal 108 MW PP (Regent) | 52 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 40 | 51 | 53 | 51 | 51 | 51 | 52 | 51 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 928363
| Feni Lanka Power | 105 | 105 | 105 | 105 | 105 | 78 | 52 | 17 | 17 | 17 | 17 | 17 | 17 | 88 | 105 | 105 | 105 | 52 |  | 52 | 52 | 105 | 105 | 105 | 105 | 105 | 1781820
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 29 | 28 | 31 | 32 | 34 | 32 | 35 | 84 | 84 |  | 84 | 84 | 86 | 87 | 87 | 52 | 19 | 829080
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 0 | [5 empty] | 17 | 54 | 54 | 72 | 72 | 72 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 72 | 1166400
77 | Siddhirganj 100 PP(Dutch Bangla) | [14 empty] | 2 | 24 | 24 | 20 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 109997
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 288480
79 | Kodda 150 MW PP | 23 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 42 | 48 | 48 | 58 | 58 | 47 | 48 | 48 | 70 |  | 118 | 136 | 142 | 144 | 144 | 56 | 32 | 1190400
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 49 | 52 | 52 | 46 | 52 | 52 | 52 | 837321
| Gazipur 100 MW PP | 34 | 17 | 17 | 0 |  |  | 17 | 17 | 52 | 52 | 52 | 52 | 52 | 35 | 35 | 35 | 52 | 52 |  | 88 | 88 | 88 | 88 | 88 | 88 | 34 | 1074240
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 2 | 2 | 4 | 5 | 4 | 4 | 3 | 3 | 1 | 0 | [9 empty] | 29520
| Jodiac Power | 17 | 17 | 0 |  | 0 | 1 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 22 | 54 | 54 | 51 | 17 | 17 | 17 | 451268
| Karnaphuli Power Ltd. | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 34 | 49 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1295522
82 | Madanganj 102 PP(Summit) | 1 | 0 | [8 empty] | 2 | 17 | 17 | 17 | 17 | 51 | 51 | 51 |  | 55 | 85 | 85 | 55 | 34 | 34 | 34 | 453233
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 275 | 283 | 277 | 299 | 286 | 291 | 281 | 310 | 312 | 298 | 307 | 310 | 266 | 307 | 313 | 255 | 250 | 307 |  | 273 | 290 | 289 | 292 | 250 | 297 | 294 | 7000029
87 | Meghnaghat 100 MW(IEL) | [12 empty] | 1 | 3 | 7 | 8 | 8 | 8 |  | 8 | 0 |  |  |  |  | 0 | 43200
| Meghnaghat 104 MW PP (OPCL) | 35 | 17 | 22 | 34 | 34 | 34 | 17 | 17 | 17 | 17 | 17 | 18 | 40 | 58 | 72 | 69 | 72 | 72 |  | 71 | 72 | 72 | 72 | 72 | 72 | 72 | 1102080
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 58 | 58 | 58 | 58 | 58 | 0 | [7 empty] | 46 | 47 | 47 | 47 | 12 |  | 47 | 47 | 58 | 58 | 58 | 46 | 46 | 781680
92 | Fenchuganj 44 MW (Energyprima) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 46 | 48 | 47 | 46 | 46 | 46 | 40 | 44 | 44 |  | 44 | 46 | 47 | 48 | 48 | 48 | 48 | 1127304
93 | Ashuganj 51 MW PP (Midland) | 51 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 35 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 932188
94 | Gagnagar 102 MW PP (Digital Power) | 50 | 8 | 8 | 8 | 0 | [5 empty] | 8 | 40 | 40 | 58 | 58 | 58 | 58 | 58 |  | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 966816
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 5 | 0 |  |  | 0 | 0 |  |  | 3 | 6 | 6 | 23 | 35 |  | 39 | 39 | 40 | 39 | 39 | 39 | 11 | 290400
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 | [9 empty] | 0 |  |  |  |  | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [11 empty] | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 40 | 30 | 40 | 15 | 15 | 15 | 255387
100 | Manikganj 55 MW PP (Northern) | 17 | 0 | [6 empty] | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 518765
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 112 | 112 | 112 | 112 | 80 | 112 | 112 | 112 | 80 |  | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 2401200
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 0 | [9 empty] | 11850
103 | Kamalaghat 54 MW PP(Banco Energy) | [9 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 383040
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 68 | 68 | 106 | 98 | 97 | 97 | 94 | 68 | 68 | 68 |  | 142 | 153 | 153 | 153 | 153 | 68 | 67 | 2114400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 19 | 17 | 17 | 17 | 17 | 17 | 17 | 23 |  | 100 | 110 | 120 | 124 | 124 | 59 | 44 | 1087632
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 819840
116 | Chandpur 200 MW (Desh energy) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 38 | 68 | 68 | 68 | 68 | 68 | 68 | 77 |  | 87 | 87 | 86 | 86 | 86 | 86 | 48 | 1356000
117 | Ashuganj 150 MW PP (Midland) | 10 | 0 | [8 empty] | 1 | 2 | 2 | 2 | 13 | 38 | 50 | 55 |  | 80 | 110 | 107 | 95 | 60 | 10 | 10 | 558690
118 | Bibiyana-III 400 MW CCPP | 404 | 403 | 403 | 403 | 403 | 351 | 352 | 352 | 404 | 404 | 405 | 403 | 403 | 397 | 400 | 405 | 404 | 392 |  | 403 | 409 | 409 | 405 | 405 | 405 | 405 | 9543000
| Jamalpur 115 MW PP (United) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 47 | 56 | 56 | 56 | 56 | 19 | 19 | 19 |  | 94 | 94 | 94 | 94 | 94 | 18 | 18 | 942000
| Anwara 300 MW PP (United) | 70 | 70 | 70 | 70 | 70 | 15 | 15 | 15 | 15 | 15 | 15 | 60 | 100 | 100 | 120 | 120 | 120 | 150 |  | 276 | 278 | 282 | 282 | 69 | 69 | 70 | 2318400
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 12 | 0 |  |  |  | 12 |  |  | 22 | 38 | 38 | 38 | 38 |  | 45 | 50 | 50 | 50 | 50 | 50 | 50 | 603840
| Anlima Energy Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 34 | 34 | 34 | 34 | 30 | 18 | 17 |  | 31 | 51 | 51 | 51 | 51 | 51 | 51 | 717600
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 28 | 17 | 8 | 17 | 17 | 31 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 787680
| Spectra Solar Plant Ltd. | [6 empty] | 3 | 12 | 25 | 30 | 32 | 35 | 33 | 29 | 23 | 15 | 4 | [9 empty] | 233995
| Chandpur 115(Doreen) | 53 | 53 | 50 | 54 | 53 | 54 | 53 | 55 | 54 | 54 | 50 | 52 | 53 | 52 | 52 | 53 | 52 | 52 |  | 52 | 53 | 52 | 53 | 52 | 53 | 53 | 1278720
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 26 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 38 | 54 |  | 34 | 54 | 54 | 54 | 54 | 54 | 17 | 831960
| Mirsharai 150 MW (Oil) | [17 empty] | 14 |  | 0 | [5 empty] | 0 | 1673
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 0 | 2 | 7 | 7 | 2 | 1 |  | 0 | 0 | 0 | 26 | 0 | 0 | 1 | 46560
| Matarbari 2*600 MW (CPGCL) | [19 empty] | 16 | 16 | 42 | 175 | 207 | 267 | 267 | 734545
120 | Eastern Zone Total | 7118 | 6895 | 6834 | 6577 | 6521 | 6165 | 6157 | 6237 | 6420 | 6808 | 7043 | 7252 | 7304 | 7109 | 7416 | 7410 | 7260 | 7410 |  | 8286 | 8522 | 8615 | 8606 | 8260 | 7837 | 7693 | 174315501
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 48 | 0 | [8 empty] | 16 | 16 | 16 | 16 | 15 | 15 | 15 | 15 |  | 70 | 83 | 82 | 49 | 46 | 48 | 48 | 501120
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 22 |  | 41 | 0 | [5 empty] | 41760
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 35 | 35 | 17 | 0 | [5 empty] | 1 | 6 | 17 | 17 | 22 | 35 | 36 | 36 |  | 41 | 39 | 41 | 44 | 46 | 60 | 71 | 566880
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 0 | 13 | 36 | 67 | 83 | 96 | 99 | 93 | 83 | 65 | 40 | 2 | [9 empty] | 685440
131 | Rampal 1320 MW (BIFPCL) | 521 | 522 | 520 | 518 | 521 | 522 | 523 | 523 | 521 | 521 | 521 | 520 | 520 | 520 | 515 | 521 | 521 | 516 |  | 531 | 521 | 520 | 522 | 521 | 519 | 520 | 12509090
132 | United Payra Power Ltd. | 17 | 0 | [15 empty] | 11 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 141600
133 | Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 185 | 185 | 220 | 220 | 223 | 216 | 220 | 220 | 218 | 180 | 220 |  | 212 | 224 | 220 | 180 | 180 | 180 | 220 | 4900882
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [19 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 85440
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 260 | 205 | 153 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 180 | 180 | 150 | 150 |  | 268 | 307 | 307 | 307 | 307 | 307 | 307 | 4778200
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 69 | 69 | 69 | 69 | 40 | 40 | 40 | 40 | 40 | 65 | 66 | 66 | 66 | 66 | 64 | 62 | 62 | 65 |  | 62 | 65 | 62 | 66 | 62 | 66 | 66 | 1444000
140 | Bhola 33 MW PP (Venture) | 30 | 29 | 28 | 27 | 26 | 24 | 22 | 20 | 19 | 19 | 22 | 23 | 23 | 24 | 25 | 24 | 22 | 27 |  | 29 | 31 | 28 | 31 | 33 | 33 | 33 | 615362
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 49875
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 15 | 0 | [15 empty] | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 132336
146 | Bheramara HVDC | 910 | 910 | 910 | 909 | 909 | 909 | 908 | 909 | 909 | 909 | 909 | 909 | 909 | 908 | 909 | 909 | 909 | 908 |  | 908 | 777 | 778 | 778 | 892 | 892 | 891 | 21616000
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 1100 | 1100 | 1100 | 1020 | 980 | 940 | 930 | 940 | 940 | 940 | 990 | 1040 | 1160 | 1200 | 1244 | 1220 | 1200 | 1120 |  | 1220 | 1244 | 1232 | 1244 | 1244 | 1244 | 1244 | 28528400
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4379500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 10 | 38 | 38 | 31 | 31 | 0 |  | 114892
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 4 | 2 | 5 | 5 | 5 | 5 | 4 | 2 | 0 | [9 empty] | 36660
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 197 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 160 | 160 | 176 | 188 | 140 | 143 |  | 180 | 182 | 181 | 190 | 205 | 207 | 205 | 4155027
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 184 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 146 | 150 | 163 | 170 | 140 | 147 |  | 184 | 186 | 186 | 185 | 183 | 177 | 171 | 3982809
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 380 | 380 | 380 | 380 | 340 | 300 | 300 | 300 | 300 | 300 | 260 | 330 | 414 | 414 | 414 | 340 | 320 | 340 |  | 414 | 360 | 360 | 320 | 320 | 320 | 360 | 8419672
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 4 | 5 |  | 5 | 0 | [5 empty] | 10560
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 191754
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern) | [25 empty] | 0 | 0
167 | Katakhali 50 MW Peaking PP | [17 empty] | 7 |  | 38 | 39 | 40 | 40 | 40 | 40 | 0 | 197968
168 | Santahar 50 MW Peaking PP | [17 empty] | 15 |  | 25 | 25 | 32 | 32 | 32 | 0 |  | 134581
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 22 |  | 40 | 40 | 40 | 40 | 40 | 0 |  | 164272
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [19 empty] | 55 | 90 | 90 | 94 | 94 | 94 | 94 | 528000
172 | Confidence Power Bogura Unit-1 113 MW | [19 empty] | 90 | 113 | 113 | 113 | 113 | 70 | 70 | 580704
173 | Rangpur 20 MW GTPP | [21 empty] | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | [21 empty] | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 49 | 0 | [12 empty] | 2 | 70 | 92 | 99 |  | 99 | 99 | 99 | 99 | 99 | 99 | 70 | 852777
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 6 | 6 | 7 | 7 | 7 | 6 | 3 | 1 | 0 | [8 empty] | 43805
178 | Energypac Power Venture Thakurgaon Ltd. | [17 empty] | 35 |  | 0 | 35 | 108 | 113 | 113 | 75 | 75 | 485760
| Intraco Solar 30 MW | [5 empty] | 0 |  | 1 | 1 | 6 | 34 | 34 | 36 | 31 | 7 | 17 | 4 | 0 | [8 empty] | 169628
| Adani Power Jharkhanda Ltd | 1262 | 1264 | 1213 | 1216 | 1217 | 1202 | 1164 | 1164 | 1160 | 1150 | 1158 | 1164 | 1171 | 1159 | 1196 | 1211 | 1209 | 1113 |  | 1208 | 1220 | 1216 | 1208 | 1301 | 1318 | 1370 | 29023636
178 | Teesta Solar Limited |  |  |  |  | 0 | 2 | 32 | 50 | 135 | 157 | 176 | 127 | 153 | 177 | 118 | 76 | 9 | [9 empty] | 1153940