## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-09-28 | Thursday
|  | Date (day): | 2023-09-28 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14957.6 | MW |  |  | (b) At Evening Peak Hour : |  | 16878 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-09-27 | 2023-09-28 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 150 | 150 | 150 | 30 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  |  | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 52 | 22 | 53 | 53 | 55 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 397 | 409 | 412 | 412
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 332 | 327 | 330 | 330 | 30
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 390 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 16 | 72 | 82 | 18 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 276 | 281 | 310 | 310 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 17 | 80 | 85 | 85 |  | 17 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 24 | 15 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 55 | 55 | 20 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 17 | 19 | 20 | 20
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 40 | 40 | 170 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 10 | 90 | 92 | 92 |  | 8 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 160 | 188 | 0 | 0
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 20 | 92 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 35 | 17 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 64 | 149 | 48 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 35 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 37 | 37 | 38 | 38 |  | 42 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 14 | 28 | 30 | 30
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 25 | 8 | 25 | 27 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 30 | 95 | 300 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 134 | 17 | 149
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 105 | 35 | 105
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 72 | 54 | 72 | 32 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 126 | 54 | 126 | 36 |  | Fuel shortage
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 31 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 34 | 54 | 17 | 54
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 5763 | 5422 | 2281 | 3063 | 2954 | 3434 | 613 | 835
38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 98 | 105 | 100 | 100 | 75 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
39 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 17 | 8 | 17 | 8 |  | Fuel shortage
40 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 17 | 0 | 20 | 0
41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 40 | 6 | 40
42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 201 | 201 | 196 | 196
43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 218 | 219 | 225 | 225
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 51 | 51 | 51 | 54 |  | Fuel shortage
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 32 | 71 | 40 | 71 | 27 |  | Fuel shortage
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 0 | 0 | 102 |  | Fuel shortage
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 58 | 58 | 70 | 70 | 30 |  | Fuel shortage
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 37 | 45 | 25 | 50 | 50 |  | Fuel shortage
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 9 | 9 | 11 | 11 | 11 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 6 | 15 | 15 | 35
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 70 | 190 | 120 | 285 |  | 15 | Engine problem
54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 54 | 17 | 54
55 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 45 | 55 | 55 | 55 | 55 |  | Fuel shortage
56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 50 | 38 | 63 | 37 |  | Fuel shortage
57 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 34 | 51 | 34 | 51 | 65 |  | Fuel shortage
58 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 17 | 54 | 150
| SS Power I |  | Coal | SS Power | 0 | 0 | 0 | 350 | 350 | 350 | 350 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 1 | 0 | 10 | 20 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 556 | 556 | 600 | 600 |  |  | On test.
| Chattogram area Total |  |  |  |  | 2605 | 2545 | 1844 | 2171 | 2050 | 2494 | 622 | 345
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 205 | 180 | 200 | 200 | 21 |  | Gas shortage
60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 290 | 330 | 330 |  |  | FGMO
61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 280 | 330 | 330 |  |  | FGMO
62 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 49 | 49 | 50 | 50
64 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
65 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 90 | 135 | 108 | 145 | 50 |  | Gas shortae
66 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 50 |  |  | Gas shortage
67 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 43 | 50 | 150
68 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 31 |  | 21 | Machine problem
69 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
70 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 29 | 17 | 68 | 85 | 115 |  | Fuel shortage
71 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
72 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 10 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 136 | 156 | 149 | 165
73 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
74 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 52 | 52
75 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 88 | 105 | 105 |  | 9 | Engine problem
77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 15 | 87 | 27 | 85 | 28 |  | Fuel shortage
78 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 35 | 17 | 34 |  | 20 | Engine problem
79 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 53 | 53 | 34 | 50 | 65 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2896 | 1283 | 1589 | 1644 | 1935 | 279 | 630
80 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 12 | 32 | 43 | 43 | 159 |  | Gas shortage
81 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
82 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
83 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
84 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 115 | 162 | 115 | 160 | 40 |  | Fuel shortage
85 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 37 | 85 | 37 | 104 | 11 |  | Fuel shortage
86 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 43 | 0 | 50 | 0
87 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 18 | 18 | 18 | 4 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 245 | 315 | 282.6 | 343 | 159 | 4
88 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 42 | 43 | 43 | 43 |  | 27 | Machine problem.
89 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 40 | 40 |  | 50 | Machine problem
90 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 112 | 112 |  | 51 | ST Under maint.
91 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
92 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 50 | 50 | 50
93 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 45 | 44 | 40 | 46 |  | 4 | Engine problem
94 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 8 | 11 | 11
95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 66 |  | Gas shortage
96 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 75 | 84 | 86 | 86
97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 184 | 183 | 185 | 185 |  | 46 | Machine problem
99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 16 | 17 | 17 | 17
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 | 17 |  | Gas shortage
101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 290 | 300 | 300 |  |  | FGMO
102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 406 | 390 | 400 | 400 |  |  | FGMO
103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 385 | 0 | 380 | 380
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1679 | 1269 | 1682 | 1688 | 83 | 608
105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 901 | 774 | 938 | 938
106 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 32 | 32 | 82 | 33 |  | Fuel shortage
107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 26 | 25 | 40 |  | 14 | Engine problem
108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 20 | 0 | 40 | 69 |  | Fuel shortage
110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
111 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 16 | 0 | 16 | 24 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 54 | 54 | 72 | 33 |  | Fuel shortage
113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 100 | 100
114 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 92 | 0 | 100 | 0
115 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
116 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 524 | 520 | 520 | 520
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3125 | 3121 | 1534 | 1457 | 1769 | 1808 | 1035 | 14
117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 16 | 110
118 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 21 | 28 | 23 | 25 |  | 15 | Engine problem
119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 69 | 134 | 65 | 65 |  | 129 | GT-2 & ST under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
120 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1050 | 1200 | 1244 | 1244
121 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
122 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 35 | 150
123 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 200 | 307 | 300 | 300
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1560 | 1922 | 1903 | 2114 | 0 | 144
124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 32 | 0 | 38 | 14 |  | Fuel shortage
126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 18 | 0 | 0 |  | 71 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 14 | 28 | 28
128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 8 | 34 | 42 | 8
129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 30 | 40 | 10
130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 150 | 195 | 150 | 180 | 30 |  | Gas shortage
131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 150 | 137 | 140 | 140 | 80 |  | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 360 | 370 | 360 | 400
134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 24 | 32 | 18 |  | Fuel shortage
135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 52 | 0
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 63 | 50 | 91 |  | 13 | Engine problem
139 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 94 | 90 | 90 | 23 |  | Fuel shortage
141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 35 | 113 | 0
142 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1155 | 1362 | 1300 | 1400
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 1828 | 2494 | 2255 | 2654 | 774 | 87
143 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
144 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 180 | 180 | 180 | 180 |  | 94 | Machine problem
145 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 14 | 0 | 0 | 20
146 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 106 | 35 | 113 | 0
148 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
149 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 113 | 35 | 115
150 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 21 | 0 | 30 | 0
151 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 199 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 407 | 413 | 418 | 408 | 125 | 179
| Total |  |  |  |  | 24611 | 23871 | 12661 | 14693 | 14957.6 | 16878 | 3690 | 2846
A. |  | 2023-09-27 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 14693 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
2 | Minimum Generation : |  |  | 11405 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14900 | MW
3 | Day peak Generation : |  |  | 12661 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14327.75 | MW
4 | Evening peak Generation : |  |  | 14693 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 198 | MW
5 | Total Energy Generation : |  | 313.296 | MKWHr | By Solar | 2.533 | MKWHr
| By Gas : | 142.2848 | MKWHr |  | By Oil: | 36.5791 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 102.5491 | MKWHr |  | By Hydro: | 4.8965 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.0768 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3690 | MW | Dhaka | 5077.95 | 5077.95 |  | 0 |  | 18:00 |  | 194.82
|  |  | For Plants S/D or M/C prob = |  |  | 2846 | MW | Chittagong | 1401 | 1401 |  | 0 |  | 19:00 |  | 168.08
|  |  | Total = |  |  | 6536 | MW | Khulna | 1758.4 | 1758.4 |  | 0 |  | 19:30 |  | 169.035
7 | Total Gas Supplied : |  |  | 1063.43 | MMCFD |  |  | Rajshahi | 1484.4 | 1484.4 |  | 0 |  | 20:00 |  | 197.685
8 | Fuel Cost : | i) Gas : | Taka | 160382840.72 | ii) Oil : | Taka | 483427439.41 | Comilla | 1364 | 1334 |  | 30 |  | 21:00 |  | 190.045
|  | iii) Coal : | Taka | 723476230.15 | Total | Taka | 1367286510.28 | Mymensingh | 1211 | 1136 |  | 75 |  | 22:00 |  | 209.145
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 638 | 545 |  | 93 |  | 23:00 |  | 386.775
| ii) During Peak Demand : |  |  | 956 | MW (W to E) at | 20:00 | hrs | Barisal | 430 | 430 |  | 0 |  | 24:00 |  | 416.38
| iii) Maximum : |  |  | 830 | MW at | 18:30 | hrs | Rangpur | 963 | 963 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.2°C |  |  | Total | 14327.75 | 14129.75 |  | 198
B. |  | 2023-09-28 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 33.2°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 14500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 16878 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 12300 | MW
4 | Reserve(Generation end) |  |  |  | 2378 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 309.1807 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11348 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.9236 | MKWHr. | ii) HVDC Flow at Peak Time |  | 774 | MW at | 20:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.4531 | MKWHr. | iii) Maximum HVDC Flow : |  | 902 | MW at | 15:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 107.77 |  | (b) Today: | 107.96 |  | (c) Rule Curve: |  | 105.28
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-09-27 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 409 | 332 |  | 0 | 450 | 272 | 0 | 40 | 15 | 190 | 0 | 0 | 8 | 91 | 26 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 20 | 19 | 18 | 25 | 32 | 8 | 0 | 126 | 75 | 97 | 0 | 8 | 225 | 0 | 0 | 0 |  | 12 | 57 | 0 | 35 | 0 | 6 | 9 | 40 | 0 | 0 | 0 | 290 | 310 | 209 | 147 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 25 | 18 | 10 | 33 | 12 | 154 | 72 | 0 | 18 | 0 | 43 | 30 | 50 | 48 | 112 | 0 | 0 | 81 | 0 | 183 | 17 | 0 | 10 | 285 | 8 | 5 | 0 | 0 | 0 | 0 | 68 | 0 | 36 | 0 | 25 | 34 | 10 | 405 | 18 | 34 | 51 | 0 | 70 | 0 | 55 | 105 | 9 | 25 | 400 | 55 | 0 | 17 | 21 | 0 | 35 | 0 | 54 | 17 | 0 | 0 | 0 | 405 | 3 | 266 | 0 | 0 |  | 892 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 32 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 360 | 60 | 0 | 50 | 15 | 49 | 0 | 0 | 50 | 1244 | 220 | 0 | 17 | 0 | 0 | 36 | 0 | 0 | 520 | 0 | 307 | 1413 | 0 | 0 |  | 7371 | 5993 | 13364 | 3751 | 892 | 2542 | 0 | 1403 | 4335 | 201 | 0 | 83 | 154 | 0 | 3 | 435.48 | 107.72
2:00 | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 408 | 332 |  | 0 | 450 | 267 | 0 | 20 | 15 | 190 | 0 | 0 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 20 | 19 | 18 | 25 | 32 | 8 | 0 | 126 | 75 | 100 | 0 | 8 | 225 | 0 | 0 | 0 |  | 12 | 0 | 0 | 46 | 0 | 6 | 9 | 40 | 0 | 0 | 0 | 290 | 270 | 209 | 147 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 25 | 18 | 10 | 33 | 12 | 152 | 72 | 0 | 18 | 0 | 43 | 30 | 50 | 48 | 112 | 0 | 0 | 81 | 0 | 183 | 17 | 0 | 10 | 280 | 8 | 5 | 0 | 0 | 0 | 0 | 68 | 0 | 34 | 0 | 25 | 34 | 0 | 405 | 18 | 34 | 51 | 0 | 70 | 0 | 55 | 105 | 9 | 25 | 400 | 35 | 0 | 17 | 17 | 0 | 35 | 0 | 53 | 17 | 0 | 0 | 0 | 404 | 4 | 268 | 0 | 0 |  | 892 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 320 | 72 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 1244 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 521 | 0 | 307 | 1410 | 0 | 0 |  | 7143 | 5757 | 12900 | 3713 | 892 | 2490 | 0 | 1098 | 4334 | 201 | 0 | 16 | 152 | 0 | 4 | 382 | 107.73
3:00 | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 408 | 332 |  | 0 | 450 | 294 | 0 | 3 | 0 | 190 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 0 | 25 | 32 | 8 | 0 | 126 | 75 | 110 | 0 | 8 | 225 | 0 | 0 | 0 |  | 12 | 0 | 0 | 25 | 0 | 6 | 9 | 40 | 0 | 0 | 0 | 290 | 270 | 209 | 147 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 25 | 18 | 10 | 33 | 12 | 152 | 74 | 0 | 18 | 0 | 43 | 30 | 50 | 48 | 112 | 0 | 0 | 81 | 0 | 183 | 17 | 0 | 10 | 275 | 8 | 5 | 0 | 0 | 0 | 0 | 68 | 0 | 34 | 0 | 25 | 34 | 0 | 405 | 18 | 34 | 51 | 0 | 70 | 0 | 55 | 105 | 9 | 25 | 400 | 35 | 0 | 0 | 17 | 0 | 35 | 0 | 52 | 17 | 0 | 0 | 0 | 402 | 2 | 266 | 0 | 0 |  | 891 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 320 | 35 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1172 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 0 | 241 | 1409 | 0 | 0 |  | 7015 | 5511 | 12526 | 3706 | 891 | 2512 | 0 | 856 | 4190 | 201 | 0 | 16 | 152 | 0 | 2 | 357.17 | 107.74
4:00 | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 408 | 331 |  | 0 | 450 | 284 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 25 | 32 | 8 | 0 | 126 | 75 | 105 | 0 | 8 | 224 | 0 | 0 | 0 |  | 12 | 0 | 0 | 25 | 0 | 6 | 9 | 40 | 0 | 0 | 0 | 290 | 270 | 210 | 147 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 25 | 18 | 10 | 33 | 12 | 150 | 74 | 0 | 18 | 0 | 43 | 30 | 47 | 48 | 112 | 0 | 0 | 81 | 0 | 183 | 17 | 0 | 10 | 295 | 8 | 5 | 0 | 0 | 0 | 0 | 68 | 0 | 34 | 0 | 25 | 34 | 0 | 404 | 18 | 34 | 51 | 0 | 70 | 0 | 41 | 105 | 9 | 25 | 396 | 17 | 0 | 0 | 17 | 0 | 35 | 0 | 53 | 17 | 0 | 0 | 0 | 406 | 12 | 266 | 0 | 0 |  | 891 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 320 | 17 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1152 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 521 | 0 | 200 | 1341 | 0 | 0 |  | 6987 | 5368 | 12355 | 3697 | 891 | 2518 | 0 | 804 | 4066 | 201 | 0 | 16 | 150 | 0 | 12 | 329.475 | 107.75
5:00 | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 408 | 332 |  | 0 | 450 | 280 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 25 | 32 | 8 | 0 | 126 | 75 | 106 | 0 | 8 | 224 | 0 | 0 | 0 |  | 12 | 0 | 0 | 25 | 0 | 6 | 9 | 40 | 0 | 0 | 0 | 290 | 270 | 210 | 118 | 0 | 47 | 0 | 0 | 20 | 0 | 0 | 25 | 0 | 0 | 33 | 12 | 138 | 73 | 0 | 18 | 0 | 43 | 30 | 47 | 48 | 112 | 0 | 0 | 78 | 0 | 183 | 17 | 0 | 10 | 285 | 8 | 5 | 0 | 0 | 0 | 0 | 68 | 0 | 34 | 0 | 25 | 34 | 0 | 404 | 19 | 34 | 51 | 0 | 70 | 0 | 55 | 105 | 9 | 25 | 395 | 17 | 0 | 0 | 17 | 0 | 19 | 0 | 52 | 17 | 0 | 0 | 0 | 404 | 1 | 266 | 0 | 0 |  | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 320 | 17 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1122 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 518 | 0 | 200 | 1319 | 0 | 0 |  | 6852 | 5253 | 12105 | 3624 | 891 | 2439 | 0 | 786 | 4009 | 201 | 0 | 16 | 138 | 0 | 1 | 281.725 | 107.76
6:00 | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 393 | 282 |  | 0 | 380 | 260 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 18 | 25 | 32 | 8 | 0 | 126 | 75 | 106 | 0 | 8 | 228 | 0 | 0 | 0 |  | 12 | 0 | 0 | 12 | 0 | 6 | 9 | 0 | 0 | 0 | 0 | 290 | 270 | 212 | 107 | 0 | 50 | 0 | 0 | 20 | 0 | 0 | 25 | 0 | 0 | 33 | 12 | 134 | 34 | 0 | 18 | 0 | 43 | 30 | 47 | 48 | 112 | 0 | 0 | 78 | 0 | 183 | 17 | 0 | 10 | 270 | 8 | 5 | 0 | 0 | 0 | 0 | 68 | 0 | 34 | 0 | 25 | 34 | 0 | 404 | 19 | 34 | 51 | 0 | 70 | 3 | 55 | 59 | 9 | 25 | 390 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 52 | 17 | 0 | 0 | 0 | 382 | 0 | 268 | 0 | 0 |  | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 326 | 17 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1072 | 180 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 514 | 0 | 200 | 1262 | 2 | 0 |  | 6502 | 5114 | 11616 | 3568 | 891 | 2197 | 0 | 728 | 3878 | 201 | 0 | 16 | 134 | 3 | 0 | 175.72 | 107.77
7:00 | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 350 | 283 |  | 0 | 350 | 300 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 18 | 25 | 32 | 8 | 0 | 126 | 75 | 96 | 0 | 8 | 225 | 0 | 0 | 0 |  | 12 | 0 | 0 | 12 | 0 | 6 | 9 | 25 | 0 | 0 | 0 | 300 | 275 | 208 | 76 | 0 | 50 | 0 | 0 | 20 | 0 | 0 | 20 | 16 | 8 | 33 | 12 | 128 | 35 | 0 | 18 | 0 | 43 | 30 | 47 | 48 | 80 | 0 | 0 | 78 | 0 | 183 | 17 | 0 | 10 | 265 | 8 | 5 | 0 | 0 | 0 | 0 | 67 | 0 | 34 | 3 | 25 | 34 | 0 | 378 | 19 | 34 | 51 | 0 | 70 | 17 | 55 | 17 | 9 | 25 | 360 | 17 | 9 | 0 | 17 | 0 | 17 | 3 | 53 | 17 | 0 | 0 | 0 | 405 | 18 | 267 | 0 | 0 |  | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 320 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1022 | 180 | 0 | 0 | 1 | 9 | 0 | 0 | 0 | 523 | 5 | 200 | 1168 | 32 | 0 |  | 6410 | 4995 | 11405 | 3506 | 892 | 2156 | 0 | 661 | 3765 | 201 | 0 | 16 | 128 | 62 | 18 | 186.225 | 107.78
8:00 | 0 | 0 | 155 | 0 | 0 | 52 | 0 | 347 | 266 |  | 0 | 320 | 299 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 18 | 25 | 32 | 8 | 0 | 126 | 75 | 108 | 0 | 8 | 224 | 0 | 0 | 0 |  | 12 | 0 | 0 | 12 | 0 | 6 | 9 | 12 | 0 | 0 | 0 | 350 | 310 | 207 | 78 | 0 | 50 | 0 | 0 | 20 | 0 | 0 | 8 | 18 | 8 | 33 | 12 | 124 | 34 | 0 | 18 | 0 | 43 | 30 | 47 | 48 | 80 | 0 | 0 | 78 | 0 | 183 | 17 | 0 | 10 | 280 | 0 | 8 | 0 | 0 | 0 | 0 | 67 | 0 | 35 | 11 | 25 | 34 | 0 | 378 | 19 | 34 | 51 | 1 | 70 | 17 | 55 | 17 | 9 | 25 | 360 | 17 | 22 | 0 | 17 | 0 | 17 | 12 | 53 | 17 | 0 | 0 | 0 | 400 | 7 | 267 | 0 | 0 |  | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 280 | 17 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1022 | 184 | 0 | 0 | 2 | 29 | 0 | 0 | 0 | 522 | 14 | 200 | 1169 | 85 | 0 |  | 6457 | 4994 | 11451 | 3547 | 892 | 2076 | 0 | 650 | 3760 | 201 | 0 | 16 | 124 | 178 | 7 | 123.195 | 107.79
9:00 | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 330 | 302 |  | 0 | 380 | 265 | 0 | 4 | 0 | 160 | 0 | 0 | 3 | 16 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 17 | 19 | 18 | 25 | 28 | 8 | 0 | 127 | 75 | 95 | 0 | 8 | 228 | 0 | 0 | 0 |  | 18 | 0 | 0 | 12 | 0 | 6 | 9 | 4 | 0 | 0 | 0 | 280 | 310 | 208 | 78 | 0 | 50 | 0 | 0 | 39 | 0 | 0 | 8 | 18 | 8 | 33 | 12 | 120 | 26 | 0 | 18 | 1 | 43 | 30 | 47 | 48 | 80 | 0 | 0 | 78 | 0 | 183 | 17 | 0 | 9 | 310 | 8 | 11 | 0 | 5 | 0 | 0 | 67 | 0 | 35 | 11 | 25 | 34 | 0 | 404 | 19 | 52 | 51 | 2 | 70 | 17 | 55 | 17 | 9 | 25 | 400 | 17 | 37 | 17 | 17 | 0 | 17 | 24 | 52 | 17 | 0 | 0 | 0 | 400 | 6 | 384 | 0 | 0 |  | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 320 | 17 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 1022 | 184 | 0 | 0 | 1 | 42 | 0 | 0 | 0 | 522 | 23 | 200 | 1162 | 131 | 0 |  | 6768 | 5092 | 11860 | 3512 | 892 | 2214 | 0 | 752 | 3870 | 202 | 0 | 16 | 120 | 276 | 6 | 181.45 | 107.8
10:00 | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 331 | 263 |  | 0 | 350 | 286 | 0 | 17 | 12 | 160 | 0 | 0 | 8 | 16 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 17 | 19 | 18 | 25 | 30 | 8 | 0 | 127 | 75 | 100 | 0 | 8 | 222 | 0 | 0 | 0 |  | 18 | 0 | 0 | 12 | 0 | 0 | 9 | 6 | 0 | 0 | 0 | 280 | 270 | 180 | 78 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 8 | 33 | 12 | 120 | 27 | 0 | 18 | 1 | 42 | 30 | 47 | 45 | 80 | 0 | 0 | 78 | 0 | 183 | 17 | 0 | 9 | 270 | 8 | 11 | 0 | 30 | 0 | 0 | 67 | 0 | 35 | 11 | 25 | 34 | 0 | 404 | 19 | 52 | 51 | 4 | 70 | 17 | 55 | 17 | 9 | 25 | 386 | 17 | 36 | 17 | 17 | 0 | 17 | 28 | 54 | 34 | 0 | 0 | 0 | 350 | 5 | 556 | 0 | 0 |  | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 280 | 17 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 1022 | 185 | 0 | 0 | 2 | 60 | 0 | 0 | 0 | 522 | 23 | 200 | 1158 | 168 | 0 |  | 6837 | 5106 | 11943 | 3432 | 892 | 2097 | 0 | 820 | 3988 | 202 | 0 | 48 | 120 | 339 | 5 | 120.33 | 107.81
11:00 | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 344 | 301 |  | 0 | 350 | 300 | 0 | 17 | 15 | 160 | 0 | 0 | 8 | 16 | 64 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 17 | 19 | 18 | 25 | 8 | 8 | 0 | 126 | 75 | 105 | 0 | 8 | 220 | 0 | 0 | 0 |  | 18 | 8 | 0 | 58 | 0 | 6 | 9 | 6 | 0 | 0 | 0 | 290 | 280 | 185 | 76 | 0 | 45 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 8 | 25 | 6 | 124 | 12 | 0 | 18 | 2 | 42 | 30 | 49 | 45 | 80 | 0 | 0 | 78 | 0 | 183 | 17 | 0 | 9 | 295 | 8 | 11 | 0 | 30 | 0 | 0 | 114 | 0 | 23 | 15 | 30 | 34 | 0 | 404 | 37 | 52 | 51 | 5 | 70 | 17 | 55 | 17 | 8 | 25 | 384 | 17 | 45 | 17 | 27 | 0 | 17 | 28 | 52 | 34 | 0 | 0 | 0 | 350 | 2 | 554 | 0 | 0 |  | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 280 | 17 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 1022 | 185 | 0 | 0 | 4 | 92 | 0 | 0 | 0 | 522 | 26 | 200 | 1164 | 199 | 0 |  | 7071 | 5176 | 12247 | 3415 | 892 | 2170 | 0 | 957 | 3992 | 201 | 0 | 72 | 124 | 422 | 2 | 30.56 | 107.82
12:00 | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 397 | 332 |  | 0 | 420 | 276 | 0 | 17 | 15 | 160 | 0 | 0 | 10 | 20 | 64 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 17 | 19 | 18 | 25 | 14 | 8 | 0 | 126 | 75 | 98 | 0 | 8 | 218 | 0 | 0 | 0 |  | 18 | 32 | 0 | 58 | 0 | 6 | 9 | 6 | 0 | 0 | 0 | 280 | 270 | 205 | 90 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 8 | 25 | 12 | 136 | 12 | 0 | 18 | 2 | 42 | 30 | 50 | 45 | 112 | 0 | 0 | 75 | 0 | 184 | 16 | 0 | 10 | 305 | 8 | 11 | 0 | 30 | 0 | 0 | 115 | 0 | 17 | 17 | 37 | 29 | 0 | 406 | 37 | 52 | 51 | 5 | 70 | 17 | 45 | 17 | 15 | 25 | 385 | 17 | 43 | 35 | 34 | 0 | 17 | 31 | 53 | 34 | 0 | 0 | 0 | 350 | 1 | 556 | 0 | 0 |  | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 360 | 17 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1050 | 220 | 0 | 0 | 5 | 92 | 0 | 0 | 0 | 524 | 21 | 200 | 1155 | 199 | 0 |  | 7332 | 5329 | 12661 | 3481 | 901 | 2425 | 0 | 983 | 4015 | 201 | 0 | 96 | 136 | 422 | 1 | 26.74 | 107.83
13:00 | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 396 | 286 |  | 0 | 420 | 292 | 8 | 26 | 15 | 160 | 0 | 0 | 50 | 50 | 64 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 17 | 19 | 18 | 25 | 14 | 8 | 0 | 125 | 75 | 100 | 0 | 8 | 217 | 0 | 0 | 0 |  | 18 | 32 | 0 | 58 | 0 | 6 | 9 | 12 | 0 | 0 | 0 | 315 | 295 | 204 | 105 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 8 | 33 | 12 | 138 | 12 | 0 | 18 | 2 | 42 | 30 | 50 | 44 | 112 | 0 | 0 | 78 | 0 | 184 | 17 | 0 | 10 | 280 | 8 | 11 | 0 | 75 | 0 | 0 | 116 | 0 | 17 | 18 | 37 | 17 | 0 | 354 | 37 | 52 | 51 | 4 | 70 | 17 | 36 | 17 | 36 | 25 | 370 | 55 | 44 | 54 | 34 | 0 | 34 | 30 | 53 | 34 | 0 | 0 | 0 | 350 | 1 | 554 | 0 | 0 |  | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 390 | 17 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1100 | 224 | 0 | 0 | 1 | 65 | 0 | 0 | 0 | 521 | 35 | 200 | 1156 | 43 | 0 |  | 7507 | 5238 | 12745 | 3483 | 901 | 2426 | 0 | 1190 | 4061 | 200 | 0 | 96 | 138 | 249 | 1 | 33.425 | 107.84
14:00 | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 373 | 287 |  | 0 | 420 | 306 | 17 | 34 | 15 | 160 | 0 | 0 | 50 | 50 | 62 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 19 | 18 | 25 | 20 | 8 | 0 | 125 | 75 | 105 | 0 | 8 | 214 | 0 | 0 | 0 |  | 18 | 40 | 0 | 58 | 0 | 6 | 9 | 8 | 0 | 0 | 0 | 315 | 310 | 205 | 107 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 8 | 33 | 12 | 148 | 12 | 0 | 18 | 1 | 42 | 30 | 50 | 44 | 112 | 0 | 0 | 78 | 0 | 183 | 17 | 0 | 10 | 310 | 8 | 11 | 0 | 95 | 0 | 0 | 116 | 0 | 17 | 16 | 37 | 17 | 0 | 354 | 37 | 52 | 34 | 4 | 70 | 17 | 50 | 17 | 37 | 25 | 370 | 69 | 38 | 54 | 34 | 0 | 35 | 29 | 54 | 34 | 0 | 0 | 0 | 350 | 5 | 553 | 0 | 0 |  | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 414 | 17 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 1100 | 224 | 0 | 0 | 4 | 41 | 0 | 0 | 0 | 522 | 30 | 200 | 1160 | 36 | 0 |  | 7630 | 5226 | 12856 | 3478 | 901 | 2493 | 0 | 1259 | 4065 | 200 | 0 | 102 | 148 | 205 | 5 | 22.92 | 107.82
15:00 | 0 | 0 | 154 | 0 | 0 | 52 | 0 | 393 | 331 |  | 0 | 420 | 297 | 18 | 34 | 15 | 160 | 0 | 0 | 50 | 50 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 19 | 18 | 25 | 20 | 8 | 0 | 125 | 75 | 105 | 0 | 8 | 215 | 0 | 0 | 0 |  | 18 | 39 | 0 | 58 | 0 | 6 | 9 | 5 | 0 | 0 | 0 | 310 | 305 | 205 | 107 | 0 | 46 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 10 | 33 | 12 | 144 | 12 | 0 | 18 | 2 | 40 | 30 | 50 | 44 | 113 | 0 | 0 | 78 | 0 | 180 | 17 | 0 | 10 | 310 | 8 | 11 | 0 | 95 | 0 | 0 | 116 | 0 | 17 | 13 | 37 | 17 | 0 | 366 | 37 | 52 | 34 | 3 | 70 | 17 | 55 | 39 | 39 | 25 | 381 | 53 | 7 | 54 | 34 | 0 | 35 | 23 | 53 | 34 | 0 | 0 | 0 | 350 | 6 | 556 | 0 | 0 |  | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 414 | 17 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1140 | 220 | 0 | 0 | 5 | 31 | 0 | 0 | 0 | 522 | 24 | 200 | 1229 | 56 | 0 |  | 7687 | 5341 | 13028 | 3517 | 902 | 2522 | 0 | 1290 | 4177 | 200 | 0 | 103 | 144 | 167 | 6 | 68.76 | 107.86
16:00 | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 398 | 323 |  | 0 | 420 | 268 | 17 | 34 | 15 | 160 | 0 | 0 | 44 | 50 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 19 | 18 | 25 | 20 | 8 | 0 | 125 | 75 | 107 | 0 | 8 | 218 | 0 | 0 | 0 |  | 18 | 40 | 0 | 58 | 0 | 6 | 9 | 7 | 0 | 0 | 0 | 305 | 305 | 205 | 107 | 0 | 46 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 10 | 33 | 12 | 142 | 12 | 0 | 18 | 1 | 40 | 30 | 50 | 20 | 112 | 0 | 0 | 81 | 0 | 181 | 17 | 0 | 10 | 280 | 8 | 11 | 0 | 45 | 0 | 0 | 67 | 0 | 17 | 6 | 37 | 17 | 0 | 366 | 18 | 52 | 34 | 1 | 70 | 17 | 55 | 70 | 39 | 25 | 388 | 66 | 20 | 54 | 34 | 0 | 35 | 19 | 53 | 34 | 0 | 0 | 0 | 350 | 4 | 554 | 0 | 0 |  | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 414 | 24 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1210 | 220 | 0 | 0 | 2 | 41 | 0 | 0 | 0 | 520 | 13 | 200 | 1211 | 50 | 0 |  | 7522 | 5413 | 12935 | 3552 | 901 | 2436 | 0 | 1216 | 4225 | 200 | 0 | 104 | 142 | 155 | 4 | 119.375 | 107.87
17:00 | 0 | 0 | 143 | 0 | 0 | 52 | 0 | 399 | 273 |  | 0 | 370 | 252 | 16 | 34 | 15 | 160 | 0 | 0 | 24 | 24 | 64 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 19 | 18 | 25 | 21 | 8 | 0 | 125 | 75 | 105 | 0 | 8 | 220 | 0 | 0 | 0 |  | 18 | 40 | 0 | 58 | 0 | 18 | 9 | 12 | 0 | 0 | 0 | 290 | 305 | 207 | 107 | 0 | 47 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 10 | 33 | 12 | 140 | 12 | 0 | 18 | 0 | 40 | 30 | 50 | 20 | 80 | 0 | 0 | 84 | 0 | 181 | 17 | 0 | 10 | 270 | 8 | 11 | 0 | 45 | 0 | 0 | 77 | 0 | 17 | 0 | 37 | 17 | 0 | 330 | 18 | 52 | 34 | 0 | 70 | 17 | 55 | 70 | 84 | 25 | 386 | 72 | 5 | 54 | 34 | 0 | 35 | 7 | 53 | 36 | 0 | 0 | 0 | 350 | 7 | 542 | 0 | 0 |  | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 10 | 0 | 67 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 300 | 52 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1180 | 180 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 520 | 4 | 200 | 1206 | 16 | 0 |  | 7317 | 5181 | 12498 | 3485 | 901 | 2132 | 0 | 1290 | 4178 | 200 | 0 | 115 | 140 | 50 | 7 | 145.16 | 107.88
18:00 | 0 | 0 | 150 | 0 | 0 | 22 | 0 | 337 | 292 |  | 0 | 330 | 310 | 17 | 35 | 28 | 160 | 0 | 0 | 24 | 32 | 64 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 19 | 18 | 25 | 28 | 17 | 0 | 125 | 75 | 105 | 0 | 8 | 216 | 0 | 0 | 0 |  | 18 | 58 | 17 | 58 | 0 | 37 | 9 | 14 | 0 | 0 | 0 | 340 | 315 | 201 | 113 | 0 | 48 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 10 | 33 | 12 | 166 | 21 | 0 | 18 | 0 | 41 | 30 | 31 | 28 | 112 | 0 | 0 | 84 | 0 | 181 | 17 | 0 | 10 | 270 | 8 | 8 | 0 | 45 | 0 | 0 | 67 | 0 | 33 | 0 | 41 | 17 | 10 | 369 | 18 | 70 | 51 | 0 | 70 | 21 | 55 | 70 | 86 | 25 | 360 | 72 | 0 | 54 | 51 | 0 | 35 | 0 | 54 | 54 | 0 | 0 | 0 | 350 | 2 | 555 | 0 | 0 |  | 902 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 31 | 15 | 8 | 68 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 12 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 414 | 54 | 0 | 6 | 15 | 55 | 0 | 0 | 35 | 1110 | 180 | 0 | 2 | 0 | 0 | 36 | 0 | 0 | 521 | 0 | 205 | 1212 | 0 | 0 |  | 7581 | 5415 | 12996 | 3486 | 902 | 2288 | 0 | 1609 | 4133 | 200 | 12 | 198 | 166 | 0 | 2 | 194.82 | 107.88
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 150 | 0 | 0 | 22 | 0 | 396 | 333 |  | 0 | 390 | 292 | 17 | 69 | 25 | 185 | 0 | 0 | 62 | 92 | 149 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 18 | 25 | 28 | 25 | 0 | 125 | 75 | 100 | 0 | 17 | 218 | 0 | 0 | 0 |  | 18 | 71 | 17 | 58 | 0 | 40 | 9 | 22 | 0 | 0 | 0 | 285 | 280 | 180 | 135 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 160 | 30 | 0 | 18 | 0 | 41 | 30 | 50 | 32 | 112 | 0 | 0 | 84 | 0 | 182 | 17 | 0 | 10 | 290 | 8 | 8 | 0 | 95 | 0 | 0 | 162 | 0 | 117 | 0 | 42 | 17 | 85 | 391 | 85 | 105 | 51 | 0 | 180 | 54 | 55 | 88 | 86 | 50 | 0 | 72 | 0 | 126 | 48 | 0 | 35 | 0 | 53 | 54 | 0 | 17 | 0 | 350 | 1 | 556 | 0 | 0 |  | 901 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 37 | 21 | 16 | 68 | 27 | 16 | 0 | 0 | 0 | 32 | 5 | 63 | 0 | 8 | 39 | 8 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 16 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 320 | 54 | 0 | 86 | 15 | 101 | 0 | 0 | 113 | 1170 | 220 | 0 | 17 | 0 | 0 | 108 | 0 | 0 | 520 | 0 | 260 | 1344 | 0 | 0 |  | 8363 | 6161 | 14524 | 3159 | 901 | 2390 | 0 | 2834 | 4380 | 200 | 16 | 483 | 160 | 0 | 1 | 168.08 | 107.9
19:30 | 0 | 0 | 150 | 0 | 0 | 22 | 0 | 409 | 332 |  | 0 | 390 | 296 | 17 | 80 | 25 | 189 | 0 | 0 | 90 | 92 | 149 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 18 | 25 | 28 | 25 | 0 | 125 | 75 | 100 | 0 | 17 | 219 | 0 | 0 | 0 |  | 18 | 71 | 16 | 58 | 0 | 40 | 9 | 27 | 0 | 0 | 0 | 285 | 280 | 184 | 135 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 162 | 31 | 0 | 18 | 0 | 41 | 30 | 50 | 35 | 112 | 0 | 0 | 84 | 0 | 182 | 17 | 0 | 10 | 300 | 8 | 8 | 0 | 95 | 0 | 0 | 162 | 0 | 133 | 0 | 44 | 17 | 10 | 376 | 85 | 105 | 51 | 0 | 180 | 54 | 55 | 88 | 86 | 50 | 0 | 72 | 0 | 126 | 51 | 0 | 35 | 0 | 53 | 54 | 0 | 17 | 0 | 350 | 0 | 556 | 0 | 0 |  | 773 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 26 | 20 | 16 | 98 | 27 | 16 | 0 | 0 | 0 | 32 | 5 | 63 | 14 | 8 | 39 | 8 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 16 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 370 | 54 | 0 | 94 | 15 | 106 | 0 | 0 | 113 | 1200 | 220 | 0 | 17 | 0 | 0 | 108 | 0 | 0 | 520 | 0 | 275 | 1369 | 0 | 0 |  | 8377 | 6206 | 14583 | 3205 | 773 | 2461 | 0 | 2846 | 4450 | 200 | 16 | 470 | 162 | 0 | 0 | 169.035 | 0
20:00 | 0 | 0 | 150 | 0 | 0 | 22 | 0 | 409 | 327 |  | 0 | 390 | 281 | 16 | 80 | 24 | 188 | 0 | 0 | 90 | 92 | 149 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 18 | 25 | 28 | 25 | 0 | 126 | 75 | 105 | 0 | 17 | 219 | 0 | 0 | 0 |  | 18 | 71 | 17 | 58 | 0 | 40 | 9 | 15 | 0 | 0 | 0 | 290 | 280 | 180 | 135 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 156 | 32 | 0 | 18 | 0 | 43 | 30 | 50 | 44 | 112 | 0 | 0 | 84 | 0 | 183 | 17 | 0 | 10 | 290 | 8 | 8 | 0 | 95 | 0 | 0 | 162 | 0 | 134 | 0 | 45 | 17 | 43 | 390 | 85 | 105 | 51 | 0 | 190 | 54 | 55 | 88 | 87 | 50 | 0 | 72 | 0 | 126 | 51 | 0 | 35 | 0 | 53 | 54 | 0 | 17 | 0 | 350 | 0 | 556 | 0 | 0 |  | 774 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 26 | 20 | 16 | 134 | 28 | 16 | 0 | 0 | 0 | 32 | 18 | 63 | 14 | 8 | 40 | 8 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 14 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 370 | 54 | 0 | 94 | 15 | 106 | 0 | 0 | 113 | 1200 | 220 | 0 | 17 | 0 | 0 | 113 | 0 | 0 | 520 | 0 | 307 | 1362 | 0 | 0 |  | 8407 | 6286 | 14693 | 3264 | 774 | 2429 | 0 | 2895 | 4475 | 201 | 14 | 485 | 156 | 0 | 0 | 197.685 | 107.89
21:00 | 0 | 0 | 150 | 0 | 0 | 32 | 0 | 413 | 332 |  | 0 | 420 | 290 | 0 | 80 | 24 | 189 | 0 | 0 | 80 | 92 | 115 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 18 | 25 | 28 | 25 | 0 | 126 | 75 | 100 | 0 | 17 | 220 | 0 | 0 | 0 |  | 18 | 40 | 17 | 58 | 0 | 40 | 9 | 34 | 0 | 0 | 0 | 310 | 305 | 180 | 135 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 160 | 32 | 0 | 18 | 0 | 41 | 30 | 50 | 47 | 112 | 0 | 0 | 84 | 0 | 183 | 17 | 0 | 10 | 280 | 8 | 8 | 0 | 45 | 0 | 0 | 162 | 0 | 131 | 0 | 46 | 17 | 10 | 390 | 85 | 88 | 51 | 0 | 190 | 54 | 55 | 106 | 87 | 50 | 0 | 71 | 0 | 126 | 51 | 0 | 35 | 0 | 54 | 54 | 0 | 17 | 0 | 350 | 0 | 555 | 0 | 0 |  | 774 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 31 | 16 | 0 | 0 | 0 | 0 | 24 | 32 | 14 | 8 | 39 | 8 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 414 | 54 | 0 | 94 | 15 | 106 | 0 | 0 | 113 | 1212 | 220 | 0 | 17 | 0 | 0 | 113 | 0 | 0 | 520 | 0 | 307 | 1408 | 0 | 0 |  | 8345 | 6256 | 14601 | 3307 | 774 | 2542 | 0 | 2769 | 4532 | 201 | 0 | 316 | 160 | 0 | 0 | 190.045 | 107.9
22:00 | 0 | 0 | 150 | 0 | 0 | 32 | 0 | 411 | 333 |  | 0 | 420 | 298 | 0 | 58 | 15 | 175 | 0 | 0 | 31 | 92 | 115 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 18 | 25 | 30 | 25 | 0 | 127 | 75 | 105 | 0 | 17 | 219 | 0 | 0 | 0 |  | 18 | 40 | 0 | 58 | 0 | 40 | 9 | 34 | 0 | 0 | 0 | 310 | 305 | 180 | 137 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 160 | 55 | 0 | 18 | 0 | 43 | 30 | 50 | 48 | 112 | 0 | 0 | 81 | 0 | 183 | 17 | 0 | 10 | 285 | 8 | 8 | 0 | 45 | 0 | 0 | 162 | 0 | 115 | 0 | 47 | 17 | 10 | 390 | 75 | 70 | 51 | 0 | 190 | 17 | 55 | 106 | 87 | 50 | 0 | 72 | 0 | 126 | 51 | 0 | 35 | 0 | 53 | 54 | 0 | 17 | 0 | 350 | 0 | 556 | 0 | 0 |  | 774 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 31 | 16 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 8 | 39 | 0 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 414 | 54 | 0 | 94 | 15 | 113 | 0 | 0 | 113 | 1222 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 521 | 0 | 307 | 1408 | 0 | 0 |  | 8199 | 6232 | 14431 | 3324 | 774 | 2556 | 0 | 2596 | 4544 | 202 | 0 | 275 | 160 | 0 | 0 | 209.145 | 107.9
23:00 | 0 | 0 | 150 | 0 | 0 | 32 | 0 | 412 | 332 |  | 0 | 420 | 298 | 0 | 52 | 15 | 140 | 0 | 0 | 35 | 92 | 64 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 18 | 25 | 31 | 25 | 0 | 127 | 75 | 100 | 0 | 8 | 218 | 0 | 0 | 0 |  | 18 | 40 | 0 | 58 | 0 | 40 | 9 | 39 | 0 | 0 | 0 | 310 | 305 | 180 | 157 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 158 | 72 | 0 | 18 | 0 | 41 | 30 | 50 | 48 | 112 | 0 | 0 | 81 | 0 | 183 | 17 | 0 | 10 | 280 | 8 | 8 | 0 | 45 | 0 | 0 | 67 | 0 | 112 | 0 | 48 | 17 | 12 | 390 | 18 | 70 | 51 | 0 | 197 | 17 | 55 | 106 | 69 | 50 | 15 | 72 | 0 | 126 | 51 | 0 | 35 | 0 | 52 | 54 | 0 | 17 | 0 | 350 | 0 | 556 | 0 | 0 |  | 793 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 31 | 16 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 39 | 0 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 360 | 54 | 0 | 94 | 32 | 106 | 0 | 0 | 113 | 1222 | 220 | 0 | 25 | 0 | 0 | 115 | 0 | 0 | 521 | 0 | 307 | 1413 | 0 | 0 |  | 7981 | 6214 | 14195 | 3317 | 793 | 2521 | 0 | 2431 | 4549 | 202 | 0 | 224 | 158 | 0 | 0 | 386.775 | 107.91
24:00 | 0 | 0 | 150 | 0 | 0 | 35 | 0 | 411 | 282 |  | 0 | 450 | 286 | 24 | 80 | 15 | 100 | 0 | 92 | 82 | 91 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 19 | 18 | 25 | 32 | 8 | 0 | 127 | 75 | 105 | 0 | 8 | 224 | 0 | 0 | 0 |  | 12 | 40 | 0 | 58 | 0 | 7 | 9 | 41 | 0 | 0 | 0 | 310 | 305 | 180 | 157 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 152 | 72 | 0 | 18 | 0 | 41 | 30 | 50 | 45 | 112 | 0 | 0 | 81 | 0 | 183 | 17 | 0 | 10 | 280 | 8 | 8 | 0 | 97 | 0 | 0 | 68 | 0 | 18 | 0 | 25 | 17 | 48 | 383 | 18 | 35 | 51 | 0 | 178 | 17 | 55 | 106 | 15 | 50 | 35 | 63 | 0 | 108 | 51 | 0 | 35 | 0 | 54 | 17 | 0 | 17 | 0 | 350 | 0 | 556 | 0 | 0 |  | 792 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 136 | 31 | 32 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 39 | 0 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 360 | 54 | 0 | 94 | 50 | 113 | 0 | 0 | 113 | 1222 | 220 | 0 | 72 | 0 | 0 | 115 | 0 | 0 | 520 | 0 | 307 | 1408 | 0 | 0 |  | 7809 | 6305 | 14114 | 3377 | 792 | 2491 | 0 | 2333 | 4543 | 202 | 0 | 224 | 152 | 0 | 0 | 416.38 | 107.91
KWH | 0 | 0 | 3584094 | 0 | 0 | 1070545 | 0 | 9396230 | 7502000 |  | 0 | 9367000 | 6907025 | 146880 | 680253 | 329201 | 4249565 | 0 | 22000 | 628800 | 978912 | 1336800 | 0 | 0 | 0 | 0 | 388080 | 529005 | 497519 | 387000 | 456000 | 411120 | 599100 | 616100 | 285600 | 0 | 3076495 | 1820000 | 2400000 | 0 | 245523 | 5210628 | 0 | 0 | 0 |  | 392160 | 653280 | 72415 | 978480 | 0 | 370560 | 218688 | 560640 | 0 | 0 | 0 | 7574300 | 7105000 | 4800000 | 2826909 | 0 | 1148688 | 0 | 0 | 1107396 | 0 | 0 | 565018 | 404892 | 204840 | 804100 | 278200 | 3453120 | 860160 | 0 | 411948 | 12300 | 992000 | 681480 | 1157400 | 734544 | 2444482 | 0 | 0 | 1906560 | 0 | 4730380 | 393000 | 0 | 243000 | 7004500 | 170880 | 198210 | 0 | 1018 | 0 | 0 | 2251200 | 0 | 1147536 | 120690 | 794880 | 626400 | 237527 | 9316000 | 798000 | 1307520 | 1216909 | 27719 | 2408727 | 456391 | 1296358 | 1603980 | 819840 | 745920 | 7192400 | 1104000 | 284530 | 1160640 | 784091 | 0 | 738000 | 228069 | 1291200 | 798120 | 0 | 100363 | 0 | 9016362 | 76800 | 11090909 | 0 | 0 |  | 20923636 | 0 | 0 | 0 | 354240 | 0 | 0 | 0 | 74400 | 48512 | 49875 | 1892000 | 590768 | 126816 | 0 | 0 | 0 | 74143 | 20878 | 266912 | 23840 | 33924 | 208452 | 26578 | 159120 | 0 | 0 | 170730 | 0 | 0 | 4374000 | 32000 | 0 | 4549773 | 0 | 0 | 0 | 0 | 0 | 3855418 | 0 | 8464836 | 846720 | 0 | 689184 | 165024 | 908899 | 0 | 42912 | 788256 | 29221400 | 5112273 | 0 | 181200 | 31740 | 532800 | 733056 | 0 | 0 | 12472730 | 190403 | 5694500 | 30679159 | 1061810 | 0 |  | 177623104 | 135672917 | 313296021 | 85284924 | 20923636 | 56999878 | 0 | 33531860 | 102549060 | 4896495 | 32000 | 3015275 | 3453120 | 2532973 | 76800 | 0
Fuel Cost | 0 | 0 | 5232777.24 | 0 | 0 | 1423824.85 | 0 | 9866041.5 | 8102160 |  | 0 | 10210030 | 7666797.75 | 1642118.4 | 9013352.25 | 4361913.25 | 4759512.8 | 0 | 38500 | 9193056 | 13773291.84 | 21669528 | 0 | 0 | 0 | 0 | 4936377.6 | 7141567.5 | 6671729.79 | 290250 | 342000 | 0 | 0 | 0 | 4858056 | 0 | 830653.65 | 491400 | 4536000 | 0 | 4014301.05 | 5419053.12 | 0 | 0 | 0 |  | 5117688 | 10896710.4 | 1232503.3 | 13219264.8 | 0 | 4287379.2 | 277733.76 | 1866931.2 | 0 | 0 | 0 | 8407473 | 7744450 | 5568000 | 3646712.61 | 0 | 1298017.44 | 0 | 0 | 1849351.32 | 0 | 0 | 7599492.1 | 554702.04 | 153630 | 1407175 | 208650 | 24793401.6 | 937574.4 | 0 | 560249.28 | 196062 | 1359040 | 899553.6 | 2013876 | 1270761.12 | 2811154.3 | 0 | 0 | 4346956.8 | 0 | 4777683.8 | 844950 | 0 | 481140 | 7004500 | 128160 | 150639.6 | 0 | 13895.7 | 0 | 0 | 30346176 | 0 | 15893373.6 | 1410866.1 | 8203161.6 | 8556624 | 3151983.29 | 8570720 | 9703680 | 18906739.2 | 15393898.85 | 431307.64 | 28278454.98 | 4970097.99 | 13780285.54 | 21766008.6 | 10567737.6 | 8786937.6 | 6617008 | 14296800 | 4111458.5 | 14728521.6 | 8922955.58 | 0 | 9638280 | 2725424.55 | 19329264 | 10511240.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 62770908 | 0 | 0 | 0 | 3687638.4 | 0 | 0 | 0 | 1339944 | 873216 | 716703.75 | 2119040 | 1146089.92 | 1382294.4 | 0 | 0 | 0 | 1243378.11 | 365156.22 | 4174503.68 | 183568 | 561781.44 | 3524923.32 | 362258.14 | 2684354.4 | 0 | 0 | 129242.61 | 0 | 0 | 37091520 | 1344640 | 0 | 5277736.68 | 0 | 0 | 0 | 0 | 0 | 4472284.88 | 0 | 8380187.64 | 11379916.8 | 0 | 8153046.72 | 2384596.8 | 11543017.3 | 0 | 474177.6 | 9569427.84 | 242537620 | 5214518.46 | 0 | 1340880 | 358979.4 | 6249744 | 11237748.48 | 0 | 0 | 113377115.7 | 0 | 68163165 | 262306809.45 | 0 | 0 |  | 574008760.18 | 898122133.14 | 1472130893.32 | 92947848.75 | 62770908 | 67434991.97 | 0 | 434078581.98 | 723476230.15 | 1322053.65 | 1344640 | 48004217.43 | 24793401.6 | 15958019.79 | 0 | 0
Yesterday Day Peak | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 397 | 332 |  | 0 | 420 | 276 | 0 | 17 | 15 | 160 | 0 | 0 | 10 | 20 | 64 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 17 | 19 | 18 | 25 | 14 | 8 | 0 | 126 | 75 | 98 | 0 | 8 | 218 | 0 | 0 | 0 |  | 18 | 32 | 0 | 58 | 0 | 6 | 9 | 6 | 0 | 0 | 0 | 280 | 270 | 205 | 90 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 8 | 25 | 12 | 136 | 12 | 0 | 18 | 2 | 42 | 30 | 50 | 45 | 112 | 0 | 0 | 75 | 0 | 184 | 16 | 0 | 10 | 305 | 8 | 11 | 0 | 30 | 0 | 0 | 115 | 0 | 17 | 17 | 37 | 29 | 0 | 406 | 37 | 52 | 51 | 5 | 70 | 17 | 45 | 17 | 15 | 25 | 385 | 17 | 43 | 35 | 34 | 0 | 17 | 31 | 53 | 34 | 0 | 0 | 0 | 350 | 1 | 556 | 0 | 0 |  | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 360 | 17 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1050 | 220 | 0 | 0 | 5 | 92 | 0 | 0 | 0 | 524 | 21 | 200 | 1155 | 199 | 0 |  | 12661 | DayPeak
Yesterday Evening Peak | 0 | 0 | 150 | 0 | 0 | 22 | 0 | 409 | 327 |  | 0 | 390 | 281 | 16 | 80 | 24 | 188 | 0 | 0 | 90 | 92 | 149 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 19 | 18 | 25 | 28 | 25 | 0 | 126 | 75 | 105 | 0 | 17 | 219 | 0 | 0 | 0 | 0 | 18 | 71 | 17 | 58 | 0 | 40 | 9 | 15 | 0 | 0 | 0 | 290 | 280 | 180 | 135 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 156 | 32 | 0 | 18 | 0 | 43 | 30 | 50 | 44 | 112 | 0 | 0 | 84 | 0 | 183 | 17 | 0 | 10 | 290 | 8 | 8 | 0 | 95 | 0 | 0 | 162 | 0 | 134 | 0 | 45 | 17 | 43 | 390 | 85 | 105 | 51 | 0 | 190 | 54 | 55 | 88 | 87 | 50 | 0 | 72 | 0 | 126 | 51 | 0 | 35 | 0 | 53 | 54 | 0 | 17 | 0 | 350 | 0 | 556 | 0 | 0 |  | 774 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 26 | 20 | 16 | 134 | 28 | 16 | 0 | 0 | 0 | 32 | 18 | 63 | 14 | 8 | 40 | 8 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 14 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 370 | 54 | 0 | 94 | 15 | 106 | 0 | 0 | 113 | 1200 | 220 | 0 | 17 | 0 | 0 | 113 | 0 | 0 | 520 | 0 | 307 | 1362 | 0 | 0 |  | 14693 | EvPeak
Forecast for Evening | 0 | 0 | 150 | 0 | 0 | 53 | 0 | 412 | 330 | 0 | 0 | 450 | 310 | 82 | 85 | 55 | 0 | 0 | 40 | 92 | 102 | 149 | 55 | 0 | 0 | 0 | 35 | 35 | 55 | 20 | 19 | 19 | 25 | 30 | 25 | 0 | 121 | 75 | 100 | 0 | 17 | 225 |  | 0 | 0 | 0 | 18 | 71 | 0 | 70 | 0 | 40 | 11 | 35 | 0 | 0 | 0 | 330 | 330 | 200 | 145 | 0 | 50 | 0 | 0 | 50 | 0 | 31 | 52 | 18 | 10 | 33 | 12 | 165 | 43 | 0 | 18 | 0 | 43 | 40 | 50 | 46 | 112 | 0 | 0 | 86 | 0 | 185 | 17 | 0 | 10 | 300 | 8 | 11 | 0 | 300 | 0 | 0 | 160 | 0 | 149 | 0 | 50 | 85 | 150 | 400 | 104 | 105 | 51 | 0 | 285 | 54 | 55 | 105 | 85 | 63 | 380 | 72 | 0 | 126 | 51 | 0 | 34 |  | 50 | 54 | 0 | 150 |  | 350 | 20 | 600 | 0 |  |  | 938 | 0 | 0 |  | 82 | 0 | 0 | 0 | 40 | 40 | 16 | 65 | 25 | 110 | 0 | 0 | 0 | 38 | 0 | 91 | 28 | 42 | 40 | 52 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 180 |  | 0 | 0 | 0 | 0 | 140 | 0 | 400 | 72 | 0 | 90 | 100 | 113 | 0 | 0 | 113 | 1244 | 220 |  | 150 |  |  | 115 | 0 |  | 520 |  | 300 | 1400 |  | 0
Forecast for Day | 0 | 0 | 150 | 0 | 0 | 53 | 0 | 412 | 330 | 0 | 0 | 450 | 310 | 72 | 85 | 15 | 0 | 0 | 40 | 92 | 102 | 48 | 55 | 0 | 0 | 0 | 17 | 35 | 55 | 20 | 19 | 19 | 25 | 30 | 8 | 0 | 121 | 75 | 100 | 0 | 8 | 225 |  | 0 | 0 | 0 | 18 | 40 | 0 | 70 | 0 | 6 | 11 | 15 | 0 | 0 | 0 | 330 | 330 | 200 | 108 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 149 | 43 | 0 | 18 | 1.6 | 43 | 40 | 50 | 40 | 112 | 0 | 0 | 86 | 0 | 185 | 17 | 0 | 10 | 300 | 8 | 11 | 0 | 300 | 0 | 0 | 115 | 0 | 17 | 20 | 25 | 68 | 50 | 400 | 37 | 35 | 51 | 5 | 120 | 17 | 55 | 105 | 27 | 38 | 380 | 54 | 50 | 54 | 34 | 0 | 17 | 35 | 34 | 17 | 0 | 54 |  | 350 | 10 | 600 | 0 |  |  | 938 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 25 | 0 | 0 | 65 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 28 | 34 | 30 | 0 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 360 | 54 | 0 | 90 | 100 | 35 | 0 | 8 | 35 | 1244 | 220 |  | 35 | 6 | 100 | 35 | 0 |  | 520 | 30 | 300 | 1300 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 150 | 0 | 0 | 32 | 0 | 301 | 247 | 0 | 0 | 320 | 275 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 19 | 18 | 25 | 30 | 8 | 0 | 127 | 75 | 108 | 0 | 8 | 223 | 0 | 0 | 0 | 0 | 12 | 40 | 0 | 58 | 0 | 6 | 9 | 28 | 0 | 0 | 0 | 275 | 270 | 180 | 108 | 0 | 50 | 0 | 0 | 10 | 0 | 0 | 25 | 18 | 10 | 33 | 12 | 130 | 32 | 0 | 19 | 0 | 41 | 30 | 47 | 45 | 80 | 0 | 0 | 78 | 0 | 185 | 17 | 0 | 10 | 275 | 8 | 11 | 0 | 0 | 0 | 0 | 68 | 0 | 17 | 5 | 25 | 17 | 0 | 371 | 19 | 35 | 17 | 2 | 70 | 17 | 55 | 106 | 9 | 25 | 245 | 0 | 26 | 0 | 17 | 0 | 17 | 14 | 54 | 17 | 0 | 0 | 0 | 320 | 2 | 556 | 0 | 0 | 0 | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 80 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 280 | 0 | 0 | 0 | 0 | 34 | 0 | 2 | 0 | 900 | 180 | 0 | 0 | 2 | 38 | 0 | 0 | 0 | 524 | 15 | 256 | 1202 | 90 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
[128 empty] | 399274 |  | 399226 | [74 empty] | 292.3904
| Minimum Generation |  | 11405 | 7:00 | [202 empty] | 142284802
| Highest Generation |  | 14693 | 20:00 | [202 empty] | 142.2848 |  |  |  |  | 2.533
| Day Peak Generation |  | 12661 | 12:00 | [202 empty] | 36579135
| Evening Peak Generation |  | 14693 | 20:00 | [202 empty] | 36.5791 |  |  | 56999878 |  | 4.8965
| HVDC Max Flow |  | 902 | 15:00 | [202 empty] | 20.9236 |  |  |  |  | 0.0768
| HVDC EvPeak Flow |  | 774 | 20:00 | [200 empty] | 313296021 |  | 3.4531 |  | 102.5491
| Load factor L.F |  | 88.85% | [166 empty] | 1275.5 | [36 empty] | 313.296

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-09-28
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-09-27 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 12661 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 11348
Evening Peak Generation : |  |  | 14693 | MW Hour : | 20:00 | Available Max Generation : |  | 16878
E.P. Demand (at gen end) : |  |  | 14900 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 14500
Maximum Generation : |  |  | 14693 | MW Hour : | 20:00 | Reserve(Generation end) |  | 2378
Total Gen. (MKWH) : |  |  | 313.296 | System Load Factor : | 88.85% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 830 | MW at | 18:30 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-09-28
Actual : |  | 107.96 | Ft.(MSL) , | Rule curve : | 105.28 | Ft.( MSL )
Gas Consumed : |  | Total = | 1063.43 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 160382840.72
: |  |  | Coal : | 723476230.15 | Oil : | 483427439.41 | Total : | 1367286510.28
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4857.5703 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1336.484 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1872.677 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1628.1782 |  |  | 0 | 0%
Cumilla Area |  | 30 | 720:00 | 1339.4547 |  |  | 0 | 0%
Mymensingh Area |  | 75 | 1800:00 | 996.477 |  |  | 0 | 0%
Sylhet Area |  | 93 | 2232:00 | 558.2777 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 465.5121 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 910.4541 |  |  | 0 | 0%
Total |  | 198 |  | 13965.0851 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
09:15 | 17:50 | Charsaidpur 132/33kV S/S 132/33 kV GT-2 HT Scheduled S/D Due to yearly maintenance
| 09:27 | Jamalpur 132/33kV S/S T-2 HT is restored.
| 09:30 | Natore 132/33kV S/S TR-3 (425 T) HT is restored.
| 09:48 | Cumilla(N)-Daudkandi 132 kV Ckt-2 is restored.
| 09:48 | Natore 132/33kV S/S TR-3 (425 T) LT is restored.
10:01 |  | BSRM-Mirsharai 230 kV Ckt-2 Scheduled S/D from BSRM 230/33kV end Due to Deadline Checking. and from Mirsorai
230/33kV end Due to Annual maintenance work
10:24 | 12:26 | Saidpur 132/33kV S/S TR-2 (404T) LT Scheduled S/D Due to 33 KV Nilphamari -01 incoming isolator red hot
10:25 | 12:25 | Saidpur 132/33kV S/S TR-2 (404T) HT Scheduled S/D
12:00 |  | Day Peak Gen. 12662 MW
14:42 | 16:14 | Barishal 230/132kV S/S 230kV BUS Project Work S/D Due to Protection work of GIS
| 15:41 | Mirsorai 230/33kV S/S 150 MW Power Station -02 is restored.
15:47 | 17:19 | Barishal 230/132kV S/S ATR-1 HT Project Work S/D Due to project work
15:47 | 17:18 | Barishal 230/132kV S/S ATR-1 LT Project Work S/D Due to project work
| 15:59 | Madunaghat 132/33kV S/S TR-2(517T) HT is restored.
18:05 |  | Sylhet 132/33kV S/S T4 LT Tripped showing OC relays Due to Over load
18:37 |  | Bibiyana South 400 MW CCPP GT and ST tripped due to GBC inlet pressure high.
19:23 |  | Bhola 225 MW CCPP GT-2 synchronized.
19:29 |  | Relliance 718MW 400/15.5kV 335MVA GSUT-12 step up transformer charged.
19:49 |  | Evening peak generation 14693 MW at 20:00.
22:00 |  | Bibiyana South 400 MW CCPP GT synchronized.
00:10 |  | Siddhirganj 335 MW CCPP GT shut down
03:33 |  | Bibiyana South 400 MW CCPP ST synchronized
05:30 |  | Siddhirganj 230/132kV S/S MTR 2 HT Tripped showing Siprotec 7ut86 relays Due to PRV Fault
05:30 |  | Siddhirganj 132/33kV S/S 132kV MTR 2 Tripped showing no relays Due to 230 Kv Side
06:51 |  | Jamalpur 132/33kV S/S T-2 HT Scheduled S/D Due to 33 kv T1&T2 section DS high temperature maintenance. |  |  |  |  | 45.0MW Power interrup.
06:51 |  | Jamalpur 132/33kV S/S T-1 HT Scheduled S/D Due to 33 kv T1&T2 section DS high temperature maintenance. |  |  |  |  | 45.0MW Power interrup.
06:51 |  | Jamalpur 132/33kV S/S T-2 LT Scheduled S/D Due to 33 kv T1&T2 section DS high temperature maintenance. |  |  |  |  | 45.0MWPower interrup.
06:51 |  | Jamalpur 132/33kV S/S T-1 LT Scheduled S/D Due to 33 kv T1&T2 section DS high temperature maintenance. |  |  |  |  | 50.0MW Power interrup.
07:00 |  | Minimum Generation :11401 MW
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-09-27 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 150 | 3584094
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 22 | 1070545 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 409 | 9396230
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 327 | 7502000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 390 | 9367000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 16 | 146880 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 281 | 6907025 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 80 | 680253 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 24 | 329201 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 387000 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 22000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 90 | 628800 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 188 | 4249565 | ST Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 92 | 978912 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 388080 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 1336800
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 529005 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 497519
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 37 | 867120 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 599100 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 616100 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 285600 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 95 | 1018 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 134 | 1147536 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1307520
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 72 | 1104000 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 1160640 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 228069
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 798120
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5422 | 3063 | 56115732
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 105 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 245523 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 120690
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 40 | 370560 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 201 | 4896495
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 219 | 5210628
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 1216909 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 71 | 653280 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 72415 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 58 | 978480 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 45 | 794880 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 9 | 218688 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 15 | 560640
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27719
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 190 | 2408727 | Low demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 456391
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 55 | 1296358 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 745920 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 51 | 784091 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 17 | 100363 | Low demand
| SS Power I |  | SS Power | 0 | 0 | 350 | 9016362
| Cox's Bazar Wind |  | IPP | 66 | 0 | 0 | 76800 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 556 | 11090909 | On test.
| Chattogram area Total |  |  |  | 2545 | 2171 | 43742828
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 180 | 4800000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 290 | 7574300 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 280 | 7105000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 49 | 1148688
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 135 | 2826909 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1107396
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 43 | 237527 | Low demand
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 626400 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 404892 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 204840
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 156 | 3453120
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 804100
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 565018
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 12 | 278200 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 88 | 1603980 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 87 | 819840 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 738000 | Machine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 53 | 1291200 | Fuel shortage
| Cumilla Area Total |  |  |  | 2896 | 1589 | 35589410
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 32 | 860160 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 411948 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12300
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 162 | 2251200 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 85 | 798000 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 284530
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 392160 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 315 | 5010298
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 992000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 681480 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2444482 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1157400
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 44 | 734544 | Engine problem
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 198210 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under maint.
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1906560
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 183 | 4730380 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 393000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 170880 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7004500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 390 | 9316000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 243000
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 0 | 7192400 | Tripped at 18:37
| Sylhet Area Total |  |  |  | 2427 | 1269 | 37164836
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 774 | 20923636
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 32 | 354240 | Low demand
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 26 | 74400 | Low demand
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 20 | 48512 | Low demand
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 16 | 49875 | Low demand
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 54 | 846720 | Low demand
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 165024 | Low demand
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 532800
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 220 | 0 | 0 | Reserve
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 520 | 12472730
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3121 | 1457 | 35467937
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 126816 | Low demand
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 28 | 590768 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 134 | 1892000 | ST Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1200 | 29221400
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5112273
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 181200 | Low demand
| Barisal 307 MW |  | IPP | 307*1 | 307 | 307 | 5694500
| Barisal Area Total |  |  |  | 2265 | 1922 | 42818957
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 74143 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 18 | 20878 | Low demand
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 14 | 23840 | Low demand
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 33924 | Low demand
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 208452 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 195 | 4549773 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 137 | 3855418 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 370 | 8464836 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 159120 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 170730 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 26578 | Low demand
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 63 | 266912 | Low demand
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 689184 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 788256
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 31740
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1362 | 30679159
| Rajshahi Area Total |  |  |  | 3631 | 2494 | 50042943
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 180 | 4374000 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 14 | 32000
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 106 | 908899 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 42912
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 113 | 733056 | Engine problem
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 190403
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1061810
| Rangpur Area Total |  |  |  | 950 | 413 | 7343080
| Total |  |  |  | 23871 | 14693 | 313296021
| Eastern Grid Total |  |  |  | 13904 | 8407 | 177623104
| Western Grid Total |  |  |  | 9967 | 6286 | 135672917
| National Grid Total |  |  |  | 23871 | 14693 | 313296021
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-09-27
| (a) ENTIRE EASTERN GRID : |  | 9493.95 | MW | (b) ENTIRE WESTERN GRID : |  | 4635.8 | MW
| i) Dhaka area |  | 5077.95 | MW | i) Khulna area |  | 1758.4 | MW
| ii) Chittagong area |  | 1401 | MW | ii) Rajshahi area |  | 1484.4 | MW
| iii) Comilla area |  | 1334 | MW | iii) Barisal area |  | 430 | MW
| iv) Mymensingh area |  | 1136 | MW | iv) Rangpur area |  | 963 | MW
| v) Sylhet area |  | 545 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 14129.75 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 13 | 08:00 | Chhatak | 34 | 01:00 | Kamrangirchar | 81.3 | 13:00 | Narshingdi | 185 | 00:00 | Shikalbaha-230 | N/A | N/A
2 | AKSML | 90 | 10:00 | Chowmuhani | 217 | 22:00 | Kaptai | N/A | N/A | Natore | 146 | 18:30 | Shitalakhya | 104.2 | 12:00
3 | Aftabnagar | 36 | 00:00 | Chuadanga | 113 | 21:00 | Kazla | 95 | 16:00 | Nawabganj | 47.5 | 22:00 | Sholosohor | 44 | 15:00
4 | Agargaon | 91 | 13:00 | Coxsbazar | 131 | 18:30 | Keranigonj | 70 | 18:00 | Netrakona | 142 | 20:00 | Shyampur | 134 | 07:00
5 | Agrabad | 80 | 15:00 | Cumilla(N) | 180 | 18:30 | Khagrachori | 34 | 18:30 | New | 78 | 15:00 | Siddhirganj | 120 | 12:00
6 | Amnura | 54 | 21:00 | Cumilla(S) | 166 | 18:00 | Khulna | 99 | 20:00 | Niamatpur | 83 | 21:00 | Sirajganj | 124 | 19:30
7 | Ashuganj | 73 | 00:00 | Daudkandi | 154 | 20:00 | Khulshi | 186 | 18:30 | Noapara | 49 | 18:30 | Sonargaon | 94 | 00:00
8 | BIPTC | N/A | N/A | Dhaka | 32 | 11:00 | Kishoreganj | 156 | 18:30 | PHP | 6 | 20:00 | Sreemongol | 72 | 19:00
9 | BSRM | 145 | 10:00 | Dhamrai | 132 | 15:00 | Kodda | 295 | 19:00 | Pabna | 130 | 18:30 | Sreepur | 84 | 16:00
10 | Bagerhat | 93 | 22:00 | Dhanmondi | 140 | 13:00 | Kulaura | 50 | 18:00 | Palashbari | 123 | 19:00 | Srinagar | 46.8 | 21:00
11 | Bakulia | 104 | 18:30 | Dohazari | 86 | 19:00 | Kurigram | 75 | 18:30 | Panchagarh | 61 | 19:00 | Sunamganj | 50 | 18:00
12 | Banani | 34 | 12:00 | Faridpur | 160 | 21:00 | Kushtia | 138 | 18:30 | Patuakhali | 105 | 00:00 | Sylhet | 165 | 18:00
13 | Bangabhaban | 17 | 10:00 | Fatullah | 65 | 15:00 | Lalbag | 91 | 18:30 | Payra | 24 | 22:00 | TK | 32 | 23:00
14 | Barapukuria | 64 | 20:00 | Fenchuganj | 50 | 18:00 | Lalmonirhat | 56 | 19:00 | Postogola | 60 | 00:00 | Tangail | 235 | 21:00
15 | Barguna | 22 | 23:00 | Feni | 119 | 20:00 | MI_Cement | 19.9 | 13:00 | Purbachal | 21 | 18:30 | Thakurgaon | 100 | 21:00
16 | Barishal | 102 | 19:30 | GPH | 72 | 03:00 | Madanganj | 26 | 00:00 | Purbasadipur | 122 | 19:30 | Tongi | 124 | 15:00
17 | Barishal-230 | 96 | 22:00 | Ghorashal | 74 | 18:30 | Madaripur | 108 | 22:00 | Rahim | 42 | 04:00 | Ullon | 44 | 20:00
18 | Baroaulia | 71 | 00:00 | Goalpara | 36 | 19:30 | Madartek | 90.23 | 23:00 | Rajbari | 82 | 18:30 | Uttara | 73 | 13:00
19 | Baroirhat | 60 | 20:00 | Gollamari | 56 | 13:00 | Madunaghat | 55 | 19:00 | Rajendrapur | 102 | 19:00 | UttaraNew | 71 | 18:30
20 | Bashundhara | 147 | 13:00 | Gopalganj | 107.4 | 19:30 | Magura | 68 | 18:30 | Rajshahi | 160 | 23:00 | Zigatola | 70 | 19:00
21 | BashundharaCement | 0 | 00:00 | Gulshan | 128 | 11:00 | Mahasthangarh | 74 | 00:00 | Rajshahi-230 | 36 | 23:00
22 | Beanibazar | 80 | 18:00 | Halishahar | 73 | 14:00 | Manikganj | 125 | 20:00 | Ramganj | 114 | 22:00
23 | Benapole | 62 | 22:00 | HaripurSBU | 147 | 01:00 | Maniknagar | 96 | 13:00 | Rampur | 30 | 19:00
24 | Bhaluka | 128 | 12:00 | Hasnabad | 108 | 22:00 | Matarbari | 47 | 18:30 | Rangamati | 18 | 19:30
25 | Bhandaria | 50 | 22:00 | Hathazari | 80 | 18:00 | Matuail | 67 | 12:00 | Rangpur | 151 | 19:00
26 | Bhangura | 37 | 20:00 | Ishurdi | 77 | 20:00 | Millgate | 112 | 18:00 | Ruppur | 6.4 | 11:00
27 | Bheramara(GK) | 66 | 18:30 | Jaldhaka | 80 | 19:00 | Mirpur | 141 | 18:30 | SSM | 0 | 00:00
28 | Bhulta | 248 | 21:00 | Jamalpur | 165 | 20:00 | Mirsorai | 4 | 00:00 | Saidpur | 108 | 18:30
29 | Bog-Sherpur | 60 | 18:30 | Jashore | 140 | 20:00 | Mithapukur | 52 | 18:30 | Satkhira | 127 | 23:00
30 | Bogura | 173 | 19:30 | Jhenaidah | 139 | 18:30 | Modern | 0 | 00:00 | Satmasjid | 98 | 18:30
31 | Borhanuddin | 64 | 00:00 | Joydebpur | 181 | 18:30 | Mogbazar | 144.8 | 15:00 | Savar | 196 | 12:00
32 | Brahmanbaria | 158 | 02:00 | Joypurhat | 61 | 21:00 | Mongla | 38 | 09:00 | ShahCement | 34 | 11:00
33 | Cantonment | 152 | 13:00 | Juldah | 22 | 12:00 | Motijheel | 43 | 13:00 | Shahjadpur | 109 | 21:00
34 | Chandpur | 73 | 20:00 | KSRM | 25 | 10:00 | Munshiganj | 106 | 00:00 | Shahjibazar | 117 | 18:00
35 | Chandraghona | 32 | 19:00 | Kabirpur | 292 | 18:00 | Mymensingh | 223 | 18:00 | Shahmirpur | 50 | 00:00
36 | Chapai | 64 | 21:00 | Kachua | 71 | 22:00 | Naogaon | 128 | 21:00 | Shariatpur | 84 | 22:00
37 | Charsaidpur | 28 | 01:00 | Kallyanpur | 114 | 23:00 | Narail | 60 | 21:00 | Sherpur | 144 | 19:00
38 | Chauddagram | 60 | 00:00 | Kalurghat | 36 | 10:00 | Narinda | 76 | 13:00 | Shikalbaha | 25 | 06:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-09-27 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 391 | 06:00 | 377 | 12:00 | Gopalganj | 400 | 08:00 | 389 | 12:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 372 | 05:00 | 358 | 12:00
| Bhulta | 392 | 05:00 | 377 | 12:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 399 | 07:00 | 391 | 11:00 | Payra | 410 | 07:00 | 403 | 22:00
| BIPTC | 400 | 06:00 | 391 | 16:00 | Rahanpur | 402 | 18:00 | 393 | 00:00
| Bogura | N/A | N/A | N/A | N/A | Rampal | 402 | 07:00 | 390 | 22:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 228 | 05:00 | 217 | 12:00 | Hasnabad | 228 | 19:00 | 219 | 12:00
| AKSML | 230 | 21:00 | 225 | 10:00 | Hathazari | 231 | 17:00 | 226 | 15:00
| Aminbazar | 230 | 04:00 | 219 | 11:00 | Ishurdi | 235 | 06:00 | 224 | 12:00
| Ashuganj | 233 | 06:00 | 225 | 12:00 | Jhenaidah | 227 | 09:00 | 212 | 22:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 230 | 05:00 | 219 | 12:00
| Baghabari | 227 | 05:00 | 219 | 22:00 | Keranigonj | 228 | 06:00 | 217 | 12:00
| Barapukuria | 219 | 05:00 | 213 | 15:00 | Khulna(S) | 231 | 06:00 | 218 | 22:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 236 | 06:00 | 230 | 22:00 | Maniknagar | 229 | 05:00 | 218 | 12:00
| Bheramara | 236 | 06:00 | 225 | 14:00 | Meghnaghat | 236 | 00:00 | 230 | 10:00
| Bhulta | 232 | 06:00 | 222 | 12:00 | Mirsorai | 229 | 19:30 | 225 | 10:00
| Bibiana | 230 | 06:00 | 223 | 12:00 | Rajshahi | 232 | 05:00 | 219 | 00:00
| BIPTC | 235 | 06:00 | 222 | 12:00 | Rampal | 230 | 06:00 | 221 | 18:00
| Bogura | 228 | 18:00 | 222 | 22:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 242 | 09:00 | 237 | 00:00 | Rampura | 231 | 05:00 | 220 | 12:00
| BSRM | 230 | 06:00 | 224 | 10:00 | Shikalbaha | 232 | 19:30 | 226 | 16:00
| Cumilla(N) | 228 | 06:00 | 222 | 15:00 | Shyampur | 229 | 05:00 | 219 | 12:00
| Fenchuganj | 233 | 05:00 | 229 | 12:00 | Siddhirganj | 230 | 05:00 | 222 | 12:00
| Ghorashal | 235 | 08:00 | 230 | 00:00 | Sirajgonj | 238 | 07:00 | 232 | 12:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 229 | 06:00 | 222 | 12:00
| GPH | 230 | 02:00 | 225 | 15:00 | Tongi | 227 | 05:00 | 214 | 11:00
| Haripur | 228 | 19:00 | 222 | 11:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 135 | 08:00 | 126 | 12:00 | Lalbag | 131 | 06:00 | 122 | 12:00
| Agargaon | 132 | 06:00 | 123 | 12:00 | Lalmonirhat | 128 | 09:00 | 120 | 18:30
| Agrabad | 134 | 05:00 | 129 | 14:00 | Madanganj | 134 | 19:30 | 126 | 12:00
| AKS | 131 | 04:00 | 128 | 11:00 | Madaripur | 129 | 09:00 | 124 | 21:00
| Aminbazar | 133 | 20:00 | 126 | 11:00 | Madartek | 135 | 04:00 | 126 | 12:00
| Amnura | 138 | 19:30 | 122 | 21:00 | Madunaghat | 135 | 18:30 | 130 | 15:00
| Ashuganj | 138 | 06:00 | 135 | 11:00 | Magura | 136 | 04:00 | 124 | 18:30
| Bagerhat | 130 | 17:00 | 120 | 18:00 | Mahasthangarh | 134 | 06:00 | 126 | 02:00
| Bakulia | 135 | 17:00 | 130 | 10:00 | Manikganj | 132 | 18:30 | 124 | 11:00
| Banani | 136 | 05:00 | 126 | 12:00 | Maniknagar | 133 | 04:00 | 126 | 11:00
| Bangabhaban | 133 | 04:00 | 124 | 12:00 | Matarbari | 125 | 08:00 | 114 | 18:30
| Barapukuria | 136 | 05:00 | 130 | 15:00 | Matuail | 132 | 03:00 | 127 | 12:00
| Barguna | 135 | 08:00 | 128 | 00:00 | Millgate | 138 | 00:00 | 122 | 12:00
| Barishal | 134 | 08:00 | 125 | 02:00 | Mirpur | 131 | 18:30 | 123 | 12:00
| Barishal-230 | 136 | 06:00 | 130 | 22:00 | Mithapukur | 131 | 06:00 | 122 | 02:00
| Baroaulia | 135 | 18:30 | 130 | 10:00 | MI_Cement | 134 | 18:30 | 126.8 | 12:00
| Baroirhat | 129 | 09:00 | 122 | 15:00 | Modern | 134 | 06:00 | 130 | 10:00
| Bashundhara | 136 | 06:00 | 122 | 12:00 | Mogbazar | 136 | 06:00 | 126 | 12:00
| BashundharaCement | 134 | 19:30 | 126 | 12:00 | Mongla | 129 | 09:00 | 120 | 22:00
| Beanibazar | 125 | 06:00 | 120 | 18:00 | Motijheel | 133 | 04:00 | 124 | 12:00
| Benapole | 133 | 06:00 | 122 | 18:30 | Munshiganj | 133 | 18:30 | 127 | 12:00
| Bhaluka | 123 | 06:00 | 117 | 12:00 | Mymensingh | 132 | 18:30 | 115 | 12:00
| Bhandaria | 132 | 17:00 | 120 | 22:00 | Naogaon | 132 | 08:00 | 124 | 01:00
| Bhangura | 138 | 06:00 | 132 | 00:00 | Narail | 136 | 06:00 | 124 | 19:00
| Bheramara | 135 | 06:00 | 127 | 18:30 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara(GK) | 135 | 06:00 | 127 | 22:00 | Narshingdi | 127 | 18:00 | 120 | 00:00
| Bhulta | 126 | 18:00 | 120 | 16:00 | Natore | 132 | 07:00 | 122 | 00:00
| Bog-Sherpur | 137 | 18:00 | 129 | 02:00 | Nawabganj | 130 | 05:00 | 123 | 15:00
| Bogura | 138 | 18:00 | 114 | 00:00 | Netrakona | 132 | 18:30 | 118 | 16:00
| Bogura-230 | 138 | 18:00 | 131 | 15:00 | New | 134 | 05:00 | 123 | 12:00
| Brahmanbaria | 125 | 07:00 | 120 | 00:00 | Niamatpur | 132 | 09:00 | 120 | 02:00
| Cantonment | 131 | 05:00 | 122 | 12:00 | Noapara | 133 | 09:00 | 123 | 22:00
| Chandpur | 127 | 17:00 | 116 | 18:00 | Pabna | 135 | 05:00 | 126 | 22:00
| Chandraghona | 136 | 06:00 | 132 | 12:00 | Palashbari | 130 | 10:00 | 123 | 01:00
| Chapai | 131 | 10:00 | 125 | 21:00 | Panchagarh | 132 | 18:00 | 114 | 15:00
| Charsaidpur | 134 | 19:30 | 127 | 12:00 | Patuakhali | 136 | 10:00 | 132 | 00:00
| Chauddagram | 130 | 17:00 | 123 | 16:00 | Payra | 137 | 06:00 | 135 | 00:00
| Chhatak | 129 | 09:00 | 122 | 18:00 | PHP | 128 | 08:00 | 121 | 15:00
| Chowmuhani | 127 | 17:00 | 115 | 23:00 | Postogola | 133 | 06:00 | 127 | 12:00
| Chuadanga | 133 | 09:00 | 116 | 18:30 | Purbachal | 135 | 03:00 | 121 | 12:00
| Coxsbazar | 125 | 06:00 | 113 | 22:00 | Purbasadipur | 129 | 18:00 | 117 | 13:00
| Cumilla(N) | 133 | 08:00 | 127 | 15:00 | Rahanpur | 133 | 06:00 | 130 | 00:00
| Cumilla(S) | 133 | 17:00 | 124 | 18:00 | Rahim | 133 | 18:00 | 129 | 11:00
| Daudkandi | 126 | 17:00 | 116 | 12:00 | Rajbari | 129 | 06:00 | 120 | 22:00
| Dhaka | 136 | 05:00 | 127 | 12:00 | Rajendrapur | 133 | 19:00 | 122 | 15:00
| Dhamrai | 132 | 05:00 | 123 | 12:00 | Rajshahi | 133 | 07:00 | 124 | 00:00
| Dhanmondi | 133 | 03:00 | 125.7 | 12:00 | Rajshahi-230 | 134 | 09:00 | 121 | 02:00
| Dohazari | 130 | 07:00 | 124 | 00:00 | Ramganj | 124 | 09:00 | 113 | 22:00
| Faridpur | 129 | 06:00 | 121 | 22:00 | Rampur | 133 | 06:00 | 129 | 15:00
| Fatullah | 135 | 18:30 | 128 | 12:00 | Rampura | 136 | 06:00 | 126 | 11:00
| Fenchuganj | 133 | 18:30 | 129 | 15:00 | Rangamati | 135 | 07:00 | 123 | 19:00
| Feni | 130 | 17:00 | 122 | 15:00 | Rangpur | 129 | 20:00 | 121 | 14:00
| Ghorashal | 137 | 01:00 | 133 | 10:00 | Ruppur | 136 | 06:00 | 130 | 00:00
| Goalpara | 134 | 06:00 | 126 | 18:30 | Saidpur | 130 | 18:00 | 121 | 02:00
| Gollamari | 132 | 06:00 | 125 | 22:00 | Satkhira | 130 | 09:00 | 117 | 22:00
| Gopalganj | 129 | 09:00 | 122 | 22:00 | Satmasjid | 131 | 05:00 | 122 | 12:00
| Gopalganj-400 | 129 | 08:00 | 123 | 22:00 | Savar | 132 | 18:30 | 123 | 12:00
| Gulshan | 136 | 06:00 | 126 | 12:00 | ShahCement | 134 | 19:30 | 127 | 12:00
| Halishahar | 134 | 07:00 | 129 | 15:00 | Shahjadpur | 142 | 07:00 | 134 | 22:00
| Haripur | 133 | 18:00 | 129 | 11:00 | Shahjibazar | 127 | 09:00 | 122 | 15:00
| HaripurSBU | 133 | 18:00 | 129 | 11:00 | Shahmirpur | 134 | 17:00 | 130 | 05:00
| Hasnabad | 133 | 03:00 | 128 | 12:00 | Shariatpur | 129 | 07:00 | 121 | 22:00
| Hathazari | 136 | 17:00 | 133 | 10:00 | Sherpur | 131 | 18:30 | 122 | 21:00
| Ishurdi | 138 | 09:00 | 130 | 00:00 | Shikalbaha | 124 | 07:00 | 118 | 15:00
| Jaldhaka | 128 | 06:00 | 119 | 02:00 | Shikalbaha-230 | 135 | 08:00 | 131 | 01:00
| Jamalpur | 134 | 18:30 | 110 | 18:00 | Shitalakhya | 134 | 18:30 | 126.8 | 12:00
| Jashore | 134 | 09:00 | 122 | 22:00 | Sholosohor | 133 | 06:00 | 129 | 15:00
| Jhenaidah | 138 | 09:00 | 126 | 22:00 | Shyampur | 133 | 19:30 | 128 | 15:00
| Jhenaidah-230 | 138 | 06:00 | 127 | 18:30 | Shyampur-230 | 134 | 05:00 | 128 | 12:00
| Joydebpur | 135 | 18:30 | 126 | 12:00 | Siddhirganj | 133 | 18:30 | 128 | 12:00
| Joypurhat | 131 | 06:00 | 121 | 03:00 | Sirajganj | 136 | 07:00 | 127 | 22:00
| Juldah | 135 | 17:00 | 131 | 15:00 | Sonargaon | 130 | 18:00 | 126 | 09:00
| Kabirpur | 134 | 20:00 | 119 | 12:00 | Sreemongol | 128 | 09:00 | 123 | 00:00
| Kachua | 129 | 17:00 | 118 | 18:00 | Sreepur | 125 | 07:00 | 120 | 12:00
| Kaliakoir | 135 | 05:00 | 127 | 12:00 | Srinagar | 131 | 07:00 | 123 | 12:00
| Kallyanpur | 133 | 19:30 | 127 | 09:00 | SSM | 138 | 01:00 | 132 | 15:00
| Kalurghat | 134 | 19:30 | 131 | 01:00 | Sunamganj | 127 | 10:00 | 119 | 18:00
| Kamrangirchar | 131 | 02:00 | 123 | 12:00 | Sylhet | 128 | 06:00 | 126 | 13:00
| Kaptai | N/A | N/A | N/A | N/A | Tangail | 131 | 05:00 | 123 | 12:00
| Kazla | 133 | 06:00 | 125 | 12:00 | Thakurgaon | 132 | 20:00 | 112 | 15:00
| Keranigonj | 131 | 05:00 | 123 | 12:00 | TK | 135 | 07:00 | 130 | 14:00
| Khagrachori | 135 | 06:00 | 130 | 15:00 | Tongi | 134 | 05:00 | 125 | 11:00
| Khulna | 132 | 09:00 | 123 | 22:00 | Ullon | 136 | 04:00 | 126 | 12:00
| Khulna(S) | 133 | 06:00 | 125 | 22:00 | Uttara | 131 | 20:00 | 124 | 12:00
| Khulshi | 133 | 17:00 | 128 | 15:00 | UttaraNew | 131 | 18:30 | 124 | 10:00
| Kishoreganj | 130 | 05:00 | 123 | 00:00 | Zigatola | 131 | 06:00 | 124 | 12:00
| Kodda | 135 | 20:00 | 123 | 15:00
| KSRM | 134 | 01:00 | 129 | 16:00
| Kulaura | 130 | 07:00 | 127 | 16:00
| Kurigram | 131 | 06:00 | 121 | 15:00
| Kushtia | 135 | 06:00 | 125 | 18:30

## L-Curve
Date | 2023-09-27
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1000 | 7809 | 6305 | 14114 |  |  |  | QF-LDC-11
0:30 | 1090 | 7590 | 6149 | 13739 | Date: | 2023-09-27
1:00 | 1180 | 7371 | 5993 | 13364
1:30 | 1192 | 7257 | 5875 | 13132
2:00 | 1204 | 7143 | 5757 | 12900
2:30 | 1177 | 7079 | 5634 | 12713 | [5 empty] | Gen. at Eve. Peak | 14693 | 14693 MW (20:00 )
3:00 | 1150 | 7015 | 5511 | 12526 | [6 empty] | 20:00
3:30 | 1133 | 7001 | 5439.5 | 12440.5 | [5 empty] | Gen. at Day Peak | 12661 | 12661 MW (12:00 )
4:00 | 1116 | 6987 | 5368 | 12355 | [6 empty] | 12:00
4:30 | 1105 | 6919.5 | 5310.5 | 12230 | [5 empty] | Highest Generation | 14693
5:00 | 1094 | 6852 | 5253 | 12105 | [6 empty] | 20:00
5:30 | 1087 | 6677 | 5183.5 | 11860.5
6:00 | 1080 | 6502 | 5114 | 11616
6:30 | 1139 | 6456 | 5054.5 | 11510.5
7:00 | 1198 | 6410 | 4995 | 11405
7:30 | 1249 | 6433.5 | 4994.5 | 11428
8:00 | 1300 | 6457 | 4994 | 11451
8:30 | 1330 | 6612.5 | 5043 | 11655.5
9:00 | 1360 | 6768 | 5092 | 11860
9:30 | 1405 | 6802.5 | 5099 | 11901.5
10:00 | 1450 | 6837 | 5106 | 11943
10:30 | 1443 | 6954 | 5141 | 12095
11:00 | 1436 | 7071 | 5176 | 12247
11:30 | 1416 | 7201.5 | 5252.5 | 12454
12:00 | 1396 | 7332 | 5329 | 12661
12:30 | 1261 | 7419.5 | 5283.5 | 12703
13:00 | 1126 | 7507 | 5238 | 12745
13:30 | 1123 | 7568.5 | 5232 | 12800.5
14:00 | 1120 | 7630 | 5226 | 12856
14:30 | 1183 | 7658.5 | 5283.5 | 12942
15:00 | 1246 | 7687 | 5341 | 13028
15:30 | 1278 | 7604.5 | 5377 | 12981.5
16:00 | 1310 | 7522 | 5413 | 12935
16:30 | 1281 | 7419.5 | 5297 | 12716.5
17:00 | 1252 | 7317 | 5181 | 12498
17:30 | 1236 | 7449 | 5298 | 12747
18:00 | 1220 | 7581 | 5415 | 12996
18:30 | 1085 | 7972 | 5788 | 13760
19:00 | 950 | 8363 | 6161 | 14524
19:30 | 952 | 8377 | 6206 | 14583
20:00 | 956 | 8407 | 6286 | 14693 |  |  |  | Executive Engineer
20:30 | 956 | 8376 | 6271 | 14647 |  |  |  | Network Operation Division
21:00 | 956 | 8345 | 6256 | 14601
21:30 | 963 | 8272 | 6244 | 14516
22:00 | 970 | 8199 | 6232 | 14431 |  |  |  |  | Page 6 of 7
22:30 | 986 | 8090 | 6223 | 14313
23:00 | 1002 | 7981 | 6214 | 14195
23:30 | 1001 | 7895 | 6259.5 | 14154.5
24:00 | 1000 | 7809 | 6305 | 14114
14693 MW (20:00 )
12661 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-09-27 |  | Energy |  | 313296021
[15 empty] | 43734 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3377 | 792 | 2491 | 0 | 2333 | 4543 | 202 | 0 | 224 | 152 | 0 | 0 | 416.38
0:30 | 3564 | 842 | 2516.5 | 0 | 1868 | 4439 | 201.5 | 0 | 153.5 | 153 | 0 | 1.5 | 425.93 |  |  | Date: | 43734
1:00 | 3751 | 892 | 2542 | 0 | 1403 | 4335 | 201 | 0 | 83 | 154 | 0 | 3 | 435.48
1:30 | 3732 | 892 | 2516 | 0 | 1250.5 | 4334.5 | 201 | 0 | 49.5 | 153 | 0 | 3.5 | 408.74 | [9 empty] | Total Energy | 313.296 | 313.296 | Total Energy Gen 313.296 MKWHr Energy Not Served 4.781 MKWHr Energy Requirement 318.077 MKWHr
2:00 | 3713 | 892 | 2490 | 0 | 1098 | 4334 | 201 | 0 | 16 | 152 | 0 | 4 | 382 | [9 empty] | Energy not Served | 4.7811 | 4.7811
2:30 | 3709.5 | 891.5 | 2501 | 0 | 977 | 4262 | 201 | 0 | 16 | 152 | 0 | 3 | 369.585 | [9 empty] | Energy Requirement | 318.0771 | 318.0771
3:00 | 3706 | 891 | 2512 | 0 | 856 | 4190 | 201 | 0 | 16 | 152 | 0 | 2 | 357.17
3:30 | 3701.5 | 891 | 2515 | 0 | 830 | 4128 | 201 | 0 | 16 | 151 | 0 | 7 | 343.3225 | [8 empty] | Shortage
4:00 | 3697 | 891 | 2518 | 0 | 804 | 4066 | 201 | 0 | 16 | 150 | 0 | 12 | 329.475
4:30 | 3660.5 | 891 | 2478.5 | 0 | 795 | 4037.5 | 201 | 0 | 16 | 144 | 0 | 6.5 | 305.6
5:00 | 3624 | 891 | 2439 | 0 | 786 | 4009 | 201 | 0 | 16 | 138 | 0 | 1 | 281.725
5:30 | 3596 | 891 | 2318 | 0 | 757 | 3943.5 | 201 | 0 | 16 | 136 | 1.5 | 0.5 | 228.7225
6:00 | 3568 | 891 | 2197 | 0 | 728 | 3878 | 201 | 0 | 16 | 134 | 3 | 0 | 175.72
6:30 | 3537 | 891.5 | 2176.5 | 0 | 694.5 | 3821.5 | 201 | 0 | 16 | 131 | 32.5 | 9 | 180.9725 | [7 empty] | Coal
7:00 | 3506 | 892 | 2156 | 0 | 661 | 3765 | 201 | 0 | 16 | 128 | 62 | 18 | 186.225
7:30 | 3526.5 | 892 | 2116 | 0 | 655.5 | 3762.5 | 201 | 0 | 16 | 126 | 120 | 12.5 | 154.71 | [6 empty] | Oil
8:00 | 3547 | 892 | 2076 | 0 | 650 | 3760 | 201 | 0 | 16 | 124 | 178 | 7 | 123.195
8:30 | 3529.5 | 892 | 2145 | 0 | 701 | 3815 | 201.5 | 0 | 16 | 122 | 227 | 6.5 | 152.3225
9:00 | 3512 | 892 | 2214 | 0 | 752 | 3870 | 202 | 0 | 16 | 120 | 276 | 6 | 181.45
9:30 | 3472 | 892 | 2155.5 | 0 | 786 | 3929 | 202 | 0 | 32 | 120 | 307.5 | 5.5 | 150.89
10:00 | 3432 | 892 | 2097 | 0 | 820 | 3988 | 202 | 0 | 48 | 120 | 339 | 5 | 120.33
10:30 | 3423.5 | 892 | 2133.5 | 0 | 888.5 | 3990 | 201.5 | 0 | 60 | 122 | 380.5 | 3.5 | 75.445
11:00 | 3415 | 892 | 2170 | 0 | 957 | 3992 | 201 | 0 | 72 | 124 | 422 | 2 | 30.56
11:30 | 3448 | 896.5 | 2297.5 | 0 | 970 | 4003.5 | 201 | 0 | 84 | 130 | 422 | 1.5 | 28.65
12:00 | 3481 | 901 | 2425 | 0 | 983 | 4015 | 201 | 0 | 96 | 136 | 422 | 1 | 26.74
12:30 | 3482 | 901 | 2425.5 | 0 | 1086.5 | 4038 | 200.5 | 0 | 96 | 137 | 335.5 | 1 | 24.83
13:00 | 3483 | 901 | 2426 | 0 | 1190 | 4061 | 200 | 0 | 96 | 138 | 249 | 1 | 22.92
13:30 | 3483 | 901 | 2426 | 0 | 1190 | 4061 | 200 | 0 | 96 | 138 | 249 | 1 | 22.92
14:00 | 3483 | 901 | 2426 | 0 | 1190 | 4061 | 200 | 0 | 96 | 138 | 249 | 1 | 22.92
14:30 | 3500 | 901.5 | 2474 | 0 | 1240 | 4119 | 200 | 0 | 99.5 | 141 | 208 | 3.5 | 45.84
15:00 | 3517 | 902 | 2522 | 0 | 1290 | 4177 | 200 | 0 | 103 | 144 | 167 | 6 | 68.76
15:30 | 3534.5 | 901.5 | 2479 | 0 | 1253 | 4201 | 200 | 0 | 103.5 | 143 | 161 | 5 | 94.0675
16:00 | 3552 | 901 | 2436 | 0 | 1216 | 4225 | 200 | 0 | 104 | 142 | 155 | 4 | 119.375
16:30 | 3518.5 | 901 | 2284 | 0 | 1253 | 4201.5 | 200 | 0 | 109.5 | 141 | 102.5 | 5.5 | 132.2675
17:00 | 3485 | 901 | 2132 | 0 | 1290 | 4178 | 200 | 0 | 115 | 140 | 50 | 7 | 145.16
17:30 | 3485.5 | 901.5 | 2210 | 0 | 1449.5 | 4155.5 | 200 | 6 | 156.5 | 153 | 25 | 4.5 | 169.99
18:00 | 3486 | 902 | 2288 | 0 | 1609 | 4133 | 200 | 12 | 198 | 166 | 0 | 2 | 194.82
18:30 | 3322.5 | 901.5 | 2339 | 0 | 2221.5 | 4256.5 | 200 | 14 | 340.5 | 163 | 0 | 1.5 | 181.45
19:00 | 3159 | 901 | 2390 | 0 | 2834 | 4380 | 200 | 16 | 483 | 160 | 0 | 1 | 168.08
19:30 | 3205 | 773 | 2461 | 0 | 2846 | 4450 | 200 | 16 | 470 | 162 | 0 | 0 | 182.8825
20:00 | 3264 | 774 | 2429 | 0 | 2895 | 4475 | 201 | 14 | 485 | 156 | 0 | 0 | 197.685
20:30 | 3285.5 | 774 | 2485.5 | 0 | 2832 | 4503.5 | 201 | 7 | 400.5 | 158 | 0 | 0 | 193.865
21:00 | 3307 | 774 | 2542 | 0 | 2769 | 4532 | 201 | 0 | 316 | 160 | 0 | 0 | 190.045
21:30 | 3315.5 | 774 | 2549 | 0 | 2682.5 | 4538 | 201.5 | 0 | 295.5 | 160 | 0 | 0 | 199.595
22:00 | 3324 | 774 | 2556 | 0 | 2596 | 4544 | 202 | 0 | 275 | 160 | 0 | 0 | 209.145
22:30 | 3320.5 | 783.5 | 2538.5 | 0 | 2513.5 | 4546.5 | 202 | 0 | 249.5 | 159 | 0 | 0 | 297.96
23:00 | 3317 | 793 | 2521 | 0 | 2431 | 4549 | 202 | 0 | 224 | 158 | 0 | 0 | 386.775
23:30 | 3347 | 792.5 | 2506 | 0 | 2382 | 4546 | 202 | 0 | 224 | 155 | 0 | 0 | 401.5775 |  |  | Max Temp. in Dhaka |  | 33.2°C
24:00 | 3377 | 792 | 2491 | 0 | 2333 | 4543 | 202 | 0 | 224 | 152 | 0 | 0 | 416.38
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 313.296 MKWHr Energy Not Served 4.781 MKWHr Energy Requirement 318.077 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-09-27
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 127 | 127 | 126 | 126 | 125 | 125 | 125 | 125 | 125 | 125 |  | 125 | 125 | 126 | 126 | 127 | 127 | 127 | 3076495
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1820000
3 | Chattogram TPP-1 | 97 | 100 | 110 | 105 | 106 | 106 | 96 | 108 | 95 | 100 | 105 | 98 | 100 | 105 | 105 | 107 | 105 | 105 |  | 100 | 100 | 105 | 100 | 105 | 100 | 105 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 17 | 17 | 17 | 17 | 17 | 8 | 8 | 245523
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 3 | 11 | 11 | 11 | 15 | 17 | 18 | 16 | 13 | 6 | [10 empty] | 120690
6 | Sikalbaha 225MW CCPP (Gas) | 225 | 225 | 225 | 224 | 224 | 228 | 225 | 224 | 228 | 222 | 220 | 218 | 217 | 214 | 215 | 218 | 220 | 216 |  | 218 | 219 | 219 | 220 | 219 | 218 | 224 | 5210628
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 17 |  | 17 | 16 | 17 | 17 |  |  | 0 | 72415
12 | Hathazari 100 MW peaking PP | 57 | 0 | [8 empty] | 8 | 32 | 32 | 40 | 39 | 40 | 40 | 58 |  | 71 | 71 | 71 | 40 | 40 | 40 | 40 | 653280
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 34 | 34 | 34 | 34 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1216909
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [25 empty] | 92 | 22000
17 | Siddhirganj 335 MW CCPP | 190 | 190 | 190 | 190 | 190 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 |  | 185 | 189 | 188 | 189 | 175 | 140 | 100 | 4249565
18 | Kodda 300 MW PP Unit-2 (Summit) | [8 empty] | 5 | 30 | 30 | 30 | 75 | 95 | 95 | 45 | 45 | 45 |  | 95 | 95 | 95 | 45 | 45 | 45 | 97 | 1018
19 | Ashuganj 195 MW PP (APSCL-United) | 147 | 147 | 147 | 147 | 118 | 107 | 76 | 78 | 78 | 78 | 76 | 90 | 105 | 107 | 107 | 107 | 107 | 113 |  | 135 | 135 | 135 | 135 | 137 | 157 | 157 | 2826909
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 155 | 150 | 150 | 150 | 150 | 150 | 150 | 154 | 150 | 143 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3584094
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 405 | 404 | 402 | 406 | 404 | 382 | 405 | 400 | 400 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 |  | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 9016362
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 50 | 50 | 50 | 50 | 47 | 50 | 50 | 50 | 50 | 50 | 45 | 49 | 49 | 49 | 46 | 46 | 47 | 48 |  | 49 | 49 | 49 | 49 | 49 | 49 | 50 | 1148688
33 | Ashuganj 225 MW CCPP | 209 | 209 | 209 | 210 | 210 | 212 | 208 | 207 | 208 | 180 | 185 | 205 | 204 | 205 | 205 | 205 | 207 | 201 |  | 180 | 184 | 180 | 180 | 180 | 180 | 180 | 4800000
34 | Ashuganj 450 MW CCPP(South) | 310 | 270 | 270 | 270 | 270 | 270 | 275 | 310 | 310 | 270 | 280 | 270 | 295 | 310 | 305 | 305 | 305 | 315 |  | 280 | 280 | 280 | 305 | 305 | 305 | 305 | 7105000
| Ashuganj 450 MW CCPP(North) | 290 | 290 | 290 | 290 | 290 | 290 | 300 | 350 | 280 | 280 | 290 | 280 | 315 | 315 | 310 | 305 | 290 | 340 |  | 285 | 285 | 290 | 310 | 310 | 310 | 310 | 7574300
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 409 | 408 | 408 | 408 | 408 | 393 | 350 | 347 | 330 | 331 | 344 | 397 | 396 | 373 | 393 | 398 | 399 | 337 |  | 396 | 409 | 409 | 413 | 411 | 412 | 411 | 9396230
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 380 | 350 | 320 | 380 | 350 | 350 | 420 | 420 | 420 | 420 | 420 | 370 | 330 |  | 390 | 390 | 390 | 420 | 420 | 420 | 450 | 9367000
41 | Haripur 360 MW CCPP(HPL) | 332 | 332 | 332 | 331 | 332 | 282 | 283 | 266 | 302 | 263 | 301 | 332 | 286 | 287 | 331 | 323 | 273 | 292 |  | 333 | 332 | 327 | 332 | 333 | 332 | 282 | 7502000
42 | RPCL 210MW CCPP | 72 | 72 | 74 | 74 | 73 | 34 | 35 | 34 | 26 | 27 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 21 |  | 30 | 31 | 32 | 32 | 55 | 72 | 72 | 860160
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 9 | 22 | 37 | 36 | 45 | 43 | 44 | 38 | 7 | 20 | 5 | [9 empty] | 284530
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 42 | 42 | 42 | 40 | 40 | 40 | 41 |  | 41 | 41 | 43 | 41 | 43 | 41 | 41 | 992000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 681480
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86 MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 75 | 78 | 78 | 78 | 81 | 84 | 84 |  | 84 | 84 | 84 | 84 | 81 | 81 | 81 | 1906560
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 184 | 184 | 183 | 180 | 181 | 181 | 181 |  | 182 | 182 | 183 | 183 | 183 | 183 | 183 | 4730380
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 393000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 243000
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 198210
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 49 | 50 | 50 | 50 | 50 | 50 | 50 | 31 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1157400
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 170880
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 280 | 275 | 295 | 285 | 270 | 265 | 280 | 310 | 270 | 295 | 305 | 280 | 310 | 310 | 280 | 270 | 270 |  | 290 | 300 | 290 | 280 | 285 | 280 | 280 | 7004500
| Bibiyana South 400 MW | 400 | 400 | 400 | 396 | 395 | 390 | 360 | 360 | 400 | 386 | 384 | 385 | 370 | 370 | 381 | 388 | 386 | 360 | [6 empty] | 15 | 35 | 7192400
58 | Nababganj 55 MW PP (Southern power ) | [10 empty] | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 497519
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 12 | 392160
60 | Barabkunda 22 MW PP (Regent) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 218688
61 | Narshingdi 22 MW PP (Doreen) | 20 | 20 | 20 | 0 | 0 | 19 | 19 | 17 | 17 | 17 | 17 | 17 | 17 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 387000
62 | Tangail 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 411948
63 | Impoprt (Tripura) | 154 | 152 | 152 | 150 | 138 | 134 | 128 | 124 | 120 | 120 | 124 | 136 | 138 | 148 | 144 | 142 | 140 | 166 |  | 160 | 162 | 156 | 160 | 160 | 158 | 152 | 3453120
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 40 | 40 | 0 | 25 | 12 | 4 | 6 | 6 | 6 | 12 | 8 | 5 | 7 | 12 | 14 |  | 22 | 27 | 15 | 34 | 34 | 39 | 41 | 560640
65 | Feni 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 0 | 0 | 16 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 404892
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 0 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 204840
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 804100
68 | Cumilla 25 MW PP (Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 6 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 278200
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456000
70 | Summit Madhabdi | 18 | 18 | 0 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 411120
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 599100
72 | Rupganj 33 MW PP(Summit) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 28 | 30 | 8 | 14 | 14 | 20 | 20 | 20 | 21 | 28 |  | 28 | 28 | 28 | 28 | 30 | 31 | 32 | 616100
73 | Ghorashal 108 MW PP (Regent) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 22 |  | 22 | 22 | 22 | 32 | 32 | 32 | 35 | 1070545
| Feni Lanka Power | 105 | 105 | 105 | 105 | 105 | 59 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 39 | 70 | 70 | 70 |  | 88 | 88 | 88 | 106 | 106 | 106 | 106 | 1603980
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 15 | 36 | 37 | 39 | 39 | 84 | 86 |  | 86 | 86 | 87 | 87 | 87 | 69 | 15 | 819840
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 0 | [5 empty] | 17 | 17 | 17 | 35 | 54 | 54 | 54 | 54 | 54 | 54 |  | 126 | 126 | 126 | 126 | 126 | 126 | 108 | 1160640
77 | Siddhirganj 100 PP(Dutch Bangla) | 8 | 0 | [6 empty] | 3 | 8 | 8 | 10 | 50 | 50 | 50 | 44 | 24 | 24 |  | 62 | 90 | 90 | 80 | 31 | 35 | 82 | 628800
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 17 |  | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 285600
79 | Kodda 150 MW PP | 26 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 48 | 64 | 64 | 64 | 62 | 64 | 64 | 64 | 64 |  | 149 | 149 | 149 | 115 | 115 | 64 | 64 | 1336800
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 25 | 25 | 25 | 25 | 25 | 25 | 20 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 565018
| Gazipur 100 MW PP | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 70 |  | 105 | 105 | 105 | 88 | 70 | 70 | 35 | 1307520
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 4 | 5 | 5 | 4 | 4 | 3 | 1 | 0 | [9 empty] | 27719
| Jodiac Power | [5 empty] | 3 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 21 |  | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 456391
| Karnaphuli Power Ltd. | 55 | 55 | 55 | 41 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 45 | 36 | 50 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1296358
82 | Madanganj 102 PP(Summit) | 40 | 20 | 3 | 0 |  |  |  |  | 4 | 17 | 17 | 17 | 26 | 34 | 34 | 34 | 34 | 35 |  | 69 | 80 | 80 | 80 | 58 | 52 | 80 | 680253
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 272 | 267 | 294 | 284 | 280 | 260 | 300 | 299 | 265 | 286 | 300 | 276 | 292 | 306 | 297 | 268 | 252 | 310 |  | 292 | 296 | 281 | 290 | 298 | 298 | 286 | 6907025
87 | Meghnaghat 100 MW(IEL) | [12 empty] | 8 | 17 | 18 | 17 | 16 | 17 |  | 17 | 17 | 16 |  |  |  | 24 | 146880
| Meghnaghat 104 MW PP (OPCL) | 55 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 55 | 69 | 53 | 66 | 72 | 72 |  | 72 | 72 | 72 | 71 | 72 | 72 | 63 | 1104000
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 35 | 46 | 25 | 25 | 25 | 12 | 12 | 12 | 12 | 12 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 |  | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 978480
92 | Fenchuganj 44 MW (Energyprima) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 45 | 45 | 45 | 44 | 44 | 44 | 20 | 20 | 28 |  | 32 | 35 | 44 | 47 | 48 | 48 | 45 | 734544
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 20 | 20 | 20 | 20 | 39 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1107396
94 | Gagnagar 102 MW PP (Digital Power) | 91 | 50 | 0 | [5 empty] | 16 | 16 | 16 | 20 | 50 | 50 | 50 | 50 | 24 | 32 |  | 92 | 92 | 92 | 92 | 92 | 92 | 91 | 978912
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 0 | 6 | 6 | 6 | 6 | 6 | 6 | 18 | 37 |  | 40 | 40 | 40 | 40 | 40 | 40 | 7 | 370560
96 | Chattogram 108 MW PP (ECPV) | [20 empty] | 0 |  |  |  |  | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | 0 | [6 empty] | 12 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 28 |  | 25 | 25 | 24 | 24 | 15 | 15 | 15 | 329201
100 | Manikganj 55 MW PP (Northern) | 35 | 17 | 0 | [5 empty] | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 529005
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 112 | 112 | 80 | 80 | 80 | 80 | 80 | 112 | 112 | 112 | 113 | 112 | 80 | 112 |  | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 2444482
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 1 | 2 | 1 | 0 | [9 empty] | 12300
103 | Kamalaghat 54 MW PP(Banco Energy) | [8 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 388080
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 68 | 68 | 68 | 68 | 68 | 68 | 67 | 67 | 67 | 67 | 114 | 115 | 116 | 116 | 116 | 67 | 77 | 67 |  | 162 | 162 | 162 | 162 | 162 | 67 | 68 | 2251200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 36 | 34 | 34 | 34 | 34 | 34 | 34 | 35 | 35 | 35 | 23 | 17 | 17 | 17 | 17 | 17 | 17 | 33 |  | 117 | 133 | 134 | 131 | 115 | 112 | 18 | 1147536
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 30 | 37 | 37 | 37 | 37 | 37 | 37 | 41 |  | 42 | 44 | 45 | 46 | 47 | 48 | 25 | 794880
116 | Chandpur 200 MW (Desh energy) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 29 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 626400
117 | Ashuganj 150 MW PP (Midland) | 10 | 0 | [15 empty] | 10 |  | 85 | 10 | 43 | 10 | 10 | 12 | 48 | 237527
118 | Bibiyana-III 400 MW CCPP | 405 | 405 | 405 | 404 | 404 | 404 | 378 | 378 | 404 | 404 | 404 | 406 | 354 | 354 | 366 | 366 | 330 | 369 |  | 391 | 376 | 390 | 390 | 390 | 390 | 383 | 9316000
| Jamalpur 115 MW PP (United) | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 37 | 37 | 37 | 37 | 37 | 18 | 18 | 18 |  | 85 | 85 | 85 | 85 | 75 | 18 | 18 | 798000
| Anwara 300 MW PP (United) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 180 | 180 | 190 | 190 | 190 | 197 | 178 | 2408727
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 745920
| Anlima Energy Ltd. | 21 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 27 | 34 | 34 | 34 | 34 | 34 | 34 | 51 |  | 48 | 51 | 51 | 51 | 51 | 51 | 51 | 784091
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 19 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 738000
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 3 | 12 | 24 | 28 | 28 | 31 | 30 | 29 | 23 | 19 | 7 | [9 empty] | 228069
| Chandpur 115(Doreen) | 54 | 53 | 52 | 53 | 52 | 52 | 53 | 53 | 52 | 54 | 52 | 53 | 53 | 54 | 53 | 53 | 53 | 54 |  | 53 | 53 | 53 | 54 | 53 | 52 | 54 | 1291200
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 36 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 17 | 798120
| Mirsharai 150 MW (Oil) | [19 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 100363
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 3 | 4 | 2 | 12 | 1 | 0 | 18 | 7 | 6 | 5 | 2 | 1 | 1 | 5 | 6 | 4 | 7 | 2 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 76800
| Matarbari 2*600 MW (CPGCL) | 266 | 268 | 266 | 266 | 266 | 268 | 267 | 267 | 384 | 556 | 554 | 556 | 554 | 553 | 556 | 554 | 542 | 555 |  | 556 | 556 | 556 | 555 | 556 | 556 | 556 | 11090909
120 | Eastern Zone Total | 7371 | 7143 | 7015 | 6987 | 6852 | 6502 | 6410 | 6457 | 6768 | 6837 | 7071 | 7332 | 7507 | 7630 | 7687 | 7522 | 7317 | 7581 |  | 8363 | 8377 | 8407 | 8345 | 8199 | 7981 | 7809 | 177623104
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 88 | 48 | 16 | 16 | 0 | [12 empty] | 12 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 354240
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 1 | 31 |  | 37 | 26 | 26 |  |  |  |  | 74400
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 60 | 72 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 24 | 52 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 846720
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 1 | 9 | 29 | 42 | 60 | 92 | 92 | 65 | 41 | 31 | 41 | 17 | [9 empty] | 532800
131 | Rampal 1320 MW (BIFPCL) | 520 | 521 | 520 | 521 | 518 | 514 | 523 | 522 | 522 | 522 | 522 | 524 | 521 | 522 | 522 | 520 | 520 | 521 |  | 520 | 520 | 520 | 520 | 521 | 521 | 520 | 12472730
132 | United Payra Power Ltd. | 17 | 0 | [15 empty] | 2 |  | 17 | 17 | 17 | 17 | 17 | 25 | 72 | 181200
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 184 | 184 | 185 | 185 | 220 | 224 | 224 | 220 | 220 | 180 | 180 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5112273
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 0 | [17 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 126816
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 307 | 307 | 241 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 205 |  | 260 | 275 | 307 | 307 | 307 | 307 | 307 | 5694500
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 69 | 69 | 69 | 67 | 67 | 67 | 68 |  | 68 | 98 | 134 | 134 | 136 | 136 | 136 | 1892000
140 | Bhola 33 MW PP (Venture) | 32 | 30 | 30 | 30 | 27 | 25 | 22 | 22 | 18 | 17 | 13 | 21 | 20 | 20 | 20 | 21 | 21 | 27 |  | 27 | 27 | 28 | 31 | 31 | 31 | 31 | 590768
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 8 |  | 16 | 16 | 16 |  |  |  | 8 | 49875
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 10 | 15 |  | 21 | 20 | 20 |  |  |  | 0 | 48512
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 15 | 0 | [15 empty] | 15 |  | 15 | 15 | 15 | 15 | 15 | 32 | 50 | 165024
146 | Bheramara HVDC | 892 | 892 | 891 | 891 | 891 | 891 | 892 | 892 | 892 | 892 | 892 | 901 | 901 | 901 | 902 | 901 | 901 | 902 |  | 901 | 773 | 774 | 774 | 774 | 793 | 792 | 20923636
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 1244 | 1244 | 1172 | 1152 | 1122 | 1072 | 1022 | 1022 | 1022 | 1022 | 1022 | 1050 | 1100 | 1100 | 1140 | 1210 | 1180 | 1110 |  | 1170 | 1200 | 1200 | 1212 | 1222 | 1222 | 1222 | 29221400
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4374000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 32 | 32 | 32 |  |  |  |  | 74143
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 2 | 1 | 2 | 4 | 5 | 1 | 4 | 5 | 2 | 0 | [9 empty] | 31740
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 205 | 205 | 205 | 205 | 170 | 170 | 170 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 167 | 192 | 180 | 157 |  | 187 | 195 | 195 | 194 | 194 | 196 | 198 | 4549773
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 165 | 165 | 164 | 167 | 161 | 166 | 180 | 150 | 150 | 150 | 150 | 150 | 151 | 144 | 136 | 137 | 137 | 137 |  | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 3855418
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 360 | 320 | 320 | 320 | 320 | 326 | 320 | 280 | 320 | 280 | 280 | 360 | 390 | 414 | 414 | 414 | 300 | 414 |  | 320 | 370 | 370 | 414 | 414 | 360 | 360 | 8464836
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [19 empty] | 5 | 5 | 18 | 24 |  |  |  | 20878
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 170730
165 | Amnura 50 MW PP(Sinha) | [20 empty] | 14 | 14 | 14 |  |  | 0 | 23840
166 | Katakhali 50 MW PP (Northern) | [19 empty] | 8 | 8 | 8 | 8 | 8 |  | 0 | 33924
167 | Katakhali 50 MW Peaking PP | [19 empty] | 39 | 39 | 40 | 39 | 39 | 39 | 39 | 208452
168 | Santahar 50 MW Peaking PP | [19 empty] | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 159120
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 8 | 8 | 8 | 8 |  |  | 0 | 26578
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 13 |  | 63 | 63 | 63 | 32 | 32 | 32 | 32 | 266912
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 50 | 35 | 0 | [14 empty] | 6 |  | 86 | 94 | 94 | 94 | 94 | 94 | 94 | 689184
172 | Confidence Power Bogura Unit-1 113 MW | 50 | 0 | [15 empty] | 35 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 788256
173 | Rangpur 20 MW GTPP |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 |  | 16 | 16 | 14 | 0 | 0 |  | 0 | 32000
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 49 | 34 | 34 | 34 | 34 | 34 | 0 | [10 empty] | 55 |  | 101 | 106 | 106 | 106 | 113 | 106 | 113 | 908899
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 2 | 4 | 6 | 6 | 7 | 7 | 6 | 3 | 2 | 1 | [9 empty] | 42912
178 | Energypac Power Venture Thakurgaon Ltd. | 36 | 0 | [15 empty] | 36 |  | 108 | 108 | 113 | 113 | 115 | 115 | 115 | 733056
| Intraco Solar 30 MW | [5 empty] | 0 | 5 | 14 | 23 | 23 | 26 | 21 | 35 | 30 | 24 | 13 | 4 | 0 | [8 empty] | 190403
| Adani Power Jharkhanda Ltd | 1413 | 1410 | 1409 | 1341 | 1319 | 1262 | 1168 | 1169 | 1162 | 1158 | 1164 | 1155 | 1156 | 1160 | 1229 | 1211 | 1206 | 1212 |  | 1344 | 1369 | 1362 | 1408 | 1408 | 1413 | 1408 | 30679159
178 | Teesta Solar Limited | [5 empty] | 2 | 32 | 85 | 131 | 168 | 199 | 199 | 43 | 36 | 56 | 50 | 16 | [9 empty] | 1061810