## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-09-30 | Saturday
|  | Date (day): | 2023-09-30 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14816.6 | MW |  |  | (b) At Evening Peak Hour : |  | 16909 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-09-29 | 2023-09-30 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 170 | 150 | 150 | 30
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  |  | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 30 | 62 | 42 | 62 | 46 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 334 | 362 | 412 | 412
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 308 | 330 | 330 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 82 | 82 | 18 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 277 | 287 | 310 | 310 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 4 | 85 | 85 |  | 17 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 55 | 55 | 20 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 20 | 20 | 20
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 190 | 96 | 160 | 160 | 50 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 88 | 88 |  | 12 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Engine problem
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 8 | 50 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 0 | 17 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 47 | 98 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 35 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 33 | 37 | 38 | 38 |  | 42 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 22 | 28 | 30 | 30
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 25 | 8 | 25 | 27 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 300 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 51 | 108 | 17 | 149
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 35 | 35 | 105
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 17 | 54 | 72 | 32 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 17 | 54 | 126 | 36 |  | Fuel shortage
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 19 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 54
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 5763 | 5422 | 1976 | 2145 | 3107 | 3559 | 484 | 1174
38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 105 | 105 | 75 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
39 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 17 | 8 | 17 | 8 |  | Fuel shortage
40 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 6 | 0 | 20 | 0
41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 24 | 40 | 40 | 40
42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 201 | 201 | 201 | 201
43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 222 | 225 | 225 | 225
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 34 | 34 | 34 | 71 |  | Fuel shortage
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 40 | 70 | 28 |  | Fuel shortage
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 17 | 17 | 17 | 85 |  | Fuel shortage
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 12 | 12 | 35 | 60 | 40 |  | Fuel shortage
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 37 | 50 | 25 | 50 | 50 |  | Fuel shortage
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 9 | 9 | 11 | 11 | 11 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 25 | 42 | 10 | 35
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 77 | 175 | 70 | 300
54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 54
55 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 55 | 55 | 55 | 55 | 55 |  | Fuel shortage
56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 56 | 25 | 50 | 50 |  | Fuel shortage
57 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 18 | 34 | 68 | 68 | 48 |  | Fuel shortage
58 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 0 | 54 | 150
| SS Power I |  | Coal | SS Power | 0 | 0 | 0 | 612 | 546 | 500 | 550 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 0 | 4 | 10 | 20 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 300 | 300 | 300 | 300 |  |  | On test.
| Chattogram area Total |  |  |  |  | 2605 | 2545 | 1783 | 1934 | 1875 | 2412 | 629 | 330
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 205 | 178 | 200 | 200 |  |  | FGMO
60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 330 | 280 | 300 | 300 |  |  | FGMO
61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 250 | 280 | 300 | 300 |  |  | FGMO
62 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 240 | 230 | 250 | 300 |  | 100 | Gas shortage
63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 5 | 5 | 5 |  | 40 | Gas shortage
64 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
65 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortae
66 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 20 | 51 | 51 | 50 |  |  | Gas shortage
67 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 150 | 150
68 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 23 | 0 | 31 |  | 21 | Machine problem
69 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
70 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 17 | 17 | 17 | 183 |  | Fuel shortage
71 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 11 | 18 | 18 | 18 |  | 4 | Engine problem
72 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 11 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 116 | 146 | 149 | 165
73 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 32 | 33 | 33 | 33
74 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 30 | 52 | 52 | 52
75 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
76 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 52 | 17 | 52 |  | 62 | Engine problem
77 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 28 | 77 | 28 | 88 | 25 |  | Fuel shortage
78 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 34 |  | 20 | Engine problem
79 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 54 | 54 | 54 | 54 | 61 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2896 | 1402 | 1544 | 1671 | 1879 | 456 | 423
80 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 28 | 72 | 35 | 65 | 137 |  | Gas shortage
81 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
82 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
83 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
84 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 105 | 126 | 115 | 160 | 40 |  | Fuel shortage
85 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 74 | 94 | 37 | 104 | 11 |  | Fuel shortage
86 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 47 | 0 | 50 | 0
87 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 18 | 18 | 18 | 4 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 292 | 328 | 274.6 | 365 | 137 | 4
88 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 42 | 40 | 43 | 43 |  | 27 | Machine problem.
89 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 28 | 30 | 30 | 30 |  | 60 | Machine problem
90 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 112 | 112 |  | 51 | ST Under maint.
91 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
92 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 50 | 50 | 50
93 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 39 | 46 | 40 | 46 |  | 4 | Engine problem
94 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 0 | 11 | 11
95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 66 |  | Gas shortage
96 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 84 | 86 | 86
97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 180 | 180 | 185 | 185 |  | 46 | Machine problem
99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 16 | 17 | 17 | 17
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 | 17 |  | Gas shortage
101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 290 | 300 | 300 |  |  | FGMO
102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 380 | 380 | 400 | 400 |  |  | FGMO
103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 230 | 260 | 380 | 380
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1468 | 1507 | 1672 | 1678 | 83 | 618
105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 902 | 787 | 938 | 938
106 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 16 | 16 | 49 | 66 |  | Fuel shortage
107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 31 | 25 | 40 |  | 14 | Engine problem
108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 | 69 |  | Fuel shortage
110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
111 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 16 | 24 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 54 | 54 | 55 | 50 |  | Fuel shortage
113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 100 | 100
114 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 29 | 0 | 100 | 0
115 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
116 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 400 | 567 | 520 | 520
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3125 | 3121 | 1331 | 1470 | 1753 | 1758 | 1085 | 14
117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 16 | 110
118 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 22 | 28 | 23 | 25 |  | 15 | Engine problem
119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 132 | 138 | 130 | 130 |  | 64 | ST under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
120 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1000 | 1210 | 1244 | 1244
121 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 95 | 220 | 220 | 220
122 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 35 | 150
123 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 150 | 256 | 200 | 300
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1399 | 1852 | 1868 | 2179 | 0 | 79
124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 38 | 14 |  | Fuel shortage
126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 0 |  | 71 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 28 | 28
128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 34 | 42 | 8
129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 40 | 10
130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 170 | 170 | 150 | 170 | 40 |  | Gas shortage
131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 148 | 160 | 140 | 165 | 55 |  | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 350 | 350 | 360 | 400
134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 24 | 32 | 18 |  | Fuel shortage
135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 52
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 16 | 50 | 91 |  | 13 | Engine problem
139 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 35 | 92 | 21 |  | Fuel shortage
141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 35 | 113
142 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1112 | 1409 | 1200 | 1400
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 1791 | 2215 | 2100 | 2671 | 757 | 87
143 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
144 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 180 | 180 | 180 | 180 |  | 94 | Machine problem
145 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113
148 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
149 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 114 | 35 | 115
150 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 37 | 0 | 30 | 0
151 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 186 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 410 | 407 | 496 | 408 | 125 | 179
| Total |  |  |  |  | 24611 | 23871 | 11852 | 13402 | 14816.6 | 16909 | 3756 | 2908
A. |  | 2023-09-29 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 13529 | MW at | 1:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
2 | Minimum Generation : |  |  | 11006 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13485 | MW
3 | Day peak Generation : |  |  | 11852 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12860.9 | MW
4 | Evening peak Generation : |  |  | 13402 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 79 | MW
5 | Total Energy Generation : |  | 298.6704 | MKWHr | By Solar | 2.3458 | MKWHr
| By Gas : | 139.6808 | MKWHr |  | By Oil: | 28.3097 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 98.8786 | MKWHr |  | By Hydro: | 4.7145 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.0936 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3756 | MW | Dhaka | 4257.2 | 4257.2 |  | 0 |  | 18:00 |  | 96
|  |  | For Plants S/D or M/C prob = |  |  | 2908 | MW | Chittagong | 1220.1 | 1220.1 |  | 0 |  | 19:00 |  | 23
|  |  | Total = |  |  | 6664 | MW | Khulna | 1573 | 1573 |  | 0 |  | 19:30 |  | 66
7 | Total Gas Supplied : |  |  | 1062.02 | MMCFD |  |  | Rajshahi | 1427.6 | 1427.6 |  | 0 |  | 20:00 |  | 79
8 | Fuel Cost : | i) Gas : | Taka | 153249976.614 | ii) Oil : | Taka | 372174490.5 | Comilla | 1319 | 1299 |  | 20 |  | 21:00 |  | 90
|  | iii) Coal : | Taka | 685853535.45 | Total | Taka | 1211278002.564 | Mymensingh | 1113 | 1083 |  | 30 |  | 22:00 |  | 198.64
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 593 | 564 |  | 29 |  | 23:00 |  | 345.71
| ii) During Peak Demand : |  |  | 890 | MW (W to E) at | 20:00 | hrs | Barisal | 401 | 401 |  | 0 |  | 24:00 |  | 355.26
| iii) Maximum : |  |  | 690 | MW at | 18:30 | hrs | Rangpur | 957 | 957 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 35.6°C |  |  | Total | 12860.9 | 12781.9 |  | 79
B. |  | 2023-09-30 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 35.6°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 14000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 16909 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 11500 | MW
4 | Reserve(Generation end) |  |  |  | 2909 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 309.0684 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10305 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.4909 | MKWHr. | ii) HVDC Flow at Peak Time |  | 787 | MW at | 20:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.1565 | MKWHr. | iii) Maximum HVDC Flow : |  | 910 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 108.12 |  | (b) Today: | 108.09 |  | (c) Rule Curve: |  | 105.76
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-09-29 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 150 | 0 | 0 | 42 | 0 | 404 | 326 |  | 0 | 420 | 260 | 9 | 17 | 20 | 0 | 0 | 195 | 9 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 18 | 25 | 30 | 8 | 0 | 125 | 75 | 109 | 0 | 8 | 227 | 0 | 0 | 0 |  | 12 | 48 | 17 | 36 | 0 | 6 | 9 | 42 | 0 | 0 | 0 | 280 | 250 | 181 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 30 | 27 | 18 | 0 | 33 | 12 | 152 | 41 | 0 | 19 | 0 | 42 | 30 | 50 | 47 | 112 | 0 | 0 | 78 | 0 | 180 | 17 | 0 | 10 | 295 | 8 | 0 | 0 | 15 | 0 | 0 | 68 | 0 | 17 | 0 | 25 | 17 | 13 | 379 | 19 | 35 | 17 | 0 | 70 | 0 | 55 | 105 | 9 | 25 | 394 | 35 | 0 | 17 | 20 | 0 | 11 | 0 | 54 | 17 | 240 | 17 | 0 | 612 | 0 | 270 | 0 | 0 |  | 901 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 16 | 130 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 414 | 54 | 0 | 50 | 85 | 107 | 0 | 0 | 50 | 1220 | 220 | 0 | 17 | 0 | 0 | 75 | 0 | 0 | 524 | 0 | 307 | 1415 | 0 | 0 |  | 7284 | 6245 | 13529 | 3832 | 901 | 2409 | 0 | 1379 | 4528 | 200 | 0 | 128 | 152 | 0 | 0 | 449.805 | 108.11
2:00 | 0 | 0 | 150 | 0 | 0 | 42 | 0 | 412 | 331 |  | 0 | 370 | 275 | 9 | 34 | 15 | 0 | 0 | 157 | 9 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 18 | 25 | 31 | 8 | 0 | 125 | 75 | 107 | 0 | 8 | 226 | 0 | 0 | 0 |  | 12 | 48 | 17 | 36 | 0 | 6 | 9 | 42 | 0 | 0 | 0 | 280 | 250 | 188 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 21 | 25 | 18 | 10 | 33 | 12 | 152 | 46 | 0 | 19 | 0 | 41 | 30 | 50 | 47 | 112 | 0 | 0 | 78 | 0 | 180 | 17 | 0 | 10 | 270 | 8 | 3 | 0 | 15 | 0 | 0 | 68 | 0 | 17 | 0 | 25 | 17 | 30 | 379 | 19 | 35 | 17 | 0 | 70 | 0 | 45 | 105 | 9 | 25 | 392 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 53 | 17 | 240 | 17 | 0 | 612 | 0 | 270 | 0 | 0 |  | 901 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 16 | 134 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 370 | 54 | 0 | 50 | 19 | 88 | 0 | 0 | 50 | 1220 | 220 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 532 | 0 | 307 | 1396 | 0 | 0 |  | 7177 | 6071 | 13248 | 3841 | 901 | 2310 | 0 | 1208 | 4517 | 200 | 0 | 119 | 152 | 0 | 0 | 431.66 | 108.11
3:00 | 0 | 0 | 150 | 0 | 0 | 42 | 0 | 411 | 331 |  | 0 | 400 | 280 | 8 | 30 | 15 | 0 | 0 | 155 | 9 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 18 | 25 | 31 | 8 | 0 | 125 | 75 | 107 | 0 | 8 | 226 | 0 | 0 | 0 |  | 12 | 48 | 17 | 36 | 0 | 6 | 9 | 42 | 0 | 0 | 0 | 280 | 250 | 190 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 21 | 25 | 18 | 10 | 33 | 12 | 148 | 35 | 0 | 19 | 0 | 41 | 30 | 50 | 47 | 112 | 0 | 0 | 78 | 0 | 180 | 17 | 0 | 10 | 280 | 8 | 3 | 0 | 15 | 0 | 0 | 69 | 0 | 17 | 0 | 25 | 17 | 0 | 371 | 19 | 35 | 17 | 0 | 70 | 0 | 52 | 105 | 9 | 25 | 391 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 54 | 17 | 240 | 17 | 0 | 612 | 0 | 270 | 0 | 0 |  | 903 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 16 | 136 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 370 | 54 | 0 | 50 | 0 | 34 | 0 | 0 | 35 | 1220 | 220 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 520 | 0 | 307 | 1321 | 0 | 0 |  | 7171 | 5826 | 12997 | 3792 | 903 | 2346 | 0 | 1059 | 4430 | 200 | 0 | 119 | 148 | 0 | 0 | 384.865 | 108.11
4:00 | 0 | 0 | 150 | 0 | 0 | 42 | 0 | 416 | 332 |  | 0 | 400 | 274 | 9 | 12 | 15 | 0 | 0 | 100 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 18 | 25 | 31 | 8 | 0 | 125 | 75 | 105 | 0 | 8 | 226 | 0 | 0 | 0 |  | 12 | 48 | 17 | 36 | 0 | 6 | 9 | 42 | 0 | 0 | 0 | 280 | 250 | 193 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 21 | 25 | 18 | 10 | 33 | 12 | 146 | 17 | 0 | 19 | 0 | 41 | 30 | 50 | 44 | 112 | 0 | 0 | 78 | 0 | 183 | 17 | 0 | 10 | 275 | 8 | 3 | 0 | 15 | 0 | 0 | 67 | 0 | 17 | 0 | 25 | 17 | 0 | 378 | 19 | 35 | 17 | 0 | 70 | 0 | 55 | 105 | 9 | 25 | 392 | 17 | 0 | 17 | 17 | 0 | 0 | 0 | 54 | 17 | 240 | 17 | 0 | 612 | 0 | 270 | 0 | 0 |  | 901 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 370 | 54 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 1160 | 220 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 525 | 0 | 281 | 1313 | 0 | 0 |  | 7058 | 5661 | 12719 | 3730 | 901 | 2331 | 0 | 951 | 4341 | 200 | 0 | 119 | 146 | 0 | 0 | 363.855 | 108.12
5:00 | 0 | 0 | 150 | 0 | 0 | 42 | 0 | 389 | 302 |  | 0 | 360 | 273 | 8 | 0 | 15 | 0 | 0 | 101 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 20 | 19 | 18 | 25 | 31 | 8 | 0 | 125 | 75 | 104 | 0 | 8 | 226 | 0 | 0 | 0 |  | 12 | 40 | 17 | 36 | 0 | 6 | 9 | 42 | 0 | 0 | 0 | 280 | 250 | 198 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 21 | 25 | 18 | 10 | 33 | 12 | 142 | 17 | 0 | 19 | 0 | 41 | 30 | 47 | 47 | 112 | 0 | 0 | 78 | 0 | 184 | 17 | 0 | 10 | 280 | 8 | 3 | 0 | 15 | 0 | 0 | 67 | 0 | 17 | 0 | 25 | 17 | 0 | 379 | 19 | 35 | 17 | 0 | 70 | 0 | 55 | 105 | 9 | 25 | 360 | 17 | 0 | 17 | 17 | 0 | 0 | 0 | 53 | 17 | 240 | 17 | 0 | 622 | 11 | 270 | 0 | 0 |  | 901 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 340 | 54 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 1120 | 223 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 523 | 0 | 230 | 1314 | 0 | 0 |  | 6970 | 5534 | 12504 | 3687 | 901 | 2237 | 0 | 956 | 4259 | 200 | 0 | 111 | 142 | 0 | 11 | 330.43 | 108.12
6:00 | 0 | 0 | 140 | 0 | 0 | 32 | 0 | 349 | 257 |  | 0 | 330 | 228 | 9 | 5 | 15 | 0 | 0 | 101 | 6 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 20 | 19 | 18 | 25 | 31 | 8 | 0 | 125 | 75 | 102 | 0 | 0 | 226 | 0 | 0 | 0 |  | 12 | 40 | 17 | 36 | 0 | 6 | 9 | 42 | 0 | 0 | 0 | 280 | 250 | 200 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 21 | 25 | 18 | 10 | 33 | 12 | 126 | 35 | 0 | 19 | 0 | 41 | 30 | 47 | 47 | 112 | 0 | 0 | 78 | 0 | 184 | 17 | 0 | 10 | 265 | 8 | 3 | 0 | 15 | 0 | 0 | 67 | 0 | 17 | 0 | 25 | 17 | 1 | 378 | 19 | 35 | 17 | 0 | 70 | 2 | 55 | 87 | 9 | 25 | 228 | 17 | 0 | 17 | 17 | 0 | 14 | 0 | 54 | 17 | 240 | 17 | 0 | 612 | 5 | 244 | 0 | 0 |  | 902 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 280 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 1040 | 188 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 523 | 0 | 191 | 1163 | 1 | 0 |  | 6606 | 5045 | 11651 | 3399 | 902 | 1996 | 0 | 958 | 3953 | 200 | 0 | 111 | 126 | 1 | 5 | 619.795 | 108.12
7:00 | 0 | 0 | 145 | 0 | 0 | 17 | 0 | 331 | 242 |  | 0 | 300 | 239 | 8 | 17 | 15 | 0 | 0 | 78 | 9 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 20 | 19 | 18 | 25 | 31 | 8 | 0 | 126 | 75 | 107 | 0 | 0 | 227 | 0 | 0 | 0 |  | 12 | 40 | 17 | 36 | 0 | 6 | 9 | 42 | 0 | 0 | 0 | 280 | 250 | 207 | 8 | 0 | 5 | 0 | 0 | 8 | 0 | 21 | 25 | 0 | 0 | 33 | 12 | 110 | 50 | 0 | 19 | 0 | 41 | 30 | 47 | 47 | 80 | 0 | 0 | 78 | 0 | 184 | 17 | 0 | 10 | 255 | 8 | 3 | 0 | 15 | 0 | 0 | 67 | 0 | 17 | 3 | 25 | 17 | 8 | 378 | 19 | 35 | 17 | 1 | 70 | 17 | 55 | 17 | 9 | 25 | 230 | 17 | 7 | 17 | 17 | 0 | 17 | 4 | 54 | 17 | 240 | 17 | 0 | 612 | 3 | 262 | 0 | 0 |  | 902 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 260 | 17 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 980 | 176 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 450 | 6 | 150 | 1111 | 29 | 0 |  | 6455 | 4756 | 11211 | 3365 | 902 | 1826 | 0 | 865 | 3745 | 201 | 0 | 143 | 110 | 51 | 3 | 323.745 | 108.12
8:00 | 0 | 0 | 150 | 0 | 0 | 17 | 0 | 332 | 242 |  | 0 | 300 | 247 | 9 | 17 | 15 | 0 | 0 | 80 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 20 | 19 | 18 | 25 | 31 | 8 | 0 | 126 | 75 | 105 | 0 | 0 | 226 | 0 | 0 | 0 |  | 12 | 40 | 17 | 12 | 0 | 6 | 9 | 41 | 0 | 0 | 0 | 280 | 250 | 212 | 8 | 0 | 5 | 0 | 0 | 8 | 0 | 0 | 25 | 0 | 0 | 33 | 12 | 108 | 42 | 0 | 19 | 1 | 42 | 30 | 47 | 47 | 80 | 0 | 0 | 75 | 0 | 184 | 17 | 0 | 10 | 255 | 8 | 8 | 0 | 15 | 0 | 0 | 68 | 0 | 17 | 6 | 25 | 17 | 10 | 378 | 19 | 35 | 17 | 2 | 70 | 17 | 55 | 17 | 9 | 25 | 230 | 17 | 23 | 17 | 17 | 0 | 17 | 9 | 53 | 17 | 240 | 17 | 0 | 612 | 0 | 267 | 0 | 0 |  | 901 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 260 | 17 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 980 | 180 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 451 | 15 | 150 | 1119 | 80 | 0 |  | 6425 | 4728 | 11153 | 3373 | 901 | 1831 | 0 | 716 | 3759 | 201 | 0 | 122 | 108 | 142 | 0 | 159.485 | 108.12
9:00 | 0 | 0 | 150 | 0 | 0 | 14 | 0 | 333 | 246 |  | 0 | 300 | 253 | 0 | 7 | 15 | 0 | 0 | 74 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 18 | 25 | 30 | 8 | 0 | 126 | 75 | 105 | 0 | 0 | 224 | 0 | 0 | 0 |  | 18 | 0 | 17 | 12 | 0 | 6 | 9 | 40 | 0 | 0 | 0 | 280 | 250 | 209 | 8 | 0 | 5 | 0 | 0 | 8 | 0 | 0 | 25 | 0 | 0 | 33 | 12 | 110 | 35 | 0 | 18 | 2 | 42 | 30 | 47 | 45 | 112 | 0 | 0 | 75 | 0 | 182 | 17 | 0 | 10 | 270 | 8 | 8 | 0 | 15 | 0 | 0 | 67 | 0 | 17 | 6 | 25 | 17 | 10 | 378 | 19 | 35 | 17 | 2 | 70 | 17 | 55 | 0 | 9 | 25 | 230 | 17 | 22 | 17 | 17 | 0 | 17 | 14 | 54 | 17 | 240 | 0 | 0 | 612 | 0 | 268 | 0 | 0 |  | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 260 | 17 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 980 | 180 | 0 | 0 | 3 | 4 | 0 | 0 | 0 | 401 | 24 | 150 | 1061 | 137 | 0 |  | 6318 | 4688 | 11006 | 3352 | 902 | 1885 | 0 | 653 | 3652 | 201 | 0 | 33 | 110 | 218 | 0 | 252.12 | 108.12
10:00 | 0 | 0 | 150 | 0 | 0 | 12 | 0 | 314 | 246 |  | 0 | 300 | 276 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 19 | 18 | 25 | 30 | 8 | 0 | 126 | 75 | 110 | 0 | 0 | 223 | 0 | 0 | 0 |  | 18 | 0 | 17 | 12 | 0 | 6 | 9 | 32 | 0 | 0 | 0 | 280 | 250 | 203 | 8 | 0 | 5 | 0 | 0 | 8 | 0 | 0 | 19 | 0 | 0 | 33 | 12 | 110 | 30 | 0 | 18 | 2 | 42 | 30 | 41 | 44 | 80 | 0 | 0 | 75 | 0 | 182 | 17 | 0 | 10 | 260 | 8 | 11 | 0 | 0 | 0 | 0 | 77 | 0 | 17 | 8 | 25 | 17 | 8 | 380 | 19 | 35 | 34 | 3 | 73 | 17 | 55 | 0 | 28 | 12 | 230 | 17 | 51 | 17 | 17 | 0 | 17 | 16 | 54 | 17 | 240 | 0 | 0 | 612 | 0 | 300 | 0 | 0 |  | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 970 | 180 | 0 | 0 | 3 | 4 | 0 | 0 | 0 | 400 | 32 | 150 | 1060 | 168 | 0 |  | 6339 | 4670 | 11009 | 3335 | 902 | 1819 | 0 | 644 | 3672 | 201 | 0 | 33 | 110 | 293 | 0 | 277.905 | 108.12
11:00 | 0 | 0 | 150 | 0 | 0 | 12 | 0 | 312 | 285 |  | 0 | 300 | 288 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 19 | 17 | 25 | 30 | 8 | 0 | 126 | 75 | 107 | 0 | 0 | 219 | 0 | 0 | 0 |  | 18 | 0 | 17 | 12 | 0 | 10 | 9 | 31 | 0 | 0 | 0 | 280 | 250 | 203 | 8 | 0 | 5 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 33 | 12 | 108 | 30 | 0 | 18 | 2 | 41 | 29 | 44 | 44 | 80 | 0 | 0 | 75 | 0 | 180 | 17 | 0 | 10 | 300 | 8 | 11 | 0 | 0 | 0 | 0 | 96 | 0 | 20 | 13 | 37 | 17 | 0 | 380 | 84 | 35 | 34 | 2 | 77 | 17 | 55 | 17 | 28 | 12 | 230 | 0 | 43 | 35 | 17 | 0 | 17 | 19 | 54 | 17 | 240 | 0 | 0 | 612 | 0 | 300 | 0 | 0 |  | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 970 | 98 | 0 | 0 | 4 | 17 | 0 | 0 | 0 | 400 | 37 | 150 | 1060 | 198 | 0 |  | 6541 | 4725 | 11266 | 3385 | 902 | 1873 | 0 | 750 | 3672 | 201 | 0 | 33 | 108 | 342 | 0 | 175.72 | 108.11
12:00 | 0 | 0 | 150 | 0 | 0 | 30 | 0 | 334 | 308 |  | 0 | 350 | 277 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 19 | 14 | 25 | 22 | 8 | 0 | 126 | 75 | 100 | 0 | 0 | 222 | 0 | 0 | 0 |  | 18 | 0 | 17 | 12 | 0 | 24 | 9 | 25 | 0 | 0 | 0 | 330 | 250 | 205 | 8 | 0 | 5 | 0 | 0 | 20 | 0 | 0 | 30 | 11 | 10 | 32 | 12 | 116 | 28 | 0 | 18 | 2 | 42 | 28 | 44 | 39 | 112 | 0 | 0 | 78 | 0 | 180 | 16 | 0 | 10 | 290 | 8 | 11 | 0 | 0 | 0 | 0 | 105 | 0 | 51 | 6 | 37 | 17 | 0 | 380 | 74 | 35 | 34 | 5 | 77 | 17 | 55 | 17 | 28 | 12 | 230 | 0 | 47 | 54 | 18 | 0 | 17 | 19 | 54 | 17 | 240 | 0 | 0 | 612 | 0 | 300 | 0 | 0 |  | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1000 | 95 | 0 | 0 | 3 | 29 | 0 | 0 | 0 | 400 | 37 | 150 | 1112 | 186 | 0 |  | 6921 | 4931 | 11852 | 3595 | 902 | 2058 | 0 | 852 | 3754 | 201 | 0 | 33 | 116 | 341 | 0 | 141.34 | 108.11
13:00 | 0 | 0 | 150 | 0 | 0 | 50 | 0 | 361 | 330 |  | 0 | 400 | 293 | 0 | 0 | 0 | 0 | 0 | 122 | 0 | 40 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 19 | 14 | 25 | 28 | 8 | 0 | 126 | 75 | 100 | 0 | 0 | 219 | 0 | 0 | 0 |  | 18 | 0 | 17 | 12 | 0 | 26 | 9 | 25 | 0 | 0 | 0 | 280 | 250 | 203 | 8 | 0 | 5 | 0 | 0 | 45 | 0 | 0 | 52 | 18 | 10 | 32 | 12 | 122 | 28 | 0 | 18 | 2 | 40 | 28 | 48 | 42 | 112 | 0 | 0 | 75 | 0 | 180 | 17 | 0 | 10 | 280 | 8 | 11 | 0 | 0 | 0 | 0 | 105 | 0 | 53 | 4 | 37 | 17 | 0 | 380 | 72 | 35 | 34 | 1 | 80 | 17 | 55 | 17 | 28 | 12 | 230 | 0 | 42 | 54 | 34 | 0 | 17 | 13 | 54 | 17 | 240 | 0 | 0 | 612 | 0 | 300 | 0 | 0 |  | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1090 | 180 | 0 | 0 | 3 | 10 | 0 | 0 | 0 | 409 | 34 | 150 | 1110 | 182 | 0 |  | 7012 | 5212 | 12224 | 3573 | 901 | 2334 | 0 | 911 | 3851 | 201 | 0 | 33 | 122 | 298 | 0 | 187.18 | 108.11
14:00 | 0 | 0 | 150 | 0 | 0 | 62 | 0 | 341 | 300 |  | 0 | 350 | 301 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 19 | 14 | 25 | 28 | 8 | 0 | 126 | 75 | 100 | 0 | 0 | 219 | 0 | 0 | 0 |  | 18 | 0 | 17 | 12 | 0 | 26 | 9 | 25 | 0 | 0 | 0 | 280 | 250 | 201 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 50 | 18 | 10 | 30 | 12 | 124 | 30 | 0 | 18 | 1 | 40 | 28 | 49 | 39 | 112 | 0 | 0 | 75 | 0 | 180 | 17 | 0 | 10 | 280 | 8 | 11 | 0 | 0 | 0 | 0 | 106 | 0 | 53 | 2 | 37 | 17 | 0 | 376 | 73 | 35 | 34 | 1 | 79 | 17 | 55 | 17 | 29 | 12 | 230 | 0 | 39 | 17 | 34 | 0 | 17 | 14 | 54 | 17 | 240 | 0 | 0 | 612 | 3 | 300 | 0 | 0 |  | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 1050 | 180 | 0 | 0 | 2 | 36 | 0 | 0 | 0 | 402 | 32 | 150 | 1105 | 131 | 0 |  | 6863 | 4906 | 11769 | 3437 | 902 | 2164 | 0 | 842 | 3799 | 201 | 0 | 33 | 124 | 264 | 3 | 172.855 | 108.11
15:00 | 0 | 0 | 150 | 0 | 0 | 62 | 0 | 358 | 305 |  | 0 | 350 | 269 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 19 | 14 | 25 | 28 | 8 | 0 | 124 | 75 | 100 | 0 | 1 | 220 | 0 | 0 | 0 |  | 18 | 0 | 17 | 12 | 0 | 26 | 9 | 25 | 0 | 0 | 0 | 280 | 275 | 202 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 43 | 18 | 10 | 30 | 12 | 134 | 30 | 0 | 18 | 1 | 37 | 28 | 49 | 42 | 112 | 0 | 0 | 74 | 0 | 178 | 17 | 0 | 10 | 300 | 8 | 11 | 0 | 0 | 0 | 0 | 106 | 0 | 53 | 4 | 37 | 17 | 0 | 380 | 73 | 35 | 34 | 0 | 87 | 17 | 55 | 17 | 29 | 12 | 230 | 0 | 29 | 17 | 34 | 0 | 17 | 10 | 54 | 17 | 240 | 0 | 0 | 612 | 3 | 300 | 0 | 0 |  | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 1050 | 220 | 0 | 0 | 3 | 21 | 0 | 0 | 0 | 402 | 16 | 150 | 1110 | 150 | 0 |  | 6963 | 4977 | 11940 | 3535 | 901 | 2249 | 0 | 844 | 3804 | 199 | 0 | 33 | 134 | 238 | 3 | 200.55 | 108.1
16:00 | 0 | 0 | 130 | 0 | 0 | 42 | 0 | 357 | 305 |  | 0 | 320 | 240 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 19 | 14 | 25 | 28 | 8 | 0 | 124 | 75 | 100 | 0 | 8 | 224 | 0 | 0 | 0 |  | 18 | 0 | 17 | 12 | 0 | 39 | 9 | 27 | 0 | 0 | 0 | 280 | 275 | 179 | 8 | 0 | 5 | 0 | 0 | 10 | 0 | 0 | 42 | 18 | 10 | 21 | 12 | 130 | 30 | 0 | 18 | 1 | 37 | 28 | 50 | 42 | 80 | 0 | 0 | 78 | 0 | 178 | 17 | 0 | 10 | 270 | 8 | 11 | 0 | 0 | 0 | 0 | 68 | 0 | 53 | 2 | 37 | 17 | 0 | 378 | 18 | 35 | 34 | 0 | 86 | 17 | 55 | 17 | 29 | 62 | 230 | 0 | 22 | 17 | 34 | 0 | 17 | 3 | 54 | 17 | 240 | 0 | 0 | 635 | 1 | 300 | 0 | 0 |  | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 20 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1040 | 180 | 0 | 0 | 2 | 12 | 0 | 0 | 0 | 403 | 8 | 150 | 1105 | 43 | 0 |  | 6606 | 4699 | 11305 | 3327 | 901 | 1982 | 0 | 819 | 3813 | 199 | 0 | 37 | 130 | 96 | 1 | 233.975 | 108.1
17:00 | 0 | 0 | 130 | 0 | 0 | 22 | 0 | 356 | 305 |  | 0 | 320 | 257 | 0 | 2 | 0 | 0 | 0 | 98 | 0 | 8 | 76 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 19 | 14 | 25 | 28 | 8 | 0 | 125 | 75 | 102 | 0 | 8 | 226 | 0 | 0 | 0 |  | 18 | 0 | 17 | 12 | 0 | 40 | 9 | 40 | 0 | 0 | 0 | 280 | 275 | 178 | 8 | 0 | 5 | 0 | 0 | 10 | 0 | 0 | 42 | 18 | 10 | 33 | 12 | 138 | 43 | 0 | 18 | 0 | 40 | 28 | 50 | 44 | 80 | 0 | 0 | 84 | 0 | 178 | 17 | 0 | 10 | 275 | 8 | 11 | 0 | 0 | 0 | 0 | 67 | 0 | 53 | 1 | 37 | 17 | 1 | 378 | 18 | 35 | 34 | 0 | 87 | 17 | 52 | 17 | 29 | 53 | 230 | 0 | 3 | 17 | 34 | 0 | 17 | 2 | 53 | 17 | 230 | 0 | 0 | 487 | 0 | 300 | 0 | 0 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 18 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 300 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1000 | 180 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 376 | 3 | 150 | 1009 | 24 | 0 |  | 6554 | 4510 | 11064 | 3363 | 907 | 2003 | 0 | 812 | 3502 | 200 | 0 | 97 | 138 | 42 | 0 | 129.88 | 108.1
18:00 | 0 | 0 | 130 | 0 | 0 | 61 | 0 | 311 | 260 |  | 0 | 400 | 305 | 5 | 17 | 10 | 0 | 0 | 95 | 0 | 8 | 147 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 19 | 14 | 25 | 28 | 25 | 0 | 125 | 75 | 95 | 0 | 10 | 217 | 0 | 0 | 0 |  | 18 | 60 | 17 | 12 | 0 | 40 | 9 | 40 | 0 | 0 | 0 | 335 | 295 | 200 | 8 | 0 | 5 | 0 | 0 | 22 | 0 | 0 | 42 | 18 | 10 | 32 | 12 | 140 | 72 | 0 | 18 | 0 | 40 | 29 | 33 | 45 | 112 | 0 | 0 | 84 | 0 | 179 | 17 | 0 | 10 | 270 | 8 | 8 | 0 | 42 | 0 | 0 | 67 | 0 | 68 | 0 | 37 | 17 | 8 | 378 | 18 | 35 | 34 | 0 | 120 | 20 | 55 | 27 | 73 | 55 | 230 | 0 | 0 | 17 | 34 | 0 | 17 | 0 | 54 | 17 | 230 | 0 | 0 | 375 | 4 | 300 | 0 | 0 |  | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 130 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 414 | 12 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 950 | 220 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 400 | 0 | 150 | 1090 | 0 | 0 |  | 6990 | 4909 | 11899 | 3486 | 906 | 2309 | 0 | 1152 | 3445 | 200 | 0 | 257 | 140 | 0 | 4 | 96 | 108.09
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 170 | 0 | 0 | 62 | 0 | 387 | 330 |  | 0 | 450 | 287 | 8 | 17 | 15 | 0 | 0 | 96 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 18 | 25 | 28 | 25 | 0 | 125 | 75 | 99 | 0 | 17 | 223 | 0 | 0 | 0 |  | 18 | 36 | 17 | 12 | 0 | 40 | 9 | 40 | 0 | 0 | 0 | 280 | 280 | 178 | 8 | 0 | 5 | 0 | 0 | 42 | 0 | 23 | 46 | 18 | 10 | 33 | 12 | 140 | 72 | 0 | 18 | 0 | 40 | 29 | 50 | 46 | 112 | 0 | 0 | 84 | 0 | 180 | 17 | 0 | 10 | 280 | 8 | 0 | 0 | 15 | 0 | 0 | 126 | 0 | 97 | 0 | 50 | 17 | 10 | 376 | 94 | 35 | 34 | 0 | 175 | 17 | 55 | 52 | 76 | 55 | 230 | 6 | 0 | 35 | 34 | 0 | 17 | 0 | 53 | 17 | 230 | 0 | 0 | 393 | 5 | 300 | 0 | 0 |  | 910 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 42 | 0 | 0 | 76 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 350 | 30 | 0 | 33 | 15 | 108 | 0 | 0 | 35 | 1070 | 220 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 465 | 0 | 190 | 1237 | 0 | 0 |  | 7365 | 5519 | 12884 | 3517 | 910 | 2397 | 0 | 1626 | 3835 | 200 | 0 | 254 | 140 | 0 | 5 | 23 | 108.09
19:30 | 0 | 0 | 166 | 0 | 0 | 62 | 0 | 363 | 330 |  | 0 | 450 | 286 | 0 | 4 | 0 | 0 | 0 | 96 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 18 | 25 | 28 | 25 | 0 | 125 | 75 | 100 | 0 | 17 | 225 | 0 | 0 | 0 |  | 18 | 4 | 17 | 12 | 0 | 40 | 9 | 40 | 0 | 0 | 0 | 280 | 280 | 179 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 23 | 52 | 18 | 10 | 33 | 12 | 142 | 72 | 0 | 18 | 0 | 40 | 30 | 50 | 46 | 112 | 0 | 0 | 84 | 0 | 180 | 17 | 0 | 9 | 295 | 8 | 0 | 0 | 0 | 0 | 0 | 126 | 0 | 97 | 0 | 50 | 17 | 0 | 377 | 94 | 35 | 34 | 0 | 175 | 17 | 55 | 52 | 76 | 56 | 230 | 17 | 0 | 17 | 34 | 0 | 17 | 0 | 54 | 17 | 230 | 0 | 0 | 501 | 6 | 300 | 0 | 0 |  | 787 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 31 | 0 | 0 | 130 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 8 | 0 | 0 | 178 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 350 | 53 | 0 | 35 | 15 | 113 | 0 | 0 | 35 | 1100 | 220 | 0 | 0 | 0 | 0 | 114 | 0 | 0 | 565 | 0 | 199 | 1326 | 0 | 0 |  | 7368 | 5703 | 13071 | 3556 | 787 | 2419 | 0 | 1597 | 4169 | 200 | 0 | 195 | 142 | 0 | 6 | 66 | 0
20:00 | 0 | 0 | 170 | 0 | 0 | 62 | 0 | 362 | 330 |  | 0 | 450 | 287 | 0 | 4 | 0 | 0 | 0 | 96 | 0 | 8 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 18 | 25 | 28 | 25 | 0 | 126 | 75 | 100 | 0 | 17 | 225 | 0 | 0 | 0 |  | 18 | 0 | 17 | 12 | 0 | 40 | 9 | 42 | 0 | 0 | 0 | 280 | 280 | 178 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 23 | 52 | 18 | 11 | 33 | 12 | 146 | 72 | 0 | 18 | 0 | 40 | 30 | 50 | 46 | 112 | 0 | 0 | 84 | 0 | 180 | 17 | 0 | 10 | 290 | 8 | 0 | 0 | 0 | 0 | 0 | 126 | 0 | 108 | 0 | 50 | 17 | 0 | 380 | 94 | 35 | 34 | 0 | 175 | 17 | 55 | 52 | 77 | 56 | 260 | 17 | 0 | 17 | 34 | 0 | 17 | 0 | 54 | 17 | 230 | 0 | 0 | 546 | 4 | 300 | 0 | 0 |  | 787 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 31 | 0 | 0 | 138 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 350 | 54 | 0 | 35 | 15 | 113 | 0 | 0 | 35 | 1210 | 220 | 0 | 0 | 0 | 0 | 114 | 0 | 0 | 567 | 0 | 256 | 1409 | 0 | 0 |  | 7458 | 5944 | 13402 | 3600 | 787 | 2420 | 0 | 1610 | 4468 | 201 | 0 | 166 | 146 | 0 | 4 | 79 | 108.09
21:00 | 0 | 0 | 130 | 0 | 0 | 62 | 0 | 369 | 338 |  | 0 | 450 | 269 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 8 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 18 | 25 | 28 | 25 | 0 | 126 | 75 | 103 | 0 | 17 | 225 | 0 | 0 | 0 |  | 18 | 0 | 17 | 12 | 0 | 1 | 9 | 42 | 0 | 0 | 0 | 280 | 270 | 178 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 23 | 52 | 18 | 11 | 33 | 12 | 140 | 75 | 0 | 18 | 0 | 43 | 30 | 50 | 47 | 112 | 0 | 0 | 84 | 0 | 180 | 17 | 0 | 10 | 270 | 8 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 108 | 0 | 50 | 17 | 0 | 376 | 85 | 17 | 34 | 0 | 135 | 17 | 55 | 52 | 77 | 57 | 392 | 17 | 0 | 0 | 34 | 0 | 17 | 0 | 54 | 17 | 230 | 0 | 0 | 553 | 8 | 300 | 0 | 0 |  | 787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 138 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 414 | 54 | 0 | 35 | 15 | 113 | 0 | 0 | 35 | 1220 | 220 | 0 | 0 | 0 | 0 | 114 | 0 | 0 | 571 | 0 | 307 | 1410 | 0 | 0 |  | 7354 | 5982 | 13336 | 3576 | 787 | 2455 | 0 | 1478 | 4541 | 201 | 0 | 150 | 140 | 0 | 8 | 90 | 108.09
22:00 | 0 | 0 | 130 | 0 | 0 | 62 | 0 | 413 | 336 |  | 0 | 450 | 268 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 12 | 25 | 30 | 25 | 0 | 126 | 75 | 100 | 0 | 17 | 224 | 0 | 0 | 0 |  | 18 | 0 | 17 | 12 | 0 | 6 | 9 | 42 | 0 | 0 | 0 | 280 | 270 | 180 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 23 | 52 | 18 | 11 | 33 | 12 | 144 | 73 | 0 | 18 | 0 | 43 | 30 | 50 | 45 | 112 | 0 | 0 | 81 | 0 | 180 | 17 | 0 | 10 | 290 | 8 | 2 | 0 | 0 | 0 | 0 | 136 | 0 | 108 | 0 | 50 | 17 | 0 | 379 | 85 | 17 | 34 | 0 | 135 | 17 | 55 | 52 | 77 | 57 | 392 | 17 | 0 | 0 | 34 | 0 | 17 | 0 | 53 | 17 | 230 | 0 | 0 | 555 | 13 | 300 | 0 | 0 |  | 787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 138 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 414 | 54 | 0 | 35 | 15 | 113 | 0 | 0 | 35 | 1220 | 220 | 0 | 0 | 0 | 0 | 114 | 0 | 0 | 580 | 0 | 307 | 1419 | 0 | 0 |  | 7439 | 6003 | 13442 | 3617 | 787 | 2470 | 0 | 1482 | 4561 | 201 | 0 | 167 | 144 | 0 | 13 | 198.64 | 108.09
23:00 | 0 | 0 | 130 | 0 | 0 | 62 | 0 | 414 | 337 |  | 0 | 450 | 258 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 19 | 25 | 29 | 25 | 0 | 126 | 75 | 103 | 0 | 10 | 225 | 0 | 0 | 0 |  | 18 | 0 | 17 | 12 | 0 | 6 | 9 | 42 | 0 | 0 | 0 | 280 | 270 | 207 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 23 | 52 | 18 | 11 | 33 | 12 | 142 | 72 | 0 | 18 | 0 | 43 | 30 | 50 | 45 | 112 | 0 | 0 | 81 | 0 | 182 | 17 | 0 | 10 | 290 | 8 | 2 | 0 | 0 | 0 | 0 | 77 | 0 | 60 | 0 | 50 | 17 | 0 | 376 | 18 | 17 | 34 | 0 | 135 | 17 | 55 | 17 | 43 | 58 | 392 | 17 | 0 | 0 | 34 | 0 | 17 | 0 | 53 | 17 | 230 | 0 | 0 | 555 | 21 | 271 | 0 | 0 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 414 | 54 | 0 | 35 | 15 | 113 | 0 | 0 | 35 | 1220 | 222 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 573 | 0 | 307 | 1429 | 0 | 0 |  | 7211 | 6097 | 13308 | 3650 | 908 | 2463 | 0 | 1234 | 4535 | 201 | 0 | 154 | 142 | 0 | 21 | 345.71 | 108.09
24:00 | 0 | 0 | 170 | 0 | 0 | 62 | 0 | 413 | 338 |  | 0 | 450 | 268 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 18 | 25 | 29 | 8 | 0 | 126 | 75 | 104 | 0 | 8 | 225 | 0 | 0 | 0 |  | 12 | 0 | 17 | 12 | 0 | 0 | 9 | 42 | 0 | 0 | 0 | 285 | 270 | 206 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 23 | 52 | 18 | 11 | 33 | 12 | 140 | 73 | 0 | 18 | 0 | 43 | 30 | 50 | 45 | 112 | 0 | 0 | 81 | 0 | 182 | 17 | 0 | 10 | 300 | 8 | 2 | 0 | 0 | 0 | 0 | 67 | 0 | 29 | 0 | 25 | 17 | 0 | 377 | 19 | 17 | 34 | 0 | 143 | 17 | 55 | 17 | 28 | 58 | 397 | 22 | 0 | 0 | 34 | 0 | 17 | 0 | 54 | 17 | 230 | 0 | 0 | 550 | 25 | 268 | 0 | 0 |  | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 143 | 54 | 0 | 35 | 15 | 113 | 0 | 0 | 35 | 1220 | 224 | 0 | 0 | 0 | 0 | 114 | 0 | 0 | 570 | 0 | 307 | 1417 | 0 | 0 |  | 7237 | 5891 | 13128 | 3836 | 909 | 2215 | 0 | 1136 | 4512 | 201 | 0 | 154 | 140 | 0 | 25 | 355.26 | 108.09
KWH | 0 | 0 | 3552469 | 0 | 0 | 983772 | 0 | 8843270 | 7286000 |  | 0 | 8843000 | 6565789 | 85440 | 153659 | 205090 | 0 | 0 | 2724000 | 46080 | 322992 | 934560 | 0 | 0 | 0 | 0 | 169200 | 119314 | 7079 | 435528 | 456000 | 394920 | 584500 | 709100 | 288000 | 0 | 2894509 | 1820000 | 2400000 | 0 | 169003 | 5342794 | 0 | 0 | 0 |  | 392400 | 427016 | 408307 | 419880 | 0 | 396480 | 213552 | 985440 | 0 | 0 | 0 | 7226900 | 6422000 | 4675000 | 200727 | 0 | 136584 | 0 | 0 | 932624 | 0 | 310320 | 836482 | 324432 | 187020 | 790000 | 277000 | 3156480 | 994560 | 0 | 419148 | 12750 | 973000 | 687360 | 1146000 | 1069632 | 2433191 | 0 | 0 | 1821120 | 0 | 4678960 | 393000 | 0 | 245160 | 6829000 | 187968 | 137504 | 0 | 225818 | 0 | 0 | 2056800 | 0 | 1107216 | 58995 | 813120 | 425760 | 103709 | 9073000 | 1041600 | 798720 | 673272 | 18719 | 2371091 | 373578 | 1328140 | 1064760 | 754320 | 807360 | 6991400 | 286080 | 350340 | 488160 | 632291 | 0 | 409680 | 121416 | 1304640 | 432720 | 5815300 | 148872 | 0 | 14023635 | 93600 | 6567272 | 0 | 0 |  | 21490909 | 0 | 0 | 0 | 336960 | 0 | 0 | 0 | 133440 | 896 | 42000 | 2692000 | 557944 | 71808 | 0 | 0 | 0 | 0 | 6667 | 68952 | 0 | 0 | 0 | 46483 | 172720 | 0 | 0 | 169182 | 0 | 0 | 4378500 | 0 | 0 | 4105327 | 0 | 0 | 0 | 0 | 0 | 3955127 | 0 | 8075091 | 721440 | 0 | 562848 | 266832 | 1061011 | 0 | 50011 | 456384 | 28041900 | 4738418 | 0 | 34800 | 29760 | 132480 | 987456 | 0 | 0 | 11345450 | 248158 | 5170900 | 29350909 | 1323220 | 0 |  | 167844449 | 130825983 | 298670432 | 86967905 | 21490909 | 52712908 | 0 | 25697956 | 98878566 | 4714509 | 0 | 2611750 | 3156480 | 2345849 | 93600 | 0
Fuel Cost | 0 | 0 | 5186604.74 | 0 | 0 | 1308416.76 | 0 | 9285433.5 | 7868880 |  | 0 | 9638870 | 7288025.79 | 955219.2 | 2035981.75 | 2717442.5 | 0 | 0 | 4767000 | 673689.6 | 4544497.44 | 15149217.6 | 0 | 0 | 0 | 0 | 2152224 | 1610739 | 94929.39 | 326646 | 342000 | 0 | 0 | 0 | 4898880 | 0 | 781517.43 | 491400 | 4536000 | 0 | 2763199.05 | 5556505.76 | 0 | 0 | 0 |  | 5120820 | 7122626.88 | 6949385.14 | 5672578.8 | 0 | 4587273.6 | 271211.04 | 3281515.2 | 0 | 0 | 0 | 8021859 | 6999980 | 5423000 | 258937.83 | 0 | 154339.92 | 0 | 0 | 1557482.08 | 0 | 5359226.4 | 11250682.9 | 444471.84 | 140265 | 1382500 | 207750 | 22663526.4 | 1084070.4 | 0 | 570041.28 | 203235 | 1333010 | 907315.2 | 1994040 | 1850463.36 | 2798169.65 | 0 | 0 | 4152153.6 | 0 | 4725749.6 | 844950 | 0 | 485416.8 | 6829000 | 140976 | 104503.04 | 0 | 3082415.7 | 0 | 0 | 27725664 | 0 | 15334941.6 | 689651.55 | 8391398.4 | 5815881.6 | 1376218.43 | 8347160 | 12665856 | 11549491.2 | 8516890.8 | 291267.64 | 27836608.34 | 4068264.42 | 14118128.2 | 14448793.2 | 9723184.8 | 9510700.8 | 6432088 | 3704736 | 5062413 | 6194750.4 | 7195471.58 | 0 | 5350420.8 | 1450921.2 | 19530460.8 | 5698922.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 64472727 | 0 | 0 | 0 | 3507753.6 | 0 | 0 | 0 | 2403254.4 | 16128 | 603540 | 3015040 | 1082411.36 | 782707.2 | 0 | 0 | 0 | 0 | 116605.83 | 1078409.28 | 0 | 0 | 0 | 633563.29 | 2913786.4 | 0 | 0 | 128070.774 | 0 | 0 | 37129680 | 0 | 0 | 4762179.32 | 0 | 0 | 0 | 0 | 0 | 4587947.32 | 0 | 7994340.09 | 9696153.6 | 0 | 6658491.84 | 3855722.4 | 13474839.7 | 0 | 552621.55 | 5540501.76 | 232747770 | 4833186.36 | 0 | 257520 | 336585.6 | 1553990.4 | 15137700.48 | 0 | 0 | 103130140.5 | 0 | 61895673 | 250950271.95 | 0 | 0 |  | 463978546.33 | 845849313.004 | 1309827859.334 | 90028667.734 | 64472727 | 63221308.88 | 0 | 331065850.57 | 685853535.45 | 1272917.43 | 0 | 41108639.93 | 22663526.4 | 10140685.94 | 0 | 0
Yesterday Day Peak | 0 | 0 | 150 | 0 | 0 | 30 | 0 | 334 | 308 |  | 0 | 350 | 277 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 19 | 14 | 25 | 22 | 8 | 0 | 126 | 75 | 100 | 0 | 0 | 222 | 0 | 0 | 0 |  | 18 | 0 | 17 | 12 | 0 | 24 | 9 | 25 | 0 | 0 | 0 | 330 | 250 | 205 | 8 | 0 | 5 | 0 | 0 | 20 | 0 | 0 | 30 | 11 | 10 | 32 | 12 | 116 | 28 | 0 | 18 | 2 | 42 | 28 | 44 | 39 | 112 | 0 | 0 | 78 | 0 | 180 | 16 | 0 | 10 | 290 | 8 | 11 | 0 | 0 | 0 | 0 | 105 | 0 | 51 | 6 | 37 | 17 | 0 | 380 | 74 | 35 | 34 | 5 | 77 | 17 | 55 | 17 | 28 | 12 | 230 | 0 | 47 | 54 | 18 | 0 | 17 | 19 | 54 | 17 | 240 | 0 | 0 | 612 | 0 | 300 | 0 | 0 |  | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1000 | 95 | 0 | 0 | 3 | 29 | 0 | 0 | 0 | 400 | 37 | 150 | 1112 | 186 | 0 |  | 11852 | DayPeak
Yesterday Evening Peak | 0 | 0 | 170 | 0 | 0 | 62 | 0 | 362 | 330 |  | 0 | 450 | 287 | 0 | 4 | 0 | 0 | 0 | 96 | 0 | 8 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 18 | 25 | 28 | 25 | 0 | 126 | 75 | 100 | 0 | 17 | 225 | 0 | 0 | 0 | 0 | 18 | 0 | 17 | 12 | 0 | 40 | 9 | 42 | 0 | 0 | 0 | 280 | 280 | 178 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 23 | 52 | 18 | 11 | 33 | 12 | 146 | 72 | 0 | 18 | 0 | 40 | 30 | 50 | 46 | 112 | 0 | 0 | 84 | 0 | 180 | 17 | 0 | 10 | 290 | 8 | 0 | 0 | 0 | 0 | 0 | 126 | 0 | 108 | 0 | 50 | 17 | 0 | 380 | 94 | 35 | 34 | 0 | 175 | 17 | 55 | 52 | 77 | 56 | 260 | 17 | 0 | 17 | 34 | 0 | 17 | 0 | 54 | 17 | 230 | 0 | 0 | 546 | 4 | 300 | 0 | 0 |  | 787 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 31 | 0 | 0 | 138 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 350 | 54 | 0 | 35 | 15 | 113 | 0 | 0 | 35 | 1210 | 220 | 0 | 0 | 0 | 0 | 114 | 0 | 0 | 567 | 0 | 256 | 1409 | 0 | 0 |  | 13402 | EvPeak
Forecast for Evening | 0 | 0 | 150 | 0 | 0 | 62 | 0 | 412 | 330 | 0 | 0 | 450 | 310 | 82 | 85 | 55 | 0 | 0 | 160 | 88 | 102 | 149 | 55 | 0 | 0 | 0 | 35 | 35 | 55 | 20 | 19 | 19 | 25 | 30 | 25 | 0 | 126 | 75 | 105 | 0 | 17 | 225 |  | 0 | 0 | 0 | 18 | 70 | 17 | 60 | 0 | 40 | 11 | 35 | 0 | 0 | 0 | 300 | 300 | 200 | 8 | 0 | 5 | 0 | 0 | 50 | 0 | 31 | 52 | 18 | 10 | 33 | 12 | 165 | 65 | 0 | 18 | 0 | 43 | 30 | 50 | 46 | 112 | 0 | 0 | 86 | 0 | 185 | 17 | 0 | 10 | 300 | 8 | 11 | 0 | 300 | 0 | 0 | 160 | 0 | 149 | 0 | 50 | 17 | 150 | 400 | 104 | 105 | 34 | 0 | 300 | 54 | 55 | 52 | 88 | 50 | 380 | 72 | 0 | 126 | 68 | 0 | 34 |  | 54 | 54 | 300 | 150 |  | 550 | 20 | 300 | 0 |  |  | 938 | 0 | 0 |  | 49 | 0 | 0 | 0 | 40 | 40 | 16 | 130 | 25 | 110 | 0 | 0 | 0 | 38 | 0 | 91 | 28 | 42 | 40 | 52 | 32 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 170 |  | 0 | 0 | 0 | 0 | 165 | 0 | 400 | 55 | 0 | 92 | 100 | 113 | 0 | 0 | 113 | 1244 | 220 |  | 150 |  |  | 115 | 0 |  | 520 |  | 300 | 1400 |  | 0
Forecast for Day | 0 | 0 | 150 | 0 | 0 | 42 | 0 | 412 | 330 | 0 | 0 | 450 | 310 | 82 | 85 | 55 | 0 | 0 | 160 | 88 | 50 | 98 | 55 | 0 | 0 | 0 | 17 | 35 | 55 | 20 | 19 | 19 | 25 | 30 | 8 | 0 | 126 | 75 | 105 | 0 | 8 | 225 |  | 0 | 0 | 0 | 18 | 40 | 17 | 35 | 0 | 40 | 11 | 10 | 0 | 0 | 0 | 300 | 300 | 200 | 8 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 149 | 35 | 0 | 18 | 1.6 | 43 | 30 | 50 | 40 | 112 | 0 | 0 | 86 | 0 | 185 | 17 | 0 | 10 | 300 | 8 | 11 | 0 | 300 | 0 | 0 | 115 | 0 | 17 | 20 | 25 | 17 | 150 | 400 | 37 | 35 | 34 | 5 | 70 | 17 | 55 | 17 | 28 | 25 | 380 | 54 | 50 | 54 | 68 | 0 | 17 | 35 | 54 | 17 | 250 | 54 |  | 500 | 10 | 300 | 0 |  |  | 938 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 25 | 0 | 0 | 130 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 28 | 34 | 30 | 0 | 24 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 360 | 54 | 0 | 35 | 100 | 113 | 0 | 8 | 35 | 1244 | 220 |  | 35 | 6 | 100 | 35 | 0 |  | 520 | 30 | 200 | 1200 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 130 | 0 | 0 | 12 | 0 | 301 | 242 | 0 | 0 | 300 | 262 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 0 | 25 | 23 | 0 | 0 | 126 | 75 | 105 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 6 | 9 | 6 | 0 | 0 | 0 | 280 | 240 | 171 | 8 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 8 | 18 | 11 | 33 | 12 | 112 | 35 | 0 | 18 | 0 | 43 | 30 | 11 | 10 | 80 | 0 | 0 | 30 | 0 | 184 | 17 | 0 | 10 | 260 | 8 | 8 | 0 | 0 | 0 | 0 | 68 | 0 | 17 | 0 | 25 | 17 | 0 | 378 | 19 | 0 | 17 | 3 | 15 | 0 | 50 | 17 | 9 | 12 | 330 | 0 | 2 | 0 | 17 | 0 | 17 | 5 | 54 | 12 | 250 | 0 | 0 | 500 | 9 | 271 | 0 | 0 | 0 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 880 | 183 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 412 | 0 | 150 | 1159 | 59 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
[128 empty] | 399274 |  | 399226 | [74 empty] | 292.3904
| Minimum Generation |  | 11006 | 9:00 | [202 empty] | 139680813
| Highest Generation |  | 13529 | 1:00 | [202 empty] | 139.6808 |  |  |  |  | 2.3458
| Day Peak Generation |  | 11852 | 12:00 | [202 empty] | 28309706
| Evening Peak Generation |  | 13402 | 20:00 | [202 empty] | 28.3097 |  |  | 52712908 |  | 4.7145
| HVDC Max Flow |  | 910 | 19:00 | [202 empty] | 21.4909 |  |  |  |  | 0.0936
| HVDC EvPeak Flow |  | 787 | 20:00 | [200 empty] | 298670432 |  | 3.1565 |  | 98.8786
| Load factor L.F |  | 91.98% | [166 empty] | 1275.5 | [36 empty] | 298.6704

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-09-30
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-09-29 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 11852 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 10305
Evening Peak Generation : |  |  | 13402 | MW Hour : | 20:00 | Available Max Generation : |  | 16909
E.P. Demand (at gen end) : |  |  | 13485 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 14000
Maximum Generation : |  |  | 13529 | MW Hour : | 1:00 | Reserve(Generation end) |  | 2909
Total Gen. (MKWH) : |  |  | 298.6704 | System Load Factor : | 91.98% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 690 | MW at | 18:30 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-09-30
Actual : |  | 108.09 | Ft.(MSL) , | Rule curve : | 105.76 | Ft.( MSL )
Gas Consumed : |  | Total = | 1062.02 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 153249976.614
: |  |  | Coal : | 685853535.45 | Oil : | 372174490.5 | Total : | 1211278002.564
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4922.2264 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1354.6424 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1898.2311 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1650.4979 |  |  | 0 | 0%
Cumilla Area |  | 20 | 480:00 | 1357.7644 |  |  | 0 | 0%
Mymensingh Area |  | 30 | 720:00 | 1010.1526 |  |  | 0 | 0%
Sylhet Area |  | 29 | 696:00 | 565.8815 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 471.9053 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 922.9569 |  |  | 0 | 0%
Total |  | 79 |  | 14154.2586 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
| 08:05 | Rangpur 132/33kV S/S T-1(414T) HT is restored.
| 08:05 | Rangpur 132/33kV S/S T-2 (404T) HT is restored.
08:41 | 16:27 | Tangail 132/33kV S/S Kaliakair-2 Project Work S/D. | [5 empty] | 90 MW load interrup.
| 09:02 | Keranigonj 230/132/33kV S/S Lalbagh-3 is restored.
| 09:06 | Sylhet 132/33kV S/S T4 LT is restored.
| 09:42 | Feni 132/33kV S/S T-1(405T) LT is restored.
| 09:42 | Feni 132/33kV S/S T-1(405T) HT is restored.
09:51 | 16:21 | Siddhirganj 230/132kV S/S 335MW EGCB 2 Scheduled S/D Due to ST Transformer schedele check for EGCB end.
| 10:06 | Keranigonj 230/132/33kV S/S Earthing Trafo-1 HT is restored.
| 10:07 | Keranigonj 230/132/33kV S/S Earthing Trafo-1 LT is restored.
| 10:37 | Ashuganj 230/132/33kV S/S 132 kv Busbar-2 is restored.
10:50 | 12:07 | Baghabari PS ---Ishurdi 132 KV ckt Trip [ Baghabari PS END], SF-6 Gas Pressure Low. No Signal in Relay Panel.
| 10:57 | Ashuganj 230/132/33kV S/S TR-OAT-12 LT is restored.
| 10:58 | Ashuganj 230/132/33kV S/S TR-OAT-12 HT is restored.
11:07 | 11:20 | Feni-PHP 132kV Ckt-1 Tripped from Feni 132/33kV end showing Distance Relay Power swing B,C,Z2 relays.
11:37 | 12:26 | Sreepur 230/132/33kV S/S 132/33 kV T-1 LT Tripped showing Master Relay operate. relays.
12:23 | 13:21 | Madunaghat 132/33kV S/S TR-1(507T) LT Forced S/D Due to Emergency Red hot maintenance work by BPDB | [5 empty] | 42 MW load interrup.
| 14:01 | Sirajganj 132/33kV S/S T4-(445) LT is restored.
| 14:01 | Sirajganj 132/33kV S/S T4-(445) HT is restored.
| 14:01 | Sirajganj 132/33kV S/S T3-(435) HT is restored.
| 14:01 | Sirajganj 132/33kV S/S T3-(435) LT is restored.
15:25 | 21:20 | Shahmirpur 132/33kV S/S 416T HT Forced S/D Due to Transformer Trip at 14:07 (Differential Relay trip(87/87N)
signal and T2 Protection General Trip signal) due to 33 kv karnafully Tunnel feeder trip .
16:02 |  | Siddhirganj GT-2 was shutdown due to abnormal sound. | [5 empty] | 100 MW generation interrup.
16:39 | 17:07 | Shikalbaha 230/132kV S/S Hathazari-02 Tripped showing Teleprotection relays Due to Zcom Tripping. | [5 empty] | 41 MW load interrup.
16:43 | 17:16 | Madunaghat_I 400/230kV S/S ATR-01 LT Tripped showing RET670 relays.
16:43 | 17:16 | Madunaghat_I 400/230kV S/S ATR-01 HT Tripped showing RET670 relays.
17:55 |  | Sylhet 132/33kV S/S T4 LT Tripped showing Ins O/C. relays.
18:08 | 18:22 | Sreepur 230/132 kV grids S/S due to tripping of 33 kV Incomer-1 & 2. | [5 empty] | 48 MW load interrup.
20:13 | 00:04 | Chapai 132/33kV S/S T-1 (405T) LT Forced S/D Due to T1 33 kv CB R phase red hot maintenance .
20:13 | 00:04 | Chapai 132/33kV S/S T-1 (405T) HT Forced S/D Due to T1 33 kv CB R phase red hot maintenance .
| 21:14 | Hathazari-Kaptai 132kV Ckt-2 is restored.
| 22:13 | Mirpur-Uttara 3PH 132kV Ckt-1 is restored.
23:43 | 23:55 | Thakurgaon 132/33kV S/S T-3(432T) HT Tripped. | [5 empty] | 13 MW load interrup.
| 21:14 | Hathazari-Kaptai 132kV Ckt-2 is restored.
| 22:13 | Mirpur-Uttara 3PH 132kV Ckt-1 is restored.
23:43 | 23:55 | Thakurgaon 132/33kV S/S T-3(432T) HT Tripped showing N/A relays Due to 33kV Feeder fault under T-2 Transformer.
23:43 | 00:10 | Thakurgaon 132/33kV S/S T-2(412T) HT Tripped showing 33 kV O/C, E/F fault Lockout relays Due to 33 kV Feeder fault.
23:43 | 00:12 | Thakurgaon 132/33kV S/S T-2(412T) LT Tripped showing Lockout relays Due to 33 kV Feeder fault.
00:20 | 00:35 | Bhulta-Haripur 132 kV Ckt-1 Tripped from Bhulta 132/33kV end showing MCGG( over current trip), MVAJ(backup | [5 empty] | 172 MW load interrup in
|  | protection trip), MVAX(TCS-1 trip) relays Due to For KPPGL S/D, line load increased. So the line tripped for over load. | [5 empty] | Bhulta 132/33 kV end.
| 01:38 | Siddhirganj GT GT-2 was sync.
0:57 | 6:38 | Sirajganj GAS 410 MW Unit-4 ST was dhutdown.
06:40 |  | Tangail 132/33kV S/S Kaliakair-2 Project Work S/D Due to project work.
07:16 |  | Fenchuganj -Sylhet 132kV Ckt-1 Project Work S/D from Sylhet 132/33kV end Due to For South Surma GIS Grid Line
LILI Purpose.
07:17 |  | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Project Work S/D from Fenchuganj 230/132/33kV end.
07:29 |  | Sirajganj 132/33kV S/S T4-(445) LT Project Work S/D.
07:29 |  | Sirajganj 132/33kV S/S T3-(435) LT Project Work S/D.
07:30 |  | Sirajganj 132/33kV S/S T3-(435) HT Project Work S/D. | [5 empty] | 3 MW load interrup.
7:30 |  | Sirajganj 132/33kV S/S T4-(445) HT Project Work S/D. | [5 empty] | 9 MW load interrup.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-09-29 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 170 | 3552469
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 62 | 983772 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 362 | 8843270 | Frequency Control
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 330 | 7286000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8843000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 0 | 85440 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 287 | 6565789 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 4 | 153659 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 0 | 205090 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 20 | 435528 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 96 | 2724000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 0 | 46080 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 322992
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 169200
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 47 | 934560 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 119314 | Reserve
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 7079 | Reserve
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 37 | 850920 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 584500 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 709100 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 288000 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 225818 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 108 | 1107216 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 35 | 798720
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 286080 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 488160 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 121416
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 432720 | Low demand
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5422 | 2145 | 47169892
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 169003 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 58995
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 40 | 396480 | Low demand
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 201 | 4714509
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 225 | 5342794
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 34 | 673272 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 427016 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 408307 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 12 | 419880 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 813120 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 9 | 213552 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 985440
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 18719
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 175 | 2371091 | Low demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 373578
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 55 | 1328140 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 56 | 807360 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 34 | 632291 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 0 | 148872 | Low demand
| SS Power I |  | SS Power | 0 | 0 | 546 | 14023635
| Cox's Bazar Wind |  | IPP | 66 | 0 | 4 | 93600 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 300 | 6567272 | On test.
| Chattogram area Total |  |  |  | 2545 | 1934 | 43386926
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 178 | 4675000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7226900 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 280 | 6422000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 230 | 5815300
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 136584
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 932624
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 103709 | Reserve
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 23 | 310320 | Low demand
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 425760 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 324432 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 187020
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 146 | 3156480
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 790000
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 836482
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 12 | 277000 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 52 | 1064760 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 77 | 754320 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 409680 | Machine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 54 | 1304640 | Fuel shortage
| Cumilla Area Total |  |  |  | 2896 | 1544 | 35353738
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 72 | 994560 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 419148 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12750
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 126 | 2056800 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 94 | 1041600 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 350340
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 392400 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 328 | 5267598
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 40 | 973000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 687360 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2433191 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1146000
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 46 | 1069632 | Engine problem
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 137504 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under maint.
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1821120
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 180 | 4678960 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 393000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 187968 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 6829000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 380 | 9073000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 245160
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 260 | 6991400
| Sylhet Area Total |  |  |  | 2427 | 1507 | 36666295
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 787 | 21490909
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 336960 | Low demand
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 31 | 133440
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 896 | Reserve
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 42000 | Reserve
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 54 | 721440 | Low demand
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 266832 | Low demand
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 132480
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 220 | 0 | 0 | Reserve
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 567 | 11345450
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3121 | 1470 | 34470407
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 71808 | Reserve
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 28 | 557944 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 138 | 2692000 | ST Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1210 | 28041900
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4738418
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 34800 | Low demand
| Barisal 307 MW |  | IPP | 307*1 | 307 | 256 | 5170900
| Barisal Area Total |  |  |  | 2265 | 1852 | 41307770
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 6667 | Reserve
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 170 | 4105327 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 160 | 3955127 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 350 | 8075091 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 172720 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 169182 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 46483 | Reserve
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 16 | 68952 | Low demand
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 562848 | Low demand
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 456384 | Low demand
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 29760
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1409 | 29350909
| Rajshahi Area Total |  |  |  | 3631 | 2215 | 46999450
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 180 | 4378500 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1061011 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 50011
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 114 | 987456 | Engine problem
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 248158
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1323220
| Rangpur Area Total |  |  |  | 950 | 407 | 8048356
| Total |  |  |  | 23871 | 13402 | 298670432
| Eastern Grid Total |  |  |  | 13904 | 7458 | 167844449
| Western Grid Total |  |  |  | 9967 | 5944 | 130825983
| National Grid Total |  |  |  | 23871 | 13402 | 298670432
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-09-29
| (a) ENTIRE EASTERN GRID : |  | 8423.3 | MW | (b) ENTIRE WESTERN GRID : |  | 4358.6 | MW
| i) Dhaka area |  | 4257.2 | MW | i) Khulna area |  | 1573 | MW
| ii) Chittagong area |  | 1220.1 | MW | ii) Rajshahi area |  | 1427.6 | MW
| iii) Comilla area |  | 1299 | MW | iii) Barisal area |  | 401 | MW
| iv) Mymensingh area |  | 1083 | MW | iv) Rangpur area |  | 957 | MW
| v) Sylhet area |  | 564 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 12781.9 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 10 | 01:00 | Chhatak | 37 | 22:00 | Kamrangirchar | 43.8 | 00:00 | Narshingdi | 186 | 22:00 | Shikalbaha-230 | N/A | N/A
2 | AKSML | 98 | 08:00 | Chowmuhani | 219 | 18:30 | Kaptai | N/A | N/A | Natore | 149 | 21:00 | Shitalakhya | 84 | 00:00
3 | Aftabnagar | 40 | 00:00 | Chuadanga | 110 | 00:00 | Kazla | 89 | 00:00 | Nawabganj | 55.7 | 22:00 | Sholosohor | 33 | 16:00
4 | Agargaon | 78 | 00:00 | Coxsbazar | 127 | 00:00 | Keranigonj | 64 | 00:00 | Netrakona | 139 | 20:00 | Shyampur | 138 | 04:00
5 | Agrabad | 63 | 00:00 | Cumilla(N) | 168 | 01:00 | Khagrachori | 28 | 00:00 | New | 66.4 | 00:00 | Siddhirganj | 102 | 00:00
6 | Amnura | 51 | 01:00 | Cumilla(S) | 156 | 00:00 | Khulna | 93 | 00:00 | Niamatpur | 89 | 22:00 | Sirajganj | 116 | 21:00
7 | Ashuganj | 67 | 02:00 | Daudkandi | 142 | 19:00 | Khulshi | 159 | 23:00 | Noapara | 46 | 00:00 | Sonargaon | 92 | 00:00
8 | BIPTC | N/A | N/A | Dhaka | 14 | 15:00 | Kishoreganj | 136 | 15:00 | PHP | 4 | 10:00 | Sreemongol | 75 | 00:00
9 | BSRM | 191 | 23:00 | Dhamrai | 118 | 00:00 | Kodda | 234 | 00:00 | Pabna | 119 | 00:00 | Sreepur | 72 | 00:00
10 | Bagerhat | 94 | 00:00 | Dhanmondi | 112 | 18:00 | Kulaura | 52 | 00:00 | Palashbari | 128 | 21:00 | Srinagar | 46 | 00:00
11 | Bakulia | 88 | 00:00 | Dohazari | 90 | 22:00 | Kurigram | 72 | 18:30 | Panchagarh | 62 | 19:00 | Sunamganj | 61 | 19:30
12 | Banani | 25.8 | 16:00 | Faridpur | 156 | 00:00 | Kushtia | 136 | 21:00 | Patuakhali | 114 | 00:00 | Sylhet | 160 | 19:30
13 | Bangabhaban | 5 | 16:00 | Fatullah | 63 | 00:00 | Lalbag | 60 | 13:00 | Payra | 26 | 00:00 | TK | 29.6 | 00:00
14 | Barapukuria | 60 | 18:30 | Fenchuganj | 49 | 18:30 | Lalmonirhat | 55 | 20:00 | Postogola | 60 | 00:00 | Tangail | 249 | 18:30
15 | Barguna | 22 | 00:00 | Feni | 118 | 18:30 | MI_Cement | 19.7 | 12:00 | Purbachal | 21 | 00:00 | Thakurgaon | 103 | 19:00
16 | Barishal | 103 | 00:00 | GPH | 11 | 04:00 | Madanganj | 26 | 00:00 | Purbasadipur | 123 | 20:00 | Tongi | 99 | 00:00
17 | Barishal-230 | 100 | 00:00 | Ghorashal | 70 | 21:00 | Madaripur | 111 | 00:00 | Rahim | 23 | 00:00 | Ullon | 50 | 23:00
18 | Baroaulia | 54 | 23:00 | Goalpara | 36 | 00:00 | Madartek | 91.02 | 00:00 | Rajbari | 82 | 00:00 | Uttara | 70 | 15:00
19 | Baroirhat | 58 | 18:00 | Gollamari | 54 | 00:00 | Madunaghat | 51 | 18:30 | Rajendrapur | 92 | 13:00 | UttaraNew | 74 | 00:00
20 | Bashundhara | 144 | 18:00 | Gopalganj | 109.6 | 00:00 | Magura | 62 | 00:00 | Rajshahi | 156 | 00:00 | Zigatola | 77 | 00:00
21 | BashundharaCement | 0 | 00:00 | Gulshan | 98 | 15:00 | Mahasthangarh | 82 | 00:00 | Rajshahi-230 | 35 | 00:00
22 | Beanibazar | 82 | 00:00 | Halishahar | 60 | 18:30 | Manikganj | 98 | 19:30 | Ramganj | 112 | 19:30
23 | Benapole | 62 | 00:00 | HaripurSBU | 147 | 00:00 | Maniknagar | 72 | 00:00 | Rampur | 30 | 00:00
24 | Bhaluka | 114 | 05:00 | Hasnabad | 99 | 00:00 | Matarbari | 44 | 00:00 | Rangamati | 16 | 19:30
25 | Bhandaria | 50 | 00:00 | Hathazari | 72 | 20:00 | Matuail | 58 | 00:00 | Rangpur | 148 | 21:00
26 | Bhangura | 38 | 21:00 | Ishurdi | 76 | 18:30 | Millgate | 86 | 00:00 | Ruppur | 5.6 | 11:00
27 | Bheramara(GK) | 65 | 00:00 | Jaldhaka | 84 | 18:30 | Mirpur | 136 | 00:00 | SSM | 0 | 00:00
28 | Bhulta | 226 | 02:00 | Jamalpur | 169 | 20:00 | Mirsorai | 5 | 15:00 | Saidpur | 98 | 21:00
29 | Bog-Sherpur | 68 | 18:30 | Jashore | 134 | 00:00 | Mithapukur | 52 | 19:30 | Satkhira | 128 | 00:00
30 | Bogura | 168 | 22:00 | Jhenaidah | 127 | 00:00 | Modern | 0 | 00:00 | Satmasjid | 115 | 00:00
31 | Borhanuddin | 67 | 03:00 | Joydebpur | 148 | 15:00 | Mogbazar | 113.9 | 18:00 | Savar | 152 | 00:00
32 | Brahmanbaria | 161 | 21:00 | Joypurhat | 61 | 00:00 | Mongla | 26 | 09:00 | ShahCement | 26 | 12:00
33 | Cantonment | 140 | 00:00 | Juldah | 21 | 10:00 | Motijheel | 34 | 16:00 | Shahjadpur | 103 | 00:00
34 | Chandpur | 70 | 21:00 | KSRM | 41 | 08:00 | Munshiganj | 108 | 00:00 | Shahjibazar | 134 | 00:00
35 | Chandraghona | 36 | 14:00 | Kabirpur | 214 | 03:00 | Mymensingh | 246 | 18:30 | Shahmirpur | 42 | 02:00
36 | Chapai | 62 | 00:00 | Kachua | 84 | 21:00 | Naogaon | 130 | 20:00 | Shariatpur | 86 | 00:00
37 | Charsaidpur | 21 | 00:00 | Kallyanpur | 117 | 00:00 | Narail | 58 | 00:00 | Sherpur | 142 | 22:00
38 | Chauddagram | 61 | 00:00 | Kalurghat | 24 | 00:00 | Narinda | 64 | 00:00 | Shikalbaha | 27 | 00:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-09-29 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 396 | 06:00 | 379 | 00:00 | Gopalganj | 404 | 08:00 | 388 | 00:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 380 | 18:00 | 366 | 00:00
| Bhulta | 398 | 08:00 | 384 | 01:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 402 | 05:00 | 393 | 21:00 | Payra | 413 | 09:00 | 403 | 00:00
| BIPTC | 400 | 08:00 | 394 | 01:00 | Rahanpur | 404 | 07:00 | 386 | 21:00
| Bogura | N/A | N/A | N/A | N/A | Rampal | 407 | 17:00 | 388 | 00:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 231 | 06:00 | 222 | 00:00 | Hasnabad | 232 | 06:00 | 223 | 23:00
| AKSML | 235 | 18:00 | 227 | 03:00 | Hathazari | 234 | 16:00 | 227 | 17:00
| Aminbazar | 233 | 07:00 | 223 | 00:00 | Ishurdi | 236 | 17:00 | 220 | 00:00
| Ashuganj | 235 | 06:00 | 221 | 19:00 | Jhenaidah | 229 | 17:00 | 209 | 00:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 237 | 18:30 | 223 | 01:00
| Baghabari | 229 | 17:00 | 216 | 00:00 | Keranigonj | 231 | 06:00 | 222 | 00:00
| Barapukuria | 221 | 07:00 | 209 | 00:00 | Khulna(S) | 233 | 06:00 | 218 | 00:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 238 | 07:00 | 229 | 00:00 | Maniknagar | 232 | 06:00 | 225 | 01:00
| Bheramara | 236 | 06:00 | 220 | 00:00 | Meghnaghat | 239 | 07:00 | 232 | 00:00
| Bhulta | 235 | 07:00 | 227 | 01:00 | Mirsorai | 232 | 18:30 | 224 | 21:00
| Bibiana | 232 | 07:00 | 224 | 23:00 | Rajshahi | 233 | 17:00 | 215 | 00:00
| BIPTC | 236 | 17:00 | 217 | 00:00 | Rampal | 233 | 17:00 | 217 | 00:00
| Bogura | 229 | 07:00 | 215 | 01:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 242 | 07:00 | 235 | 02:00 | Rampura | 233 | 04:00 | 225 | 00:00
| BSRM | 232 | 06:00 | 224 | 03:00 | Shikalbaha | 233 | 16:00 | 227 | 02:00
| Cumilla(N) | 232 | 17:00 | 224 | 01:00 | Shyampur | 232 | 06:00 | 224 | 00:00
| Fenchuganj | 238 | 06:00 | 228 | 23:00 | Siddhirganj | 234 | 08:00 | 227 | 00:00
| Ghorashal | 235 | 18:30 | 230 | 00:00 | Sirajgonj | 238 | 17:00 | 229 | 00:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 233 | 06:00 | 222 | 01:00
| GPH | 232 | 06:00 | 225 | 03:00 | Tongi | 229 | 07:00 | 219 | 00:00
| Haripur | 232 | 07:00 | 225 | 00:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 137 | 06:00 | 131 | 00:00 | Lalbag | 134 | 07:00 | 126 | 23:00
| Agargaon | 133 | 06:00 | 126 | 00:00 | Lalmonirhat | 130 | 08:00 | 119 | 00:00
| Agrabad | 136 | 16:00 | 131 | 01:00 | Madanganj | 135 | 08:00 | 129 | 23:00
| AKS | 132 | 05:00 | 129 | 13:00 | Madaripur | 132 | 09:00 | 124 | 00:00
| Aminbazar | 137 | 17:00 | 130 | 00:00 | Madartek | 136 | 06:00 | 130 | 23:00
| Amnura | 135 | 17:00 | 120 | 00:00 | Madunaghat | 136 | 07:00 | 132 | 01:00
| Ashuganj | 140 | 06:00 | 135 | 01:00 | Magura | 138 | 17:00 | 124 | 00:00
| Bagerhat | 136 | 17:00 | 120 | 00:00 | Mahasthangarh | 136 | 07:00 | 125 | 23:00
| Bakulia | 136 | 15:00 | 132 | 01:00 | Manikganj | 134 | 17:00 | 125 | 23:00
| Banani | 137 | 06:00 | 130 | 12:00 | Maniknagar | 135 | 06:00 | 129 | 00:00
| Bangabhaban | 135 | 07:00 | 130 | 00:00 | Matarbari | 137 | 16:00 | 115 | 00:00
| Barapukuria | 136 | 07:00 | 128 | 00:00 | Matuail | 135.5 | 08:00 | 130 | 23:00
| Barguna | 136 | 07:00 | 127 | 00:00 | Millgate | 134 | 17:00 | 128 | 00:00
| Barishal | 136 | 17:00 | 125 | 00:00 | Mirpur | 135 | 07:00 | 128 | 23:00
| Barishal-230 | 137 | 07:00 | 131 | 00:00 | Mithapukur | 133 | 07:00 | 122 | 03:00
| Baroaulia | 136 | 16:00 | 130 | 23:00 | MI_Cement | 135.4 | 06:00 | 129.5 | 23:00
| Baroirhat | 129 | 00:00 | 122 | 21:00 | Modern | 135 | 18:00 | 131 | 02:00
| Bashundhara | 138 | 07:00 | 127 | 00:00 | Mogbazar | 138 | 06:00 | 131 | 00:00
| BashundharaCement | 135 | 08:00 | 124 | 17:00 | Mongla | 135 | 17:00 | 120 | 00:00
| Beanibazar | 128 | 06:00 | 120 | 23:00 | Motijheel | 135 | 07:00 | 130 | 00:00
| Benapole | 137 | 17:00 | 120 | 00:00 | Munshiganj | 135 | 07:00 | 129 | 23:00
| Bhaluka | 127 | 06:00 | 116 | 01:00 | Mymensingh | 135 | 11:00 | 114 | 01:00
| Bhandaria | 134 | 08:00 | 120 | 01:00 | Naogaon | 133 | 07:00 | 119 | 22:00
| Bhangura | 138 | 06:00 | 129 | 00:00 | Narail | 139 | 08:00 | 122 | 00:00
| Bheramara | 135 | 06:00 | 124 | 00:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara(GK) | 136 | 17:00 | 124 | 00:00 | Narshingdi | 130 | 17:00 | 121 | 01:00
| Bhulta | 128 | 14:00 | 122 | 00:00 | Natore | 132 | 17:00 | 119 | 00:00
| Bog-Sherpur | 137 | 07:00 | 125 | 21:00 | Nawabganj | 132 | 06:00 | 126 | 00:00
| Bogura | 138 | 06:00 | 110 | 00:00 | Netrakona | 135 | 15:00 | 118 | 04:00
| Bogura-230 | 138 | 07:00 | 127 | 23:00 | New | 136 | 17:00 | 129 | 00:00
| Brahmanbaria | 136 | 06:00 | 119 | 23:00 | Niamatpur | 130 | 07:00 | 114 | 21:00
| Cantonment | 132 | 06:00 | 126 | 00:00 | Noapara | 138 | 17:00 | 124 | 00:00
| Chandpur | 128 | 17:00 | 116 | 21:00 | Pabna | 136 | 17:00 | 124 | 00:00
| Chandraghona | 138 | 18:00 | 133 | 01:00 | Palashbari | 130 | 08:00 | 120 | 00:00
| Chapai | 131 | 17:00 | 120 | 00:00 | Panchagarh | 133 | 06:00 | 120 | 00:00
| Charsaidpur | 136 | 17:00 | 129 | 23:00 | Patuakhali | 137 | 17:00 | 130 | 01:00
| Chauddagram | 130 | 17:00 | 121 | 14:00 | Payra | 139 | 17:00 | 134 | 00:00
| Chhatak | 128 | 06:00 | 121 | 00:00 | PHP | 128 | 00:00 | 120 | 23:00
| Chowmuhani | 124 | 16:00 | 113 | 23:00 | Postogola | 136 | 07:00 | 130 | 00:00
| Chuadanga | 135 | 17:00 | 114 | 00:00 | Purbachal | 137 | 08:00 | 127 | 00:00
| Coxsbazar | 126 | 15:00 | 114 | 00:00 | Purbasadipur | 129 | 06:00 | 119 | 00:00
| Cumilla(N) | 136 | 17:00 | 128 | 13:00 | Rahanpur | 133 | 07:00 | 127 | 22:00
| Cumilla(S) | 132 | 16:00 | 125 | 23:00 | Rahim | 135 | 07:00 | 130 | 23:00
| Daudkandi | 126 | 06:00 | 119 | 23:00 | Rajbari | 130 | 08:00 | 118 | 00:00
| Dhaka | 137 | 06:00 | 131 | 23:00 | Rajendrapur | 147 | 19:30 | 124 | 02:00
| Dhamrai | 136 | 18:00 | 128 | 00:00 | Rajshahi | 132 | 06:00 | 120 | 00:00
| Dhanmondi | 135 | 06:00 | 130 | 23:00 | Rajshahi-230 | 136 | 17:00 | 120 | 00:00
| Dohazari | 132 | 09:00 | 127 | 00:00 | Ramganj | 122 | 16:00 | 112 | 21:00
| Faridpur | 130 | 08:00 | 120 | 00:00 | Rampur | 135 | 07:00 | 130 | 01:00
| Fatullah | 136 | 06:00 | 131 | 00:00 | Rampura | 136 | 04:00 | 130 | 00:00
| Fenchuganj | 136 | 06:00 | 129 | 00:00 | Rangamati | 136 | 06:00 | 132 | 02:00
| Feni | 128 | 19:00 | 121 | 23:00 | Rangpur | 131 | 08:00 | 121 | 00:00
| Ghorashal | 140 | 06:00 | 134 | 00:00 | Ruppur | 138 | 17:00 | 127 | 00:00
| Goalpara | 139 | 17:00 | 126 | 00:00 | Saidpur | 130 | 07:00 | 120 | 00:00
| Gollamari | 137 | 17:00 | 127 | 00:00 | Satkhira | 136 | 17:00 | 119 | 00:00
| Gopalganj | 132 | 17:00 | 123 | 23:00 | Satmasjid | 132 | 06:00 | 126 | 00:00
| Gopalganj-400 | 131 | 08:00 | 123 | 00:00 | Savar | 136 | 06:00 | 128 | 23:00
| Gulshan | 136 | 07:00 | 130 | 06:00 | ShahCement | 136 | 17:00 | 129 | 23:00
| Halishahar | 136 | 16:00 | 131 | 01:00 | Shahjadpur | 142 | 17:00 | 132 | 23:00
| Haripur | 135 | 07:00 | 131 | 00:00 | Shahjibazar | 135 | 06:00 | 121 | 01:00
| HaripurSBU | 135 | 07:00 | 130 | 23:00 | Shahmirpur | 136 | 15:00 | 131 | 05:00
| Hasnabad | 136 | 06:00 | 132 | 00:00 | Shariatpur | 131 | 08:00 | 122 | 00:00
| Hathazari | 137 | 05:00 | 133 | 21:00 | Sherpur | 137 | 15:00 | 110 | 23:00
| Ishurdi | 138 | 06:00 | 127 | 00:00 | Shikalbaha | 124 | 06:00 | 115 | 17:00
| Jaldhaka | 131 | 07:00 | 119 | 00:00 | Shikalbaha-230 | 137 | 18:30 | 132 | 01:00
| Jamalpur | 138 | 15:00 | 114 | 18:00 | Shitalakhya | 135.4 | 06:00 | 129.5 | 23:00
| Jashore | 138 | 17:00 | 121 | 00:00 | Sholosohor | 135 | 06:00 | 131 | 01:00
| Jhenaidah | 140 | 17:00 | 124 | 00:00 | Shyampur | 133 | 19:30 | 127 | 04:00
| Jhenaidah-230 | 140 | 17:00 | 125 | 00:00 | Shyampur-230 | 136 | 06:00 | 131 | 00:00
| Joydebpur | 140 | 01:00 | 130 | 00:00 | Siddhirganj | 136 | 08:00 | 130 | 23:00
| Joypurhat | 131 | 07:00 | 116 | 23:00 | Sirajganj | 136 | 06:00 | 125 | 00:00
| Juldah | 136 | 15:00 | 132 | 01:00 | Sonargaon | 132 | 18:30 | 126 | 14:00
| Kabirpur | 137 | 18:30 | 126 | 00:00 | Sreemongol | 133 | 06:00 | 122 | 01:00
| Kachua | 128 | 17:00 | 118 | 21:00 | Sreepur | 128 | 06:00 | 121 | 01:00
| Kaliakoir | 137 | 18:30 | 130 | 01:00 | Srinagar | 133 | 08:00 | 126 | 00:00
| Kallyanpur | 136 | 06:00 | 131 | 00:00 | SSM | 140 | 19:00 | 136 | 00:00
| Kalurghat | 136 | 07:00 | 132 | 02:00 | Sunamganj | 127 | 06:00 | 117 | 00:00
| Kamrangirchar | 135 | 06:00 | 126 | 23:00 | Sylhet | 131 | 06:00 | 126 | 00:00
| Kaptai | N/A | N/A | N/A | N/A | Tangail | 132 | 06:00 | 120 | 23:00
| Kazla | 134 | 07:00 | 129 | 00:00 | Thakurgaon | 132 | 06:00 | 118 | 03:00
| Keranigonj | 134 | 07:00 | 127 | 00:00 | TK | 137 | 16:00 | 131 | 05:00
| Khagrachori | 136 | 18:30 | 131 | 00:00 | Tongi | 136 | 17:00 | 128 | 00:00
| Khulna | 138 | 17:00 | 125 | 00:00 | Ullon | 136 | 06:00 | 131 | 00:00
| Khulna(S) | 137 | 06:00 | 126 | 00:00 | Uttara | 135 | 06:00 | 128 | 23:00
| Khulshi | 134 | 05:00 | 130 | 01:00 | UttaraNew | 133 | 18:00 | 126 | 00:00
| Kishoreganj | 131 | 06:00 | 123 | 01:00 | Zigatola | 133 | 08:00 | 127 | 00:00
| Kodda | 137 | 06:00 | 124 | 02:00
| KSRM | 136 | 16:00 | 131 | 04:00
| Kulaura | 133 | 06:00 | 126 | 01:00
| Kurigram | 130 | 05:00 | 116 | 22:00
| Kushtia | 136 | 17:00 | 123 | 00:00

## L-Curve
Date | 2023-09-29
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1000 | 7237 | 5891 | 13128 |  |  |  | QF-LDC-11
0:30 | 1040 | 7260.5 | 6068 | 13328.5 | Date: | 2023-09-29
1:00 | 1080 | 7284 | 6245 | 13529
1:30 | 1075 | 7230.5 | 6158 | 13388.5
2:00 | 1070 | 7177 | 6071 | 13248
2:30 | 1030 | 7174 | 5948.5 | 13122.5 | [5 empty] | Gen. at Eve. Peak | 13402 | 13402 MW (20:00 )
3:00 | 990 | 7171 | 5826 | 12997 | [6 empty] | 20:00
3:30 | 965 | 7114.5 | 5743.5 | 12858 | [5 empty] | Gen. at Day Peak | 11852 | 11852 MW (12:00 )
4:00 | 940 | 7058 | 5661 | 12719 | [6 empty] | 12:00
4:30 | 940 | 7014 | 5597.5 | 12611.5 | [5 empty] | Highest Generation | 13529
5:00 | 940 | 6970 | 5534 | 12504 | [6 empty] | 1:00
5:30 | 900 | 6788 | 5289.5 | 12077.5
6:00 | 860 | 6606 | 5045 | 11651
6:30 | 890 | 6530.5 | 4900.5 | 11431
7:00 | 920 | 6455 | 4756 | 11211
7:30 | 935 | 6440 | 4742 | 11182
8:00 | 950 | 6425 | 4728 | 11153
8:30 | 975 | 6371.5 | 4708 | 11079.5
9:00 | 1000 | 6318 | 4688 | 11006
9:30 | 1060 | 6328.5 | 4679 | 11007.5
10:00 | 1120 | 6339 | 4670 | 11009
10:30 | 1135 | 6440 | 4697.5 | 11137.5
11:00 | 1150 | 6541 | 4725 | 11266
11:30 | 1165 | 6731 | 4828 | 11559
12:00 | 1180 | 6921 | 4931 | 11852
12:30 | 1160 | 6966.5 | 5071.5 | 12038
13:00 | 1140 | 7012 | 5212 | 12224
13:30 | 1090 | 6937.5 | 5059 | 11996.5
14:00 | 1040 | 6863 | 4906 | 11769
14:30 | 1060 | 6913 | 4941.5 | 11854.5
15:00 | 1080 | 6963 | 4977 | 11940
15:30 | 1040 | 6784.5 | 4838 | 11622.5
16:00 | 1000 | 6606 | 4699 | 11305
16:30 | 975 | 6580 | 4604.5 | 11184.5
17:00 | 950 | 6554 | 4510 | 11064
17:30 | 915 | 6772 | 4709.5 | 11481.5
18:00 | 880 | 6990 | 4909 | 11899
18:30 | 850 | 7177.5 | 5214 | 12391.5
19:00 | 820 | 7365 | 5519 | 12884
19:30 | 840 | 7368 | 5703 | 13071
20:00 | 890 | 7458 | 5944 | 13402 |  |  |  | Executive Engineer
20:30 | 830 | 7406 | 5963 | 13369 |  |  |  | Network Operation Division
21:00 | 770 | 7354 | 5982 | 13336
21:30 | 795 | 7396.5 | 5992.5 | 13389
22:00 | 820 | 7439 | 6003 | 13442 |  |  |  |  | Page 6 of 7
22:30 | 915 | 7325 | 6050 | 13375
23:00 | 1010 | 7211 | 6097 | 13308
23:30 | 1005 | 7224 | 5994 | 13218
24:00 | 1000 | 7237 | 5891 | 13128
13402 MW (20:00 )
11852 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-09-29 |  | Energy |  | 298670432
QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3836 | 909 | 2215 | 0 | 1136 | 4512 | 201 | 0 | 154 | 140 | 0 | 25 | 355.26
0:30 | 3834 | 905 | 2312 | 0 | 1257.5 | 4520 | 200.5 | 0 | 141 | 146 | 0 | 12.5 | 402.5325 |  | Date: | 43736
1:00 | 3832 | 901 | 2409 | 0 | 1379 | 4528 | 200 | 0 | 128 | 152 | 0 | 0 | 449.805
1:30 | 3836.5 | 901 | 2359.5 | 0 | 1293.5 | 4522.5 | 200 | 0 | 123.5 | 152 | 0 | 0 | 440.7325 | [7 empty] | Total Energy | 298.6704 | 298.6704 | Total Energy Gen 298.670 MKWHr Energy Not Served 5.939 MKWHr Energy Requirement 304.609 MKWHr
2:00 | 3841 | 901 | 2310 | 0 | 1208 | 4517 | 200 | 0 | 119 | 152 | 0 | 0 | 431.66 | [7 empty] | Energy not Served | 5.9386 | 5.9386
2:30 | 3816.5 | 902 | 2328 | 0 | 1133.5 | 4473.5 | 200 | 0 | 119 | 150 | 0 | 0 | 408.2625 | [7 empty] | Energy Requirement | 304.6091 | 304.6091
3:00 | 3792 | 903 | 2346 | 0 | 1059 | 4430 | 200 | 0 | 119 | 148 | 0 | 0 | 384.865
3:30 | 3761 | 902 | 2338.5 | 0 | 1005 | 4385.5 | 200 | 0 | 119 | 147 | 0 | 0 | 374.36
4:00 | 3730 | 901 | 2331 | 0 | 951 | 4341 | 200 | 0 | 119 | 146 | 0 | 0 | 363.855
4:30 | 3708.5 | 901 | 2284 | 0 | 953.5 | 4300 | 200 | 0 | 115 | 144 | 0 | 5.5 | 347.1425
5:00 | 3687 | 901 | 2237 | 0 | 956 | 4259 | 200 | 0 | 111 | 142 | 0 | 11 | 330.43
5:30 | 3543 | 901.5 | 2116.5 | 0 | 957 | 4106 | 200 | 0 | 111 | 134 | 0.5 | 8 | 475.1125
6:00 | 3399 | 902 | 1996 | 0 | 958 | 3953 | 200 | 0 | 111 | 126 | 1 | 5 | 619.795
6:30 | 3382 | 902 | 1911 | 0 | 911.5 | 3849 | 200.5 | 0 | 127 | 118 | 26 | 4 | 471.77 | [6 empty] | Coal
7:00 | 3365 | 902 | 1826 | 0 | 865 | 3745 | 201 | 0 | 143 | 110 | 51 | 3 | 323.745
7:30 | 3369 | 901.5 | 1828.5 | 0 | 790.5 | 3752 | 201 | 0 | 132.5 | 109 | 96.5 | 1.5 | 241.615 | [5 empty] | Oil
8:00 | 3373 | 901 | 1831 | 0 | 716 | 3759 | 201 | 0 | 122 | 108 | 142 | 0 | 159.485
8:30 | 3362.5 | 901.5 | 1858 | 0 | 684.5 | 3705.5 | 201 | 0 | 77.5 | 109 | 180 | 0 | 205.8025
9:00 | 3352 | 902 | 1885 | 0 | 653 | 3652 | 201 | 0 | 33 | 110 | 218 | 0 | 252.12
9:30 | 3343.5 | 902 | 1852 | 0 | 648.5 | 3662 | 201 | 0 | 33 | 110 | 255.5 | 0 | 265.0125
10:00 | 3335 | 902 | 1819 | 0 | 644 | 3672 | 201 | 0 | 33 | 110 | 293 | 0 | 277.905
10:30 | 3360 | 902 | 1846 | 0 | 697 | 3672 | 201 | 0 | 33 | 109 | 317.5 | 0 | 226.8125
11:00 | 3385 | 902 | 1873 | 0 | 750 | 3672 | 201 | 0 | 33 | 108 | 342 | 0 | 175.72
11:30 | 3490 | 902 | 1965.5 | 0 | 801 | 3713 | 201 | 0 | 33 | 112 | 341.5 | 0 | 158.53
12:00 | 3595 | 902 | 2058 | 0 | 852 | 3754 | 201 | 0 | 33 | 116 | 341 | 0 | 141.34
12:30 | 3584 | 901.5 | 2196 | 0 | 881.5 | 3802.5 | 201 | 0 | 33 | 119 | 319.5 | 0 | 157.0975
13:00 | 3573 | 901 | 2334 | 0 | 911 | 3851 | 201 | 0 | 33 | 122 | 298 | 0 | 172.855
13:30 | 3573 | 901 | 2334 | 0 | 911 | 3851 | 201 | 0 | 33 | 122 | 298 | 0 | 172.855
14:00 | 3573 | 901 | 2334 | 0 | 911 | 3851 | 201 | 0 | 33 | 122 | 298 | 0 | 172.855
14:30 | 3554 | 901 | 2291.5 | 0 | 877.5 | 3827.5 | 200 | 0 | 33 | 128 | 268 | 1.5 | 186.7025
15:00 | 3535 | 901 | 2249 | 0 | 844 | 3804 | 199 | 0 | 33 | 134 | 238 | 3 | 200.55
15:30 | 3431 | 901 | 2115.5 | 0 | 831.5 | 3808.5 | 199 | 0 | 35 | 132 | 167 | 2 | 217.2625
16:00 | 3327 | 901 | 1982 | 0 | 819 | 3813 | 199 | 0 | 37 | 130 | 96 | 1 | 233.975
16:30 | 3345 | 904 | 1992.5 | 0 | 815.5 | 3657.5 | 199.5 | 0 | 67 | 134 | 69 | 0.5 | 181.9275
17:00 | 3363 | 907 | 2003 | 0 | 812 | 3502 | 200 | 0 | 97 | 138 | 42 | 0 | 129.88
17:30 | 3424.5 | 906.5 | 2156 | 0 | 982 | 3473.5 | 200 | 0 | 177 | 139 | 21 | 2 | 112.94
18:00 | 3486 | 906 | 2309 | 0 | 1152 | 3445 | 200 | 0 | 257 | 140 | 0 | 4 | 96
18:30 | 3501.5 | 908 | 2353 | 0 | 1389 | 3640 | 200 | 0 | 255.5 | 140 | 0 | 4.5 | 59.5
19:00 | 3517 | 910 | 2397 | 0 | 1626 | 3835 | 200 | 0 | 254 | 140 | 0 | 5 | 23
19:30 | 3556 | 787 | 2419 | 0 | 1597 | 4169 | 200 | 0 | 195 | 142 | 0 | 6 | 51
20:00 | 3600 | 787 | 2420 | 0 | 1610 | 4468 | 201 | 0 | 166 | 146 | 0 | 4 | 79
20:30 | 3588 | 787 | 2437.5 | 0 | 1544 | 4504.5 | 201 | 0 | 158 | 143 | 0 | 6 | 84.5
21:00 | 3576 | 787 | 2455 | 0 | 1478 | 4541 | 201 | 0 | 150 | 140 | 0 | 8 | 90
21:30 | 3596.5 | 787 | 2462.5 | 0 | 1480 | 4551 | 201 | 0 | 158.5 | 142 | 0 | 10.5 | 144.32
22:00 | 3617 | 787 | 2470 | 0 | 1482 | 4561 | 201 | 0 | 167 | 144 | 0 | 13 | 198.64
22:30 | 3633.5 | 847.5 | 2466.5 | 0 | 1358 | 4548 | 201 | 0 | 160.5 | 143 | 0 | 17 | 272.175
23:00 | 3650 | 908 | 2463 | 0 | 1234 | 4535 | 201 | 0 | 154 | 142 | 0 | 21 | 345.71
23:30 | 3743 | 908.5 | 2339 | 0 | 1185 | 4523.5 | 201 | 0 | 154 | 141 | 0 | 23 | 350.485 |  | Max Temp. in Dhaka |  | 35.6°C
24:00 | 3836 | 909 | 2215 | 0 | 1136 | 4512 | 201 | 0 | 154 | 140 | 0 | 25 | 355.26
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 298.670 MKWHr Energy Not Served 5.939 MKWHr Energy Requirement 304.609 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-09-29
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 125 | 125 | 125 | 125 | 125 | 125 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 124 | 124 | 125 | 125 |  | 125 | 125 | 126 | 126 | 126 | 126 | 126 | 2894509
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1820000
3 | Chattogram TPP-1 | 109 | 107 | 107 | 105 | 104 | 102 | 107 | 105 | 105 | 110 | 107 | 100 | 100 | 100 | 100 | 100 | 102 | 95 |  | 99 | 100 | 100 | 103 | 100 | 103 | 104 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 | 0 | [8 empty] | 1 | 8 | 8 | 10 |  | 17 | 17 | 17 | 17 | 17 | 10 | 8 | 169003
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 3 | 6 | 6 | 8 | 13 | 6 | 4 | 2 | 4 | 2 | 1 | [9 empty] | 58995
6 | Sikalbaha 225MW CCPP (Gas) | 227 | 226 | 226 | 226 | 226 | 226 | 227 | 226 | 224 | 223 | 219 | 222 | 219 | 219 | 220 | 224 | 226 | 217 |  | 223 | 225 | 225 | 225 | 224 | 225 | 225 | 5342794
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 408307
12 | Hathazari 100 MW peaking PP | 48 | 48 | 48 | 48 | 40 | 40 | 40 | 40 | 0 | [8 empty] | 60 |  | 36 | 4 | 0 |  |  |  |  | 427016
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 673272
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 30 | 21 | 21 | 21 | 21 | 21 | 21 | 0 | [11 empty] | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 310320
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 195 | 157 | 155 | 100 | 101 | 101 | 78 | 80 | 74 | 78 | 102 | 190 | 122 | 124 | 189 | 82 | 98 | 95 |  | 96 | 96 | 96 | 38 | 38 | 37 | 95 | 2724000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 0 | [7 empty] | 42 |  | 15 | 0 |  |  |  |  | 0 | 225818
19 | Ashuganj 195 MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 150 | 150 | 150 | 150 | 150 | 140 | 145 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 130 | 130 | 130 |  | 170 | 166 | 170 | 130 | 130 | 130 | 170 | 3552469
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 612 | 612 | 612 | 612 | 622 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 635 | 487 | 375 |  | 393 | 501 | 546 | 553 | 555 | 555 | 550 | 14023635
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 136584
33 | Ashuganj 225 MW CCPP | 181 | 188 | 190 | 193 | 198 | 200 | 207 | 212 | 209 | 203 | 203 | 205 | 203 | 201 | 202 | 179 | 178 | 200 |  | 178 | 179 | 178 | 178 | 180 | 207 | 206 | 4675000
34 | Ashuganj 450 MW CCPP(South) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 275 | 275 | 275 | 295 |  | 280 | 280 | 280 | 270 | 270 | 270 | 270 | 6422000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 330 | 280 | 280 | 280 | 280 | 280 | 335 |  | 280 | 280 | 280 | 280 | 280 | 280 | 285 | 7226900
| Ashuganj 420 MW CCPP(East) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5815300
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 404 | 412 | 411 | 416 | 389 | 349 | 331 | 332 | 333 | 314 | 312 | 334 | 361 | 341 | 358 | 357 | 356 | 311 |  | 387 | 363 | 362 | 369 | 413 | 414 | 413 | 8843270
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 420 | 370 | 400 | 400 | 360 | 330 | 300 | 300 | 300 | 300 | 300 | 350 | 400 | 350 | 350 | 320 | 320 | 400 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 8843000
41 | Haripur 360 MW CCPP(HPL) | 326 | 331 | 331 | 332 | 302 | 257 | 242 | 242 | 246 | 246 | 285 | 308 | 330 | 300 | 305 | 305 | 305 | 260 |  | 330 | 330 | 330 | 338 | 336 | 337 | 338 | 7286000
42 | RPCL 210MW CCPP | 41 | 46 | 35 | 17 | 17 | 35 | 50 | 42 | 35 | 30 | 30 | 28 | 28 | 30 | 30 | 30 | 43 | 72 |  | 72 | 72 | 72 | 75 | 73 | 72 | 73 | 994560
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 7 | 23 | 22 | 51 | 43 | 47 | 42 | 39 | 29 | 22 | 3 | [9 empty] | 350340
44 | Fenchugonj CCPP Phase-1 | 42 | 41 | 41 | 41 | 41 | 41 | 41 | 42 | 42 | 42 | 41 | 42 | 40 | 40 | 37 | 37 | 40 | 40 |  | 40 | 40 | 40 | 43 | 43 | 43 | 43 | 973000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 28 | 28 | 28 | 28 | 28 | 28 | 29 |  | 29 | 30 | 30 | 30 | 30 | 30 | 30 | 687360
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86 MW PP (Shahjibazar) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 75 | 75 | 75 | 75 | 78 | 75 | 75 | 74 | 78 | 84 | 84 |  | 84 | 84 | 84 | 84 | 81 | 81 | 81 | 1821120
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 180 | 180 | 180 | 183 | 184 | 184 | 184 | 184 | 182 | 182 | 180 | 180 | 180 | 180 | 178 | 178 | 178 | 179 |  | 180 | 180 | 180 | 180 | 180 | 182 | 182 | 4678960
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 393000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 9 | 10 | 10 | 10 | 10 | 10 | 245160
54 | Hobiganj 11 MW PP Cofidence-E | 0 | 3 | 3 | 3 | 3 | 3 | 3 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | [5 empty] | 2 | 2 | 2 | 137504
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 47 | 47 | 47 | 47 | 47 | 41 | 44 | 44 | 48 | 49 | 49 | 50 | 50 | 33 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1146000
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 187968
57 | Bibiana-II 341 MW CCPP (Summit) | 295 | 270 | 280 | 275 | 280 | 265 | 255 | 255 | 270 | 260 | 300 | 290 | 280 | 280 | 300 | 270 | 275 | 270 |  | 280 | 295 | 290 | 270 | 290 | 290 | 300 | 6829000
| Bibiyana South 400 MW | 394 | 392 | 391 | 392 | 360 | 228 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 260 | 392 | 392 | 392 | 397 | 6991400
58 | Nababganj 55 MW PP (Southern power ) | 0 | [24 empty] | 0 | 7079
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 12 | 392400
60 | Barabkunda 22 MW PP (Regent) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 213552
61 | Narshingdi 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 19 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 435528
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 419148
63 | Impoprt (Tripura) | 152 | 152 | 148 | 146 | 142 | 126 | 110 | 108 | 110 | 110 | 108 | 116 | 122 | 124 | 134 | 130 | 138 | 140 |  | 140 | 142 | 146 | 140 | 144 | 142 | 140 | 3156480
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 41 | 40 | 32 | 31 | 25 | 25 | 25 | 25 | 27 | 40 | 40 |  | 40 | 40 | 42 | 42 | 42 | 42 | 42 | 985440
65 | Feni 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 0 |  |  |  |  | 11 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 324432
66 | Feni 11 MW PP (Doreen) | 0 | 10 | 10 | 10 | 10 | 10 | 0 |  |  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 187020
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 32 | 30 | 30 | 21 | 33 | 32 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 790000
68 | Cumilla 25 MW PP (Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 277000
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456000
70 | Summit Madhabdi | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | 18 | 18 | 18 | 18 | 12 | 19 | 18 | 394920
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 584500
72 | Rupganj 33 MW PP(Summit) | 30 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 22 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 30 | 29 | 29 | 709100
73 | Ghorashal 108 MW PP (Regent) | 42 | 42 | 42 | 42 | 42 | 32 | 17 | 17 | 14 | 12 | 12 | 30 | 50 | 62 | 62 | 42 | 22 | 61 |  | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 983772
| Feni Lanka Power | 105 | 105 | 105 | 105 | 105 | 87 | 17 | 17 | 0 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 27 |  | 52 | 52 | 52 | 52 | 52 | 17 | 17 | 1064760
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 28 | 28 | 28 | 28 | 29 | 29 | 29 | 29 | 73 |  | 76 | 76 | 77 | 77 | 77 | 43 | 28 | 754320
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 54 | 54 | 17 | 17 | 17 | 17 | 17 |  | 35 | 17 | 17 | 0 |  |  | 0 | 488160
77 | Siddhirganj 100 PP(Dutch Bangla) | 9 | 9 | 9 | 0 |  | 6 | 9 | 9 | 0 | [16 empty] | 0 | 46080
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 288000
79 | Kodda 150 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 48 | 48 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 76 | 147 |  | 64 | 48 | 47 | 47 | 64 | 82 | 82 | 934560
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 27 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 19 | 8 | 30 | 52 | 50 | 43 | 42 | 42 | 42 |  | 46 | 52 | 52 | 52 | 52 | 52 | 52 | 836482
| Gazipur 100 MW PP | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 798720
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 2 | 3 | 2 | 5 | 1 | 1 | 0 | 0 | [10 empty] | 18719
| Jodiac Power | [5 empty] | 2 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 373578
| Karnaphuli Power Ltd. | 55 | 45 | 52 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 52 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1328140
82 | Madanganj 102 PP(Summit) | 17 | 34 | 30 | 12 | 0 | 5 | 17 | 17 | 7 | 0 | [6 empty] | 2 | 17 |  | 17 | 4 | 4 | 0 |  |  | 0 | 153659
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 260 | 275 | 280 | 274 | 273 | 228 | 239 | 247 | 253 | 276 | 288 | 277 | 293 | 301 | 269 | 240 | 257 | 305 |  | 287 | 286 | 287 | 269 | 268 | 258 | 268 | 6565789
87 | Meghnaghat 100 MW(IEL) | 9 | 9 | 8 | 9 | 8 | 9 | 8 | 9 | 0 | [8 empty] | 5 |  | 8 | 0 |  |  |  |  | 0 | 85440
| Meghnaghat 104 MW PP (OPCL) | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | [8 empty] | 6 | 17 | 17 | 17 | 17 | 17 | 22 | 286080
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 419880
92 | Fenchuganj 44 MW (Energyprima) | 47 | 47 | 47 | 44 | 47 | 47 | 47 | 47 | 45 | 44 | 44 | 39 | 42 | 39 | 42 | 42 | 44 | 45 |  | 46 | 46 | 46 | 47 | 45 | 45 | 45 | 1069632
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 8 | 8 | 8 | 8 | 8 | 20 | 45 | 51 | 51 | 10 | 10 | 22 |  | 42 | 51 | 51 | 51 | 51 | 51 | 51 | 932624
94 | Gagnagar 102 MW PP (Digital Power) | 50 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 8 | 8 | 24 | 40 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 322992
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 10 | 24 | 26 | 26 | 26 | 39 | 40 | 40 |  | 40 | 40 | 40 | 1 | 6 | 6 | 0 | 396480
96 | Chattogram 108 MW PP (ECPV) | [20 empty] | 0 |  |  |  |  | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 20 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 0 | [7 empty] | 10 |  | 15 | 0 |  |  |  |  | 0 | 205090
100 | Manikganj 55 MW PP (Northern) |  |  |  | 0 | 35 | 35 | 35 | 17 | 0 | [16 empty] | 0 | 119314
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 112 | 112 | 80 | 80 | 112 | 80 | 80 | 112 | 112 | 112 | 112 | 80 | 80 | 112 |  | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 2433191
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 0 | [9 empty] | 12750
103 | Kamalaghat 54 MW PP(Banco Energy) | [9 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [7 empty] | 0 | 169200
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 68 | 68 | 69 | 67 | 67 | 67 | 67 | 68 | 67 | 77 | 96 | 105 | 105 | 106 | 106 | 68 | 67 | 67 |  | 126 | 126 | 126 | 136 | 136 | 77 | 67 | 2056800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 51 | 53 | 53 | 53 | 53 | 53 | 68 |  | 97 | 97 | 108 | 108 | 108 | 60 | 29 | 1107216
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 813120
116 | Chandpur 200 MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 425760
117 | Ashuganj 150 MW PP (Midland) | 13 | 30 | 0 |  |  | 1 | 8 | 10 | 10 | 8 | 0 | [5 empty] | 1 | 8 |  | 10 | 0 |  |  |  |  | 0 | 103709
118 | Bibiyana-III 400 MW CCPP | 379 | 379 | 371 | 378 | 379 | 378 | 378 | 378 | 378 | 380 | 380 | 380 | 380 | 376 | 380 | 378 | 378 | 378 |  | 376 | 377 | 380 | 376 | 379 | 376 | 377 | 9073000
| Jamalpur 115 MW PP (United) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 84 | 74 | 72 | 73 | 73 | 18 | 18 | 18 |  | 94 | 94 | 94 | 85 | 85 | 18 | 19 | 1041600
| Anwara 300 MW PP (United) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 73 | 77 | 77 | 80 | 79 | 87 | 86 | 87 | 120 |  | 175 | 175 | 175 | 135 | 135 | 135 | 143 | 2371091
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 12 | 12 | 12 | 12 | 12 | 12 | 62 | 53 | 55 |  | 55 | 56 | 56 | 57 | 57 | 58 | 58 | 807360
| Anlima Energy Ltd. | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 632291
| Bhairob 54.5 MW | 11 | 17 | 17 | 0 | 0 | 14 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 409680
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 4 | 9 | 14 | 16 | 19 | 19 | 13 | 14 | 10 | 3 | 2 | [9 empty] | 121416
| Chandpur 115(Doreen) | 54 | 53 | 54 | 54 | 53 | 54 | 54 | 53 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 53 | 54 |  | 53 | 54 | 54 | 54 | 53 | 53 | 54 | 1304640
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 432720
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | [16 empty] | 0 | 148872
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 0 | 0 | 0 | 11 | 5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 1 | 0 | 4 |  | 5 | 6 | 4 | 8 | 13 | 21 | 25 | 93600
| Matarbari 2*600 MW (CPGCL) | 270 | 270 | 270 | 270 | 270 | 244 | 262 | 267 | 268 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 271 | 268 | 6567272
120 | Eastern Zone Total | 7284 | 7177 | 7171 | 7058 | 6970 | 6606 | 6455 | 6425 | 6318 | 6339 | 6541 | 6921 | 7012 | 6863 | 6963 | 6606 | 6554 | 6990 |  | 7365 | 7368 | 7458 | 7354 | 7439 | 7211 | 7237 | 167844449
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 47 | 47 | 47 | 47 | 31 | 31 | 23 | 7 | 0 | [10 empty] | 16 | 16 | 16 | 0 |  |  | 0 | 336960
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 21 |  | 42 | 31 | 31 | 31 | 31 |  |  | 133440
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 0 | [6 empty] | 2 | 12 |  | 30 | 53 | 54 | 54 | 54 | 54 | 54 | 721440
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 1 | 1 | 4 | 4 | 17 | 29 | 10 | 36 | 21 | 12 | 7 | [9 empty] | 132480
131 | Rampal 1320 MW (BIFPCL) | 524 | 532 | 520 | 525 | 523 | 523 | 450 | 451 | 401 | 400 | 400 | 400 | 409 | 402 | 402 | 403 | 376 | 400 |  | 465 | 565 | 567 | 571 | 580 | 573 | 570 | 11345450
132 | United Payra Power Ltd. | 17 | 0 | [23 empty] | 0 | 34800
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 223 | 188 | 176 | 180 | 180 | 180 | 98 | 95 | 180 | 180 | 220 | 180 | 180 | 220 |  | 220 | 220 | 220 | 220 | 220 | 222 | 224 | 4738418
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 0 |  |  |  |  | 16 | 0 | [9 empty] | 16 | [7 empty] | 0 | 71808
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 307 | 307 | 307 | 281 | 230 | 191 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 190 | 199 | 256 | 307 | 307 | 307 | 307 | 5170900
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 130 | 134 | 136 | 130 | 136 | 80 | 80 | 80 | 80 | 80 | 132 | 132 | 132 | 100 | 100 | 80 | 80 | 130 |  | 76 | 130 | 138 | 138 | 138 | 136 | 136 | 2692000
140 | Bhola 33 MW PP (Venture) | 34 | 34 | 25 | 23 | 22 | 21 | 17 | 14 | 17 | 17 | 20 | 22 | 22 | 22 | 22 | 20 | 18 | 25 |  | 26 | 26 | 28 | 28 | 31 | 31 | 31 | 557944
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 16 | 16 | 16 | 0 | [21 empty] | 0 | 42000
143 | Gopalganj 100 MW Peaking PP | [26 empty] | 896
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 85 | 19 | 0 | [16 empty] | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 266832
146 | Bheramara HVDC | 901 | 901 | 903 | 901 | 901 | 902 | 902 | 901 | 902 | 902 | 902 | 902 | 901 | 902 | 901 | 901 | 907 | 906 |  | 910 | 787 | 787 | 787 | 787 | 908 | 909 | 21490909
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 1220 | 1220 | 1220 | 1160 | 1120 | 1040 | 980 | 980 | 980 | 970 | 970 | 1000 | 1090 | 1050 | 1050 | 1040 | 1000 | 950 |  | 1070 | 1100 | 1210 | 1220 | 1220 | 1220 | 1220 | 28041900
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 178 | 180 | 180 | 180 | 180 | 180 | 4378500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 2 | 3 | 3 | 4 | 3 | 3 | 2 | 3 | 2 | 0 | [9 empty] | 29760
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 186 | 184 | 184 | 184 | 187 | 140 | 140 | 140 | 140 | 140 | 140 | 170 | 189 | 150 | 145 | 130 | 130 | 140 |  | 170 | 170 | 170 | 140 | 140 | 140 | 175 | 4105327
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 173 | 190 | 160 | 160 | 160 | 140 | 140 | 140 | 140 | 140 | 140 | 148 | 191 | 150 | 145 | 130 | 130 | 130 |  | 153 | 160 | 160 | 130 | 130 | 130 | 173 | 3955127
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 370 | 370 | 370 | 340 | 280 | 260 | 260 | 260 | 230 | 270 | 350 | 414 | 300 | 350 | 300 | 300 | 414 |  | 350 | 350 | 350 | 414 | 414 | 414 | 143 | 8075091
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [15 empty] | 4 | 4 | [9 empty] | 6667
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 169182
165 | Amnura 50 MW PP(Sinha) | [20 empty] | 0 | [5 empty] | 0
166 | Katakhali 50 MW PP (Northern) | [25 empty] | 0 | 0
167 | Katakhali 50 MW Peaking PP | [25 empty] | 0 | 0
168 | Santahar 50 MW Peaking PP | 0 | [16 empty] | 12 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 172720
169 | Natore 52 MW PP (Rajlanka) | 16 | 16 | 0 | [22 empty] | 0 | 46483
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 40 | 40 | 16 | 0 |  |  |  | 68952
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 50 | 50 | 50 | 35 | 35 | 35 | 35 | 0 | [11 empty] | 33 | 35 | 35 | 35 | 35 | 35 | 35 | 562848
172 | Confidence Power Bogura Unit-1 113 MW | 50 | 50 | 35 | 0 |  | 35 | 35 | 0 | [11 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 456384
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 107 | 88 | 34 | 34 | 34 | 34 | 0 | [10 empty] | 55 |  | 108 | 113 | 113 | 113 | 113 | 113 | 113 | 1061011
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 3 | 4 | 6 | 7 | 7 | 7 | 6 | 4 | 3 | 2 | [9 empty] | 50011
178 | Energypac Power Venture Thakurgaon Ltd. | 75 | 55 | 36 | 36 | 36 | 36 | 0 | [10 empty] | 50 |  | 113 | 114 | 114 | 114 | 114 | 115 | 114 | 987456
| Intraco Solar 30 MW | [5 empty] | 0 | 6 | 15 | 24 | 32 | 37 | 37 | 34 | 32 | 16 | 8 | 3 | 0 | [8 empty] | 248158
| Adani Power Jharkhanda Ltd | 1415 | 1396 | 1321 | 1313 | 1314 | 1163 | 1111 | 1119 | 1061 | 1060 | 1060 | 1112 | 1110 | 1105 | 1110 | 1105 | 1009 | 1090 |  | 1237 | 1326 | 1409 | 1410 | 1419 | 1429 | 1417 | 29350909
178 | Teesta Solar Limited | [5 empty] | 1 | 29 | 80 | 137 | 168 | 198 | 186 | 182 | 131 | 150 | 43 | 24 | [9 empty] | 1323220