## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:August 2023
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2023-08-01 |  | 2023-07-01 |  | 2022-08-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 14889 | 2023-08-30 | 15164 | 2023-07-26 | 13985 | 2022-08-25 | 15648 | 2023-04-19
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
2 | Minimum Generation (MW) | 8071 | 2023-08-01 | 8071 | 2023-07-01 | 9620 | 2022-08-12 | 8071 | 2023-07-01
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | 6:00
3 | Maximum Evening Peak Generation (MW) | 14889 | 2023-08-30 | 14655 | 2023-06-08 | 13985 | 2022-08-25 | 15648 | 2023-04-19
|  |  | 21:00 |  | 20:00 |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 13382 | 2023-08-29 | 13419 | 2023-07-24 | 11848 | 2022-08-25 | 13415 | 2023-04-19
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 14889 | 2023-08-30 | 15700 | 2023-07-30 | 14745 | 2022-08-31 | 16096 | 2023-04-19
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 13968.6452 |  | 14160.6129 |  | 13078.4194 |  | - | -
7 | Average Generation (MW) at Day Peak | 12169.7097 |  | 12085.4516 |  | 10988.2258 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 936 | 2023-08-29 | 927 | 2023-07-02 | 922 | 2022-08-08 | 956 | 27/3/2019
|  |  | 4:30 |  | 21:00 |  | 3:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 170 | 2023-08-05 | 182 | 2023-07-13 | 182 | 2022-08-07 | 194 | 12/06/19
|  |  | 19:00 |  | 15:00 |  | 15:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 634 | 2023-08-19 | 1100 | 2023-07-19 | 1537 | 2022-08-06 | 4395 | 04/10/2022
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 14036 | 2023-08-19 | 14448 | 2023-07-19 | 12132 | 44779 | 13200 | 04/10/2022
|  | - | 21:00 |  | 21:00 | - | 0.875 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2023-08-28 | 0 | 2023-07-03 | 54 | 44788 | - | -
|  |  | 19:30 |  | 21:00 |  | 21:00 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 13253 | 2023-08-08 | 12454 | 2023-07-03 | 13051 | 2022-08-15 | - | -
|  |  | 19:30 |  | 21:00 |  | 21:00 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 1042 | 2023-08-17 | 1806 | 2023-07-20 | 1638 | 44785 | - | -
|  |  | 12:00 |  | 12:00 |  | 10:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 12309 | 2023-08-17 | 12359 | 2023-07-20 | 9923 | 44785 | - | -
|  |  | 12:00 |  | 12:00 |  | 10:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2023-08-08 | 0 | 2023-07-03 | 0 | 44788 | - | -
|  |  | 12:00 |  | 21:00 |  | 10:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 10921 | 2023-08-08 | 9951 | 2023-07-03 | 10622 | 44788 | - | -
|  |  | 12:00 |  | 21:00 |  | 10:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 26 |  | 24 |  | 31 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 22 |  | 24 |  | 30 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 2157.9023 |  | 1774.0473 |  | 1900.8429 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 186.3465 |  | 45.3987 |  | 135.2896 |  | - | -
22 | Net Generation of BPDB (MKWH) | 1971.5558 |  | 1728.6486 |  | 1765.5533 |  | - | -
23 | Net Generation of IPP (MKWH) | 4950.6608 |  | 5418.6942 |  | 5487.1901 |  | - | -
24 | Net Generation of REB (MKWH) | 132.336 |  | 119.8463 |  | 127.2082 |  | - | -
24 | Net Generation of Rental Power Plant (MKWH) | 273.6692 |  | 406.1896 |  | 411.3038 |  | - | -
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 7328.2218 |  | 7673.3787 |  | 7791.2554 |  | 7842.9924 | April'22
26 | Energy Generation by Gas (MKWH) | 4451.0325 |  | 4793.0721 |  | 4273.9758 |  | 493.07 | July-23
27 | Energy Generation by Diesel (MKWH) | 171.571 |  | 254.4028 |  | 623.3092 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1284.8303 |  | 1645.587 |  | 1993.2091 |  | 2365.7466 | April'22
29 | Energy Generation by Hydro (MKWH) | 128.7252 |  | 45.1338 |  | 95.7122 |  | 104.66 | Sep-22
30 | Energy Generation by Solar (MKWH) | 32.4167 |  | 45.4439 |  | 37.0888 |  | 40.67 | July-23
31 | Energy Generation by Coal (MKWH) | 1079.4416 |  | 935.1378 |  | 903.25 |  | 950.96 | Sep'22
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 758.441 |  | 773.3438 |  | 776.6715 |  | 776.67 | August-22
33 | Monthly Load Factor (%) | 81.9186 |  | 84.9553 |  | 92.6177 |  | 92.62 | August-22

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:August 2023
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 14889 | 2023-08-30 | 21:00
Generation Period
| Dhaka | MW | 5116.25
| Chattogram | MW | 1407.8
| Cumilla | MW | 1103
| Mymensingh | MW | 1163
| Sylhet | MW | 521
a) | Total supply in East zone | MW | 9311.05
| Khulna | MW | 1834.9
| Barisal | MW | 485.6
| Rajshahi | MW | 1544
| Rangpur | MW | 916
b) | Total supply in West zone | MW | 4780.5
c) | Total supply in both zone ( a+b) | MW | 14091.55
Ref: | 27.21.0000.603.16.087.20.706 | Date: 17/09/2023
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(East-West I/C)
Month:August 2023
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 550 | 2023-08-11 | 20:00
| b) Ishurdi end | MW | 278 | 2023-08-17 | 15:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 1000 | 2023-08-02 | 9:00
| b) Ishurdi end | MW | 8 | 2023-08-29 | 23:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 0.072429
| b) Ishurdi end | MKWH | 97.9716
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 95.0325
| b) Ishurdi end | MKWH | 0.070319
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 200 | 2023-08-01 | 0:00
| b)Serajganj end | MW | 650 | 2023-08-31 | 9:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 300 | 2023-08-24 | 14:00
| b)Sirajganj end | MW | -170 | 2023-08-01 | 5:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 0.0003
| b)Sirajganj end | MKWH | 305.198
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 301.4364
| b)Sirajganj end | MKWH | 0
30 | Transmission loss of EWI /NO-2 | % | 1.233'%
31 | Maximum power Export through EWI/ NO-3
a) | a) Gopalganj end | AMPS | 2172 | 17.08.2023 | 15:00
|  | MW | 1450
b) | b) Aminbazar end | AMPS | -
|  | MW | -
32 | Maximum power Import through EWI/ NO-3
a) | a) Gopalganj end | AMPS | -
|  | MW | -
b) | b) Aminbazar end | AMPS | 2206
|  | MW | 1436
33 | Daily Maximum Energy Export through EWI/NO-3
a) | a) Gopalganj end | MkWh | 28.991 | 17.08.2023 | N/A
b) | a) Aminbazar end | MkWh | - | -
34 | Daily Maximum Energy Import through EWI/ NO-3
a) | a) Gopalganj end | MkWh | - | - | N/A
b) | a) Aminbazar end | MkWh | 28.3207 | 17.08.2023
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
a) | a) Gopalganj end | MkWh | 685.3055
b) | b) Aminbazar end | MkWh | -
36 | Total Energy Import through EWI/ NO-3
a) | a) Gopalganj end | MkWh | -
b) | b) Aminbazar end | MkWh | 683.644
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10
| a) Gopalganj end | % | 0.24244
| b) Aminbazar end | % | 0
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
[9 empty] | QF-LDC-23 | 8
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: August 2023
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 HT | 2023-08-03 10:22 | 2023-08-03 11:40 | 1:18 | T | Unknown | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-08-03 17:17 | 2023-08-03 18:44 | 1:27 | E/O | Pbs Feeder red hot | 30 | 43.5 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-1 LT | 2023-08-01 23:32 | 2023-08-02 02:05 | 2:33 | T | SPS trip | 35 | 89.25 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-2 HT | 2023-08-19 23:25 | 2023-08-20 02:29 | 3:04 | E/O | 33 kv t2 extantion bud DS Redhot work | 40 | 122.6667 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-2 HT | 2023-08-24 14:53 | 2023-08-24 17:17 | 2:24 | E/O | 33kv T-2 Bus R-Phase Conductor Redhot Remove work. | 40 | 96 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-2 LT | 2023-08-01 23:32 | 2023-08-01 23:40 | 0:08 | T | SPS trip | 35 | 4.6667 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | Main bus | 2023-08-02 15:09 | 2023-08-02 16:53 | 1:44 | E/O | Main bus shutdown due to 132 kV Kadda ckt-1 main bus DS (B phase) bus side connector red hot maintenance . | 20 | 34.6667 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) LT | 2023-08-03 18:31 | 2023-08-03 18:39 | 0:08 | T | Over Current- 33kv Itna Fauit O/C, E/F | 30 | 4 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) LT | 2023-08-22 12:22 | 2023-08-22 14:35 | 2:13 | E/O | 33KV Hossenpur Feeder Bus Connector Loop Burn Out. Shut Down Taken by PBS | 14 | 31.0333 | No interruption
Satmasjid 132/33kV Grid Sub-Station | 132/33 KV Transformer-2 HT | 2023-08-28 10:40 | 2023-08-28 12:10 | 1:30 | E/O | TC PRV TRV Trip, K-86-2OPTD, TRAFO TROVBLE RELAY-K355. | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 01 HT | 2023-08-01 17:08 | 2023-08-01 17:16 | 0:08 | T | Tripped showing E/F realy | 40 | 5.3333 | Power interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 02 LT | 2023-08-01 17:08 | 2023-08-01 17:17 | 0:09 | T | Tripped showing E/F realy | 40 | 6 | Power interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 02 LT | 2023-08-12 14:07 | 2023-08-12 14:16 | 0:09 | T | Tripped showing E/F realy | 34 | 5.1 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-1 LT | 2023-08-07 17:24 | 2023-08-07 17:47 | 0:23 | T | Due to Korotia(pbs) Feeder fault | 45 | 17.25 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-1 LT | 2023-08-27 13:46 | 2023-08-27 14:07 | 0:21 | T | Due to 33kv OLD REB feeder C.T Blast. | 55 | 19.25 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 LT | 2023-08-07 17:24 | 2023-08-07 17:47 | 0:23 | T | Due to Korotia(pbs) Feeder fault | 45 | 17.25 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 LT | 2023-08-27 13:46 | 2023-08-27 14:08 | 0:22 | T | Due to 33kv OLD REB feeder C.T Blast. | 55 | 20.1667 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-3 LT | 2023-08-01 08:30 | 2023-08-01 10:23 | 1:53 | E/O | Red hot at 33kv Jamuna feeder(PBS) at 33kv T3 bus section. | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-4 LT | 2023-08-02 00:07 | 2023-08-02 00:52 | 0:45 | E/O | Red hot at 33kV bus side. | 14 | 10.5 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | T-03 HT | 2023-08-04 04:25 | 2023-08-04 06:04 | 1:39 | E/O | DS-823 Maintenance | 0 | 0 | No interruption
|  |  | Total : | 22:41 |  | Unserved Energy: |  | 526.6333
Dhaka (South) Grid Circle :
Bhulta 132/33kV Grid Sub-Station | 132kV BUS | 2023-08-29 06:49 | 2023-08-29 09:00 | 2:11 | E/O | None | 0 | 0 | No interruption
Bhulta 132/33kV Grid Sub-Station | GT1 HT | 2023-08-29 06:27 | 2023-08-29 09:06 | 2:39 | E/O | Due to red hot maintenance. GT 01 B Phase loop change. | 40 | 106 | Power interruption
Bhulta 132/33kV Grid Sub-Station | GT2 HT | 2023-08-25 19:45 | 2023-08-26 23:44 | 27:59 | E/O | Huge red hot of LT bushing Y phase GT-2 | 50 | 1399.1667 | Power interruption
Bhulta 132/33kV Grid Sub-Station | GT2 HT | 2023-08-29 14:04 | 2023-08-29 15:53 | 1:49 | E/O | Red hot maintenance | 40 | 72.6667 | Power interruption
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 HT | 2023-08-05 15:25 | 2023-08-05 18:17 | 2:52 | T | Prv 02 Trip. | 0 | 0 | No interruption
Lalbag 132/33kV Grid Sub-Station | Tr-Load HT | 2023-08-13 06:53 | 2023-08-13 16:56 | 10:03 | T | The transformer had oil leakage issue which made the GT2 run with lower oil level and caused a sudden trip. | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | T-3 HT | 2023-08-18 06:15 | 2023-08-18 08:43 | 2:28 | E/O | heating issues | 47 | 115.9333 | Power interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 HT | 2023-08-27 22:22 | 2023-08-27 23:23 | 1:01 | E/O | Due to Red hot | 20 | 20.3333 | Power interruption
Shitalakhya 132/33kV Grid Sub-Station | 132 kV Bus-1 | 2023-08-29 11:01 | 2023-08-29 12:42 | 1:41 | E/O | Red hot maintenance | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 HT | 2023-08-08 16:12 | 2023-08-08 17:36 | 1:24 | E/O | MIEZ 33 KV feeder Heat sink burned. | 25 | 35 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2023-08-07 04:10 | 2023-08-07 05:08 | 0:58 | T | 33Kv outgoing MIZ feeder trip (Feeder control by pbs) at that time 33kv Incomming tr-01 trip. | 20 | 19.3333 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2023-08-09 13:16 | 2023-08-09 15:04 | 1:48 | E/O | Maintenance work of PBS at Bus section-01 under the Transformer of Tr-01. | 35 | 63 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2023-08-24 21:10 | 2023-08-24 21:33 | 0:23 | T | PBS Sonargaon feeder trip | 0 | 0 | No interruption
|  |  | Total : | 57:16 |  | Unserved Energy: |  | 1831.4333
Chattogram Grid Circle :
Baroirhat 132/33kV Grid Sub-Station | TR-1, 406T LT | 2023-08-09 15:29 | 2023-08-09 17:33 | 2:04 | E/O | PBS taken this Shutdown for 33 kv bus red hot maintenance work. | 21 | 43.4 | Power interruption
Baroirhat 132/33kV Grid Sub-Station | TR-1, 406T LT | 2023-08-21 10:55 | 2023-08-21 12:02 | 1:07 | E/O | Redhot maintenance work | 15 | 16.75 | Power interruption
Chandraghona 132/33kV Grid Sub-Station | TR-01(406T) HT | 2023-08-13 10:09 | 2023-08-13 10:42 | 0:33 | E/O | 33 KV bus Work | 17 | 9.35 | Power interruption
Chandraghona 132/33kV Grid Sub-Station | TR-01(406T) LT | 2023-08-14 13:40 | 2023-08-14 13:53 | 0:13 | T | 33 kv Kodala & Hosnabad feeder Trip E/F, O/C. Transformer T1 Secondary Trip by E/F, O/C. | 16 | 3.4667 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-1 HT | 2023-08-01 16:28 | 2023-08-01 17:59 | 1:31 | E/O | Banshkhali 33KV PBS feeder taken T-01 33KV Bus shutdown for redhot maintenance at Banshkhali 33KV PBS bus DS. | 15 | 22.75 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-1 LT | 2023-08-03 08:34 | 2023-08-03 09:03 | 0:29 | T | due to PDB 33kv 16/20 MVA transformer fault.( 16/20 MVA transformer secondary and primary breaker did not trip) | 30 | 14.5 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-1 LT | 2023-08-03 14:17 | 2023-08-03 14:29 | 0:12 | T | Due to 16/20 MVA 33Kv transformer fault. | 28 | 5.6 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 HT | 2023-08-09 16:10 | 2023-08-09 16:40 | 0:30 | E/O | ***Actual Date(08/08/23) & Time(19;08). No internet at actual time.So with the concern of NLDC AE we posted in OIS in this way. SD taken for Flood Water Level Increased. | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 LT | 2023-08-03 14:17 | 2023-08-03 14:29 | 0:12 | E/O | For Safety reason due to Heavy Flashing and firing of 33 Kv 16/20MVA transformer. | 28 | 5.6 | Power interruption
Halishahar 132/33kV Grid Sub-Station | 403T(TR-1) LT | 2023-08-04 08:04 | 2023-08-04 08:39 | 0:35 | T | Due to 33 kv Baraka ckt-01 fault | 2.5 | 1.4583 | Power interruption
Halishahar 132/33kV Grid Sub-Station | 413T(TR-2) LT | 2023-08-04 08:04 | 2023-08-04 08:39 | 0:35 | T | Due to 33 kv Baraka ckt-01 fault | 2.5 | 1.4583 | Power interruption
Hathazari 230/132/33kV Grid Sub-Station | T-01 HT | 2023-08-06 08:50 | 2023-08-06 22:10 | 13:20 | T | Y-ph CT puncture. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | T-02 LT | 2023-08-06 13:21 | 2023-08-06 15:24 | 2:03 | T | cable punture Bph | 44 | 90.2 | Power interruption
Hathazari 230/132/33kV Grid Sub-Station | T-02 LT | 2023-08-06 22:24 | 2023-08-07 18:15 | 19:51 | E/O | 33 KV B-phase cable puncture. | 0 | 0 | No interruption
Kalurghat 132/33kV Grid Sub-Station | 33 KV BUS-1 | 2023-08-12 11:09 | 2023-08-12 13:13 | 2:04 | E/O | 33 KV B-phase cable puncture. | 0 | 0 | No interruption
Kalurghat 132/33kV Grid Sub-Station | 33 KV BUS-2 | 2023-08-12 13:25 | 2023-08-12 13:37 | 0:12 | E/O | 33 KV B-phase cable puncture. | 0 | 0 | No interruption
Khagrachori 132/33kV Grid Sub-Station | TR-2 HT | 2023-08-05 13:24 | 2023-08-05 18:29 | 5:05 | T | Main Tank PRD | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | 405T (T1) LT | 2023-08-09 03:54 | 2023-08-09 04:38 | 0:44 | T | 33kV BPDB (madarbari) feeder fault with 33kV Bus to Bus isolator's Y & B-phase Loop Broken. | 84 | 61.6 | Power interruption
Khulshi 132/33kV Grid Sub-Station | 415T (T2) LT | 2023-08-09 03:55 | 2023-08-09 09:54 | 5:59 | T | 33 kV BPDB (Madarbari) Feeder fault with 33 kV Bus to Bus isolator's Y & B-phase Loop Broken. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | TR-1(507T) HT | 2023-08-17 17:24 | 2023-08-17 18:49 | 1:25 | E/O | For hot spot and loose connection tightening at 132kv GIS Duck end. | 27 | 38.25 | Power interruption
Madunaghat 132/33kV Grid Sub-Station | TR-1(507T) LT | 2023-08-30 13:21 | 2023-08-30 13:55 | 0:34 | T | For Mohora-1 BPDB 33KV feeder E/F, O/C tripping | 38 | 21.5333 | Power interruption
Shahmirpur 132/33kV Grid Sub-Station | 416T LT | 2023-08-06 10:36 | 2023-08-06 11:41 | 1:05 | E/O | à¦…à¦•à§à¦¸à¦¿à¦²à¦¿à§Ÿà¦¾à¦°à¦¿ à¦Ÿà§à¦°à¦¾à¦¨à§à¦¸à¦«à¦°à¦®à¦¾à¦° à§©à§©/à§¦.à§ªà¦•à§‡à¦­à¦¿ à¦Ÿà¦¿-à§¦à§§ à¦¡à§à¦°à¦ª à¦†à¦‰à¦Ÿ à¦«à¦¿à¦‰à¦œ à¦ªà¦°à¦¿à¦¬à¦°à§à¦¤à¦¨ | 0 | 0 | No interruption
TK chemical 132kV Grid Sub-Station | 48/64MVA T-2(415T) HT | 2023-08-01 08:44 | 2023-08-01 09:20 | 0:36 | T | Trip,Diffential, y-Phase Diffential, R-Phase Diffential. | 24.5 | 14.7 | Power interruption
TK chemical 132kV Grid Sub-Station | 48/64MVA T-2(415T) LT | 2023-08-30 08:41 | 2023-08-30 09:46 | 1:05 | E/O | red hot | 0 | 0 | No interruption
|  |  | Total : | 62:04 |  | Unserved Energy: |  | 350.6167
Cumilla Grid Circle :
Beanibazar 132/33kV Grid Sub-Station | 132 KV Transformer TR-01 HT | 2023-08-14 20:49 | 2023-08-14 23:56 | 3:07 | T | Earthquake | 20 | 62.3333 | Power interruption
Beanibazar 132/33kV Grid Sub-Station | 132KV Transformer TR-02 LT | 2023-08-06 12:01 | 2023-08-06 15:49 | 3:48 | E/O | 33 kv Red Hot | 20 | 76 | Power interruption
Brahmanbaria 132/33kV Grid Sub-Station | 402T LT | 2023-08-05 15:38 | 2023-08-05 15:48 | 0:10 | T |  | 60 | 10 | Power interruption
Chhatak 132/33kV Grid Sub-Station | T-1 HT | 2023-08-25 19:17 | 2023-08-25 19:22 | 0:05 | T | sunamganj 33kv pdb feeder trail. | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | TR1 | 2023-08-13 07:10 | 2023-08-13 13:06 | 5:56 | E/O | 33 kV Maizdee feeder bus isolator red hot maintenance. | 30 | 178 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | TR1-415T HT | 2023-08-08 14:13 | 2023-08-09 00:20 | 10:07 | E/O | 33 Kv Bus D/S red-hot maintenance | 30 | 303.5 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | TR1-415T HT | 2023-08-13 17:04 | 2023-08-13 18:20 | 1:16 | E/O | Red hot Maintenance of 33 kv Incoming DS | 30 | 38 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | TR3 | 2023-08-07 15:12 | 2023-08-07 16:10 | 0:58 | E/O | T-3 Bus S/D for Chow-T-3 bus Isolator red hot maintenance by BPDB. | 30 | 29 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | TR3-435T LT | 2023-08-06 16:06 | 2023-08-06 16:12 | 0:06 | T | 33 KV Datterhat feeder O/C E/F Trip | 25 | 2.5 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-1 LT | 2023-08-04 06:55 | 2023-08-04 07:17 | 0:22 | T | 33 KV REB Bagmara Feeder Fault | 25 | 9.1667 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-1 LT | 2023-08-13 06:39 | 2023-08-13 07:02 | 0:23 | T | 33 KV Kasba feeder fault. | 25 | 9.5833 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-1 LT | 2023-08-31 04:07 | 2023-08-31 04:32 | 0:25 | T | 33KV Choddogram REB & kasba PDB Feeder Fault | 30 | 12.5 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-2 HT | 2023-08-14 07:45 | 2023-08-14 09:35 | 1:50 | E/O | Kasba 33KV PDB feeder Red hot | 20 | 36.6667 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-2 LT | 2023-08-04 06:55 | 2023-08-04 07:17 | 0:22 | T | Same | 25 | 9.1667 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-2 LT | 2023-08-13 06:39 | 2023-08-13 07:02 | 0:23 | T | 33 KV kasba feeder fault. | 25 | 9.5833 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-2 LT | 2023-08-31 04:07 | 2023-08-31 04:32 | 0:25 | T | Same | 30 | 12.5 | Power interruption
Feni 132/33kV Grid Sub-Station | T-2(415T) HT | 2023-08-12 09:25 | 2023-08-12 11:28 | 2:03 | E/O | Red hot maintenance work | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 LT | 2023-08-01 12:00 | 2023-08-01 12:04 | 0:04 | E/O | Emergency loadshed Instructed by NLDC for Mainten Grid Voltage. | 32 | 2.1333 | Power interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 LT | 2023-08-04 15:59 | 2023-08-04 16:02 | 0:03 | T | due to PBS 33kv Chunarughat feeder trip showing E/F | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-2 HT | 2023-08-01 15:40 | 2023-08-01 15:44 | 0:04 | T | heavy rain and thundering | 35 | 2.3333 | Power interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-2 HT | 2023-08-30 15:20 | 2023-08-30 15:25 | 0:05 | T | Lightning Arrester counter meter (Red phase) blast. | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-2 HT | 2023-08-30 15:26 | 2023-08-30 18:10 | 2:44 | E/O | 132kV Lightning Arrester Work( Red phase) | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T1 HT | 2023-08-09 19:41 | 2023-08-09 21:28 | 1:47 | T |  | 45 | 80.25 | Power interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-08-09 19:41 | 2023-08-09 20:08 | 0:27 | T |  | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-08-09 20:15 | 2023-08-09 20:38 | 0:23 | T |  | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-08-29 09:36 | 2023-08-29 09:48 | 0:12 | T |  | 35 | 7 | Power interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-08-31 19:08 | 2023-08-31 21:38 | 2:30 | T | Over load | 0 | 0 | No interruption
|  |  | Total : | 40:05 |  | Unserved Energy: |  | 890.2167
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Transformer-1 (403T) LT | 2023-08-02 17:32 | 2023-08-02 17:43 | 0:11 | T | 33Kv Rampal feeder O/C inst. (A+B+C) time. | 17 | 3.1167 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-2 (413 T) LT | 2023-08-02 17:32 | 2023-08-02 17:45 | 0:13 | T | 33Kv Rampal feeder O/C inst. (A+B+C) time. | 17 | 3.6833 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-1 (405T) HT | 2023-08-09 00:07 | 2023-08-09 03:38 | 3:31 | T | Jalokhati 33 kv feeder fault. | 52 | 182.8667 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 2023-08-03 03:28 | 2023-08-03 04:10 | 0:42 | T | 33 kV PBS Nolcity feeder trip due to EF. | 50 | 35 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 2023-08-07 15:46 | 2023-08-07 15:52 | 0:06 | T | For dopdopia 2 feeder trial, | 45 | 4.5 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 2023-08-10 09:44 | 2023-08-10 14:19 | 4:35 | E/O | To improve grounding system of T1 transformer | 17 | 77.9167 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) HT | 2023-08-03 03:28 | 2023-08-03 04:10 | 0:42 | T | 33 kV PBS nolcity feeder trip due to EF. | 30 | 21 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) HT | 2023-08-07 15:35 | 2023-08-07 16:04 | 0:29 | T | For 33kv feeder Dopdopia 1, 2 trip o/c, e/f. | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) HT | 2023-08-09 00:07 | 2023-08-09 00:14 | 0:07 | T | 33kv jalokati fedder fault | 32 | 3.7333 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2023-08-03 16:47 | 2023-08-03 17:19 | 0:32 | E/O | Self protection test | 0 | 0 | No interruption
Benapole 132/33kV Grid Sub-Station | Transformer-2(416T) LT | 2023-08-14 23:25 | 2023-08-15 01:14 | 1:49 | E/O | T2 shutdown due to jikorgacha feeder redhot maintenance | 20 | 36.3333 | No interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-08-10 13:55 | 2023-08-10 16:52 | 2:57 | T | PRD Trip | 0 | 0 | No interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-08-10 15:31 | 2023-08-10 16:51 | 1:20 | E/O | PRD SIGNAL IMBALANCE | 0 | 0 | No interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-08-14 09:16 | 2023-08-14 10:26 | 1:10 | E/O | T2 33 KV BUS DS Y Phase High Temperature Maintenance. | 13 | 15.1667 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-08-26 06:30 | 2023-08-26 08:04 | 1:34 | E/O | Red hot maintenance | 12 | 18.8 | Power interruption
Faridpur 132/33kV Grid Sub-Station | 33 KV Bus | 2023-08-26 11:08 | 2023-08-26 11:35 | 0:27 | E/O | 33 kv harukandi feeder DS maintenance work | 22 | 9.9 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-08-26 08:32 | 2023-08-26 09:53 | 1:21 | E/O | Bus Section-02 Isolator Jumper Maintenance (R-phase) | 38 | 51.3 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-08-26 11:03 | 2023-08-26 11:36 | 0:33 | E/O | 33 kv harukandi feeder DS maintenance work | 22 | 12.1 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-08-04 04:40 | 2023-08-04 05:14 | 0:34 | T | 33kV Bus PT Blast (Y-phase) | 60 | 34 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-08-24 22:55 | 2023-08-24 23:13 | 0:18 | T | 33kV Feeder Kanaipur-01 & REB-01 fault | 71 | 21.3 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-08-25 00:54 | 2023-08-25 01:01 | 0:07 | T | Unknown | 60 | 7 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-08-04 04:40 | 2023-08-04 05:14 | 0:34 | T | 33kV Bus PT Blast (Y-phase) | 60 | 34 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-08-24 22:55 | 2023-08-24 23:14 | 0:19 | T | 33kV Feeder Kanaipur-01 & REB-01 Fault | 71 | 22.4833 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-08-25 00:54 | 2023-08-25 01:01 | 0:07 | T | Unknown | 60 | 7 | Power interruption
Gollamari 132/33kV Grid Sub-Station | 132kV Bus Coupler | 2023-08-22 14:44 | 2023-08-22 14:46 | 0:02 | E/O | Remote Test, SPMD Khulna. | 0 | 0 | No interruption
Gollamari 132/33kV Grid Sub-Station | Tr-1 LT | 2023-08-22 19:06 | 2023-08-22 19:30 | 0:24 | T | Due to 33Kv Feeder Fault | 33 | 13.2 | Power interruption
Gollamari 132/33kV Grid Sub-Station | Tr-2 LT | 2023-08-22 19:06 | 2023-08-22 19:30 | 0:24 | T | Due to 33KV Feeder Fault | 11 | 4.4 | Power interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T LT | 2023-08-31 06:18 | 2023-08-31 08:15 | 1:57 | E/O | Red hot maintenance.132 kv side R - phase CB. | 0 | 0 | No interruption
Mongla 132/33kV Grid Sub-Station | T-1 HT | 2023-08-10 08:34 | 2023-08-10 09:24 | 0:50 | T | 33 kv old port feeder loop disconnect | 12 | 10 | Power interruption
Mongla 132/33kV Grid Sub-Station | T-2 LT | 2023-08-10 10:19 | 2023-08-10 12:58 | 2:39 | E/O | 33 kv old port feeder loop reconnection | 12 | 31.8 | Power interruption
Rampal 400/230kV Grid Sub-Station | ICT-1 HT | 2023-08-31 13:16 | 2023-08-31 16:04 | 2:48 | T | Differential protection relay Y-PH Operated. | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) LT | 2023-08-03 00:52 | 2023-08-03 02:35 | 1:43 | E/O | Emergency maint. Work | 60 | 103 | Power interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) LT | 2023-08-23 23:45 | 2023-08-24 00:01 | 0:16 | T | Due to 33 KV kajirhat feeder CT blast | 58 | 15.4667 | Power interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-2 (T-2) LT | 2023-08-23 23:45 | 2023-08-24 00:01 | 0:16 | T | Due to 33 KV kajirhat feeder CT blast | 42 | 11.2 | No interruption
|  |  | Total : | 35:37 |  | Unserved Energy: |  | 790.2667
HVDC Grid Circle :
Baghabari 230/132kV Grid Sub-Station | T-2 Bank HT | 2023-08-09 00:53 | 2023-08-09 02:13 | 1:20 | T |  | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Transformer T-2 HT | 2023-08-08 00:40 | 2023-08-08 00:55 | 0:15 | T | 33kv magura ckt fault(wzpdcl) | 48 | 12 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T-1 HT | 2023-08-06 06:31 | 2023-08-06 07:28 | 0:57 | E/O | Red hot maintenance | 30 | 28.5 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T-1 LT | 2023-08-03 14:22 | 2023-08-03 17:24 | 3:02 | E/O | Emergency maint. Work | 50 | 151.6667 | Power interruption
Shahjadpur 132/33kV Grid Sub-Station | T-2(415T) LT | 2023-08-16 09:50 | 2023-08-16 11:17 | 1:27 | E/O | LT side B-phase redhot and 33 kv à¦¬à¦¾à¦¸à¦¬à¦¾à¦°à§‡à¦° à¦°à§‡à¦¡ à¦¹à¦Ÿ à¦ªà¦²à§à¦²à§€ à¦¬à¦¿à¦¦à§à¦¯à§à§Ž à¦¬à¦¾à¦¸à¦¬à¦¾à¦°à§‡ à¦•à¦¾à¦œ à¦•à¦°à¦¬à§‡ à¥¤ | 12 | 17.4 | Power interruption
Shahjadpur 132/33kV Grid Sub-Station | T-3(425T) HT | 2023-08-17 07:30 | 2023-08-17 07:50 | 0:20 | E/O | T-3 50/75 MVA X-former LT side R-phase redhot maintenance. | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | T-3(425T) LT | 2023-08-01 09:53 | 2023-08-01 10:45 | 0:52 | E/O | 132 kV T-3 X-Former LT Busing (R-Phase) red-hot maintenance. | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | T-4(435T) HT | 2023-08-10 10:35 | 2023-08-10 11:22 | 0:47 | E/O | 33 kV incoming D/S Y phase red hot | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | T-4(435T) HT | 2023-08-19 11:29 | 2023-08-19 13:37 | 2:08 | E/O | Red-hot maintanace 33 kv R phase DS for T-4 Transformer. | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | T-4(435T) LT | 2023-08-01 15:58 | 2023-08-01 17:50 | 1:52 | E/O | Emergency maint. Work | 0 | 0 | No interruption
|  |  | Total : | 13:00 |  | Unserved Energy: |  | 209.5667
Bogura Grid Circle:
Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-1 (404T) LT | 2023-08-02 11:05 | 2023-08-02 11:49 | 0:44 | T | 33 kV feeder fault. | 66 | 48.4 | Power interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-2 (414T) LT | 2023-08-02 11:05 | 2023-08-02 11:48 | 0:43 | T | 33 kV feeder fault. | 66 | 47.3 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-08-09 07:27 | 2023-08-09 12:39 | 5:12 | E/O | 33kv CB red hot | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-08-27 07:15 | 2023-08-27 09:40 | 2:25 | E/O | Red hot maintenance. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-4 HT | 2023-08-28 20:25 | 2023-08-28 20:35 | 0:10 | E/O | Bus shift. | 34 | 5.6667 | Power interruption
Bogura 230/132kV Grid Sub-Station | 132KV Main 1 | 2023-08-24 14:18 | 2023-08-24 16:18 | 2:00 | E/O | ISOLATOR MAINTENANCE | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 2 | 2023-08-30 06:02 | 2023-08-30 07:20 | 1:18 | E/O | Red Hot Maintenance . | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-02 HT | 2023-08-19 20:33 | 2023-08-19 22:16 | 1:43 | E/O | red Hot Maintenance | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | 33 KV BUS | 2023-08-27 16:44 | 2023-08-27 18:55 | 2:11 | E/O | Bus Section-01. Red hot on the T-1 33kv Bus isolator. | 16 | 34.9333 | Power interruption
Jaldhaka 132/33kV Grid Sub-Station | 406T LT | 2023-08-27 00:40 | 2023-08-27 01:05 | 0:25 | T | 33kv NESCO Jaldhaka Feeder fault | 28 | 11.6667 | Power interruption
Jaldhaka 132/33kV Grid Sub-Station | 406T LT | 2023-08-27 16:37 | 2023-08-27 18:57 | 2:20 | E/O | Red hot on the T-1 33kv Bus isolator. | 16 | 37.3333 | Power interruption
Jaldhaka 132/33kV Grid Sub-Station | 416T LT | 2023-08-27 00:40 | 2023-08-27 01:05 | 0:25 | T | 33kv NESCO Jaldhaka Feeder fault | 28 | 11.6667 | Power interruption
Joypurhat 132/33kV Grid Sub-Station | Transformer T-4 (437 T) HT | 2023-08-11 13:42 | 2023-08-11 14:14 | 0:32 | T | 432B CB trip | 0 | 0 | No interruption
Kurigram 132/33kV Grid Sub-Station | Transformer T-2 (Tr-413T) HT | 2023-08-10 11:39 | 2023-08-10 13:04 | 1:25 | E/O | Tr-02 LV temperature high. | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-1 HT | 2023-08-20 08:38 | 2023-08-20 09:17 | 0:39 | T | Trip | 22.5 | 14.625 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2023-08-06 00:22 | 2023-08-06 01:42 | 1:20 | E/O | T-1 132 kv CT (R-Phase) Red Hot Maintanance. | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2023-08-12 15:50 | 2023-08-12 16:10 | 0:20 | T | Trip | 47 | 15.6667 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2023-08-14 19:55 | 2023-08-14 21:10 | 1:15 | E/O | Red hot maintenance. | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2023-08-16 10:45 | 2023-08-16 15:30 | 4:45 | T | Heavy flashing when closing to capacitor bank-6 33 kv bus isolator. | 50 | 237.5 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2023-08-20 15:26 | 2023-08-20 17:18 | 1:52 | E/O | Mohadebpur 33kv pbs feeder bus DS maintanance | 30 | 56 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2023-08-21 10:36 | 2023-08-21 12:51 | 2:15 | E/O | T1&T2 33KV BUS COUPLER RED HOT MAINTENANCE | 30 | 67.5 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-2 LT | 2023-08-09 20:11 | 2023-08-09 20:48 | 0:37 | E/O | Red hot maintenance | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-2 LT | 2023-08-12 15:50 | 2023-08-12 16:05 | 0:15 | T | Trip | 47 | 11.75 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-2 LT | 2023-08-16 10:45 | 2023-08-16 11:05 | 0:20 | T | Heavy flashing when closing to capacitor bank-6 33 kv bus isolator. | 50 | 16.6667 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-2 LT | 2023-08-20 08:38 | 2023-08-20 09:13 | 0:35 | T | Trip | 22.5 | 13.125 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-2 LT | 2023-08-21 10:36 | 2023-08-21 12:50 | 2:14 | E/O | T1&T2 33KV BUS COUPLER RED HOT MAINTENANCE | 30 | 67 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-3 LT | 2023-08-01 17:30 | 2023-08-01 20:20 | 2:50 | E/O | Emergency red hot maintenance. | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-3 LT | 2023-08-06 21:21 | 2023-08-06 21:57 | 0:36 | T | Rain fall and lightning. | 58 | 34.8 | Power interruption
Niamatpur 132/33kV Grid Sub-Station | 407T HT | 2023-08-21 07:44 | 2023-08-21 09:12 | 1:28 | E/O | Capacitor bank-1,Red hot maintenance work. | 18 | 26.4 | Power interruption
Panchagarh 132/33kV Grid Sub-Station | 407T LT | 2023-08-28 11:20 | 2023-08-28 11:55 | 0:35 | E/O | Due to emergency maintenance in NESCO 33kV feeder bus DS. | 16 | 9.3333 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | T-1 Transformer (403T) HT | 2023-08-17 15:20 | 2023-08-17 16:04 | 0:44 | T | Tripped showing No Operated relays. | 40 | 29.3333 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | T-3 Transformer (423T) HT | 2023-08-17 15:20 | 2023-08-17 15:55 | 0:35 | T | Tripped showing ALSOM MCGG relays. | 20 | 11.6667 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-2(415T) LT | 2023-08-26 12:33 | 2023-08-26 14:35 | 2:02 | E/O | Same Cause | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) HT | 2023-08-22 07:02 | 2023-08-22 10:04 | 3:02 | E/O | JE. Mr. Sujon, NPBS-1 requested for T-3 33KV bus shutdown. | 30 | 91 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) LT | 2023-08-20 14:55 | 2023-08-20 15:10 | 0:15 | T | Taherpur 33KV Natore PBS-1 Feeder Fault. (O/C, E/F) | 55 | 13.75 | Power interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132/33 kV T-02 (416T) HT | 2023-08-13 05:06 | 2023-08-13 09:47 | 4:41 | T | PRD Main trip,HV 50N/50N trip | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | T1-(415) HT | 2023-08-12 17:52 | 2023-08-12 18:46 | 0:54 | E/O | Emergency red hot maintenance of 33 CT (T-1) | 20 | 18 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T1-(415) LT | 2023-08-21 16:27 | 2023-08-21 17:43 | 1:16 | E/O | Emergency Red Hot Maintenance | 28 | 35.4667 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T1-(415) LT | 2023-08-31 08:05 | 2023-08-31 09:48 | 1:43 | E/O | Red Hot has become visible at 33kV T1+T2 connecting BUS Cupler DS.(This S/D has been taken By AGM com -PBS-2 and they will work on it) | 40 | 68.6667 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T2-(425) LT | 2023-08-16 22:33 | 2023-08-17 00:02 | 1:29 | E/O | Emergency Red Hot Maintenance | 15 | 22.25 | Power interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) LT | 2023-08-10 23:38 | 2023-08-11 00:19 | 0:41 | T | Neckmorad 33 kV(PBS) Feeder Fault | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) LT | 2023-08-13 06:44 | 2023-08-13 06:57 | 0:13 | T | Neckmorad 33 kV(PBS) Feeder Fault | 25 | 5.4167 | Power interruption
Thakurgaon 132/33kV Grid Sub-Station | T-2(412T) HT | 2023-08-10 23:38 | 2023-08-11 00:18 | 0:40 | T | Neckmorad 33 kV(PBS) Feeder Fault | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-2(412T) LT | 2023-08-13 06:44 | 2023-08-13 06:57 | 0:13 | T | Neckmorad 33 kV(PBS) Feeder Fault | 25 | 5.4167 | Power interruption
Thakurgaon 132/33kV Grid Sub-Station | T-3(432T) HT | 2023-08-10 23:38 | 2023-08-11 00:20 | 0:42 | T | Neckmorad 33 kV(PBS) Feeder Fault | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-3(432T) HT | 2023-08-13 06:44 | 2023-08-13 06:55 | 0:11 | T | Neckmorad 33 kV(PBS) Feeder Fault | 7 | 1.2833 | Power interruption
|  |  | Total : | 62:50 |  | Unserved Energy: |  | 1069.5833
Others :
Ashuganj 230/132/33kV Sub-Station | 230kV Busbar-1 | 2023-08-22 20:52 | 2023-08-22 21:11 | 0:19 | E/O | AIS (89-A) Bus isolator loop conductor cutting | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 HT | 2023-08-16 23:33 | 2023-08-16 23:40 | 0:07 | T |  | 0 | 0 | No interruption
|  |  | Total : | 0:26 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 329:36 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance | [9 empty] | 498.6333
Month: August 2023 | [9 empty] | 75.4667
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks | 574.1
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV Grid Sub-Station | Kallyanpur-01 | 2023-08-02 10:08 | 2023-08-02 10:25 | 0:17 | T | Distance Relay operate | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-1 | 2023-08-01 12:06 | 2023-08-01 12:34 | 0:28 | T | Tripped showing Distance-C phase relays. | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Sreepur- Bhaluka 132 kV Ckt- 01 | 2023-08-16 23:30 | 2023-08-17 00:14 | 0:44 | T | Over current | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Sreepur- Bhaluka 132 kV Ckt- 02 | 2023-08-16 23:30 | 2023-08-17 00:14 | 0:44 | T | Over Current | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Ghorashal ckt-1 | 2023-08-05 13:28 | 2023-08-05 16:11 | 2:43 | E/O | LA B-Phase Red hot maintenance | 57 | 154.85 | Power interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Lalbag Ckt-01 | 2023-08-02 10:08 | 2023-08-02 15:43 | 5:35 | T | Distance Relay operate | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Lalbag Ckt-02 | 2023-08-02 13:38 | 2023-08-02 15:43 | 2:05 | E/O | opgw maintenance | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-1 | 2023-08-05 13:21 | 2023-08-05 13:34 | 0:13 | T | Lightning | 0 | 0 | No interruption
New Tongi 132/33kV Grid Sub-Station | New Tongi L-2 | 2023-08-15 21:31 | 2023-08-16 11:00 | 13:29 | E/O | Tr-2 Incomer 33kv to 33kv BUS cable fault | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Sirajganj Ckt-1 | 2023-08-14 15:05 | 2023-08-14 15:40 | 0:35 | T | Distance Relay operate | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | RPCL-1 | 2023-08-02 10:40 | 2023-08-02 10:55 | 0:15 | T | Distance Trip.(RPCL End) | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-1 | 2023-08-19 10:45 | 2023-08-19 11:40 | 0:55 | E/O | For Kabirpur end Side Works | 0 | 0 | No interruption
|  |  | Total : | 28:03 |  | Unserved Energy: |  | 154.85
Dhaka (South) Grid Circle :
Bhulta 132/33kV Grid Sub-Station | Narsingdi | 2023-08-29 06:28 | 2023-08-29 09:04 | 2:36 | E/O | None | 0 | 0 | No interruption |  | 120.3333 | 251.2167
Gulshan 132/33kV Grid Sub-Station | Rampura-1 & 2 | 2023-08-10 05:14 | 2023-08-10 05:56 | 0:42 | T | 1. Distance protection 21/1 : Z1,BN.2 | 52 | 36.4 | Power interruption |  | 14.7833
Haripur 230/132kV Grid Sub-Station | Narsingdi | 2023-08-30 11:12 | 2023-08-30 11:24 | 0:12 | T | Trip | 80 | 16 | Power interruption
Haripur 230/132kV Grid Sub-Station | Narsingdi | 2023-08-31 15:44 | 2023-08-31 15:56 | 0:12 | T |  | 58 | 11.6 | Power interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2023-08-01 12:48 | 2023-08-01 13:16 | 0:28 | T | Storm. | 55 | 25.6667 | Power interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2023-08-02 01:55 | 2023-08-02 02:10 | 0:15 | T | Unknown | 21 | 5.25 | Power interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2023-08-28 11:27 | 2023-08-28 16:40 | 5:13 | E/O | Load Management by NLDC | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | Shitallakhya | 2023-08-31 22:58 | 2023-08-31 23:16 | 0:18 | T | Unknown | 20 | 6 | Power interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Shitalakhya 132 kv Ckt | 2023-08-31 14:38 | 2023-09-01 22:16 | 31:38 | E/O | Emergency maint.work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2023-08-31 14:39 | 2023-09-16 06:21 | 375:42 | E/O | Emergency maint.work | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Kazla Ckt -1 | 2023-08-09 04:17 | 2023-08-09 15:45 | 11:28 | T | Line fault | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | 230kV Siddhirganj-Maniknagar ckt-1 | 2023-08-02 16:26 | 2023-08-02 18:53 | 2:27 | T | ERS Tower broken. | 320 | 784 | Power interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2023-08-01 12:59 | 2023-08-01 13:13 | 0:14 | T | Trip due to Thunderstorm | 30 | 7 | Power interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2023-08-27 17:36 | 2023-08-27 17:47 | 0:11 | T | Tee zone-2 prot. trip(87TEE-2) | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-02 | 2023-08-01 12:59 | 2023-08-01 13:11 | 0:12 | T | Trip due to Thunderstorm | 30 | 6 | Power interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-02 | 2023-08-27 17:36 | 2023-08-27 19:26 | 1:50 | T | Distance trip (21.Z1) | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Bhulta Ckt-04 | 2023-08-28 23:55 | 2023-08-29 09:29 | 9:34 | E/O | Bhulta 230kV circuit-4 due to temperature rise(red hot) at Line DS 111S | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Gulshan Ckt-01 | 2023-08-10 05:14 | 2023-08-10 05:56 | 0:42 | T | Distance trip | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Gulshan Ckt-02 | 2023-08-10 05:14 | 2023-08-10 05:14 | 0:00 | T | Distance trip | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Gulshan Ckt-02 | 2023-08-10 07:45 | 2023-08-11 14:09 | 30:24 | E/O | Shutdown given for Line resistance test(megger), due to circuit trip at 05:14 | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Gulshan Ckt-02 | 2023-08-24 17:40 | 2023-09-07 00:26 | 318:46 | T | Tripped showing Distance Trip- Z1 (Y-Phase). 2). INST. | 0 | 0 | No interruption
Shitalakhya 132/33kV Grid Sub-Station | 132 kV Digital Powerplant | 2023-08-23 18:55 | 2023-08-23 19:59 | 1:04 | T | Due to MI Cement PT Blast | 90 | 96 | Power interruption
Shitalakhya 132/33kV Grid Sub-Station | 132 kV Hasnabad | 2023-08-01 17:09 | 2023-08-01 17:25 | 0:16 | T | General Trip | 0 | 0 | No interruption
Shitalakhya 132/33kV Grid Sub-Station | 132 kV Hasnabad | 2023-08-23 18:55 | 2023-08-23 19:43 | 0:48 | T | Due to MI Cement PT Blast | 90 | 72 | Power interruption
Shitalakhya 132/33kV Grid Sub-Station | 132 kV Hasnabad | 2023-08-31 22:58 | 2023-08-31 23:16 | 0:18 | T | tripped showing Master trip relay. | 95 | 28.5 | Power interruption
Shitalakhya 132/33kV Grid Sub-Station | 132 kV MI Cement | 2023-08-23 18:55 | 2023-08-24 23:51 | 28:56 | T | Due to MI Cement PT Blast | 90 | 2604 | Power interruption
Shitalakhya 132/33kV Grid Sub-Station | 132 kV Madanganj | 2023-08-23 18:55 | 2023-08-23 19:29 | 0:34 | T | Due to MI Cement PT Blast | 90 | 51 | Power interruption
Siddhirganj 132/33kV Grid Sub-Station | 100MW Dutch Bangla | 2023-08-24 13:19 | 2023-08-24 14:39 | 1:20 | T | E/F, O/C GE, Trip | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2023-08-24 13:19 | 2023-08-24 13:44 | 0:25 | T | LBB INITIATION,86 | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2023-08-30 15:41 | 2023-08-30 16:02 | 0:21 | E/O | A small pice telephone conductor hanging on Line conductor(B-phase)at EGCB plant end. | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT2 | 2023-08-10 09:55 | 2023-08-10 11:57 | 2:02 | E/O | Oil leakage checking | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT2 | 2023-08-11 09:45 | 2023-08-11 12:22 | 2:37 | E/O | Transformer Checking by EGCB. | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 132kV MTR 2 | 2023-08-08 09:55 | 2023-08-08 11:32 | 1:37 | E/O | Oli Filing | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Haripur 1 | 2023-08-28 09:42 | 2023-08-28 16:38 | 6:56 | E/O | Overload | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Haripur 2 | 2023-08-28 09:42 | 2023-08-28 16:39 | 6:57 | E/O | Overload | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | 335MW EGCB 1 | 2023-08-17 13:13 | 2023-08-17 14:25 | 1:12 | T | Tripped showing Distance relay | 210 | 252 | Power interruption
Siddhirganj 230/132kV Grid Sub-Station | Maniknagar 1 | 2023-08-02 16:26 | 2023-08-02 16:29 | 0:03 | T | Line Fault | 330 | 16.5 | Power interruption
Siddhirganj 230/132kV Grid Sub-Station | Maniknagar 2 | 2023-08-12 22:10 | 2023-08-13 01:57 | 3:47 | T | trip | 225 | 851.25 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Bus-Coupler | 2023-08-07 04:24 | 2023-08-07 04:33 | 0:09 | T | general trip | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | OPML(IEL-1) | 2023-08-07 04:24 | 2023-08-07 04:32 | 0:08 | T |  | 0 | 0 | No interruption
|  |  | Total : | 852:34 |  | Unserved Energy: |  | 4869.1667
Chattogram Grid Circle :
Chandraghona 132/33kV Grid Sub-Station | Chandraghona-Kaptai Ckt-02 | 2023-08-06 10:30 | 2023-08-06 10:30 | 0:00 | T | General trip with zcom distance 5.84 ckt km | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona-Kaptai Ckt-02 | 2023-08-06 12:32 | 2023-08-06 16:38 | 4:06 | E/O | Fault | 0 | 0 | No interruption
Coxsbazar 132/33kV Grid Sub-Station | Doh-Cox Ckt-2 | 2023-08-13 14:07 | 2023-08-13 15:20 | 1:13 | E/O | Tree trimming | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-1 | 2023-08-07 00:02 | 2023-08-07 00:13 | 0:11 | T | Distance Distance-R Distance-G Distance Aided trip | 60 | 11 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-2 | 2023-08-07 00:02 | 2023-08-07 00:29 | 0:27 | T |  | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-2 | 2023-08-22 23:52 | 2023-08-23 00:54 | 1:02 | E/O | High temperance maintenance. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Baroaulia-02 | 2023-08-07 04:57 | 2023-08-07 05:43 | 0:46 | T | distance trip | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Baroiarhat-01 | 2023-08-30 19:38 | 2023-08-31 13:18 | 17:40 | T | None | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Baroiarhat-02 | 2023-08-30 19:38 | 2023-08-30 19:50 | 0:12 | T | Tripped showing backup & distance relay. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Chandraghona-2 | 2023-08-16 13:28 | 2023-08-16 13:49 | 0:21 | T | General trip Zone-01,Zcom B-phase Fault | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-T.K. chemical complex | 2023-08-09 09:56 | 2023-08-27 16:05 | 438:09 | E/O | On the instruction of NLDC | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Dohazari Ckt-2 | 2023-08-08 18:31 | 2023-08-09 10:38 | 16:07 | E/O |  | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Interconnection-2 | 2023-08-19 10:05 | 2023-08-19 12:40 | 2:35 | E/O | Bay maintenance at Shikalbahab132KV end. | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Interconnection-2 | 2023-08-22 09:32 | 2023-08-23 16:38 | 31:06 | E/O | Current Flow being 0 Amp. at Y phase. | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Modunaghat Ckt-1 | 2023-08-19 08:45 | 2023-08-19 16:42 | 7:57 | E/O | Line maintenance | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Modunaghat Ckt-2(T.K Chemical) | 2023-08-27 10:44 | 2023-08-27 15:25 | 4:41 | E/O |  | 0 | 0 | No interruption
|  |  | Total : | 526:33 |  | Unserved Energy: |  | 11
Cumilla Grid Circle :
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-2 | 2023-08-19 14:58 | 2023-08-19 16:38 | 1:40 | E/O | Emergency maintenance Ashugonj sub-station | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni line-01 | 2023-08-10 06:38 | 2023-08-10 07:00 | 0:22 | T | Line Jumper Open Y phase | 20 | 7.3333 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni line-01 | 2023-08-10 07:01 | 2023-08-10 19:23 | 12:22 | E/O | Line Maintenance | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | HFPL line | 2023-08-01 11:30 | 2023-08-03 16:38 | 53:08 | T | Tripped | 56 | 2975.4667 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Ashuganj Ckt-2 | 2023-08-20 12:20 | 2023-08-20 13:15 | 0:55 | T | Distance Relay Operated | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Titas 50 MW Power Plant Line | 2023-08-20 10:12 | 2023-08-20 11:24 | 1:12 | T | 132 KV line touch by crane of Banglatrac | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Titas 50 MW Power Plant Line | 2023-08-22 05:55 | 2023-08-22 08:41 | 2:46 | E/O | Red Hot remove work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sreemongal-1 | 2023-08-30 15:19 | 2023-08-30 15:19 | 0:00 | T | Over Current, Srimangal SS LA burst. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sreemongal-2 | 2023-08-30 15:19 | 2023-08-30 15:19 | 0:00 | T | Over Current, Srimangal SS LA Burst. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Chowddagram Ckt-2 | 2023-08-17 15:37 | 2023-08-17 16:50 | 1:13 | T | Un known | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Chowddagram Ckt-2 | 2023-08-17 16:54 | 2023-08-17 19:35 | 2:41 | E/O | Tube well boring pipe touch the( B- Phase) live conductor of chauddagram ckt -2 between tower no. 482-483 | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Chowmuhani Ckt-1 | 2023-08-10 06:36 | 2023-08-10 19:21 | 12:45 | T |  | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Chowmuhani Ckt-2 | 2023-08-05 11:54 | 2023-08-05 12:48 | 0:54 | E/O | Line maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | Shajibazar-Sreemongal Ckt-02 | 2023-08-16 11:24 | 2023-08-16 11:33 | 0:09 | T | None | 0 | 0 | No interruption
|  |  | Total : | 90:07 |  | Unserved Energy: |  | 2982.8
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Bagerhat- Bhandaria | 2023-08-01 12:56 | 2023-08-01 13:41 | 0:45 | E/O | Emergency tree trimming of span 12 to 13 Tower middle spot of 132 Kv Bagerhat- Bhandaria Line. | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Bagerhat- Bhandaria | 2023-08-16 13:04 | 2023-08-16 13:45 | 0:41 | E/O | Emergengy Tree trimming. | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | 132kv Bhandaria ckt | 2023-08-01 11:19 | 2023-08-01 11:26 | 0:07 | T | Bad weather | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV 50MW Power Station ckt-1 | 2023-08-15 14:08 | 2023-08-15 15:13 | 1:05 | E/O | Power Station End work | 0 | 0 | No interruption
|  |  | Total : | 2:38 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
BIPTC | Baharampur-3 | 2023-08-10 17:27 | 2023-08-11 02:58 | 9:31 | T | Tripped by distance relay | 0 | 0 | No interruption
BIPTC | Rajshahi-2 | 2023-08-10 15:11 | 2023-08-10 16:32 | 1:21 | E/O | Problem found in HVDC- Rajshahi Ckt-02 44 number tower | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kv Natore-1 | 2023-08-29 22:18 | 2023-08-29 22:38 | 0:20 | T | overload | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kv Natore-2 | 2023-08-29 22:18 | 2023-08-29 22:38 | 0:20 | T | overload | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV Ghorashal 2 | 2023-08-20 08:29 | 2023-08-20 10:27 | 1:58 | T | Tripped by distance relay | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | Narail Ckt. - 2 | 2023-08-15 21:08 | 2023-08-15 21:18 | 0:10 | T | Thundering | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | Narail Ckt. - 2 | 2023-08-27 14:53 | 2023-08-27 16:26 | 1:33 | E/O | instructions by ALDC. Khulna. | 0 | 0 | No interruption
Pabna 132/33kV Grid Sub-Station | Pabna-Shahjadpur Line | 2023-08-28 15:27 | 2023-08-29 00:55 | 9:28 | E/O | Only CB (113B) Open. | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | 132 KV Shahjadpur-Bghabari-2 | 2023-08-27 22:05 | 2023-08-28 | 1:55 | T | sky wire à¦›à¦¿à§œà§‡ à¦²à¦¾à¦‡à¦¨à§‡à¦° à¦‰à¦ªà¦° à¦ªà§œà§‡ trip à¦•à¦°à§‡à¥¤ | 0 | 0 | No interruption
|  |  | Total : | 26:36 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Amnura 132/33kV Grid Sub-Station | Amnura - 50MW RPP | 2023-08-08 07:28 | 2023-08-08 22:57 | 15:29 | T | None | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | Amnura - Rajshahi | 2023-08-29 09:30 | 2023-08-29 09:40 | 0:10 | T |  | 8 | 3.0667 | Power interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Bogura Ckt-1 | 2023-08-01 19:44 | 2023-08-22 20:15 | 504:31 | E/O | According to NLDC's instructions. | 8 | 2.6667 | Power interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-1 | 2023-08-22 20:23 | 2023-08-29 00:55 | 148:32 | E/O | According to NLDC's instructions. | 60 | 23 | Power interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-2 | 2023-08-22 20:24 | 2023-08-23 17:24 | 21:00 | E/O | According to NLDC's instructions. | 58 | 22.2333 | Power interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-2 | 2023-08-23 17:28 | 2023-08-28 08:26 | 110:58 | E/O | With the permission of ALDC Bogura | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-2 | 2023-08-29 09:13 | 2023-08-29 09:13 | 0:00 | E/O | ALDC Recommendation | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | New Bogura-2 | 2023-08-24 14:20 | 2023-08-24 16:44 | 2:24 | E/O | In order by ALDC. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-4 | 2023-08-25 15:44 | 2023-08-25 17:33 | 1:49 | E/O | Red Hot Maintenance | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-4 | 2023-08-30 06:02 | 2023-08-30 07:20 | 1:18 | E/O | Red Hot Maintenance. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Sherpur 132 KV Line-2 | 2023-08-04 19:21 | 2023-08-19 22:40 | 363:19 | E/O | Transformer Overload. | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai-Amnura | 2023-08-29 21:25 | 2023-08-29 21:35 | 0:10 | T | O/C | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai-Rajshahi | 2023-08-29 21:25 | 2023-08-29 22:09 | 0:44 | T | Unknown | 0 | 0 | No interruption
Mahasthangarh 132/33kV Grid Sub-Station | Mahasthangarh-Polashbari 1 | 2023-08-31 08:06 | 2023-08-31 08:17 | 0:11 | T |  | 106 | 19.4333 | Power interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Joy Ckt-1 | 2023-08-24 15:54 | 2023-08-24 16:26 | 0:32 | T | Trip | 40 | 21.3333 | Power interruption
Palashbari 132/33kV Grid Sub-Station | Mahasthangarh-01 | 2023-08-25 16:02 | 2023-08-25 17:38 | 1:36 | E/O | Request to NLDC | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | Mahasthangarh-02 | 2023-08-25 16:04 | 2023-08-25 17:38 | 1:34 | E/O | Request to NLDC | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | Mahasthangarh-02 | 2023-08-31 08:10 | 2023-08-31 08:18 | 0:08 | T | Over Current. | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-GTPS | 2023-08-29 18:45 | 2023-08-29 19:01 | 0:16 | T | Suddenly Drop the Grid Voltage | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Kurigram | 2023-08-31 08:09 | 2023-08-31 08:32 | 0:23 | T | Mohastan to Polashbari 132 KV line trip. | 62 | 23.7667 | Power interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Saidpur-1 | 2023-08-31 12:01 | 2023-08-31 12:10 | 0:09 | T | None | 36 | 5.4 | Power interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Saidpur-2 | 2023-08-31 12:01 | 2023-08-31 12:19 | 0:18 | T |  | 36 | 10.8 | Power interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Teesta Solar-2 | 2023-08-25 18:12 | 2023-08-25 21:18 | 3:06 | E/O | DC converter Replace | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Baghabari Express | 2023-08-28 08:30 | 2023-08-29 08:48 | 24:18 | E/O | Corrective maintence at shahjadpur end. and By the instruction of XEN , NLDC | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Shahjadpur | 2023-08-27 22:10 | 2023-08-29 08:49 | 34:39 | T | Sky wire tore apart near Shahjadpur S/S side. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-1 | 2023-08-28 08:28 | 2023-08-29 00:55 | 16:27 | E/O | By the instruction of XEN , NLDC | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 2023-08-28 08:28 | 2023-08-28 08:30 | 0:02 | E/O | By the instruction of XEN , NLDC | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 2023-08-29 09:13 | 2023-09-04 15:03 | 149:50 | E/O | Line conductor stringing. | 0 | 0 | No interruption
Sirajgonj 230 kV Switching Station | SNWPCL (Unit-04) | 2023-08-17 06:15 | 2023-08-17 10:33 | 4:18 | E/O | Bay DS, Y Phase Red Hot detected | 0 | 0 | No interruption
|  |  | Total : | 1408:11 |  | Unserved Energy: |  | 131.7
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 2934:42 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: August 2023
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) HT | 2023-08-04 06:14 | 2023-08-04 10:12 | 3:58 | S/O | Replacing Faulty 33kV LAs of 230/132/33kV Tr-1 | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 02 | 2023-08-25 10:30 | 2023-08-25 13:05 | 2:35 | S/O | Loop armarung | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 LT | 2023-08-22 14:06 | 2023-08-22 16:49 | 2:43 | S/O | Red hot maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 01 LT | 2023-08-10 07:03 | 2023-08-10 10:59 | 3:56 | S/O | 33 kv Bus coupler problem | 65 | 255.6667 | Power interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-08-23 06:13 | 2023-08-23 08:46 | 2:33 | S/O | Red-hot maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-08-10 05:58 | 2023-08-10 08:36 | 2:38 | S/O | Hot point maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-08-05 15:05 | 2023-08-05 18:35 | 3:30 | S/O | Redhot maintenance | 30 | 105 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-2 HT | 2023-08-10 06:28 | 2023-08-10 12:26 | 5:58 | S/O | 33kv T-2 extension bus conductor replace work purpose. | 20 | 119.3333 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-3 HT | 2023-08-01 08:42 | 2023-08-01 12:45 | 4:03 | S/O | Neutral grounding conductor replacement work | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-4 HT | 2023-08-16 08:20 | 2023-08-16 09:56 | 1:36 | S/O | High temperature reduce maintenance work. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Reserve bus | 2023-08-10 06:03 | 2023-08-10 08:02 | 1:59 | S/O | red hot maintenance work. | 58 | 115.0333 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-2 HT | 2023-08-20 15:14 | 2023-08-20 16:51 | 1:37 | S/O | 33KV Boroibari feeder Bus side red hot | 110 | 177.8333 | Power interruption
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 HT | 2023-08-21 06:10 | 2023-08-21 08:42 | 2:32 | S/O | Red Hot at LT side T joint | 270 | 684 | Power interruption | ok
Kallyanpur 132/33kV Grid Sub-Station | GT-1 (132kV) HT | 2023-08-13 10:05 | 2023-08-13 16:08 | 6:03 | S/O | Maintenance Work | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-2 (132kV) HT | 2023-08-13 16:09 | 2023-08-13 18:04 | 1:55 | S/O | Relay testing | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-2 (132kV) HT | 2023-08-16 16:19 | 2023-08-16 16:31 | 0:12 | S/O | 33 kV CB SF6 Gass Refill Work. | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Bus-A | 2023-08-05 09:54 | 2023-08-05 10:42 | 0:48 | S/O | Maintenance Work | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) HT | 2023-08-02 15:55 | 2023-08-02 16:45 | 0:50 | S/O | T3 X-Former Oil leakage Fixing work by CCC | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) HT | 2023-08-17 14:20 | 2023-08-17 16:25 | 2:05 | S/O | Maintenance Work | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) LT | 2023-08-17 09:06 | 2023-08-17 13:52 | 4:46 | S/O | Redhot removal | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Bus A | 2023-08-12 06:20 | 2023-08-12 08:30 | 2:10 | S/O | 132kV Solar Ckt Shut down due of High Temperature Maintenance in 132kV Solar Ckt A-Bus DS( 501S) -R & Y Phase Clamp. Shut down taken by Mr. Wang Hong Qiang, Manager, HDFC, Sinpower. | 185 | 400.8333 | Power interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-2 (414T) HT | 2023-08-05 06:10 | 2023-08-05 07:50 | 1:40 | S/O | S/D due to Red hot maintenance work for 33kV Gafagaon Feeders 33kV Bus DS(R-Ph) upper clamp. | 85 | 141.6667 | Power interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-3 (424T) HT | 2023-08-19 07:00 | 2023-08-19 09:22 | 2:22 | S/O | High temperature on Y-Phase CT clamp | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-A | 2023-08-20 23:47 | 2023-08-21 09:49 | 10:02 | S/O | Red hot maintenance | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-B | 2023-08-16 10:18 | 2023-08-16 15:52 | 5:34 | S/O | DPBS-3 Shutdown for Red hot maintenance | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-B | 2023-08-26 09:12 | 2023-08-26 18:09 | 8:57 | S/O | Red hot maintenance of 33kV L-31 Bus Incomer by DPBS-3 | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-2 HT | 2023-08-26 09:20 | 2023-08-26 17:58 | 8:38 | S/O | Red hot maintenance of 132kV Bushing terminals | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Transfer Bus | 2023-08-26 10:35 | 2023-08-26 17:40 | 7:05 | S/O | Alignment work of 132kV T-2 Main Bus-II DS (411M) | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 01 LT | 2023-08-14 12:08 | 2023-08-14 13:35 | 1:27 | S/O | oiltc oil sample | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 02 LT | 2023-08-14 11:20 | 2023-08-14 12:05 | 0:45 | S/O | oiltc oil sample | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 HT | 2023-08-05 06:57 | 2023-08-05 08:42 | 1:45 | S/O | 33kv T2 bus red hot | 40 | 70 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-4 HT | 2023-08-05 06:51 | 2023-08-05 08:42 | 1:51 | S/O | 33kv T2 bus red hot | 10 | 18.5 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-4 LT | 2023-08-14 16:03 | 2023-08-14 18:54 | 2:51 | S/O | Shakhipur 33kv feeder CT change | 0 | 0 | No interruption
|  |  | Total : | 111:24 |  | Unserved Energy: |  | 2087.8667
Dhaka (South) Grid Circle : | [13 empty] | 39.3333
Bhulta 132/33kV Grid Sub-Station | GT1 LT | 2023-08-03 16:56 | 2023-08-03 17:55 | 0:59 | S/O | GT-1 33 kv side red hot maintenance work. | 70 | 68.8333 | Power interruption
Haripur 230/132kV Grid Sub-Station | 132kV Bus Coupler | 2023-08-18 08:41 | 2023-08-18 15:20 | 6:39 | S/O | Maintanance work | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 132kV Main Bus Sec-2 | 2023-08-18 08:40 | 2023-08-18 15:20 | 6:40 | S/O | Maintanance work | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Auto TR-3 HT | 2023-08-18 08:23 | 2023-08-18 15:22 | 6:59 | S/O | Maintanance work | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 HT | 2023-08-05 15:45 | 2023-08-05 18:17 | 2:32 | S/O | To do the maintenace work of PRV 02 device. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 LT | 2023-08-22 07:45 | 2023-08-22 10:55 | 3:10 | S/O | MOG related maintenance work. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Earthing Trafo-1 HT | 2023-08-22 07:46 | 2023-08-22 10:54 | 3:08 | S/O | MOG related maintenance work ATR-01 | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) LT | 2023-08-18 07:29 | 2023-08-18 18:31 | 11:02 | S/O | Oil Filling Work. | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | Auxiliary Transformer-02 HT | 2023-08-18 07:29 | 2023-08-18 18:32 | 11:03 | S/O | Oil Filling Work. | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | T-3 HT | 2023-08-31 21:10 | 2023-08-31 22:48 | 1:38 | S/O | 33KV (T3) CB Loop Connection Point Hotspot Mainteance Work. | 50 | 81.6667 | Power interruption
Nawabganj 132/33kV Grid Sub-Station | TR-1 LT | 2023-08-26 08:32 | 2023-08-26 13:11 | 4:39 | S/O | 33kv bus -01 S/D Due to bus Coupler Maintenance work. | 25.5 | 118.575 | Power interruption
Nawabganj 132/33kV Grid Sub-Station | TR-2 LT | 2023-08-26 08:35 | 2023-08-26 13:14 | 4:39 | S/O | 33kv bus -01 S/D Due to bus Coupler Maintenance work. | 25.5 | 118.575 | Power interruption
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 HT | 2023-08-08 09:57 | 2023-08-08 11:30 | 1:33 | S/O | OLTC Conservator Oil Level Low. | 0 | 0 | No interruption |  |  |  |  | 39.3333
Sonargaon 132/33kV Grid Sub-Station | Tr-1 HT | 2023-08-26 09:01 | 2023-08-26 10:22 | 1:21 | S/O | PBS 33kv kabilganj feeder Redhot maintenance. Work performed by PBS. | 30 | 40.5 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2023-08-06 07:13 | 2023-08-06 09:24 | 2:11 | S/O | S/D taken by PBS for corrective Maintenance . | 35 | 76.4167 | Power interruption
|  |  | Total : | 68:13 |  | Unserved Energy: |  | 504.5667
Chattogram Grid Circle :
Bakulia 132/33kV Grid Sub-Station | T-3 (422T) HT | 2023-08-19 07:07 | 2023-08-19 09:19 | 2:12 | S/O | 132/33 kV, Tr-02 Shutdown due to Over current relay replace by Ctg SPMD | 9 | 19.8 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-1 HT | 2023-08-23 07:42 | 2023-08-23 08:16 | 0:34 | S/O | 50/75 MVA 132/33KV (422T) T-3 transformer marshalling box to transformer relay panel CT new cable connection work & transformer both side hot spot maintenance work. | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 HT | 2023-08-02 05:58 | 2023-08-02 07:27 | 1:29 | S/O | High temperature maintenance. | 40 | 59.3333 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 HT | 2023-08-03 06:00 | 2023-08-03 08:53 | 2:53 | S/O | Keranihat 33 kv pbs maintenance work. | 30 | 86.5 | Power interruption
Hathazari 230/132/33kV Grid Sub-Station | T-01 HT | 2023-08-01 17:50 | 2023-08-01 18:50 | 1:00 | S/O | high temperature maintenance. | 0 | 0 | No interruption
TK chemical 132kV Grid Sub-Station | 50/75 MVA T-1(405T) HT | 2023-08-09 10:00 | 2023-08-09 13:08 | 3:08 | D/W | 33 kV XLPE B Ph Cable Fixing | 0 | 0 | No interruption
TK chemical 132kV Grid Sub-Station | 50/75 MVA T-1(405T) HT | 2023-08-23 11:16 | 2023-08-23 16:26 | 5:10 | D/W | 33 kV XLPE B Ph Cable Fixing | 0 | 0 | No interruption
|  |  | Total : | 16:26 |  |  |  | 165.6333
Cumilla Grid Circle :
Beanibazar 132/33kV Grid Sub-Station | 132KV Transformer TR-02 HT | 2023-08-12 11:02 | 2023-08-12 16:50 | 5:48 | S/O | Development work | 10 | 58 | Power interruption
Beanibazar 132/33kV Grid Sub-Station | 132KV Transformer TR-02 HT | 2023-08-23 17:40 | 2023-08-23 19:26 | 1:46 | S/O | 33 kv bus red hot | 45 | 79.5 | Power interruption
Chandpur 132/33kV Grid Sub-Station | Bus-B | 2023-08-12 11:54 | 2023-08-12 15:53 | 3:59 | S/O | Bus pt glass broken | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | T-1 HT | 2023-08-29 08:56 | 2023-08-29 09:48 | 0:52 | S/O | shut down for checking neutral bushing connection, proposed from SPMD, Cumilla | 1 | 0.86667 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-2 LT | 2023-08-04 16:09 | 2023-08-04 17:39 | 1:30 | S/O | PDB taken S/D for Work. | 20 | 30 | Power interruption
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-08-30 09:30 | 2023-08-30 13:58 | 4:28 | S/O | Scada Connection | 15 | 67 | Power interruption
Daudkandi 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-08-30 13:59 | 2023-08-30 16:03 | 2:04 | S/O | Scada connection | 15 | 31 | Power interruption
Kulaura 132/33kV Grid Sub-Station | TR-1 HT | 2023-08-19 11:07 | 2023-08-19 16:05 | 4:58 | S/O | 33KV bus maintenance by PBS. | 25 | 124.1667 | Power interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 LT | 2023-08-24 08:06 | 2023-08-24 08:53 | 0:47 | S/O | 33 KV side Breaker loop joint hotspot Maintenance. Load flow by TR-04. | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 LT | 2023-08-05 08:25 | 2023-08-05 08:59 | 0:34 | S/O | Shutdown taken by PBS, Habigonj for 33KV feeder hot spot Maintenance. | 40 | 22.6667 | Power interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-2 LT | 2023-08-31 13:33 | 2023-08-31 17:07 | 3:34 | S/O | 132 kV LA Change. | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-3 HT | 2023-08-21 10:40 | 2023-08-21 11:05 | 0:25 | S/O | SF6 Gass Refill. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T1 HT | 2023-08-09 14:20 | 2023-08-09 15:41 | 1:21 | S/O | Oil Leaking Maintenance | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T1 HT | 2023-08-10 05:50 | 2023-08-10 08:10 | 2:20 | S/O | 33 KV T1A U/G Cable Maintenance | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T1 HT | 2023-08-30 13:52 | 2023-08-30 14:14 | 0:22 | S/O | Cable maintenance of station Aux-1 | 45 | 16.5 | Power interruption
Sylhet 132/33kV Grid Sub-Station | T1 LT | 2023-08-05 05:40 | 2023-08-05 07:04 | 1:24 | S/O | Red hot Maintenance | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T2 HT | 2023-08-29 06:50 | 2023-08-29 09:48 | 2:58 | D/W | Amberkhana-1 Redhot Maintenance | 15 | 44.5 | Power interruption
|  |  | Total : | 39:10 |  | Unserved Energy: |  | 474.2
Khulna Grid Circle : | [12 empty] | 251.2167
Bagerhat 132/33kV Grid Sub-Station | Transformer-3 ( 423 T) LT | 2023-08-26 07:21 | 2023-08-26 10:17 | 2:56 | S/O | 33 kv feeder rizar change work | 25 | 73.3333 | Power interruption |  |  |  | 113.55
Barguna 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-08-19 09:48 | 2023-08-19 11:50 | 2:02 | S/O | 33 KV BREB-2 Feeder D/S load side Redhot Maintenance. | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) HT | 2023-08-03 03:30 | 2023-08-03 04:10 | 0:40 | S/O | For checking physical condition | 30 | 20 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2023-08-10 15:09 | 2023-08-10 23:25 | 8:16 | S/O | To improve grounding system of T2 Transformer. | 0 | 0 | No interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-08-30 16:16 | 2023-08-30 16:25 | 0:09 | S/O | WZPDCL taken S/D For Renovation work | 10 | 1.5 | Power interruption |  |  |  | 364.7667
Faridpur 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-08-06 09:25 | 2023-08-06 12:23 | 2:58 | D/W | Project Work | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-08-06 12:42 | 2023-08-06 15:11 | 2:29 | D/W | Project work | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-3 LT | 2023-08-07 09:06 | 2023-08-07 19:32 | 10:26 | D/W | Due to maint.work | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-3 LT | 2023-08-29 09:30 | 2023-08-29 13:15 | 3:45 | D/W | Project work | 0 | 0 | No interruption
Gollamari 132/33kV Grid Sub-Station | Tr-1 LT | 2023-08-09 17:02 | 2023-08-09 17:59 | 0:57 | S/O | Red hot maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | T1 HT | 2023-08-10 07:03 | 2023-08-10 09:59 | 2:56 | S/O | 33 kv incoming -1 DS finger adjustment work. | 10 | 29.3333 | Power interruption
Gopalganj 132/33kV Grid Sub-Station | T1 LT | 2023-08-19 08:26 | 2023-08-19 14:40 | 6:14 | S/O | Due to high side R & B phage bushing top maintenance of Transformer-1 by energyp | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | T1 LT | 2023-08-27 07:26 | 2023-08-27 08:47 | 1:21 | S/O | BPBS -1 red hot maintenance | 10 | 13.5 | Power interruption
Gopalganj 132/33kV Grid Sub-Station | T2 LT | 2023-08-11 07:15 | 2023-08-11 10:53 | 3:38 | S/O | 33 kv REB Feeder & bus joint maintenance. | 30 | 109 | Power interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-02 HT | 2023-08-31 09:53 | 2023-08-31 15:53 | 6:00 | D/W | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-02 LT | 2023-08-16 09:58 | 2023-08-16 17:36 | 7:38 | D/W | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-02 LT | 2023-08-27 10:20 | 2023-08-30 16:49 | 78:29 | D/W | Fire protection work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-03 HT | 2023-08-07 08:27 | 2023-08-07 17:54 | 9:27 | D/W | fire fighting work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-03 HT | 2023-08-16 09:59 | 2023-08-16 17:35 | 7:36 | D/W | Due to project work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-03 LT | 2023-08-04 09:37 | 2023-08-04 17:47 | 8:10 | S/O | Fire fighting work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-03 LT | 2023-08-05 09:37 | 2023-08-05 17:37 | 8:00 | D/W | Due to project work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-03 LT | 2023-08-06 09:27 | 2023-08-06 17:38 | 8:11 | D/W | Due to project work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-03 LT | 2023-08-08 10:15 | 2023-08-08 17:44 | 7:29 | D/W | Due to project work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-03 LT | 2023-08-09 10:18 | 2023-08-09 17:41 | 7:23 | D/W | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-03 LT | 2023-08-14 10:02 | 2023-08-14 18:14 | 8:12 | S/O | Fire fighting work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-03 LT | 2023-08-17 09:24 | 2023-08-17 17:55 | 8:31 | D/W | Due to project work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-03 LT | 2023-08-18 09:36 | 2023-08-18 19:38 | 10:02 | D/W | Due to project work | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-1 LT | 2023-08-28 07:12 | 2023-08-28 11:24 | 4:12 | S/O | Red hot maintenance work | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-2 LT | 2023-08-28 11:32 | 2023-08-28 14:42 | 3:10 | S/O | Over Heating Maintenance. | 0 | 0 | No interruption
Narail 132/33kV Grid Sub-Station | TR1 (403-T) LT | 2023-08-03 13:15 | 2023-08-03 13:35 | 0:20 | S/O | Protection work | 0 | 0 | No interruption
Narail 132/33kV Grid Sub-Station | TR2 (413-T) LT | 2023-08-03 13:54 | 2023-08-03 15:20 | 1:26 | S/O | Protection work | 0 | 0 | No interruption
Narail 132/33kV Grid Sub-Station | TR2 (413-T) LT | 2023-08-21 06:50 | 2023-08-21 08:25 | 1:35 | S/O | Red hot maintenance work in 33 kV feeder No-06 | 25 | 39.5833 | Power interruption
Narail 132/33kV Grid Sub-Station | TR2 (413-T) LT | 2023-08-26 06:48 | 2023-08-26 08:49 | 2:01 | S/O | Red hot maintenance in 33 kV feeder no-06 source side DS ( Y- phase) | 20 | 40.3333 | Power interruption
Noapara 132/33kV Grid Sub-Station | BUS-B | 2023-08-09 09:01 | 2023-08-23 16:44 | 343:43 | D/W | Upgradation of B-Bus . | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | T-2 LT | 2023-08-25 06:25 | 2023-08-25 17:56 | 11:31 | D/W | 33kv bus S/D | 28 | 322.4667 | Power interruption | ok
Noapara 132/33kV Grid Sub-Station | T-4 LT | 2023-08-03 13:11 | 2023-08-03 14:05 | 0:54 | S/O | High Temp Maintenance | 20 | 18 | Power interruption
Noapara 132/33kV Grid Sub-Station | T-4 LT | 2023-08-25 06:25 | 2023-08-25 18:01 | 11:36 | D/W | 33kv bus S/D | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 415T (T-2) HT | 2023-08-26 08:35 | 2023-08-26 14:13 | 5:38 | S/O | Loop changing work | 8 | 45.0667 | Power interruption
Rampal 400/230kV Grid Sub-Station | Generator Transformer-1 (GT-1) HT | 2023-08-03 11:36 | 2023-08-14 15:16 | 267:40 | D/W | Maintenance Work Purpose | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-2 (T-2) LT | 2023-08-04 09:04 | 2023-08-04 11:05 | 2:01 | S/O | Red hot maintenance | 25 | 50.4167 | Power interruption
Shariatpur 132/33kV Grid Sub-Station | Auxiliary-01 (PGCB) LT | 2023-08-18 08:20 | 2023-08-18 09:30 | 1:10 | S/O | Red hot Maintenance by Pbs. | 10 | 11.6667 | Power interruption
Shariatpur 132/33kV Grid Sub-Station | Main Bus - 1 | 2023-08-07 12:34 | 2023-08-07 19:07 | 6:33 | S/O | Bus coupler isolator ( Bus section -1) signal problem solution. | 0 | 0 | No interruption
Shariatpur 132/33kV Grid Sub-Station | T1-406T HT | 2023-08-18 08:23 | 2023-08-18 09:29 | 1:06 | S/O | Red hot Maintenance by Pbs. | 10 | 11 | Power interruption
|  |  | Total : | 888:31 |  | Unserved Energy : |  | 785.2
HVDC Grid Circle
Baghabari 230/132kV Grid Sub-Station | T-2 Bank HT | 2023-08-28 16:09 | 2023-08-28 21:17 | 5:08 | S/O | Maintenance work at PDB end. | 0 | 0 | No interruption
Bheramara(GK) 132/33kV Grid Sub-Station | TR-2 LT | 2023-08-28 14:19 | 2023-08-28 15:48 | 1:29 | S/O | PBS 33kV feeder red hot repair clamp change | 22 | 32.6333 | Power interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Bus-2 | 2023-08-12 15:39 | 2023-08-12 18:11 | 2:32 | S/O | Bus isolator Maintenance | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-1 HT | 2023-08-02 06:16 | 2023-08-02 08:44 | 2:28 | S/O | 33 kv bus maintenance | 30 | 74 | Power interruption
Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-2 HT | 2023-08-04 10:01 | 2023-08-04 12:35 | 2:34 | S/O | station auxilary x-former maint..work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-2 HT | 2023-08-10 10:06 | 2023-08-10 13:35 | 3:29 | S/O | Auxiliary transformer maintenance work. | 25 | 87.0833 | Power interruption
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 HT | 2023-08-12 07:32 | 2023-08-12 15:07 | 7:35 | S/O | Centrifuging OLTC oil | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | T2 LT | 2023-08-16 06:10 | 2023-08-16 09:20 | 3:10 | S/O | 33 kv Isolator installation (Koburhat feeder ,WZPDCL) | 35 | 110.8333 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2023-08-25 07:25 | 2023-08-25 09:48 | 2:23 | D/W | New 33KV Square Feeder Bus Connection. | 30 | 71.5 | Power interruption
|  |  | Total : | 30:48 |  | Unserved Energy : |  | 376.05
Bogura Grid Circle:
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T LT | 2023-08-18 09:19 | 2023-08-18 11:09 | 1:50 | S/O | Red hot Maintenance work | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-08-04 15:33 | 2023-08-04 17:21 | 1:48 | S/O | 33kv nesco work | 45 | 81 | Power interruption
Bogura 230/132kV Grid Sub-Station | 132KV Main 2 | 2023-08-24 17:16 | 2023-08-24 17:16 | 0:00 | D/W | Due to maint.work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 1 | 2023-08-19 06:07 | 2023-08-21 12:12 | 54:05 | D/W | 230kV Bogura(W) Ckt.-3 DS Replacement work. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 1 | 2023-08-28 09:04 | 2023-08-28 09:58 | 0:54 | S/O | 230 kV Bogura(W) Ckt.-4 DS Replacement work. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 2 | 2023-08-07 08:47 | 2023-08-07 11:32 | 2:45 | S/O | Isolator arm change | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 2 | 2023-08-12 07:02 | 2023-08-12 10:12 | 3:10 | S/O | 230kV Main Bus-2 S/D (Shift) for 230kV Bogura (W) Ckt.-3 Red Hot Maintenance. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 2 | 2023-08-25 06:39 | 2023-08-25 09:48 | 3:09 | S/O | Isolator replacement work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 2 | 2023-08-28 06:15 | 2023-08-28 08:53 | 2:38 | S/O | Isolator Replacement Work. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 2 | 2023-08-28 10:13 | 2023-08-28 12:12 | 1:59 | S/O | 230kV bogura(w) Ckt..-4 DS Replacement work. | 0 | 0 | No interruption |  |  | 2:19
Bogura 230/132kV Grid Sub-Station | T-01 HT | 2023-08-19 06:42 | 2023-08-19 08:17 | 1:35 | S/O | Red Hot Maintenance work ,(R-Phase Loop Change) | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-02 LT | 2023-08-11 06:06 | 2023-08-11 09:45 | 3:39 | S/O | Bushing conductor replacement | 143 | 521.95 | Power interruption |  | ok
Chapai 132/33kV Grid Sub-Station | T-2 (415T) HT | 2023-08-30 09:11 | 2023-08-31 13:55 | 28:44 | S/O | OLTC oil centifuse | 0 | 0 | No interruption
Mahasthangarh 132/33kV Grid Sub-Station | 416T MTR 2 LT | 2023-08-19 07:08 | 2023-08-19 09:31 | 2:23 | S/O | 33 KV Busbar Maintenance work of 33KV Kalai Feeder of PBS | 15 | 35.75 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2023-08-31 06:54 | 2023-08-31 09:18 | 2:24 | S/O | Red hot maintanance of mohadebpur pbs 33kv feeder. | 42 | 100.8 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-3 HT | 2023-08-12 12:42 | 2023-08-13 19:26 | 30:44 | D/W | 33kv CB change | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | TR-1 (405 T) LT | 2023-08-24 07:09 | 2023-08-24 08:39 | 1:30 | S/O | L.T ioop maintanance(change). | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | TR1-414T HT | 2023-08-08 16:30 | 2023-08-08 17:36 | 1:06 | S/O | Red Hot. | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) HT | 2023-08-21 11:54 | 2023-08-21 12:29 | 0:35 | S/O |  | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-3 (424T) HT | 2023-08-14 07:05 | 2023-08-14 08:25 | 1:20 | S/O | 33kv Bus Maintenance | 10 | 13.3333 | Power interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2023-08-14 07:35 | 2023-08-14 08:55 | 1:20 | S/O | 33 BODA (TPBS) feeder bus connection. | 0 | 0 | No interruption
|  |  | Total : | 147:38 |  | Unserved Energy : |  | 752.8333
Others :Nil
|  |  | Total : | 0:00 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1302:10 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: August 2023
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV Grid Sub-Station | Manikgonj Power Plant-01 | 2023-08-10 09:50 | 2023-08-10 15:16 | 5:26 | S/O | Red hot maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Mirpur-01 | 2023-08-25 10:35 | 2023-08-25 14:01 | 3:26 | S/O | Bay equipment Maintanence | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-1 | 2023-08-21 09:14 | 2023-08-21 16:38 | 7:24 | D/W | GIS project work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-1 | 2023-08-22 09:04 | 2023-08-22 18:37 | 9:33 | D/W | 132kv GIS work purpose. | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Kishoreganj 132 kV Ckt-2 | 2023-08-05 09:41 | 2023-08-05 11:14 | 1:33 | S/O | Maintenance work at kishoreganj end | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Mymensingh- Bhaluka 132 kV Ckt- 02 | 2023-08-18 06:06 | 2023-08-18 10:43 | 4:37 | S/O | Mymensingh side | 40 | 184.6667 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | 132KV PPM Jamalpur Power Plant | 2023-08-01 21:12 | 2023-08-01 23:32 | 2:20 | S/O | Line D.S maintenance work purpose. | 0 | 81.3333 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | 132KV PPM Jamalpur Power Plant | 2023-08-14 10:20 | 2023-08-14 16:42 | 6:22 | S/O | Disconncetor Switch Maintenance(Power plant end) | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Ghorashal ckt-2 | 2023-08-24 05:47 | 2023-08-24 09:54 | 4:07 | S/O | R phase LA high temperature Maintenance | 80 | 329.3333 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | Tongi-1 | 2023-08-10 06:08 | 2023-08-10 07:49 | 1:41 | S/O | red hot maintenance work. | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2023-08-17 09:06 | 2023-08-17 13:52 | 4:46 | S/O | Redhot removal | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | 50 MW Solar Plant | 2023-08-12 06:03 | 2023-08-12 11:30 | 5:27 | S/O | 132kV Solar Ckt Shut down due of High Temperature Maintenance in 132kV Solar Ckt A-Bus DS( 501S) -R & Y Phase Clamp. Shut down taken by Mr. Wang Hong Qiang, Manager, HDFC, Sinpower. | 0 | 0 | No interruption
|  |  | Total : | 56:42 |  | Unserved Energy: |  | 595.3333
Dhaka (South) Grid Circle :
Haripur 230/132kV Grid Sub-Station | Bhulta | 2023-08-09 06:21 | 2023-08-09 07:36 | 1:15 | S/O | CB to CT Loop Change Y phase | 70 | 87.5 | Power interruption
Haripur 230/132kV Grid Sub-Station | EGCB 412MW | 2023-08-19 06:59 | 2023-08-19 15:49 | 8:50 | S/O | Jack bus to CB Loop Change Work . | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Narsingdi | 2023-08-12 06:54 | 2023-08-12 10:17 | 3:23 | S/O | Maintanance Work. | 57 | 192.85 | Power interruption
Hasnabad 230/132kV Grid Sub-Station | Shyampur-APR-Hasnabad Ckt-2 | 2023-08-18 06:52 | 2023-08-18 21:03 | 14:11 | S/O | LILO Connection out at APR Power Plant. | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Shyampur-APR-Hasnabad Ckt-2 | 2023-08-19 07:13 | 2023-08-19 21:18 | 14:05 | S/O | LILO connection out at APR Power Plant. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aminbazar-1 | 2023-08-14 14:14 | 2023-08-14 16:38 | 2:24 | S/O | SPMD work at Aminbazar. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aminbazar-1 | 2023-08-21 10:35 | 2023-08-21 12:58 | 2:23 | S/O | Maintenance work at aminbazar end. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Mero Rail - 1 | 2023-08-20 15:09 | 2023-08-20 15:09 | 0:00 | S/O | Cable Termination Work | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | 230kV Siddhirganj-Maniknagar ckt-2 | 2023-08-21 05:55 | 2023-08-21 05:55 | 0:00 | S/O | Re-Routing of Tower . | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 230 kV APR (D04) | 2023-08-18 06:55 | 2023-08-18 20:46 | 13:51 | S/O | Hasnabad grid will work at APR END | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 230 kV APR (D04) | 2023-08-19 07:14 | 2023-08-19 21:21 | 14:07 | S/O | Hasnabad grid will work at APR Circuit | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | Maniknagar 2 | 2023-08-18 07:31 | 2023-08-18 18:31 | 11:00 | S/O | Transformer will work for Maniknagar end. | 0 | 0 | No interruption
Srinagar 132/33kV Grid Sub-Station | Keraniganj-01 | 2023-08-02 08:50 | 2023-08-02 17:55 | 9:05 | S/O | Sreenagar- Keraniganj Line -01 Shutdown as per requist by NLDC for Keraniganj side work done. | 0 | 0 | No interruption
|  |  | Total : | 94:34 |  | Unserved Energy: |  | 280.35
Chattogram Grid Circle :
Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-2 | 2023-08-01 06:08 | 2023-08-01 11:08 | 5:00 | S/O | Bus coupler Bay conductor change. Doha-sik-01 is on duty. | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-2 | 2023-08-27 14:30 | 2023-08-27 15:52 | 1:22 | S/O | High Temperature maintenance of Xfer Bus DS (R) of Bus coupler Bay | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Shikolbaha-02 | 2023-08-22 16:08 | 2023-08-22 18:12 | 2:04 | D/W | Project work | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-AKSPL Line | 2023-08-03 12:34 | 2023-08-03 15:31 | 2:57 | S/O | CT Change & Replace in AKSPL Sub-Station. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Sikalbaha ckt | 2023-08-17 09:06 | 2023-08-17 16:03 | 6:57 | S/O | For line inspection and river-crossing conductor(Karnafully River) maintenance work. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Sikalbaha ckt | 2023-08-18 09:51 | 2023-08-18 17:23 | 7:32 | S/O | For river-crossing(Karnafully river) conductor strengthening work. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Sikalbaha ckt | 2023-08-19 08:44 | 2023-08-19 16:41 | 7:57 | S/O | Line inspection and maintenance work. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Sikalbaha ckt | 2023-08-20 09:08 | 2023-08-20 16:35 | 7:27 | S/O | Line inspection and maintenance work. | 0 | 0 | No interruption
Rangamati 132/33kV Grid Sub-Station | Chandraghona Ckt-02 | 2023-08-17 09:18 | 2023-08-17 11:28 | 2:10 | S/O | Red hot. | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Dohazari ckt-1 | 2023-08-02 10:32 | 2023-08-02 15:22 | 4:50 | S/O | Line maintenance. | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Hathazari-02 | 2023-08-21 12:38 | 2023-08-21 17:32 | 4:54 | D/W | Line maintenance. | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Hathazari-02 | 2023-08-22 16:11 | 2023-08-22 18:08 | 1:57 | D/W | Line maintenance. | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Modunaghat Ckt-1 | 2023-08-17 09:07 | 2023-08-17 16:03 | 6:56 | S/O | Maintenance at Madunaghat end. | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Modunaghat Ckt-1 | 2023-08-18 09:50 | 2023-08-18 17:22 | 7:32 | S/O | Line maintenance. | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Modunaghat Ckt-1 | 2023-08-20 09:07 | 2023-08-20 16:35 | 7:28 | S/O | Line maintenance. | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Modunaghat Ckt-2(T.K Chemical) | 2023-08-16 08:37 | 2023-08-16 12:23 | 3:46 | S/O | Maintenance at T.K.Chemical end | 0 | 0 | No interruption
TK chemical 132kV Grid Sub-Station | T.K. chemical-Sikalbaha | 2023-08-09 10:03 | 2023-08-09 12:55 | 2:52 | D/W | Line maintenance. | 0 | 0 | No interruption
TK chemical 132kV Grid Sub-Station | T.K. chemical-Sikalbaha | 2023-08-23 11:21 | 2023-08-23 16:18 | 4:57 | D/W | Line maintenance. | 0 | 0 | No interruption
|  |  | Total : | 88:38 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Daudkandi Ckt-2 | 2023-08-31 11:19 | 2023-08-31 13:10 | 1:51 | S/O | Daudkandi End SCADA operation test. | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Tripura Ckt-1 | 2023-08-25 09:02 | 2023-08-25 18:09 | 9:07 | S/O | BUS SIDE ISOLATOR REALIGNMENT WORK SM NAGAR END . | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-1 | 2023-08-31 08:52 | 2023-08-31 11:16 | 2:24 | D/W | Cumilla(N)-1 Line shutdown for SCADA Connection work. | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Sonargaon-1 | 2023-08-29 09:02 | 2023-08-29 15:54 | 6:52 | D/W | 132 KV Sonargaon-1 Line Shutdown for SCADA Connection Work. | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Sonargaon-2 | 2023-08-29 15:58 | 2023-08-29 18:53 | 2:55 | D/W | SCADA connection Work | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Sonargaon-2 | 2023-08-30 16:13 | 2023-08-30 16:44 | 0:31 | D/W | Scada cnnection test | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | Shahjibazar-Ashuganj Ckt-03 | 2023-08-26 06:42 | 2023-08-26 07:16 | 0:34 | S/O | S/D taken by Ashugonj Side.( Corrective maintenance at Ashugonj End) | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | 20 MW PP | 2023-08-20 15:40 | 2023-08-20 16:26 | 0:46 | D/W | Schedule Maintenance Purpose. | 0 | 0 | No interruption
|  |  | Total : | 25:00 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Faridpur 132/33kV Grid Sub-Station | 132 KV 50MW Power Station ckt-1 | 2023-08-08 08:58 | 2023-08-08 20:28 | 11:30 | D/W | Project Work | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Gopalganj (400kv) ckt-1 | 2023-08-09 08:53 | 2023-08-09 13:45 | 4:52 | S/O | Installation of Junction Box | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Rajbari ckt-2 | 2023-08-08 12:55 | 2023-08-08 17:21 | 4:26 | D/W | Project work | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Khulna Central Ckt-2 | 2023-08-24 06:11 | 2023-08-24 09:27 | 3:16 | S/O | CB & DS Conductor Change for Central ss End. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Rampal Ckt-2 | 2023-08-01 12:28 | 2023-08-01 13:30 | 1:02 | S/O | Protection test work | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | khulna central - 1 | 2023-08-26 09:01 | 2023-08-26 12:40 | 3:39 | S/O | Upgradation Work. | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Faridpur - 2 | 2023-08-08 12:48 | 2023-08-08 17:20 | 4:32 | S/O | Faridpur SS side work(Joint box replacement). | 0 | 0 | No interruption
|  |  | Total : | 33:17 |  | Unserved Energy: |  | 0
HVDC Grid Circle :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-2 | 2023-08-21 18:33 | 2023-08-21 19:32 | 0:59 | D/W | Due to Maintenance. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-2 | 2023-08-22 06:50 | 2023-08-22 17:30 | 10:40 | D/W | Due to Maintenance. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-3 | 2023-08-12 07:33 | 2023-08-12 10:10 | 2:37 | S/O | Red Hot Maintenance. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-3 | 2023-08-19 06:20 | 2023-08-19 07:28 | 1:08 | D/W | 230kV Bogura(W) Ckt.-3 DS Replacement work. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-3 | 2023-08-25 06:37 | 2023-08-25 10:15 | 3:38 | S/O | Isolator replacement work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-3 | 2023-08-28 05:45 | 2023-08-28 08:39 | 2:54 | S/O | Isolator Replacement Work. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-4 | 2023-08-07 08:50 | 2023-08-07 11:30 | 2:40 | S/O | Isolator arm change | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-4 | 2023-08-28 09:08 | 2023-08-28 12:12 | 3:04 | S/O | 230 kV Bogura(W) Ckt.-4 DS Replacement work. | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai Rahanpur ckt 1 | 2023-08-05 06:51 | 2023-08-08 20:32 | 85:41 | S/O | Project work | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132 kV Chapainawabganj | 2023-08-24 07:45 | 2023-08-24 13:20 | 5:35 | S/O | Due to Maintenance. | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 230 Kv BIPTC Ckt-02 | 2023-08-10 15:11 | 2023-08-10 16:32 | 1:21 | S/O | Due to Maintenance. | 0 | 0 | No interruption | ok
Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 2023-08-21 06:55 | 2023-08-21 19:31 | 12:36 | S/O | CONDUCTOR STRINGING | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 2023-08-22 06:55 | 2023-08-22 17:30 | 10:35 | S/O | Conductor stringing. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 2023-08-23 08:01 | 2023-08-23 17:24 | 9:23 | S/O | Sirajgonj-Sherpur- 132kV Ckt-02 conductor stringing | 0 | 0 | No interruption
|  |  | Total : | 152:51 |  | Unserved Energy: |  | 0
Others :NIL
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 451:02 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:August 2023
| Area | Previous Month (July' 2023) |  |  |  | Current Month (August '2023)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 30 | 10 | 39 | 79 | 19 | 13 | 45 | 77
2 | Dhaka (South) Grid Circle. | 5 | 9 | 10 | 24 | 31 | 21 | 28 | 80
3 | Chattogram Grid Circle. | 6 | 10 | 11 | 27 | 19 | 21 | 12 | 52
4 | Cumilla Grid Circle. | 19 | 46 | 29 | 94 | 27 | 14 | 25 | 66
5 | Khulna Grid Circle. | 10 | 14 | 42 | 66 | 22 | 16 | 50 | 88
6 | HVDC Grid Circle | 7 | 15 | 16 | 38 | 8 | 11 | 9 | 28
7 | Bogura Grid Circle. | 14 | 30 | 31 | 75 | 35 | 41 | 23 | 98
8 | Others | 4 | 5 |  | 9 | 1 | 1 |  | 2
9 | Total | 95 | 139 | 178 | 412 | 162 | 138 | 192 | 491
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:August 2023
| Area | Previous Month (July' 2023) |  |  |  | Current Month (August '2023)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 280.97 | 360.7 | 920.26 | 1561.93 | 253.97 | 427.52 | 2683.2 | 3364.69
2 | Dhaka (South) Grid Circle. | 33 | 280.1 | 151.75 | 464.85 | 4888.5 | 1812.1 | 784.92 | 7485.52
3 | Chattogram Grid Circle. | 0 | 157.08 | 13.67 | 170.75 | 225.52 | 136.1 | 165.63 | 527.25
4 | Cumilla Grid Circle. | 246.9 | 606.98 | 562.23 | 1416.11 | 3209.72 | 663.3 | 474.2 | 4347.22
5 | Khulna Grid Circle. | 73.6 | 251.5 | 292.78 | 617.88 | 433.95 | 356.32 | 785.25 | 1575.52
6 | HVDC Grid Circle | 582.83 | 175.92 | 226.57 | 985.32 | 12 | 197.57 | 376.05 | 585.62
7 | Bogura Grid Circle. | 98.3 | 390.5 | 1589.05 | 2077.85 | 623.23 | 577.98 | 752.83 | 1954.04
8 | Others | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Total | 1315.6 | 2222.78 | 3756.31 | 7294.69 | 9646.89 | 4170.89 | 6022.08 | 19839.86
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:August 2023
A) Power Interruption | [10 empty] | 2 | 1
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 16 | 10 | 26 | 9 | 1 | 16 | 2614.5
2 | Dhaka (South) | 5031.6 | 8 | 6 | 14 |  | 2 | 12 | 2336
3 | Chattogram | 2042 | 15 | 3 | 18 | 4 | 5 | 9 | 516.25
4 | Khulna | 2434 | 27 | 13 | 27 | 14 | 7 | 19 | 1575.47
5 | HVDC | 5954.3 | 4 | 5 | 9 | 1 | 1 | 7 | 585.62 |  |  | 1 | 1
6 | Bogura | 3145.6 | 29 | 5 | 34 | 10 | 8 | 16 | 1821.58
7 | Cumilla | 2981 | 19 | 10 | 29 | 12 | 3 | 14 | 1364.42
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 10813.84
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.87%
3 | Chattogram | 99.93%
4 | Khulna | 99.89%
5 | HVDC | 99.98% | [6 empty] | Executive Engineer
6 | Bogura | 99.9% | [6 empty] | Information Management Division
7 | Cumilla | 99.85% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:August 2023
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 1 | 2 | 3 |  |  | 3 | 750.18
2 | Dhaka (South) | 990.29 | - | 18 | 2 | 20 | 10 | 4 | 6 | 5149.52
3 | Chattogram | 917 | - | 1 | - | 1 | 1 | - | - | 11
4 | Khulna | 1238.4 | - | - | - | - | - | - | - | -
5 | HVDC | 1325 | - | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | 9 | - | 9 | 5 | 1 | 3 | 131.7
7 | Cumilla | 1648.16 | - | 2 |  | 2 | 1 |  | 1 | 2982.8
8 | Others | - | - | - | - | - | - | - | - | -
| Total | 10176.6215 | [7 empty] | 9025.2
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.99%
4 | Khulna | 100%
5 | Bheramara (HVDC) | 100%
6 | Bogura | 99.96%
7 | Cumilla | 99.98%
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:August 2023
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2023-08-01 | 14 | - | 17 | 56hr41 min | 3 | 08hr55 min | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:August 2023
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Dhamrai 132/33kV Grid Sub-Station | 1 | 1:27 | 43.5
Jamalpur 132/33kV Grid Sub-Station | 4 | 8:09 | 312.58
Kabirpur 132/33kV Grid Sub-Station | 1 | 1:44 | 34.6667
Kishoreganj 132/33kV Grid Sub-Station | 2 | 2:21 | 35.03
Sherpur 132/33kV Grid Sub-Station | 3 | 0:26 | 16.43
Tangail 132/33kV Grid Sub-Station | 5 | 2:14 | 84.42
Joydebpur 132/33kV Grid Sub-Station | 1 | 2:43 | 154.85
Bhaluka 132/33kV Grid Sub-Station | 1 | 3:56 | 255.6667
Dhamrai 132/33kV Grid Sub-Station | 1 | 3:30 | 105
Jamalpur 132/33kV Grid Sub-Station | 1 | 5:58 | 119.3333
Kabirpur 132/33kV Grid Sub-Station | 2 | 3:36 | 292.87
Kaliakoir 400/230/132kV Grid Sub-Station | 1 | 2:32 | 684
Mymensingh 132/33kV Grid Sub-Station | 2 | 3:50 | 542.5
Tangail 132/33kV Grid Sub-Station | 2 | 3:36 | 88.5
Mymensingh- Bhaluka 132 kV Ckt- 02 | 1 | 4:37 | 184.6667
132KV PPM Jamalpur Power Plant | 1 | 2:20 | 81.3333
Joydebpur 132/33kV Grid Sub-Station | 1 | 4:07 | 329.3333
Bhulta 132/33kV Grid Sub-Station | 3 | 32:27 | 1577.8
Narshingdi 132/33kV Grid Sub-Station | 1 | 2:28 | 115.9333
Rampura 230/132kV Grid Sub-Station | 1 | 1:01 | 20.3333
Sonargaon 132/33kV Grid Sub-Station | 3 | 4:10 | 117.3
Gulshan 132/33kV Grid Sub-Station | 1 | 0:42 | 36.4
Haripur 230/132kV Grid Sub-Station | 4 | 1:07 | 58.58
Hasnabad 132/33kV Grid Substation | 1 | 0:18 | 6
Maniknagar 230/132kV Grid Sub-Station | 1 | 2:27 | 784
Rampura 230/132kV Grid Sub-Station | 2 | 0:26 | 13
Shitalakhya 132/33kV Grid Sub-Station | 5 | 31:40 | 2851.5
Siddhirganj 230/132kV Grid Sub-Station | 4 | 5:02 | 1119.75
Bhulta 132/33kV Grid Sub-Station | 1 | 0:59 | 68.8333
Narshingdi 132/33kV Grid Sub-Station | 1 | 1:38 | 81.6667
Nawabganj 132/33kV Grid Sub-Station | 2 | 9:18 | 237.2
Sonargaon 132/33kV Grid Sub-Station | 2 | 3:32 | 116.9
Haripur 230/132kV Grid Sub-Station | 2 | 4:38 | 280.4
Baroirhat 132/33kV Grid Sub-Station | 2 | 3:11 | 60.2
Chandraghona 132/33kV Grid Sub-Station | 2 | 0:46 | 12.8
Dohazari 132/33kV Grid Sub-Station | 4 | 2:24 | 48.4
Halishahar 132/33kV Grid Sub-Station | 2 | 1:10 | 2.9
Hathazari 230/132/33kV Grid Sub-Station | 1 | 2:03 | 90.2
Khulshi 132/33kV Grid Sub-Station | 1 | 0:44 | 61.6
Madunaghat 132/33kV Grid Sub-Station | 2 | 1:59 | 59.8
TK chemical 132kV Grid Sub-Station | 1 | 0:36 | 14.7
Dohazari 132/33kV Grid Sub-Station | 1 | 0:11 | 11
Bakulia 132/33kV Grid Sub-Station | 1 | 2:12 | 19.8
Dohazari 132/33kV Grid Sub-Station | 2 | 4:22 | 145.8
Beanibazar 132/33kV Grid Sub-Station | 2 | 6:55 | 138.3
Brahmanbaria 132/33kV Grid Sub-Station | 1 | 0:10 | 10
Chowmuhani 132/33kV Grid Sub-Station | 5 | 18:23 | 551
Cumilla(S) 132/33kV Grid Sub-Station | 7 | 4:10 | 99.2
Shahjibazar 132/33kV Grid Sub-Station | 1 | 0:04 | 2.1333
Sreemongol 132/33kV Grid Sub-Station | 1 | 0:04 | 2.3333
Sylhet 132/33kV Grid Sub-Station | 2 | 1:59 | 87.2
Chowmuhani 132/33kV Grid Sub-Station | 2 | 53:30 | 2982.8
Beanibazar 132/33kV Grid Sub-Station | 2 | 7:34 | 137.5
Chhatak 132/33kV Grid Sub-Station | 1 | 0:52 | 0.86667
Cumilla(S) 132/33kV Grid Sub-Station | 1 | 1:30 | 30
Daudkandi 132/33kV Grid Sub-Station | 2 | 6:32 | 98
Kulaura 132/33kV Grid Sub-Station | 1 | 4:58 | 124.1667
Shahjibazar 132/33kV Grid Sub-Station | 1 | 0:34 | 22.6667
Sylhet 132/33kV Grid Sub-Station | 2 | 3:20 | 61
Bagerhat 132/33kV Grid Sub-Station | 2 | 0:24 | 6.8
Barishal 132/33kV Grid Sub-Station | 6 | 9:43 | 325.02
Benapole 132/33kV Grid Sub-Station | 1 | 1:49 | 36.3333
Bhandaria 132/33kV Grid Sub-Station | 2 | 2:44 | 33.97
Faridpur 132/33kV Grid Sub-Station | 9 | 4:20 | 199.08
Gollamari 132/33kV Grid Sub-Station | 2 | 0:48 | 17.6
Mongla 132/33kV Grid Sub-Station | 2 | 3:29 | 41.8
Satkhira 132/33kV Grid Sub-Station | 3 | 2:15 | 129.67
Bagerhat 132/33kV Grid Sub-Station | 1 | 2:56 | 73.3333
Barishal 132/33kV Grid Sub-Station | 1 | 0:40 | 20
Bhandaria 132/33kV Grid Sub-Station | 1 | 0:09 | 1.5
Gopalganj 132/33kV Grid Sub-Station | 1 | 7:55 | 151.83
Narail 132/33kV Grid Sub-Station | 2 | 5:37 | 79.92
Noapara 132/33kV Grid Sub-Station | 2 | 12:25 | 340.47
Patuakhali 132/33kV Grid Sub-Station | 1 | 5:38 | 45.0667
Satkhira 132/33kV Grid Sub-Station | 1 | 2:01 | 50.4167
Shariatpur 132/33kV Grid Sub-Station | 2 | 2:16 | 22.67
Jhenaidah 132/33kV Grid Sub-Station | 1 | 0:15 | 12
Kushtia 132/33kV Grid Sub-Station | 2 | 3:59 | 180.2
Shahjadpur 132/33kV Grid Sub-Station | 1 | 1:27 | 17.4
Bheramara(GK) 132/33kV Grid Sub-Station | 1 | 1:29 | 32.6333
Ishurdi 132/33kV Grid Sub-Station | 2 | 5:57 | 161.1
Kushtia 132/33kV Grid Sub-Station | 1 | 3:10 | 110.8333
Pabna 132/33kV Grid Sub-Station | 1 | 2:23 | 71.5
Bog-Sherpur 132/33kV Grid Sub-Station | 3 | 1:37 | 101.37
Jaldhaka 132/33kV Grid Sub-Station | 4 | 5:21 | 95.6
Naogaon 132/33kV Grid Sub-Station | 10 | 13:51 | 534.63
Niamatpur 132/33kV Grid Sub-Station | 1 | 1:28 | 26.4
Panchagarh 132/33kV Grid Sub-Station | 1 | 0:35 | 9.3333
Purbasadipur 132/33kV Grid Sub-Station | 2 | 1:19 | 41
Rajshahi 132/33kV Grid Sub-Station | 2 | 3:17 | 104.7
Sirajganj 132/33kV Grid Sub-Station | 4 | 5:22 | 144.4
Thakurgaon 132/33kV Grid Sub-Station | 3 | 0:37 | 12.1
Amnura 132/33kV Grid Sub-Station | 2 | 504:41 | 5.7
Bog-Sherpur 132/33kV Grid Sub-Station | 2 | 169:32 | 45.2
Chapai 132/33kV Grid Sub-Station | 1 | 0:11 | 19.4333
Mahasthangarh 132/33kV Grid Sub-Station | 1 | 0:32 | 21.3333
Rangpur 132/33kV Grid Sub-Station | 3 | 0:50 | 40
Bogura 132/33kV Grid Sub-Station | 2 | 5:57 | 602.95
Mahasthangarh 132/33kV Grid Sub-Station | 1 | 2:23 | 35.75
Naogaon 132/33kV Grid Sub-Station | 1 | 2:24 | 100.8
Saidpur 132/33kV Grid Sub-Station | 1 | 1:20 | 13.3333
Total Unserved energy : | 206 | 1094:18 | 19839.8233
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:August 2023
Sl. No | Name | date_time | ss_MW
1 | Aftabnagar 132/33kV Grid Sub-Station | 2023-08-21 13:00 | 62
2 | Agargaon 230/132kV Grid Sub-Station | 2023-08-01 13:00 | 107
3 | Banani 132/33kV Grid Sub-Station | 2023-08-30 12:00 | 85.4
4 | Bangabhaban 132/33kV Grid Sub-Station | 2023-08-01 10:00 | 22
5 | Bashundhara 132/33kV Grid Sub-Station | 2023-08-28 15:00 | 185
6 | BashundharaCement 132/33kV Sub-Station | 2023-08-02 13:00 | 6
7 | Bhulta 132/33kV Grid Sub-Station | 2023-08-12 15:00 | 280
8 | Cantonment 132/33kV GIS Grid Sub-Station | 2023-08-01 13:00 | 171
9 | Charsaidpur 132/33kV Sub-Station | 2023-08-16 10:00 | 50
10 | Dhaka University 132/33kV Grid Sub-Station | 2023-08-28 13:00 | 48
11 | Dhamrai 132/33kV Grid Sub-Station | 2023-08-21 19:00 | 136
12 | Dhanmondi 132/33kV Grid Sub-Station | 2023-08-21 13:00 | 168
13 | Fatullah 132/33kV Grid Sub-Station | 2023-08-23 18:30 | 78
14 | Ghorashal 230/132/33kV Sub-Station | 2023-08-05 22:00 | 81
15 | Gulshan 132/33kV Grid Sub-Station | 2023-08-01 12:00 | 148
16 | HaripurSBU 132/33kV Sub-Station | 2023-08-10 10:00 | 166
17 | Hasnabad 132/33kV Grid Substation | 2023-08-01 20:00 | 123
18 | Joydebpur 132/33kV Grid Sub-Station | 2023-08-21 19:30 | 190
19 | Kabirpur 132/33kV Grid Sub-Station | 2023-08-21 10:00 | 308
20 | Kallyanpur 132/33kV Grid Sub-Station | 2023-08-28 16:00 | 123
21 | Kamrangirchar 132/33kV Grid Sub-Station | 2023-08-28 13:00 | 72
22 | Kazla 132/33kV Grid Sub-Station | 2023-08-02 21:00 | 96
23 | Keranigonj 230/132/33kV Grid Sub-Station | 2023-08-17 19:30 | 78
24 | Kodda 132/33kV Grid Sub-Station | 2023-08-12 19:00 | 307
25 | Lalbag 132/33kV Grid Sub-Station | 2023-08-28 13:00 | 98
26 | Madanganj 132/33kV Grid Sub-Station | 2023-08-30 | 46
27 | Madartek 132/33kV Grid Sub-Station | 2023-08-30 23:00 | 96.62
28 | Manikganj 132/33kV Grid Sub-Station | 2023-08-30 19:00 | 131
29 | Maniknagar 132/33kV Grid Sub-Station | 2023-08-01 13:00 | 110
30 | Matuail 132/33kV Grid Sub-Station | 2023-08-29 10:00 | 76
31 | Millgate Tongi 132/33kV Grid Sub-Station | 2023-08-17 12:00 | 117
32 | Mirpur 132/33kV Grid Sub-Station | 2023-08-30 19:00 | 149
33 | Mogbazar 132/33kV Grid Sub-Station | 2023-08-01 13:00 | 147
34 | Motijheel 132/33kV Grid Sub-Station | 2023-08-28 13:00 | 47
35 | Munshiganj 132/33kV Grid Sub-Station | 2023-08-17 23:00 | 111
36 | Narinda 132/33kV Grid Sub-Station | 2023-08-01 16:00 | 92
37 | Narshingdi 132/33kV Grid Sub-Station | 2023-08-30 19:30 | 191
38 | Nawabganj 132/33kV Grid Sub-Station | 2023-08-01 23:00 | 57.4
39 | New Tongi 132/33kV Grid Sub-Station | 2023-08-01 12:00 | 88
40 | Postogola 132/33kV Grid Sub-Station | 2023-08-09 15:00 | 66
41 | Purbachal 132/33kV Grid Sub-Station | 2023-08-30 15:00 | 24
42 | Rahim Steel 132/33kV Sub-Station | 2023-08-09 08:00 | 50
43 | Rajendrapur 132/33kV Grid Sub-Station | 2023-08-19 19:30 | 108
44 | Satmasjid 132/33kV Grid Sub-Station | 2023-08-30 19:00 | 123
45 | Savar 132/33kV Grid Sub-Station | 2023-08-17 18:30 | 204
46 | Shitalakhya 132/33kV Grid Sub-Station | 2023-08-17 16:00 | 110
47 | Shyampur 132/33kV Grid Sub-Station | 2023-08-24 09:00 | 176
48 | Siddhirganj 132/33kV Grid Sub-Station | 2023-08-25 14:00 | 138
49 | Sonargaon 132/33kV Grid Sub-Station | 2023-08-30 22:00 | 110
50 | Sreepur 230/132/33kV Grid Sub-Station | 2023-08-29 15:00 | 84
51 | Srinagar 132/33kV Grid Sub-Station | 2023-08-20 21:00 | 50.6
52 | Tongi 230/132/33kV Grid Sub-Station | 2023-08-16 12:00 | 146
53 | Ullon 132/33kV Grid Sub-Station | 2023-08-16 23:00 | 54
54 | Uttara 132/33kV Grid Sub-Station | 2023-08-21 16:00 | 89
55 | UttaraNew 132/33kV Grid Sub-Station | 2023-08-01 13:00 | 73
56 | Zigatola 132/33kV Grid Sub-Station | 2023-08-01 12:00 | 94
57 | Agrabad 132/33kV Grid Sub-Station | 2023-08-05 14:00 | 94
58 | AKS 132/33kV Grid Sub-Station | 2023-08-01 01:00 | 16
59 | AKSML 230/33kV Grid Sub-Station | 2023-08-15 07:00 | 115
60 | Bakulia 132/33kV Grid Sub-Station | 2023-08-01 11:00 | 106
61 | Baroaulia 132/33kV Grid Sub-Station | 2023-08-17 | 79
62 | Baroirhat 132/33kV Grid Sub-Station | 2023-08-17 19:00 | 71
63 | BSRM 230/33kV Grid Sub-Station | 2023-08-31 18:30 | 190
64 | Chandraghona 132/33kV Grid Sub-Station | 2023-08-18 19:00 | 33
65 | Coxsbazar 132/33kV Grid Sub-Station | 2023-08-16 21:00 | 130
66 | Dohazari 132/33kV Grid Sub-Station | 2023-08-02 22:00 | 110
67 | GPH 230/33kV Grid Sub-Station | 2023-08-05 12:00 | 93
68 | Halishahar 132/33kV Grid Sub-Station | 2023-08-01 09:00 | 81
69 | Hathazari 230/132/33kV Grid Sub-Station | 2023-08-17 19:00 | 83
70 | Juldah 132/33kV Grid Sub-Station | 2023-08-19 13:00 | 28
71 | Kalurghat 132/33kV Grid Sub-Station | 2023-08-16 15:00 | 36
72 | Khagrachori 132/33kV Grid Sub-Station | 2023-08-19 19:00 | 36
73 | Khulshi 132/33kV Grid Sub-Station | 2023-08-30 18:30 | 189
74 | KSRM 132/33kV Grid Sub-Station | 2023-08-09 04:00 | 58.5
75 | Madunaghat 132/33kV Grid Sub-Station | 2023-08-16 19:30 | 56
76 | Matarbari 132/33kV Sub-Station | 2023-08-14 19:00 | 50
77 | Mirsorai 230/33kV Grid Sub-Station | 2023-08-03 21:00 | 4.9
78 | Modern Steel 132/11kV Grid Sub-Station | 2023-08-28 10:00 | 0.2
79 | Rampur 230/132/33 kV GIS Grid Sub-Station | 2023-08-30 19:30 | 38
80 | Rangamati 132/33kV Grid Sub-Station | 2023-08-01 19:30 | 20
81 | Shahmirpur 132/33kV Grid Sub-Station | 2023-08-17 23:00 | 77
82 | Shikalbaha 132/33kV Sub-Station | 2023-08-12 19:00 | 44
83 | Sholosohor 132/33kV Grid Sub-Station | 2023-08-19 09:00 | 41
84 | SSM 132/33kV Grid Sub-Station | 2023-08-29 14:00 | 16
85 | TK chemical 132kV Grid Sub-Station | 2023-08-30 20:00 | 32.5
86 | Ashuganj 230/132/33kV Sub-Station | 2023-08-03 | 89
87 | Brahmanbaria 132/33kV Grid Sub-Station | 2023-08-23 22:00 | 170
88 | Chandpur 132/33kV Grid Sub-Station | 2023-08-15 21:00 | 78
89 | Chauddagram 132/33kV Grid Sub-Station | 2023-08-29 22:00 | 66
90 | Chowmuhani 132/33kV Grid Sub-Station | 2023-08-19 20:00 | 232
91 | Cumilla(N) 230/132/33kV Grid Sub-Station | 2023-08-20 21:00 | 201
92 | Cumilla(S) 132/33kV Grid Sub-Station | 2023-08-29 18:30 | 179
93 | Daudkandi 132/33kV Grid Sub-Station | 2023-08-30 18:30 | 153
94 | Feni 132/33kV Grid Sub-Station | 2023-08-17 22:00 | 128
95 | Kachua 132/33kV Grid Sub-Station | 2023-08-30 19:30 | 99
96 | PHP 132/33kV Sub-Station | 2023-08-10 17:00 | 11
97 | Ramganj 132/33kV Grid Sub-Station | 2023-08-02 22:00 | 118
98 | Bhaluka 132/33kV Grid Sub-Station | 2023-08-19 10:00 | 150
99 | Jamalpur 132/33kV Grid Sub-Station | 2023-08-31 22:00 | 179
100 | Kishoreganj 132/33kV Grid Sub-Station | 2023-08-01 20:00 | 156
101 | Mymensingh 132/33kV Grid Sub-Station | 2023-08-01 | 243
102 | Netrakona 132/33kV Grid Sub-Station | 2023-08-30 22:00 | 146
103 | Sherpur 132/33kV Grid Sub-Station | 2023-08-19 19:00 | 164
104 | Tangail 132/33kV Grid Sub-Station | 2023-08-29 19:30 | 250
105 | Beanibazar 132/33kV Grid Sub-Station | 2023-08-01 19:00 | 82
106 | Chhatak 132/33kV Grid Sub-Station | 2023-08-18 22:00 | 38
107 | Fenchuganj 230/132/33kV Grid Sub-Station | 2023-08-29 19:00 | 51
108 | Kulaura 132/33kV Grid Sub-Station | 2023-08-18 23:00 | 58
109 | Shahjibazar 132/33kV Grid Sub-Station | 2023-08-14 23:00 | 134
110 | Sreemongol 132/33kV Grid Sub-Station | 2023-08-19 21:00 | 76
111 | Sunamganj 132/33kV Grid Sub-Station | 2023-08-17 20:00 | 61
112 | Sylhet 132/33kV Grid Sub-Station | 2023-08-17 18:30 | 182
113 | Bagerhat 132/33kV Grid Sub-Station | 2023-08-16 23:00 | 97
114 | Benapole 132/33kV Grid Sub-Station | 2023-08-27 21:00 | 72
115 | Bheramara(GK) 132/33kV Grid Sub-Station | 2023-08-21 19:00 | 71
116 | Chuadanga 132/33kV Grid Sub-Station | 2023-08-31 19:00 | 123
117 | Faridpur 132/33kV Grid Sub-Station | 2023-08-06 13:00 | 184
118 | Goalpara 132/33kV Grid Sub-Station | 2023-08-03 13:00 | 38
119 | Gollamari 132/33kV Grid Sub-Station | 2023-08-31 08:00 | 62
120 | Gopalganj 132/33kV Grid Sub-Station | 2023-08-30 22:00 | 112
121 | Jashore 132/33kV Grid Sub-Station | 2023-08-02 19:30 | 155
122 | Jhenaidah 132/33kV Grid Sub-Station | 2023-08-20 20:00 | 142
123 | Khulna (C) 132/33kV Grid Sub-Station | 2023-08-30 21:00 | 108
124 | Kushtia 132/33kV Grid Sub-Station | 2023-08-19 19:30 | 156
125 | Madaripur 132/33kV Grid Sub-Station | 2023-08-30 22:00 | 118
126 | Magura 132/33kV Grid Sub-Station | 2023-08-27 21:00 | 69
127 | Mongla 132/33kV Grid Sub-Station | 2023-08-03 12:00 | 40
128 | Narail 132/33kV Grid Sub-Station | 2023-08-30 19:30 | 64
129 | Noapara 132/33kV Grid Sub-Station | 2023-08-30 19:00 | 53
130 | Rajbari 132/33kV Grid Sub-Station | 2023-08-21 19:30 | 80
131 | Satkhira 132/33kV Grid Sub-Station | 2023-08-30 22:00 | 133
132 | Shariatpur 132/33kV Grid Sub-Station | 2023-08-30 22:00 | 91
133 | Barguna 132/33kV Grid Sub-Station | 2023-08-03 22:00 | 22
134 | Barishal 132/33kV Grid Sub-Station | 2023-08-21 21:00 | 112
135 | Barishal 230/132kV Grid Sub-Station | 2023-08-30 22:00 | 112
136 | Bhandaria 132/33kV Grid Sub-Station | 2023-08-20 22:00 | 54
137 | Borhanuddin 230/33kV Grid Sub-Station | 2023-08-16 23:00 | 70
138 | Patuakhali 132/33kV Grid Sub-Station | 2023-08-30 22:00 | 117
139 | Payra 400/132/33kV Grid Sub-Station | 2023-08-23 21:00 | 31.2
140 | Amnura 132/33kV Grid Sub-Station | 2023-08-03 21:00 | 73
141 | Bhangura 132/33kV Grid Sub-Station | 2023-08-28 20:00 | 40
142 | Bog-Sherpur 132/33kV Grid Sub-Station | 2023-08-01 19:30 | 86
143 | Bogura 132/33kV Grid Sub-Station | 2023-08-17 20:00 | 189
144 | Chapai 132/33kV Grid Sub-Station | 2023-08-01 23:00 | 83
145 | Ishurdi 132/33kV Grid Sub-Station | 2023-08-17 19:30 | 84
146 | Joypurhat 132/33kV Grid Sub-Station | 2023-08-01 19:30 | 69
147 | Mahasthangarh 132/33kV Grid Sub-Station | 2023-08-03 06:00 | 120
148 | Naogaon 132/33kV Grid Sub-Station | 2023-08-01 22:00 | 158
149 | Natore 132/33kV Grid Sub-Station | 2023-08-21 22:00 | 173
150 | Niamatpur 132/33kV Grid Sub-Station | 2023-08-01 13:00 | 100
151 | Pabna 132/33kV Grid Sub-Station | 2023-08-17 21:00 | 130
152 | Rajshahi 132/33kV Grid Sub-Station | 2023-08-29 23:00 | 179
153 | Rajshahi 230/132/33kV Grid Sub-Station | 2023-08-20 23:00 | 45
154 | Ruppur 132/11kV Grid Sub-Station | 2023-08-17 16:00 | 6.2
155 | Shahjadpur 132/33kV Grid Sub-Station | 2023-08-30 20:00 | 120
156 | Sirajganj 132/33kV Grid Sub-Station | 2023-08-01 21:00 | 130
157 | Barapukuria 230/132/33kV Grid Sub-Station | 2023-08-01 19:30 | 76
158 | Jaldhaka 132/33kV Grid Sub-Station | 2023-08-18 21:00 | 84
159 | Kurigram 132/33kV Grid Sub-Station | 2023-08-02 19:00 | 72
160 | Lalmonirhat 132/33kV Grid Sub-Station | 2023-08-31 19:00 | 62
161 | Mithapukur 132/33kV Grid Sub-Station | 2023-08-02 | 62
162 | Palashbari 132/33kV Grid Sub-Station | 2023-08-19 21:00 | 152
163 | Panchagarh 132/33kV Grid Sub-Station | 2023-08-01 20:00 | 64
164 | Purbasadipur 132/33kV Grid Sub-Station | 2023-08-01 12:00 | 165
165 | Rangpur 132/33kV Grid Sub-Station | 2023-08-30 20:00 | 161
166 | Saidpur 132/33kV Grid Sub-Station | 2023-08-01 23:00 | 125
167 | Thakurgaon 132/33kV Grid Sub-Station | 2023-08-01 01:00 | 114
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
Note on A7: MIDT:

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:August 2023
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 5239.7 | 2023-08-21 | 19:00
Chattogram | 1499 | 2023-08-29 | 21:00
Cumilla | 1390 | 2023-08-29 | 21:00
Mymensingh | 1177 | 2023-08-15 | 19:30
Sylhet | 624 | 2023-08-19 | 20:00
Khulna | 1790.6 | 2023-08-28 | 20:00
Barishal | 496.4 | 2023-08-21 | 22:00
Rajshahi | 1620.4 | 2023-08-01 | 21:00
Rangpur | 1037 | 2023-08-01 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month:August 2023
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar 400/230/132kV Grid Sub-Station | 400 | 408 | 2023-08-04 17:00 | 383 | 2023-08-12 12:00
2 | Bhulta 400/230kV Grid Sub-Station | 400 | 399 | 2023-08-07 05:00 | 379 | 2023-08-31 09:00
3 | Bibiana 400/230kV Sub-Station | 400 | 408 | 2023-08-08 20:00 | 390 | 2023-08-30 12:00
4 | BIPTC | 400 | 408 | 2023-08-18 06:00 | 386 | 2023-08-21 16:00
5 | Gopalganj 400/132kV Grid Sub-Station | 400 | 411 | 2023-08-10 08:00 | 368 | 2023-08-02 12:00
6 | Kaliakoir 400/230/132kV Grid Sub-Station | 400 | 388 | 2023-08-25 05:00 | 353 | 2023-08-21 19:30
7 | Madunaghat_I 400/230kV Grid Sub-Station | 400 | 400 | 2023-08-03 19:30 | 365 | 2023-08-22 18:30
8 | Payra 400kV Sub-Station | 400 | 416 | 2023-08-25 15:00 | 404 | 2023-08-12 15:00
9 | Rampal 400/230kV Grid Sub-Station | 400 | 413 | 2023-08-10 06:00 | 390 | 2023-08-11 20:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon 230/132kV Grid Sub-Station | 230 | 236 | 2023-08-04 14:00 | 221 | 2023-08-20 17:00
2 | AKSML 230/33kV Grid Sub-Station | 230 | 241 | 2023-08-08 19:00 | 216 | 2023-08-22 13:00
3 | Baghabari 230/132kV Grid Sub-Station | 230 | 233 | 2023-08-25 09:00 | 215 | 2023-08-20 19:00
4 | Barapukuria 230/132/33kV Grid Sub-Station | 230 | 225 | 2023-08-25 15:00 | 203 | 2023-08-29 19:00
5 | Barishal 230/132kV Grid Sub-Station | 230 | 241 | 2023-08-12 20:00 | 229 | 2023-08-08 19:30
6 | Bheramara 230/132kV Grid Sub-Station | 230 | 255 | 2023-08-09 13:00 | 216 | 2023-08-21 14:00
7 | Bogura 230/132kV Grid Sub-Station | 230 | 233 | 2023-08-01 18:00 | 208 | 2023-08-29 22:00
8 | BSRM 230/33kV Grid Sub-Station | 230 | 239 | 2023-08-11 19:30 | 219 | 2023-08-22 16:00
9 | Cumilla(N) 230/132/33kV Grid Sub-Station | 230 | 233 | 2023-08-04 14:00 | 220 | 2023-08-30 19:00
10 | Fenchuganj 230/132/33kV Grid Sub-Station | 230 | 238 | 2023-08-10 08:00 | 227 | 2023-08-01 15:00
11 | Ghorashal 230/132/33kV Sub-Station | 230 | 240 | 2023-08-04 15:00 | 225 | 2023-08-06 07:00
12 | GPH 230/33kV Grid Sub-Station | 230 | 239 | 2023-08-19 07:00 | 218 | 2023-08-22 13:00
13 | Haripur 230/132kV Grid Sub-Station | 230 | 235 | 2023-08-04 14:00 | 221 | 2023-08-31 09:00
14 | Hasnabad 230/132kV Grid Sub-Station | 230 | 235 | 2023-08-04 13:00 | 219 | 2023-08-31 07:00
15 | Hathazari 230/132/33kV Grid Sub-Station | 230 | 239 | 2023-08-10 21:00 | 218 | 2023-08-22 12:00
16 | Ishurdi 230/132kV Grid Sub-Station | 230 | 239 | 2023-08-02 01:00 | 217 | 2023-08-21 12:00
17 | Jhenaidah 230/132kV Grid Sub-Station | 230 | 231 | 2023-08-25 08:00 | 202 | 2023-08-21
18 | Keranigonj 230/132/33kV Grid Sub-Station | 230 | 235 | 2023-08-04 14:00 | 220 | 2023-08-21 12:00
19 | Khulna(S) 230/132kV Grid Sub-Station | 230 | 238 | 2023-08-25 15:00 | 220 | 2023-08-13 19:00
20 | Maniknagar 230/132kV Grid Sub-Station | 230 | 234 | 2023-08-04 14:00 | 220 | 2023-08-21 12:00
21 | Meghnaghat 230/132kV Grid Sub-Station | 230 | 240 | 2023-08-04 18:00 | 224 | 2023-08-31 09:00
22 | Mirsorai 230/33kV Grid Sub-Station | 230 | 239 | 2023-08-03 19:30 | 215 | 2023-08-22 16:00
23 | Rajshahi 230/132/33kV Grid Sub-Station | 230 | 234 | 2023-08-31 | 208 | 2023-08-21 14:00
24 | Rampura 230/132kV Grid Sub-Station | 230 | 235 | 2023-08-04 14:00 | 220 | 2023-08-31 09:00
25 | Shikalbaha 230/132kV Grid Sub-Station | 230 | 238 | 2023-08-09 19:30 | 218 | 2023-08-22 13:00
26 | Shyampur 230/132kV Grid Sub-Station | 230 | 235 | 2023-08-04 14:00 | 220 | 2023-08-21 12:00
27 | Siddhirganj 230/132kV Grid Sub-Station | 230 | 238 | 2023-08-07 03:00 | 223 | 2023-08-21 12:00
28 | Sirajgonj 230 kV Switching Station | 230 | 239 | 2023-08-01 18:00 | 225 | 2023-08-21 14:00
29 | Sreepur 230/132/33kV Grid Sub-Station | 230 | 234 | 2023-08-25 15:00 | 220 | 2023-08-21 15:00
30 | Tongi 230/132/33kV Grid Sub-Station | 230 | 234 | 2023-08-04 07:00 | 218 | 2023-08-31 08:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar 132/33kV Grid Sub-Station | 132 | 138 | 2023-08-28 06:00 | 126 | 2023-08-16 10:00
2 | Agrabad 132/33kV Grid Sub-Station | 132 | 139 | 2023-08-05 21:00 | 124 | 2023-08-22 12:00
3 | AKS 132/33kV Grid Sub-Station | 132 | 137 | 2023-08-06 19:00 | 124 | 2023-08-22 12:00
4 | Amnura 132/33kV Grid Sub-Station | 132 | 143 | 2023-08-14 18:00 | 116 | 2023-08-30 22:00
5 | Ashuganj 230/132/33kV Sub-Station | 132 | 140 | 2023-08-01 18:00 | 125 | 2023-08-31 10:00
6 | Bagerhat 132/33kV Grid Sub-Station | 132 | 139 | 2023-08-01 13:00 | 119 | 2023-08-21 19:00
7 | Bakulia 132/33kV Grid Sub-Station | 132 | 141 | 2023-08-01 13:00 | 126 | 2023-08-22 13:00
8 | Banani 132/33kV Grid Sub-Station | 132 | 139 | 2023-08-28 06:00 | 124 | 2023-08-30 13:00
9 | Bangabhaban 132/33kV Grid Sub-Station | 132 | 137 | 2023-08-02 19:00 | 125 | 2023-08-21 12:00
10 | Barguna 132/33kV Grid Sub-Station | 132 | 141 | 2023-08-01 23:00 | 129 | 2023-08-18 22:00
11 | Barishal 132/33kV Grid Sub-Station | 132 | 140 | 2023-08-01 20:00 | 127 | 2023-08-15 22:00
12 | Baroaulia 132/33kV Grid Sub-Station | 132 | 140 | 2023-08-03 21:00 | 126 | 2023-08-22 17:00
13 | Baroirhat 132/33kV Grid Sub-Station | 132 | 138 | 2023-08-20 18:00 | 120 | 2023-08-30 18:30
14 | Bashundhara 132/33kV Grid Sub-Station | 132 | 138 | 2023-08-12 01:00 | 123 | 2023-08-31 09:00
15 | BashundharaCement 132/33kV Sub-Station | 132 | 136 | 2023-08-28 18:00 | 125 | 2023-08-07 16:00
16 | Beanibazar 132/33kV Grid Sub-Station | 132 | 131 | 2023-08-12 17:00 | 121 | 2023-08-01 04:00
17 | Benapole 132/33kV Grid Sub-Station | 132 | 139 | 2023-08-25 10:00 | 120 | 2023-08-20 19:00
18 | Bhaluka 132/33kV Grid Sub-Station | 132 | 130 | 2023-08-01 15:00 | 115 | 2023-08-21 14:00
19 | Bhandaria 132/33kV Grid Sub-Station | 132 | 142 | 2023-08-01 20:00 | 123 | 2023-08-15 22:00
20 | Bhangura 132/33kV Grid Sub-Station | 132 | 140 | 2023-08-28 12:00 | 125 | 2023-08-20 19:00
21 | Bheramara(GK) 132/33kV Grid Sub-Station | 132 | 136 | 2023-08-02 06:00 | 121 | 2023-08-21 12:00
22 | Bhulta 132/33kV Grid Sub-Station | 132 | 130 | 2023-08-29 07:00 | 118 | 2023-08-01 16:00
23 | Bog-Sherpur 132/33kV Grid Sub-Station | 132 | 139 | 2023-08-25 10:00 | 113 | 2023-08-21 15:00
24 | Bogura 132/33kV Grid Sub-Station | 132 | 140 | 2023-08-01 18:00 | 113 | 2023-08-19 21:00
25 | Brahmanbaria 132/33kV Grid Sub-Station | 132 | 134 | 2023-08-29 01:00 | 119 | 2023-08-14 22:00
26 | Cantonment 132/33kV GIS Grid Sub-Station | 132 | 135 | 2023-08-04 14:00 | 124 | 2023-08-21 12:00
27 | Chandpur 132/33kV Grid Sub-Station | 132 | 142 | 2023-08-01 12:00 | 114 | 2023-08-15 01:00
28 | Chandraghona 132/33kV Grid Sub-Station | 132 | 140 | 2023-08-03 19:30 | 129 | 2023-08-22 12:00
29 | Chapai 132/33kV Grid Sub-Station | 132 | 136 | 2023-08-01 18:00 | 119 | 2023-08-29 23:00
30 | Charsaidpur 132/33kV Sub-Station | 132 | 137 | 2023-08-28 18:00 | 126 | 2023-08-08 12:00
31 | Chauddagram 132/33kV Grid Sub-Station | 132 | 136 | 2023-08-01 11:00 | 117 | 2023-08-31 07:00
32 | Chhatak 132/33kV Grid Sub-Station | 132 | 132 | 2023-08-28 06:00 | 120 | 2023-08-01 19:00
33 | Chowmuhani 132/33kV Grid Sub-Station | 132 | 135 | 2023-08-01 11:00 | 113 | 2023-08-16
34 | Chuadanga 132/33kV Grid Sub-Station | 132 | 136 | 2023-08-25 16:00 | 115 | 2023-08-20 22:00
35 | Coxsbazar 132/33kV Grid Sub-Station | 132 | 137 | 2023-08-01 14:00 | 113 | 2023-08-21 18:30
36 | Cumilla(S) 132/33kV Grid Sub-Station | 132 | 138 | 2023-08-01 13:00 | 123 | 2023-08-29 13:00
37 | Daudkandi 132/33kV Grid Sub-Station | 132 | 135 | 2023-08-01 13:00 | 124 | 2023-08-08
38 | Dhaka University 132/33kV Grid Sub-Station | 132 | 138 | 2023-08-28 03:00 | 126 | 2023-08-21 12:00
39 | Dhamrai 132/33kV Grid Sub-Station | 132 | 140 | 2023-08-10 07:00 | 126 | 2023-08-20 17:00
40 | Dhanmondi 132/33kV Grid Sub-Station | 132 | 136 | 2023-08-07 04:00 | 125 | 2023-08-21 12:00
41 | Dohazari 132/33kV Grid Sub-Station | 132 | 140 | 2023-08-01 13:00 | 121 | 2023-08-22 17:00
42 | Faridpur 132/33kV Grid Sub-Station | 132 | 133 | 2023-08-12 06:00 | 122 | 2023-08-21 12:00
43 | Fatullah 132/33kV Grid Sub-Station | 132 | 133 | 2023-08-04 19:30 | 122 | 2023-08-31 09:00
44 | Feni 132/33kV Grid Sub-Station | 132 | 140 | 2023-08-21 18:00 | 118 | 2023-08-31 07:00
45 | Goalpara 132/33kV Grid Sub-Station | 132 | 141 | 2023-08-02 18:00 | 126 | 2023-08-20 22:00
46 | Gollamari 132/33kV Grid Sub-Station | 132 | 141 | 2023-08-29 03:00 | 127 | 2023-08-16 01:00
47 | Gopalganj 132/33kV Grid Sub-Station | 132 | 137 | 2023-08-05 18:00 | 124 | 2023-08-30 22:00
48 | Gulshan 132/33kV Grid Sub-Station | 132 | 138 | 2023-08-28 06:00 | 125 | 2023-08-21 13:00
49 | Halishahar 132/33kV Grid Sub-Station | 132 | 140 | 2023-08-03 19:30 | 123 | 2023-08-13 23:00
50 | HaripurSBU 132/33kV Sub-Station | 132 | 141 | 2023-08-16 23:00 | 124 | 2023-08-29 23:00
51 | Hasnabad 132/33kV Grid Substation | 132 | 138 | 2023-08-04 14:00 | 128 | 2023-08-30 12:00
52 | Ishurdi 132/33kV Grid Sub-Station | 132 | 137 | 2023-08-25 08:00 | 123 | 2023-08-21 12:00
53 | Jaldhaka 132/33kV Grid Sub-Station | 132 | 135 | 2023-08-25 15:00 | 113 | 2023-08-01 04:00
54 | Jamalpur 132/33kV Grid Sub-Station | 132 | 137 | 2023-08-12 18:30 | 113 | 2023-08-02 06:00
55 | Jashore 132/33kV Grid Sub-Station | 132 | 138 | 2023-08-25 10:00 | 122 | 2023-08-20 19:00
56 | Jhenaidah 132/33kV Grid Sub-Station | 132 | 141 | 2023-08-25 08:00 | 125 | 2023-08-20 19:00
57 | Joydebpur 132/33kV Grid Sub-Station | 132 | 140 | 2023-08-03 19:00 | 126 | 2023-08-27 12:00
58 | Joypurhat 132/33kV Grid Sub-Station | 132 | 132 | 2023-08-08 06:00 | 113 | 2023-08-20 23:00
59 | Juldah 132/33kV Grid Sub-Station | 132 | 141 | 2023-08-02 19:00 | 126 | 2023-08-22 12:00
60 | Kabirpur 132/33kV Grid Sub-Station | 132 | 140 | 2023-08-04 18:30 | 121 | 2023-08-03 22:00
61 | Kachua 132/33kV Grid Sub-Station | 132 | 138 | 2023-08-05 18:00 | 117 | 2023-08-16 06:00
62 | Kallyanpur 132/33kV Grid Sub-Station | 132 | 133 | 2023-08-25 11:00 | 123 | 2023-08-01 12:00
63 | Kalurghat 132/33kV Grid Sub-Station | 132 | 140 | 2023-08-06 19:30 | 127 | 2023-08-22 12:00
64 | Kamrangirchar 132/33kV Grid Sub-Station | 132 | 140 | 2023-08-04 14:00 | 121 | 2023-08-01 12:00
65 | Kazla 132/33kV Grid Sub-Station | 132 | 136 | 2023-08-04 09:00 | 125 | 2023-08-21 13:00
66 | Khagrachori 132/33kV Grid Sub-Station | 132 | 139 | 2023-08-01 13:00 | 127 | 2023-08-21 18:30
67 | Khulna (C) 132/33kV Grid Sub-Station | 132 | 139 | 2023-08-02 03:00 | 124 | 2023-08-21 14:00
68 | Khulshi 132/33kV Grid Sub-Station | 132 | 138 | 2023-08-03 19:30 | 124 | 2023-08-22 12:00
69 | Kishoreganj 132/33kV Grid Sub-Station | 132 | 134 | 2023-08-12 06:00 | 122 | 2023-08-21 12:00
70 | Kodda 132/33kV Grid Sub-Station | 132 | 140 | 2023-08-04 18:30 | 123 | 2023-08-19 15:00
71 | KSRM 132/33kV Grid Sub-Station | 132 | 141 | 2023-08-03 19:30 | 125 | 2023-08-22 12:00
72 | Kulaura 132/33kV Grid Sub-Station | 132 | 133 | 2023-08-04 16:00 | 127 | 2023-08-01 12:00
73 | Kurigram 132/33kV Grid Sub-Station | 132 | 134 | 2023-08-29 19:30 | 113 | 2023-08-06 19:00
74 | Kushtia 132/33kV Grid Sub-Station | 132 | 135 | 2023-08-01 | 120 | 2023-08-20 19:00
75 | Lalbag 132/33kV Grid Sub-Station | 132 | 139 | 2023-08-04 14:00 | 123 | 2023-08-08 23:00
76 | Lalmonirhat 132/33kV Grid Sub-Station | 132 | 134 | 2023-08-13 03:00 | 114 | 2023-08-01 05:00
77 | Madanganj 132/33kV Grid Sub-Station | 132 | 136 | 2023-08-28 18:00 | 125 | 2023-08-07 16:00
78 | Madaripur 132/33kV Grid Sub-Station | 132 | 136 | 2023-08-12 06:00 | 125 | 2023-08-08 12:00
79 | Madartek 132/33kV Grid Sub-Station | 132 | 137 | 2023-08-28 06:00 | 126 | 2023-08-08 12:00
80 | Madunaghat 132/33kV Grid Sub-Station | 132 | 141 | 2023-08-03 19:30 | 126 | 2023-08-22 13:00
81 | Magura 132/33kV Grid Sub-Station | 132 | 139 | 2023-08-25 15:00 | 123 | 2023-08-19 22:00
82 | Mahasthangarh 132/33kV Grid Sub-Station | 132 | 138 | 2023-08-25 10:00 | 121 | 2023-08-01 05:00
83 | Manikganj 132/33kV Grid Sub-Station | 132 | 138 | 2023-08-11 18:30 | 124 | 2023-08-26 10:00
84 | Maniknagar 132/33kV Grid Sub-Station | 132 | 137 | 2023-08-07 05:00 | 125 | 2023-08-30 13:00
85 | Matarbari 132/33kV Sub-Station | 132 | 139 | 2023-08-01 14:00 | 113 | 2023-08-21 18:00
86 | Matuail 132/33kV Grid Sub-Station | 132 | 136 | 2023-08-07 04:00 | 121 | 2023-08-16 04:00
87 | Millgate Tongi 132/33kV Grid Sub-Station | 132 | 138 | 2023-08-25 19:00 | 123 | 2023-08-31 09:00
88 | Mirpur 132/33kV Grid Sub-Station | 132 | 137 | 2023-08-04 14:00 | 123 | 2023-08-30 13:00
89 | Mithapukur 132/33kV Grid Sub-Station | 132 | 135 | 2023-08-25 15:00 | 116 | 2023-08-01 05:00
90 | Modern Steel 132/11kV Grid Sub-Station | 132 | 139 | 2023-08-05 21:00 | 124 | 2023-08-22 12:00
91 | Mogbazar 132/33kV Grid Sub-Station | 132 | 139 | 2023-08-28 06:00 | 126 | 2023-08-21 13:00
92 | Mongla 132/33kV Grid Sub-Station | 132 | 138 | 2023-08-01 13:00 | 120 | 2023-08-20 19:00
93 | Motijheel 132/33kV Grid Sub-Station | 132 | 137 | 2023-08-02 19:00 | 125 | 2023-08-21 12:00
94 | Munshiganj 132/33kV Grid Sub-Station | 132 | 137 | 2023-08-28 18:00 | 126 | 2023-08-08 11:00
95 | Mymensingh 132/33kV Grid Sub-Station | 132 | 144 | 2023-08-21 12:00 | 113 | 2023-08-18 19:00
96 | Naogaon 132/33kV Grid Sub-Station | 132 | 133 | 2023-08-10 18:00 | 113 | 2023-08-01 03:00
97 | Narail 132/33kV Grid Sub-Station | 132 | 139 | 2023-08-23 15:00 | 120 | 2023-08-20 19:00
98 | Narshingdi 132/33kV Grid Sub-Station | 132 | 133 | 2023-08-01 13:00 | 116 | 2023-08-12 09:00
99 | Natore 132/33kV Grid Sub-Station | 132 | 136 | 2023-08-23 08:00 | 116 | 2023-08-21 12:00
100 | Nawabganj 132/33kV Grid Sub-Station | 132 | 139 | 2023-08-04 14:00 | 127 | 2023-08-22 09:00
101 | Netrakona 132/33kV Grid Sub-Station | 132 | 134 | 2023-08-23 21:00 | 114 | 2023-08-03 20:00
102 | New Tongi 132/33kV Grid Sub-Station | 132 | 138 | 2023-08-10 06:00 | 124 | 2023-08-31 09:00
103 | Niamatpur 132/33kV Grid Sub-Station | 132 | 134 | 2023-08-08 06:00 | 113 | 2023-08-01 01:00
104 | Noapara 132/33kV Grid Sub-Station | 132 | 138 | 2023-08-01 | 124 | 2023-08-20 19:00
105 | Pabna 132/33kV Grid Sub-Station | 132 | 135 | 2023-08-25 15:00 | 120 | 2023-08-21 12:00
106 | Palashbari 132/33kV Grid Sub-Station | 132 | 134 | 2023-08-25 10:00 | 114 | 2023-08-01 05:00
107 | Panchagarh 132/33kV Grid Sub-Station | 132 | 137 | 2023-08-29 20:00 | 113 | 2023-08-01 05:00
108 | Patuakhali 132/33kV Grid Sub-Station | 132 | 142 | 2023-08-16 19:00 | 132 | 2023-08-15 22:00
109 | PHP 132/33kV Sub-Station | 132 | 137 | 2023-08-01 13:00 | 119 | 2023-08-22 16:00
110 | Postogola 132/33kV Grid Sub-Station | 132 | 139 | 2023-08-02 18:30 | 128 | 2023-08-08 12:00
111 | Purbachal 132/33kV Grid Sub-Station | 132 | 138 | 2023-08-04 08:00 | 123 | 2023-08-31 09:00
112 | Purbasadipur 132/33kV Grid Sub-Station | 132 | 134 | 2023-08-13 05:00 | 113 | 2023-08-01 21:00
113 | Rahim Steel 132/33kV Sub-Station | 132 | 136 | 2023-08-01 13:00 | 127 | 2023-08-28 10:00
114 | Rajbari 132/33kV Grid Sub-Station | 132 | 132 | 2023-08-12 06:00 | 119 | 2023-08-20 19:00
115 | Rajendrapur 132/33kV Grid Sub-Station | 132 | 138 | 2023-08-11 18:30 | 124 | 2023-08-19 16:00
116 | Rajshahi 132/33kV Grid Sub-Station | 132 | 136 | 2023-08-01 18:00 | 119 | 2023-08-21 14:00
117 | Ramganj 132/33kV Grid Sub-Station | 132 | 138 | 2023-08-01 11:00 | 113 | 2023-08-10 04:00
118 | Rangamati 132/33kV Grid Sub-Station | 132 | 139 | 2023-08-01 13:00 | 128 | 2023-08-21 18:30
119 | Rangpur 132/33kV Grid Sub-Station | 132 | 133 | 2023-08-01 18:00 | 113 | 2023-08-17 04:00
120 | Ruppur 132/11kV Grid Sub-Station | 132 | 136 | 2023-08-23 08:00 | 122 | 2023-08-21 14:00
121 | Saidpur 132/33kV Grid Sub-Station | 132 | 135 | 2023-08-13 04:00 | 113 | 2023-08-16 08:00
122 | Satkhira 132/33kV Grid Sub-Station | 132 | 138 | 2023-08-01 14:00 | 120 | 2023-08-20 22:00
123 | Satmasjid 132/33kV Grid Sub-Station | 132 | 135 | 2023-08-04 14:00 | 124 | 2023-08-20 12:00
124 | Savar 132/33kV Grid Sub-Station | 132 | 138 | 2023-08-04 14:00 | 123 | 2023-08-31 09:00
125 | Shahjadpur 132/33kV Grid Sub-Station | 132 | 141 | 2023-08-08 06:00 | 119 | 2023-08-26 09:00
126 | Shahjibazar 132/33kV Grid Sub-Station | 132 | 134 | 2023-08-04 16:00 | 119 | 2023-08-01 12:00
127 | Shahmirpur 132/33kV Grid Sub-Station | 132 | 141 | 2023-08-02 18:30 | 125 | 2023-08-22 12:00
128 | Shariatpur 132/33kV Grid Sub-Station | 132 | 136 | 2023-08-12 07:00 | 123 | 2023-08-30 22:00
129 | Sherpur 132/33kV Grid Sub-Station | 132 | 135 | 2023-08-19 19:30 | 113 | 2023-08-01 06:00
130 | Shitalakhya 132/33kV Grid Sub-Station | 132 | 139 | 2023-08-18 22:00 | 126 | 2023-08-08 11:00
131 | Sholosohor 132/33kV Grid Sub-Station | 132 | 139 | 2023-08-05 21:00 | 125 | 2023-08-22 12:00
132 | Shyampur 132/33kV Grid Sub-Station | 132 | 132 | 2023-08-04 18:00 | 123 | 2023-08-03 11:00
133 | Siddhirganj 132/33kV Grid Sub-Station | 132 | 136 | 2023-08-04 14:00 | 127 | 2023-08-21 12:00
134 | Sirajganj 132/33kV Grid Sub-Station | 132 | 137 | 2023-08-25 14:00 | 113 | 2023-08-28 20:00
135 | Sonargaon 132/33kV Grid Sub-Station | 132 | 136 | 2023-08-04 19:30 | 125 | 2023-08-09 09:00
136 | Sreemongol 132/33kV Grid Sub-Station | 132 | 133 | 2023-08-04 16:00 | 123 | 2023-08-21 18:30
137 | Srinagar 132/33kV Grid Sub-Station | 132 | 138 | 2023-08-04 14:00 | 127 | 2023-08-21 12:00
138 | SSM 132/33kV Grid Sub-Station | 132 | 142 | 2023-08-06 09:00 | 128 | 2023-08-17 13:00
139 | Sunamganj 132/33kV Grid Sub-Station | 132 | 130 | 2023-08-27 18:00 | 117 | 2023-08-01 20:00
140 | Sylhet 132/33kV Grid Sub-Station | 132 | 132 | 2023-08-04 18:00 | 125 | 2023-08-01 20:00
141 | Tangail 132/33kV Grid Sub-Station | 132 | 135 | 2023-08-12 18:30 | 120 | 2023-08-03 20:00
142 | Thakurgaon 132/33kV Grid Sub-Station | 132 | 136 | 2023-08-11 | 113 | 2023-08-01 23:00
143 | TK chemical 132kV Grid Sub-Station | 132 | 141 | 2023-08-06 18:30 | 126 | 2023-08-22 12:00
144 | Ullon 132/33kV Grid Sub-Station | 132 | 140 | 2023-08-10 01:00 | 126 | 2023-08-21 12:00
145 | Uttara 132/33kV Grid Sub-Station | 132 | 137 | 2023-08-04 14:00 | 126 | 2023-08-01 12:00
146 | UttaraNew 132/33kV Grid Sub-Station | 132 | 138 | 2023-08-25 19:00 | 123 | 2023-08-16 12:00
147 | Zigatola 132/33kV Grid Sub-Station | 132 | 139 | 2023-08-04 15:00 | 128 | 2023-08-21 12:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:August 2023
substation | transformer | voltage_level | mw | mva | date_time
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 | 400/230 | 390 | 551.5433 | 2023-08-31 08:00
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 | 400/230 | 452 | 511.7656 | 2023-08-03 11:00
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | -260 | 302.1854 | 2023-08-08 09:00
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | -260 | 302.1854 | 2023-08-08 09:00
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | -181 | 181.3974 | 2023-08-01 05:00
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | -178 | 178.4741 | 2023-08-01 05:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 102 | 275.5721 | 2023-08-19 12:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 45 | 402.5233 | 2023-08-26 11:00
Madunaghat_I 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 374 | 402.2188 | 2023-08-07 12:00
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | -13192 | 13192.0001 | 2023-08-31 18:00
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | -256.77 | 259.0641 | 2023-08-21 22:00
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 221 | 283.7693 | 2023-08-25 11:00
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | -180 | 180.4688 | 2023-08-27 19:00
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | -124 | 128.5768 | 2023-08-13 19:30
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | -180 | 180.4688 | 2023-08-27 19:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 299 | 334.5161 | 2023-08-23 01:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 299 | 316.5707 | 2023-08-23 07:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | -83 | 90.471 | 2023-08-18 22:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | -83 | 90.471 | 2023-08-18 22:00
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
substation | transformer | voltage_level | mw | mva | date_time
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 195 | 210.7724 | 2023-08-01 13:00
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 252 | 270.749 | 2023-08-04 10:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 183 | 185.4427 | 2023-08-22 16:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 183 | 185.4427 | 2023-08-22 16:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 144 | 148.4318 | 2023-08-22 07:00
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 115 | 132.0984 | 2023-08-24 21:00
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 187 | 187.131 | 2023-08-09 19:00
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 216 | 244.2376 | 2023-08-09 02:00
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 155 | 166.2077 | 2023-08-10 01:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 199 | 206.7293 | 2023-08-25 17:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 188 | 203.5387 | 2023-08-06 19:30
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 243 | 252.8814 | 2023-08-06 19:30
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 175 | 178.0842 | 2023-08-04
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 175 | 178.0842 | 2023-08-04
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | -105 | 118.072 | 2023-08-05 19:30
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | -105 | 118.072 | 2023-08-05 19:30
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 210 | 214.56 | 2023-08-03 19:30
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 210 | 214.56 | 2023-08-03 19:30
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 284 | 289.4685 | 2023-08-03 19:30
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-01 | 230/132 | 188 | 207.1545 | 2023-08-19 07:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-02 | 230/132 | 190 | 201.1368 | 2023-08-19 21:00
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 225 | 231.6247 | 2023-08-24 21:00
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 105 | 105 | 2023-08-05 09:00
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 76 | 107.4802 | 2023-08-09 06:00
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 162 | 174.9286 | 2023-08-28 12:00
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 162 | 174.9286 | 2023-08-28 12:00
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 162 | 174.9286 | 2023-08-28 12:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 53 | 89.4036 | 2023-08-14 22:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 53 | 89.4036 | 2023-08-14 22:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 53 | 89.4036 | 2023-08-14 22:00
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 112 | 115.2085 | 2023-08-30 12:00
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 112 | 115.2085 | 2023-08-30 12:00
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 112 | 115.2085 | 2023-08-30 12:00
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 64 | 134.2386 | 2023-08-28 03:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 120 | 136 | 2023-08-29 22:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 120 | 136 | 2023-08-29 22:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 120 | 136 | 2023-08-29 22:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | -222 | 250.4795 | 2023-08-30 19:30
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | -166 | 257.6141 | 2023-08-23 09:00
Kaliakoir 400/230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 206 | 209.8476 | 2023-08-18 23:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 164 | 170.8801 | 2023-08-21 23:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 0 | 0 | 2023-08-01
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 259 | 270.2036 | 2023-08-22 10:00
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | -143 | 144.8378 | 2023-08-22 22:00
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | -143 | 144.8378 | 2023-08-22 22:00
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | -1123 | 1123.1287 | 2023-08-26 03:00
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 212 | 226.241 | 2023-08-18 15:00
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 166 | 181.7471 | 2023-08-01 13:00
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | -175 | 195.4329 | 2023-08-21 12:00
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | -185 | 194.7973 | 2023-08-29 17:00
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 1 | 1.4142 | 2023-08-01
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 1 | 1 | 2023-08-29 15:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 01 | 230/132 | 211 | 212.3605 | 2023-08-30 13:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 | 230/132 | 211 | 212.3605 | 2023-08-30 13:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 | 230/132 | 211 | 212.3605 | 2023-08-30 13:00
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
substation | transformer | voltage_level | mw | mva | date_time
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 233 | 255.566 | 2023-08-29 21:00
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 233 | 255.566 | 2023-08-29 21:00
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 119 | 131.947 | 2023-08-05 10:00
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 119 | 131.947 | 2023-08-05 10:00
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 239 | 264.7961 | 2023-08-08 11:00
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 239 | 264.7961 | 2023-08-08 11:00
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 172.85 | 181.0708 | 2023-08-09 19:00
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 173.61 | 181.8619 | 2023-08-09 19:00
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 218 | 221.2871 | 2023-08-21 10:00
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 218 | 221.2871 | 2023-08-21 10:00
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 218 | 221.2871 | 2023-08-21 10:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-37
|  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month: August 2023 | [6 empty] | (For Evening Peak) | [7 empty] | Month: August 2023 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2023-08-01 | 13870 | 13870 | 96 | 19:30 | 10 | 0 | 0 | 0 | 36 | 0 | 25 | 0 | 25 | - | 2023-08-01 | 12897 | 13300 | 385 | 12:00 | 160 | 0 | 0 | 0 | 55 | 170 | 0 | 0 | 0 | -
2023-08-02 | 14373 | 14373 | 217 | 20:00 | 0 | 0 | 0 | 20 | 30 | 105 | 62 | 0 | 0 | - | 2023-08-02 | 12196 | 12350 | 147 | 12:00 | 20 | 102 | 0 | 0 | 10 | 15 | 0 | 0 | 0 | -
2023-08-03 | 14623 | 14623 | 209 | 21:00 | 10 | 0 | 0 | 48 | 20 | 84 | 47 | 0 | 0 | - | 2023-08-03 | 12729 | 12900 | 163 | 12:00 | 23 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | -
2023-08-04 | 13395 | 13395 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-08-04 | 11626 | 11689 | 60 | 12:00 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | -
2023-08-05 | 14049 | 14049 | 160 | 21:00 | 15 | 0 | 0 | 33 | 15 | 75 | 0 | 0 | 22 | - | 2023-08-05 | 12395 | 12650 | 244 | 12:00 | 159 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | -
2023-08-06 | 13501 | 13501 | 133 | 21:00 | 25 | 25 | 0 | 30 | 0 | 15 | 0 | 0 | 38 | - | 2023-08-06 | 11786 | 11850 | 61 | 12:00 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-08-07 | 12729 | 12729 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-08-07 | 11453 | 11550 | 93 | 12:00 | 48 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | -
2023-08-08 | 13253 | 13253 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-08-08 | 10921 | 10921 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-08-09 | 13661 | 13661 | 110 | 21:00 | 60 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | - | 2023-08-09 | 12258 | 12258 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-08-10 | 13879 | 13879 | 160 | 19:30 | 0 | 0 | 0 | 35 | 0 | 78 | 0 | 0 | 47 | - | 2023-08-10 | 12235 | 12500 | 253 | 12:00 | 118 | 35 | 0 | 0 | 35 | 30 | 35 | 0 | 0 | -
2023-08-11 | 13333 | 13333 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-08-11 | 11365 | 11396 | 30 | 12:00 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | -
2023-08-12 | 13800 | 13800 | 85 | 21:00 | 25 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | - | 2023-08-12 | 11989 | 12200 | 202 | 12:00 | 90 | 0 | 0 | 0 | 20 | 92 | 0 | 0 | 0 | -
2023-08-13 | 13665 | 13665 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-08-13 | 11620 | 11660 | 38 | 12:00 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-08-14 | 13972 | 13972 | 122 | 21:00 | 20 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | - | 2023-08-14 | 12295 | 12550 | 244 | 12:00 | 82 | 0 | 0 | 0 | 52 | 110 | 0 | 0 | 0 | -
2023-08-15 | 13781 | 13781 | 117 | 21:00 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 97 | - | 2023-08-15 | 11476 | 11476 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-08-16 | 14311 | 14311 | 419 | 21:00 | 0 | 0 | 0 | 30 | 90 | 160 | 39 | 0 | 100 | - | 2023-08-16 | 12424 | 13000 | 550 | 12:00 | 95 | 80 | 85 | 0 | 90 | 80 | 40 | 30 | 50 | -
2023-08-17 | 14392 | 14392 | 437 | 21:00 | 45 | 0 | 10 | 45 | 113 | 114 | 10 | 0 | 100 | - | 2023-08-17 | 12309 | 13400 | 1042 | 12:00 | 175 | 145 | 125 | 115 | 155 | 115 | 75 | 25 | 112 | -
2023-08-18 | 13805 | 13805 | 145 | 21:00 | 0 | 0 | 0 | 0 | 39 | 79 | 0 | 0 | 27 | - | 2023-08-18 | 11453 | 11453 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-08-19 | 14036 | 14036 | 634 | 21:00 | 10 | 77 | 164 | 82 | 55 | 90 | 0 | 0 | 156 | - | 2023-08-19 | 12284 | 12365 | 77 | 12:00 | 25 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | -
2023-08-20 | 14651 | 14651 | 524 | 21:00 | 10 | 0 | 75 | 70 | 79 | 150 | 20 | 0 | 120 | - | 2023-08-20 | 12738 | 13600 | 823 | 12:00 | 260 | 170 | 0 | 45 | 131 | 137 | 45 | 0 | 35 | -
2023-08-21 | 14701 | 14701 | 629 | 21:00 | 35 | 35 | 84 | 110 | 120 | 90 | 45 | 0 | 110 | - | 2023-08-21 | 12786 | 13600 | 348 | 12:00 | 168 | 0 | 0 | 0 | 30 | 150 | 0 | 0 | 0 | -
2023-08-22 | 14244 | 14244 | 257 | 21:00 | 0 | 0 | 0 | 0 | 25 | 217 | 15 | 0 | 0 | - | 2023-08-22 | 13210 | 13380 | 162 | 12:00 | 77 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | -
2023-08-23 | 14030 | 14030 | 143 | 20:00 | 20 | 0 | 0 | 0 | 0 | 115 | 8 | 0 | 0 | - | 2023-08-23 | 12511 | 12600 | 85 | 12:00 | 35 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | -
2023-08-24 | 14182 | 14182 | 41 | 20:00 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | - | 2023-08-24 | 12731 | 12731 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-08-25 | 12278 | 12278 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-08-25 | 10484 | 10484 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-08-26 | 13496 | 13496 | 61 | 19:30 | 30 | 0 | 0 | 0 | 11 | 10 | 10 | 0 | 0 | - | 2023-08-26 | 10904 | 10904 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-08-27 | 14251 | 14251 | 95 | 19:30 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 30 | - | 2023-08-27 | 12365 | 12365 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-08-28 | 14347 | 14347 | 194 | 20:00 | 15 | 0 | 0 | 105 | 0 | 50 | 0 | 0 | 24 | - | 2023-08-28 | 11818 | 12600 | 747 | 12:00 | 162 | 110 | 212 | 117 | 36 | 110 | 0 | 0 | 0 | -
2023-08-29 | 14716 | 14716 | 271 | 21:00 | 10 | 0 | 0 | 0 | 10 | 51 | 0 | 0 | 200 |  | 2023-08-29 | 13382 | 13382 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023-08-30 | 14889 | 14889 | 393 | 21:00 | 25 | 0 | 0 | 20 | 150 | 80 | 60 | 0 | 58 |  | 2023-08-30 | 13320 | 13490 | 162 | 12:00 | 76 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0
2023-08-31 | 14815 | 14815 | 463 | 21:00 | 40 | 0 | 0 | 78 | 100 | 85 | 60 | 0 | 100 |  | 2023-08-31 | 13301 | 13800 | 477 | 12:00 | 90 | 80 | 82 | 0 | 80 | 90 | 25 | 30 | 0
| Max. L/S | - |  | - | [10 empty] | Max. L/S | - |  | 1042
| Min. L/S | - | 54 | - | [10 empty] | Min. L/S | - |  | 0
| No. of Days | - | 31 | - | [10 empty] | No. of Days | - | 31
| Average L/S |  | 21566 | [11 empty] | Average L/S |  | 19669
|  | - | - | - | [11 empty] | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:August 2023
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 14889 | 2023-08-30 | 21:00
2 | Maximum Day Peak Genaration | MW | 13382 | 2023-08-29 | 12:00
3 | Maximum Evening Peak Demand | MW | 14889 | 2023-08-30 | 21:00
4 | Minimum Generation | MW | 8071 | 2023-08-01 | 6:00
5 | Average of the daily evening peak Genaration | MW | 13968.6452 | - | -
6 | Average of the daily day peak Genaration | MW | 12169.7097 | - | -
7 | Maximum load shed | MW | 634 | 2023-06-06 | 21:00
8 | Minimum load shed | MW | 30 | 2023-06-26 | 21:00
9 | Total nos. of load shed days | Day | 25 | - | -
10 | Average load shed ( Avg. of the 30 days in the month) | MW/Day | 197.2581 | - | -
11 | Total Generation | MkWh | 9188.4632 | - | -
12 | Total Generation by BPDB | MkWh | 2157.9023 | % of total Gen. | 23.48%
13 | Total Generation by IPP | MkWh | 2068.9141 | '' | 22.52%
14 | A) Total Generation by Generation Companies | MkWh | 2881.7466 | '' | 31.36%
| B) Total Generation by REB | MkWh | 132.336 | " | 1.44%
| C) Total Generation by RENTAL | MkWh | 273.6692 | " | 2.978%
| D) Total Imported from India (BIPTC) | MkWh | 658.6327 | " | 7.168%
| E) Total Imported from Tripura, India (A.C) | MkWh | 1015.2622 | " | 11.05%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4451.0325 | % of total Gen. | 48.47%
| B) Oil | MkWh | 1456.8463 | '' | 15.87%
| C) Hydro | MkWh | 128.7252 | '' | 1.402%
| D) Solar | MkWh | 59.1982 | '' | 0.6447%
| E) Coal | MkWh | 2328.2862 | '' | 25.36%
| F) BIPTC (Import from India) | MkWh | 658.6327 | '' | 7.173%
| G) A.C (Import from Tripura, India) | MkWh | 99.8083 | '' | 1.087%
| H) Wind | MkWh | 5.9338 | '' | 0.1253%
16 | Maximun of the daily total Generation . | MkWh | 310.7938 | 2023-08-22
17 | Monthly Load factor | % | 81.9186 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 36053.0382 | - | -
| A) Gas | M.Taka | 4928.9089 | - | -
| B) Liquid fuel | M.Taka | 16368.9403 | - | -
| C) Coal | M.Taka | 11033.204 | - | -
| D) BIPTC (Import from India) | M.Taka | 3003.3652 | - | -
| E) Tripura(Import from India) | M.Taka | 718.6199 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1449.5782 | 2023-08-24
| A) Gas | M.Taka | 169.628 | 2023-08-09
| B) Liquid fuel | M.Taka | 842.4268 | 2023-08-03
| C) Coal | M.Taka | 681.0284 | 2023-08-24
| D) BIPTC (Import from India) | M.Taka | 100.5621 | 2023-08-24
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 3.9237
| B) Excluding Hydro & Solar | Taka/kWhR | 4.0083
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 98.34 | 31/08/2023 | 06:00
b) | Actual | FT (MSL) | 104.66 | 31/08/2023 | 6:00
22 | Peak Genaration of August 2022 | MW | 13985 | 25/08/2022 | 21:00
23 | Peak Demand of August 2022 | MW | 14745 | 31/08/2022 | 21:00
24 | Maximum peak Generation recorded upto 31/08/2023 | MW | 15648 | 19/04/2023 | 21:00
25 | Maximum peak Demand recorded upto 31/08/2023 | MW | 16096 | 19/04/2023 | 21:00
26 | Maximum load shed recorded upto 30/06/2023 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## FGMO
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month:August 2023
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
1 | Bibiyana-III 400 MW CCPP | BPDB | 400 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | [14 empty] | √
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220
6 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
7 | Meghnaghat CCPP(Summit) | IPP | 335
8 | Ashuganj 225 MW CCPP | APSCL | 221
9 | Ashuganj 450 MW CCPP(North) | APSCL | 361
10 | Ashuganj 450 MW CCPP(South) | APSCL | 360
11 | Ashuganj 420 MW CCPP(East) | APSCL | 400
12 | Ashuganj 55 MW PP (Precision) | QRPP | 55
13 | Bheramara 410 MW CCPP | NWPGCL | 410
14 | Haripur 412 MW CCPP | EGCB | 412
15 | Fenchugonj CCPP Phase-1 | BPDB | 97
16 | Fenchugonj CCPP Phase-2 | BPDB | 104
17 | Siddhirganj 2x120 MW GTPP | EGCB | 210
18 | Shikalbaha 225 MW CCPP | BPDB | 225
19 | Shikalbaha Peaking GT | BPDB | 150
20 | Shahjibazar 330 MW CCPP | BPDB | 330
21 | Chandpur 150 MW CCPP | BPDB | 163
22 | Bhola 225 MW CCPP | BPDB | 194
23 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
24 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
25 | Siddhirganj 335 MW CCPP | EGCB | 335
26 | Bibiyana-III 400 MW CCPP | BPDB | 400
27 | Sylhet 225 MW CCPP | BPDB | 231
28 | RPCL 210 MW CCPP | IPP | 210
29 | Khulna 225 MW CCPP | NWPGCL | 230
30 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
31 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
32 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
33 | Bibiyana South 400 MW CCPP | BPDB | 383
34 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
35 | Shajibazar 100 MW PP | BPDB | 100
36 | Payra 1320 MW Unit-1 | BCPCL | 622
37 | Kushiara 163 MW CCPP (KP) | IPP | 163
38 | Haripur 360MW CCPP(HPL) | IPP | 360
39 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450
* Data is collected from Daily Operational Reports
due to gas shortage