## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-10-18 | Wednesday
|  | Date (day): | 2023-10-18 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12607.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14730 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-10-17 | 2023-10-18 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 140 | 140 | 140 | 140
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  |  | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 411 | 409 | 410 | 412
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 323 | 292 | 330 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 42 | 75 | 66 | 75 |  | 25 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 307 | 250 | 300 | 300 | 35 |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 48 | 95 | 80 | 95 |  | 7 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 15 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 24 | 25 | 44 | 44 | 31 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 15 | 17 | 17 | 17 |  | 5 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 55 | 66 | 55 | 65 | 35 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 330 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 25 | 58 | 80 | 92 |  | 10 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 0 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 149 | 16 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 0 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 0 | 55
| Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | 0 | 0 | 0
25 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 30 | 30 | 37 | 37 |  | 43 | Engine problem
26 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33 |  | 0 | Engine problem
27 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 14 | 20 | 24 | 24 |  | 9 | Engine problem
28 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 25 | 8 | 25 | 27 |  | Fuel shortage
29 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
30 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 80 | 130 | 80 | 130 | 168 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
31 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 118 | 17 | 105 | 44 |  | Fuel shortage
32 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 105 | 35 | 105
33 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 35 | 72 | 17 | 72 | 32 |  | Fuel shortage
34 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 72 | 17 | 72 | 90 |  | Fuel shortage
35 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 0 | 0 | 35 | 0
36 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 55 | 55 | 55
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 5655 | 5422 | 2497 | 3156 | 2696 | 3302 | 1045 | 859
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
38 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 17 | 8 | 17 | 8 |  | Fuel shortage
39 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 19 | 6 | 40 | 10 |  | Fuel shortage
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 151 | 153 | 162 | 197 |  | 33 | #01 under maint.
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 223 | 225 | 225
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 17 | 17 | 88 |  | Fuel shortage
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 24 | 66 | 65 | 70 | 28 |  | Fuel shortage
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 | 102 |  | under maint.
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 12 | 12 | 25 | 25 | 75 |  | Fuel shortage
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 12 | 12 | 12 | 12 | 10 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 18 | 10 | 18
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 70 | 214 | 70 | 270 | 30 |  | Fuel shortage
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 17 | 17 | 93 |  | Fuel shortage
55 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
56 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 34 | 51 | 34 | 51 | 65 |  | Fuel shortage
57 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 35 | 114 | 33 | 160
58 | SS Power I |  | Coal | SS Power | 1*612 | 612 | 612 | 621 | 621 | 600 | 600 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 0 | 0 | 10 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 138 | 144 | 150 | 150 |  |  | On test.
| Chattogram area Total |  |  |  |  | 3217 | 3157 | 1427 | 1739 | 1510 | 1920 | 1010 | 363
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 200 | 176 | 210 | 210 |  |  | FGMO
60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 340 | 280 | 300 | 300 |  |  | FGMO
61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 300 | 300 | 300 |  |  | FGMO
62 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 280 | 375 | 300 | 300 | 100 |  | Gas shortage
63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 50 | 50 | 50 | 50
| Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortae
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 5 | 118 | 6 | 150
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 47
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 34 | 17 | 17 | 183 |  | Fuel shortage
70 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 96 | 140 | 149 | 165
72 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 16 | 52
74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 102 | 17 | 114
76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 78 | 27 | 75 | 38 |  | Fuel shortage
77 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 54 | 35 | 54 |  | 0 | Engine problem
78 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 36 | 95 | 36 | 95 | 20 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2904 | 2896 | 1534 | 1970 | 1588 | 2054 | 536 | 180
79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 26 | 34 | 32 | 65 | 137 |  | Gas shortage
80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 16 | 19 | 19
| Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 0 | 0 | 0 | 0 | 0 | 0
81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 28 | 102 | 18 | 100 | 100 |  | Fuel shortage
83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 79 | 99 | 60 | 99 | 16 |  | Fuel shortage
84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 51 | 0 | 50 | 0
85 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 18 | 18 | 18 | 4 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 622 | 614 | 219 | 269 | 198.6 | 301 | 137 | 0
86 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 42 | 43 | 43 | 43 |  | 27 | Machine problem.
87 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 20 | 30 | 30 |  | 60 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 |  | 0
89 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
90 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 42 | 50 | 50 | 50
91 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 44 | 47 | 48 | 48
92 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 3 | 11 | 11
93 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 61 | 60 | 60
94 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 85 | 86 | 86
95 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 159 | 157 | 158 | 158 |  | 73 | Machine problem
97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 17 | 17
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 9 |  | Gas shortage
99 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 265 | 300 | 300 |  |  | FGMO
100 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 405 | 368 | 400 | 400
101 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
102 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 0 | 0 | 0 | 0 |  | 383 | Under maint
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1337 | 1288 | 1392 | 1392 | 9 | 973
103 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 895 | 757 | 910 | 750
104 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 81 | 49 | 81 | 34 |  | Fuel shortage
105 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 26 | 0 | 26 |  | 28 | Engine problem
106 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
107 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 51 | 58 |  | Fuel shortage
108 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
109 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 16 | 16 | 0 | 24 | 16 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
110 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 53 | 35 | 53 | 52 |  | Fuel shortage
111 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 15 | 50 | 100 | 105
112 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 71 | 0 | 100 | 0
113 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0
114 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 401 | 571 | 450 | 520
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 1414 | 1554 | 1644 | 1610 | 816 | 28
115 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 32 | 16 | 110
116 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 20 | 27 | 21 | 28 |  | 12 | Engine problem
117 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 130 | 126 | 130 | 130 |  | 64 | ST under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 860 | 1244 | 1000 | 1244
119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 222 | 220 | 220
120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 12 | 54 | 38 | 150
121 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 150 | 150 | 150 | 150 | 157 |  | Coal shortage
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1408 | 1855 | 1575 | 2032 | 157 | 76
122 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
123 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 26 | 0 | 31 | 21 |  | Fuel shortage
124 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 16 |  | 55 | Engine problem
125 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 28 | 28
126 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 42 | 34 | 42 |  | 8 | Engine problem
127 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 39 | 39 | 30 | 39 |  | 11 | Engine problem
128 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 214 | 209 | 200 | 200 | 10
129 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
130 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 208 | 205 | 200 | 200 | 20
131 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 360 | 380 | 400 | 14
132 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 24 | 30 | 20 |  | Fuel shortage
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
133 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
134 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
135 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 47 | 94 | 50 | 92 |  | 12 | Engine problem
136 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
137 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 35 | 50 | 63 |  | Fuel shortage
138 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 35 | 35 | 55 | 58 |  | Fuel shortage
139 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 522 | 530 | 525 | 525 | 971
| Rajshahi Area Total |  |  |  |  | 3653 | 3631 | 1536 | 1594 | 1566 | 1727 | 1812 | 86
140 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
141 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
142 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 16 | 0 | 0 | 20
143 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
144 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 6 | 107 | 30 | 107 | 6 |  | Fuel shortage
145 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
146 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 114 | 70 | 115
147 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0
148 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 163 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 382 | 407 | 438 | 392 | 131 | 189
| Total |  |  |  |  | 25059 | 24599 | 11754 | 13832 | 12607.6 | 14730 | 5653 | 2754
A. |  | 2023-10-17 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 13832 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 10151 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13832 | MW
3 | Day peak Generation : |  |  | 11754 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13235.47 | MW
4 | Evening peak Generation : |  |  | 13832 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 284.2766 | MKWHr | By Solar | 2.515 | MKWHr
| By Gas : | 144.4396 | MKWHr |  | By Oil: | 36.2769 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 74.0359 | MKWHr |  | By Hydro: | 3.6166 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.00048 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5653 | MW | Dhaka | 4993.27 | 4993.27 |  | 0 |  | 18:00 |  | 563
|  |  | For Plants S/D or M/C prob = |  |  | 2754 | MW | Chittagong | 1268 | 1268 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 8407 | MW | Khulna | 1559.9 | 1559.9 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 1059.11 | MMCFD |  |  | Rajshahi | 1309.8 | 1309.8 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 153449893.43 | ii) Oil : | Taka | 470048873.5 | Comilla | 1299.5 | 1299.5 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 493507489.15 | Total | Taka | 1117006256.08 | Mymensingh | 1093 | 1093 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 539 | 539 |  | 0 |  | 23:00 |  | 205.325
| ii) During Peak Demand : |  |  | 286 | MW (W to E) at | 19:30 | hrs | Barisal | 411 | 411 |  | 0 |  | 24:00 |  | 226.335
| iii) Maximum : |  |  | 232 | MW at | 20:00 | hrs | Rangpur | 762 | 762 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.5°C |  |  | Total | 13235.47 | 13235.47 |  | 0
B. |  | 2023-10-18 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 33.5°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 14000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14730 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 12000 | MW
4 | Reserve(Generation end) |  |  |  | 730 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 287.7293 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10120 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.6109 | MKWHr. | ii) HVDC Flow at Peak Time |  | 757 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.7811 | MKWHr. | iii) Maximum HVDC Flow : |  | 901 | MW at | 5:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 106 |  | (b) Today: | 105.84 |  | (c) Rule Curve: |  | 107.6
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-10-17 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 419 | 326 |  | 0 | 450 | 278 | 41 | 96 | 15 | 336 | 0 | 0 | 34 | 24 | 16 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 12 | 30 | 20 | 8 | 0 | 79 | 75 | 0 | 0 | 8 | 227 | 0 | 0 | 0 |  | 6 | 66 | 0 | 12 | 0 | 6 | 12 | 36 | 0 | 0 | 0 | 300 | 270 | 192 | 0 | 0 | 51 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 10 | 25 | 12 | 140 | 72 | 0 | 16 | 0 | 43 | 25 | 50 | 48 | 163 | 0 | 59 | 85 | 0 | 159 | 0 | 0 | 10 | 295 | 16 | 8 | 0 | 47 | 0 | 0 | 18 | 0 | 17 | 0 | 12 | 17 | 11 | 401 | 60 | 17 | 17 | 0 | 70 | 0 | 17 | 52 | 42 | 12 | 0 | 17 | 0 | 17 | 46 | 0 | 35 | 0 | 32 | 17 | 310 | 17 | 0 | 612 | 0 | 144 | 0 | 0 |  | 900 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 7 | 0 | 8 | 130 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 42 | 0 | 8 | 16 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 414 | 54 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 1120 | 220 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 150 | 525 | 0 | 0 |  | 7026 | 4861 | 11887 | 3784 | 900 | 2453 | 0 | 1146 | 3171 | 154 | 0 | 139 | 140 | 0 | 0 | 275.04 | 106.05
2:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 420 | 334 |  | 0 | 450 | 286 | 52 | 96 | 15 | 336 | 0 | 0 | 24 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 12 | 30 | 20 | 8 | 0 | 78 | 75 | 0 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 66 | 0 | 12 | 0 | 6 | 12 | 36 | 0 | 0 | 0 | 300 | 270 | 196 | 0 | 0 | 51 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 10 | 25 | 12 | 136 | 72 | 0 | 16 | 0 | 43 | 25 | 50 | 45 | 163 | 0 | 59 | 85 | 0 | 160 | 0 | 0 | 10 | 280 | 16 | 8 | 0 | 47 | 0 | 0 | 18 | 0 | 17 | 0 | 12 | 17 | 13 | 403 | 60 | 17 | 17 | 0 | 70 | 0 | 17 | 52 | 38 | 12 | 0 | 17 | 0 | 17 | 17 | 0 | 35 | 0 | 36 | 17 | 310 | 17 | 0 | 612 | 0 | 144 | 0 | 0 |  | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 350 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 35 | 1040 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 150 | 526 | 0 | 0 |  | 6965 | 4412 | 11377 | 3792 | 900 | 2386 | 0 | 874 | 3037 | 153 | 0 | 99 | 136 | 0 | 0 | 212.965 | 106.04
3:00 | 0 | 0 | 141 | 0 | 0 | 0 | 0 | 420 | 336 |  | 0 | 450 | 282 | 21 | 86 | 15 | 300 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 12 | 30 | 20 | 8 | 0 | 77 | 75 | 0 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 66 | 0 | 12 | 0 | 6 | 12 | 37 | 0 | 0 | 0 | 300 | 270 | 196 | 0 | 0 | 51 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 10 | 25 | 12 | 118 | 72 | 0 | 16 | 0 | 43 | 25 | 50 | 48 | 163 | 0 | 60 | 85 | 0 | 160 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 18 | 0 | 17 | 0 | 12 | 17 | 10 | 403 | 60 | 17 | 17 | 0 | 70 | 0 | 17 | 52 | 38 | 12 | 0 | 17 | 0 | 0 | 17 | 0 | 35 | 0 | 36 | 17 | 310 | 17 | 0 | 612 | 0 | 142 | 0 | 0 |  | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 350 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1040 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 150 | 528 | 0 | 0 |  | 6766 | 4387 | 11153 | 3758 | 900 | 2397 | 0 | 683 | 3046 | 152 | 0 | 99 | 118 | 0 | 0 | 188.135 | 106.03
4:00 | 0 | 0 | 141 | 0 | 0 | 0 | 0 | 421 | 336 |  | 0 | 380 | 281 | 0 | 15 | 0 | 300 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 12 | 30 | 20 | 8 | 0 | 76 | 75 | 0 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 65 | 0 | 12 | 0 | 6 | 12 | 38 | 0 | 0 | 0 | 300 | 270 | 208 | 0 | 0 | 51 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 10 | 25 | 12 | 126 | 72 | 0 | 16 | 0 | 43 | 25 | 50 | 48 | 163 | 0 | 60 | 85 | 0 | 158 | 0 | 0 | 10 | 280 | 16 | 8 | 0 | 0 | 0 | 0 | 18 | 0 | 17 | 0 | 12 | 17 | 0 | 403 | 60 | 17 | 17 | 0 | 70 | 0 | 17 | 52 | 26 | 12 | 0 | 16 | 0 | 0 | 17 | 0 | 35 | 0 | 27 | 17 | 310 | 17 | 0 | 612 | 0 | 142 | 0 | 0 |  | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 320 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 850 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 150 | 525 | 0 | 0 |  | 6564 | 4162 | 10726 | 3771 | 900 | 2286 | 0 | 544 | 2850 | 151 | 0 | 98 | 126 | 0 | 0 | 70.67 | 106.02
5:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 410 | 319 |  | 0 | 380 | 309 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 12 | 30 | 20 | 8 | 0 | 76 | 75 | 0 | 0 | 8 | 224 | 0 | 0 | 0 |  | 6 | 65 | 0 | 12 | 0 | 6 | 12 | 32 | 0 | 0 | 0 | 300 | 270 | 205 | 0 | 0 | 51 | 0 | 0 | 10 | 0 | 0 | 8 | 18 | 10 | 25 | 12 | 126 | 72 | 0 | 16 | 0 | 43 | 25 | 22 | 48 | 163 | 0 | 60 | 85 | 0 | 158 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 18 | 0 | 17 | 0 | 12 | 17 | 0 | 365 | 60 | 17 | 17 | 0 | 70 | 0 | 17 | 17 | 9 | 12 | 0 | 16 | 0 | 0 | 17 | 0 | 35 | 0 | 18 | 17 | 310 | 17 | 0 | 612 | 0 | 144 | 0 | 0 |  | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 320 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 800 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 150 | 526 | 0 | 0 |  | 6381 | 4085 | 10466 | 3716 | 901 | 2231 | 0 | 440 | 2803 | 151 | 0 | 98 | 126 | 0 | 0 | 61.12 | 106.01
6:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 351 | 316 |  | 0 | 340 | 260 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 12 | 30 | 20 | 8 | 0 | 76 | 75 | 0 | 0 | 8 | 225 | 0 | 0 | 0 |  | 6 | 65 | 0 | 12 | 0 | 6 | 12 | 38 | 0 | 0 | 0 | 280 | 270 | 210 | 0 | 0 | 51 | 0 | 0 | 10 | 0 | 0 | 8 | 18 | 10 | 25 | 12 | 102 | 33 | 0 | 16 | 0 | 43 | 25 | 22 | 45 | 163 | 0 | 61 | 85 | 0 | 158 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 18 | 0 | 17 | 0 | 12 | 17 | 0 | 366 | 60 | 17 | 17 | 0 | 70 | 0 | 17 | 17 | 9 | 12 | 0 | 16 | 0 | 0 | 17 | 0 | 35 | 0 | 18 | 17 | 310 | 17 | 0 | 612 | 0 | 144 | 0 | 0 |  | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 320 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 800 | 180 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 401 | 0 | 150 | 530 | 0 | 0 |  | 6158 | 3993 | 10151 | 3552 | 900 | 2100 | 0 | 440 | 2807 | 151 | 0 | 98 | 102 | 1 | 0 | 46.795 | 106
7:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 351 | 316 |  | 0 | 340 | 299 | 0 | 9 | 5 | 300 | 0 | 0 | 5 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 12 | 30 | 20 | 8 | 0 | 76 | 40 | 0 | 0 | 8 | 222 | 0 | 0 | 0 |  | 6 | 65 | 0 | 12 | 0 | 6 | 12 | 29 | 0 | 0 | 0 | 280 | 320 | 208 | 0 | 0 | 51 | 0 | 0 | 10 | 0 | 0 | 8 | 18 | 10 | 25 | 12 | 78 | 33 | 0 | 16 | 0 | 43 | 25 | 22 | 48 | 163 | 0 | 61 | 85 | 0 | 159 | 0 | 0 | 10 | 285 | 16 | 8 | 0 | 5 | 0 | 0 | 18 | 0 | 17 | 4 | 12 | 17 | 1 | 365 | 60 | 17 | 17 | 0 | 70 | 0 | 17 | 17 | 9 | 12 | 0 | 17 | 6 | 0 | 17 | 0 | 35 | 4 | 18 | 17 | 310 | 17 | 0 | 612 | 0 | 143 | 0 | 0 |  | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 320 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 800 | 180 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 401 | 4 | 150 | 527 | 25 | 0 |  | 6219 | 3944 | 10163 | 3514 | 901 | 2125 | 0 | 474 | 2803 | 116 | 0 | 98 | 78 | 54 | 0 | 21.01 | 105.99
8:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 352 | 316 |  | 0 | 340 | 313 | 0 | 17 | 15 | 300 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 12 | 30 | 20 | 8 | 0 | 76 | 40 | 0 | 0 | 8 | 223 | 0 | 0 | 0 |  | 6 | 65 | 0 | 12 | 0 | 6 | 12 | 5 | 0 | 0 | 0 | 280 | 275 | 207 | 0 | 0 | 51 | 0 | 0 | 10 | 0 | 0 | 8 | 18 | 10 | 25 | 12 | 82 | 27 | 0 | 16 | 1 | 43 | 25 | 22 | 45 | 163 | 0 | 61 | 85 | 0 | 159 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 15 | 0 | 0 | 18 | 0 | 17 | 11 | 12 | 17 | 5 | 366 | 59 | 17 | 17 | 2 | 70 | 10 | 17 | 17 | 9 | 12 | 0 | 16 | 16 | 0 | 17 | 0 | 35 | 0 | 17 | 17 | 310 | 17 | 0 | 612 | 0 | 144 | 0 | 0 |  | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 320 | 0 | 0 | 0 | 0 | 6 | 0 | 1 | 0 | 800 | 180 | 0 | 0 | 2 | 33 | 0 | 0 | 0 | 395 | 14 | 150 | 527 | 80 | 0 |  | 6218 | 4027 | 10245 | 3448 | 901 | 2126 | 0 | 516 | 2798 | 116 | 0 | 98 | 82 | 160 | 0 | 23.875 | 105.99
9:00 | 0 | 0 | 137 | 0 | 0 | 0 | 0 | 379 | 316 |  | 0 | 340 | 255 | 0 | 17 | 15 | 300 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 30 | 8 | 8 | 0 | 76 | 40 | 0 | 0 | 8 | 227 | 0 | 0 | 0 |  | 6 | 65 | 0 | 12 | 0 | 6 | 12 | 2 | 0 | 0 | 0 | 280 | 270 | 209 | 0 | 0 | 51 | 0 | 0 | 30 | 0 | 0 | 8 | 18 | 10 | 25 | 12 | 82 | 27 | 0 | 16 | 1 | 43 | 27 | 42 | 48 | 163 | 0 | 61 | 85 | 0 | 159 | 0 | 0 | 10 | 295 | 16 | 8 | 0 | 20 | 0 | 0 | 18 | 0 | 17 | 15 | 12 | 17 | 6 | 403 | 60 | 35 | 17 | 3 | 70 | 17 | 17 | 17 | 9 | 12 | 0 | 16 | 36 | 0 | 17 | 0 | 35 | 0 | 18 | 17 | 310 | 17 | 0 | 612 | 0 | 140 | 0 | 0 |  | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 340 | 0 | 0 | 0 | 0 | 6 | 0 | 4 | 0 | 800 | 220 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 402 | 23 | 150 | 525 | 126 | 0 |  | 6300 | 4217 | 10517 | 3549 | 900 | 2162 | 0 | 549 | 2799 | 116 | 0 | 98 | 82 | 262 | 0 | 21.965 | 105.98
10:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 403 | 327 |  | 0 | 300 | 307 | 0 | 17 | 15 | 280 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 19 | 11 | 25 | 8 | 8 | 0 | 76 | 40 | 0 | 0 | 8 | 218 | 0 | 0 | 0 |  | 18 | 57 | 0 | 12 | 0 | 6 | 12 | 2 | 0 | 0 | 0 | 310 | 300 | 202 | 0 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 8 | 25 | 12 | 84 | 27 | 0 | 16 | 2 | 43 | 27 | 42 | 46 | 163 | 0 | 60 | 84 | 0 | 159 | 0 | 0 | 10 | 295 | 16 | 8 | 0 | 75 | 0 | 0 | 18 | 0 | 17 | 18 | 12 | 17 | 5 | 404 | 60 | 35 | 17 | 4 | 70 | 17 | 17 | 17 | 9 | 12 | 0 | 17 | 44 | 0 | 18 | 0 | 35 | 0 | 20 | 32 | 280 | 17 | 0 | 623 | 0 | 144 | 0 | 0 |  | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 350 | 0 | 0 | 0 | 0 | 6 | 0 | 5 | 0 | 800 | 220 | 0 | 0 | 4 | 72 | 0 | 0 | 0 | 401 | 29 | 150 | 526 | 149 | 0 |  | 6476 | 4278 | 10754 | 3577 | 897 | 2215 | 0 | 634 | 2814 | 116 | 0 | 90 | 84 | 327 | 0 | 0 | 105.98
11:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 409 | 332 |  | 0 | 420 | 310 | 9 | 26 | 15 | 330 | 0 | 0 | 18 | 25 | 16 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 19 | 11 | 25 | 21 | 8 | 0 | 76 | 75 | 0 | 0 | 8 | 218 | 0 | 0 | 0 |  | 18 | 48 | 0 | 12 | 0 | 6 | 12 | 2 | 0 | 0 | 0 | 330 | 325 | 201 | 0 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 8 | 17 | 10 | 25 | 12 | 92 | 27 | 0 | 16 | 2 | 43 | 25 | 42 | 46 | 163 | 0 | 59 | 84 | 0 | 159 | 0 | 0 | 10 | 315 | 16 | 8 | 0 | 82 | 0 | 0 | 28 | 0 | 17 | 19 | 12 | 17 | 5 | 405 | 78 | 35 | 17 | 4 | 70 | 17 | 17 | 17 | 9 | 12 | 0 | 23 | 49 | 8 | 34 | 0 | 35 | 0 | 36 | 22 | 280 | 35 | 0 | 620 | 0 | 142 | 0 | 0 |  | 894 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 8 | 130 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 3 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 414 | 0 | 0 | 0 | 0 | 6 | 0 | 6 | 0 | 840 | 220 | 0 | 0 | 5 | 76 | 0 | 0 | 0 | 399 | 34 | 150 | 538 | 162 | 0 |  | 6918 | 4489 | 11407 | 3731 | 894 | 2428 | 0 | 793 | 2859 | 151 | 0 | 102 | 92 | 357 | 0 | 0 | 105.97
12:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 411 | 323 |  | 0 | 450 | 307 | 42 | 48 | 15 | 330 | 0 | 0 | 55 | 25 | 16 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 19 | 11 | 25 | 14 | 8 | 0 | 76 | 75 | 0 | 0 | 8 | 215 | 0 | 0 | 0 |  | 18 | 24 | 0 | 12 | 0 | 6 | 12 | 2 | 0 | 0 | 0 | 340 | 325 | 200 | 0 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 10 | 25 | 12 | 96 | 26 | 0 | 16 | 1 | 42 | 0 | 42 | 44 | 163 | 0 | 59 | 84 | 0 | 159 | 0 | 0 | 10 | 305 | 16 | 8 | 0 | 80 | 0 | 0 | 28 | 0 | 17 | 20 | 12 | 17 | 5 | 405 | 79 | 35 | 17 | 4 | 70 | 17 | 17 | 17 | 9 | 12 | 0 | 35 | 51 | 17 | 34 | 0 | 35 | 0 | 36 | 35 | 280 | 35 | 0 | 621 | 0 | 138 | 0 | 0 |  | 895 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 130 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 34 | 39 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 414 | 0 | 0 | 0 | 15 | 6 | 0 | 7 | 35 | 860 | 220 | 0 | 12 | 4 | 71 | 0 | 0 | 0 | 401 | 36 | 150 | 522 | 163 | 0 |  | 7014 | 4740 | 11754 | 3746 | 895 | 2435 | 0 | 1051 | 2862 | 151 | 0 | 161 | 96 | 357 | 0 | 43.93 | 105.97
13:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 408 | 321 |  | 0 | 450 | 311 | 57 | 63 | 15 | 330 | 0 | 0 | 57 | 25 | 16 | 25 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 19 | 11 | 25 | 20 | 8 | 0 | 78 | 75 | 0 | 0 | 8 | 218 | 0 | 0 | 0 |  | 18 | 24 | 0 | 12 | 0 | 6 | 12 | 2 | 0 | 0 | 0 | 291 | 285 | 188 | 0 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 10 | 25 | 12 | 100 | 25 | 0 | 16 | 2 | 41 | 0 | 42 | 43 | 163 | 0 | 59 | 84 | 0 | 159 | 0 | 0 | 10 | 310 | 16 | 8 | 0 | 80 | 0 | 0 | 28 | 0 | 17 | 19 | 12 | 17 | 5 | 405 | 79 | 35 | 17 | 4 | 70 | 17 | 17 | 17 | 9 | 12 | 0 | 50 | 48 | 17 | 34 | 0 | 35 | 0 | 36 | 35 | 315 | 35 | 0 | 533 | 0 | 140 | 0 | 0 |  | 894 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 16 | 130 | 20 | 48 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 42 | 39 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 212 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 414 | 9 | 0 | 30 | 50 | 6 | 0 | 7 | 35 | 920 | 220 | 0 | 17 | 5 | 78 | 0 | 0 | 0 | 403 | 24 | 150 | 521 | 170 | 0 |  | 6940 | 4940 | 11880 | 3682 | 894 | 2441 | 0 | 1255 | 2837 | 153 | 0 | 161 | 100 | 357 | 0 | 162.35 | 105.96
14:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 409 | 311 |  | 0 | 450 | 312 | 58 | 95 | 15 | 325 | 0 | 0 | 57 | 25 | 16 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 19 | 11 | 25 | 20 | 8 | 0 | 78 | 75 | 0 | 0 | 8 | 217 | 0 | 0 | 0 |  | 18 | 16 | 0 | 12 | 0 | 6 | 12 | 4 | 0 | 0 | 0 | 305 | 305 | 168 | 0 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 10 | 25 | 12 | 102 | 23 | 0 | 16 | 2 | 41 | 0 | 47 | 39 | 163 | 0 | 60 | 83 | 0 | 159 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 50 | 0 | 0 | 28 | 0 | 17 | 16 | 12 | 17 | 5 | 405 | 79 | 35 | 17 | 4 | 70 | 17 | 17 | 17 | 9 | 12 | 0 | 53 | 39 | 17 | 34 | 0 | 35 | 0 | 35 | 35 | 320 | 35 | 0 | 500 | 0 | 141 | 0 | 0 |  | 895 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 16 | 130 | 17 | 80 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 42 | 39 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 212 | 0 | 0 | 0 | 0 | 0 | 207 | 0 | 414 | 37 | 0 | 35 | 105 | 6 | 0 | 5 | 35 | 980 | 220 | 0 | 17 | 3 | 67 | 0 | 0 | 0 | 402 | 23 | 150 | 526 | 130 | 0 |  | 6890 | 5066 | 11956 | 3694 | 895 | 2421 | 0 | 1380 | 2869 | 153 | 0 | 153 | 102 | 289 | 0 | 156.62 | 105.97
15:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 408 | 291 |  | 0 | 450 | 288 | 62 | 86 | 15 | 325 | 0 | 0 | 57 | 25 | 16 | 23 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 19 | 11 | 33 | 20 | 8 | 0 | 77 | 75 | 0 | 0 | 8 | 219 | 0 | 0 | 0 |  | 18 | 20 | 0 | 12 | 0 | 6 | 12 | 2 | 0 | 0 | 0 | 300 | 295 | 174 | 0 | 0 | 25 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 10 | 25 | 12 | 110 | 23 | 0 | 16 | 1 | 41 | 0 | 47 | 39 | 163 | 0 | 60 | 83 | 0 | 158 | 0 | 0 | 10 | 300 | 16 | 0 | 0 | 47 | 0 | 0 | 28 | 0 | 17 | 12 | 12 | 17 | 5 | 40 | 79 | 35 | 17 | 2 | 70 | 17 | 17 | 17 | 9 | 12 | 0 | 53 | 25 | 17 | 34 | 0 | 35 | 0 | 36 | 35 | 320 | 35 | 0 | 450 | 0 | 140 | 0 | 0 |  | 894 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 16 | 130 | 18 | 64 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 42 | 38 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 207 | 0 | 380 | 51 | 0 | 35 | 69 | 6 | 0 | 4 | 35 | 1000 | 220 | 0 | 17 | 2 | 48 | 0 | 0 | 0 | 401 | 20 | 150 | 526 | 102 | 0 |  | 6376 | 4979 | 11355 | 3293 | 894 | 2342 | 0 | 1355 | 2837 | 152 | 0 | 156 | 110 | 216 | 0 | 491.825 | 106.09
16:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 412 | 292 |  | 0 | 450 | 280 | 67 | 95 | 15 | 330 | 0 | 0 | 66 | 25 | 16 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 19 | 11 | 33 | 20 | 8 | 0 | 77 | 75 | 0 | 0 | 8 | 219 | 0 | 0 | 0 |  | 18 | 24 | 0 | 12 | 0 | 6 | 12 | 2 | 0 | 0 | 0 | 280 | 280 | 202 | 0 | 0 | 10 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 10 | 25 | 12 | 114 | 27 | 0 | 16 | 1 | 42 | 0 | 47 | 46 | 163 | 0 | 60 | 83 | 0 | 158 | 0 | 0 | 10 | 290 | 8 | 0 | 0 | 47 | 0 | 0 | 18 | 0 | 17 | 6 | 12 | 17 | 7 | 404 | 60 | 35 | 17 | 1 | 70 | 17 | 17 | 17 | 28 | 12 | 0 | 53 | 12 | 17 | 34 | 0 | 47 | 0 | 36 | 35 | 360 | 17 | 0 | 450 | 0 | 142 | 0 | 0 |  | 895 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 8 | 80 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 42 | 38 | 8 | 14 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 207 | 0 | 380 | 53 | 0 | 35 | 15 | 10 | 0 | 2 | 35 | 850 | 182 | 0 | 17 | 1 | 26 | 25 | 0 | 0 | 374 | 10 | 150 | 526 | 50 | 0 |  | 6754 | 4535 | 11289 | 3631 | 895 | 2294 | 0 | 1276 | 2662 | 152 | 0 | 156 | 114 | 109 | 0 | 535.755 | 106.09
17:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 410 | 291 |  | 0 | 450 | 253 | 67 | 95 | 15 | 332 | 0 | 0 | 66 | 25 | 32 | 24 | 0 | 0 | 0 | 17 | 17 | 17 | 17 | 19 | 11 | 33 | 20 | 8 | 0 | 77 | 75 | 0 | 0 | 8 | 221 | 0 | 0 | 0 |  | 18 | 24 | 0 | 12 | 0 | 14 | 12 | 4 | 0 | 0 | 0 | 280 | 280 | 206 | 0 | 0 | 10 | 0 | 0 | 51 | 0 | 0 | 9 | 0 | 10 | 25 | 12 | 114 | 30 | 0 | 16 | 0 | 42 | 0 | 50 | 46 | 163 | 0 | 61 | 84 | 0 | 157 | 0 | 0 | 10 | 300 | 16 | 3 | 0 | 50 | 0 | 0 | 18 | 0 | 26 | 1 | 12 | 18 | 5 | 362 | 60 | 35 | 17 | 0 | 103 | 17 | 17 | 17 | 28 | 12 | 0 | 53 | 2 | 17 | 34 | 0 | 54 | 0 | 43 | 38 | 350 | 17 | 0 | 450 | 1 | 137 | 0 | 0 |  | 894 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 25 | 0 | 8 | 76 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 42 | 38 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 207 | 0 | 380 | 53 | 0 | 35 | 15 | 30 | 0 | 1 | 55 | 800 | 182 | 0 | 17 | 0 | 5 | 35 | 0 | 0 | 373 | 2 | 150 | 525 | 9 | 0 |  | 6793 | 4464 | 11257 | 3574 | 894 | 2284 | 0 | 1430 | 2605 | 152 | 0 | 183 | 114 | 20 | 1 | 518.565 | 106.08
18:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 381 | 292 |  | 0 | 450 | 310 | 66 | 95 | 15 | 325 | 0 | 0 | 66 | 58 | 98 | 24 | 0 | 0 | 0 | 35 | 35 | 55 | 17 | 19 | 11 | 33 | 20 | 14 | 0 | 77 | 75 | 0 | 0 | 9 | 221 | 0 | 0 | 0 |  | 18 | 57 | 0 | 12 | 0 | 19 | 12 | 4 | 0 | 0 | 0 | 285 | 290 | 203 | 0 | 0 | 10 | 0 | 0 | 51 | 0 | 0 | 43 | 12 | 0 | 25 | 12 | 136 | 30 | 0 | 16 | 0 | 42 | 0 | 50 | 46 | 163 | 0 | 60 | 84 | 0 | 157 | 0 | 0 | 10 | 305 | 16 | 3 | 0 | 100 | 0 | 0 | 18 | 0 | 107 | 0 | 12 | 34 | 16 | 350 | 60 | 105 | 17 | 0 | 203 | 17 | 17 | 18 | 77 | 12 | 0 | 54 | 0 | 72 | 35 | 0 | 54 | 0 | 69 | 55 | 345 | 17 | 0 | 540 | 1 | 141 | 0 | 0 |  | 894 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 32 | 0 | 8 | 132 | 27 | 16 | 0 | 0 | 0 | 26 | 0 | 92 | 0 | 42 | 38 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 16 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 414 | 53 | 0 | 35 | 15 | 60 | 0 | 0 | 55 | 860 | 220 | 0 | 17 | 0 | 0 | 112 | 0 | 0 | 501 | 0 | 150 | 524 | 0 | 0 |  | 7658 | 4952 | 12610 | 3562 | 894 | 2426 | 0 | 2177 | 2886 | 152 | 16 | 360 | 136 | 0 | 1 | 563 | 106.08
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 410 | 292 |  | 0 | 450 | 282 | 67 | 95 | 15 | 333 | 0 | 0 | 66 | 58 | 149 | 25 | 0 | 0 | 0 | 35 | 35 | 55 | 17 | 19 | 11 | 33 | 20 | 25 | 0 | 78 | 75 | 0 | 0 | 17 | 224 | 0 | 0 | 0 |  | 18 | 66 | 0 | 12 | 0 | 19 | 12 | 13 | 0 | 0 | 0 | 305 | 305 | 176 | 0 | 0 | 30 | 0 | 0 | 51 | 0 | 0 | 53 | 18 | 10 | 25 | 12 | 126 | 33 | 0 | 16 | 0 | 43 | 0 | 50 | 47 | 163 | 0 | 61 | 84 | 0 | 157 | 0 | 0 | 10 | 290 | 16 | 3 | 0 | 130 | 0 | 0 | 94 | 0 | 111 | 0 | 12 | 34 | 63 | 370 | 99 | 105 | 17 | 0 | 203 | 17 | 17 | 106 | 78 | 12 | 0 | 71 | 0 | 72 | 51 | 0 | 54 | 0 | 95 | 55 | 375 | 89 | 0 | 621 | 0 | 142 | 0 | 0 |  | 757 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 32 | 0 | 16 | 126 | 27 | 32 | 0 | 0 | 0 | 26 | 0 | 94 | 0 | 42 | 37 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 16 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 414 | 53 | 0 | 45 | 48 | 107 | 0 | 0 | 35 | 1140 | 220 | 0 | 54 | 0 | 0 | 114 | 0 | 0 | 570 | 0 | 150 | 530 | 0 | 0 |  | 8343 | 5369 | 13712 | 3731 | 757 | 2393 | 0 | 2720 | 3323 | 153 | 16 | 493 | 126 | 0 | 0 | 0 | 106.07
19:30 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 409 | 292 |  | 0 | 450 | 250 | 75 | 95 | 15 | 330 | 0 | 0 | 66 | 58 | 149 | 25 | 0 | 0 | 0 | 35 | 35 | 55 | 17 | 19 | 11 | 33 | 20 | 25 | 0 | 78 | 75 | 0 | 0 | 17 | 223 | 0 | 0 | 0 |  | 18 | 66 | 0 | 12 | 0 | 19 | 12 | 18 | 0 | 0 | 0 | 280 | 300 | 176 | 0 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 25 | 12 | 140 | 34 | 0 | 16 | 0 | 43 | 20 | 50 | 47 | 163 | 0 | 61 | 85 | 0 | 157 | 0 | 0 | 10 | 265 | 16 | 3 | 0 | 130 | 0 | 0 | 102 | 0 | 118 | 0 | 12 | 34 | 118 | 368 | 99 | 105 | 17 | 0 | 214 | 17 | 17 | 102 | 78 | 12 | 0 | 72 | 0 | 72 | 51 | 0 | 54 | 0 | 95 | 55 | 375 | 114 | 0 | 621 | 0 | 144 | 0 | 0 |  | 757 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 26 | 0 | 16 | 126 | 27 | 32 | 0 | 0 | 0 | 26 | 0 | 94 | 0 | 42 | 39 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 16 | 0 | 209 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 360 | 53 | 0 | 35 | 50 | 107 | 0 | 0 | 35 | 1244 | 222 | 0 | 54 | 0 | 0 | 114 | 0 | 0 | 571 | 0 | 150 | 530 | 0 | 0 |  | 8422 | 5410 | 13832 | 3729 | 757 | 2290 | 0 | 2803 | 3430 | 153 | 16 | 514 | 140 | 0 | 0 | 0 | 0
20:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 409 | 298 |  | 0 | 450 | 275 | 74 | 95 | 15 | 290 | 0 | 0 | 66 | 58 | 115 | 24 | 0 | 0 | 0 | 35 | 35 | 55 | 17 | 19 | 0 | 33 | 20 | 25 | 0 | 78 | 75 | 0 | 0 | 8 | 222 | 0 | 0 | 0 |  | 18 | 66 | 0 | 12 | 0 | 19 | 12 | 20 | 0 | 0 | 0 | 280 | 280 | 176 | 0 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 25 | 12 | 138 | 34 | 0 | 16 | 0 | 43 | 20 | 50 | 47 | 163 | 0 | 61 | 85 | 0 | 157 | 0 | 0 | 9 | 270 | 16 | 3 | 0 | 130 | 0 | 0 | 103 | 0 | 115 | 0 | 12 | 34 | 110 | 368 | 99 | 105 | 17 | 0 | 214 | 17 | 17 | 52 | 78 | 12 | 0 | 71 | 0 | 72 | 51 | 0 | 54 | 0 | 95 | 55 | 375 | 124 | 0 | 620 | 0 | 144 | 0 | 0 |  | 757 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 29 | 0 | 8 | 130 | 26 | 32 | 0 | 0 | 0 | 26 | 0 | 92 | 0 | 8 | 40 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 16 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 360 | 53 | 0 | 35 | 50 | 107 | 0 | 0 | 55 | 1244 | 220 | 0 | 54 | 0 | 0 | 75 | 0 | 0 | 571 | 0 | 150 | 530 | 0 | 0 |  | 8288 | 5297 | 13585 | 3607 | 757 | 2324 | 0 | 2669 | 3429 | 153 | 16 | 492 | 138 | 0 | 0 | 0 | 106.07
21:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 410 | 312 |  | 0 | 450 | 265 | 74 | 95 | 15 | 290 | 0 | 0 | 66 | 58 | 82 | 25 | 0 | 0 | 0 | 35 | 35 | 55 | 18 | 19 | 11 | 33 | 20 | 25 | 0 | 78 | 75 | 0 | 0 | 8 | 224 | 0 | 0 | 0 |  | 18 | 66 | 0 | 12 | 0 | 19 | 12 | 26 | 0 | 0 | 0 | 280 | 280 | 176 | 0 | 0 | 51 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 25 | 12 | 136 | 35 | 0 | 16 | 0 | 43 | 20 | 50 | 47 | 163 | 0 | 61 | 85 | 0 | 157 | 0 | 0 | 10 | 285 | 16 | 3 | 0 | 130 | 0 | 0 | 103 | 0 | 109 | 0 | 12 | 34 | 135 | 368 | 99 | 105 | 17 | 0 | 106 | 17 | 17 | 52 | 79 | 12 | 0 | 71 | 0 | 72 | 51 | 0 | 54 | 0 | 95 | 55 | 375 | 124 | 0 | 620 | 0 | 144 | 0 | 0 |  | 752 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 33 | 0 | 8 | 132 | 28 | 32 | 0 | 0 | 0 | 26 | 5 | 92 | 0 | 8 | 38 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 360 | 53 | 0 | 35 | 50 | 56 | 0 | 0 | 55 | 1244 | 222 | 0 | 54 | 0 | 0 | 75 | 0 | 0 | 570 | 0 | 150 | 530 | 0 | 0 |  | 8209 | 5237 | 13446 | 3626 | 752 | 2354 | 0 | 2531 | 3428 | 153 | 0 | 466 | 136 | 0 | 0 | 0 | 106.07
22:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 410 | 322 |  | 0 | 450 | 257 | 73 | 95 | 15 | 272 | 0 | 0 | 66 | 58 | 82 | 24 | 0 | 0 | 0 | 35 | 0 | 55 | 18 | 19 | 10 | 33 | 20 | 25 | 0 | 124 | 75 | 0 | 0 | 8 | 225 | 0 | 0 | 0 |  | 18 | 66 | 0 | 12 | 0 | 19 | 12 | 23 | 0 | 0 | 0 | 280 | 275 | 176 | 0 | 0 | 51 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 136 | 54 | 0 | 16 | 0 | 43 | 20 | 50 | 47 | 163 | 0 | 62 | 85 | 0 | 158 | 0 | 0 | 10 | 280 | 16 | 5 | 0 | 130 | 0 | 0 | 103 | 0 | 109 | 0 | 12 | 17 | 142 | 368 | 100 | 70 | 17 | 0 | 106 | 17 | 17 | 52 | 78 | 12 | 0 | 54 | 0 | 72 | 51 | 0 | 54 | 0 | 73 | 55 | 375 | 124 | 0 | 621 | 0 | 142 | 0 | 0 |  | 752 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 27 | 0 | 8 | 126 | 28 | 32 | 0 | 0 | 0 | 26 | 15 | 92 | 0 | 8 | 38 | 8 | 35 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 360 | 54 | 0 | 35 | 15 | 49 | 0 | 0 | 55 | 1180 | 220 | 0 | 54 | 0 | 0 | 75 | 0 | 0 | 570 | 0 | 150 | 531 | 0 | 0 |  | 8135 | 5164 | 13299 | 3628 | 752 | 2346 | 0 | 2369 | 3364 | 199 | 0 | 505 | 136 | 0 | 0 | 0 | 105.91
23:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 369 | 327 |  | 0 | 450 | 302 | 74 | 95 | 15 | 260 | 0 | 0 | 54 | 58 | 82 | 25 | 0 | 0 | 0 | 35 | 0 | 35 | 18 | 19 | 10 | 33 | 20 | 25 | 0 | 111 | 75 | 0 | 0 | 8 | 222 | 0 | 0 | 0 |  | 15 | 66 | 0 | 12 | 0 | 19 | 12 | 26 | 0 | 0 | 0 | 280 | 270 | 177 | 0 | 0 | 51 | 0 | 0 | 51 | 0 | 0 | 51 | 18 | 10 | 33 | 12 | 132 | 74 | 0 | 16 | 0 | 43 | 22 | 50 | 40 | 163 | 0 | 61 | 85 | 0 | 158 | 17 | 0 | 10 | 270 | 16 | 5 | 0 | 130 | 0 | 0 | 18 | 0 | 61 | 0 | 12 | 17 | 100 | 368 | 60 | 70 | 17 | 0 | 70 | 17 | 17 | 88 | 79 | 12 | 0 | 54 | 0 | 72 | 51 | 0 | 43 | 0 | 41 | 55 | 320 | 143 | 0 | 612 | 0 | 144 | 0 | 0 |  | 766 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 27 | 0 | 8 | 100 | 27 | 32 | 0 | 0 | 0 | 26 | 18 | 92 | 0 | 8 | 38 | 8 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 360 | 54 | 0 | 35 | 15 | 35 | 0 | 0 | 35 | 1120 | 190 | 0 | 17 | 0 | 0 | 74 | 0 | 0 | 570 | 0 | 150 | 522 | 0 | 0 |  | 7798 | 4987 | 12785 | 3525 | 766 | 2351 | 0 | 2007 | 3288 | 186 | 0 | 530 | 132 | 0 | 0 | 205.325 | 105.9
24:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 373 | 327 |  | 0 | 450 | 296 | 67 | 95 | 15 | 260 | 0 | 0 | 49 | 58 | 82 | 23 | 0 | 0 | 0 | 17 | 0 | 17 | 18 | 19 | 10 | 25 | 20 | 8 | 0 | 112 | 75 | 0 | 0 | 8 | 224 | 0 | 0 | 0 |  | 18 | 66 | 0 | 12 | 0 | 6 | 12 | 23 | 0 | 0 | 0 | 275 | 270 | 205 | 0 | 0 | 51 | 0 | 0 | 51 | 0 | 0 | 51 | 18 | 10 | 33 | 12 | 134 | 72 | 0 | 16 | 0 | 43 | 22 | 50 | 47 | 163 | 0 | 61 | 85 | 0 | 158 | 17 | 0 | 10 | 295 | 16 | 5 | 0 | 72 | 0 | 0 | 18 | 0 | 28 | 0 | 12 | 17 | 5 | 403 | 60 | 17 | 17 | 0 | 70 | 17 | 17 | 70 | 35 | 12 | 0 | 17 | 0 | 72 | 51 | 0 | 35 | 0 | 18 | 55 | 320 | 143 | 0 | 620 | 0 | 145 | 0 | 0 |  | 766 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 5 | 0 | 0 | 100 | 27 | 16 | 0 | 0 | 0 | 26 | 0 | 92 | 0 | 42 | 38 | 8 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 360 | 54 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 1150 | 190 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 571 | 0 | 150 | 525 | 0 | 0 |  | 7441 | 4932 | 12373 | 3610 | 766 | 2374 | 0 | 1481 | 3331 | 187 | 0 | 490 | 134 | 0 | 0 | 226.335 | 105.89
KWH | 0 | 0 | 3360750 | 0 | 0 | 0 | 0 | 9703420 | 7608000 |  | 0 | 9522000 | 7022109 | 963840 | 1449835 | 331670 | 7457858 | 0 | 0 | 888000 | 636480 | 924480 | 363548 | 0 | 0 | 0 | 233640 | 136254 | 406143 | 359892 | 456000 | 257040 | 777100 | 474800 | 296160 | 0 | 1956627 | 1660000 | 0 | 0 | 226902 | 5184298 | 0 | 0 | 0 |  | 330000 | 1265376 | 0 | 263160 | 0 | 233280 | 289584 | 411360 | 0 | 0 | 0 | 7524700 | 6969000 | 4719000 | 0 | 0 | 1057752 | 0 | 0 | 1027572 | 0 | 0 | 481397 | 395388 | 237960 | 637400 | 295500 | 2781120 | 973440 | 0 | 362124 | 12600 | 1008000 | 442920 | 1042800 | 1099008 | 3912300 | 0 | 1452192 | 2021760 | 0 | 3272670 | 39000 | 0 | 254340 | 7177000 | 388416 | 148464 | 0 | 1528036 | 0 | 0 | 799200 | 0 | 960336 | 134730 | 296640 | 507360 | 664072 | 9279000 | 1689600 | 997440 | 423199 | 29398 | 2150291 | 318512 | 425710 | 890340 | 801360 | 303360 | 0 | 897600 | 328560 | 646560 | 802909 | 0 | 1012680 | 0 | 992640 | 824400 | 7916900 | 1098982 | 0 | 14121817 | 480 | 3563636 | 0 | 0 |  | 20610909 | 0 | 0 | 0 | 745920 | 0 | 0 | 0 | 216000 | 0 | 164625 | 2808000 | 537477 | 443232 | 0 | 0 | 0 | 162962 | 22355 | 929296 | 0 | 415192 | 443764 | 120192 | 117130 | 0 | 0 | 243720 | 0 | 0 | 4159900 | 35000 | 0 | 5055291 | 0 | 0 | 0 | 0 | 0 | 5023073 | 0 | 9109672 | 653760 | 0 | 553248 | 518976 | 676905 | 0 | 40983 | 600576 | 25194100 | 5123564 | 0 | 367200 | 28440 | 550080 | 629184 | 0 | 0 | 10676360 | 215965 | 3665500 | 12654545 | 1174280 | 0 |  | 169589177 | 114687376 | 284276553 | 88570652 | 20610909 | 55868962 | 0 | 31061564 | 74035858 | 3616627 | 35000 | 5180345 | 2781120 | 2515036 | 480 | 0
Fuel Cost | 0 | 0 | 4906695 | 0 | 0 | 0 | 0 | 10188591 | 8216640 |  | 0 | 10378980 | 7794540.99 | 10775731.2 | 19210313.75 | 4394627.5 | 8352800.96 | 0 | 0 | 12982560 | 8955273.6 | 14985820.8 | 3351912.56 | 0 | 0 | 0 | 2971900.8 | 1839429 | 5446377.63 | 269919 | 342000 | 0 | 0 | 0 | 5037681.6 | 0 | 528289.29 | 448200 | 0 | 0 | 3709847.7 | 5391669.92 | 0 | 0 | 0 |  | 4306500 | 21106471.68 | 0 | 3555291.6 | 0 | 2699049.6 | 367771.68 | 1369828.8 | 0 | 0 | 0 | 8352417 | 7596210 | 5474040 | 0 | 0 | 1195259.76 | 0 | 0 | 1716045.24 | 0 | 0 | 6474789.65 | 541681.56 | 178470 | 1115450 | 221625 | 19968441.6 | 1061049.6 | 0 | 492488.64 | 200844 | 1380960 | 584654.4 | 1814472 | 1901283.84 | 4499145 | 0 | 2817252.48 | 4609612.8 | 0 | 3305396.7 | 83850 | 0 | 503593.2 | 7177000 | 291312 | 112832.64 | 0 | 20857691.4 | 0 | 0 | 10773216 | 0 | 13300653.6 | 1574993.7 | 3061324.8 | 6930537.6 | 8812235.44 | 8536680 | 20545536 | 14422982.4 | 5353467.35 | 457432.88 | 25244416.34 | 3468595.68 | 4525297.3 | 12081913.8 | 10329530.4 | 3573580.8 | 0 | 11623920 | 4747692 | 8204846.4 | 9137104.42 | 0 | 13225600.8 | 0 | 14859820.8 | 10857348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 61832727 | 0 | 0 | 0 | 7765027.2 | 0 | 0 | 0 | 3890160 | 0 | 2365661.25 | 3144960 | 1042705.38 | 4831228.8 | 0 | 0 | 0 | 2732872.74 | 390988.95 | 14534189.44 | 0 | 6875579.52 | 7504049.24 | 1638216.96 | 1975983.1 | 0 | 0 | 184496.04 | 0 | 0 | 35275952 | 1470700 | 0 | 5864137.56 | 0 | 0 | 0 | 0 | 0 | 5826764.68 | 0 | 9018575.28 | 8786534.4 | 0 | 6544923.84 | 7499203.2 | 8596693.5 | 0 | 452862.15 | 7290992.64 | 209111030 | 5226035.28 | 0 | 2717280 | 321656.4 | 6452438.4 | 9645390.72 | 0 | 0 | 97048112.4 | 0 | 43876035 | 108196359.75 | 0 | 0 |  | 514061310.68 | 699930522.82 | 1213991833.5 | 88181435.62 | 61832727 | 65268457.81 | 0 | 401457637.55 | 493507489.15 | 976489.29 | 1470700 | 67120535.95 | 19968441.6 | 14207919.53 | 0 | 0
Yesterday Day Peak | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 411 | 323 |  | 0 | 450 | 307 | 42 | 48 | 15 | 330 | 0 | 0 | 55 | 25 | 16 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 19 | 11 | 25 | 14 | 8 | 0 | 76 | 75 | 0 | 0 | 8 | 215 | 0 | 0 | 0 |  | 18 | 24 | 0 | 12 | 0 | 6 | 12 | 2 | 0 | 0 | 0 | 340 | 325 | 200 | 0 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 10 | 25 | 12 | 96 | 26 | 0 | 16 | 1 | 42 | 0 | 42 | 44 | 163 | 0 | 59 | 84 | 0 | 159 | 0 | 0 | 10 | 305 | 16 | 8 | 0 | 80 | 0 | 0 | 28 | 0 | 17 | 20 | 12 | 17 | 5 | 405 | 79 | 35 | 17 | 4 | 70 | 17 | 17 | 17 | 9 | 12 | 0 | 35 | 51 | 17 | 34 | 0 | 35 | 0 | 36 | 35 | 280 | 35 | 0 | 621 | 0 | 138 | 0 | 0 |  | 895 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 130 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 34 | 39 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 414 | 0 | 0 | 0 | 15 | 6 | 0 | 7 | 35 | 860 | 220 | 0 | 12 | 4 | 71 | 0 | 0 | 0 | 401 | 36 | 150 | 522 | 163 | 0 |  | 11754 | DayPeak
Yesterday Evening Peak | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 409 | 292 |  | 0 | 450 | 250 | 75 | 95 | 15 | 330 | 0 | 0 | 66 | 58 | 149 | 25 | 0 | 0 | 0 | 35 | 35 | 55 | 17 | 19 | 11 | 33 | 20 | 25 | 0 | 78 | 75 | 0 | 0 | 17 | 223 | 0 | 0 | 0 | 0 | 18 | 66 | 0 | 12 | 0 | 19 | 12 | 18 | 0 | 0 | 0 | 280 | 300 | 176 | 0 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 25 | 12 | 140 | 34 | 0 | 16 | 0 | 43 | 20 | 50 | 47 | 163 | 0 | 61 | 85 | 0 | 157 | 0 | 0 | 10 | 265 | 16 | 3 | 0 | 130 | 0 | 0 | 102 | 0 | 118 | 0 | 12 | 34 | 118 | 368 | 99 | 105 | 17 | 0 | 214 | 17 | 17 | 102 | 78 | 12 | 0 | 72 | 0 | 72 | 51 | 0 | 54 | 0 | 95 | 55 | 375 | 114 | 0 | 621 | 0 | 144 | 0 | 0 |  | 757 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 26 | 0 | 16 | 126 | 27 | 32 | 0 | 0 | 0 | 26 | 0 | 94 | 0 | 42 | 39 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 16 | 0 | 209 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 360 | 53 | 0 | 35 | 50 | 107 | 0 | 0 | 35 | 1244 | 222 | 0 | 54 | 0 | 0 | 114 | 0 | 0 | 571 | 0 | 150 | 530 | 0 | 0 |  | 13832 | EvPeak
Forecast for Evening | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 412 | 330 |  | 0 | 450 | 300 | 75 | 95 | 15 | 335 | 0 | 0 | 65 | 92 | 149 | 44 | 0 | 0 | 0 | 35 | 35 | 55 | 17 | 19 | 18 | 33 | 24 | 25 | 0 | 122 | 75 | 0 | 0 | 17 | 225 | 0 | 0 | 0 |  | 18 | 70 | 0 | 25 | 0 | 40 | 12 | 18 | 0 | 0 | 0 | 300 | 300 | 210 | 0 | 0 | 50 | 0 | 0 | 51 | 0 | 47 | 52 | 18 | 11 | 33 | 12 | 165 | 65 | 0 | 19 | 0 | 43 | 30 | 50 | 48 | 163 | 0 | 60 | 86 | 0 | 158 | 17 | 0 | 10 | 300 | 16 | 11 | 0 | 130 | 0 | 0 | 100 | 0 | 105 | 0 | 12 | 17 | 150 | 400 | 99 | 105 | 17 | 0 | 270 | 17 | 17 | 114 | 75 | 12 | 0 | 72 | 0 | 72 | 51 | 0 | 54 | 0 | 95 | 55 | 300 | 160 | 0 | 600 | 10 | 150 | 0 | 0 |  | 750 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 26 | 51 | 24 | 130 | 28 | 110 | 0 | 0 | 0 | 31 | 16 | 92 | 28 | 42 | 39 | 8 | 30 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 400 | 53 | 0 | 50 | 105 | 107 | 0 | 0 | 55 | 1244 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 520 | 0 | 150 | 525 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 410 | 330 | 0 | 0 | 450 | 300 | 66 | 80 | 15 | 335 | 0 | 0 | 55 | 80 | 16 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 18 | 33 | 24 | 8 | 0 | 122 | 40 | 0 | 0 | 8 | 225 |  | 0 | 0 | 0 | 18 | 65 | 0 | 25 | 0 | 6 | 12 | 10 | 0 | 0 | 0 | 300 | 300 | 210 | 0 | 0 | 50 | 0 | 0 | 51 | 0 | 0 | 16 | 18 | 11 | 33 | 12 | 149 | 32 | 0 | 19 | 1.6 | 43 | 30 | 50 | 48 | 163 | 0 | 60 | 86 | 0 | 158 | 17 | 0 | 10 | 300 | 16 | 11 | 0 | 80 | 0 | 0 | 18 | 0 | 17 | 20 | 12 | 17 | 6 | 400 | 60 | 35 | 17 | 5 | 70 | 17 | 17 | 17 | 27 | 12 | 0 | 17 | 50 | 17 | 34 | 0 | 35 | 35 | 36 | 55 | 300 | 33 |  | 600 | 10 | 150 | 0 |  |  | 910 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 28 | 34 | 30 | 8 | 24 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 380 | 35 | 0 | 35 | 100 | 30 | 0 | 8 | 35 | 1000 | 220 |  | 38 | 6 | 100 | 70 | 0 |  | 450 | 30 | 150 | 525 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 372 | 334 | 0 | 0 | 400 | 302 | 0 | 17 | 0 | 260 | 0 | 0 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 4 | 25 | 22 | 8 | 0 | 122 | 75 | 0 | 0 | 8 | 224 | 0 | 0 | 0 | 0 | 6 | 40 | 0 | 12 | 0 | 6 | 12 | 7 | 0 | 0 | 0 | 315 | 270 | 184 | 0 | 0 | 51 | 0 | 0 | 10 | 0 | 0 | 16 | 18 | 8 | 33 | 12 | 106 | 26 | 0 | 16 | 1 | 43 | 22 | 50 | 48 | 163 | 0 | 40 | 85 | 0 | 157 | 17 | 0 | 10 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 18 | 0 | 17 | 10 | 12 | 17 | 5 | 371 | 60 | 17 | 17 | 2 | 16 | 13 | 17 | 17 | 9 | 12 | 0 | 17 | 19 | 0 | 17 | 0 | 35 | 13 | 18 | 17 | 280 | 145 | 0 | 500 | 0 | 146 | 0 | 0 | 0 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 840 | 220 | 0 | 0 | 2 | 29 | 0 | 0 | 0 | 373 | 12 | 150 | 523 | 66 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
[22 empty] | 299565 | [26 empty] | 399366 | [49 empty] | 299523 |  | 299563 |  | 399588 |  | 299281 | 299229 | 299524 |  | 399747 |  |  |  |  | 399575 | 399337 | 399589 | [8 empty] | 399245 |  |  | 399274 |  | 399226 |  | 399630 | [12 empty] | 599468 | [34 empty] | 499268 | 599634 |  |  |  | 499720 | [19 empty] | 292.3904
| Minimum Generation |  | 10151 | 6:00 | [202 empty] | 144439614
| Highest Generation |  | 13832 | 19:30 | [202 empty] | 144.4396 |  |  |  |  | 2.515
| Day Peak Generation |  | 11754 | 12:00 | [202 empty] | 36276909
| Evening Peak Generation |  | 13832 | 19:30 | [202 empty] | 36.2769 |  |  | 55868962 |  | 3.6166
| HVDC Max Flow |  | 901 | 5:00 | [202 empty] | 20.6109 |  |  |  |  | 0.00048
| HVDC EvPeak Flow |  | 757 | 19:30 | [200 empty] | 284276553 |  | 2.7811 |  | 74.0359
| Load factor L.F |  | 85.63% | [166 empty] | 1275.5 | [36 empty] | 284.2766

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-10-18
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-10-17 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 11754 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 10120
Evening Peak Generation : |  |  | 13832 | MW Hour : | 19:30 | Available Max Generation : |  | 14730
E.P. Demand (at gen end) : |  |  | 13832 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 14000
Maximum Generation : |  |  | 13832 | MW Hour : | 19:30 | Reserve(Generation end) |  | 730
Total Gen. (MKWH) : |  |  | 284.2766 | System Load Factor : | 85.63% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 232 | MW at | 20:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-10-18
Actual : |  | 105.84 | Ft.(MSL) , | Rule curve : | 107.6 | Ft.( MSL )
Gas Consumed : |  | Total = | 1059.11 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 153449893.43
: |  |  | Coal : | 493507489.15 | Oil : | 470048873.5 | Total : | 1117006256.08
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4857.5703 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1336.484 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1872.677 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1628.1782 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1339.4547 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 996.477 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 558.2777 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 465.5121 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 910.4541 |  |  | 0 | 0%
Total |  | 0 |  | 13965.0851 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:17 | 14:59 | Palashbari 132/33kV S/S TR1-414T LT Scheduled S/D Due to Annual maintenance
08:18 | 14:59 | Palashbari 132/33kV S/S TR1-414T HT Scheduled S/D Due to Annual maintenance
08:20 | 16:12 | Saidpur 132/33kV S/S TR-3 (424T) LT Scheduled S/D Due to Annual maintenance
08:20 | 16:44 | Jaldhaka 132/33kV S/S Bus A Scheduled S/D Due to Annual maintenance
08:22 | 16:11 | Saidpur 132/33kV S/S TR-3 (424T) HT Scheduled S/D Due to Annual maintenance
08:36 | 17:37 | Chandraghona-Madunaghat 132 kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end Due to Annual shutdown and from
Chandraghona 132/33kV end Due to Annual maintenance
08:40 | 16:33 | Panchagarh 132/33kV S/S T-1(407T) LT Scheduled S/D Due to Annual Maintenance.
| 08:40 | Chowmuhani-Feni 132 kV Ckt-1 is restored.
08:40 | 16:33 | Panchagarh 132/33kV S/S T-1(407T) HT Scheduled S/D Due to Annual Maintenance.
08:45 | 15:45 | Ashuganj-Kishoreganj 132kV Ckt-1 Scheduled S/D from Ashuganj 230/132/33kV end Due to Annual maintenance of
kishoreganj end.
08:56 | 09:03 | Ashuganj-Kishoreganj 132kV Ckt-2 Tripped from Ashuganj 230/132/33kV end showing 1)Distance B and C phase 2)
Zone-2 relays.
09:07 | 15:53 | Jamalpur-Mymensingh 132kV Ckt-1 Scheduled S/D from Jamalpur 132/33kV end Due to Annual Maintenance work
09:11 | 16:21 | Mongla 132/33kV S/S T-2 LT Scheduled S/D Due to Annual maintenance |  |  |  |  | 5.0MW load interrup.
09:12 | 15:39 | Mongla 132/33kV S/S T-2 HT Scheduled S/D Due to Annual maintenance |  |  |  |  | 5.0MW load interrup.
09:20 |  | Rangpur 132 kV Bus-Coupler Breaker S/D
09:23 | 16:20 | Bashundhara-Tongi 132 kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Annual maintenance work
09:26 | 15:46 | Ashuganj-Kishoreganj 132kV Ckt-1 Scheduled S/D from Kishoreganj 132/33kV end Due to For A/M
09:31 | 13:08 | Jhenaidah 230/132kV S/S Transformer- 1 LT Project Work S/D Due to Transformer colling fan maintenance
09:32 | 13:03 | Jhenaidah 230/132kV S/S Transformer- 1 HT Project Work S/D Due to Transformer colling fan maintenance
09:43 | 16:06 | Joydebpur-Kodda B 132 kV Ckt-2 Scheduled S/D from Joydebpur 132/33kV end Due to Annual maintenance.
| 09:44 | Gollamari 132/33kV S/S Tr-2 HT is restored.
| 09:45 | Gollamari 132/33kV S/S Tr-2 LT is restored.
09:48 | 11:47 | Rajbari 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Annual maintenance work
09:48 | 11:48 | Rajbari 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Annual maintenance work
09:50 | 13:13 | Mirpur-Uttara 132kV Ckt-1 Tripped from Mirpur 132/33kV end showing main protection trip relay. relays Due to When
Uttara old ckt loaded then Uttara old & Bus coupler CB Triped .
09:54 | 15:27 | Khulna (C) S/S Tr-3 405T LT Scheduled S/D Due to Annual Maintanance
09:55 | 15:26 | Khulna (C) S/S Tr-3 405T HT Scheduled S/D Due to Annual Maintanance
10:16 | 15:28 | Mirsorai 230/33kV S/S Bus-1 Scheduled S/D Due to Annual Maintanance
10:48 | 13:25 | Baghabari-Shahjadpur 132 kV Ckt-1 Forced S/D from Shahjadpur 132/33kV end Due to Maintenance work at
Baghabari Power Station
11:03 | 12:39 | Ashuganj-Kishoreganj 132kV Ckt-2 Tripped from Ashuganj 230/132/33kV end showing Distance C Phase. relays. and from |  |  |  |  | 40.0MW load interrup.
|  | Kishoreganj 132/33kV end showing Distance-5.5km Zone-01 relays. |  |  |  |  | Kishoreganj 132/33kV end.
12:00 |  | Day Peak Gen. 11754 MW
12:05 |  | Rangpur 132 kV Bus-Coupler Breaker Sync
12:18 |  | Rampura 230/132kV S/S Capacitor Bank- 1 Tripped showing UBCR1 relays Due to Cell to cell loop problem
12:19 | 13:13 | Jhenaidah 132/33kV S/S Jhenaidah-Jhenaidah New-1,132kV Circuit-1(L4) Forced S/D Due to Jhenaidah 230/132 kV
Transformer Over Load
12:20 | 13:14 | Jhenaidah 132/33kV S/S Jhenaidah-Jhenaidah New-2,132kV Circuit-2(L3) Forced S/D Due to Jhenaidah 230/132 kV
Transformer Over Load
12:23 | 13:14 | Jhenaidah-Jhenaidah(New) 132kV Ckt-3 Forced S/D from Jhenaidah 132/33kV end Due to Jhenaidah 230/132 kV
Transformer Over Load
12:46 | 16:46 | Cox'sbazar-Dohazari 132 kV Ckt-2 Scheduled S/D from Coxsbazar 132/33kV end Due to Distance Relay installation
| 13:01 | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-2 is restored.
| 13:01 | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-1 is restored.
13:25 | 16:18 | Baghabari 230/132kV S/S T-1 HT Forced S/D Due to Loop Maintenance for PDB 132 kv Side
13:25 | 16:18 | Baghabari 230/132kV S/S T-1 LT Forced S/D Due to Loop Maintenance for PDB 132 kv Side.
13:58 | 17:48 | HVDC Bheramera- Rajshahi 230kV Ckt-1 Project Work S/D from BIPTC end Due to Ruppur power evacuation project.
13:58 | 17:48 | Rajshahi 230/132/33kV S/S 230 Kv BIPTC Ckt-01 Scheduled S/D
13:59 | 17:49 | Rajshahi 230/132/33kV S/S 230 Kv BIPTC Ckt-02 Scheduled S/D
13:59 | 17:49 | HVDC Bheramera- Rajshahi 230kV Ckt-2 Project Work S/D from BIPTC end Due to Ruppur power evacuation project.
| 14:36 | Bagerhat 132/33kV S/S Transformer-1 (403T) HT is restored.
| 14:37 | Bagerhat 132/33kV S/S Transformer-1 (403T) LT is restored.
14:42 | 16:20 | Mongla 132/33kV S/S T-1 LT Tripped showing Earth fault (ins) relays Due to Unwanted flashing of 33kv bus section |  |  |  |  | 28.0MW load interrup.
That's why T1-A tripped.
| 15:44 | Hasnabad 230/132kV S/S AUTO TR-2 HT is restored.
| 15:45 | Hasnabad 230/132kV S/S AUTO TR-2 LT is restored.
15:53 | 16:20 | Maniknagar 132/33kV S/S Motijheel Ckt-1 Scheduled S/D Due to Motijheel Ckt -1 SCADA work. (Motijheel end, shut down
by DPDC)
| 16:06 | Joydebpur-Kodda B 132 kV Ckt-2 is restored.
16:25 | 16:55 | Maniknagar 132/33kV S/S Motijheel Ckt-2 Scheduled S/D Due to Motijheel Ckt -2 SCADA work .(Motijheel end, Shut down
by DPDC)
17:35 | 20:26 | Naogaon 132/33kV S/S Nao-SPPP Ckt-1 Forced S/D Due to measuring PT Check and Maintanance.
19:30 |  | Evening peak generation: 13832 MW
21:54 | 22:19 | Pabna- Shahjadpur 132kV Ckt-1 Tripped from Shahjadpur 132/33kV end showing Distance Relay, Phase B relays.
06:00 |  | Minimum generation: 10120 MW.
07:05 |  | Bagerhat 132/33kV S/S Transformer-1 (403T) LT Scheduled S/D Due to Annual maintenance work
07:06 |  | Bagerhat 132/33kV S/S Transformer-1 (403T) HT Scheduled S/D Due to Annual maintenance work
07:35 |  | Barishal-Barishal(N) 132 kV Ckt-2 Forced S/D from Barishal 230/132kV end Due to From barishal south and from Barishal
132/33kV end Due to For Bypass DS Work
07:35 |  | Barishal-Barishal(N) 132 kV Ckt-2 Forced S/D from Barishal 230/132kV end Due to From barishal south and from Barishal
132/33kV end Due to For Bypass DS Work
07:35 |  | Barishal-Barishal(N) 132 kV Ckt-2 Forced S/D from Barishal 230/132kV end Due to From barishal south and from Barishal
132/33kV end Due to For Bypass DS Work
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-10-17 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 140 | 3360750 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 409 | 9703420
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 292 | 7608000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9522000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 75 | 963840 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 250 | 7022109 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 95 | 1449835 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 331670 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 25 | 363548 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 17 | 359892 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 66 | 888000 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 7457858
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 58 | 636480 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 233640 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 924480
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 136254 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 406143
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 30 | 713040 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 777100
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 20 | 474800 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 296160 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 130 | 1528036 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 118 | 960336 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 997440
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 72 | 897600 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 646560 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 824400
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5422 | 3156 | 59483391
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 226902 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 134730
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 233280 | Machine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 153 | 3616627 | #01 under maint.
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 223 | 5184298
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 423199 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 66 | 1265376 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 12 | 263160 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 296640 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 12 | 289584 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 18 | 411360
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29398
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 214 | 2150291 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 318512 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 425710 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 303360 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 51 | 802909 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 114 | 1098982 | Fuel shortage
| SS Power I |  | SS Power | 1*612 | 612 | 621 | 14121817
| Cox's Bazar Wind |  | IPP | 66 | 0 | 0 | 480 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 144 | 3563636 | On test.
| Chattogram area Total |  |  |  | 3157 | 1739 | 35160251
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 176 | 4719000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7524700 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 6969000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 375 | 7916900 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 50 | 1057752
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1027572
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 118 | 664072 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 507360 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 395388 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 237960
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 140 | 2781120
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 637400 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 481397
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 12 | 295500 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 102 | 890340 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 78 | 801360 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 54 | 1012680
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 95 | 992640 | Fuel shortage
| Cumilla Area Total |  |  |  | 2896 | 1970 | 38912141
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 34 | 973440 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 362124 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12600
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 102 | 799200 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 99 | 1689600 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 328560
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 330000 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 269 | 4495524
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1008000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 20 | 442920 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3912300
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1042800
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 47 | 1099008
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 3 | 148464 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1452192
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 2021760
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 157 | 3272670 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 39000 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 388416 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 265 | 7177000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 368 | 9279000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 254340
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 0 | 0 | Under maint.
| Sylhet Area Total |  |  |  | 2427 | 1288 | 31537870
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 757 | 20610909
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 81 | 745920 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 26 | 216000 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 16 | 164625 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 653760 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 50 | 518976 | High voltage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 550080
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | TG Test
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 571 | 10676360
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 1554 | 34136630
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 443232 | Engine problem
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 27 | 537477 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 126 | 2808000 | ST Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 25194100
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 222 | 5123564
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 367200 | High voltage
| Barisal 307 MW |  | IPP | 307*1 | 307 | 150 | 3665500 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1855 | 38139073
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 26 | 162962 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 22355 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Fuel shortage
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 415192 | Fuel shortage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 39 | 443764 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 209 | 5055291
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 205 | 5023073
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 360 | 9109672
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 117130 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 243720
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 120192 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 929296 | High voltage
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 553248 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 600576 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 28440
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 530 | 12654545 | Coal shortage
| Rajshahi Area Total |  |  |  | 3631 | 1594 | 35479456
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4159900 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 35000
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 676905 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 40983
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 114 | 629184
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 215965
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1174280
| Rangpur Area Total |  |  |  | 950 | 407 | 6932217
| Total |  |  |  | 24599 | 13832 | 284276553
| Eastern Grid Total |  |  |  | 14516 | 8422 | 169589177
| Western Grid Total |  |  |  | 10083 | 5410 | 114687376
| National Grid Total |  |  |  | 24599 | 13832 | 284276553
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-10-17
| (a) ENTIRE EASTERN GRID : |  | 9192.77 | MW | (b) ENTIRE WESTERN GRID : |  | 4042.7 | MW
| i) Dhaka area |  | 4993.27 | MW | i) Khulna area |  | 1559.9 | MW
| ii) Chittagong area |  | 1268 | MW | ii) Rajshahi area |  | 1309.8 | MW
| iii) Comilla area |  | 1299.5 | MW | iii) Barisal area |  | 411 | MW
| iv) Mymensingh area |  | 1093 | MW | iv) Rangpur area |  | 762 | MW
| v) Sylhet area |  | 539 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 13235.47 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 29 | 20:00 | Kamrangirchar | 66 | 13:00 | Narshingdi | 188 | 21:00 | Shikalbaha | 29 | 00:00
2 | AKSML | 104 | 13:00 | Chowmuhani | 221 | 21:00 | Kaptai | N/A | N/A | Natore | 128 | 19:30 | Shikalbaha-230 | N/A | N/A
3 | Aftabnagar | 34 | 13:00 | Chuadanga | 100 | 18:30 | Kazla | 106 | 12:00 | Nawabganj | 40.4 | 22:00 | Shitalakhya | 104.1 | 15:00
4 | Agargaon | 86 | 13:00 | Coxsbazar | 126 | 18:00 | Keranigonj | 60 | 18:00 | Netrakona | 120 | 19:30 | Sholosohor | 44 | 18:00
5 | Agrabad | 78 | 18:00 | Cumilla(N) | 178 | 19:30 | Khagrachori | 28 | 18:00 | New | 80 | 12:00 | Shyampur | 132 | 01:00
6 | Amnura | 44 | 19:00 | Cumilla(S) | 140 | 01:00 | Khulna | 86 | 18:00 | Niamatpur | 65 | 21:00 | Siddhirganj | 114 | 15:00
7 | Ashuganj | 79.5 | 19:00 | Daudkandi | 136 | 19:30 | Khulshi | 178 | 18:30 | Noapara | 45 | 18:00 | Sirajganj | 112 | 19:00
8 | BIPTC | N/A | N/A | Dhaka | 30 | 11:00 | Kishoreganj | 130 | 19:00 | PHP | 9 | 11:00 | Sonargaon | 106 | 01:00
9 | BSRM | 134 | 01:00 | Dhamrai | 132 | 18:30 | Kodda | 294 | 19:00 | Pabna | 109 | 19:00 | Sreemongol | 63 | 18:00
10 | Bagerhat | 85 | 18:30 | Dhanmondi | 130 | 13:00 | Kulaura | 44 | 18:30 | Palashbari | 100 | 18:30 | Sreepur | 78.1 | 18:00
11 | Bakulia | 101 | 19:00 | Dohazari | 82 | 18:30 | Kurigram | 60 | 18:00 | Panchagarh | 52 | 18:30 | Srinagar | 41.76 | 22:00
12 | Banani | 50.2 | 13:00 | Faridpur | 141 | 18:30 | Kushtia | 134 | 18:30 | Patuakhali | 97 | 22:00 | Sunamganj | 48 | 18:30
13 | Bangabhaban | 14 | 10:00 | Fatullah | 65 | 12:00 | Lalbag | 90 | 13:00 | Payra | 24.2 | 22:00 | Sylhet | 14 | 18:00
14 | Barapukuria | 55 | 18:00 | Fenchuganj | 38 | 19:00 | Lalmonirhat | 44 | 18:00 | Postogola | 58 | 12:00 | Sylhet-132 | 140 | 19:00
15 | Barguna | 18 | 00:00 | Feni | 106 | 22:00 | MI_Cement | 19.5 | 15:00 | Purbachal | 21 | 00:00 | TK | 30.5 | 18:00
16 | Barishal | 100 | 18:00 | GPH | 13 | 04:00 | Madanganj | 42 | 18:00 | Purbasadipur | 110 | 18:30 | Tangail | 217 | 19:30
17 | Barishal-230 | 76 | 19:30 | Ghorashal | 72 | 20:00 | Madaripur | 95 | 21:00 | Rahim | 41 | 00:00 | Thakurgaon | 81 | 19:00
18 | Baroaulia | 68 | 01:00 | Goalpara | 38 | 13:00 | Madartek | 78.98 | 00:00 | Rajbari | 68 | 18:30 | Tongi | 101 | 18:30
19 | Baroirhat | 54 | 18:30 | Gollamari | 64 | 13:00 | Madunaghat | 55 | 18:00 | Rajendrapur | 92 | 19:00 | Ullon | 36 | 22:00
20 | Bashundhara | 166 | 13:00 | Gopalganj | 97.7 | 19:00 | Magura | 60 | 18:00 | Rajshahi | 137 | 20:00 | Uttara | 70 | 11:00
21 | BashundharaCement | 6 | 11:00 | Gulshan | 122 | 13:00 | Mahasthangarh | 70 | 18:30 | Rajshahi-230 | 32 | 22:00 | UttaraNew | 45 | 00:00
22 | Beanibazar | 66 | 18:30 | Halishahar | 81.5 | 15:00 | Manikganj | 107 | 19:30 | Ramganj | 108 | 20:00 | Zigatola | 72 | 16:00
23 | Benapole | 58 | 18:30 | HaripurSBU | 156 | 10:00 | Maniknagar | 98 | 13:00 | Rampur | 30 | 18:00
24 | Bhaluka | 150 | 19:30 | Hasnabad | 104 | 18:30 | Matarbari | 43 | 19:30 | Rangamati | 18 | 18:00
25 | Bhandaria | 54 | 19:30 | Hathazari | 68 | 18:00 | Matuail | 74 | 10:00 | Rangpur | 115 | 18:30
26 | Bhangura | 32 | 19:00 | Ishurdi | 68 | 18:00 | Millgate | 101 | 15:00 | Ruppur | 5.6 | 10:00
27 | Bheramara(GK) | 57 | 18:30 | Jaldhaka | 68 | 19:00 | Mirpur | 134 | 18:00 | SSM | 0 | 00:00
28 | Bhulta | 244 | 18:30 | Jamalpur | 147 | 19:30 | Mirsorai | 4 | 00:00 | Saidpur | 92 | 18:00
29 | Bog-Sherpur | 60 | 18:30 | Jashore | 125 | 18:30 | Mithapukur | 66 | 18:00 | Satkhira | 110 | 20:00
30 | Bogura | 142 | 18:30 | Jhenaidah | 123 | 18:00 | Modern | 0 | 00:00 | Satmasjid | 106 | 18:00
31 | Borhanuddin | 50 | 00:00 | Joydebpur | 176 | 18:30 | Mogbazar | 125.3 | 13:00 | Savar | 194 | 18:00
32 | Brahmanbaria | 175 | 20:00 | Joypurhat | 49 | 22:00 | Mongla | 36 | 00:00 | SevenRings | 9.55 | 17:00
33 | Cantonment | 122 | 12:00 | Juldah | 20 | 07:00 | Motijheel | 38 | 11:00 | ShahCement | 25 | 10:00
34 | Chandpur | 69 | 18:30 | KSRM | 33 | 17:00 | Munshiganj | 96 | 00:00 | Shahjadpur | 103 | 19:30
35 | Chandraghona | 30 | 18:00 | Kabirpur | 300 | 18:30 | Mymensingh | 219 | 21:00 | Shahjibazar | 112 | 22:00
36 | Chapai | 60 | 21:00 | Kachua | 72 | 19:00 | Naogaon | 119 | 21:00 | Shahmirpur | 50 | 01:00
37 | Charsaidpur | 29 | 16:00 | Kallyanpur | 105 | 00:00 | Narail | 55 | 18:00 | Shariatpur | 70 | 19:30
38 | Chauddagram | 57 | 19:00 | Kalurghat | 32 | 09:00 | Narinda | 73 | 13:00 | Sherpur | 122 | 19:30
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-10-17 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 400 | 06:00 | 386 | 12:00 | Gopalganj | 408 | 06:00 | 396 | 12:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 386 | 17:00 | 369 | 12:00
| Bhulta | 401 | 22:00 | 389 | 12:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 408 | 22:00 | 395 | 12:00 | Payra | 415 | 06:00 | 409 | 18:30
| BIPTC | 404 | 05:00 | 394 | 18:30 | Rahanpur | 413 | 17:00 | 405 | 18:00
| Bogura | N/A | N/A | N/A | N/A | Rampal | 409 | 06:00 | 397 | 11:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 235 | 06:00 | 223 | 12:00 | Hasnabad | 234 | 17:00 | 228 | 14:00
| AKSML | 232 | 21:00 | 224 | 12:00 | Hathazari | 233 | 20:00 | 223 | 12:00
| Aminbazar | 237 | 04:00 | 224 | 18:30 | Ishurdi | 234 | 04:00 | 223 | 11:00
| Ashuganj | 238 | 07:00 | 232 | 10:00 | Jhenaidah | 228 | 06:00 | 216 | 19:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 236 | 22:00 | 226 | 11:00
| Baghabari | 230 | 00:00 | 224 | 10:00 | Keranigonj | 234 | 06:00 | 224 | 12:00
| Barapukuria | 225 | 17:00 | 220 | 00:00 | Khulna(S) | 232 | 05:00 | 224 | 12:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 237 | 08:00 | 233 | 00:00 | Maniknagar | 234 | 06:00 | 224 | 12:00
| Bheramara | 234 | 06:00 | 222 | 11:00 | Meghnaghat | 242 | 04:00 | 237 | 11:00
| Bhulta | 239 | 22:00 | 229 | 12:00 | Mirsorai | 236 | 23:00 | 225 | 12:00
| Bibiana | 236 | 22:00 | 227 | 12:00 | Rajshahi | 232 | 06:00 | 218 | 11:00
| BIPTC | 234 | 04:00 | 221 | 11:00 | Rampal | 233 | 06:00 | 225 | 11:00
| Bogura | 236 | 00:00 | 230 | 18:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 241 | 07:00 | 237 | 01:00 | Rampura | 235 | 05:00 | 225 | 12:00
| BSRM | 236 | 19:30 | 224 | 12:00 | Shikalbaha | 231 | 20:00 | 223 | 15:00
| Cumilla(N) | 234 | 19:30 | 225 | 12:00 | Shyampur | 235 | 06:00 | 225 | 12:00
| Fenchuganj | 239 | 19:00 | 232 | 12:00 | Siddhirganj | 236 | 18:00 | 229 | 12:00
| Ghorashal | 240 | 04:00 | 235 | 00:00 | Sirajgonj | 242 | 06:00 | 237 | 11:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 236 | 06:00 | 229 | 11:00
| GPH | 233 | 19:30 | 222 | 12:00 | Tongi | 234 | 23:00 | 222 | 11:00
| Haripur | 235 | 22:00 | 227 | 12:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 138 | 06:00 | 128 | 12:00 | Lalbag | 134 | 06:00 | 127 | 12:00
| Agargaon | 135 | 06:00 | 127 | 12:00 | Lalmonirhat | 132 | 06:00 | 127 | 00:00
| Agrabad | 132 | 03:00 | 127 | 12:00 | Madanganj | 137 | 21:00 | 129 | 10:00
| AKS | 132 | 06:00 | 126 | 12:00 | Madaripur | 131 | 14:00 | 129 | 11:00
| Aminbazar | 140 | 04:00 | 132 | 13:00 | Madartek | 137 | 06:00 | 129 | 12:00
| Amnura | 134 | 00:00 | 129 | 11:00 | Madunaghat | 134 | 07:00 | 129 | 12:00
| Ashuganj | 141 | 07:00 | 138 | 10:00 | Magura | 138 | 05:00 | 117 | 13:00
| Bagerhat | 136 | 15:00 | 126 | 10:00 | Mahasthangarh | 136 | 06:00 | 130 | 18:30
| Bakulia | 133 | 05:00 | 127 | 12:00 | Manikganj | 132 | 18:30 | 121 | 12:00
| Banani | 138 | 06:00 | 126 | 12:00 | Maniknagar | 136 | 06:00 | 128 | 12:00
| Bangabhaban | 134 | 00:00 | 127 | 12:00 | Matarbari | 126 | 09:00 | 113 | 21:00
| Barapukuria | 139 | 17:00 | 134 | 14:00 | Matuail | 135.4 | 22:00 | 129 | 10:00
| Barguna | 137 | 08:00 | 132 | 18:30 | Millgate | 137 | 06:00 | 126 | 12:00
| Barishal | 136 | 17:00 | 130 | 18:30 | Mirpur | 140 | 06:00 | 130 | 13:00
| Barishal-230 | 136 | 08:00 | 133 | 00:00 | Mithapukur | 134 | 06:00 | 129 | 01:00
| Baroaulia | 133 | 06:00 | 128 | 12:00 | MI_Cement | 137 | 20:00 | 129 | 10:00
| Baroirhat | 133 | 18:00 | 122 | 12:00 | Modern | 133 | 06:00 | 127 | 12:00
| Bashundhara | 138 | 06:00 | 127 | 12:00 | Mogbazar | 138 | 07:00 | 130 | 12:00
| BashundharaCement | 137 | 21:00 | 129 | 10:00 | Mongla | 136 | 16:00 | 125 | 12:00
| Beanibazar | 129 | 06:00 | 125 | 14:00 | Motijheel | 135 | 02:00 | 127 | 12:00
| Benapole | 138 | 05:00 | 126 | 12:00 | Munshiganj | 137 | 22:00 | 129 | 10:00
| Bhaluka | 128 | 07:00 | 122 | 11:00 | Mymensingh | 134 | 04:00 | 119 | 12:00
| Bhandaria | 134 | 08:00 | 125 | 18:00 | Naogaon | 135 | 09:00 | 124 | 18:00
| Bhangura | 140 | 00:00 | 133 | 11:00 | Narail | 138 | 06:00 | 117 | 13:00
| Bheramara | 135 | 06:00 | 126 | 13:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara(GK) | 135 | 04:00 | 126 | 13:00 | Narshingdi | 137 | 19:00 | 120 | 10:00
| Bhulta | 127 | 18:00 | 118 | 10:00 | Natore | 135 | 17:00 | 125 | 11:00
| Bog-Sherpur | 137 | 01:00 | 131 | 18:30 | Nawabganj | 134 | 06:00 | 128 | 10:00
| Bogura | 138 | 06:00 | 117 | 11:00 | Netrakona | 134 | 22:00 | 125 | 18:00
| Bogura-230 | 138 | 00:00 | 133 | 18:00 | New | 138 | 06:00 | 128 | 11:00
| Brahmanbaria | 130 | 06:00 | 124 | 18:30 | Niamatpur | 134 | 06:00 | 122 | 18:00
| Cantonment | 135 | 06:00 | 127 | 12:00 | Noapara | 137 | 06:00 | 129 | 11:00
| Chandpur | 135 | 18:00 | 119 | 12:00 | Pabna | 137 | 21:00 | 127 | 13:00
| Chandraghona | 136 | 07:00 | 131 | 12:00 | Palashbari | 133 | 06:00 | 126 | 18:00
| Chapai | 135 | 00:00 | 131 | 10:00 | Panchagarh | 136 | 19:30 | 119 | 14:00
| Charsaidpur | 137 | 18:00 | 130 | 10:00 | Patuakhali | 138 | 17:00 | 133 | 00:00
| Chauddagram | 134 | 18:00 | 122 | 12:00 | Payra | 139 | 04:00 | 135 | 14:00
| Chhatak | 130 | 06:00 | 125 | 18:00 | PHP | 131 | 18:00 | 121 | 12:00
| Chowmuhani | 130 | 18:00 | 117 | 12:00 | Postogola | 137 | 17:00 | 130 | 10:00
| Chuadanga | 136 | 06:00 | 123 | 12:00 | Purbachal | 139 | 22:00 | 126 | 12:00
| Coxsbazar | 125 | 08:00 | 111 | 16:00 | Purbasadipur | 132 | 17:00 | 123 | 00:00
| Cumilla(N) | 136 | 18:00 | 128 | 12:00 | Rahanpur | 137 | 17:00 | 133 | 00:00
| Cumilla(S) | 136 | 18:30 | 126 | 14:00 | Rahim | 134 | 00:00 | 127 | 14:00
| Daudkandi | 132 | 18:00 | 122 | 10:00 | Rajbari | 131 | 06:00 | 124 | 13:00
| Dhaka | 137 | 03:00 | 129 | 13:00 | Rajendrapur | 134 | 20:00 | 120 | 12:00
| Dhamrai | 134 | 07:00 | 124 | 12:00 | Rajshahi | 134 | 17:00 | 126 | 11:00
| Dhanmondi | 135.5 | 22:00 | 128 | 10:00 | Rajshahi-230 | 134 | 06:00 | 127 | 11:00
| Dohazari | 129 | 06:00 | 123 | 14:00 | Ramganj | 134 | 18:00 | 117 | 01:00
| Faridpur | 131 | 06:00 | 126 | 11:00 | Rampur | 133 | 07:00 | 123 | 01:00
| Fatullah | 138 | 21:00 | 131 | 12:00 | Rampura | 137 | 04:00 | 129 | 12:00
| Fenchuganj | 136 | 09:00 | 132 | 12:00 | Rangamati | 134 | 06:00 | 130 | 12:00
| Feni | 130 | 18:00 | 122 | 12:00 | Rangpur | 132 | 06:00 | 127 | 00:00
| Ghorashal | 140 | 00:00 | 135 | 11:00 | Ruppur | 137 | 06:00 | 130 | 12:00
| Goalpara | 138 | 15:00 | 130 | 12:00 | Saidpur | 133 | 17:00 | 126 | 00:00
| Gollamari | 137 | 17:00 | 130 | 12:00 | Satkhira | 134 | 06:00 | 125 | 18:30
| Gopalganj | 133 | 14:00 | 127 | 11:00 | Satmasjid | 135 | 06:00 | 127 | 12:00
| Gopalganj-400 | 131 | 06:00 | 126 | 12:00 | Savar | 138 | 04:00 | 129 | 12:00
| Gulshan | 137 | 06:00 | 129 | 12:00 | SevenRings | 141 | 23:00 | 135 | 10:00
| Halishahar | 132 | 05:00 | 127 | 12:00 | ShahCement | 137 | 18:00 | 130 | 10:00
| Haripur | 136 | 18:00 | 130 | 10:00 | Shahjadpur | 144 | 02:00 | 136 | 11:00
| HaripurSBU | 134 | 00:00 | 127 | 14:00 | Shahjibazar | 133 | 07:00 | 127 | 18:30
| Hasnabad | 137 | 22:00 | 130 | 10:00 | Shahmirpur | 132 | 03:00 | 127 | 12:00
| Hathazari | 136 | 09:00 | 131 | 02:00 | Shariatpur | 131 | 07:00 | 126 | 18:30
| Ishurdi | 138 | 17:00 | 130 | 11:00 | Sherpur | 132 | 22:00 | 120 | 15:00
| Jaldhaka | 133 | 05:00 | 124 | 13:00 | Shikalbaha | 122 | 07:00 | 116 | 12:00
| Jamalpur | 136 | 22:00 | 122 | 18:00 | Shikalbaha-230 | 135 | 18:00 | 125 | 18:00
| Jashore | 137 | 17:00 | 127 | 11:00 | Shitalakhya | 137 | 20:00 | 129 | 10:00
| Jhenaidah | 139 | 06:00 | 118 | 13:00 | Sholosohor | 133 | 06:00 | 127 | 12:00
| Jhenaidah-230 | 140 | 06:00 | 129 | 11:00 | Shyampur | 138 | 21:00 | 132 | 12:00
| Joydebpur | 138 | 20:00 | 130 | 12:00 | Shyampur-230 | 137 | 06:00 | 131 | 12:00
| Joypurhat | 134 | 06:00 | 124 | 18:00 | Siddhirganj | 136 | 17:00 | 130 | 10:00
| Juldah | 132 | 04:00 | 128 | 09:00 | Sirajganj | 138 | 06:00 | 128 | 00:00
| Kabirpur | 135 | 04:00 | 122 | 12:00 | Sonargaon | 136 | 17:00 | 127 | 09:00
| Kachua | 135 | 18:00 | 121 | 12:00 | Sreemongol | 133 | 09:00 | 128 | 00:00
| Kaliakoir | 136 | 17:00 | 128 | 11:00 | Sreepur | 130 | 06:00 | 125 | 11:00
| Kallyanpur | 139 | 01:00 | 131 | 12:00 | Srinagar | 134 | 06:00 | 128 | 11:00
| Kalurghat | 133 | 18:00 | 128 | 12:00 | SSM | 138 | 19:00 | 131 | 10:00
| Kamrangirchar | 138 | 01:00 | 130 | 17:00 | Sunamganj | 128 | 06:00 | 122 | 18:30
| Kaptai | N/A | N/A | N/A | N/A | Sylhet | 131 | 09:00 | 128 | 12:00
| Kazla | 135 | 00:00 | 128 | 13:00 | Sylhet-132 | 131 | 06:00 | 128 | 18:30
| Keranigonj | 135 | 06:00 | 128 | 12:00 | Tangail | 133 | 17:00 | 125 | 12:00
| Khagrachori | 133 | 05:00 | 113 | 17:00 | Thakurgaon | 134 | 19:30 | 121 | 13:00
| Khulna | 137 | 15:00 | 129 | 12:00 | TK | 134 | 07:00 | 128 | 12:00
| Khulna(S) | 137 | 06:00 | 130 | 11:00 | Tongi | 140 | 23:00 | 130 | 11:00
| Khulshi | 131 | 06:00 | 125 | 12:00 | Ullon | 136 | 22:00 | 129 | 12:00
| Kishoreganj | 135 | 06:00 | 121 | 12:00 | Uttara | 137 | 00:00 | 126 | 12:00
| Kodda | 137 | 18:00 | 119 | 12:00 | UttaraNew | 139 | 04:00 | 129 | 14:00
| KSRM | 135 | 19:30 | 128 | 12:00 | Zigatola | 134 | 05:00 | 128 | 13:00
| Kulaura | 133 | 05:00 | 130 | 14:00
| Kurigram | 130 | 05:00 | 124 | 13:00
| Kushtia | 135 | 04:00 | 121 | 13:00

## L-Curve
Date | 2023-10-17
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 606 | 7441 | 4932 | 12373 |  |  |  | QF-LDC-11
0:30 | 595 | 7233.5 | 4896.5 | 12130 | Date: | 2023-10-17
1:00 | 584 | 7026 | 4861 | 11887
1:30 | 587 | 6995.5 | 4636.5 | 11632
2:00 | 590 | 6965 | 4412 | 11377
2:30 | 605 | 6865.5 | 4399.5 | 11265 | [5 empty] | Gen. at Eve. Peak | 13832 | 13832 MW (19:30 )
3:00 | 620 | 6766 | 4387 | 11153 | [6 empty] | 19:30
3:30 | 683 | 6665 | 4274.5 | 10939.5 | [5 empty] | Gen. at Day Peak | 11754 | 11754 MW (12:00 )
4:00 | 746 | 6564 | 4162 | 10726 | [6 empty] | 12:00
4:30 | 747 | 6472.5 | 4123.5 | 10596 | [5 empty] | Highest Generation | 13832
5:00 | 748 | 6381 | 4085 | 10466 | [6 empty] | 19:30
5:30 | 728 | 6269.5 | 4039 | 10308.5
6:00 | 708 | 6158 | 3993 | 10151
6:30 | 664 | 6188.5 | 3968.5 | 10157
7:00 | 620 | 6219 | 3944 | 10163
7:30 | 660 | 6218.5 | 3985.5 | 10204
8:00 | 700 | 6218 | 4027 | 10245
8:30 | 845 | 6259 | 4122 | 10381
9:00 | 990 | 6300 | 4217 | 10517
9:30 | 1013 | 6388 | 4247.5 | 10635.5
10:00 | 1036 | 6476 | 4278 | 10754
10:30 | 1105 | 6697 | 4383.5 | 11080.5
11:00 | 1174 | 6918 | 4489 | 11407
11:30 | 1182 | 6966 | 4614.5 | 11580.5
12:00 | 1190 | 7014 | 4740 | 11754
12:30 | 1172 | 6977 | 4840 | 11817
13:00 | 1154 | 6940 | 4940 | 11880
13:30 | 1150 | 6915 | 5003 | 11918
14:00 | 1146 | 6890 | 5066 | 11956
14:30 | 1171 | 6633 | 5022.5 | 11655.5
15:00 | 1196 | 6376 | 4979 | 11355
15:30 | 1216 | 6565 | 4757 | 11322
16:00 | 1236 | 6754 | 4535 | 11289
16:30 | 1186 | 6773.5 | 4499.5 | 11273
17:00 | 1136 | 6793 | 4464 | 11257
17:30 | 906 | 7225.5 | 4708 | 11933.5
18:00 | 676 | 7658 | 4952 | 12610
18:30 | 548 | 8000.5 | 5160.5 | 13161
19:00 | 420 | 8343 | 5369 | 13712
19:30 | 286 | 8422 | 5410 | 13832
20:00 | 232 | 8288 | 5297 | 13585 |  |  |  | Executive Engineer
20:30 | 251 | 8248.5 | 5267 | 13515.5 |  |  |  | Network Operation Division
21:00 | 270 | 8209 | 5237 | 13446
21:30 | 270 | 8172 | 5200.5 | 13372.5
22:00 | 270 | 8135 | 5164 | 13299 |  |  |  |  | Page 6 of 7
22:30 | 390 | 7966.5 | 5075.5 | 13042
23:00 | 510 | 7798 | 4987 | 12785
23:30 | 558 | 7619.5 | 4959.5 | 12579
24:00 | 606 | 7441 | 4932 | 12373
13832 MW (19:30 )
11754 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-10-17 |  | Energy |  | 284276553
[15 empty] | 43754 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3610 | 766 | 2374 | 0 | 1481 | 3331 | 187 | 0 | 490 | 134 | 0 | 0 | 226.335
0:30 | 3697 | 833 | 2413.5 | 0 | 1313.5 | 3251 | 170.5 | 0 | 314.5 | 137 | 0 | 0 | 250.6875 |  |  | Date: | 43754
1:00 | 3784 | 900 | 2453 | 0 | 1146 | 3171 | 154 | 0 | 139 | 140 | 0 | 0 | 275.04
1:30 | 3788 | 900 | 2419.5 | 0 | 1010 | 3104 | 153.5 | 0 | 119 | 138 | 0 | 0 | 244.0025 | [9 empty] | Total Energy | 284.2766 | 284.2766 | Total Energy Gen 284.277 MKWHr Energy Not Served 3.775 MKWHr Energy Requirement 288.052 MKWHr
2:00 | 3792 | 900 | 2386 | 0 | 874 | 3037 | 153 | 0 | 99 | 136 | 0 | 0 | 212.965 | [9 empty] | Energy not Served | 3.7754 | 3.7754
2:30 | 3775 | 900 | 2391.5 | 0 | 778.5 | 3041.5 | 152.5 | 0 | 99 | 127 | 0 | 0 | 200.55 | [9 empty] | Energy Requirement | 288.052 | 288.052
3:00 | 3758 | 900 | 2397 | 0 | 683 | 3046 | 152 | 0 | 99 | 118 | 0 | 0 | 188.135
3:30 | 3764.5 | 900 | 2341.5 | 0 | 613.5 | 2948 | 151.5 | 0 | 98.5 | 122 | 0 | 0 | 129.4025 | [8 empty] | Shortage
4:00 | 3771 | 900 | 2286 | 0 | 544 | 2850 | 151 | 0 | 98 | 126 | 0 | 0 | 70.67
4:30 | 3743.5 | 900.5 | 2258.5 | 0 | 492 | 2826.5 | 151 | 0 | 98 | 126 | 0 | 0 | 65.895
5:00 | 3716 | 901 | 2231 | 0 | 440 | 2803 | 151 | 0 | 98 | 126 | 0 | 0 | 61.12
5:30 | 3634 | 900.5 | 2165.5 | 0 | 440 | 2805 | 151 | 0 | 98 | 114 | 0.5 | 0 | 53.9575
6:00 | 3552 | 900 | 2100 | 0 | 440 | 2807 | 151 | 0 | 98 | 102 | 1 | 0 | 46.795
6:30 | 3533 | 900.5 | 2112.5 | 0 | 457 | 2805 | 133.5 | 0 | 98 | 90 | 27.5 | 0 | 33.9025 | [7 empty] | Coal
7:00 | 3514 | 901 | 2125 | 0 | 474 | 2803 | 116 | 0 | 98 | 78 | 54 | 0 | 21.01
7:30 | 3481 | 901 | 2125.5 | 0 | 495 | 2800.5 | 116 | 0 | 98 | 80 | 107 | 0 | 22.4425 | [6 empty] | Oil
8:00 | 3448 | 901 | 2126 | 0 | 516 | 2798 | 116 | 0 | 98 | 82 | 160 | 0 | 23.875
8:30 | 3498.5 | 900.5 | 2144 | 0 | 532.5 | 2798.5 | 116 | 0 | 98 | 82 | 211 | 0 | 22.92
9:00 | 3549 | 900 | 2162 | 0 | 549 | 2799 | 116 | 0 | 98 | 82 | 262 | 0 | 21.965
9:30 | 3563 | 898.5 | 2188.5 | 0 | 591.5 | 2806.5 | 116 | 0 | 94 | 83 | 294.5 | 0 | 10.9825
10:00 | 3577 | 897 | 2215 | 0 | 634 | 2814 | 116 | 0 | 90 | 84 | 327 | 0 | 0
10:30 | 3654 | 895.5 | 2321.5 | 0 | 713.5 | 2836.5 | 133.5 | 0 | 96 | 88 | 342 | 0 | 0
11:00 | 3731 | 894 | 2428 | 0 | 793 | 2859 | 151 | 0 | 102 | 92 | 357 | 0 | 0
11:30 | 3738.5 | 894.5 | 2431.5 | 0 | 922 | 2860.5 | 151 | 0 | 131.5 | 94 | 357 | 0 | 21.965
12:00 | 3746 | 895 | 2435 | 0 | 1051 | 2862 | 151 | 0 | 161 | 96 | 357 | 0 | 43.93
12:30 | 3714 | 894.5 | 2438 | 0 | 1153 | 2849.5 | 152 | 0 | 161 | 98 | 357 | 0 | 100.275
13:00 | 3682 | 894 | 2441 | 0 | 1255 | 2837 | 153 | 0 | 161 | 100 | 357 | 0 | 156.62
13:30 | 3682 | 894 | 2441 | 0 | 1255 | 2837 | 153 | 0 | 161 | 100 | 357 | 0 | 156.62
14:00 | 3682 | 894 | 2441 | 0 | 1255 | 2837 | 153 | 0 | 161 | 100 | 357 | 0 | 156.62
14:30 | 3487.5 | 894 | 2391.5 | 0 | 1305 | 2837 | 152.5 | 0 | 158.5 | 105 | 286.5 | 0 | 324.2225
15:00 | 3293 | 894 | 2342 | 0 | 1355 | 2837 | 152 | 0 | 156 | 110 | 216 | 0 | 491.825
15:30 | 3462 | 894.5 | 2318 | 0 | 1315.5 | 2749.5 | 152 | 0 | 156 | 112 | 162.5 | 0 | 513.79
16:00 | 3631 | 895 | 2294 | 0 | 1276 | 2662 | 152 | 0 | 156 | 114 | 109 | 0 | 535.755
16:30 | 3602.5 | 894.5 | 2289 | 0 | 1353 | 2633.5 | 152 | 0 | 169.5 | 114 | 64.5 | 0.5 | 527.16
17:00 | 3574 | 894 | 2284 | 0 | 1430 | 2605 | 152 | 0 | 183 | 114 | 20 | 1 | 518.565
17:30 | 3568 | 894 | 2355 | 0 | 1803.5 | 2745.5 | 152 | 8 | 271.5 | 125 | 10 | 1 | 540.7825
18:00 | 3562 | 894 | 2426 | 0 | 2177 | 2886 | 152 | 16 | 360 | 136 | 0 | 1 | 563
18:30 | 3646.5 | 825.5 | 2409.5 | 0 | 2448.5 | 3104.5 | 152.5 | 16 | 426.5 | 131 | 0 | 0.5 | 281.5
19:00 | 3731 | 757 | 2393 | 0 | 2720 | 3323 | 153 | 16 | 493 | 126 | 0 | 0 | 0
19:30 | 3729 | 757 | 2290 | 0 | 2803 | 3430 | 153 | 16 | 514 | 140 | 0 | 0 | 0
20:00 | 3607 | 757 | 2324 | 0 | 2669 | 3429 | 153 | 16 | 492 | 138 | 0 | 0 | 0
20:30 | 3616.5 | 754.5 | 2339 | 0 | 2600 | 3428.5 | 153 | 8 | 479 | 137 | 0 | 0 | 0
21:00 | 3626 | 752 | 2354 | 0 | 2531 | 3428 | 153 | 0 | 466 | 136 | 0 | 0 | 0
21:30 | 3627 | 752 | 2350 | 0 | 2450 | 3396 | 176 | 0 | 485.5 | 136 | 0 | 0 | 0
22:00 | 3628 | 752 | 2346 | 0 | 2369 | 3364 | 199 | 0 | 505 | 136 | 0 | 0 | 0
22:30 | 3576.5 | 759 | 2348.5 | 0 | 2188 | 3326 | 192.5 | 0 | 517.5 | 134 | 0 | 0 | 102.6625
23:00 | 3525 | 766 | 2351 | 0 | 2007 | 3288 | 186 | 0 | 530 | 132 | 0 | 0 | 205.325
23:30 | 3567.5 | 766 | 2362.5 | 0 | 1744 | 3309.5 | 186.5 | 0 | 510 | 133 | 0 | 0 | 215.83 |  |  | Max Temp. in Dhaka |  | 33.5°C
24:00 | 3610 | 766 | 2374 | 0 | 1481 | 3331 | 187 | 0 | 490 | 134 | 0 | 0 | 226.335
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 284.277 MKWHr Energy Not Served 3.775 MKWHr Energy Requirement 288.052 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-10-17
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 79 | 78 | 77 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 78 | 78 | 77 | 77 | 77 | 77 |  | 78 | 78 | 78 | 78 | 124 | 111 | 112 | 1956627
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 40 | 40 | 40 | 40 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1660000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 |  | 17 | 17 | 8 | 8 | 8 | 8 | 8 | 226902
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 4 | 11 | 15 | 18 | 19 | 20 | 19 | 16 | 12 | 6 | 1 | [9 empty] | 134730
6 | Sikalbaha 225MW CCPP (Gas) | 227 | 226 | 226 | 226 | 224 | 225 | 222 | 223 | 227 | 218 | 218 | 215 | 218 | 217 | 219 | 219 | 221 | 221 |  | 224 | 223 | 222 | 224 | 225 | 222 | 224 | 5184298
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [24 empty] | 0 | 0 | 0
12 | Hathazari 100 MW peaking PP | 66 | 66 | 66 | 65 | 65 | 65 | 65 | 65 | 65 | 57 | 48 | 24 | 24 | 16 | 20 | 24 | 24 | 57 |  | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 1265376
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 423199
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 336 | 336 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 280 | 330 | 330 | 330 | 325 | 325 | 330 | 332 | 325 |  | 333 | 330 | 290 | 290 | 272 | 260 | 260 | 7457858
18 | Kodda 300 MW PP Unit-2 (Summit) | 47 | 47 | 0 |  |  |  | 5 | 15 | 20 | 75 | 82 | 80 | 80 | 50 | 47 | 47 | 50 | 100 |  | 130 | 130 | 130 | 130 | 130 | 130 | 72 | 1528036
19 | Ashuganj 195 MW PP (APSCL-United) | [25 empty] | 0 | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 140 | 140 | 141 | 141 | 140 | 140 | 140 | 140 | 137 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3360750
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 623 | 620 | 621 | 533 | 500 | 450 | 450 | 450 | 540 |  | 621 | 621 | 620 | 620 | 621 | 612 | 620 | 14121817
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 50 | 50 | 50 | 50 | 50 | 25 | 10 | 10 | 10 |  | 30 | 50 | 50 | 51 | 51 | 51 | 51 | 1057752
33 | Ashuganj 225 MW CCPP | 192 | 196 | 196 | 208 | 205 | 210 | 208 | 207 | 209 | 202 | 201 | 200 | 188 | 168 | 174 | 202 | 206 | 203 |  | 176 | 176 | 176 | 176 | 176 | 177 | 205 | 4719000
34 | Ashuganj 450 MW CCPP(South) | 270 | 270 | 270 | 270 | 270 | 270 | 320 | 275 | 270 | 300 | 325 | 325 | 285 | 305 | 295 | 280 | 280 | 290 |  | 305 | 300 | 280 | 280 | 275 | 270 | 270 | 6969000
| Ashuganj 450 MW CCPP(North) | 300 | 300 | 300 | 300 | 300 | 280 | 280 | 280 | 280 | 310 | 330 | 340 | 291 | 305 | 300 | 280 | 280 | 285 |  | 305 | 280 | 280 | 280 | 280 | 280 | 275 | 7524700
| Ashuganj 420 MW CCPP(East) | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 280 | 280 | 280 | 315 | 320 | 320 | 360 | 350 | 345 |  | 375 | 375 | 375 | 375 | 375 | 320 | 320 | 7916900
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 419 | 420 | 420 | 421 | 410 | 351 | 351 | 352 | 379 | 403 | 409 | 411 | 408 | 409 | 408 | 412 | 410 | 381 |  | 410 | 409 | 409 | 410 | 410 | 369 | 373 | 9703420
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 380 | 380 | 340 | 340 | 340 | 340 | 300 | 420 | 450 | 450 | 450 | 450 | 450 | 450 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 9522000
41 | Haripur 360 MW CCPP(HPL) | 326 | 334 | 336 | 336 | 319 | 316 | 316 | 316 | 316 | 327 | 332 | 323 | 321 | 311 | 291 | 292 | 291 | 292 |  | 292 | 292 | 298 | 312 | 322 | 327 | 327 | 7608000
42 | RPCL 210MW CCPP | 72 | 72 | 72 | 72 | 72 | 33 | 33 | 27 | 27 | 27 | 27 | 26 | 25 | 23 | 23 | 27 | 30 | 30 |  | 33 | 34 | 34 | 35 | 54 | 74 | 72 | 973440
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 6 | 16 | 36 | 44 | 49 | 51 | 48 | 39 | 25 | 12 | 2 | [9 empty] | 328560
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 41 | 41 | 41 | 42 | 42 | 42 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1008000
45 | Fenchugonj CCPP Phase-2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 27 | 27 | 25 | 0 | [8 empty] | 20 | 20 | 20 | 20 | 22 | 22 | 442920
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 59 | 59 | 60 | 60 | 60 | 61 | 61 | 61 | 61 | 60 | 59 | 59 | 59 | 60 | 60 | 60 | 61 | 60 |  | 61 | 61 | 61 | 61 | 62 | 61 | 61 | 1452192
48 | Shahjibazar 86 MW PP (Shahjibazar) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 84 | 84 | 84 | 84 | 83 | 83 | 83 | 84 | 84 |  | 84 | 85 | 85 | 85 | 85 | 85 | 85 | 2021760
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 159 | 160 | 160 | 158 | 158 | 158 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 158 | 158 | 157 | 157 |  | 157 | 157 | 157 | 157 | 158 | 158 | 158 | 3272670
51 | Sylhet 20 MW GTPP | [24 empty] | 17 | 17 | 39000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 9 | 10 | 10 | 10 | 10 | 254340
54 | Hobiganj 11 MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  | 3 | 3 |  | 3 | 3 | 3 | 3 | 5 | 5 | 5 | 148464
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 22 | 22 | 22 | 22 | 42 | 42 | 42 | 42 | 42 | 47 | 47 | 47 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1042800
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 388416
57 | Bibiana-II 341 MW CCPP (Summit) | 295 | 280 | 290 | 280 | 290 | 290 | 285 | 300 | 295 | 295 | 315 | 305 | 310 | 300 | 300 | 290 | 300 | 305 |  | 290 | 265 | 270 | 285 | 280 | 270 | 295 | 7177000
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 0 | [11 empty] | 17 | 17 | 17 | 17 | 17 | 55 |  | 55 | 55 | 55 | 55 | 55 | 35 | 17 | 406143
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 15 | 18 | 330000
60 | Barabkunda 22 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 289584
61 | Narshingdi 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 17 | 17 |  | 17 | 17 | 17 | 18 | 18 | 18 | 18 | 359892
62 | Tangail 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 362124
63 | Impoprt (Tripura) | 140 | 136 | 118 | 126 | 126 | 102 | 78 | 82 | 82 | 84 | 92 | 96 | 100 | 102 | 110 | 114 | 114 | 136 |  | 126 | 140 | 138 | 136 | 136 | 132 | 134 | 2781120
64 | Malancha, Ctg. EPZ (United) | 36 | 36 | 37 | 38 | 32 | 38 | 29 | 5 | 2 | 2 | 2 | 2 | 2 | 4 | 2 | 2 | 4 | 4 |  | 13 | 18 | 20 | 26 | 23 | 26 | 23 | 411360
65 | Feni 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 18 | 18 | 18 | 18 | 18 |  | 12 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 395388
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 237960
67 | Jangalia 33 MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 637400
68 | Cumilla 25 MW PP (Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 295500
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456000
70 | Summit Madhabdi | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 0 | 11 | 10 | 10 | 10 | 257040
71 | Maona 33 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 777100
72 | Rupganj 33 MW PP(Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 8 | 8 | 21 | 14 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 474800
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 52 | 52 | 52 | 52 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 |  | 106 | 102 | 52 | 52 | 52 | 88 | 70 | 890340
| Chowmuhani 113 MW | 42 | 38 | 38 | 26 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 28 | 28 | 77 |  | 78 | 78 | 78 | 79 | 78 | 79 | 35 | 801360
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 0 | [7 empty] | 8 | 17 | 17 | 17 | 17 | 17 | 17 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 646560
77 | Siddhirganj 100 PP(Dutch Bangla) | 34 | 24 | 0 |  |  |  | 5 | 8 | 8 | 8 | 18 | 55 | 57 | 57 | 57 | 66 | 66 | 66 |  | 66 | 66 | 66 | 66 | 66 | 54 | 49 | 888000
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 14 |  | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 296160
79 | Kodda 150 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 98 |  | 149 | 149 | 115 | 82 | 82 | 82 | 82 | 924480
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 43 |  | 53 | 52 | 52 | 52 | 52 | 51 | 51 | 481397
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 105 |  | 105 | 105 | 105 | 105 | 70 | 70 | 17 | 997440
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 2 | 3 | 4 | 4 | 4 | 4 | 4 | 2 | 1 | [10 empty] | 29398
| Jodiac Power | 0 | [6 empty] | 10 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 318512
| Karnaphuli Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 425710
82 | Madanganj 102 PP(Summit) | 96 | 96 | 86 | 15 | 0 |  | 9 | 17 | 17 | 17 | 26 | 48 | 63 | 95 | 86 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 1449835
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 35 | 0 | [8 empty] | 13 | 24 | 25 | 24 | 23 | 24 | 24 | 24 |  | 25 | 25 | 24 | 25 | 24 | 25 | 23 | 363548
86 | Meghnaghat CCPP ( Summit) | 278 | 286 | 282 | 281 | 309 | 260 | 299 | 313 | 255 | 307 | 310 | 307 | 311 | 312 | 288 | 280 | 253 | 310 |  | 282 | 250 | 275 | 265 | 257 | 302 | 296 | 7022109
87 | Meghnaghat 100 MW(IEL) | 41 | 52 | 21 | 0 | [6 empty] | 9 | 42 | 57 | 58 | 62 | 67 | 67 | 66 |  | 67 | 75 | 74 | 74 | 73 | 74 | 67 | 963840
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 16 | 16 | 16 | 17 | 16 | 16 | 17 | 23 | 35 | 50 | 53 | 53 | 53 | 53 | 54 |  | 71 | 72 | 71 | 71 | 54 | 54 | 17 | 897600
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 263160
92 | Fenchuganj 44 MW (Energyprima) | 48 | 45 | 48 | 48 | 48 | 45 | 48 | 45 | 48 | 46 | 46 | 44 | 43 | 39 | 39 | 46 | 46 | 46 |  | 47 | 47 | 47 | 47 | 47 | 40 | 47 | 1099008
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 10 | 10 | 10 | 10 | 30 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1027572
94 | Gagnagar 102 MW PP (Digital Power) | 24 | 24 | 0 |  |  |  | 8 | 8 | 8 | 8 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 58 |  | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 636480
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 14 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 6 | 233280
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | 15 | 0 |  |  | 5 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 331670
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 17 | 35 |  | 35 | 35 | 35 | 35 |  |  | 0 | 136254
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3912300
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 1 | 2 | 2 | 1 | 1 | [10 empty] | 12600
103 | Kamalaghat 54 MW PP(Banco Energy) | 0 | [15 empty] | 17 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 233640
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 28 | 28 | 28 | 28 | 28 | 18 | 18 | 18 |  | 94 | 102 | 103 | 103 | 103 | 18 | 18 | 799200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 26 | 107 |  | 111 | 118 | 115 | 109 | 109 | 61 | 28 | 960336
115 | Juldah 100 MW PP Unit-3 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 296640
116 | Chandpur 200 MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 34 |  | 34 | 34 | 34 | 34 | 17 | 17 | 17 | 507360
117 | Ashuganj 150 MW PP (Midland) | 11 | 13 | 10 | 0 |  |  | 1 | 5 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 7 | 5 | 16 |  | 63 | 118 | 110 | 135 | 142 | 100 | 5 | 664072
118 | Bibiyana-III 400 MW CCPP | 401 | 403 | 403 | 403 | 365 | 366 | 365 | 366 | 403 | 404 | 405 | 405 | 405 | 405 | 40 | 404 | 362 | 350 |  | 370 | 368 | 368 | 368 | 368 | 368 | 403 | 9279000
| Jamalpur 115 MW PP (United) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 59 | 60 | 60 | 78 | 79 | 79 | 79 | 79 | 60 | 60 | 60 |  | 99 | 99 | 99 | 99 | 100 | 60 | 60 | 1689600
| Anwara 300 MW PP (United) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 103 | 203 |  | 203 | 214 | 214 | 106 | 106 | 70 | 70 | 2150291
| Juldah unit-2 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 303360
| Anlima Energy Ltd. | 46 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 35 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 802909
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 47 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 43 | 35 | 1012680
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 4
| Chandpur 115(Doreen) | 32 | 36 | 36 | 27 | 18 | 18 | 18 | 17 | 18 | 20 | 36 | 36 | 36 | 35 | 36 | 36 | 43 | 69 |  | 95 | 95 | 95 | 95 | 73 | 41 | 18 | 992640
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 32 | 22 | 35 | 35 | 35 | 35 | 35 | 38 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 824400
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 |  | 89 | 114 | 124 | 124 | 124 | 143 | 143 | 1098982
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480
| Matarbari 2*600 MW (CPGCL) | 144 | 144 | 142 | 142 | 144 | 144 | 143 | 144 | 140 | 144 | 142 | 138 | 140 | 141 | 140 | 142 | 137 | 141 |  | 142 | 144 | 144 | 144 | 142 | 144 | 145 | 3563636
120 | Eastern Zone Total | 7026 | 6965 | 6766 | 6564 | 6381 | 6158 | 6219 | 6218 | 6300 | 6476 | 6918 | 7014 | 6940 | 6890 | 6376 | 6754 | 6793 | 7658 |  | 8343 | 8422 | 8288 | 8209 | 8135 | 7798 | 7441 | 169589177
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 0 | [8 empty] | 6 | 16 | 36 | 37 | 58 | 30 | 30 | 40 |  | 75 | 81 | 80 | 80 | 80 | 81 | 81 | 745920
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 7 | 0 | [14 empty] | 25 | 32 |  | 32 | 26 | 29 | 33 | 27 | 27 | 5 | 216000
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 54 | 0 | [10 empty] | 9 | 37 | 51 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 54 | 54 | 54 | 653760
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 1 | 11 | 33 | 54 | 72 | 76 | 71 | 78 | 67 | 48 | 26 | 5 | [8 empty] | 0 | 550080
131 | Rampal 1320 MW (BIFPCL) | 450 | 395 | 404 | 401 | 401 | 401 | 401 | 395 | 402 | 401 | 399 | 401 | 403 | 402 | 401 | 374 | 373 | 501 |  | 570 | 571 | 571 | 570 | 570 | 570 | 571 | 10676360
132 | United Payra Power Ltd. | 17 | 0 | [9 empty] | 12 | 17 | 17 | 17 | 17 | 17 | 17 |  | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 367200
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 182 | 182 | 220 |  | 220 | 222 | 220 | 222 | 220 | 190 | 190 | 5123564
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 0 | [9 empty] | 16 | 48 | 80 | 64 | 16 | 16 | 16 |  | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 443232
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3665500
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 130 | 130 | 130 | 132 | 132 | 78 | 80 | 80 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 80 | 76 | 132 |  | 126 | 126 | 130 | 132 | 126 | 100 | 100 | 2808000
140 | Bhola 33 MW PP (Venture) | 27 | 26 | 25 | 24 | 23 | 21 | 18 | 17 | 16 | 18 | 19 | 20 | 20 | 17 | 18 | 18 | 20 | 27 |  | 27 | 27 | 26 | 28 | 28 | 27 | 27 | 537477
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 0 | [8 empty] | 8 | 16 | 16 | 16 | 16 | 8 | 8 | 8 |  | 16 | 16 | 8 | 8 | 8 | 8 | 0 | 164625
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 15 | 0 | [9 empty] | 15 | 50 | 105 | 69 | 15 | 15 | 15 |  | 48 | 50 | 50 | 50 | 15 | 15 | 0 | 518976
146 | Bheramara HVDC | 900 | 900 | 900 | 900 | 901 | 900 | 901 | 901 | 900 | 897 | 894 | 895 | 894 | 895 | 894 | 895 | 894 | 894 |  | 757 | 757 | 757 | 752 | 752 | 766 | 766 | 20610909
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 1120 | 1040 | 1040 | 850 | 800 | 800 | 800 | 800 | 800 | 800 | 840 | 860 | 920 | 980 | 1000 | 850 | 800 | 860 |  | 1140 | 1244 | 1244 | 1244 | 1180 | 1120 | 1150 | 25194100
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4159900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 162962
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 2 | 0 | 4 | 5 | 4 | 5 | 3 | 2 | 1 | 0 | [9 empty] | 28440
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 214 | 214 | 214 | 214 | 214 | 214 | 170 | 170 | 170 | 170 | 193 | 214 | 212 | 212 | 210 | 210 | 205 | 190 |  | 214 | 209 | 180 | 180 | 180 | 180 | 200 | 5055291
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 210 | 211 | 211 | 211 | 211 | 211 | 170 | 170 | 170 | 170 | 189 | 208 | 208 | 207 | 207 | 207 | 207 | 194 |  | 206 | 205 | 180 | 180 | 180 | 180 | 191 | 5023073
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 350 | 350 | 320 | 320 | 320 | 320 | 320 | 340 | 350 | 414 | 414 | 414 | 414 | 380 | 380 | 380 | 414 |  | 414 | 360 | 360 | 360 | 360 | 360 | 360 | 9109672
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [22 empty] | 5 | 15 | 18 |  | 22355
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 243720
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern) | 42 | 0 | [8 empty] | 16 | 34 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 8 | 8 | 8 | 8 | 42 | 415192
167 | Katakhali 50 MW Peaking PP | [10 empty] | 3 | 39 | 39 | 39 | 38 | 38 | 38 | 38 |  | 37 | 39 | 40 | 38 | 38 | 38 | 38 | 443764
168 | Santahar 50 MW Peaking PP | 16 | 0 | [13 empty] | 14 | [7 empty] | 35 | 38 | 38 | 117130
169 | Natore 52 MW PP (Rajlanka) | 8 | 0 | [9 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 120192
170 | Chapainawabganj 100 MW Peaking PP | 17 | 0 | [9 empty] | 47 | 47 | 47 | 47 | 47 | 47 | 92 |  | 94 | 94 | 92 | 92 | 92 | 92 | 92 | 929296
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 0 | [10 empty] | 30 | 35 | 35 | 35 | 35 | 35 |  | 45 | 35 | 35 | 35 | 35 | 35 | 35 | 553248
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 0 | [8 empty] | 35 | 35 | 35 | 35 | 35 | 55 | 55 |  | 35 | 35 | 55 | 55 | 55 | 35 | 35 | 600576
173 | Rangpur 20 MW GTPP | [17 empty] | 16 |  | 16 | 16 | 16 | 0 | 0 | 0 | 0 | 35000
175 | Saidpur 20 MW GTPP | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 10 | 30 | 60 |  | 107 | 107 | 107 | 56 | 49 | 35 | 34 | 676905
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 4 | 5 | 6 | 7 | 7 | 5 | 4 | 2 | 1 | [9 empty] | 40983
178 | Energypac Power Venture Thakurgaon Ltd. | [15 empty] | 25 | 35 | 112 |  | 114 | 114 | 75 | 75 | 75 | 74 | 0 | 629184
| Intraco Solar 30 MW | [5 empty] | 0 | 4 | 14 | 23 | 29 | 34 | 36 | 24 | 23 | 20 | 10 | 2 | [9 empty] | 215965
| Adani Power Jharkhanda Ltd | 525 | 526 | 528 | 525 | 526 | 530 | 527 | 527 | 525 | 526 | 538 | 522 | 521 | 526 | 526 | 526 | 525 | 524 |  | 530 | 530 | 530 | 530 | 531 | 522 | 525 | 12654545
178 | Teesta Solar Limited | [6 empty] | 25 | 80 | 126 | 149 | 162 | 163 | 170 | 130 | 102 | 50 | 9 | [9 empty] | 1174280