## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2019-04-14 | Sunday
|  | Date (day): | 2019-04-14 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13221 | MW |  |  | (b) At Evening Peak Hour : |  | 14200 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-04-13 | 2019-04-14 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 38 | 38 | 38 | 38 |  | 47 | Unit-1 under maint.
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 94 | 43 | 140 | 140 |  |  | On test.
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 99 | 51 | 270 | 270 |  |  | On test.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 120 | 120 | 120 | 120
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 340 | 250 | 360 | 360
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 20 | 0 | 40 | 40
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 52 | 12 | 50 | 50
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 337 | 325 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 0 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 351 | 300 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 370 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 92 | 92 |  | 8 | Engine problem
11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 275 | 260 | 305 | 305
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 19 | 19
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 100 | 100 | 120 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract expired
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 218 | 110 | 0 | 0
0 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
21 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 0 | 102 | 102
22 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 6 | 24 | 48 | 48
23 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 0 | 54 | 54
24 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 16 | 149 | 149
25 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 18 | 18 | 55 | 55
26 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 0 | 55 | 55
27 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 40 | 60 | 60 |  | 48 | Engine problem
28 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 57 | 57 | 57 |  | 23 | Engine problem
29 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
30 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 17 | 33 | 33
31 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 51 | 51 | 50 | 50
32 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 40 | 40 | 40 | 40 | 65 |  | Gas shortage
33 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 200 | 300
34 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
35 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
36 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
37 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 0 | 17 | 149 | 149
| Dhaka area Total |  |  |  |  | 6034 | 5798 | 2659 | 2211 | 4706 | 4906 | 340 | 126
38 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 110 | 110 | 110 |  | 70 | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
39 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 4 | 25 | 25 | 25
40 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 13.98 | 0 | 20 | 0
41 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 40 | 50 | 50
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 82 | 80 | 110 | 110 |  | 120 | Low water lavel
43 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
44 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 203 | 225 | 225 |  |  | FGMO
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 120 | 125 | 150 | 150
46 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 41 | 32 | 41 | 41 |  | 10 | Engine problem
47 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 47 | 50 | 50
48 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 83 | 68 | 83
49 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 10 | 78 | 78 |  | 22 | Engine problem
50 | Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 100 | 100 | 84 | 100 | 100 | 100
51 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 33 | 40 | 40
52 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 7 | 52 | 100 | 100
| Chattogram area Total |  |  |  |  | 1761 | 1681 | 837.98 | 1079 | 1309 | 1304 | 60 | 262
53 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Gas shortage
54 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 219 | 191 | 221 | 221 |  |  | FGMO
55 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 250 | 360 | 360
56 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 200 | 360 | 360
57 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 30 | 40 | 40 | 40
58 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
59 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage
60 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 63 | 53 | 195 | 195
61 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 5 | 5 | 40 | 40 |  | 11 | Engine problem
62 | Midland 150MW |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 150 | 150
63 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
64 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 100 | 100
66 | Chandpur Desh 200MW |  | HFO | IPP | 0 | 200 | 200 | 0 | 34 | 200 | 200
67 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 0 | 22 | 22
68 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 8 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 124 | 82 | 131 | 160
69 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 8 | 33 | 33 | 33
70 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
71 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 17 | 10 | 21 | 21
72 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1135 | 966 | 2046 | 2225 | 362 | 145
73 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 185 | 164 | 202 | 202
74 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 20 | 20
75 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 7 | 30 | 82 | 82 |  | 13 | Enjgine problem
76 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 1.2 | 0 | 2 | 0
77 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 0 | 0 | 200 | 200
78 | United Jamalpur PPL |  | HFO | IPP | 115 MW | 115 | 115 | 110 | 110 | 112 | 112
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 303.2 | 304 | 618 | 616 | 0 | 13
79 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 58 | 58 | 60 | 60
80 | Fenchugonj CCPP-2 |  | Gas | PDB | !F71 | 104 | 90 | 52 | 52 | 60 | 60
81 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 100 | 163 | 163
82 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 274 | 280 | 300 | 320 |  |  | FGMO
83 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 50 | 50 | 50
84 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 5 | 50 | 44 | 44
85 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
86 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 64 | 66 | 66 |  |  | FGMO
87 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 88 | 88 | 86 | 86
88 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 42 | 47 | 46 | 45 |  | 5 | Engine problem
89 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 97 | 91 | 120 | 120
90 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20
91 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 7 | 37 | 46 | 46
92 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 25 | 25 | 25 | 25 |  | 9 | Engine problem
93 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 30 | 341 | 341 |  |  | FGMO
| Bibiyana-3 285 MW |  | Gas | PDB | 285 MW | 0 | 0 | 240 | 0 | 250 | 285 |  |  | On test
94 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1416 | 993 | 1698 | 1752 | 0 | 14
95 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 46
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 840 | 942 | 772 | 852
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
96 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 16 | 115 | 115
97 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 17 | 30 | 36
98 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 |  |  | Reserve
99 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 80
100 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint.
101 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 8 | 40 | 40
0 | Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
102 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
103 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 53 | 105 | 105
| Madhumati Power Plant |  | HFO | IPP | 100 MW | 0 | 0 | 108 | 109 | 100 | 100
| Khulna Area Total |  |  |  |  | 2223 | 2209 | 965 | 1145 | 1162 | 1474 | 0 | 410
104 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 115 | 0 | 110 | 110
105 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 26
106 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 10 | 33 | 33
107 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 100 | 100 | 100 | 100
108 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 0 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 246 | 110 | 338 | 364 | 0 | 0
109 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 60 | 60 | 65 | 65
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Transformer problem
110 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
111 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 54
112 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 12 | 35 | 35 |  | 15 | Engine problem
113 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
114 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 40
115 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 202 | 184 | 200 | 200 |  |  | FGMO
116 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 189 | 186 | 225 | 225 |  |  | FGMO
117 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 118 | 204 | 200 | 200 |  |  | FGMO
118 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282 | 282 | 282 | 0 | 0 | 0 | 0 |  |  | ON test
119 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 36
120 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
121 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 16 | 5 | 17 | 17
122 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 8 | 11 | 11
123 | Rajlanka 52 MW |  | HFO | IPP | 52 | 52 | 52 | 16 | 25 | 52 | 52
124 | Chapainawabganj-100 MW |  | HFO | PDB | 104 | 104 | 104 | 50 | 50 | 100 | 100
125 | Paramount Baghabari |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Reserve
126 | Confidence CPBL-2 |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 17 | 113 | 113 |  |  | On test
| Rajshahi Area Total |  |  |  |  | 1948 | 1938 | 719 | 773 | 1090 | 1270 | 0 | 115
127 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under overhauling
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 67 | 68 | 70 | 70
128 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 184 | 184 | 184 | 184 | 90
129 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
130 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 251 | 252 | 254 | 289 | 90 | 85
| Total |  |  |  |  | 18192 | 17649 | 8532.18 | 7833 | 13221 | 14200 | 852 | 1170
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8065.9764 | 7405 | 12498.5963 | 13424.1032
A. |  | 2019-04-13 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 8875 | MW at | 1:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 7464 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 7833 | MW
3 | Day peak Generation : |  |  | 8532.18 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7405 | MW
4 | Evening peak Generation : |  |  | 7833 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 192.0434 | MKWHr | By Solar | 0.14788 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 137.9766 | MKWHr |  | By Oil: | 24.0783 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 6.0932 | MKWHr |  | By Hydro: | 1.8781 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 852 | MW | Dhaka | 2934 | 2934 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1170 | MW | Chittagong | 1106 | 1106 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2022 | MW | Khulna | 552 | 552 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1145.69 | MMCFD |  |  | Rajshahi | 709 | 709 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 101351439.596 | ii) Oil : | Taka | 174184359.2 | Comilla | 421 | 421 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 27046360.74 | Total | Taka | 302582159.536 | Mymensingh | 626 | 626 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 5.9705 | MKWHr. | Sylhet | 438 | 438 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 320 | MW (E to W) at | 21:00 | hrs | Barisal | 54 | 54 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -860 | MW at | 3:00 | hrs | Rangpur | 565 | 565 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.0° C |  |  | Total | 7405 | 7405 |  | 0
B. |  | 2019-04-14 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 35.8° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14200 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8000 | MW
4 | Reserve(Generation end) |  |  |  | 4500 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 209.8953 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5933 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.1265 | MKWHr. | ii) HVDC Flow at Peak Time |  | 942 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.7427 | MKWHr. | iii) Maximum HVDC Flow : |  | 942 | MW at | 21:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 83.5 |  | (b) Today: | 83.26 |  | (c) Rule Curve: |  | 85.4
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-04-13
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285 MW | United Jamalpur PPL | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | Paramount Baghabari | Confidence CPBL-2 | Madhumati Power Plant | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 38 | 158 | 100 | 120 | 280 | 110 | 40 | 326 | 260 | 0 | 20 | 370 | 240 | 0 | 0 | 0 | 220 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 18 | 17 | 19 | 25 | 31 | 25 | 25 | 0 | 40 | 82 | 0 | 110 | 120 | 8 | 203 | 0 | 130 | 0 | 0 | 41 | 0 | 0 | 10 | 32 | 47 | 19 | 33 | 0 | 0 | 0 | 320 | 290 | 184 | 110 | 50 | 37 | 5 | 5 | 45 | 0 | 0 | 0 | 19 | 11 | 25 | 21 | 142 | 209 | 32 | 20 | 0 | 60 | 52 | 50 | 50 | 130 | 280 | 49 | 88 | 48 | 103 | 19 | 33 | 0 | 250 | 25 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 105 | 0 | 250 | 106 |  | 650 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 11 | 0 | 8 | 120 | 23 | 32 | 0 | 0 | 50 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 8 | 0 | 67 | 184 | 0 | 0 | 180 | 0 | 184 | 0 | 96 | 0 | 183 | 0 | 0 | 90 | 0 | 0 | 109 |  | 6757 | 2118 | 8875 | 4840 | 650 | 1785 | 1046 | 251 | 82 | 79 | 142 | 0 | 0 | 83.58
2:00 | 38 | 159 | 100 | 120 | 280 | 111 | 20 | 331 | 260 | 0 | 20 | 370 | 270 | 0 | 0 | 0 | 220 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 18 | 17 | 19 | 25 | 31 | 25 | 25 | 0 | 40 | 82 | 0 | 110 | 120 | 0 | 211 | 0 | 130 | 0 | 0 | 41 | 0 | 0 | 10 | 19 | 47 | 19 | 25 | 0 | 0 | 0 | 320 | 290 | 199 | 110 | 50 | 37 | 5 | 5 | 5 | 0 | 0 | 0 | 19 | 11 | 25 | 21 | 138 | 208 | 8 | 0 | 0 | 60 | 52 | 5 | 5 | 100 | 276 | 51 | 50 | 48 | 105 | 0 | 5 | 0 | 260 | 25 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 105 | 0 | 250 | 106 |  | 649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 26 | 16 | 0 | 0 | 50 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 8 | 0 | 67 | 184 | 0 | 0 | 187 | 0 | 161 | 0 | 95 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 108 |  | 6492 | 1812 | 8304 | 4638 | 649 | 1525 | 953 | 251 | 82 | 68 | 138 | 0 | 0 | 83.57
3:00 | 38 | 158 | 100 | 120 | 280 | 111 | 20 | 338 | 260 | 0 | 20 | 370 | 250 | 0 | 0 | 0 | 220 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 18 | 17 | 19 | 25 | 31 | 25 | 25 | 0 | 40 | 82 | 0 | 110 | 120 | 0 | 203 | 0 | 120 | 0 | 0 | 38 | 0 | 0 | 10 | 0 | 47 | 19 | 25 | 0 | 0 | 0 | 320 | 290 | 186 | 110 | 50 | 37 | 5 | 5 | 5 | 0 | 0 | 0 | 19 | 11 | 25 | 21 | 132 | 208 | 0 | 0 | 0 | 60 | 52 | 5 | 5 | 100 | 276 | 51 | 50 | 48 | 104 | 0 | 5 | 0 | 290 | 20 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 88 | 0 | 250 | 109 |  | 650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 27 | 0 | 0 | 0 | 50 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 10 | 5 | 8 | 0 | 67 | 184 | 0 | 0 | 194 | 0 | 159 | 0 | 96 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 108 |  | 6421 | 1799 | 8220 | 4612 | 650 | 1552 | 873 | 251 | 82 | 68 | 132 | 0 | 0 | 83.56
4:00 | 38 | 94 | 100 | 120 | 280 | 62 | 20 | 332 | 260 | 0 | 20 | 370 | 260 | 0 | 0 | 0 | 220 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 18 | 17 | 19 | 25 | 31 | 25 | 25 | 0 | 40 | 82 | 0 | 110 | 120 | 0 | 204 | 0 | 117 | 0 | 0 | 41 | 0 | 0 | 10 | 0 | 25 | 19 | 34 | 0 | 0 | 0 | 320 | 290 | 198 | 63 | 50 | 37 | 5 | 5 | 5 | 0 | 0 | 0 | 19 | 11 | 25 | 21 | 126 | 209 | 0 | 0 | 0 | 60 | 52 | 5 | 5 | 100 | 277 | 51 | 50 | 48 | 103 | 0 | 5 | 0 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 88 | 0 | 250 | 80 |  | 637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 27 | 0 | 0 | 0 | 50 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 10 | 5 | 8 | 0 | 67 | 184 | 0 | 0 | 190 | 0 | 155 | 0 | 96 | 0 | 27 | 0 | 0 | 53 | 0 | 0 | 109 |  | 6199 | 1788 | 7987 | 4568 | 637 | 1455 | 818 | 251 | 82 | 50 | 126 | 0 | 0 | 83.54
5:00 | 38 | 65 | 100 | 120 | 280 | 62 | 20 | 328 | 260 | 0 | 20 | 370 | 260 | 0 | 0 | 0 | 220 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 18 | 17 | 19 | 25 | 22 | 25 | 25 | 0 | 40 | 82 | 0 | 110 | 120 | 0 | 204 | 0 | 114 | 0 | 0 | 41 | 0 | 0 | 10 | 0 | 18 | 19 | 34 | 0 | 0 | 0 | 320 | 290 | 184 | 63 | 50 | 37 | 5 | 5 | 5 | 0 | 0 | 0 | 19 | 11 | 25 | 21 | 120 | 208 | 0 | 0 | 0 | 60 | 52 | 5 | 5 | 100 | 276 | 51 | 50 | 48 | 103 | 0 | 5 | 0 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 60 | 0 | 250 | 40 |  | 636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 26 | 0 | 0 | 0 | 50 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 10 | 5 | 8 | 0 | 68 | 184 | 0 | 0 | 184 | 0 | 149 | 0 | 95 | 0 | 124 | 0 | 0 | 17 | 0 | 0 | 108 |  | 6057 | 1834 | 7891 | 4592 | 636 | 1453 | 706 | 252 | 82 | 50 | 120 | 0 | 0 | 83.52
6:00 | 38 | 43 | 100 | 120 | 280 | 62 | 20 | 326 | 260 | 0 | 20 | 370 | 250 | 0 | 0 | 0 | 220 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 18 | 17 | 19 | 25 | 22 | 25 | 25 | 0 | 40 | 82 | 0 | 110 | 120 | 0 | 204 | 0 | 116 | 0 | 0 | 41 | 0 | 0 | 10 | 0 | 18 | 19 | 35 | 0 | 0 | 0 | 280 | 290 | 184 | 63 | 50 | 37 | 5 | 5 | 5 | 0 | 0 | 0 | 19 | 11 | 8 | 21 | 112 | 209 | 0 | 0 | 0 | 60 | 52 | 5 | 5 | 100 | 276 | 40 | 20 | 47 | 96 | 0 | 5 | 0 | 250 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 249 | 9 |  | 636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 30 | 0 | 0 | 0 | 50 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 10 | 5 | 8 | 0 | 68 | 184 | 0 | 0 | 182 | 0 | 147 | 0 | 51 | 0 | 151 | 0 | 0 | 17 | 0 | 0 | 108 |  | 5769 | 1791 | 7560 | 4518 | 636 | 1353 | 583 | 252 | 82 | 24 | 112 | 0 | 0 | 83.5
7:00 | 38 | 43 | 100 | 120 | 280 | 63 | 20 | 328 | 260 | 0 | 20 | 340 | 270 | 0 | 0 | 0 | 220 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 35 | 18 | 17 | 19 | 25 | 31 | 25 | 25 | 0 | 40 | 83 | 0 | 110 | 120 | 0 | 203 | 0 | 113 | 0 | 0 | 41 | 0 | 0 | 10 | 0 | 18 | 19 | 30 | 0 | 0 | 0 | 280 | 290 | 186 | 63 | 50 | 37 | 5 | 5 | 5 | 0 | 0 | 0 | 19 | 11 | 8 | 15 | 104 | 206 | 0 | 0 | 0.4 | 60 | 52 | 5 | 5 | 100 | 277 | 51 | 10 | 47 | 96 | 0 | 7 | 0 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.97 | 60 | 0 | 0 | 200 | 9 |  | 677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 20 | 0 | 0 | 0 | 60 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 68 | 184 | 0 | 0 | 184 | 0 | 149 | 0 | 11 | 0 | 152 | 0 | 0 | 17 | 0 | 0 | 108 |  | 5743.37 | 1812 | 7555.37 | 4499 | 677 | 1303 | 609 | 252 | 83 | 24 | 104 | 4.37 | 0 | 83.49
8:00 | 38 | 43 | 101 | 120 | 280 | 22 | 20 | 326 | 260 | 0 | 20 | 300 | 265 | 0 | 0 | 0 | 220 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 35 | 18 | 17 | 19 | 25 | 31 | 25 | 25 | 0 | 40 | 82 | 0 | 110 | 120 | 0 | 205 | 0 | 115 | 0 | 0 | 41 | 0 | 0 | 10 | 0 | 19 | 19 | 4 | 0 | 0 | 0 | 280 | 260 | 184 | 63 | 51 | 34 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 15 | 100 | 192 | 0 | 0 | 0 | 60 | 52 | 5 | 5 | 100 | 276 | 40 | 10 | 47 | 101 | 0 | 7 | 0 | 250 | 25 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 60 | 0 | 0 | 180 | 16 |  | 833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 19 | 33 | 0 | 0 | 60 | 0 | 0 | 30 | 0 | 0 | 0 | 10 | 0 | 22 | 17 | 11 | 0 | 69 | 184 | 0 | 0 | 165 | 0 | 145 | 0 | 12 | 0 | 104 | 0 | 0 | 36 | 0 | 0 | 108 |  | 5516 | 1948 | 7464 | 4305 | 833 | 1178 | 674 | 253 | 82 | 30 | 100 | 9 | 0 | 83.48
9:00 | 38 | 43 | 100 | 120 | 280 | 22 | 20 | 327 | 264 | 0 | 20 | 300 | 245 | 0 | 0 | 0 | 220 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 35 | 18 | 17 | 19 | 25 | 31 | 25 | 25 | 8 | 40 | 82 | 0 | 110 | 120 | 0 | 202 | 0 | 115 | 0 | 0 | 41 | 0 | 0 | 10 | 0 | 19 | 19 | 15 | 0 | 0 | 0 | 280 | 260 | 184 | 63 | 50 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 15 | 104 | 191 | 2 | 0 | 1 | 58 | 52 | 5 | 5 | 100 | 280 | 62 | 50 | 47 | 93 | 0 | 6 | 0 | 275 | 25 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 60 | 0 | 0 | 290 | 69 |  | 839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 21 | 116 | 0 | 0 | 60 | 0 | 0 | 50 | 0 | 0 | 0 | 16 | 0 | 22 | 17 | 11 | 0 | 69 | 184 | 0 | 0 | 157 | 0 | 148 | 0 | 11 | 0 | 80 | 0 | 0 | 35 | 0 | 0 | 109 |  | 5773 | 2020 | 7793 | 4388 | 839 | 1258 | 806 | 253 | 82 | 50 | 104 | 13 | 0 | 83.48
10:00 | 38 | 78 | 100 | 120 | 280 | 22 | 20 | 342 | 304 | 0 | 20 | 380 | 280 | 0 | 0 | 0 | 218 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 35 | 18 | 17 | 16 | 25 | 30 | 25 | 16 | 26 | 40 | 81 | 0 | 110 | 120 | 0 | 229 | 0 | 118 | 0 | 0 | 34 | 0 | 0 | 10 | 0 | 19 | 19 | 4 | 0 | 0 | 0 | 280 | 260 | 204 | 63 | 50 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 116 | 187 | 7 | 0 | 1 | 58 | 52 | 5 | 5 | 130 | 280 | 55 | 50 | 46 | 104 | 0 | 6 | 0 | 270 | 25 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 60 | 0 | 0 | 290 | 110 |  | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 20 | 116 | 0 | 0 | 60 | 0 | 0 | 50 | 0 | 0 | 0 | 16 | 0 | 22 | 17 | 11 | 0 | 67 | 184 | 0 | 0 | 165 | 0 | 156 | 0 | 12 | 0 | 80 | 0 | 0 | 17 | 0 | 0 | 108 |  | 6056 | 2016 | 8072 | 4445 | 840 | 1391 | 879 | 251 | 81 | 50 | 116 | 19 | 0 | 83.46
11:00 | 38 | 94 | 100 | 120 | 300 | 22 | 20 | 345 | 340 | 0 | 0 | 420 | 275 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 0 | 7 | 16 | 0 | 0 | 0 | 6 | 35 | 18 | 17 | 0 | 25 | 30 | 25 | 25 | 28 | 40 | 81 | 0 | 110 | 120 | 0 | 212 | 0 | 126 | 0 | 0 | 41 | 0 | 0 | 10 | 0 | 19 | 19 | 3 | 0 | 0 | 0 | 280 | 260 | 141 | 63 | 50 | 0 | 5 | 5 | 5 | 0 | 0 | 0 | 15 | 11 | 8 | 18 | 118 | 189 | 7 | 0 | 2 | 58 | 52 | 5 | 5 | 163 | 277 | 51 | 88 | 42 | 105 | 0 | 6 | 0 | 285 | 25 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.32 | 60 | 0 | 0 | 290 | 110 |  | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 20 | 116 | 0 | 0 | 60 | 0 | 0 | 50 | 0 | 0 | 0 | 16 | 0 | 22 | 17 | 11 | 0 | 65 | 184 | 0 | 0 | 185 | 0 | 159 | 0 | 11 | 0 | 80 | 0 | 0 | 17 | 0 | 35 | 108 |  | 6131.32 | 2071 | 8202.32 | 4358 | 840 | 1547 | 925 | 249 | 81 | 66 | 118 | 18.32 | 0 | 83.45
12:00 | 38 | 94 | 99 | 120 | 340 | 52 | 20 | 337 | 351 | 0 | 0 | 420 | 275 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 0 | 7 | 16 | 0 | 0 | 0 | 6 | 35 | 18 | 17 | 0 | 25 | 30 | 25 | 25 | 51 | 40 | 82 | 0 | 110 | 120 | 4 | 204 | 0 | 120 | 0 | 0 | 41 | 0 | 0 | 10 | 7 | 19 | 19 | 4 | 0 | 0 | 0 | 280 | 300 | 219 | 63 | 50 | 30 | 5 | 5 | 5 | 0 | 0 | 0 | 18 | 11 | 8 | 17 | 124 | 185 | 7 | 0 | 1.2 | 58 | 52 | 5 | 5 | 163 | 274 | 59 | 88 | 42 | 97 | 0 | 7 | 10 | 280 | 25 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.98 | 84 | 0 | 0 | 240 | 110 |  | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 20 | 115 | 0 | 0 | 60 | 0 | 0 | 50 | 0 | 0 | 0 | 16 | 0 | 22 | 16 | 11 | 0 | 67 | 184 | 0 | 0 | 202 | 0 | 189 | 0 | 11 | 0 | 118 | 0 | 0 | 17 | 0 | 35 | 108 |  | 6351.18 | 2181 | 8532.18 | 4578 | 840 | 1594 | 982 | 251 | 82 | 66 | 124 | 15.18 | 0 | 83.44
13:00 | 38 | 94 | 98 | 120 | 340 | 52 | 20 | 325 | 357 | 0 | 0 | 420 | 240 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 7 | 16 | 0 | 0 | 0 | 10 | 35 | 18 | 17 | 13 | 25 | 30 | 25 | 25 | 51 | 40 | 84 | 0 | 110 | 120 | 8 | 206 | 0 | 125 | 0 | 0 | 41 | 0 | 0 | 10 | 33 | 26 | 19 | 4 | 0 | 0 | 0 | 280 | 300 | 187 | 63 | 50 | 39 | 5 | 5 | 5 | 0 | 0 | 0 | 18 | 11 | 10 | 17 | 132 | 172 | 7 | 20 | 2.1 | 58 | 52 | 5 | 5 | 163 | 275 | 56 | 88 | 45 | 94 | 0 | 7 | 10 | 275 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.15 | 100 | 0 | 0 | 240 | 109 |  | 840 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 100 | 21 | 115 | 0 | 0 | 55 | 0 | 0 | 50 | 12 | 0 | 0 | 17 | 0 | 22 | 17 | 11 | 0 | 67 | 184 | 0 | 0 | 193 | 0 | 197 | 0 | 11 | 0 | 142 | 0 | 0 | 17 | 0 | 40 | 108 |  | 6396.25 | 2243 | 8639.25 | 4600 | 840 | 1600 | 1045 | 251 | 84 | 66 | 132 | 21.25 | 0 | 83.43
14:00 | 38 | 94 | 200 | 120 | 300 | 52 | 20 | 327 | 302 | 0 | 0 | 350 | 320 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 0 | 7 | 16 | 0 | 25 | 0 | 12 | 35 | 18 | 17 | 13 | 25 | 30 | 25 | 17 | 51 | 40 | 84 | 0 | 110 | 120 | 8 | 222 | 0 | 120 | 0 | 0 | 41 | 0 | 0 | 10 | 45 | 44 | 19 | 6 | 0 | 0 | 0 | 280 | 300 | 201 | 63 | 50 | 39 | 5 | 5 | 5 | 0 | 0 | 0 | 18 | 11 | 8 | 17 | 144 | 155 | 7 | 20 | 1.4 | 58 | 52 | 5 | 5 | 100 | 295 | 55 | 86 | 45 | 124 | 0 | 7 | 10 | 270 | 24 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 100 | 0 | 0 | 240 | 110 |  | 839 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 100 | 21 | 115 | 0 | 0 | 55 | 0 | 0 | 50 | 12 | 0 | 0 | 17 | 0 | 22 | 16 | 11 | 0 | 67 | 184 | 0 | 0 | 188 | 0 | 190 | 0 | 11 | 0 | 142 | 0 | 0 | 35 | 0 | 53 | 108 |  | 6436.4 | 2260 | 8696.4 | 4674 | 839 | 1406 | 1214 | 251 | 84 | 66 | 144 | 18.4 | 0 | 83.42
15:00 | 38 | 134 | 240 | 120 | 380 | 52 | 20 | 332 | 353 | 0 | 0 | 420 | 215 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 7 | 16 | 0 | 29 | 0 | 12 | 35 | 18 | 17 | 16 | 25 | 30 | 25 | 17 | 42 | 40 | 84 | 0 | 110 | 120 | 8 | 204 | 0 | 120 | 0 | 0 | 41 | 0 | 0 | 10 | 45 | 45 | 19 | 2 | 0 | 0 | 0 | 360 | 360 | 185 | 102 | 50 | 39 | 5 | 5 | 5 | 0 | 0 | 0 | 18 | 11 | 8 | 17 | 146 | 157 | 12 | 20 | 0.3 | 56 | 52 | 41 | 22 | 163 | 277 | 52 | 86 | 45 | 104 | 0 | 30 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 13.1 | 100 | 0 | 0 | 0 | 108 |  | 844 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 120 | 23 | 115 | 0 | 0 | 55 | 0 | 0 | 25 | 12 | 0 | 0 | 8 | 0 | 22 | 17 | 8 | 0 | 67 | 184 | 0 | 0 | 192 | 0 | 203 | 0 | 11 | 0 | 50 | 0 | 0 | 35 | 0 | 53 | 108 |  | 6359.4 | 2176 | 8535.4 | 4619 | 844 | 1434 | 1103 | 251 | 84 | 41 | 146 | 13.4 | 0 | 83.41
16:00 | 38 | 95 | 150 | 120 | 250 | 12 | 20 | 338 | 273 | 0 | 0 | 370 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 16 | 0 | 32 | 0 | 12 | 17 | 18 | 17 | 16 | 25 | 30 | 0 | 17 | 33 | 40 | 84 | 0 | 110 | 120 | 8 | 204 | 0 | 120 | 0 | 0 | 41 | 0 | 0 | 10 | 45 | 45 | 19 | 4 | 0 | 0 | 0 | 300 | 330 | 187 | 110 | 50 | 40 | 5 | 5 | 30 | 0 | 0 | 0 | 18 | 11 | 8 | 17 | 142 | 160 | 21 | 20 | 0.1 | 56 | 51 | 47 | 46 | 163 | 278 | 55 | 40 | 45 | 103 | 0 | 30 | 10 | 0 | 24 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 34 | 7.9 | 100 | 0 | 0 | 0 | 80 |  | 845 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 120 | 26 | 110 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 69 | 184 | 0 | 0 | 162 | 0 | 155 | 0 | 11 | 0 | 59 | 0 | 0 | 35 | 0 | 17 | 108 |  | 5640 | 1998 | 7638 | 3951 | 845 | 1265 | 1074 | 253 | 84 | 16 | 142 | 8 |  | 83.4
17:00 | 38 | 43 | 40 | 120 | 200 | 0 | 0 | 352 | 225 | 0 | 0 | 300 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 12 | 0 | 0 | 0 | 19 | 25 | 30 | 0 | 17 | 25 | 40 | 84 | 0 | 105 | 120 | 8 | 184 | 0 | 120 | 0 | 0 | 41 | 0 | 13 | 10 | 12 | 44 | 19 | 10 | 0 | 0 | 0 | 240 | 250 | 191 | 30 | 50 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 19 | 11 | 8 | 17 | 100 | 162 | 0 | 0 | 0 | 57 | 51 | 47 | 50 | 163 | 257 | 40 | 20 | 45 | 103 | 0 | 36 | 10 | 0 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 2.7 | 50 | 0 | 0 | 0 | 20 |  | 844 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 8 | 0 | 120 | 24 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 68 | 184 | 0 | 0 | 152 | 0 | 135 | 0 | 11 | 0 | 124 | 0 | 0 | 35 | 0 | 17 | 108 |  | 4621.7 | 1935 | 6556.7 | 3586 | 844 | 1004 | 663 | 252 | 84 | 21 | 100 | 2.7 | 0 | 83.39
18:00 | 38 | 44 | 50 | 120 | 180 | 0 | 0 | 273 | 224 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 25 | 40 | 84 | 0 | 105 | 120 | 8 | 204 | 0 | 145 | 0 | 0 | 41 | 0 | 15 | 0 | 12 | 16 | 19 | 12 | 0 | 0 | 0 | 250 | 200 | 160 | 8 | 50 | 10 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 132 | 163 | 0 | 0 | 0 | 56 | 51 | 47 | 50 | 163 | 256 | 50 | 50 | 47 | 100 | 0 | 35 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0.1 | 45 | 0 | 0 | 0 | 18 |  | 844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 25 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 0 | 0 | 68 | 185 | 0 | 0 | 135 | 0 | 131 | 0 | 12 | 0 | 133 | 0 | 0 | 35 | 0 | 17 | 108 |  | 4417.1 | 1916 | 6333.1 | 3314 | 844 | 1025 | 666 | 253 | 84 | 15 | 132 | 0.1 | 0 | 83.38
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 38 | 43 | 46 | 120 | 300 | 12 | 0 | 320 | 359 | 0 | 0 | 420 | 260 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 19 | 0 | 0 | 0 | 18 | 0 | 0 | 25 | 8 | 33 | 13 | 25 | 40 | 84 | 0 | 105 | 120 | 9 | 203 | 0 | 145 | 0 | 0 | 41 | 50 | 83 | 10 | 27 | 13 | 19 | 18 | 0 | 0 | 0 | 300 | 270 | 193 | 54 | 50 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 40 | 165 | 0 | 0 | 0 | 58 | 51 | 47 | 50 | 163 | 286 | 61 | 50 | 47 | 83 | 0 | 37 | 10 | 0 | 25 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 100 | 0 | 0 | 0 | 18 |  | 941 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 40 | 2 | 8 | 120 | 32 | 20 | 0 | 0 | 60 | 0 | 0 | 24 | 12 | 0 | 0 | 8 | 0 | 22 | 5 | 0 | 0 | 68 | 184 | 0 | 17 | 170 | 0 | 166 | 0 | 12 | 0 | 153 | 0 | 0 | 35 | 0 | 17 | 109 |  | 5448 | 2241 | 7689 | 4005 | 941 | 1353 | 782 | 252 | 84 | 232 | 40 | 0 | 0 | 83.37
19:30 | 38 | 44 | 50 | 120 | 250 | 12 | 0 | 325 | 308 | 0 | 0 | 370 | 270 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 40 | 0 | 18 | 0 | 18 | 0 | 19 | 25 | 24 | 33 | 21 | 35 | 40 | 80 | 0 | 105 | 120 | 25 | 203 | 0 | 125 | 0 | 0 | 41 | 47 | 83 | 10 | 60 | 42 | 19 | 29 | 0 | 0 | 0 | 270 | 250 | 194 | 55 | 50 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 84 | 166 | 10 | 0 | 0 | 57 | 52 | 47 | 50 | 130 | 283 | 63 | 88 | 47 | 94 | 0 | 37 | 10 | 5 | 25 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 100 | 34 | 0 | 0 | 30 |  | 941 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 24 | 0 | 8 | 100 | 34 | 0 | 0 | 0 | 60 | 0 | 0 | 39 | 12 | 0 | 0 | 25 | 0 | 22 | 5 | 5 | 0 | 68 | 184 | 0 | 17 | 184 | 0 | 186 | 0 | 11 | 0 | 175 | 0 | 0 | 35 | 0 | 17 | 108 |  | 5524 | 2276 | 7800 | 3971 | 941 | 1275 | 971 | 252 | 80 | 226 | 84 | 0 | 0 | 0
20:00 | 38 | 43 | 50 | 120 | 250 | 12 | 0 | 330 | 309 | 0 | 0 | 370 | 250 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 40 | 0 | 18 | 0 | 18 | 0 | 19 | 25 | 24 | 33 | 21 | 44 | 40 | 80 | 0 | 110 | 120 | 25 | 203 | 0 | 125 | 0 | 0 | 41 | 47 | 83 | 10 | 81 | 40 | 19 | 31 | 0 | 0 | 0 | 195 | 200 | 183 | 55 | 50 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 106 | 164 | 15 | 0 | 0 | 58 | 52 | 49 | 50 | 100 | 283 | 62 | 88 | 47 | 87 | 0 | 37 | 10 | 15 | 25 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 100 | 34 | 0 | 0 | 65 |  | 940 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 24 | 0 | 8 | 100 | 6 | 0 | 0 | 0 | 60 | 0 | 0 | 50 | 12 | 0 | 0 | 25 | 0 | 22 | 5 | 5 | 0 | 69 | 184 | 0 | 0 | 188 | 0 | 190 | 0 | 11 | 0 | 187 | 0 | 0 | 35 | 0 | 17 | 105 |  | 5443 | 2259 | 7702 | 3855 | 940 | 1232 | 1016 | 253 | 80 | 220 | 106 | 0 | 0 | 83.36
21:00 | 38 | 43 | 51 | 120 | 250 | 12 | 0 | 325 | 300 | 0 | 0 | 370 | 260 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 40 | 0 | 24 | 0 | 18 | 0 | 19 | 25 | 32 | 33 | 17 | 51 | 40 | 80 | 0 | 110 | 120 | 25 | 203 | 0 | 125 | 0 | 0 | 32 | 47 | 83 | 10 | 52 | 40 | 19 | 33 | 0 | 0 | 0 | 250 | 200 | 191 | 53 | 50 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 8 | 33 | 10 | 82 | 164 | 30 | 0 | 0 | 58 | 52 | 50 | 50 | 100 | 280 | 64 | 88 | 47 | 91 | 0 | 37 | 10 | 30 | 25 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 100 | 34 | 0 | 0 | 110 |  | 942 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 17 | 0 | 8 | 100 | 10 | 0 | 0 | 0 | 60 | 0 | 0 | 50 | 12 | 0 | 0 | 25 | 0 | 22 | 5 | 8 | 0 | 68 | 184 | 0 | 0 | 184 | 0 | 186 | 0 | 0 | 0 | 204 | 0 | 0 | 53 | 0 | 17 | 109 |  | 5553 | 2280 | 7833 | 3949 | 942 | 1232 | 1083 | 252 | 80 | 213 | 82 | 0 | 0 | 83.35
22:00 | 38 | 44 | 51 | 120 | 250 | 12 | 0 | 328 | 300 | 0 | 0 | 370 | 270 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 40 | 0 | 24 | 0 | 18 | 0 | 0 | 25 | 32 | 33 | 25 | 43 | 40 | 80 | 0 | 110 | 120 | 25 | 197 | 0 | 80 | 0 | 0 | 32 | 8 | 52 | 10 | 52 | 41 | 19 | 3 | 0 | 0 | 0 | 245 | 200 | 202 | 53 | 50 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 76 | 163 | 30 | 20 | 0 | 60 | 52 | 50 | 50 | 100 | 287 | 51 | 88 | 48 | 97 | 0 | 37 | 10 | 45 | 25 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 100 | 30 | 0 | 0 | 110 |  | 941 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 17 | 0 | 8 | 120 | 10 | 0 | 0 | 0 | 60 | 0 | 0 | 50 | 0 | 0 | 0 | 25 | 0 | 22 | 5 | 0 | 0 | 67 | 184 | 0 | 0 | 188 | 0 | 181 | 0 | 13 | 0 | 196 | 0 | 0 | 53 | 0 | 0 | 108 |  | 5411 | 2264 | 7675 | 3903 | 941 | 1231 | 1050 | 251 | 80 | 143 | 76 | 0 | 0 | 83.34
23:00 | 38 | 43 | 50 | 120 | 250 | 12 | 0 | 342 | 300 | 0 | 0 | 370 | 280 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 40 | 0 | 27 | 17 | 18 | 0 | 19 | 25 | 32 | 33 | 25 | 43 | 40 | 80 | 0 | 110 | 120 | 25 | 215 | 0 | 110 | 0 | 0 | 32 | 0 | 0 | 10 | 52 | 35 | 19 | 33 | 0 | 0 | 0 | 240 | 200 | 198 | 62 | 50 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 33 | 7 | 84 | 180 | 30 | 20 | 0 | 60 | 52 | 50 | 50 | 100 | 288 | 65 | 88 | 48 | 118 | 0 | 37 | 10 | 95 | 25 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 110 |  | 841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 11 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 5 | 0 | 69 | 184 | 0 | 0 | 196 | 0 | 159 | 0 | 12 | 0 | 151 | 0 | 0 | 53 | 0 | 0 | 108 |  | 5557 | 1996 | 7553 | 3979 | 841 | 1320 | 980 | 253 | 80 | 16 | 84 | 0 | 0 | 83.33
24:00 | 38 | 43 | 42 | 120 | 250 | 12 | 0 | 344 | 320 | 0 | 0 | 370 | 230 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 17 | 18 | 0 | 19 | 25 | 32 | 33 | 25 | 25 | 40 | 80 | 0 | 110 | 120 | 0 | 202 | 0 | 130 | 0 | 0 | 32 | 0 | 0 | 10 | 49 | 46 | 19 | 39 | 0 | 0 | 0 | 250 | 260 | 183 | 53 | 50 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 19 | 0 | 33 | 15 | 92 | 181 | 0 | 20 | 0 | 58 | 52 | 50 | 46 | 130 | 280 | 58 | 88 | 48 | 105 | 0 | 37 | 10 | 150 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 110 |  | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 11 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 0 | 0 | 69 | 184 | 0 | 0 | 179 | 0 | 177 | 0 | 12 | 0 | 172 | 0 | 0 | 11 | 0 | 0 | 90 |  | 5545 | 1952 | 7497 | 4049 | 840 | 1418 | 765 | 253 | 80 | 0 | 92 | 0 | 0 | 83.32
KWH | 849000 | 2090500 | 2270000 | 2898000 | 6570218 | 997366 | 380008 | 8086948 | 6917000 | 0 | 213200 | 8650125 | 6429295 | 0 | 0 | 0 | 4126619 | 0 | 840000 | 0 | 0 | 57600 | 167040 | 0 | 290880 | 0 | 278880 | 568800 | 395061 | 296220 | 345204 | 600000 | 653580 | 570900 | 496800 | 614556 | 958186 | 1878082 | 0 | 2600000 | 3000000 | 179771 | 4897302 | 0 | 2939590 | 0 | 0 | 927360 | 150672 | 348763 | 275640 | 624000 | 775200 | 422592 | 461280 | 0 | 0 | 0 | 7239700 | 6564000 | 4612000 | 1639272 | 1192980 | 819216 | 129600 | 120000 | 309524 | 0 | 0 | 0 | 270144 | 152820 | 422900 | 332770 | 2742720 | 4304480 | 285120 | 160380 | 13150 | 1388000 | 1242520 | 577800 | 579000 | 3200220 | 6328000 | 1279776 | 1535040 | 1064160 | 2441740 | 17000 | 454880 | 131580 | 4345286 | 540192 | 225024 | 0 | 20070 | 0 | 0 | 0 | 0 | 164160 | 134730 | 2058240 | 612480 | 0 | 3542800 | 1953600 |  | 19126546 | 0 | 0 | 0 | 187200 | 0 | 0 | 0 | 122880 | 17152 | 100125 | 2615000 | 511334 | 1055904 | 0 | 0 | 1370000 | 0 | 0 | 872548 | 16990 | 0 | 0 | 223680 | 0 | 440400 | 216936 | 176688 | 0 | 1595782 | 4497400 | 0 | 24000 | 4590245 | 0 | 4175245 | 0 | 771328 | 0 | 3112209 | 0 | 0 | 949440 | 0 | 386880 | 2648138 |  | 142239312 | 49804050 | 192043362 | 104544468 | 19126546 | 33432139 | 22375290 | 6093182 | 1878082 | 1703055 | 2742720 | 147880 | 0
Fuel Cost | 730140 | 1797830 | 1952200 | 2492280 | 4204939.52 | 807866.46 | 357207.52 | 4933038.28 | 4219370 | 0 | 292084 | 5795583.75 | 97660991.05 | 0 | 0 | 0 | 2682302.35 | 0 | 932400 | 0 | 0 | 379584 | 1615276.8 | 0 | 1742371.2 | 0 | 1860129.6 | 4055544 | 2469131.25 | 1857299.4 | 258903 | 450000 | 0 | 0 | 0 | 5813699.76 | 1101913.9 | 0 | 0 | 2860000 | 3300000 | 1702431.37 | 3232219.32 | 0 | 3380528.5 | 0 | 0 | 8151494.4 | 1622737.44 | 3393463.99 | 1706211.6 | 4031040 | 5069808 | 359203.2 | 0 | 0 | 0 | 0 | 4488614 | 4529160 | 3228400 | 1131097.68 | 1145260.8 | 548874.72 | 111456 | 110400 | 253809.68 | 0 | 0 | 0 | 208010.88 | 114615 | 325633 | 249577.5 | 18760204.8 | 3228360 | 2620252.8 | 123492.6 | 0 | 1443520 | 1292220.8 | 554688 | 521100 | 2496171.6 | 4429600 | 1458944.64 | 1642492.8 | 1170576 | 2783583.6 | 21760 | 423038.4 | 122369.4 | 2780983.04 | 405144 | 171018.24 | 0 | 145708.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5720563.2 | 0 | 3082236 | 0 |  | 97545384.6 | 0 | 0 | 0 | 1551888 | 0 | 0 | 0 | 1383628.8 | 202050.56 | 788985 | 1804350 | 506220.66 | 7813689.6 | 0 | 0 | 1438500 | 0 | 0 | 7818030.08 | 146963.5 | 0 | 0 | 2218905.6 | 0 | 484440 | 203919.84 | 133752.816 | 0 | 9686396.74 | 17359964 | 0 | 642480 | 3121366.6 | 0 | 2922671.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 261114161.04 | 157773587.896 | 418887748.936 | 77658648.766 | 97545384.6 | 23692790.83 | 157506691.53 | 27046360.74 | 0 | 16677667.67 | 18760204.8 | 0 | 0
Yesterday Day Peak | 38 | 94 | 99 | 120 | 340 | 52 | 20 | 337 | 351 | 0 | 0 | 420 | 275 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 0 | 7 | 16 | 0 | 0 | 0 | 6 | 35 | 18 | 17 | 0 | 25 | 30 | 25 | 25 | 51 | 40 | 82 | 0 | 110 | 120 | 4 | 204 | 0 | 120 | 0 | 0 | 41 | 0 | 0 | 10 | 7 | 19 | 19 | 4 | 0 | 0 | 0 | 280 | 300 | 219 | 63 | 50 | 30 | 5 | 5 | 5 | 0 | 0 | 0 | 18 | 11 | 8 | 17 | 124 | 185 | 7 | 0 | 1.2 | 58 | 52 | 5 | 5 | 163 | 274 | 59 | 88 | 42 | 97 | 0 | 7 | 10 | 280 | 25 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.98 | 84 | 0 | 0 | 240 | 110 |  | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 20 | 115 | 0 | 0 | 60 | 0 | 0 | 50 | 0 | 0 | 0 | 16 | 0 | 22 | 16 | 11 | 0 | 67 | 184 | 0 | 0 | 202 | 0 | 189 | 0 | 11 | 0 | 118 | 0 | 0 | 17 | 0 | 35 | 108 |  | 8532.18 | DayPeak
Yesterday Evening Peak | 38 | 43 | 51 | 120 | 250 | 12 | 0 | 325 | 300 | 0 | 0 | 370 | 260 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 40 | 0 | 24 | 0 | 18 | 0 | 19 | 25 | 32 | 33 | 17 | 51 | 40 | 80 | 0 | 110 | 120 | 25 | 203 | 0 | 125 | 0 | 0 | 32 | 47 | 83 | 10 | 52 | 40 | 19 | 33 | 0 | 0 | 0 | 250 | 200 | 191 | 53 | 50 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 8 | 33 | 10 | 82 | 164 | 30 | 0 | 0 | 58 | 52 | 50 | 50 | 100 | 280 | 64 | 88 | 47 | 91 | 0 | 37 | 10 | 30 | 25 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 100 | 34 | 0 | 0 | 110 |  | 942 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 17 | 0 | 8 | 100 | 10 | 0 | 0 | 0 | 60 | 0 | 0 | 50 | 12 | 0 | 0 | 25 | 0 | 22 | 5 | 8 | 0 | 68 | 184 | 0 | 0 | 184 | 0 | 186 | 0 | 0 | 0 | 204 | 0 | 0 | 53 | 0 | 17 | 109 |  | 7833 | EvPeak
Forecast for Evening | 38 | 140 | 270 | 120 | 360 | 50 | 40 | 412 | 360 | 110 | 0 | 450 | 305 | 92 | 100 | 55 | 0 | 0 | 100 | 0 | 100 | 102 | 149 | 100 | 60 | 0 | 48 | 54 | 55 | 55 | 19 | 25 | 32 | 33 | 33 | 50 | 40 | 80 | 30 | 110 | 120 | 25 | 225 | 0 | 150 | 0 | 0 | 41 | 50 | 83 | 78 | 100 | 50 | 22 | 40 | 0 | 0 | 0 | 360 | 360 | 221 | 195 | 100 | 40 | 5 | 5 | 40 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 160 | 202 | 82 | 20 | 0 | 60 | 60 | 50 | 44 | 163 | 320 | 66 | 86 | 45 | 120 | 20 | 46 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 285 | 112 |  | 852 | 46 | 0 | 0 | 115 | 0 | 0 | 0 | 36 | 80 | 40 | 100 | 33 | 110 | 26 | 0 | 65 | 50 | 54 | 100 | 35 | 50 | 40 | 52 | 36 | 22 | 17 | 11 | 0 | 70 | 184 | 17 | 18 | 200 | 0 | 225 | 0 | 95 | 100 | 200 | 0 | 0 | 105 | 0 | 113 | 100
Forecast for Day | 38 | 140 | 270 | 120 | 360 | 50 | 40 | 412 | 360 | 110 | 0 | 450 | 305 | 92 | 100 | 55 | 0 | 0 | 100 | 0 | 100 | 102 | 149 | 100 | 60 | 0 | 48 | 54 | 55 | 55 | 19 | 25 | 32 | 33 | 33 | 50 | 40 | 80 | 30 | 110 | 120 | 25 | 225 | 0 | 150 | 0 | 0 | 41 | 50 | 68 | 78 | 100 | 50 | 22 | 40 | 0 | 0 | 0 | 360 | 360 | 221 | 195 | 100 | 40 | 5 | 5 | 40 | 0 | 0 | 52 | 22 | 11 | 33 | 21 | 131 | 202 | 82 | 20 | 2 | 60 | 60 | 50 | 44 | 163 | 300 | 66 | 86 | 46 | 120 | 20 | 46 | 10 | 341 | 25 | 11 | 100 | 200 | 200 | 100 | 200 | 100 | 149 | 20 | 100 | 200 | 150 | 250 | 112 |  | 772 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 30 | 0 | 40 | 100 | 33 | 110 | 0 | 0 | 65 | 0 | 0 | 100 | 35 | 50 |  | 52 | 0 | 22 | 17 | 11 | 0 | 70 | 184 | 0 | 0 | 200 | 0 | 225 | 0 | 95 | 0 | 200 | 0 | 0 | 105 | 0 | 113 | 100
Generation at 08:00(Today) | 38 | 74 | 50 | 120 | 250 | 0 | 0 | 300 | 230 | 0 | 0 | 300 | 280 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 18 | 17 | 0 | 25 | 32 | 33 | 25 | 0 | 40 | 84 | 0 | 110 | 120 | 0 | 211 | 0 | 130 | 0 | 0 | 8 | 0 | 0 | 10 | 0 | 6 | 19 | 42 | 0 | 0 | 0 | 60 | 200 | 197 | 53 | 50 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 11 | 0 | 10 | 80 | 160 | 0 | 0 | 1 | 58 | 52 | 5 | 5 | 100 | 268 | 40 | 5 | 5 | 97 | 0 | 7 | 10 | 285 | 25 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6 | 10 | 0 | 0 | 0 | 9 | 0 | 743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 10 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 11 | 0 | 71 | 184 | 0 | 0 | 135 | 0 | 132 | 0 | 12 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 20 | 0
199
| Minimum Generation |  | 7464 | 8:00
| Highest Generation |  | 8875 | 1:00
| Day Peak Generation |  | 8532.18 | 12:00
| Evening Peak Generation |  | 7833 | 21:00
| HVDC Max Flow |  | 942 | 21:00
| HVDC EvPeak Flow |  | 942 | 21:00
| Load factor L.F |  | 90.16%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-04-14
Till now the maximum generation is : - |  |  | 11623 MW | 19:30 | Hrs on | 2018-09-19
The Summary of Yesterday's |  | 2019-04-13 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8532.18 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 5933 | MW
Evening Peak Generation : |  | 7833 | MW Hour : | 21:00 | Available Max Generation : |  | 14200 | MW
E.P. Demand (at gen end) : |  | 7833 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 9700 | MW
Maximum Generation : |  | 8875 | MW Hour : | 1:00 | Reserve(Generation end) |  | 4500 | MW
Total Gen. (MKWH) : |  | 192.0434 | System Load Factor : | 90.16% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -860 | MW at | 3:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-04-14
Actual : | 83.26 | Ft.(MSL) , | Rule curve : | 85.4 | Ft.( MSL )
Gas Consumed : | Total = | 1145.69 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 101351439.596
|  | Coal : | 27046360.74 | Oil : | 174184359.2 | Total : | 302582159.536
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3422.2216 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1159.9332 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1038.5826 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 938.2058 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 847.976 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 684.277 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 387.5188 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 176.3127 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 527.7249 |  |  | 0 | 0%
Total | 0 |  | 9182.7527 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1 |  | 7) Ghorashal Unit-1
|  |  |  | 2) Khulna ST 110 MW |  | 8) Haripur SBU-1
3) Sikalbaha ST 60 MW
4) Bheramara 410 MW.
5) Siddhirganj ST
6) Ashuganj #3,4,5
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Tangail 132 kV main bus was under shut down from 09:00 to 10:13 for C/M. |  |  |  |  | About 111 MW power interruption occurred under
Tangail S/S areas from 09:00 to 10:13.
b) TK Chemical 132 kV busbar & its related bay were under shut down from 10:21 to 16:33 for D/W.
c) Faridpur-Bheramara 132 kV Ckt-2 was under shut down from 11:11 to 12:08 for D/W.
d) Satkhira 132/33 kV T1 transformer was under shut down from 10:24 to 12:30 due to 33 kV |  |  |  |  | About 15 MW power interruption occurred under
Kolaroya feeder work. |  |  |  |  | Satkhira S/S areas from 10:24 to 12:30.
e) Sirajgonj 230 kV switching-Sirajganj unit-4 Ckt was under shut down from 10:56 to 21:29
due to to red hot at Sirajganj 230 kV S/S end.
f) Faridpur-Bheramara 132 kV Ckt-1 was under shut down from 12:50 to 20:44 due to load
observation of Ckt-2.
g) After maintenance Sikalbaha-Bakulia 132 Ckt-2 was switched on at 13:52.
h) Summit Bibiyana-2 tripped at 14:00 due to low gas pressure and was synchronized at 19:02.
i) Aminbazar-Kaliakoir 230 kV Ckt-1 was under shut down from 14:55 to 15:21 for C/M
j) Bibiyana unit-3 tripped at 14:18 due to low gas pressure.
k) Shahjadpur-Pabna tripped at 14:31 from both end showing Dist C-phase at Shahjadpur |  |  |  |  | About 85 MW power interruption occurred under Panchagar
and was switched on at 14:58. |  |  |  |  | Thakurgaon S/S areas from 19:50 to 19:57.
l) Tangail-Mymenshing RPCL 132 kV Ckt-1 tripped at 16:45 from both end showing Dist. Z1
relays and was switched on at 17:12.
m) Tangail-Mymenshing RPCL 132 kV Ckt-2 tripped at 16:58 from both end showing Dist.
Z1 relays and was switched on at 17:19.
n) Saidpur-Purbasadipur 132 kV Ckt-1 & 2 tripped at 19:50 showing E/F, Dist. Z3 relays at
Saidpur end and were switched on at 19:57.
o) Gopalganj 132/33 kV T1 & T2 transformers tripped at 18:50 from both end showing O/C
relays and were switched on at 19:31.
p) Hasnabad 132/33 kV T1 T2 & T3 transformers tripped at 22:22 from both end showing |  |  |  |  | About 100 MW power interruption occurred under Hasnabad
O/C relays due to 33 kV Dohar feeder fault and were switched on at 22:39. |  |  |  |  | S/S areas from 22:22 to 22:39.
q) After maintenance Siddirganj-Ullon 132 kV Ckt-1 was switched on at 22:31.
r) Ishwardi-Baghabari 132 kV Ckt tripped at 23:37 showing Dist. relay at Ishwardi S/S end &
Dist. 3-phase relay
at Baghabari S/S end and was switched on at 00:12(14/4/2019)
s) Bhulta 400/230 kV ATR-1 Transformer tripped at 02:44(14/4/2019) due to operating PRD.
t) Netrokona 132/33 kV T1 & T2 Transformers tripped at 06:05(14/4/2019) showing E/F & |  |  |  |  | About 18 MW power interruption occurred under Netrokona
O/C as R-Phase, pole(Breaker) of 33 kV PBS-1 feeder got burst and 33 kV incomer breaker |  |  |  |  | S/S areas from 06:05(14/4/2019) to 06:57(14/4/2019).
& T-2 Transformer got damage and was switched on at 06:57(14/4/2019)
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-04-13 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 38 | 849000 | Unit-1 under maint.
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 43 | 2090500 | On test
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 51 | 2270000 | On test
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 120 | 2898000
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 250 | 6570218 | Frequency control
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 0 | 380008
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 12 | 997366 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 213200 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 325 | 8086948 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 0 | 0 | Reserve
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 300 | 6917000 | Frequency control
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 370 | 8650125 | Frequency control
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 260 | 6429295 | FGMO
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 345204
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 0 | 840000 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 0 | Reserve
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 110 | 4126619 | Frequency control
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 0 | 57600 | Reserve
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 24 | 278880 | Low demand
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 0 | 568800 | Reserve
25 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 16 | 167040 | Low demand
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 18 | 395061 | Low demand
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 0 | 296220 | Reserve
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 40 | 290880 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1253580 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 570900
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 17 | 496800 | Engine problem
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 51 | 614556 | Low demand
33 | Tongi GT |  | PDB | 1* 105 | 105 | 40 | 958186 | Gas shortage
34 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 0 | 20070 | Reserve
35 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
36 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
37 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
38 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 17 | 164160 | Low demand
| Dhaka area Total |  |  |  | 5798 | 2211 | 57796216
39 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 110 | 2600000 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 120 | 3000000 | Gas shortage
40 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 179771
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 134730
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 40 | 775200
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1878082 | Low water lavel
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4897302 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 125 | 2939590 | Frequency control
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 32 | 927360 | Engine problem
47 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 47 | 150672 | Reserve
48 | Dohazari Peaking |  | PDB | 6*17 | 102 | 83 | 348763
49 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 275640 | Low demand
| Juldah 100 MW Unit-3 |  | IPP | 0 | 100 | 100 | 2058240
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 422592
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 33 | 461280
51 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 52 | 624000 | Low demand
| Chattogram area Total |  |  |  | 1681 | 1079 | 21673222
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 191 | 4612000 | FGMO
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 250 | 7239700 | Frequency control
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 200 | 6564000 | Frequency control
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 40 | 819216
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 5 | 129600 | Gas shortage
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 53 | 1639272 | Low demand
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 5 | 309524 | Low demand
| Midland 150MW |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
61 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
62 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
63 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1192980 | machine problem
| Chandpur Desh 200MW |  | IPP | 0 | 200 | 34 | 612480 | Low demand
64 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 0 | 270144 | tripped at 19:20
65 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 152820
** | Tripura |  | Imported power | 0 | 160 | 82 | 2742720
66 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 422900
67 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
68 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 10 | 332770
69 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 966 | 27160126
70 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 164 | 4304480 | Gas shortage
71 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 0 | 160380 | tripped at 16:40
72 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 30 | 285120 | Low demand
73 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 13150
74 | United Mymensingh PPL |  | IPP | 200 | 200 | 0 | 0 | Reserve
| United Jamalpur PPL |  | IPP | 115 MW | 115 | 110 | 1953600
| Mymensingh Area Total |  |  |  | 637 | 304 | 6716730
75 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 58 | 1388000
76 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 52 | 1242520
77 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 100 | 3200220 | Low demand
78 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 280 | 6328000 | Frequency control
79 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 50 | 577800
80 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 50 | 579000
81 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 225024
82 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 64 | 1279776 | FGMO
83 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 88 | 1535040
84 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 47 | 1064160 | machine problem
85 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 91 | 2441740 | FGMO
86 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 17000 | Low demand
87 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 37 | 454880 | Engine problem
88 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 25 | 540192
89 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 30 | 4345286 | FGMO
| Bibiyana-3 285 MW |  | PDB | 285 MW | 0 | 0 | 3542800 | On test
90 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 131580
| Sylhet Area Total |  |  |  | 1549 | 993 | 28893018
91 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 942 | 19126546
92 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
93 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 16 | 187200 | Low demand
94 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 17 | 122880 | Low demand
95 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
96 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 0 | 17152 | Reserve
97 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
98 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 8 | 100125 | Low demand
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
99 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
| Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 53 | 949440 | Low demand
| Madhumati Power Plant |  | IPP | 100 MW | 0 | 109 | 2648138 | on test.
| Khulna Area Total |  |  |  | 2209 | 1145 | 23151481
100 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 0 | 1055904 | Reserve
101 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
102 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 10 | 511334
103 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 100 | 2615000 | ST under maintenance
104 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 0 | 771328 | Reserve
| Barisal Area Total |  |  |  | 462 | 110 | 4953566
105 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 60 | 1370000
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
106 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
107 | Bera Peaking |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
108 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 12 | 16990 | Low demand
109 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
110 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
111 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 184 | 4590245 | FGMO
112 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 186 | 4175245 | FGMO
113 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 204 | 3112209 | FGMO
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282 | 282 | 0 | 0 | under S/D
114 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
115 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 440400
116 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 5 | 216936 | Low demand
117 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 176688
118 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 25 | 223680 | Low semand
119 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 50 | 872548
| Paramount Baghabari |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
| Confidence CPBL-2 |  | IPP | 113 MW | 113 | 17 | 386880 | Low demand
| Rajshahi Area Total |  |  |  | 1938 | 773 | 15581821
120 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 68 | 1595782
121 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 184 | 4497400
122 | Rangpur GT |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
123 | Saidpur GT |  | PDB | 1*20 | 20 | 0 | 24000 | tripped at 19:47
| Rangpur Area Total |  |  |  | 484 | 252 | 6117182
| Total |  |  |  | 17649 | 7833 | 192043362
| Eastern Grid Total |  |  |  | 12556 | 5553 | 142239312
| Western Grid Total |  |  |  | 5093 | 2280 | 49804050
| National Grid Total |  |  |  | 17649 | 7833 | 192043362
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2019-04-13 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 5525 | MW | (b) ENTIRE WESTERN GRID : |  |  | 1880 | MW
i) Dhaka area |  |  | 2934 | MW | i) Khulna area |  |  | 552 | MW
ii) Chittagong area |  |  | 1106 | MW | ii) Rajshahi area |  |  | 709 | MW
iii) Comilla area |  |  | 421 | MW | iii) Barisal area |  |  | 54 | MW
iv) Mymensingh area |  |  | 626 | MW | iv) Rangpur area |  |  | 565 | MW
v) Sylhet area |  |  | 438 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 7405 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 110 | 1200 | Netrokona | 72 | 2000 | Central s/s | 63 | 1300
Munsiganj | 91 | 100 | Jamalpur | 102 | 1500 | Noapara | 63 | 100
Sonargaon | 61 | 1600 | Sherpur | 68 | 2000 | Jessore | 126 | 100
Shyampur | 172 | 1500 | Srimongal | 34 | 1800 | Jhenida | 76 | 100
Bhulta | 167 | 1200 | Shahjibazar | 102 | 2200 | Bottail | 82 | 1300
Madanganj | 53 | 1300 | Fenchuganj | 42 | 1930 | G.K Project | 36 | 100
Shitalakhya | 104 | 1500 | Kulawara | 40 | 2100 | Faridpur | 120 | 100
Rahim steel | 25 | 1800 | Sylhet | 131 | 1900 | Madaripur | 109 | 100
Matuail | 86 | 1200 | Chatak | 29 | 1930 | Gopalganj | 58 | 100
Ghorasal | 60 | 1930 | Sunamganj | 32 | 2000 | Bagerhat | 52 | 100
Narsingdi | 107 | 100 | Biani Bazar | 42 | 1930 | Mongla | 40 | 1200
Haripur (SBU) | 83 | 300 | Comilla (S) | 146 | 1500 | Satkhira | 75 | 100
Ullon | 62 | 1500 | Comilla(N) | 92 | 1700 | Gallamari | 52 | 1300
Hasnabad | 167 | 1300 | Chandpur | 91 | 1500 | Magura | 38 | 100
Magbazar | 90 | 1200 | Feni | 123 | 1830 | Chuadanga | 74 | 100
Maniknagar | 96 | 1100 | Chowmuhani | 152 | 1900 | Barisal | 108 | 1830
Bangabhaban | 18 | 1200 | Ashuganj | 47 | 1900 | Patuakhali | 80 | 1900
Narinda | 96 | 1200 | Daudkandi | 100 | 1500 | Bhandaria | 40 | 1830
Dhanmondi | 128 | 1200 | B.Baria | 110 | 2000 | Ishurdi | 41 | 1300
Lalbag | 61 | 1400 | Ramganj | 46 | 1830 | Ruppur Paromanobik | 1 | 100
Madartek | 48 | 1900 | Madunaghat | 58 | 2100 | Natore | 83 | 100
Mirpur | 90 | 1300 | Hathazari | 95 | 1900 | Bogra | 176 | 200
Kalyanpur | 96 | 1300 | Khulshi | 205 | 2000 | Noagaon | 92 | 100
Gulshan | 108 | 1300 | Halishahar | 128 | 2000 | Rajshahi | 126 | 100
Uttara | 45 | 1200 | Baraulia | 145 | 900 | C.Nawabganj | 64 | 100
Uttara(New) | 11 | 1200 | Sikalbaha | 42 | 1830 | Amnura | 34 | 100
Kamrangirchar | 69 | 1200 | Dohazari | 98 | 1900 | Pabna | 75 | 1300
Savar | 116 | 1000 | Cox'sbazar | 91 | 2100 | Shahjadpur | 78 | 1000
Bhasantec | 148 | 1300 | Chandraghona | 28 | 1900 | Serajganj | 76 | 1100
Agargaon | 44 | 1300 | Kaptai | 0 | 0 | Niyamatpur | 61 | 800
Satmosjid | 87 | 1500 | A. Khaer Stl. | 0 | 0 | Joypurhat | 40 | 1900
Tongi | 112 | 1830 | Bakulia | 101 | 1900 | Mohastangor | 9 | 1900
Kabirpur | 168 | 1500 | Julda | 0 | 0 | Rangpur | 129 | 1900
Basundhara | 122 | 1300 | TK chemical | 5 | 1830 | Lalmonirhat | 92 | 1900
Manikganj | 169 | 100 | Modern Steel | 13 | 1200 | Saidpur | 96 | 1930
Joydevpur | 175 | 1200 | Shahmirpur | 30 | 2000 | Purbasadipur | 98 | 1930
New Tongi | 104 | 1200 | Khagrachhari | 16 | 1830 | Thakurgaon | 58 | 1200
Kodda | 204 | 1500 | Matarbari | 28 | 2000 | Palashbari | 86 | 100
Dhamrai | 46 | 1400 | Baroiar Hat | 22 | 2100 | Barapukuria | 43 | 1930
Valuka | 60 | 1400 | Rangamati | 10 | 1830 | Panchagar | 34 | 1500
Tangail | 140 | 100 | Abul Khair 230 | 120 | 1500 | Joldhaka | 18 | 1930
Mymensing | 178 | 2100 | BSRM | 143 | 1900
Kishorganj | 92 | 2100 | Goalpara | 17 | 1300
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-04-13
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 396 | 1:00 | 383 | 19:00 | Kaliakoir | 385 | 17:00 | 370 | 14:00
Bheramara | 400 | 6:00 | 384 | 19:30 | Bhulta | 400 | 17:00 | 387 | 12:00
Ashuganj(N) | 402 | 5:00 | 391 | 12:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 235 | 1:00 | 232 | 18:00 | Hathazari | 221 | 21:00 | 213 | 1:00
Ishurdi | 236 | 2:00 | 225 | 12:00 | Megnaghat | 230 | 4:00 | 223 | 13:00
Ashuganj | 240 | 1:00 | 234 | 12:00 | Fenchuganj | 240 | 24:00 | 233 | 18:30
Serajganj | 232 | 16:00 | 225 | 1:00 | Siddhirganj | 229 | 5:00 | 221 | 12:00
Baghabari | 231 | 15:00 | 222 | 21:00 | Maniknagar | 227 | 5:00 | 218 | 15:00
Barapukuria | 228 | 15:00 | 221 | 8:00 | Old Airport | 229 | 17:00 | 217 | 12:00
Bogra | 231 | 16:00 | 215 | 8:00 | Barisal | 244 | 19:30 | 230 | 7:00
Khulna South | 233 | 18:00 | 210 | 13:00 | AKSML | 219 | 3:00 | 214 | 15:00
Rampura | 228 | 5:00 | 220 | 13:00 | BSRM | 223 | 6:00 | 216 | 18:30
Haripur | 228 | 17:00 | 220 | 12:00 | Bibiyana | 237 | 17:00 | 229 | 18:30
Hasnabad | 230 | 5:00 | 220 | 12:00 | Bhulta | 229 | 4:00 | 221 | 12:00
Aminbazar | 228 | 6:00 | 219 | 12:00 | Ashuganj (S) | 238 | 5:00 | 232 | 12:00
Tongi | 227 | 4:00 | 218 | 12:00 | Kaliakoir | 231 | 17:00 | 222 | 12:00
Comilla (N) | 234 | 5:00 | 229 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 133 | 1700 | 126 | 1200 | Madanhat | 132 | 700 | 126 | 1830
Munsiganj | 133 | 1700 | 125 | 1200 | Hathazari | 132 | 2100 | 128 | 1000
Megnaghat | 132 | 1700 | 126 | 1200 | Khulshi | 130 | 700 | 124 | 1830
Shyampur | 131 | 1700 | 124 | 1200 | Halishahar | 132 | 700 | 126 | 1830
Bhulta | 129 | 1700 | 121 | 1200 | Baraulia | 131 | 700 | 125 | 1800
Madanganj | 131 | 1800 | 123 | 1200 | Sikalbaha | 131 | 800 | 126 | 1830
Shitalakhya | 134 | 1700 | 123 | 1200 | Dohazari | 130 | 600 | 125 | 1830
Rahim steal | 133 | 1700 | 126 | 1200 | Cox'sbazar | 125 | 800 | 117 | 1830
Matuail | 133 | 1700 | 124 | 1200 | Chandraghona | 132 | 700 | 127 | 1830
Ghorasal | 140 | 100 | 135 | 1200 | Kaptai | 0 | 0 | 0 | 0
Narsinghdi | 130 | 600 | 121 | 1900 | A. Khaer Stl. | 130 | 2300 | 126 | 1100
Haripur (SBU) | 132 | 600 | 122 | 1100 | Bakulia | 132 | 2200 | 125 | 1800
Ullon | 133 | 600 | 126 | 1200 | Julda | 131 | 2400 | 127 | 1800
Hasnabad | 131 | 600 | 125 | 1200 | TK Chemical | 133 | 100 | 129 | 1700
Magbazar | 134 | 600 | 127 | 1300 | Modern Steel | 132 | 2200 | 126 | 1830
Maniknagar | 135 | 600 | 130 | 1200 | Shahmirpur | 130 | 600 | 127 | 1100
Bangabhaban | 131 | 500 | 122 | 1200 | Khagrachhari | 131 | 600 | 126 | 1830
Narinda | 133 | 600 | 126 | 1200 | Matarbari | 125 | 700 | 119 | 1830
Dhanmondi | 133 | 600 | 126 | 1200 | Baroiar Hat | 131 | 700 | 118 | 1830
Lalbag | 131 | 500 | 122 | 1200 | Rangamati | 131 | 700 | 126 | 1830
Madartek | 133 | 600 | 126 | 1200 | Goalpara | 137 | 1700 | 122 | 1300
Mirpur | 133 | 500 | 124 | 1200 | Central s/s | 137 | 1830 | 122 | 1300
Kalyanpur | 135 | 600 | 127 | 1200 | Noapara | 139 | 1800 | 119 | 1200
Gulshan | 132 | 600 | 126 | 1200 | Jessore | 133 | 1800 | 115 | 1300
Uttara | 131 | 600 | 123 | 1200 | Jhenida | 137 | 1700 | 115 | 200
Uttara New | 132 | 600 | 124 | 1200 | Bottail | 137 | 1700 | 124 | 700
Kamrangirchar | 132 | 500 | 122 | 1200 | G.K.Project | 141 | 1700 | 130 | 1300
Savar | 131 | 600 | 124 | 1200 | Faridpur | 135 | 1900 | 120 | 1300
Bhasantec | 137 | 600 | 129 | 1200 | Madaripur | 138 | 1930 | 125 | 1300
Agargaon | 137 | 600 | 130 | 1200 | Gopalganj | 145 | 1930 | 129 | 400
Satmosjid | 137 | 600 | 130 | 1200 | Bagerhat | 136 | 1900 | 122 | 1300
Tongi | 134 | 400 | 128 | 1300 | Mongla | 136 | 1930 | 119 | 1300
Kabirpur | 135 | 1700 | 128 | 1300 | Satkhira | 138 | 1830 | 122 | 1300
Basundhara | 128 | 100 | 122 | 1830 | Gallamari | 139 | 1800 | 123 | 1300
Manikganj | 138 | 1700 | 130 | 900 | Magura | 139 | 1800 | 115 | 100
Joydevpur | 138 | 1800 | 131 | 1200 | Chuadanga | 137 | 1800 | 110 | 100
New Tongi | 135 | 1700 | 127 | 1200 | Barisal | 141 | 900 | 132 | 400
Kodda | 137 | 1800 | 130 | 1000 | Patuakhali | 138 | 2000 | 129 | 700
Dhamrai | 136 | 1700 | 127 | 1300 | Bhandaria | 137 | 2000 | 125 | 1300
Valuka | 132 | 2300 | 124 | 700 | Ishurdi | 140 | 1600 | 131 | 700
Tangail | 138 | 1700 | 128 | 100 | Ruppur Paromanobik | 138 | 1500 | 131 | 1300
Mymensing | 137 | 1800 | 126 | 800 | Natore | 140 | 1600 | 125 | 800
Kishorganj | 136 | 1800 | 126 | 1900 | Bogra | 141 | 1600 | 128 | 700
Netrokona | 138 | 1800 | 125 | 1300 | Noagaon | 138 | 1600 | 122 | 800
Jamalpur | 136 | 1800 | 120 | 600 | Rajshahi | 134 | 1500 | 120 | 700
Sherpur | 134 | 1600 | 117 | 600 | C.Nawabganj | 135 | 1600 | 116 | 700
Srimongal | 136 | 400 | 134 | 2200 | Amnura | 135 | 1500 | 117 | 700
Shahjibazar | 135 | 100 | 130 | 2000 | Pabna | 136 | 1700 | 127 | 1100
Fenchuganj | 136 | 100 | 132 | 1900 | Shahjadpur | 144 | 1700 | 133 | 1200
Khulawara | 136 | 1100 | 131 | 1900 | Serajganj | 139 | 1600 | 128 | 700
Sylhet | 135 | 500 | 131 | 2100 | Niyamatpur | 141 | 1600 | 117 | 800
Chatak | 134 | 400 | 129 | 1900 | Joypurhat | 140 | 1600 | 120 | 800
Sunamganj | 134 | 600 | 128 | 1900 | Mohastangor | 137 | 1600 | 125 | 700
Biani Bazar | 134 | 300 | 128 | 1830 | Rangpur | 125 | 1600 | 116 | 700
Comilla(s) | 130 | 1900 | 122 | 1800 | Lalmonirhat | 122 | 1700 | 110 | 1300
Comilla(n) | 137 | 700 | 133 | 1930 | Saidpur | 123 | 1700 | 114 | 800
Chandpur | 130 | 1000 | 121 | 1500 | Purbasadipur | 128 | 2000 | 114 | 1000
Feni | 129 | 800 | 117 | 1830 | Thakurgaon | 119 | 500 | 103 | 1200
Chowmuhani | 127 | 2200 | 122 | 2400 | Palashbari | 130 | 1500 | 117 | 700
Ashuganj | 139 | 1900 | 135 | 2000 | Barapukuria | 128 | 1500 | 121 | 800
Daudkandi | 135 | 800 | 126 | 1200 | Panchagar | 117 | 500 | 101 | 1000
B.Baria | 134 | 1930 | 127 | 1900 | Joldhaka | 123 | 400 | 112 | 1200

## L-Curve
Date | 2019-04-13
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 88 | 5545 | 1952 | 7497 |  |  |  | QF-LDC-12
0:30 | 424 | 6151 | 2035 | 8186 | Date: | 2019-04-13
1:00 | 760 | 6757 | 2118 | 8875
1:30 | 800 | 6624.5 | 1965 | 8589.5
2:00 | 840 | 6492 | 1812 | 8304
2:30 | 850 | 6456.5 | 1805.5 | 8262 | [5 empty] | Gen. at Eve. Peak | 7833 | 7833 MW (21:00 )
3:00 | 860 | 6421 | 1799 | 8220 | [6 empty] | 21:00
3:30 | 830 | 6310 | 1793.5 | 8103.5 | [5 empty] | Gen. at Day Peak | 8532.18 | 8532.18 MW (12:00 )
4:00 | 800 | 6199 | 1788 | 7987 | [6 empty] | 12:00
4:30 | 760 | 6128 | 1811 | 7939 | [5 empty] | Highest Generation | 8875
5:00 | 720 | 6057 | 1834 | 7891 | [6 empty] | 1:00
5:30 | 670 | 5913 | 1812.5 | 7725.5
6:00 | 620 | 5769 | 1791 | 7560
6:30 | 630 | 5756.185 | 1801.5 | 7557.685
7:00 | 640 | 5743.37 | 1812 | 7555.37
7:30 | 590 | 5629.685 | 1880 | 7509.685
8:00 | 540 | 5516 | 1948 | 7464
8:30 | 295 | 5644.5 | 1984 | 7628.5
9:00 | 50 | 5773 | 2020 | 7793
9:30 | 40 | 5914.5 | 2018 | 7932.5
10:00 | 30 | 6056 | 2016 | 8072
10:30 | 30 | 6093.66 | 2043.5 | 8137.16
11:00 | 30 | 6131.32 | 2071 | 8202.32
11:30 | 155 | 6241.25 | 2126 | 8367.25
12:00 | 280 | 6351.18 | 2181 | 8532.18
12:30 | 325 | 6373.715 | 2212 | 8585.715
13:00 | 370 | 6396.25 | 2243 | 8639.25
13:30 | 320 | 6416.325 | 2251.5 | 8667.825
14:00 | 270 | 6436.4 | 2260 | 8696.4
14:30 | 195 | 6397.9 | 2218 | 8615.9
15:00 | 120 | 6359.4 | 2176 | 8535.4
15:30 | 240 | 5999.7 | 2087 | 8086.7
16:00 | 360 | 5640 | 1998 | 7638
16:30 | 320 | 5130.85 | 1966.5 | 7097.35
17:00 | 280 | 4621.7 | 1935 | 6556.7
17:30 | 370 | 4519.4 | 1925.5 | 6444.9
18:00 | 460 | 4417.1 | 1916 | 6333.1
18:30 | 455 | 4932.55 | 2078.5 | 7011.05
19:00 | 450 | 5448 | 2241 | 7689
19:30 | 520 | 5524 | 2276 | 7800
20:00 | 570 | 5443 | 2259 | 7702 |  |  |  | Executive Engineer
20:30 | 445 | 5498 | 2269.5 | 7767.5 |  |  |  | Network Operation Division
21:00 | 320 | 5553 | 2280 | 7833
21:30 | 268 | 5482 | 2272 | 7754
22:00 | 216 | 5411 | 2264 | 7675 |  |  |  |  | Page 6 of 7
22:30 | 184 | 5484 | 2130 | 7614
23:00 | 152 | 5557 | 1996 | 7553
23:30 | 120 | 5551 | 1974 | 7525
24:00 | 88 | 5545 | 1952 | 7497
7833 MW (21:00 )
8532.18 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-04-13 |  | Energy | 192043362
[10 empty] | 2019-04-13 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4049 | 840 | 1418 | 765 | 253 | 80 | 0 | 0 | 92
0:30 | 4444.5 | 745 | 1601.5 | 905.5 | 252 | 81 | 39.5 | 0 | 117 | Date: | 2019-04-13
1:00 | 4840 | 650 | 1785 | 1046 | 251 | 82 | 79 | 0 | 142
1:30 | 4739 | 649.5 | 1655 | 999.5 | 251 | 82 | 73.5 | 0 | 140 | [7 empty] | Total Energy | 192.0434 | Total Energy Gen 192.043 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 192.043 MKWHr
2:00 | 4638 | 649 | 1525 | 953 | 251 | 82 | 68 | 0 | 138 | [7 empty] | Energy not Served | 0
2:30 | 4625 | 649.5 | 1538.5 | 913 | 251 | 82 | 68 | 0 | 135 | [7 empty] | Energy Requirement | 192.0434
3:00 | 4612 | 650 | 1552 | 873 | 251 | 82 | 68 | 0 | 132
3:30 | 4590 | 643.5 | 1503.5 | 845.5 | 251 | 82 | 59 | 0 | 129 | [6 empty] | Shortage
4:00 | 4568 | 637 | 1455 | 818 | 251 | 82 | 50 | 0 | 126
4:30 | 4580 | 636.5 | 1454 | 762 | 251.5 | 82 | 50 | 0 | 123
5:00 | 4592 | 636 | 1453 | 706 | 252 | 82 | 50 | 0 | 120
5:30 | 4555 | 636 | 1403 | 644.5 | 252 | 82 | 37 | 0 | 116
6:00 | 4518 | 636 | 1353 | 583 | 252 | 82 | 24 | 0 | 112
6:30 | 4508.5 | 656.5 | 1328 | 596 | 252 | 82.5 | 24 | 0 | 108 |  |  |  |  | Coal
7:00 | 4499 | 677 | 1303 | 609 | 252 | 83 | 24 | 0 | 104
7:30 | 4402 | 755 | 1240.5 | 641.5 | 252.5 | 82.5 | 27 | 0 | 102 |  |  |  | Oil |  |  |  | ,
8:00 | 4305 | 833 | 1178 | 674 | 253 | 82 | 30 | 0 | 100
8:30 | 4346.5 | 836 | 1218 | 740 | 253 | 82 | 40 | 0 | 102
9:00 | 4388 | 839 | 1258 | 806 | 253 | 82 | 50 | 0 | 104
9:30 | 4416.5 | 839.5 | 1324.5 | 842.5 | 252 | 81.5 | 50 | 0 | 110
10:00 | 4445 | 840 | 1391 | 879 | 251 | 81 | 50 | 0 | 116
10:30 | 4401.5 | 840 | 1469 | 902 | 250 | 81 | 58 | 0 | 117
11:00 | 4358 | 840 | 1547 | 925 | 249 | 81 | 66 | 0 | 118
11:30 | 4468 | 840 | 1570.5 | 953.5 | 250 | 81.5 | 66 | 0 | 121
12:00 | 4578 | 840 | 1594 | 982 | 251 | 82 | 66 | 0 | 124
12:30 | 4589 | 840 | 1597 | 1013.5 | 251 | 83 | 66 | 0 | 128
13:00 | 4600 | 840 | 1600 | 1045 | 251 | 84 | 66 | 0 | 132
13:30 | 4600 | 840 | 1600 | 1045 | 251 | 84 | 66 | 0 | 132
14:00 | 4600 | 840 | 1600 | 1045 | 251 | 84 | 66 | 0 | 132
14:30 | 4609.5 | 842 | 1517 | 1074 | 251 | 84 | 53.5 | 0 | 139
15:00 | 4619 | 844 | 1434 | 1103 | 251 | 84 | 41 | 0 | 146
15:30 | 4285 | 844.5 | 1349.5 | 1088.5 | 252 | 84 | 28.5 | 0 | 144
16:00 | 3951 | 845 | 1265 | 1074 | 253 | 84 | 16 | 0 | 142
16:30 | 3768.5 | 844.5 | 1134.5 | 868.5 | 252.5 | 84 | 18.5 | 0 | 121
17:00 | 3586 | 844 | 1004 | 663 | 252 | 84 | 21 | 0 | 100
17:30 | 3450 | 844 | 1014.5 | 664.5 | 252.5 | 84 | 18 | 0 | 116
18:00 | 3314 | 844 | 1025 | 666 | 253 | 84 | 15 | 0 | 132
18:30 | 3659.5 | 892.5 | 1189 | 724 | 252.5 | 84 | 123.5 | 0 | 86
19:00 | 4005 | 941 | 1353 | 782 | 252 | 84 | 232 | 0 | 40
19:30 | 3971 | 941 | 1275 | 971 | 252 | 80 | 226 | 0 | 84
20:00 | 3855 | 940 | 1232 | 1016 | 253 | 80 | 220 | 0 | 106
20:30 | 3902 | 941 | 1232 | 1049.5 | 252.5 | 80 | 216.5 | 0 | 94
21:00 | 3949 | 942 | 1232 | 1083 | 252 | 80 | 213 | 0 | 82
21:30 | 3926 | 941.5 | 1231.5 | 1066.5 | 251.5 | 80 | 178 | 0 | 79
22:00 | 3903 | 941 | 1231 | 1050 | 251 | 80 | 143 | 0 | 76
22:30 | 3941 | 891 | 1275.5 | 1015 | 252 | 80 | 79.5 | 0 | 80
23:00 | 3979 | 841 | 1320 | 980 | 253 | 80 | 16 | 0 | 84
23:30 | 4014 | 840.5 | 1369 | 872.5 | 253 | 80 | 8 | 0 | 88 | Max Temp. in Dhaka |  | 33.0° C
24:00 | 4049 | 840 | 1418 | 765 | 253 | 80 | 0 | 0 | 92
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 192.043 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 192.043 MKWHr
Note on W13: Author:

## Generation
2019-04-13
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 82 | 82 | 82 | 82 | 82 | 82 | 83 | 82 | 82 | 81 | 81 | 82 | 84 | 84 | 84 | 84 | 84 | 84 |  | 84 | 80 | 80 | 80 | 80 | 80 | 80 | 1878082
2 | Kaptai Unit-4 & 5
3 | Chattogram ST-1 (Raozan) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 105 | 105 |  | 105 | 105 | 110 | 110 | 110 | 110 | 110 | 2600000
4 | Chittgong ST-2 (Raozan) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3000000
5 | Raozan 25 MW (RPCL) | 8 | 0 | [9 empty] | 4 | 8 | 8 | 8 | 8 | 8 | 8 |  | 9 | 25 | 25 | 25 | 25 | 25 | 0 | 179771
| Teknaf Solartech 20MW | [5 empty] | 0 | 3.97 | 9 | 12 | 18 | 16.32 | 13.98 | 19.15 | 17 | 13.1 | 7.9 | 2.7 | 0.1 |  | 0 | 0 | 0 |  |  |  |  | 134730
6 | Sikalbaha 225MW (Gas) | 203 | 211 | 203 | 204 | 204 | 204 | 203 | 205 | 202 | 229 | 212 | 204 | 206 | 222 | 204 | 204 | 184 | 204 |  | 203 | 203 | 203 | 203 | 197 | 215 | 202 | 4897302
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas) | 130 | 130 | 120 | 117 | 114 | 116 | 113 | 115 | 115 | 118 | 126 | 120 | 125 | 120 | 120 | 120 | 120 | 145 |  | 145 | 125 | 125 | 125 | 80 | 110 | 130 | 2939590
10 | Sikalbaha GT 150MW (Oil) | [15 empty] | 0
| Dohazari Peaking | [15 empty] | 0 | 13 | 15 |  | 83 | 83 | 83 | 83 | 52 | 0 | 0 | 348763
12 | Hathazari peaking | [19 empty] | 50 | 47 | 47 | 47 | 8 | 0 | 0 | 150672
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 71 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 50 | 0 | 0 | [14 empty] | 840000
17 | Siddhirganj CCPP-335 MW | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 218 | 218 | 218 | 235 | 219 | 220 | 0 | 0 |  |  | 150 | 110 | 110 | 110 | 110 | 110 | 110 | 4126619
18 | Summit Gazipur -2 | [14 empty] | 0 | 10 | 0 | 0 |  | 0 | [6 empty] | 20070
19 | Ashuganj 195MW Modular | 110 | 110 | 110 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 102 | 110 | 30 | 8 |  | 54 | 55 | 55 | 53 | 53 | 62 | 53 | 1639272
20 | Ghorasal ST: Unit-1,2 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 849000
21 | Ghorasal GT: Unit-3 | 158 | 159 | 158 | 94 | 65 | 43 | 43 | 43 | 43 | 78 | 94 | 94 | 94 | 94 | 134 | 95 | 43 | 44 |  | 43 | 44 | 43 | 43 | 44 | 43 | 43 | 2090500
22 | Ghorasal GT: Unit-4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 101 | 100 | 100 | 100 | 99 | 98 | 200 | 240 | 150 | 40 | 50 |  | 46 | 50 | 50 | 51 | 51 | 50 | 42 | 2270000
23 | Ghorasal ST: Unit-5 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2898000
24
25 | Ghorasal ST: Unit-7 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 300 | 340 | 340 | 300 | 380 | 250 | 200 | 180 |  | 300 | 250 | 250 | 250 | 250 | 250 | 250 | 6570218
26
28 | Ashuganj ST: Unit- 3
29 | Ashuganj ST: Unit- 4
30 | Ashuganj ST: Unit- 5
32 | Ashuganj Engines TSK | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 34 | 40 | 40 | 0 | 30 | 39 | 39 | 39 | 40 | 40 | 10 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 819216
33 | Ashuganj CCPP 225 MW | 184 | 199 | 186 | 198 | 184 | 184 | 186 | 184 | 184 | 204 | 141 | 219 | 187 | 201 | 185 | 187 | 191 | 160 |  | 193 | 194 | 183 | 191 | 202 | 198 | 183 | 4612000
34 | Ashuganj CCPP(South) | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 260 | 260 | 260 | 260 | 300 | 300 | 300 | 360 | 330 | 250 | 200 |  | 270 | 250 | 200 | 200 | 200 | 200 | 260 | 6564000
| Ashuganj CCPP(North) | 320 | 320 | 320 | 320 | 320 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 360 | 300 | 240 | 250 |  | 300 | 270 | 195 | 250 | 245 | 240 | 250 | 7239700
35 | Ashuganj (Precision) 55MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 129600
36 | Chandpur CCPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 51 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1192980
37 | Tongi GT | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 958186
38 | Haripur GT: Unit-1, 2 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 0 | [14 empty] | 213200
39 | Haripur 412 MW CCPP | 326 | 331 | 338 | 332 | 328 | 326 | 328 | 326 | 327 | 342 | 345 | 337 | 325 | 327 | 332 | 338 | 352 | 273 |  | 320 | 325 | 330 | 325 | 328 | 342 | 344 | 8086948
40 | Meghnaghat CCPP 450MW | 370 | 370 | 370 | 370 | 370 | 370 | 340 | 300 | 300 | 380 | 420 | 420 | 420 | 350 | 420 | 370 | 300 | 300 |  | 420 | 370 | 370 | 370 | 370 | 370 | 370 | 8650125
41 | Haripur Power CCPP 360MW | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 264 | 304 | 340 | 351 | 357 | 302 | 353 | 273 | 225 | 224 |  | 359 | 308 | 309 | 300 | 300 | 300 | 320 | 6917000
42 | Mymensingh RPCL 210MW | 209 | 208 | 208 | 209 | 208 | 209 | 206 | 192 | 191 | 187 | 189 | 185 | 172 | 155 | 157 | 160 | 162 | 163 |  | 165 | 166 | 164 | 164 | 163 | 180 | 181 | 4304480
43 | Haripur NEPC 110MW
44 | Fenchugonj CCPP-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 58 | 58 | 58 | 58 | 58 | 58 | 56 | 56 | 57 | 56 |  | 58 | 57 | 58 | 58 | 60 | 60 | 58 | 1388000
45 | Fenchugonj CCPP-2 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 51 | 51 |  | 51 | 52 | 52 | 52 | 52 | 52 | 52 | 1242520
46 | Shajibazar 330 MW | 280 | 276 | 276 | 277 | 276 | 276 | 277 | 276 | 280 | 280 | 277 | 274 | 275 | 295 | 277 | 278 | 257 | 256 |  | 286 | 283 | 283 | 280 | 287 | 288 | 280 | 6328000
47 | Shahjibazar GT: Unit- 8, 9 | 49 | 51 | 51 | 51 | 51 | 40 | 51 | 40 | 62 | 55 | 51 | 59 | 56 | 55 | 52 | 55 | 40 | 50 |  | 61 | 63 | 62 | 64 | 51 | 65 | 58 | 1279776
48 | Shahjibazar 86MW | 88 | 50 | 50 | 50 | 50 | 20 | 10 | 10 | 50 | 50 | 88 | 88 | 88 | 86 | 86 | 40 | 20 | 50 |  | 50 | 88 | 88 | 88 | 88 | 88 | 88 | 1535040
49 | Shahjibazar (EPL) 50MW | 48 | 48 | 48 | 48 | 48 | 47 | 47 | 47 | 47 | 46 | 42 | 42 | 45 | 45 | 45 | 45 | 45 | 47 |  | 47 | 47 | 47 | 47 | 48 | 48 | 48 | 1064160
50 | Sylhet GT 150 MW | 103 | 105 | 104 | 103 | 103 | 96 | 96 | 101 | 93 | 104 | 105 | 97 | 94 | 124 | 104 | 103 | 103 | 100 |  | 83 | 94 | 87 | 91 | 97 | 118 | 105 | 2441740
51 | Sylhet GT 20 MW | 19 | 0 | [24 empty] | 17000
52 | Sylhet (EPL) 50MW | 33 | 5 | 5 | 5 | 5 | 5 | 7 | 7 | 6 | 6 | 6 | 7 | 7 | 7 | 30 | 30 | 36 | 35 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 454880
53 | Sylhet (Desh) 10MW | 0 | [10 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 131580
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 2 | 11 | 0 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 225024
55 | Fenchugonj (Barakatullah) 51MW | 50 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 41 | 47 | 47 | 47 |  | 47 | 47 | 49 | 50 | 50 | 50 | 50 | 577800
56 | Shahjahanulla 25 MW | 25 | 25 | 20 | 16 | 16 | 16 | 16 | 25 | 25 | 25 | 25 | 25 | 24 | 24 | 24 | 24 | 24 | 24 |  | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 540192
57 | Summit Bibiana- 2 | 250 | 260 | 290 | 280 | 280 | 250 | 280 | 250 | 275 | 270 | 285 | 280 | 275 | 270 | 0 | 0 |  |  |  |  | 5 | 15 | 30 | 45 | 95 | 150 | 4345286
58 | Southern 55MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 0 |  | 0 | [6 empty] | 296220
59 | Sikalbaha (Energis) | 41 | 41 | 38 | 41 | 41 | 41 | 41 | 41 | 41 | 34 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 32 | 32 | 32 | 32 | 927360
60 | Barabkunda (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 422592
61 | Narshingdi (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 0 | 0 | 13 | 13 | 16 | 16 | 19 | 0 |  | 0 | 19 | 19 | 19 | 0 | 19 | 19 | 345204
62 | Tangail (Doreen) 22MW | 20 | 0 | [6 empty] | 0 |  |  |  | 20 | 20 | 20 | 20 | 0 | 0 |  | 0 | 0 | 0 | 0 | 20 | 20 | 20 | 160380
63 | Tripura | 142 | 138 | 132 | 126 | 120 | 112 | 104 | 100 | 104 | 116 | 118 | 124 | 132 | 144 | 146 | 142 | 100 | 132 |  | 40 | 84 | 106 | 82 | 76 | 84 | 92 | 2742720
64 | Malancha, Ctg. EPZ (United) | 33 | 25 | 25 | 34 | 34 | 35 | 30 | 4 | 15 | 4 | 3 | 4 | 4 | 6 | 2 | 4 | 10 | 12 |  | 18 | 29 | 31 | 33 | 3 | 33 | 39 | 461280
65 | Feni (Doreen) 22MW | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 |  |  | 15 | 18 | 18 | 18 | 18 | 18 | 19 | 0 |  | 15 | 0 | 0 |  |  |  | 19 | 270144
66 | Feni, Mohipal (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 |  | 0 |  |  | 8 | 0 |  |  | 152820
67 | Jangalia (Summit) 33MW | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 8 | 8 | 8 | 8 | 8 |  | 0 | 25 | 25 | 33 | 33 | 33 | 33 | 422900
68 | Summit Cumilla 25MW | 21 | 21 | 21 | 21 | 21 | 21 | 15 | 15 | 15 | 0 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 0 |  | 0 | 10 | 10 | 10 | 0 | 7 | 15 | 332770
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 22 | 22 | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 8 |  | 8 | 24 | 24 | 32 | 32 | 32 | 32 | 653580
71 | Summit Maona | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 0 |  |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 570900
72 | Summit Rupganj | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 25 | 25 | 25 | 17 | 17 | 17 | 17 | 0 |  | 13 | 21 | 21 | 17 | 25 | 25 | 25 | 496800
73 | Ghorashal (Regent) | 110 | 111 | 111 | 62 | 62 | 62 | 63 | 22 | 22 | 22 | 22 | 52 | 52 | 52 | 52 | 12 | 0 | 0 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 997366
76 | Siddhirganj (Desh)
77 | Siddhirganj (Dutch Bangla)
78 | Gazipur (RPCL) | [8 empty] | 8 | 26 | 28 | 51 | 51 | 51 | 42 | 33 | 25 | 25 |  | 25 | 35 | 44 | 51 | 43 | 43 | 25 | 614556
79 | Kodda 149MW | [9 empty] | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 0 |  | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 167040
80 | Jamalpur 95MW | 32 | 8 | 0 | [5 empty] | 2 | 7 | 7 | 7 | 7 | 7 | 12 | 21 | 0 | 0 |  |  | 10 | 15 | 30 | 30 | 30 | 0 | 285120
81 | Lakdhanvi 52 MW
82 | Madanganj 102MW
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj (Powerpac) 100MW
86 | Meghnaghat CCPP(Summit) | 240 | 270 | 250 | 260 | 260 | 250 | 270 | 265 | 245 | 280 | 275 | 275 | 240 | 320 | 215 | 250 | 210 | 300 |  | 260 | 270 | 250 | 260 | 270 | 280 | 230 | 6429295
87 | Meghnaghat (IEL)
88 | Ghorashal 78MW (MAX) | 40 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 0 |  | 0 | 0 | 0 |  |  |  |  | 380008
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 275640
92 | Fenchuganj (EPL) 44MW | 50 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 22 | 46 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 46 | 579000
93 | Ashuganj (Midland) 51MW | 45 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 30 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 309524
94 | Gagnagar (Orion) | [9 empty] | 0 | 7 | 7 | 7 | 7 | 7 | 7 | 0 | 0 | [8 empty] | 57600
95 | Patenga 50MW | 47 | 47 | 47 | 25 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 26 | 44 | 45 | 45 | 44 | 16 |  | 13 | 42 | 40 | 40 | 41 | 35 | 46 | 775200
96 | Chattogram ECPV 108 MW | 32 | 19 | 0 | [7 empty] | 0 | 7 | 33 | 45 | 45 | 45 | 12 | 12 |  | 27 | 60 | 81 | 52 | 52 | 52 | 49 | 624000
97 | Katpotti 51 MW | [6 empty] | 6 | 6 | 6 | 6 | 6 | 6 | 10 | 12 | 12 | 12 | 12 | 0 |  | 0 | 18 | 18 | 24 | 24 | 27 | 27 | 278880
98 | Bosila 108MW | [12 empty] | 0 | 25 | 29 | 32 | 8 | 8 |  | 19 | 40 | 40 | 40 | 40 | 40 | 0 | 290880
99 | Madanganj-55 MW
100 | Northern 55 MW | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 0 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 395061
101 | Kushiara 163 MW CCPP GT | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 163 | 163 | 163 | 100 | 163 | 163 | 163 | 163 |  | 163 | 130 | 100 | 100 | 100 | 100 | 130 | 3200220
102 | Sarishabari (Solar) | [6 empty] | 0.4 | 0 | 1 | 1 | 2 | 1.2 | 2.1 | 1.4 | 0.3 | 0.1 | 0 | 0 |  | 0 | 0 | 0 |  |  |  |  | 13150
103 | Banco Energy 54MW | 35 | 35 | 35 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 17 | 17 | 568800
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW | [14 empty] | 4 | 34 | 31 | 17 |  | 17 | 17 | 17 | 17 | 15 | 0 |  | 164160
115 | Juldah 100 MW Unit-3 | 100 | 100 | 100 | 100 | 100 | 60 | 60 | 60 | 60 | 60 | 60 | 84 | 100 | 100 | 100 | 100 | 50 | 45 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2058240
116 | Chandpur Desh 200MW | 105 | 105 | 88 | 88 | 60 | 0 | [13 empty] | 0 | 34 | 34 | 34 | 30 | 0 |  | 612480
117 | Midland 150MW
118 | Bibiyana-3 285 MW | 250 | 250 | 250 | 250 | 250 | 249 | 200 | 180 | 290 | 290 | 290 | 240 | 240 | 240 | 0 | 0 | [10 empty] | 3542800
| United Jamalpur PPL | 106 | 106 | 109 | 80 | 40 | 9 | 9 | 16 | 69 | 110 | 110 | 110 | 109 | 110 | 108 | 80 | 20 | 18 |  | 18 | 30 | 65 | 110 | 110 | 110 | 110 | 1953600
120 | Eastern Zone Total | 6757 | 6492 | 6421 | 6199 | 6057 | 5769 | 5743.37 | 5516 | 5773 | 6056 | 6131.32 | 6351.18 | 6396.25 | 6436.4 | 6359.4 | 5640 | 4621.7 | 4417.1 |  | 5448 | 5524 | 5443 | 5553 | 5411 | 5557 | 5545 | 142239312
121
122 | o
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | 16 | 0 | [9 empty] | 0 | 16 | 16 | 16 | 16 | 16 | 0 |  | 16 | 16 | 16 | 16 | 16 | 0 |  | 187200
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | 11 | 0 | [17 empty] | 40 | 24 | 24 | 17 | 17 | 0 |  | 122880
Khulna CCPP 225MW
129 | Labon Chora 105 MW | 90 | 53 | 53 | 53 | 17 | 17 | 17 | 36 | 35 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 53 | 53 | 53 | 11 | 949440
130
131
132
133
| Summit Barisal 110 MW | 32 | 16 | 0 |  |  |  |  | 33 | 116 | 116 | 116 | 115 | 115 | 115 | 115 | 110 | 16 | 16 |  | 20 | 0 | [5 empty] | 1055904
136 | Barisal GT: Unit-1, 2
137 | Bhola Aggreko 95MW | 96 | 95 | 96 | 96 | 95 | 51 | 11 | 12 | 11 | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 |  | 12 | 11 | 11 | 0 | 13 | 12 | 12 | 771328
| Bhola CCPP 194MW | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 90 | 75 | 75 | 75 | 100 | 100 | 100 | 120 | 120 | 120 | 120 |  | 120 | 100 | 100 | 100 | 120 | 120 | 120 | 2615000
140 | Bhola (Venture) 33MW | 23 | 26 | 27 | 27 | 26 | 30 | 20 | 19 | 21 | 20 | 20 | 20 | 21 | 21 | 23 | 26 | 24 | 25 |  | 32 | 34 | 6 | 10 | 10 | 11 | 11 | 511334
141 | Bangla Trak Noapara
142 | Noapara (KZA) 40MW | 8 | 0 | [9 empty] | 0 | 8 | 8 | 8 | 8 | 0 |  |  | 8 | 8 | 8 | 8 | 8 | 0 |  | 100125
143 | Gopalganj Peaking | 0 | [15 empty] | 8 | 0 |  | 2 | 0 | [5 empty] | 17152
144 | Bheramara GT-1,2,3
145 | Madhumati Power Plant | 109 | 108 | 108 | 109 | 108 | 108 | 108 | 108 | 109 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 |  | 109 | 108 | 105 | 109 | 108 | 108 | 90 | 2648138
146 | Bheramara HVDC | 650 | 649 | 650 | 637 | 636 | 636 | 677 | 833 | 839 | 840 | 840 | 840 | 840 | 839 | 844 | 845 | 844 | 844 |  | 941 | 941 | 940 | 942 | 941 | 841 | 840 | 19126546
147 | Bheramara 360 MW
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2 | 67 | 67 | 67 | 67 | 68 | 68 | 68 | 69 | 69 | 67 | 65 | 67 | 67 | 67 | 67 | 69 | 68 | 68 |  | 68 | 68 | 69 | 68 | 67 | 69 | 69 | 1595782
152 | Barapukuria Unit-3 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 185 |  | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 4497400
153 | Baghabari GT 71MW | 50 | 50 | 50 | 50 | 50 | 50 | 60 | 60 | 60 | 60 | 60 | 60 | 55 | 55 | 55 | 55 | 55 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1370000
156 | Baghabari GT 100MW
Baghabari Peaking 50MW
157 | Sirajgonj Unit-1 225MW (Gas) | 180 | 187 | 194 | 190 | 184 | 182 | 184 | 165 | 157 | 165 | 185 | 202 | 193 | 188 | 192 | 162 | 152 | 135 |  | 170 | 184 | 188 | 184 | 188 | 196 | 179 | 4590245
158 | Sirajgonj Unit-1 225MW (Oil)
| Sirajgonj Unit-2 225MW (Gas) | 184 | 161 | 159 | 155 | 149 | 147 | 149 | 145 | 148 | 156 | 159 | 189 | 197 | 190 | 203 | 155 | 135 | 131 |  | 166 | 186 | 190 | 186 | 181 | 159 | 177 | 4175245
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas) | 183 | 0 | 0 | 27 | 124 | 151 | 152 | 104 | 80 | 80 | 80 | 118 | 142 | 142 | 50 | 59 | 124 | 133 |  | 153 | 175 | 187 | 204 | 196 | 151 | 172 | 3112209
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas)
161 | Bera Peaking
162 | Bogra (GBB) | 22 | 10 | 10 | 10 | 10 | 10 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 440400
163 | Bogra (EPL) | 17 | 10 | 5 | 5 | 5 | 5 | 5 | 17 | 17 | 17 | 17 | 16 | 17 | 16 | 17 | 0 | 0 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 216936
164 | Ullapara (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 0 | 0 |  |  |  | 5 | 5 | 8 | 0 | 5 | 0 | 176688
165 | Amnura 50MW | [12 empty] | 12 | 12 | 12 | 0 | 0 | 0 |  | 12 | 12 | 12 | 12 | 0 |  |  | 16990
166 | Katakhali (Northern)
167 | Katakhali Peaking
168 | Santahar Peaking
169 | Rajlanka 52 MW | [7 empty] | 10 | 16 | 16 | 16 | 16 | 17 | 17 | 8 | 0 | 0 | 0 |  | 8 | 25 | 25 | 25 | 25 | 0 |  | 223680
170 | Chapainawabganj-100 MW | 68 | 68 | 68 | 50 | 50 | 24 | 24 | 30 | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 0 | 0 | 0 |  | 24 | 39 | 50 | 50 | 50 | 0 |  | 872548
171 | Paramount Baghabari
172 | Confidence CPBL-2 | [9 empty] | 0 | 35 | 35 | 40 | 53 | 53 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 0 |  |  | 386880
173 | Rangpur GT
175 | Saidpur GT | [17 empty] | 0 |  | 17 | 17 | 0 | 0 |  |  |  | 24000
176
177
178
178 | Western Zone Total | 2118 | 1812 | 1799 | 1788 | 1834 | 1791 | 1812 | 1948 | 2020 | 2016 | 2071 | 2181 | 2243 | 2243 | 2260 | 1998 | 1935 | 1916 |  | 2241 | 2276 | 2259 | 2280 | 2264 | 1996 | 1952 | 49804050