## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-10-26 | Thursday
|  | Date (day): | 2023-10-26 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12206.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14510 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-10-25 | 2023-10-26 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 145 | 170 | 140 | 170 |  |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  |  | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 410 | 391 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 331 | 301 | 330 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | GT-1 under S/D due to Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 1 | 25 | 17 | 17 |  | 83 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 149 | 148 | 150 | 150 | 185 |  | GT-1 under S/D due to Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 75 | 85 | 85 |  | 17 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 28 | 20 | 40 | 35 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 15 | 17 | 18 | 18 |  | 4 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 33 | 8 | 24 | 76 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 327 | 154 | 215 | 215 |  | 120 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 16 | 50 | 50 | 52 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 0 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 98 | 16 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 0 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 0 | 55
| Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
25 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 31 | 31 | 32 | 32 |  | 48 | Engine problem
26 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 25 | 25 |  | 8 | Engine problem
27 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 28 | 30 | 30
28 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 20 | 8 | 25 | 27 |  | Fuel shortage
29 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
30 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 45 | 45 | 80 | 130 | 170 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
31 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 88 | 17 | 100 | 49 |  | Fuel shortage
32 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 70 | 35 | 105
33 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 16 | 0 | 17 | 87 |  | Fuel shortage
34 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 72 | 17 | 72 | 90 |  | Fuel shortage
35 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 33 | 0 | 35 | 0
36 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 300 | 160 | 232 | 232
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 5763 | 5422 | 2141 | 2401 | 2255 | 2836 | 1579 | 1040
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
38 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 17 | 8 | 17 | 8 |  | Fuel shortage
39 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 18 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 6 | 18 | 32 |  | Fuel shortage
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 208 | 207 | 208 | 208 |  | 22 | Engine problem
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 221 | 220 | 225
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 10 | 17 | 17 | 17 | 88 |  | Fuel shortage
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 73 | 40 | 73 | 25 |  | Fuel shortage
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 17 | 32 |  | 70 | Engine problem
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 12 | 12 | 12 | 12 | 10 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 2 | 5 | 25
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 85 | 232 | 100 | 280 | 20 |  | Fuel shortage
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 17 | 17 | 17 | 37 |  | Fuel shortage
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 12 | 17 | 17 | 17 | 93 |  | Fuel shortage
55 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
56 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 34 | 17 | 34 | 82 |  | Fuel shortage
57 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 17 | 35 | 163
58 | SS Power I |  | Coal | SS Power | 1*612 | 612 | 612 | 311 | 311 | 311 | 311 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 0 | 0 | 12 | 12 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 344 | 550 | 600 | 450 |  |  | On test.
| Chattogram area Total |  |  |  |  | 3217 | 3157 | 1256 | 1782 | 1703 | 1947 | 947 | 422
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 184 | 177 | 190 | 200 | 21 |  | Gas shortage
60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 285 | 280 | 275 | 320 |  |  | FGMO
61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 240 | 240 | 250 | 300 |  |  | FGMO
62 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 240 | 230 | 300 | 350 | 50 |  | Gas shortage
63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 5 | 20 | 20 | 25 |  | Gas shortage
| Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortae
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 12 | 6 | 150
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 30
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 17 | 17 | 17 | 183 |  | Fuel shortage
70 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 15 | 18 | 18 |  | 4 | Engine problem
71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 6 | 10 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 134 | 148 | 143 | 166
72 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 25 | 33 | 33
73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 16 | 52 | 52
74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 70 | 17 | 70
76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 13 | 76 | 28 | 78 | 35 |  | Fuel shortage
77 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 35 |  | 19 | Engine problem
78 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 76 | 36 | 94 | 21 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2896 | 1236 | 1477 | 1475 | 2006 | 530 | 199
79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 27 | 23 | 30 | 45 | 157 |  | Gas shortage
80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 15 | 16 | 19 |  | 3 | Engine problem
| Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 37 | 112 | 66 | 114 | 86 |  | Fuel shortage
83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 57 | 85 | 40 | 100 | 15 |  | Fuel shortage
84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 53 | 0 | 50 | 0
85 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 12 | 6 | 12 | 10 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 200 | 247 | 209.6 | 290 | 157 | 3
86 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
87 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Under maint.
88 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 130 | 163 | 163
89 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
90 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0
91 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 40 | 43 | 48 | 48
92 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 2 | 8 | 8
93 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 57 | 50 | 62
94 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 0 | 0 | 0 | 86 |  | Gas shortage
95 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 140 | 135 | 130 | 130 |  | 101 | Machine problem
97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 16 | 18 | 17 | 17
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 15 | 15 | 16 | 16 | 9 |  | Gas shortage
99 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 250 | 300 | 300 |  |  | FGMO
100 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 398 | 401 | 400 | 400
101 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
102 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 300 | 290 | 328 | 328
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1491 | 1394 | 1513 | 1525 | 95 | 648
103 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 903 | 902 | 907 | 851
104 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 16 | 49 | 65 | 50 |  | Fuel shortage
105 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 32 | 0 | 40 |  | 14 | Engine problem
106 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
107 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 | 49 |  | Fuel shortage
108 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
109 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 0 | 16 | 24 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
110 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 53 | 74 | 31 |  | Fuel shortage
111 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 15 | 32 | 73 |  | Fuel shortage
112 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 56 | 0 | 100 | 0
113 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0
114 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 701 | 715 | 700 | 700
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 1660 | 1705 | 1824 | 1838 | 883 | 14
115 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 16 | 110
116 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 19 | 23 | 21 | 28 |  | 12 | Engine problem
117 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 130 | 124 | 130 | 130 |  | 64 | ST under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 520 | 900 | 520 | 900
119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 38 | 150
121 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 150 | 150 | 150 | 150 | 157 |  | Coal shortage
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1039 | 1450 | 1095 | 1688 | 157 | 76
122 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
123 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 30 | 22 |  | Fuel shortage
124 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 16 |  | 55 | Engine problem
125 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 28 | 28
126 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 8 | 34 | 42 |  | 8 | Engine problem
127 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 30 | 40 |  | 10 | Engine problem
128 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 152 | 150 | 150 | 170 | 40 |  | Gas shortage
129 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
130 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
131 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 212 | 180 | 250 | 250 | 154 |  | Gas shortage
132 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 24 | 38 | 12 |  | Fuel shortage
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
133 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
134 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 8 | 44 |  | Fuel shortage
135 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 40 | 50 | 94 |  | 10 | Engine problem
136 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
137 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 35 | 50 | 63 |  | Fuel shortage
138 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 35 | 55 | 58 |  | Fuel shortage
139 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 951 | 1136 | 950 | 1150 | 346
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 1331 | 1675 | 1611 | 1982 | 1550 | 83
140 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
141 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
142 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
143 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
144 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 54 | 113 | 113
145 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
146 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 35 | 70 | 115
147 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 37 | 0 | 30 | 0
148 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 200 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 414 | 259 | 521 | 398 | 125 | 189
| Total |  |  |  |  | 25339 | 24599 | 10768 | 12390 | 12206.6 | 14510 | 6023 | 2674
A. |  | 2023-10-25 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 12390 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 8504 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12425 | MW
3 | Day peak Generation : |  |  | 10768 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11947.03 | MW
4 | Evening peak Generation : |  |  | 12390 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 33 | MW
5 | Total Energy Generation : |  | 254.0576 | MKWHr | By Solar | 2.9164 | MKWHr
| By Gas : | 124.2287 | MKWHr |  | By Oil: | 18.4202 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 81.4728 | MKWHr |  | By Hydro: | 4.759 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.00048 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6023 | MW | Dhaka | 4710.53 | 4692.53 |  | 18 |  | 18:00 |  | 100
|  |  | For Plants S/D or M/C prob = |  |  | 2674 | MW | Chittagong | 1076.3 | 1076.3 |  | 0 |  | 19:00 |  | 33
|  |  | Total = |  |  | 8697 | MW | Khulna | 1419.4 | 1419.4 |  | 0 |  | 19:30 |  | 30
7 | Total Gas Supplied : |  |  | 952.3 | MMCFD |  |  | Rajshahi | 1169.8 | 1169.8 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 122298740.634 | ii) Oil : | Taka | 240417918.15 | Comilla | 1117 | 1117 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 577074745.28 | Total | Taka | 939791404.064 | Mymensingh | 1002 | 987 |  | 15 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 447 | 447 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 852 | MW (W to E) at | 19:00 | hrs | Barisal | 338 | 338 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 600 | MW at | 18:00 | hrs | Rangpur | 667 | 667 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33°C |  |  | Total | 11947.03 | 11914.03 |  | 33
B. |  | 2023-10-26 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 33°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 13500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14510 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 12000 | MW
4 | Reserve(Generation end) |  |  |  | 1010 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 276.8182 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9206 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.28 | MKWHr. | ii) HVDC Flow at Peak Time |  | 902 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.9798 | MKWHr. | iii) Maximum HVDC Flow : |  | 904 | MW at | 16:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 104.04 |  | (b) Today: | 103.77 |  | (c) Rule Curve: |  | 108.4
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-10-25 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 373 | 276 |  | 0 | 170 | 142 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 13 | 17 | 26 | 0 | 0 | 131 | 75 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 10 | 14 | 0 | 0 | 0 | 270 | 275 | 180 | 0 | 0 | 5 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 11 | 25 | 12 | 110 | 73 | 0 | 19 | 0 | 43 | 0 | 0 | 47 | 120 | 0 | 40 | 50 | 0 | 0 | 18 | 0 | 10 | 290 | 15 | 8 | 0 | 0 | 0 | 0 | 18 | 0 | 17 | 0 | 0 | 17 | 0 | 342 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 20 | 240 | 0 | 0 | 374 | 0 | 142 | 390 | 0 |  | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 771 | 0 | 150 | 1016 | 0 | 0 |  | 5534 | 4214 | 9748 | 3258 | 901 | 1977 | 0 | 153 | 3143 | 206 | 0 | 0 | 110 | 0 | 0 | 0 | 104.09
2:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 356 | 285 |  | 0 | 225 | 150 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 13 | 17 | 26 | 0 | 0 | 131 | 75 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 25 | 0 | 0 | 0 | 310 | 290 | 174 | 0 | 0 | 5 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 11 | 25 | 12 | 106 | 73 | 0 | 19 | 0 | 43 | 0 | 0 | 10 | 120 | 0 | 40 | 50 | 0 | 20 | 18 | 0 | 10 | 285 | 15 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 240 | 0 | 0 | 368 | 0 | 144 | 140 | 0 |  | 766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 768 | 0 | 150 | 913 | 0 | 0 |  | 5217 | 3990 | 9207 | 3261 | 766 | 1785 | 0 | 50 | 3033 | 206 | 0 | 0 | 106 | 0 | 0 | 0 | 104.08
3:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 407 | 335 |  | 0 | 225 | 143 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 13 | 17 | 26 | 0 | 0 | 131 | 75 | 0 | 0 | 0 | 201 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 25 | 0 | 0 | 0 | 270 | 275 | 173 | 0 | 0 | 5 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 11 | 25 | 12 | 104 | 73 | 0 | 19 | 0 | 43 | 0 | 0 | 10 | 120 | 0 | 40 | 50 | 0 | 22 | 18 | 0 | 10 | 300 | 15 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 240 | 0 | 0 | 369 | 0 | 142 | 103 | 0 |  | 618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 803 | 0 | 150 | 900 | 0 | 0 |  | 5236 | 3889 | 9125 | 3278 | 618 | 1831 | 0 | 34 | 3054 | 206 | 0 | 0 | 104 | 0 | 0 | 0 | 104.07
4:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 350 | 276 |  | 0 | 170 | 143 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 13 | 17 | 26 | 0 | 0 | 131 | 75 | 0 | 0 | 0 | 191 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 0 | 0 | 0 | 270 | 240 | 176 | 0 | 0 | 5 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 11 | 25 | 12 | 102 | 73 | 0 | 19 | 0 | 43 | 0 | 0 | 10 | 120 | 0 | 40 | 20 | 0 | 22 | 18 | 0 | 10 | 280 | 15 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 240 | 0 | 0 | 369 | 0 | 142 | 300 | 0 |  | 618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 806 | 0 | 150 | 814 | 0 | 0 |  | 5142 | 3725 | 8867 | 3148 | 618 | 1788 | 0 | 34 | 2971 | 206 | 0 | 0 | 102 | 0 | 0 | 0 | 104.06
5:00 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 307 | 245 |  | 0 | 170 | 120 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 13 | 17 | 26 | 0 | 0 | 132 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 0 | 0 | 0 | 270 | 220 | 152 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 12 | 100 | 46 | 0 | 19 | 0 | 43 | 0 | 0 | 0 | 120 | 0 | 18 | 0 | 0 | 57 | 18 | 0 | 0 | 210 | 15 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 240 | 0 | 0 | 370 | 0 | 142 | 380 | 0 |  | 617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 794 | 0 | 150 | 808 | 0 | 0 |  | 4808 | 3755 | 8563 | 2990 | 617 | 1753 | 0 | 17 | 2954 | 132 | 0 | 0 | 100 | 0 | 0 | 0 | 104.05
6:00 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 307 | 245 |  | 0 | 170 | 120 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 13 | 17 | 30 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 0 | 0 | 0 | 270 | 220 | 151 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 12 | 94 | 46 | 0 | 19 | 0 | 43 | 0 | 0 | 0 | 120 | 0 | 18 | 0 | 0 | 30 | 18 | 0 | 0 | 170 | 15 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 240 | 0 | 0 | 371 | 0 | 144 | 405 | 0 |  | 618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 795 | 0 | 150 | 806 | 0 | 0 |  | 4770 | 3734 | 8504 | 2969 | 618 | 1717 | 0 | 17 | 2956 | 133 | 0 | 0 | 94 | 0 | 0 | 0 | 104.04
7:00 | 0 | 0 | 108 | 0 | 0 | 0 | 0 | 297 | 265 |  | 0 | 170 | 143 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 13 | 17 | 30 | 2 | 0 | 133 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 24 | 0 | 0 | 0 | 290 | 220 | 151 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 12 | 90 | 30 | 0 | 19 | 0 | 43 | 0 | 0 | 0 | 120 | 0 | 61 | 0 | 0 | 30 | 17 | 0 | 0 | 220 | 15 | 8 | 0 | 0 | 0 | 0 | 5 | 0 | 3 | 0 | 0 | 0 | 0 | 352 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 3 | 0 | 0 | 0 | 17 | 2 | 0 | 0 | 240 | 0 | 0 | 370 | 0 | 146 | 405 | 0 |  | 617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 170 | 0 | 0 | 1 | 6 | 0 | 0 | 0 | 794 | 5 | 150 | 811 | 32 | 0 |  | 4963 | 3782 | 8745 | 3012 | 617 | 1802 | 0 | 65 | 2961 | 133 | 0 | 16 | 90 | 49 | 0 | 0 | 104.03
8:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 306 | 265 |  | 0 | 170 | 145 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 13 | 0 | 30 | 8 | 0 | 133 | 75 | 0 | 0 | 0 | 195 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 0 | 0 | 0 | 295 | 220 | 181 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 12 | 102 | 31 | 0 | 19 | 1 | 43 | 0 | 0 | 0 | 120 | 0 | 61 | 0 | 0 | 130 | 17 | 0 | 0 | 280 | 15 | 8 | 0 | 0 | 0 | 0 | 19 | 0 | 17 | 0 | 0 | 0 | 0 | 352 | 57 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 33 | 0 | 0 | 0 | 17 | 12 | 0 | 0 | 240 | 0 | 0 | 370 | 0 | 142 | 400 | 0 |  | 618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 520 | 170 | 0 | 0 | 2 | 41 | 0 | 0 | 0 | 786 | 7 | 150 | 815 | 88 | 0 |  | 5319 | 3834 | 9153 | 3161 | 618 | 1790 | 0 | 118 | 2953 | 208 | 0 | 16 | 102 | 187 | 0 | 0 | 104.02
9:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 336 | 286 |  | 0 | 170 | 150 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 13 | 25 | 30 | 8 | 0 | 133 | 75 | 0 | 0 | 0 | 198 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 0 | 0 | 0 | 280 | 355 | 178 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 7 | 0 | 12 | 102 | 30 | 0 | 19 | 2 | 43 | 0 | 0 | 0 | 120 | 0 | 61 | 0 | 0 | 145 | 17 | 0 | 10 | 285 | 15 | 8 | 0 | 2 | 0 | 0 | 19 | 0 | 17 | 12 | 0 | 0 | 0 | 402 | 57 | 17 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 40 | 0 | 0 | 0 | 17 | 18 | 0 | 0 | 240 | 0 | 0 | 370 | 0 | 138 | 397 | 0 |  | 618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 170 | 0 | 0 | 4 | 45 | 0 | 0 | 0 | 791 | 26 | 150 | 813 | 141 | 0 |  | 5708 | 4001 | 9709 | 3475 | 618 | 1912 | 0 | 137 | 2952 | 208 | 0 | 16 | 102 | 289 | 0 | 0 | 104.01
10:00 | 0 | 0 | 131 | 0 | 0 | 0 | 0 | 338 | 287 |  | 0 | 170 | 149 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 19 | 13 | 25 | 16 | 8 | 0 | 133 | 75 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 325 | 240 | 208 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 18 | 7 | 0 | 12 | 116 | 29 | 0 | 19 | 2 | 43 | 0 | 0 | 0 | 163 | 0 | 58 | 0 | 0 | 145 | 17 | 0 | 10 | 310 | 8 | 8 | 0 | 45 | 0 | 0 | 28 | 0 | 17 | 8 | 0 | 0 | 0 | 401 | 47 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 42 | 0 | 0 | 0 | 17 | 33 | 0 | 0 | 240 | 0 | 0 | 335 | 0 | 197 | 400 | 0 |  | 807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 520 | 170 | 0 | 0 | 5 | 81 | 0 | 0 | 0 | 751 | 33 | 150 | 815 | 178 | 0 |  | 5832 | 4191 | 10023 | 3413 | 807 | 1938 | 0 | 197 | 2938 | 208 | 0 | 16 | 116 | 390 | 0 | 0 | 104
11:00 | 0 | 0 | 128 | 0 | 0 | 0 | 0 | 386 | 337 |  | 0 | 225 | 150 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 19 | 12 | 25 | 30 | 8 | 0 | 133 | 75 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 280 | 240 | 180 | 0 | 0 | 5 | 0 | 0 | 19 | 0 | 0 | 0 | 18 | 7 | 0 | 12 | 128 | 28 | 0 | 19 | 2 | 43 | 0 | 0 | 10 | 163 | 0 | 59 | 0 | 0 | 140 | 17 | 0 | 8 | 310 | 15 | 8 | 0 | 45 | 0 | 0 | 38 | 0 | 17 | 0 | 12 | 0 | 0 | 403 | 57 | 35 | 0 | 1 | 15 | 0 | 0 | 20 | 7 | 0 | 300 | 0 | 42 | 0 | 0 | 0 | 17 | 33 | 0 | 0 | 240 | 0 | 0 | 311 | 0 | 351 | 300 | 0 |  | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 520 | 220 | 0 | 0 | 5 | 87 | 0 | 0 | 0 | 755 | 36 | 150 | 913 | 198 | 0 |  | 6079 | 4520 | 10599 | 3475 | 903 | 2013 | 0 | 276 | 3170 | 208 | 0 | 16 | 128 | 410 | 0 | 0 | 103.99
12:00 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 410 | 331 |  | 0 | 225 | 149 | 1 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 19 | 12 | 25 | 28 | 8 | 0 | 133 | 75 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 285 | 240 | 184 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 0 | 15 | 6 | 0 | 12 | 134 | 27 | 0 | 19 | 1 | 43 | 0 | 0 | 40 | 163 | 0 | 58 | 0 | 0 | 140 | 16 | 0 | 10 | 300 | 15 | 8 | 0 | 45 | 0 | 0 | 37 | 0 | 17 | 18 | 12 | 0 | 0 | 398 | 57 | 35 | 10 | 4 | 85 | 0 | 12 | 34 | 13 | 12 | 300 | 0 | 53 | 0 | 0 | 0 | 17 | 33 | 0 | 0 | 240 | 0 | 0 | 311 | 0 | 344 | 300 | 0 |  | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 520 | 220 | 0 | 0 | 5 | 56 | 0 | 0 | 0 | 701 | 37 | 150 | 951 | 200 | 0 |  | 6324 | 4444 | 10768 | 3513 | 903 | 2020 | 0 | 413 | 3147 | 208 | 0 | 16 | 134 | 414 | 0 | 0 | 103.98
13:00 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 410 | 333 |  | 0 | 225 | 148 | 14 | 14 | 0 | 330 | 0 | 0 | 7 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 19 | 12 | 25 | 22 | 8 | 0 | 130 | 75 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 295 | 240 | 194 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 0 | 15 | 6 | 4 | 12 | 150 | 13 | 0 | 19 | 2 | 43 | 0 | 0 | 39 | 163 | 0 | 55 | 0 | 0 | 135 | 16 | 0 | 10 | 310 | 15 | 8 | 0 | 80 | 0 | 0 | 37 | 0 | 21 | 18 | 12 | 0 | 2 | 405 | 66 | 35 | 17 | 2 | 150 | 8 | 17 | 34 | 27 | 12 | 300 | 0 | 50 | 17 | 27 | 0 | 17 | 32 | 30 | 0 | 240 | 0 | 0 | 311 | 0 | 344 | 200 | 0 |  | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 5 | 0 | 0 | 0 | 6 | 0 | 570 | 220 | 0 | 0 | 5 | 88 | 0 | 0 | 0 | 711 | 35 | 150 | 1013 | 187 | 0 |  | 6558 | 4567 | 11125 | 3550 | 903 | 1910 | 0 | 697 | 3269 | 205 | 0 | 16 | 150 | 425 | 0 | 0 | 103.96
14:00 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 413 | 303 |  | 0 | 225 | 150 | 25 | 60 | 15 | 330 | 0 | 0 | 9 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 19 | 12 | 25 | 28 | 8 | 0 | 130 | 75 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 6 | 10 | 0 | 0 | 0 | 0 | 280 | 240 | 182 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 0 | 15 | 9 | 16 | 12 | 146 | 13 | 0 | 19 | 2 | 43 | 0 | 0 | 44 | 163 | 0 | 55 | 0 | 0 | 135 | 16 | 0 | 10 | 285 | 15 | 8 | 0 | 55 | 0 | 0 | 37 | 0 | 27 | 0 | 12 | 7 | 6 | 403 | 66 | 35 | 17 | 1 | 200 | 17 | 17 | 34 | 28 | 12 | 300 | 0 | 40 | 17 | 34 | 0 | 17 | 14 | 35 | 0 | 240 | 35 | 0 | 310 | 0 | 345 | 200 | 0 |  | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 32 | 0 | 38 | 0 | 5 | 35 | 600 | 220 | 0 | 0 | 4 | 61 | 0 | 0 | 0 | 711 | 30 | 150 | 1015 | 160 | 0 |  | 6628 | 4636 | 11264 | 3545 | 903 | 1861 | 0 | 935 | 3301 | 205 | 0 | 51 | 146 | 317 | 0 | 0 | 103.99
15:00 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 398 | 333 |  | 0 | 225 | 149 | 25 | 65 | 15 | 326 | 0 | 0 | 17 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 19 | 12 | 25 | 28 | 8 | 0 | 131 | 75 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 6 | 17 | 0 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 280 | 240 | 164 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 21 | 15 | 9 | 17 | 12 | 146 | 12 | 0 | 18 | 1 | 43 | 0 | 0 | 40 | 163 | 0 | 50 | 0 | 0 | 135 | 16 | 0 | 10 | 290 | 15 | 8 | 0 | 45 | 0 | 0 | 37 | 0 | 29 | 12 | 12 | 17 | 10 | 404 | 66 | 35 | 17 | 0 | 106 | 17 | 17 | 70 | 29 | 12 | 300 | 0 | 32 | 17 | 34 | 0 | 17 | 20 | 35 | 0 | 240 | 35 | 0 | 311 | 0 | 544 | 150 | 0 |  | 903 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 17 | 0 | 35 | 0 | 34 | 0 | 4 | 35 | 600 | 220 | 0 | 0 | 3 | 51 | 24 | 0 | 0 | 709 | 22 | 150 | 1013 | 118 | 0 |  | 6777 | 4595 | 11372 | 3504 | 903 | 1820 | 0 | 965 | 3497 | 206 | 0 | 68 | 146 | 263 | 0 | 74.49 | 103.92
16:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 410 | 332 |  | 0 | 225 | 148 | 25 | 67 | 15 | 0 | 0 | 0 | 17 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 19 | 12 | 25 | 28 | 8 | 0 | 131 | 75 | 0 | 0 | 6 | 225 | 0 | 0 | 0 |  | 6 | 32 | 0 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 280 | 240 | 159 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 24 | 15 | 9 | 25 | 12 | 140 | 12 | 0 | 18 | 1 | 43 | 0 | 0 | 41 | 163 | 0 | 51 | 0 | 0 | 135 | 16 | 0 | 10 | 300 | 15 | 8 | 0 | 47 | 0 | 0 | 19 | 0 | 30 | 7 | 12 | 17 | 10 | 404 | 56 | 35 | 17 | 0 | 106 | 17 | 17 | 52 | 28 | 12 | 295 | 0 | 14 | 35 | 34 | 0 | 17 | 10 | 40 | 0 | 240 | 35 | 0 | 310 | 0 | 545 | 150 | 0 |  | 904 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 18 | 0 | 35 | 0 | 35 | 0 | 2 | 35 | 600 | 220 | 0 | 0 | 2 | 26 | 50 | 0 | 0 | 711 | 10 | 150 | 1058 | 60 | 0 |  | 6424 | 4598 | 11022 | 3160 | 904 | 1828 | 0 | 1025 | 3544 | 206 | 0 | 83 | 140 | 132 | 0 | 50.615 | 103.91
17:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 397 | 281 |  | 0 | 225 | 147 | 25 | 85 | 15 | 75 | 0 | 0 | 18 | 16 | 32 | 8 | 0 | 0 | 0 | 17 | 0 | 17 | 15 | 19 | 12 | 25 | 28 | 8 | 0 | 131 | 75 | 0 | 0 | 8 | 226 | 0 | 0 | 0 |  | 7 | 32 | 0 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 280 | 240 | 167 | 0 | 0 | 5 | 0 | 0 | 30 | 0 | 0 | 24 | 15 | 9 | 25 | 6 | 134 | 12 | 0 | 18 | 0 | 43 | 0 | 0 | 42 | 163 | 0 | 56 | 0 | 0 | 140 | 17 | 0 | 10 | 280 | 15 | 2 | 0 | 47 | 0 | 0 | 19 | 0 | 18 | 1 | 12 | 17 | 15 | 370 | 57 | 35 | 17 | 0 | 106 | 17 | 17 | 34 | 29 | 12 | 290 | 6 | 1 | 35 | 34 | 0 | 17 | 1 | 64 | 0 | 240 | 35 | 0 | 312 | 0 | 546 | 150 | 0 |  | 903 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 13 | 0 | 8 | 90 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 16 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 25 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 540 | 200 | 0 | 0 | 0 | 4 | 35 | 0 | 0 | 714 | 1 | 150 | 1012 | 7 | 0 |  | 6401 | 4374 | 10775 | 3151 | 903 | 1723 | 0 | 1087 | 3444 | 206 | 0 | 112 | 134 | 15 | 0 | 71.625 | 103.9
18:00 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 353 | 333 |  | 0 | 225 | 146 | 25 | 85 | 15 | 214 | 0 | 0 | 33 | 16 | 133 | 44 | 0 | 0 | 0 | 35 | 17 | 35 | 17 | 19 | 12 | 33 | 28 | 12 | 0 | 132 | 75 | 0 | 0 | 17 | 224 | 0 | 0 | 0 |  | 12 | 37 | 0 | 12 | 0 | 18 | 12 | 0 | 0 | 0 | 0 | 280 | 240 | 175 | 0 | 0 | 5 | 0 | 0 | 42 | 0 | 0 | 24 | 15 | 10 | 25 | 12 | 152 | 12 | 0 | 19 | 0 | 43 | 0 | 0 | 45 | 163 | 0 | 56 | 0 | 0 | 135 | 17 | 0 | 10 | 280 | 15 | 2 | 0 | 95 | 0 | 0 | 19 | 0 | 19 | 0 | 12 | 17 | 30 | 400 | 57 | 70 | 17 | 0 | 222 | 17 | 17 | 70 | 76 | 12 | 290 | 16 | 0 | 72 | 34 | 0 | 17 | 0 | 75 | 6 | 230 | 100 | 0 | 312 | 0 | 550 | 184 | 0 |  | 903 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 30 | 0 | 8 | 124 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 24 | 29 | 16 | 37 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 36 | 0 | 46 | 32 | 80 | 0 | 0 | 35 | 700 | 220 | 0 | 3 | 0 | 0 | 54 | 0 | 0 | 709 | 0 | 150 | 1102 | 0 | 0 |  | 7352 | 4953 | 12305 | 3348 | 903 | 1842 | 0 | 1724 | 3693 | 207 | 0 | 436 | 152 | 0 | 0 | 100 | 103.89
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 391 | 301 |  | 0 | 225 | 148 | 25 | 75 | 15 | 154 | 0 | 0 | 33 | 16 | 98 | 28 | 0 | 0 | 0 | 35 | 35 | 55 | 17 | 19 | 12 | 33 | 28 | 20 | 0 | 132 | 75 | 0 | 0 | 17 | 221 | 0 | 0 | 0 |  | 12 | 73 | 0 | 12 | 0 | 19 | 12 | 2 | 0 | 0 | 0 | 280 | 240 | 177 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 16 | 15 | 10 | 25 | 12 | 148 | 23 | 0 | 15 | 0 | 43 | 0 | 0 | 43 | 130 | 0 | 57 | 0 | 0 | 135 | 18 | 0 | 10 | 250 | 15 | 2 | 0 | 45 | 0 | 0 | 112 | 0 | 88 | 0 | 12 | 17 | 12 | 401 | 85 | 70 | 17 | 0 | 232 | 17 | 17 | 70 | 76 | 12 | 290 | 16 | 0 | 72 | 34 | 0 | 17 | 0 | 76 | 17 | 230 | 17 | 0 | 311 | 0 | 550 | 160 | 0 |  | 902 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 32 | 0 | 8 | 124 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 8 | 35 | 8 | 37 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 17 | 0 | 35 | 15 | 54 | 0 | 0 | 35 | 900 | 220 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 715 | 0 | 150 | 1136 | 0 | 0 |  | 7301 | 5089 | 12390 | 3335 | 902 | 1743 | 0 | 1791 | 3932 | 207 | 0 | 332 | 148 | 0 | 0 | 33 | 103.86
19:30 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 385 | 303 |  | 0 | 225 | 150 | 25 | 48 | 15 | 150 | 0 | 0 | 33 | 16 | 82 | 25 | 0 | 0 | 0 | 35 | 35 | 55 | 17 | 19 | 12 | 33 | 28 | 25 | 0 | 132 | 75 | 0 | 0 | 17 | 220 | 0 | 0 | 0 |  | 12 | 70 | 0 | 12 | 0 | 19 | 12 | 4 | 0 | 0 | 0 | 280 | 240 | 181 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 16 | 15 | 10 | 25 | 12 | 148 | 23 | 0 | 0 | 0 | 43 | 0 | 0 | 43 | 130 | 0 | 57 | 0 | 0 | 135 | 18 | 0 | 10 | 275 | 15 | 2 | 0 | 15 | 0 | 0 | 112 | 0 | 100 | 0 | 12 | 17 | 12 | 401 | 85 | 70 | 17 | 0 | 232 | 17 | 17 | 34 | 76 | 12 | 280 | 17 | 0 | 72 | 34 | 0 | 17 | 0 | 77 | 17 | 230 | 17 | 0 | 310 | 0 | 550 | 188 | 0 |  | 903 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 27 | 0 | 8 | 130 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 8 | 36 | 8 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 17 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 840 | 220 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 709 | 0 | 150 | 1117 | 0 | 0 |  | 7231 | 4988 | 12219 | 3309 | 903 | 1802 | 0 | 1694 | 3846 | 207 | 0 | 310 | 148 | 0 | 0 | 30 | 0
20:00 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 385 | 301 |  | 0 | 225 | 146 | 25 | 42 | 15 | 150 | 0 | 0 | 33 | 16 | 82 | 25 | 0 | 0 | 0 | 35 | 35 | 55 | 17 | 19 | 12 | 33 | 28 | 25 | 0 | 132 | 75 | 0 | 0 | 17 | 221 | 0 | 0 | 0 |  | 12 | 70 | 0 | 12 | 0 | 20 | 12 | 5 | 0 | 0 | 0 | 280 | 240 | 180 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 16 | 15 | 10 | 30 | 12 | 148 | 30 | 0 | 0 | 0 | 43 | 0 | 0 | 43 | 130 | 0 | 57 | 0 | 0 | 135 | 18 | 0 | 10 | 275 | 15 | 2 | 0 | 15 | 0 | 0 | 112 | 0 | 99 | 0 | 12 | 17 | 12 | 401 | 85 | 70 | 17 | 0 | 233 | 17 | 17 | 34 | 78 | 12 | 280 | 16 | 0 | 35 | 34 | 0 | 17 | 0 | 70 | 17 | 230 | 17 | 0 | 310 | 0 | 549 | 156 | 0 |  | 902 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 27 | 0 | 8 | 124 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 8 | 36 | 8 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 17 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 820 | 220 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 703 | 0 | 150 | 1119 | 0 | 0 |  | 7157 | 4957 | 12114 | 3315 | 902 | 1765 | 0 | 1646 | 3821 | 207 | 0 | 310 | 148 | 0 | 0 | 0 | 103.87
21:00 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 395 | 337 |  | 0 | 225 | 145 | 25 | 34 | 15 | 150 | 0 | 0 | 26 | 16 | 64 | 25 | 0 | 0 | 0 | 35 | 17 | 55 | 18 | 19 | 12 | 33 | 28 | 25 | 0 | 132 | 75 | 0 | 0 | 17 | 213 | 0 | 0 | 0 |  | 6 | 70 | 0 | 12 | 0 | 20 | 12 | 10 | 0 | 0 | 0 | 280 | 240 | 180 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 10 | 33 | 12 | 142 | 32 | 0 | 19 | 0 | 43 | 0 | 0 | 43 | 163 | 0 | 57 | 0 | 0 | 135 | 18 | 0 | 10 | 285 | 15 | 2 | 0 | 15 | 0 | 0 | 112 | 0 | 79 | 0 | 12 | 17 | 12 | 402 | 85 | 34 | 17 | 0 | 158 | 17 | 17 | 17 | 78 | 12 | 285 | 17 | 0 | 17 | 34 | 0 | 17 | 0 | 58 | 17 | 230 | 17 | 0 | 311 | 0 | 548 | 180 | 0 |  | 902 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 26 | 0 | 8 | 124 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 8 | 0 | 8 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 17 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 740 | 220 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 708 | 0 | 150 | 1068 | 0 | 0 |  | 7052 | 4812 | 11864 | 3351 | 902 | 1890 | 0 | 1422 | 3695 | 207 | 0 | 255 | 142 | 0 | 0 | 0 | 103.86
22:00 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 392 | 300 |  | 0 | 225 | 143 | 25 | 34 | 15 | 150 | 0 | 0 | 26 | 16 | 48 | 25 | 0 | 0 | 0 | 35 | 0 | 35 | 18 | 19 | 12 | 33 | 28 | 25 | 0 | 132 | 75 | 0 | 0 | 17 | 214 | 0 | 0 | 0 |  | 6 | 70 | 0 | 12 | 0 | 20 | 12 | 6 | 0 | 0 | 0 | 280 | 240 | 180 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 0 | 8 | 18 | 10 | 33 | 12 | 144 | 38 | 0 | 19 | 0 | 43 | 0 | 0 | 49 | 130 | 0 | 57 | 0 | 0 | 135 | 18 | 0 | 10 | 265 | 15 | 2 | 0 | 15 | 0 | 0 | 112 | 0 | 72 | 0 | 12 | 17 | 12 | 352 | 85 | 34 | 17 | 0 | 160 | 17 | 17 | 17 | 46 | 12 | 285 | 0 | 0 | 17 | 34 | 0 | 17 | 0 | 58 | 17 | 230 | 17 | 0 | 310 | 0 | 551 | 153 | 0 |  | 903 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 26 | 0 | 8 | 92 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 8 | 0 | 8 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213 | 17 | 0 | 0 | 15 | 34 | 0 | 0 | 0 | 740 | 200 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 724 | 0 | 150 | 1061 | 0 | 0 |  | 6778 | 4716 | 11494 | 3273 | 903 | 1761 | 0 | 1261 | 3706 | 207 | 0 | 239 | 144 | 0 | 0 | 0 | 103.85
23:00 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 335 | 285 |  | 0 | 225 | 146 | 23 | 34 | 15 | 150 | 0 | 0 | 9 | 16 | 48 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 18 | 19 | 12 | 33 | 28 | 8 | 0 | 131 | 75 | 0 | 0 | 8 | 201 | 0 | 0 | 0 |  | 6 | 70 | 0 | 12 | 0 | 20 | 12 | 11 | 0 | 0 | 0 | 280 | 240 | 183 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 11 | 33 | 12 | 142 | 69 | 0 | 19 | 0 | 43 | 0 | 0 | 49 | 130 | 0 | 57 | 0 | 0 | 135 | 18 | 0 | 10 | 260 | 15 | 2 | 0 | 15 | 0 | 0 | 18 | 0 | 72 | 0 | 12 | 17 | 12 | 342 | 56 | 34 | 17 | 0 | 161 | 17 | 17 | 17 | 46 | 12 | 310 | 0 | 0 | 17 | 34 | 0 | 17 | 0 | 64 | 13 | 230 | 17 | 0 | 310 | 0 | 550 | 189 | 0 |  | 903 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223 | 17 | 0 | 0 | 15 | 34 | 0 | 0 | 0 | 740 | 200 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 722 | 0 | 150 | 1060 | 0 | 0 |  | 6561 | 4611 | 11172 | 3261 | 903 | 1803 | 0 | 1020 | 3702 | 206 | 0 | 135 | 142 | 0 | 0 | 0 | 103.84
24:00 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 397 | 285 |  | 0 | 225 | 153 | 8 | 17 | 15 | 150 | 0 | 0 | 9 | 16 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 18 | 19 | 12 | 33 | 28 | 8 | 0 | 130 | 75 | 0 | 0 | 8 | 202 | 0 | 0 | 0 |  | 6 | 70 | 0 | 12 | 0 | 10 | 12 | 15 | 0 | 0 | 0 | 280 | 240 | 185 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 11 | 33 | 12 | 138 | 73 | 0 | 19 | 0 | 43 | 0 | 0 | 49 | 130 | 0 | 57 | 0 | 0 | 135 | 18 | 0 | 10 | 280 | 15 | 2 | 0 | 0 | 0 | 0 | 18 | 0 | 48 | 0 | 12 | 17 | 12 | 343 | 56 | 17 | 17 | 0 | 160 | 17 | 17 | 17 | 37 | 12 | 310 | 0 | 0 | 0 | 34 | 0 | 17 | 0 | 63 | 17 | 230 | 0 | 0 | 310 | 0 | 552 | 160 | 0 |  | 903 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 740 | 200 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 724 | 0 | 150 | 1055 | 0 | 0 |  | 6441 | 4522 | 10963 | 3331 | 903 | 1803 | 0 | 796 | 3701 | 205 | 0 | 86 | 138 | 0 | 0 | 0 | 103.83
KWH | 0 | 0 | 3456531 | 0 | 0 | 0 | 0 | 8980480 | 7186000 |  | 0 | 4853000 | 3491316 | 268800 | 552044 | 170073 | 5536730 | 0 | 0 | 224170 | 193104 | 660960 | 154935 | 0 | 0 | 0 | 229680 | 97849 | 265198 | 339228 | 456000 | 281880 | 699500 | 668800 | 207360 | 0 | 3163047 | 1596000 | 0 | 0 | 119188 | 4865635 | 0 | 0 | 0 |  | 114720 | 499296 | 0 | 132240 | 0 | 148800 | 264912 | 273600 | 0 | 0 | 0 | 7245400 | 6045000 | 4304000 | 0 | 0 | 148968 | 0 | 0 | 733152 | 0 | 0 | 170947 | 401976 | 224820 | 412900 | 291300 | 2979840 | 820800 | 0 | 407628 | 14000 | 1020000 | 0 | 0 | 638352 | 3475718 | 0 | 1213344 | 192960 | 0 | 2380640 | 396000 | 0 | 211320 | 6748500 | 354768 | 144318 | 0 | 720109 | 0 | 0 | 808800 | 0 | 730656 | 75735 | 162240 | 215520 | 182327 | 8979000 | 1189200 | 617280 | 221636 | 11520 | 1994727 | 213402 | 230000 | 477660 | 658560 | 144960 | 7323100 | 75840 | 336380 | 360000 | 414000 | 0 | 443880 | 217277 | 706560 | 190080 | 5867500 | 327854 | 0 | 8012726 | 480 | 8087272 | 5622272 | 0 |  | 19280000 | 0 | 0 | 0 | 147840 | 0 | 0 | 0 | 148320 | 0 | 40875 | 2483000 | 457800 | 92064 | 0 | 0 | 0 | 0 | 0 | 229344 | 0 | 63049 | 84719 | 88090 | 189075 | 0 | 0 | 229482 | 0 | 0 | 4187300 | 0 | 0 | 3679782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5501600 | 288960 | 0 | 351360 | 118824 | 426518 | 0 | 38130 | 315456 | 16418300 | 4919700 | 0 | 105600 | 37860 | 565920 | 435456 | 0 | 0 | 17963637 | 250330 | 3752700 | 23050909 | 1369280 | 0 |  | 146746280 | 107311280 | 254057560 | 79923422 | 19280000 | 44305290 | 0 | 16280637 | 81472844 | 4759047 | 0 | 2139568 | 2979840 | 2916432 | 480 | 0
Fuel Cost | 0 | 0 | 5046535.26 | 0 | 0 | 0 | 0 | 9429504 | 7760880 |  | 0 | 5289770 | 3875360.76 | 3005184 | 7314583 | 2253467.25 | 6201137.6 | 0 | 0 | 3277365.4 | 2716973.28 | 10714161.6 | 1428500.7 | 0 | 0 | 0 | 2921529.6 | 1320961.5 | 3556305.18 | 254421 | 342000 | 0 | 0 | 0 | 3527193.6 | 0 | 854022.69 | 430920 | 0 | 0 | 1948723.8 | 5060260.4 | 0 | 0 | 0 |  | 1497096 | 8328257.28 | 0 | 1786562.4 | 0 | 1721616 | 336438.24 | 911088 | 0 | 0 | 0 | 8042394 | 6589050 | 4992640 | 0 | 0 | 168333.84 | 0 | 0 | 1224363.84 | 0 | 0 | 2299237.15 | 550707.12 | 168615 | 722575 | 218475 | 21395251.2 | 894672 | 0 | 554374.08 | 223160 | 1397400 | 0 | 0 | 1104348.96 | 3997075.7 | 0 | 2353887.36 | 439948.8 | 0 | 2404446.4 | 851400 | 0 | 418413.6 | 6748500 | 266076 | 109681.68 | 0 | 9829487.85 | 0 | 0 | 10902624 | 0 | 10119585.6 | 885342.15 | 1674316.8 | 2944003.2 | 2419479.29 | 8260680 | 14460672 | 8925868.8 | 2803695.4 | 179251.2 | 23418094.98 | 2323947.78 | 2444900 | 6481846.2 | 8488838.4 | 1707628.8 | 6737252 | 982128 | 4860691 | 4568400 | 4711320 | 0 | 5797072.8 | 2596460.15 | 10577203.2 | 2503353.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 57840000 | 0 | 0 | 0 | 1539014.4 | 0 | 0 | 0 | 2671243.2 | 0 | 587373.75 | 2780960 | 888132 | 1003497.6 | 0 | 0 | 0 | 0 | 0 | 3586940.16 | 0 | 1044091.44 | 1432598.29 | 1200666.7 | 3189695.25 | 0 | 0 | 173717.874 | 0 | 0 | 35508304 | 0 | 0 | 4268547.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5446584 | 3883622.4 | 0 | 4156588.8 | 1717006.8 | 5416778.6 | 0 | 421336.5 | 3829635.84 | 136271890 | 5018094 | 0 | 781440 | 428196.6 | 6638241.6 | 6675540.48 | 0 | 0 | 163289460.33 | 0 | 44919819 | 197085271.95 | 0 | 0 |  | 332849988.47 | 703694288.684 | 1036544277.154 | 79176180.974 | 57840000 | 43122559.66 | 0 | 210495022.37 | 577074745.28 | 1284942.69 | 0 | 29922895.78 | 21395251.2 | 16232679.2 | 0 | 0
Yesterday Day Peak | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 410 | 331 |  | 0 | 225 | 149 | 1 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 19 | 12 | 25 | 28 | 8 | 0 | 133 | 75 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 285 | 240 | 184 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 0 | 15 | 6 | 0 | 12 | 134 | 27 | 0 | 19 | 1 | 43 | 0 | 0 | 40 | 163 | 0 | 58 | 0 | 0 | 140 | 16 | 0 | 10 | 300 | 15 | 8 | 0 | 45 | 0 | 0 | 37 | 0 | 17 | 18 | 12 | 0 | 0 | 398 | 57 | 35 | 10 | 4 | 85 | 0 | 12 | 34 | 13 | 12 | 300 | 0 | 53 | 0 | 0 | 0 | 17 | 33 | 0 | 0 | 240 | 0 | 0 | 311 | 0 | 344 | 300 | 0 |  | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 520 | 220 | 0 | 0 | 5 | 56 | 0 | 0 | 0 | 701 | 37 | 150 | 951 | 200 | 0 |  | 10768 | DayPeak
Yesterday Evening Peak | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 391 | 301 |  | 0 | 225 | 148 | 25 | 75 | 15 | 154 | 0 | 0 | 33 | 16 | 98 | 28 | 0 | 0 | 0 | 35 | 35 | 55 | 17 | 19 | 12 | 33 | 28 | 20 | 0 | 132 | 75 | 0 | 0 | 17 | 221 | 0 | 0 | 0 | 0 | 12 | 73 | 0 | 12 | 0 | 19 | 12 | 2 | 0 | 0 | 0 | 280 | 240 | 177 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 16 | 15 | 10 | 25 | 12 | 148 | 23 | 0 | 15 | 0 | 43 | 0 | 0 | 43 | 130 | 0 | 57 | 0 | 0 | 135 | 18 | 0 | 10 | 250 | 15 | 2 | 0 | 45 | 0 | 0 | 112 | 0 | 88 | 0 | 12 | 17 | 12 | 401 | 85 | 70 | 17 | 0 | 232 | 17 | 17 | 70 | 76 | 12 | 290 | 16 | 0 | 72 | 34 | 0 | 17 | 0 | 76 | 17 | 230 | 17 | 0 | 311 | 0 | 550 | 160 | 0 |  | 902 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 32 | 0 | 8 | 124 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 8 | 35 | 8 | 37 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 17 | 0 | 35 | 15 | 54 | 0 | 0 | 35 | 900 | 220 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 715 | 0 | 150 | 1136 | 0 | 0 |  | 12390 | EvPeak
Forecast for Evening | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 400 | 330 |  | 0 | 225 | 150 | 17 | 85 | 15 | 215 | 0 | 0 | 24 | 50 | 149 | 40 | 0 | 0 | 0 | 35 | 35 | 55 | 18 | 19 | 13 | 25 | 30 | 25 | 0 | 133 | 75 | 0 | 0 | 17 | 225 | 0 | 0 | 0 |  | 12 | 73 | 32 | 12 | 0 | 18 | 12 | 25 | 0 | 0 | 0 | 320 | 300 | 200 | 0 | 0 | 20 | 0 | 0 | 51 | 0 | 30 | 52 | 18 | 10 | 33 | 12 | 166 | 45 | 0 | 19 | 0 | 43 | 0 | 0 | 48 | 163 | 0 | 62 | 0 | 0 | 130 | 17 | 0 | 10 | 300 | 16 | 8 | 0 | 130 | 0 | 0 | 114 | 0 | 100 | 0 | 12 | 17 | 150 | 400 | 100 | 105 | 17 | 0 | 280 | 17 | 17 | 70 | 78 | 12 | 328 | 17 | 0 | 72 | 34 | 0 | 35 | 0 | 94 | 55 | 350 | 163 | 0 | 311 | 12 | 450 | 232 | 0 |  | 851 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 40 | 60 | 16 | 130 | 28 | 110 | 0 | 0 | 0 | 30 | 16 | 94 | 28 | 42 | 40 | 8 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 74 | 0 | 50 | 32 | 113 | 0 | 0 | 55 | 900 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 700 | 0 | 150 | 1150 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 400 | 330 | 0 | 0 | 225 | 150 | 17 | 85 | 15 | 215 | 0 | 0 | 8 | 50 | 16 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 13 | 25 | 30 | 8 | 0 | 133 | 75 | 0 | 0 | 8 | 220 |  | 0 | 0 | 0 | 6 | 40 | 17 | 12 | 0 | 6 | 12 | 5 | 0 | 0 | 0 | 275 | 250 | 190 | 0 | 0 | 20 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 143 | 30 | 0 | 16 | 1.6 | 43 | 0 | 0 | 48 | 163 | 0 | 50 | 0 | 0 | 130 | 17 | 0 | 10 | 300 | 16 | 8 | 0 | 80 | 0 | 0 | 66 | 0 | 17 | 20 | 12 | 17 | 6 | 400 | 40 | 35 | 17 | 5 | 100 | 17 | 17 | 17 | 28 | 12 | 328 | 0 | 50 | 17 | 17 | 0 | 17 | 35 | 36 | 55 | 300 | 35 |  | 311 | 12 | 600 | 232 | 0 |  | 907 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 28 | 34 | 30 | 8 | 24 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 53 | 0 | 35 | 15 | 113 | 0 | 8 | 35 | 520 | 220 |  | 38 | 6 | 100 | 70 | 0 |  | 700 | 30 | 150 | 950 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 338 | 275 | 0 | 0 | 170 | 149 | 0 | 17 | 0 | 150 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 12 | 33 | 30 | 2 | 0 | 132 | 75 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 12 | 0 | 6 | 12 | 9 | 0 | 0 | 0 | 275 | 250 | 183 | 0 | 0 | 5 | 0 | 0 | 10 | 0 | 0 | 9 | 18 | 11 | 26 | 12 | 110 | 27 | 0 | 19 | 1 | 43 | 0 | 0 | 5 | 120 | 0 | 40 | 0 | 0 | 135 | 17 | 0 | 10 | 275 | 8 | 8 | 0 | 0 | 0 | 0 | 56 | 0 | 14 | 12 | 12 | 10 | 0 | 330 | 19 | 17 | 17 | 2 | 16 | 8 | 17 | 17 | 3 | 12 | 310 | 0 | 6 | 0 | 3 | 0 | 17 | 12 | 17 | 0 | 230 | 0 | 0 | 311 | 0 | 454 | 185 | 0 | 0 | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 520 | 180 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 701 | 15 | 150 | 917 | 84 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
[22 empty] | 299565 | [26 empty] | 399366 | [49 empty] | 299523 |  | 299563 |  | 399588 |  | 299281 | 299229 | 299524 |  | 399747 |  |  |  |  | 399575 | 399337 | 399589 | [8 empty] | 399245 |  |  | 399274 |  | 399226 |  | 399630 | [12 empty] | 599468 | [34 empty] | 499268 | 599634 |  |  |  | 499720 | [19 empty] | 292.3904
| Minimum Generation |  | 8504 | 6:00 | [202 empty] | 124228712
| Highest Generation |  | 12390 | 19:00 | [202 empty] | 124.2287 |  |  |  |  | 2.9164
| Day Peak Generation |  | 10768 | 12:00 | [202 empty] | 18420205
| Evening Peak Generation |  | 12390 | 19:00 | [202 empty] | 18.4202 |  |  | 44305290 |  | 4.759
| HVDC Max Flow |  | 904 | 16:00 | [202 empty] | 19.28 |  |  |  |  | 0.00048
| HVDC EvPeak Flow |  | 902 | 19:00 | [200 empty] | 254057560 |  | 2.9798 |  | 81.4728
| Load factor L.F |  | 85.44% | [166 empty] | 1275.5 | [36 empty] | 254.0576

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-10-26
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-10-25 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 10768 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 9206
Evening Peak Generation : |  |  | 12390 | MW Hour : | 19:00 | Available Max Generation : |  | 14510
E.P. Demand (at gen end) : |  |  | 12425 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 13500
Maximum Generation : |  |  | 12390 | MW Hour : | 19:00 | Reserve(Generation end) |  | 1010
Total Gen. (MKWH) : |  |  | 254.0576 | System Load Factor : | 85.44% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 600 | MW at | 18:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-10-26
Actual : |  | 103.77 | Ft.(MSL) , | Rule curve : | 108.4 | Ft.( MSL )
Gas Consumed : |  | Total = | 952.3 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 122298740.634
: |  |  | Coal : | 577074745.28 | Oil : | 240417918.15 | Total : | 939791404.064
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 18 | 432:00 | 4534.2896 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1245.692 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1744.9061 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1516.5797 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1247.9061 |  |  | 0 | 0%
Mymensingh Area |  | 15 | 360:00 | 928.0993 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 520.2585 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 433.5457 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 847.94 |  |  | 0 | 0%
Total |  | 33 |  | 13019.2171 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
8:09 | 11:24 | Ishurdi-Pabna 132kV ckt Scheduled S/D from Ishurdi 132/33kV end Due to Annual maintenance and from Pabna 132/33kVend.
8:29 | 14:45 | Bashundhara-Tongi 132 kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Annual maintenance.
8:35 | 16:07 | Panchagarh 132/33kV S/S T-2(417T) LT Scheduled S/D Due to Anual maintance.
8:35 | 16:06 | Panchagarh 132/33kV S/S T-2(417T) HT Scheduled S/D Due to Anual maintance.
8:46 | 20:08 | Payra 400/132/33kV S/S 132/33 kV Transformer-03 LT Scheduled S/D Due to Annual maintenance.
8:47 | 20:03 | Payra 400/132/33kV S/S 132/33 kV Transformer-03 HT Scheduled S/D Due to Annual maintenance.
8:49 | 16:24 | Jamalpur-Mymensingh 132kV Ckt-2 Scheduled S/D from Jamalpur 132/33kV end Due to Annual Maintenance work. and from
Mymensingh 132/33kVend.
9:01 | 16:16 | Ashuganj-Kishoreganj 132kV Ckt-2 Scheduled S/D from Kishoreganj 132/33kV end Due to For annual maintenance work.
9:01 | 16:16 | Ashuganj-Kishoreganj 132kV Ckt-2 Scheduled S/D from Kishoreganj 132/33kV end Due to For annual maintenance work.
9:11 | 22:04 | Gopalganj(N)-Madaripur 132kV Ckt-2 Project Work S/D from Gopalganj 400/132kV end.
9:14 | 14:42 | Rangpur 132/33kV S/S T-1(414T) LT Scheduled S/D Due to Annual Maintenance.
9:15 | 14:40 | Rangpur 132/33kV S/S T-1(414T) HT Scheduled S/D Due to Annual Maintenance.
9:27 | 16:39 | Chauddagram-Cumilla(S) 132 kV Ckt-1 Scheduled S/D from Cumilla(S) 132/33kV end Due to Annual maintenance.
9:30 | 21:42 | Gopalganj 400/132kV S/S ATR-03 LT Project Work S/D.
9:30 | 21:42 | Gopalganj 400/132kV S/S ATR-03 LT Project Work S/D.
9:35 | 21:39 | Gopalganj 400/132kV S/S ATR-03 HT Project Work S/D.
9:48 | 16:39 | Chauddagram-Cumilla(S) 132 kV Ckt-1 Scheduled S/D from Chauddagram 132/33kV end Due to Annual Maintenance.
10:26 | 15:44 | Savar 132/33kV S/S Bus-A Scheduled S/D Due to red hot maintenance of 33kV feeders by DPBS-3.
10:27 | 10:47 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 LT Scheduled S/D Due to Energy meter changing work by BPDB.
10:27 | 10:47 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 HT Scheduled S/D Due to Energy meter changing work by BPDB.
10:48 | 11:20 | Hasnabad 132/33kV S/S 132/33kV 424 T-5 HT Scheduled S/D Due to Energy meter replacemen work.
10:48 | 11:20 | Hasnabad 132/33kV S/S 132/33kV 424 T-5 LT Scheduled S/D Due to Energy meter replacement work by BPDB.
11:41 | 12:44 | Barishal-Bhandaria 132 kV Ckt-1 Forced S/D from Bhandaria 132/33kV end Due to Emergency ROW and from Barishal 132/33kV |  |  |  |  | 27.0MW load interrup. Barishal end
end Due to Shutdown by ALDC instructions.
12:00 | - | Day peak generation: 10768 MW.
12:33 | 15:30 | Cox'sbazar-Dohazari 132 kV Ckt-2 Forced S/D from Coxsbazar 132/33kV end Due to Tree cutting.
13:11 | - | Pabna- Shahjadpur 132kV Ckt-1 Forced S/D from Pabna 132/33kV end Due to ALDC Instruction for Shahjadpur S/S work.
15:02 | - | Siddirganj CCPP 335MW tripped due to gas pressure fall.
15:26 | 16:30 | Rajshahi 230/132/33kV S/S 132/33 kV T-02 (416T) HT Scheduled S/D Due to বসন্তপুর ৩৩ কেভি ফিডারের বাস সাইড রেড হট
নিরসন কাজের জন্য।
15:26 | 16:31 | Rajshahi 230/132/33kV S/S 132/33 kV T-02 (416T) LT Scheduled S/D Due to বসন্তপুর ৩৩ কেভি ফিডারের বাস সাইডের রেটহট
নিরসন কাজের জন্য।
- | 16:11 | Siddirganj CCPP 335MW GT was sync.
- | 16:16 | Ashuganj-Kishoreganj 132kV Ckt-2 is restored.
16:31 | 17:57 | Madanganj-Munsiganj 132 kV Ckt-1 Project Work S/D from Munshiganj 132/33kV end Due to Total-Tel (Scada communication)
Work and from Madanganj 132/33kV end showing General trip. 86A&B OPTD relays Due to Munshiganj ckt-1 S/D from Munshiganj
sub station for scada work than at this time trip from Madanganj substation.
17:58 | 18:55 | Madanganj-Munsiganj 132 kV Ckt-2 Project Work S/D from Munshiganj 132/33kV end Due to Total-Tel (Scada Communication)
Work and from Madanganj 132/33kV end Due to For scada work in Munshiganj substation.
19:00 | - | Evening Peak Generation : 12390 MW
5:09 | - | Amnura-Rajshahi 132kV Ckt-1 Tripped from Rajshahi 230/132/33kV end showing Dist Relay,REL 670,REC650 relays Due to
Dist trip Zone 2,Protection lockout. and from Amnura 132/33kV end showing Distance Relay(P442), and Directional O/C & E/F
Relay(P141). relays Due to PT Blust of Y-phase for Distance Trip, Zone-1 and Over Voltage.
6:00 | - | Minimum generation 9206 MW.
6:20 | - | Maniknagar-Siddhirganj 230kV Ckt-2 Scheduled S/D from Siddhirganj 230/132kV end Due to Order of NLDC and from
Maniknagar 230/132kV end Due to Re-Routing Of line section Work.
6:39 | - | Cumilla(N) 230/132/33kV S/S 230KV T-02 LT Tripped showing Differential REF Backup EF relays Due to 33 KV Tertiary |  |  |  |  | 100.0MW load interrup.
Cable blast( R phase)
6:39 | - | Cumilla(N) 230/132/33kV S/S 230KV T-02 HT Tripped showing Differential Trip REF LV Backup EF Trip relays Due to 33KV |  |  |  |  | 100.0MW load interrup.
Tertiary Cable Blast(R phase)
7:25 | - | Payra 400/132/33kV S/S 132/33 kV Transformer-03 LT Scheduled S/D Due to Anual maintenance.
7:30 | - | Payra 400/132/33kV S/S 132/33 kV Transformer-03 HT Scheduled S/D Due to Anual maintenance.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-10-25 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 170 | 3456531
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 391 | 8980480 | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 301 | 7186000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4853000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 25 | 268800 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 148 | 3491316 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 75 | 552044 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 170073 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 28 | 154935 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 17 | 339228 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 33 | 224170 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 154 | 5536730
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 16 | 193104 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 229680 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 98 | 660960 | Low demand.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 97849 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 265198
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 31 | 737880 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 699500
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 668800 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 20 | 207360 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 45 | 720109 | Low demand.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 88 | 730656 | Low demand.
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 617280 | Low demand.
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 16 | 75840 | Low demand.
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 360000 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 217277
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 190080 | Fuel shortage
| Meghnaghat Unique power |  | IPP | 586 | 0 | 160 | 5622272 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5422 | 2401 | 47507152
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 119188 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 75735
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 148800 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 207 | 4759047
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 221 | 4865635
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 221636 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 73 | 499296 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 12 | 132240 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 162240 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 12 | 264912 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 2 | 273600
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 11520
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 232 | 1994727 | Low demand.
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 213402 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 230000 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 144960 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 34 | 414000 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 17 | 327854 | Low demand.
| SS Power I |  | SS Power | 1*612 | 612 | 311 | 8012726
| Cox's Bazar Wind |  | IPP | 66 | 0 | 0 | 480 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 550 | 8087272
| Chattogram area Total |  |  |  | 3157 | 1782 | 30959270
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 177 | 4304000 | ST under maint
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7245400 | ST under maint
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 240 | 6045000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 230 | 5867500 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 148968 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 733152
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 12 | 182327 | Low demand.
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Under maint.
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 215520 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 15 | 401976 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 224820
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 148 | 2979840
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 412900 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 16 | 170947 | Low demand.
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 12 | 291300 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 70 | 477660 | Low demand.
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 76 | 658560 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 443880 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 76 | 706560 | Fuel shortage
| Cumilla Area Total |  |  |  | 2896 | 1477 | 31510310
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 23 | 820800 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 15 | 407628 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14000
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 112 | 808800 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 85 | 1189200 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 336380
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 114720 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 247 | 3691528
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1020000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3475718
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 43 | 638352 | Engine problem
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 144318 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 57 | 1213344
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 0 | 192960 | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 135 | 2380640 | Under maint.
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 396000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 15 | 354768 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 250 | 6748500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 401 | 8979000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 211320
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 290 | 7323100
| Sylhet Area Total |  |  |  | 2427 | 1394 | 33078020
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 902 | 19280000
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 147840 | Low demand.
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 32 | 148320 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 40875 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 288960 | Low demand.
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 118824 | Transformer O/L
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 565920
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | TG Test
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 715 | 17963637
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 1705 | 38554376
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 92064 | Transformer O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 23 | 457800 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 124 | 2483000 | ST Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 900 | 16418300
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4919700
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 105600 | Transformer O/L
| Barisal 307 MW |  | IPP | 307*1 | 307 | 150 | 3752700 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1450 | 28229164
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 63049 | Low demand.
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 84719 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 150 | 3679782 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 180 | 5501600 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 189075 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 229482
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 88090 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 40 | 229344 | Low demand.
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 351360 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 315456 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 37860
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1136 | 23050909
| Rajshahi Area Total |  |  |  | 3631 | 1675 | 33820726
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4187300 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 54 | 426518 | Low demand.
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 38130
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 35 | 435456 | Low demand.
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 250330
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1369280
| Rangpur Area Total |  |  |  | 950 | 259 | 6707014
| Total |  |  |  | 24599 | 12390 | 254057560
| Eastern Grid Total |  |  |  | 14516 | 7301 | 146746280
| Western Grid Total |  |  |  | 10083 | 5089 | 107311280
| National Grid Total |  |  |  | 24599 | 12390 | 254057560
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-10-25
| (a) ENTIRE EASTERN GRID : |  | 8319.83 | MW | (b) ENTIRE WESTERN GRID : |  | 3594.2 | MW
| i) Dhaka area |  | 4692.53 | MW | i) Khulna area |  | 1419.4 | MW
| ii) Chittagong area |  | 1076.3 | MW | ii) Rajshahi area |  | 1169.8 | MW
| iii) Comilla area |  | 1117 | MW | iii) Barisal area |  | 338 | MW
| iv) Mymensingh area |  | 987 | MW | iv) Rangpur area |  | 667 | MW
| v) Sylhet area |  | 447 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11914.03 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 26 | 18:00 | Kamrangirchar | 51.9 | 13:00 | Narshingdi | 173 | 19:30 | Shikalbaha | 25 | 18:00
2 | AKSML | 106.7 | 13:00 | Chowmuhani | 170 | 19:30 | Kaptai | N/A | N/A | Natore | 115 | 18:00 | Shikalbaha-230 | N/A | N/A
3 | Aftabnagar | 32 | 13:00 | Chuadanga | 95 | 18:30 | Kazla | 89 | 16:00 | Nawabganj | 37 | 21:00 | Shitalakhya | 102.6 | 12:00
4 | Agargaon | 78 | 13:00 | Coxsbazar | 63 | 23:00 | Keranigonj | 66 | 18:30 | Netrakona | 119 | 18:30 | Sholosohor | 38 | 15:00
5 | Agrabad | 72 | 13:00 | Cumilla(N) | 131 | 18:00 | Khagrachori | 24 | 18:00 | New | 75 | 12:00 | Shyampur | 170 | 13:00
6 | Amnura | 43 | 18:30 | Cumilla(S) | 152 | 18:00 | Khulna | 87 | 18:00 | Niamatpur | 59 | 18:00 | Siddhirganj | 118 | 12:00
7 | Ashuganj | 60 | 00:00 | Daudkandi | 134 | 18:00 | Khulshi | 159 | 18:30 | Noapara | 41 | 18:30 | Sirajganj | 96 | 19:00
8 | BIPTC | N/A | N/A | Dhaka | 44 | 13:00 | Kishoreganj | 132 | 20:00 | PHP | 3 | 10:00 | Sonargaon | 97 | 16:00
9 | BSRM | 134 | 08:00 | Dhamrai | 118 | 15:00 | Kodda | 284 | 18:30 | Pabna | 102 | 18:30 | Sreemongol | 56 | 18:00
10 | Bagerhat | 75 | 18:00 | Dhanmondi | 125 | 13:00 | Kulaura | 32 | 18:00 | Palashbari | 94 | 18:00 | Sreepur | 63 | 12:00
11 | Bakulia | 84 | 18:00 | Dohazari | 26 | 20:00 | Kurigram | 56 | 18:00 | Panchagarh | 47 | 18:00 | Srinagar | 38.4 | 21:00
12 | Banani | 47 | 13:00 | Faridpur | 131 | 18:30 | Kushtia | 116 | 18:30 | Patuakhali | 81 | 22:00 | Sunamganj | 44 | 18:30
13 | Bangabhaban | 12 | 10:00 | Fatullah | 67 | 18:00 | Lalbag | 87 | 18:30 | Payra | 17 | 22:00 | Sylhet | 12 | 18:00
14 | Barapukuria | 50 | 18:30 | Fenchuganj | 31 | 18:00 | Lalmonirhat | 41 | 18:00 | Postogola | 54 | 13:00 | Sylhet-132 | 122 | 18:00
15 | Barguna | 16 | 18:00 | Feni | 95 | 18:00 | MI_Cement | 19.4 | 17:00 | Purbachal | 18 | 18:00 | TK | 22.5 | 18:00
16 | Barishal | 100 | 18:00 | GPH | 99 | 19:30 | Madanganj | 30 | 14:00 | Purbasadipur | 93 | 18:30 | Tangail | 194 | 18:30
17 | Barishal-230 | 66 | 18:00 | Ghorashal | 63 | 19:30 | Madaripur | 83 | 21:00 | Rahim | 54 | 13:00 | Thakurgaon | 73 | 18:30
18 | Baroaulia | 58 | 12:00 | Goalpara | 32 | 18:00 | Madartek | 80.56 | 20:00 | Rajbari | 60 | 18:30 | Tongi | 110 | 16:00
19 | Baroirhat | 47 | 18:00 | Gollamari | 46 | 18:30 | Madunaghat | 44 | 18:30 | Rajendrapur | 88 | 19:00 | Ullon | 38 | 13:00
20 | Bashundhara | 143 | 18:00 | Gopalganj | 87.2 | 18:30 | Magura | 52 | 18:00 | Rajshahi | 121 | 20:00 | Uttara | 61 | 13:00
21 | BashundharaCement | 6 | 00:00 | Gulshan | 112 | 14:00 | Mahasthangarh | 60 | 18:00 | Rajshahi-230 | 29 | 20:00 | UttaraNew | 42 | 18:00
22 | Beanibazar | 54 | 18:00 | Halishahar | 96.5 | 15:00 | Manikganj | 101 | 19:30 | Ramganj | 100 | 18:00 | Zigatola | 81 | 18:30
23 | Benapole | 50 | 18:00 | HaripurSBU | 159 | 15:00 | Maniknagar | 68 | 18:00 | Rampur | 24 | 18:00
24 | Bhaluka | 128 | 21:00 | Hasnabad | 83 | 19:00 | Matarbari | 1 | 12:00 | Rangamati | 16 | 18:00
25 | Bhandaria | 40 | 21:00 | Hathazari | 60 | 18:30 | Matuail | 58 | 18:00 | Rangpur | 117 | 18:30
26 | Bhangura | 26 | 18:00 | Ishurdi | 68 | 18:30 | Millgate | 93 | 16:00 | Ruppur | 5.6 | 09:00
27 | Bheramara(GK) | 54 | 18:00 | Jaldhaka | 58 | 18:00 | Mirpur | 123 | 18:00 | SSM | 2 | 11:00
28 | Bhulta | 260 | 15:00 | Jamalpur | 143 | 18:30 | Mirsorai | 3 | 11:00 | Saidpur | 90 | 18:30
29 | Bog-Sherpur | 52 | 18:30 | Jashore | 115 | 18:00 | Mithapukur | 40 | 16:00 | Satkhira | 100 | 18:30
30 | Bogura | 141 | 18:30 | Jhenaidah | 109 | 18:00 | Modern | 0 | 00:00 | Satmasjid | 98 | 13:00
31 | Borhanuddin | 45 | 21:00 | Joydebpur | 181 | 18:30 | Mogbazar | 106.4 | 16:00 | Savar | 176 | 18:00
32 | Brahmanbaria | 147 | 19:00 | Joypurhat | 45 | 18:30 | Mongla | 28 | 18:00 | SevenRings | 8.86 | 17:00
33 | Cantonment | 116 | 18:00 | Juldah | 17 | 15:00 | Motijheel | 36 | 12:00 | ShahCement | 35 | 11:00
34 | Chandpur | 61 | 18:00 | KSRM | 41 | 19:00 | Munshiganj | 85 | 18:00 | Shahjadpur | 88 | 18:30
35 | Chandraghona | 24 | 21:00 | Kabirpur | 271 | 18:30 | Mymensingh | 204 | 18:00 | Shahjibazar | 97 | 18:00
36 | Chapai | 55 | 19:00 | Kachua | 62 | 19:00 | Naogaon | 106 | 18:30 | Shahmirpur | 27.5 | 23:00
37 | Charsaidpur | 26 | 02:00 | Kallyanpur | 102 | 13:00 | Narail | 48 | 18:30 | Shariatpur | 64 | 20:00
38 | Chauddagram | 52 | 18:00 | Kalurghat | 32 | 18:00 | Narinda | 65 | 13:00 | Sherpur | 122 | 19:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-10-25 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 399 | 03:00 | 387 | 16:00 | Gopalganj | 407 | 04:00 | 397 | 16:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 383 | 01:00 | 370 | 11:00
| Bhulta | 400 | 03:00 | 388 | 11:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 408 | 18:30 | 399 | 10:00 | Payra | 415 | 02:00 | 410 | 16:00
| BIPTC | 406 | 04:00 | 394 | 15:00 | Rahanpur | 412 | 04:00 | 402 | 13:00
| Bogura | N/A | N/A | N/A | N/A | Rampal | 408 | 03:00 | 398 | 13:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 236 | 04:00 | 225 | 16:00 | Hasnabad | 234 | 04:00 | 226 | 12:00
| AKSML | 238 | 22:00 | 226 | 10:00 | Hathazari | 237 | 18:30 | 227 | 09:00
| Aminbazar | 237 | 04:00 | 228 | 11:00 | Ishurdi | 236 | 03:00 | 227 | 21:00
| Ashuganj | 235 | 02:00 | 230 | 11:00 | Jhenaidah | 229 | 03:00 | 217 | 13:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 237 | 03:00 | 227 | 15:00
| Baghabari | 234 | 14:00 | 221 | 10:00 | Keranigonj | 235 | 06:00 | 225 | 12:00
| Barapukuria | 226 | 06:00 | 220 | 00:00 | Khulna(S) | 233 | 03:00 | 225 | 13:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 237 | 02:00 | 232 | 13:00 | Maniknagar | 235 | 06:00 | 227 | 12:00
| Bheramara | 236 | 03:00 | 222 | 10:00 | Meghnaghat | 241 | 02:00 | 235 | 12:00
| Bhulta | 237 | 03:00 | 228 | 11:00 | Mirsorai | 235 | 19:30 | 226 | 10:00
| Bibiana | 235 | 18:30 | 229 | 10:00 | Rajshahi | 233 | 03:00 | 221 | 10:00
| BIPTC | 235 | 03:00 | 223 | 10:00 | Rampal | 232 | 03:00 | 225 | 15:00
| Bogura | 236 | 06:00 | 227 | 13:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 240 | 00:00 | 237 | 12:00 | Rampura | 235 | 04:00 | 225 | 05:00
| BSRM | 237 | 18:30 | 227 | 10:00 | Shikalbaha | 237 | 18:30 | 227 | 10:00
| Cumilla(N) | 233 | 18:30 | 227 | 10:00 | Shyampur | 235 | 04:00 | 225 | 16:00
| Fenchuganj | 238 | 18:30 | 232 | 02:00 | Siddhirganj | 234 | 00:00 | 229 | 09:00
| Ghorashal | 240 | 00:00 | 235 | 08:00 | Sirajgonj | 240 | 04:00 | 234 | 12:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 233 | 03:00 | 227 | 13:00
| GPH | 237 | 18:30 | 227 | 11:00 | Tongi | 232 | 04:00 | 223 | 17:00
| Haripur | 233 | 03:00 | 226 | 15:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 137 | 04:00 | 129 | 11:00 | Lalbag | 135 | 06:00 | 127 | 12:00
| Agargaon | 136 | 03:00 | 129 | 12:00 | Lalmonirhat | 133 | 06:00 | 126 | 12:00
| Agrabad | 137 | 18:30 | 130 | 10:00 | Madanganj | 137 | 05:00 | 123 | 11:00
| AKS | 135 | 00:00 | 128 | 10:00 | Madaripur | 132 | 17:00 | 127 | 14:00
| Aminbazar | 140 | 03:00 | 133 | 12:00 | Madartek | 136 | 02:00 | 130 | 10:00
| Amnura | 136 | 06:00 | 127 | 18:00 | Madunaghat | 138 | 18:00 | 132 | 10:00
| Ashuganj | 140 | 01:00 | 138 | 10:00 | Magura | 140 | 04:00 | 130 | 15:00
| Bagerhat | 135 | 06:00 | 126 | 19:00 | Mahasthangarh | 136 | 06:00 | 130 | 13:00
| Bakulia | 138 | 18:30 | 130 | 11:00 | Manikganj | 132 | 19:00 | 124 | 16:00
| Banani | 138 | 03:00 | 130 | 11:00 | Maniknagar | 137 | 03:00 | 130 | 16:00
| Bangabhaban | 137 | 06:00 | 130 | 16:00 | Matarbari | 137 | 00:00 | 132 | 12:00
| Barapukuria | 140 | 04:00 | 135 | 11:00 | Matuail | 131.8 | 07:00 | 125 | 12:00
| Barguna | 138 | 04:00 | 130 | 05:00 | Millgate | 138 | 02:00 | 128 | 11:00
| Barishal | 136 | 03:00 | 131 | 18:00 | Mirpur | 140 | 06:00 | 130 | 16:00
| Barishal-230 | 136 | 03:00 | 132 | 13:00 | Mithapukur | 136 | 04:00 | 128 | 11:00
| Baroaulia | 138 | 18:30 | 132 | 10:00 | MI_Cement | 137 | 04:00 | 127 | 12:00
| Baroirhat | 134 | 17:00 | 125 | 10:00 | Modern | 138 | 18:30 | 132 | 11:00
| Bashundhara | 139 | 03:00 | 128 | 11:00 | Mogbazar | 138 | 06:00 | 125 | 05:00
| BashundharaCement | 133 | 19:00 | 123 | 11:00 | Mongla | 133 | 17:00 | 126 | 12:00
| Beanibazar | 128 | 05:00 | 125 | 00:00 | Motijheel | 137 | 05:00 | 130 | 16:00
| Benapole | 136 | 06:00 | 126 | 13:00 | Munshiganj | 132 | 17:00 | 124 | 11:00
| Bhaluka | 154 | 09:00 | 120 | 13:00 | Mymensingh | 136 | 22:00 | 117 | 18:00
| Bhandaria | 137 | 08:00 | 126 | 12:00 | Naogaon | 135 | 06:00 | 126 | 13:00
| Bhangura | 141 | 03:00 | 133 | 11:00 | Narail | 138 | 06:00 | 128 | 13:00
| Bheramara | 136 | 03:00 | 129 | 10:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara(GK) | 136 | 06:00 | 129 | 11:00 | Narshingdi | 126 | 03:00 | 116 | 15:00
| Bhulta | 121 | 05:00 | 113 | 10:00 | Natore | 136 | 03:00 | 121 | 14:00
| Bog-Sherpur | 138 | 04:00 | 131 | 13:00 | Nawabganj | 135 | 05:00 | 127 | 12:00
| Bogura | 138 | 06:00 | 130 | 13:00 | Netrakona | 135 | 22:00 | 122 | 18:00
| Bogura-230 | 138 | 06:00 | 130 | 10:00 | New | 138 | 01:00 | 129 | 15:00
| Brahmanbaria | 127 | 07:00 | 119 | 15:00 | Niamatpur | 132 | 17:00 | 124 | 13:00
| Cantonment | 136 | 06:00 | 129 | 11:00 | Noapara | 137 | 04:00 | 129 | 13:00
| Chandpur | 132 | 17:00 | 122 | 00:00 | Pabna | 141 | 03:00 | 127 | 10:00
| Chandraghona | 138 | 18:30 | 133 | 10:00 | Palashbari | 134 | 06:00 | 128 | 12:00
| Chapai | 133 | 07:00 | 128 | 18:00 | Panchagarh | 134 | 06:00 | 117 | 13:00
| Charsaidpur | 133 | 18:30 | 123 | 12:00 | Patuakhali | 138 | 01:00 | 136 | 11:00
| Chauddagram | 132 | 16:00 | 125 | 10:00 | Payra | 140 | 03:00 | 138 | 11:00
| Chhatak | 129 | 04:00 | 124 | 00:00 | PHP | 132 | 17:00 | 123 | 10:00
| Chowmuhani | 129 | 18:30 | 119 | 00:00 | Postogola | 137 | 02:00 | 130 | 12:00
| Chuadanga | 135 | 06:00 | 124 | 13:00 | Purbachal | 139 | 02:00 | 129 | 11:00
| Coxsbazar | 138 | 06:00 | 130 | 10:00 | Purbasadipur | 133 | 06:00 | 122 | 12:00
| Cumilla(N) | 136 | 17:00 | 130 | 10:00 | Rahanpur | 134 | 03:00 | 132 | 00:00
| Cumilla(S) | 134 | 17:00 | 126 | 13:00 | Rahim | 131 | 03:00 | 126 | 11:00
| Daudkandi | 124 | 06:00 | 116 | 11:00 | Rajbari | 132 | 06:00 | 125 | 13:00
| Dhaka | 137 | 03:00 | 130 | 10:00 | Rajendrapur | 133 | 19:00 | 122 | 15:00
| Dhamrai | 134 | 04:00 | 126 | 15:00 | Rajshahi | 136 | 05:00 | 128 | 13:00
| Dhanmondi | 132 | 03:00 | 124 | 11:00 | Rajshahi-230 | 136 | 03:00 | 126 | 13:00
| Dohazari | 140 | 14:00 | 128 | 19:30 | Ramganj | 130 | 17:00 | 117 | 02:00
| Faridpur | 131 | 06:00 | 126 | 13:00 | Rampur | 138 | 18:00 | 131 | 11:00
| Fatullah | 138 | 04:00 | 130 | 12:00 | Rampura | 137 | 03:00 | 130 | 10:00
| Fenchuganj | 133 | 00:00 | 131 | 01:00 | Rangamati | 137 | 07:00 | 133 | 10:00
| Feni | 130 | 17:00 | 124 | 11:00 | Rangpur | 132 | 17:00 | 127 | 13:00
| Ghorashal | 140 | 00:00 | 136 | 08:00 | Ruppur | 138 | 05:00 | 131 | 13:00
| Goalpara | 138 | 06:00 | 129 | 14:00 | Saidpur | 134 | 06:00 | 126 | 12:00
| Gollamari | 137 | 06:00 | 131 | 13:00 | Satkhira | 135 | 06:00 | 127 | 18:00
| Gopalganj | 133 | 06:00 | 127 | 12:00 | Satmasjid | 136 | 04:00 | 129 | 11:00
| Gopalganj-400 | 131 | 04:00 | 127 | 13:00 | Savar | 139 | 06:00 | 131 | 10:00
| Gulshan | 136 | 22:00 | 129 | 11:00 | SevenRings | 140 | 03:00 | 134 | 15:00
| Halishahar | 137 | 18:30 | 130 | 11:00 | ShahCement | 133 | 18:30 | 123 | 12:00
| Haripur | 131 | 03:00 | 126 | 11:00 | Shahjadpur | 143 | 03:00 | 137 | 18:00
| HaripurSBU | 131 | 03:00 | 126 | 11:00 | Shahjibazar | 129 | 00:00 | 121 | 15:00
| Hasnabad | 136 | 00:00 | 130 | 12:00 | Shahmirpur | 138 | 19:30 | 131 | 10:00
| Hathazari | 140 | 18:30 | 132 | 11:00 | Shariatpur | 132 | 04:00 | 127 | 15:00
| Ishurdi | 139 | 06:00 | 131 | 13:00 | Sherpur | 135 | 22:00 | 120 | 07:00
| Jaldhaka | 134 | 05:00 | 119 | 09:00 | Shikalbaha | 127 | 14:00 | 121 | 10:00
| Jamalpur | 139 | 22:00 | 119 | 07:00 | Shikalbaha-230 | 139 | 19:30 | 133 | 11:00
| Jashore | 136 | 06:00 | 127 | 13:00 | Shitalakhya | 137 | 04:00 | 127 | 12:00
| Jhenaidah | 140 | 05:00 | 131 | 13:00 | Sholosohor | 137 | 18:30 | 131 | 10:00
| Jhenaidah-230 | 140 | 03:00 | 132 | 13:00 | Shyampur | 137 | 05:00 | 130 | 12:00
| Joydebpur | 137 | 20:00 | 130 | 15:00 | Shyampur-230 | 138 | 04:00 | 130 | 12:00
| Joypurhat | 134 | 06:00 | 125 | 13:00 | Siddhirganj | 132 | 06:00 | 125 | 11:00
| Juldah | 138 | 18:30 | 130 | 09:00 | Sirajganj | 137 | 06:00 | 130 | 10:00
| Kabirpur | 136 | 04:00 | 126 | 11:00 | Sonargaon | 130 | 17:00 | 123 | 11:00
| Kachua | 132 | 17:00 | 122 | 02:00 | Sreemongol | 128 | 00:00 | 124 | 15:00
| Kaliakoir | 135 | 01:00 | 129 | 11:00 | Sreepur | 128 | 02:00 | 124 | 13:00
| Kallyanpur | 141 | 06:00 | 133 | 12:00 | Srinagar | 135 | 06:00 | 127 | 15:00
| Kalurghat | 138 | 19:00 | 132 | 10:00 | SSM | 140 | 16:00 | 134 | 10:00
| Kamrangirchar | 140 | 04:00 | 128 | 12:00 | Sunamganj | 126 | 04:00 | 122 | 00:00
| Kaptai | N/A | N/A | N/A | N/A | Sylhet | 129 | 07:00 | 127 | 00:00
| Kazla | 137 | 04:00 | 130 | 16:00 | Sylhet-132 | 130 | 05:00 | 127 | 00:00
| Keranigonj | 135 | 04:00 | 128 | 12:00 | Tangail | 133 | 20:00 | 124 | 18:00
| Khagrachori | 137 | 18:30 | 132 | 10:00 | Thakurgaon | 135 | 18:30 | 121 | 13:00
| Khulna | 137 | 06:00 | 130 | 13:00 | TK | 138 | 18:00 | 133 | 09:00
| Khulna(S) | 138 | 06:00 | 131 | 13:00 | Tongi | 139 | 01:00 | 131 | 16:00
| Khulshi | 137 | 22:00 | 130 | 10:00 | Ullon | 136 | 01:00 | 129 | 11:00
| Kishoreganj | 134 | 06:00 | 124 | 16:00 | Uttara | 140 | 04:00 | 132 | 12:00
| Kodda | 136 | 19:30 | 123 | 11:00 | UttaraNew | 139 | 01:00 | 128 | 11:00
| KSRM | 139 | 18:30 | 133 | 00:00 | Zigatola | 134 | 03:00 | 127 | 13:00
| Kulaura | 131 | 01:00 | 129 | 15:00
| Kurigram | 133 | 04:00 | 125 | 13:00
| Kushtia | 135 | 05:00 | 130 | 10:00

## L-Curve
Date | 2023-10-25
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1090 | 6441 | 4522 | 10963 |  |  |  | QF-LDC-11
0:30 | 1092 | 5987.5 | 4368 | 10355.5 | Date: | 2023-10-25
1:00 | 1094 | 5534 | 4214 | 9748
1:30 | 1097 | 5375.5 | 4102 | 9477.5
2:00 | 1100 | 5217 | 3990 | 9207
2:30 | 1060 | 5226.5 | 3939.5 | 9166 | [5 empty] | Gen. at Eve. Peak | 12390 | 12390 MW (19:00 )
3:00 | 1020 | 5236 | 3889 | 9125 | [6 empty] | 19:00
3:30 | 1060 | 5189 | 3807 | 8996 | [5 empty] | Gen. at Day Peak | 10768 | 10768 MW (12:00 )
4:00 | 1100 | 5142 | 3725 | 8867 | [6 empty] | 12:00
4:30 | 1105 | 4975 | 3740 | 8715 | [5 empty] | Highest Generation | 12390
5:00 | 1110 | 4808 | 3755 | 8563 | [6 empty] | 19:00
5:30 | 1105 | 4789 | 3744.5 | 8533.5
6:00 | 1100 | 4770 | 3734 | 8504
6:30 | 1040 | 4866.5 | 3758 | 8624.5
7:00 | 980 | 4963 | 3782 | 8745
7:30 | 975 | 5141 | 3808 | 8949
8:00 | 970 | 5319 | 3834 | 9153
8:30 | 1065 | 5513.5 | 3917.5 | 9431
9:00 | 1160 | 5708 | 4001 | 9709
9:30 | 1183 | 5770 | 4096 | 9866
10:00 | 1206 | 5832 | 4191 | 10023
10:30 | 1198 | 5955.5 | 4355.5 | 10311
11:00 | 1190 | 6079 | 4520 | 10599
11:30 | 1185 | 6201.5 | 4482 | 10683.5
12:00 | 1180 | 6324 | 4444 | 10768
12:30 | 1160 | 6441 | 4505.5 | 10946.5
13:00 | 1140 | 6558 | 4567 | 11125
13:30 | 1140 | 6593 | 4601.5 | 11194.5
14:00 | 1140 | 6628 | 4636 | 11264
14:30 | 1203 | 6702.5 | 4615.5 | 11318
15:00 | 1266 | 6777 | 4595 | 11372
15:30 | 1266 | 6600.5 | 4596.5 | 11197
16:00 | 1266 | 6424 | 4598 | 11022
16:30 | 1246 | 6412.5 | 4486 | 10898.5
17:00 | 1226 | 6401 | 4374 | 10775
17:30 | 913 | 6876.5 | 4663.5 | 11540
18:00 | 600 | 7352 | 4953 | 12305
18:30 | 726 | 7326.5 | 5021 | 12347.5
19:00 | 852 | 7301 | 5089 | 12390
19:30 | 866 | 7231 | 4988 | 12219
20:00 | 856 | 7157 | 4957 | 12114 |  |  |  | Executive Engineer
20:30 | 888 | 7104.5 | 4884.5 | 11989 |  |  |  | Network Operation Division
21:00 | 920 | 7052 | 4812 | 11864
21:30 | 965 | 6915 | 4764 | 11679
22:00 | 1010 | 6778 | 4716 | 11494 |  |  |  |  | Page 6 of 7
22:30 | 1000 | 6669.5 | 4663.5 | 11333
23:00 | 990 | 6561 | 4611 | 11172
23:30 | 1040 | 6501 | 4566.5 | 11067.5
24:00 | 1090 | 6441 | 4522 | 10963
12390 MW (19:00 )
10768 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-10-25 |  | Energy |  | 254057560
QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3331 | 903 | 1803 | 0 | 796 | 3701 | 205 | 0 | 86 | 138 | 0 | 0 | 0
0:30 | 3294.5 | 902 | 1890 | 0 | 474.5 | 3422 | 205.5 | 0 | 43 | 124 | 0 | 0 | 0 |  | Date: | 43762
1:00 | 3258 | 901 | 1977 | 0 | 153 | 3143 | 206 | 0 | 0 | 110 | 0 | 0 | 0
1:30 | 3259.5 | 833.5 | 1881 | 0 | 101.5 | 3088 | 206 | 0 | 0 | 108 | 0 | 0 | 0 | [7 empty] | Total Energy | 254.0576 | 254.0576 | Total Energy Gen 254.058 MKWHr Energy Not Served 0.317 MKWHr Energy Requirement 254.374 MKWHr
2:00 | 3261 | 766 | 1785 | 0 | 50 | 3033 | 206 | 0 | 0 | 106 | 0 | 0 | 0 | [7 empty] | Energy not Served | 0.31654 | 0.31654
2:30 | 3269.5 | 692 | 1808 | 0 | 42 | 3043.5 | 206 | 0 | 0 | 105 | 0 | 0 | 0 | [7 empty] | Energy Requirement | 254.3741 | 254.3741
3:00 | 3278 | 618 | 1831 | 0 | 34 | 3054 | 206 | 0 | 0 | 104 | 0 | 0 | 0
3:30 | 3213 | 618 | 1809.5 | 0 | 34 | 3012.5 | 206 | 0 | 0 | 103 | 0 | 0 | 0
4:00 | 3148 | 618 | 1788 | 0 | 34 | 2971 | 206 | 0 | 0 | 102 | 0 | 0 | 0
4:30 | 3069 | 617.5 | 1770.5 | 0 | 25.5 | 2962.5 | 169 | 0 | 0 | 101 | 0 | 0 | 0
5:00 | 2990 | 617 | 1753 | 0 | 17 | 2954 | 132 | 0 | 0 | 100 | 0 | 0 | 0
5:30 | 2979.5 | 617.5 | 1735 | 0 | 17 | 2955 | 132.5 | 0 | 0 | 97 | 0 | 0 | 0
6:00 | 2969 | 618 | 1717 | 0 | 17 | 2956 | 133 | 0 | 0 | 94 | 0 | 0 | 0
6:30 | 2990.5 | 617.5 | 1759.5 | 0 | 41 | 2958.5 | 133 | 0 | 8 | 92 | 24.5 | 0 | 0 | [6 empty] | Coal
7:00 | 3012 | 617 | 1802 | 0 | 65 | 2961 | 133 | 0 | 16 | 90 | 49 | 0 | 0
7:30 | 3086.5 | 617.5 | 1796 | 0 | 91.5 | 2957 | 170.5 | 0 | 16 | 96 | 118 | 0 | 0 | [5 empty] | Oil
8:00 | 3161 | 618 | 1790 | 0 | 118 | 2953 | 208 | 0 | 16 | 102 | 187 | 0 | 0
8:30 | 3318 | 618 | 1851 | 0 | 127.5 | 2952.5 | 208 | 0 | 16 | 102 | 238 | 0 | 0
9:00 | 3475 | 618 | 1912 | 0 | 137 | 2952 | 208 | 0 | 16 | 102 | 289 | 0 | 0
9:30 | 3444 | 712.5 | 1925 | 0 | 167 | 2945 | 208 | 0 | 16 | 109 | 339.5 | 0 | 0
10:00 | 3413 | 807 | 1938 | 0 | 197 | 2938 | 208 | 0 | 16 | 116 | 390 | 0 | 0
10:30 | 3444 | 855 | 1975.5 | 0 | 236.5 | 3054 | 208 | 0 | 16 | 122 | 400 | 0 | 0
11:00 | 3475 | 903 | 2013 | 0 | 276 | 3170 | 208 | 0 | 16 | 128 | 410 | 0 | 0
11:30 | 3494 | 903 | 2016.5 | 0 | 344.5 | 3158.5 | 208 | 0 | 16 | 131 | 412 | 0 | 0
12:00 | 3513 | 903 | 2020 | 0 | 413 | 3147 | 208 | 0 | 16 | 134 | 414 | 0 | 0
12:30 | 3531.5 | 903 | 1965 | 0 | 555 | 3208 | 206.5 | 0 | 16 | 142 | 419.5 | 0 | 0
13:00 | 3550 | 903 | 1910 | 0 | 697 | 3269 | 205 | 0 | 16 | 150 | 425 | 0 | 0
13:30 | 3550 | 903 | 1910 | 0 | 697 | 3269 | 205 | 0 | 16 | 150 | 425 | 0 | 0
14:00 | 3550 | 903 | 1910 | 0 | 697 | 3269 | 205 | 0 | 16 | 150 | 425 | 0 | 0
14:30 | 3527 | 903 | 1865 | 0 | 831 | 3383 | 205.5 | 0 | 42 | 148 | 344 | 0 | 37.245
15:00 | 3504 | 903 | 1820 | 0 | 965 | 3497 | 206 | 0 | 68 | 146 | 263 | 0 | 74.49
15:30 | 3332 | 903.5 | 1824 | 0 | 995 | 3520.5 | 206 | 0 | 75.5 | 143 | 197.5 | 0 | 62.5525
16:00 | 3160 | 904 | 1828 | 0 | 1025 | 3544 | 206 | 0 | 83 | 140 | 132 | 0 | 50.615
16:30 | 3155.5 | 903.5 | 1775.5 | 0 | 1056 | 3494 | 206 | 0 | 97.5 | 137 | 73.5 | 0 | 61.12
17:00 | 3151 | 903 | 1723 | 0 | 1087 | 3444 | 206 | 0 | 112 | 134 | 15 | 0 | 71.625
17:30 | 3249.5 | 903 | 1782.5 | 0 | 1405.5 | 3568.5 | 206.5 | 0 | 274 | 143 | 7.5 | 0 | 85.8125
18:00 | 3348 | 903 | 1842 | 0 | 1724 | 3693 | 207 | 0 | 436 | 152 | 0 | 0 | 100
18:30 | 3341.5 | 902.5 | 1792.5 | 0 | 1757.5 | 3812.5 | 207 | 0 | 384 | 150 | 0 | 0 | 66.5
19:00 | 3335 | 902 | 1743 | 0 | 1791 | 3932 | 207 | 0 | 332 | 148 | 0 | 0 | 33
19:30 | 3309 | 903 | 1802 | 0 | 1694 | 3846 | 207 | 0 | 310 | 148 | 0 | 0 | 16.5
20:00 | 3315 | 902 | 1765 | 0 | 1646 | 3821 | 207 | 0 | 310 | 148 | 0 | 0 | 0
20:30 | 3333 | 902 | 1827.5 | 0 | 1534 | 3758 | 207 | 0 | 282.5 | 145 | 0 | 0 | 0
21:00 | 3351 | 902 | 1890 | 0 | 1422 | 3695 | 207 | 0 | 255 | 142 | 0 | 0 | 0
21:30 | 3312 | 902.5 | 1825.5 | 0 | 1341.5 | 3700.5 | 207 | 0 | 247 | 143 | 0 | 0 | 0
22:00 | 3273 | 903 | 1761 | 0 | 1261 | 3706 | 207 | 0 | 239 | 144 | 0 | 0 | 0
22:30 | 3267 | 903 | 1782 | 0 | 1140.5 | 3704 | 206.5 | 0 | 187 | 143 | 0 | 0 | 0
23:00 | 3261 | 903 | 1803 | 0 | 1020 | 3702 | 206 | 0 | 135 | 142 | 0 | 0 | 0
23:30 | 3296 | 903 | 1803 | 0 | 908 | 3701.5 | 205.5 | 0 | 110.5 | 140 | 0 | 0 | 0 |  | Max Temp. in Dhaka |  | 33°C
24:00 | 3331 | 903 | 1803 | 0 | 796 | 3701 | 205 | 0 | 86 | 138 | 0 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 254.058 MKWHr Energy Not Served 0.317 MKWHr Energy Requirement 254.374 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-10-25
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 131 | 131 | 131 | 131 | 132 | 133 | 133 | 133 | 133 | 133 | 133 | 133 | 130 | 130 | 131 | 131 | 131 | 132 |  | 132 | 132 | 132 | 132 | 132 | 131 | 130 | 3163047
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 0 |  |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1596000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [15 empty] | 6 | 8 | 17 |  | 17 | 17 | 17 | 17 | 17 | 8 | 8 | 119188
| Teknaf 20MW PP (Solartech) | [8 empty] | 12 | 8 |  | 18 | 18 | 0 | 12 | 7 | 1 | 0 | [8 empty] | 75735
6 | Sikalbaha 225MW CCPP (Gas) | 220 | 202 | 201 | 191 | 189 | 192 | 195 | 195 | 198 | 202 | 216 | 216 | 222 | 225 | 225 | 225 | 226 | 224 |  | 221 | 220 | 221 | 213 | 214 | 201 | 202 | 4865635
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [25 empty] | 0 | 0
12 | Hathazari 100 MW peaking PP | [14 empty] | 17 | 32 | 32 | 37 |  | 73 | 70 | 70 | 70 | 70 | 70 | 70 | 499296
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [11 empty] | 10 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 221636
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 280 | 280 | 280 | 250 | 250 | 250 | 250 | 250 | 300 | 300 | 332 | 327 | 330 | 330 | 326 | 0 | 75 | 214 |  | 154 | 150 | 150 | 150 | 150 | 150 | 150 | 5536730
18 | Kodda 300 MW PP Unit-2 (Summit) | [8 empty] | 2 | 45 | 45 | 45 | 80 | 55 | 45 | 47 | 47 | 95 |  | 45 | 15 | 15 | 15 | 15 | 15 | 0 | 720109
19 | Ashuganj 195 MW PP (APSCL-United) | [25 empty] | 0 | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 170 | 130 | 130 | 130 | 100 | 100 | 108 | 130 | 130 | 131 | 128 | 145 | 170 | 170 | 170 | 140 | 140 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 3456531
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 374 | 368 | 369 | 369 | 370 | 371 | 370 | 370 | 370 | 335 | 311 | 311 | 311 | 310 | 311 | 310 | 312 | 312 |  | 311 | 310 | 310 | 311 | 310 | 310 | 310 | 8012726
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 148968
33 | Ashuganj 225 MW CCPP | 180 | 174 | 173 | 176 | 152 | 151 | 151 | 181 | 178 | 208 | 180 | 184 | 194 | 182 | 164 | 159 | 167 | 175 |  | 177 | 181 | 180 | 180 | 180 | 183 | 185 | 4304000
34 | Ashuganj 450 MW CCPP(South) | 275 | 290 | 275 | 240 | 220 | 220 | 220 | 220 | 355 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 6045000
| Ashuganj 450 MW CCPP(North) | 270 | 310 | 270 | 270 | 270 | 270 | 290 | 295 | 280 | 325 | 280 | 285 | 295 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 7245400
| Ashuganj 420 MW CCPP(East) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5867500
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 373 | 356 | 407 | 350 | 307 | 307 | 297 | 306 | 336 | 338 | 386 | 410 | 410 | 413 | 398 | 410 | 397 | 353 |  | 391 | 385 | 385 | 395 | 392 | 335 | 397 | 8980480
| Meghnaghat Unique power | 390 | 140 | 103 | 300 | 380 | 405 | 405 | 400 | 397 | 400 | 300 | 300 | 200 | 200 | 150 | 150 | 150 | 184 |  | 160 | 188 | 156 | 180 | 153 | 189 | 160 | 5622272
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 170 | 225 | 225 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4853000
41 | Haripur 360 MW CCPP(HPL) | 276 | 285 | 335 | 276 | 245 | 245 | 265 | 265 | 286 | 287 | 337 | 331 | 333 | 303 | 333 | 332 | 281 | 333 |  | 301 | 303 | 301 | 337 | 300 | 285 | 285 | 7186000
42 | RPCL 210MW CCPP | 73 | 73 | 73 | 73 | 46 | 46 | 30 | 31 | 30 | 29 | 28 | 27 | 13 | 13 | 12 | 12 | 12 | 12 |  | 23 | 23 | 30 | 32 | 38 | 69 | 73 | 820800
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 3 | 33 | 40 | 42 | 42 | 53 | 50 | 40 | 32 | 14 | 1 | 0 | [8 empty] | 336380
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1020000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 18 | 18 | 61 | 61 | 61 | 58 | 59 | 58 | 55 | 55 | 50 | 51 | 56 | 56 |  | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 1213344
48 | Shahjibazar 86 MW PP (Shahjibazar) | 50 | 50 | 50 | 20 | [21 empty] | 0 | 192960
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP |  | 20 | 22 | 22 | 57 | 30 | 30 | 130 | 145 | 145 | 140 | 140 | 135 | 135 | 135 | 135 | 140 | 135 |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 2380640
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 16 | 16 | 16 | 17 | 17 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 396000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 |  |  |  |  | 10 | 10 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 211320
54 | Hobiganj 11 MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 144318
55 | Fenchugonj 51 MW PP (Barakatullah) | [25 empty] | 0 | 0
56 | Shahjahanulla 25 MW PP | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 8 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 354768
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 285 | 300 | 280 | 210 | 170 | 220 | 280 | 285 | 310 | 310 | 300 | 310 | 285 | 290 | 300 | 280 | 280 |  | 250 | 275 | 275 | 285 | 265 | 260 | 280 | 6748500
| Bibiyana South 400 MW | 290 | 300 | 320 | 320 | 330 | 330 | 330 | 330 | 330 | 330 | 300 | 300 | 300 | 300 | 300 | 295 | 290 | 290 |  | 290 | 280 | 280 | 285 | 285 | 310 | 310 | 7323100
58 | Nababganj 55 MW PP (Southern power ) | [15 empty] | 17 | 17 | 35 |  | 55 | 55 | 55 | 55 | 35 | 0 | 0 | 265198
59 | Tangail Palli Power Gen 22 MW | 6 | [9 empty] | 5 | 6 | 6 | 6 | 6 | 6 | 7 | 12 |  | 12 | 12 | 12 | 6 | 6 | 6 | 6 | 114720
60 | Barabkunda 22 MW PP (Regent) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 12 | 12 | 12 | 10 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 264912
61 | Narshingdi 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 |  |  | 18 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 17 |  | 17 | 17 | 17 | 18 | 18 | 18 | 18 | 339228
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 19 |  | 15 | 0 |  | 19 | 19 | 19 | 19 | 407628
63 | Impoprt (Tripura) | 110 | 106 | 104 | 102 | 100 | 94 | 90 | 102 | 102 | 116 | 128 | 134 | 150 | 146 | 146 | 140 | 134 | 152 |  | 148 | 148 | 148 | 142 | 144 | 142 | 138 | 2979840
64 | Malancha, Ctg. EPZ (United) | 14 | 25 | 25 | 30 | 30 | 30 | 24 | 6 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 4 | 5 | 10 | 6 | 11 | 15 | 273600
65 | Feni 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 18 | 18 | 18 | 18 | 401976
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 7 | 7 | 7 | 6 | 6 | 9 | 9 | 9 | 9 | 10 |  | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 224820
67 | Jangalia 33 MW PP (Summit) | 25 | 25 | 25 | 25 | 0 | 0 | 0 | 0 |  |  |  |  | 4 | 16 | 17 | 25 | 25 | 25 |  | 25 | 25 | 30 | 33 | 33 | 33 | 33 | 412900
68 | Cumilla 25 MW PP (Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 6 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 291300
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456000
70 | Summit Madhabdi | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 281880
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 699500
72 | Rupganj 33 MW PP(Summit) | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 16 | 30 | 28 | 22 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 668800
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | [10 empty] | 20 | 34 | 34 | 34 | 70 | 52 | 34 | 70 |  | 70 | 34 | 34 | 17 | 17 | 17 | 17 | 477660
| Chowmuhani 113 MW | 9 | [9 empty] | 7 | 13 | 27 | 28 | 29 | 28 | 29 | 76 |  | 76 | 76 | 78 | 78 | 46 | 46 | 37 | 658560
| Manikgonj 162MW PP(MPGL) | [12 empty] | 17 | 17 | 17 | 35 | 35 | 72 |  | 72 | 72 | 35 | 17 | 17 | 17 | 0 | 360000
77 | Siddhirganj 100 PP(Dutch Bangla) | [12 empty] | 7 | 9 | 17 | 17 | 18 | 33 |  | 33 | 33 | 33 | 26 | 26 | 9 | 9 | 224170
78 | Gazipur 52 MW PP | [6 empty] | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 12 |  | 20 | 25 | 25 | 25 | 25 | 8 | 8 | 207360
79 | Kodda 150 MW PP | [6 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 133 |  | 98 | 82 | 82 | 64 | 48 | 48 | 16 | 660960
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [14 empty] | 21 | 24 | 24 | 24 |  | 16 | 16 | 16 | 8 | 8 | 8 | 8 | 170947
| Gazipur 100 MW PP | [8 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 70 |  | 70 | 70 | 70 | 34 | 34 | 34 | 17 | 617280
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 1 | 2 | 1 | 4 | 2 | 1 | 0 | 0 | [10 empty] | 11520
| Jodiac Power | [12 empty] | 8 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 213402
| Karnaphuli Power Ltd. | [11 empty] | 12 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 230000
82 | Madanganj 102 PP(Summit) | [12 empty] | 14 | 60 | 65 | 67 | 85 | 85 |  | 75 | 48 | 42 | 34 | 34 | 34 | 17 | 552044
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [16 empty] | 8 | 44 |  | 28 | 25 | 25 | 25 | 25 | 0 | 0 | 154935
86 | Meghnaghat CCPP ( Summit) | 142 | 150 | 143 | 143 | 120 | 120 | 143 | 145 | 150 | 149 | 150 | 149 | 148 | 150 | 149 | 148 | 147 | 146 |  | 148 | 150 | 146 | 145 | 143 | 146 | 153 | 3491316
87 | Meghnaghat 100 MW(IEL) | [11 empty] | 1 | 14 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 23 | 8 | 268800
| Meghnaghat 104 MW PP (OPCL) | [16 empty] | 6 | 16 |  | 16 | 17 | 16 | 17 | 0 |  | 0 | 75840
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [11 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 132240
92 | Fenchuganj 44 MW (Energyprima) | 47 | 10 | 10 | 10 | [6 empty] | 10 | 40 | 39 | 44 | 40 | 41 | 42 | 45 |  | 43 | 43 | 43 | 43 | 49 | 49 | 49 | 638352
93 | Ashuganj 51 MW PP (Midland) | 10 | 10 | 10 | 10 |  |  |  |  | 0 | 5 | 19 | 51 | 51 | 51 | 51 | 51 | 30 | 42 |  | 51 | 51 | 51 | 51 | 43 | 51 | 51 | 733152
94 | Gagnagar 102 MW PP (Digital Power) | [12 empty] | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 193104
95 | Patenga 50MW PP (Baraka) | [11 empty] | 0 | 6 | 6 | 6 | 6 | 6 | 18 |  | 19 | 19 | 20 | 20 | 20 | 20 | 10 | 148800
96 | Chattogram 108 MW PP (ECPV) | [20 empty] | 0 |  |  |  |  | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [13 empty] | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 170073
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 17 |  | 35 | 35 | 35 | 17 | 0 |  | 0 | 97849
101 | Kushiara 163 MW CCPP (KP) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 |  | 130 | 130 | 130 | 163 | 130 | 130 | 130 | 3475718
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 2 | 1 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 14000
103 | Kamalaghat 54 MW PP(Banco Energy) | [16 empty] | 17 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 229680
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 18 | [5 empty] | 5 | 19 | 19 | 28 | 38 | 37 | 37 | 37 | 37 | 19 | 19 | 19 |  | 112 | 112 | 112 | 112 | 112 | 18 | 18 | 808800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | [5 empty] | 3 | 17 | 17 | 17 | 17 | 17 | 21 | 27 | 29 | 30 | 18 | 19 |  | 88 | 100 | 99 | 79 | 72 | 72 | 48 | 730656
115 | Juldah 100 MW PP Unit-3 (Acorn) | [10 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 162240
116 | Chandpur 200 MW (Desh energy) | 17 | [12 empty] | 7 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 215520
117 | Ashuganj 150 MW PP (Midland) | [12 empty] | 2 | 6 | 10 | 10 | 15 | 30 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 182327
118 | Bibiyana-III 400 MW CCPP | 342 | 341 | 342 | 341 | 341 | 341 | 352 | 352 | 402 | 401 | 403 | 398 | 405 | 403 | 404 | 404 | 370 | 400 |  | 401 | 401 | 401 | 402 | 352 | 342 | 343 | 8979000
| Jamalpur 115 MW PP (United) | 32 | 16 |  |  |  |  | 38 | 57 | 57 | 47 | 57 | 57 | 66 | 66 | 66 | 56 | 57 | 57 |  | 85 | 85 | 85 | 85 | 85 | 56 | 56 | 1189200
| Anwara 300 MW PP (United) | [10 empty] | 15 | 85 | 150 | 200 | 106 | 106 | 106 | 222 |  | 232 | 232 | 233 | 158 | 160 | 161 | 160 | 1994727
| Juldah unit-2 (Acorn) | [11 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 144960
| Anlima Energy Ltd. | [12 empty] | 27 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 414000
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 443880
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 2 | 12 | 18 | 33 | 33 | 33 | 32 | 14 | 20 | 10 | 1 | 0 | [8 empty] | 217277
| Chandpur 115(Doreen) | 17 | [11 empty] | 30 | 35 | 35 | 40 | 64 | 75 |  | 76 | 77 | 70 | 58 | 58 | 64 | 63 | 706560
| Kanchan Purbachal Power Generation Ltd. | 20 | 17 | 17 | 17 | [13 empty] | 6 |  | 17 | 17 | 17 | 17 | 17 | 13 | 17 | 190080
| Mirsharai 150 MW (Oil) | [13 empty] | 35 | 35 | 35 | 35 | 100 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 327854
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480
| Matarbari 2*600 MW (CPGCL) | 142 | 144 | 142 | 142 | 142 | 144 | 146 | 142 | 138 | 197 | 351 | 344 | 344 | 345 | 544 | 545 | 546 | 550 |  | 550 | 550 | 549 | 548 | 551 | 550 | 552 | 8087272
120 | Eastern Zone Total | 5534 | 5217 | 5236 | 5142 | 4808 | 4770 | 4963 | 5319 | 5708 | 5832 | 6079 | 6324 | 6558 | 6628 | 6777 | 6424 | 6401 | 7352 |  | 7301 | 7231 | 7157 | 7052 | 6778 | 6561 | 6441 | 146746280
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [14 empty] | 7 | 16 | 16 | 20 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 147840
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 13 | 30 |  | 32 | 27 | 27 | 26 | 26 | 0 |  | 148320
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [14 empty] | 17 | 18 | 25 | 36 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 288960
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 6 | 41 | 45 | 81 | 87 | 56 | 88 | 61 | 51 | 26 | 4 | 0 | [8 empty] | 565920
131 | Rampal 1320 MW (BIFPCL) | 771 | 768 | 803 | 806 | 794 | 795 | 794 | 786 | 791 | 751 | 755 | 701 | 711 | 711 | 709 | 711 | 714 | 709 |  | 715 | 709 | 703 | 708 | 724 | 722 | 724 | 17963637
132 | United Payra Power Ltd. | [17 empty] | 3 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 105600
133 | Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 180 | 160 | 160 | 170 | 170 | 170 | 170 | 220 | 220 | 220 | 220 | 220 | 220 | 200 | 220 |  | 220 | 220 | 220 | 220 | 200 | 200 | 200 | 4919700
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [19 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 92064
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3752700
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 90 | 90 | 90 | 90 | 80 | 80 | 80 | 80 | 80 | 80 | 130 | 130 | 130 | 130 | 130 | 130 | 90 | 124 |  | 124 | 130 | 124 | 124 | 92 | 100 | 100 | 2483000
140 | Bhola 33 MW PP (Venture) | 21 | 20 | 20 | 19 | 18 | 17 | 15 | 14 | 14 | 15 | 16 | 19 | 19 | 19 | 18 | 17 | 17 | 23 |  | 23 | 23 | 23 | 23 | 24 | 24 | 24 | 457800
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [16 empty] | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40875
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [17 empty] | 32 |  | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 118824
146 | Bheramara HVDC | 901 | 766 | 618 | 618 | 617 | 618 | 617 | 618 | 618 | 807 | 903 | 903 | 903 | 903 | 903 | 904 | 903 | 903 |  | 902 | 903 | 902 | 902 | 903 | 903 | 903 | 19280000
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 520 | 520 | 520 | 520 | 520 | 520 | 520 | 520 | 520 | 520 | 520 | 520 | 570 | 600 | 600 | 600 | 540 | 700 |  | 900 | 840 | 820 | 740 | 740 | 740 | 740 | 16418300
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4187300
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 1 | 2 | 4 | 5 | 5 | 5 | 5 | 4 | 3 | 2 | 0 | [9 empty] | 37860
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 140 | 140 | 140 | 145 | 152 | 152 | 151 | 150 | 151 | 151 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3679782
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 257 | 275 | 300 | 220 | 300 | 280 | 270 | 220 | 308 | 259 | 255 | 212 | 192 | 191 | 171 | 171 | 178 | 171 |  | 180 | 180 | 180 | 198 | 213 | 223 | 221 | 5501600
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [25 empty] | 0 | 0
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 229482
165 | Amnura 50 MW PP(Sinha) | [20 empty] | 0 | [5 empty] | 0
166 | Katakhali 50 MW PP (Northern) | [15 empty] | 8 | 8 | 24 |  | 8 | 8 | 8 | 8 | 8 | 0 |  | 63049
167 | Katakhali 50 MW Peaking PP | [17 empty] | 29 |  | 35 | 36 | 36 | 0 |  |  |  | 84719
168 | Santahar 50 MW Peaking PP | [17 empty] | 37 |  | 37 | 38 | 38 | 38 | 38 | 0 |  | 189075
169 | Natore 52 MW PP (Rajlanka) | [15 empty] | 8 | 16 | 16 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 88090
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 70 |  | 40 | 40 | 40 | 40 | 40 | 0 | 0 | 229344
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [12 empty] | 5 | 32 | 35 | 35 | 35 | 46 |  | 35 | 35 | 35 | 35 | 0 |  | 0 | 351360
172 | Confidence Power Bogura Unit-1 113 MW | [13 empty] | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 0 |  | 0 | 315456
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [13 empty] | 38 | 34 | 35 | 35 | 80 |  | 54 | 34 | 34 | 34 | 34 | 34 | 0 | 426518
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 2 |  | 6 | 6 | 7 | 6 | 5 | 4 | 2 | 0 | [9 empty] | 38130
178 | Energypac Power Venture Thakurgaon Ltd. | [14 empty] | 24 | 50 | 35 | 54 |  | 35 | 35 | 35 | 35 | 35 | 35 | 0 | 435456
| Intraco Solar 30 MW | [6 empty] | 5 | 7 | 26 | 33 | 36 | 37 | 35 | 30 | 22 | 10 | 1 | 0 | [8 empty] | 250330
| Adani Power Jharkhanda Ltd | 1016 | 913 | 900 | 814 | 808 | 806 | 811 | 815 | 813 | 815 | 913 | 951 | 1013 | 1015 | 1013 | 1058 | 1012 | 1102 |  | 1136 | 1117 | 1119 | 1068 | 1061 | 1060 | 1055 | 23050909
178 | Teesta Solar Limited | [6 empty] | 32 | 88 | 141 | 178 | 198 | 200 | 187 | 160 | 118 | 60 | 7 | 0 | [8 empty] | 1369280