## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-10-29 | Sunday
|  | Date (day): | 2023-10-29 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11557.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14344 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-10-28 | 2023-10-29 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 180 | 130 | 180
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  |  | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 417 | 420 | 400 | 412
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 325 | 327 | 330 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | GT-1 under S/D due to Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 5 | 8 | 8 | 8 | 92 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 152 | 152 | 150 | 150 | 185 |  | GT-1 under S/D due to Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 52 | 85 | 97
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 10 | 45 | 30 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 9 | 8 | 8 | 92 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 254 | 260 | 250 | 300 |  | 35
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 8 | 8 | 8 | 94 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 0 | 17 | 37 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 48 | 16 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 0 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 0 | 55
| Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
25 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 31 | 31 | 32 | 32 |  | 48 | Engine problem
26 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
27 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 32 | 30 | 33 | 33
28 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 25 | 8 | 25 | 27 |  | Fuel shortage
29 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
30 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 10 | 15 | 80 | 130 | 170 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
31 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 82 | 17 | 136 | 13 |  | Fuel shortage
32 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 34 | 35 | 88 |  | 17 | Engine problem
33 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 17 | 0 | 17 | 87 |  | Fuel shortage
34 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 35 | 17 | 35 | 127 |  | Fuel shortage
35 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 30 | 0 | 35 | 0
36 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 100 | 63 | 100 | 100
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 5763 | 5422 | 1858 | 2191 | 2098 | 2736 | 1743 | 864
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
38 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 3 | 8 | 17 | 8 |  | Fuel shortage
39 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 6 | 19 | 31 |  | Fuel shortage
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 206 | 205 | 205 | 205 |  | 25 | Engine problem
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 215 | 210 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 17 | 17 | 88 |  | Fuel shortage
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 66 | 40 | 70 | 28 |  | Fuel shortage
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 34 | 17 | 34 |  | 68 | Engine problem
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 10 | 12 | 12 | 12 | 88 |  | Fuel shortage
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 12 | 12 | 12 | 12 | 10 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 1 | 20 | 10 | 20
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 100 | 150 | 100 | 270 |  | 30 | Engine problem
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 17 | 17 | 17 | 37 |  | Fuel shortage
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 11 | 17 | 17 | 17 | 93 |  | Fuel shortage
55 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
56 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 3 | 34 | 17 | 34 | 82 |  | Fuel shortage
57 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 17 | 35 | 163
58 | SS Power I |  | Coal | SS Power | 1*612 | 612 | 612 | 325 | 602 | 480 | 600 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 1 | 2 | 10 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 199 | 193 | 180 | 180 |  |  | On test.
| Chattogram area Total |  |  |  |  | 3217 | 3157 | 1165 | 1659 | 1442 | 1936 | 929 | 453
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 163 | 188 | 190 | 200 | 21 |  | Gas shortage
60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 280 | 275 | 300 |  |  | FGMO
61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 240 | 250 | 260 |  |  | FGMO
62 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 250 | 230 | 250 | 250 | 150 |  | Gas shortage
63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 0 | 0 | 0 | 45 |  | Gas shortage
| Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortae
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 66 | 6 | 150
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 30
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 17 | 17 | 17 | 183 |  | Fuel shortage
70 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 16 | 18 | 18 |  | 4 | Engine problem
71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 9 | 9 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 130 | 158 | 143 | 166
72 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 16 | 52 | 52
74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 17 | 17 | 17 | 97 |  | Fuel shortage
76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 7 | 37 | 28 | 78 | 35 |  | Fuel shortage
77 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 35 |  | 19 | Engine problem
78 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 18 | 90 | 18 | 90 | 25 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2896 | 1258 | 1477 | 1388 | 1770 | 751 | 199
79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 32 | 33 | 30 | 45 | 157 |  | Gas shortage
80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 16 | 16 | 19 |  | 3 | Engine problem
| Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 8 | 64 | 66 | 100 | 100 |  | Fuel shortage
83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 87 | 40 | 85 | 30 |  | Fuel shortage
84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 51 | 0 | 50 | 0
85 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 6 | 12 | 10 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 155 | 206 | 209.6 | 261 | 157 | 3
86 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
87 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Under maint.
88 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
89 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
90 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0
91 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 42 | 42 | 42 | 42
92 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 2 | 2 | 2 |  | 9 | Engine problem
93 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 57 | 50 | 62
94 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 0 | 0 | 0 | 86 |  | Gas shortage
95 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 192 | 191 | 180 | 190 |  | 41 | Machine problem
97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 16 | 18 | 17 | 18
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 9 |  | Gas shortage
99 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 270 | 300 | 300 |  |  | FGMO
100 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 365 | 367 | 400 | 400
101 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
102 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 310 | 310 | 300 | 310
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1520 | 1489 | 1523 | 1556 | 95 | 597
103 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 897 | 802 | 902 | 902
104 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 49 | 65 | 50 |  | Fuel shortage
105 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 40 |  | 14 | Engine problem
106 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
107 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 | 49 |  | Fuel shortage
108 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
109 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 0 | 16 | 24 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
110 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 53 | 74 | 31 |  | Fuel shortage
111 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 9 | 15 | 32 | 73 |  | Fuel shortage
112 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 84 | 0 | 100 | 0
113 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0
114 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 354 | 352 | 350 | 400
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 1335 | 1171 | 1469 | 1589 | 883 | 14
115 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 16 | 110
116 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 16 | 23 | 21 | 25 |  | 15 | Engine problem
117 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 130 | 128 | 130 | 130 |  | 64 | ST under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 700 | 1210 | 800 | 1244
119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 222 | 220 | 220
120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 38 | 150
121 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 150 | 150 | 150 | 150 | 157 |  | Coal shortage
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1216 | 1733 | 1375 | 2029 | 157 | 79
122 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
123 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 30 | 22 |  | Fuel shortage
124 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 16 |  | 55 | Engine problem
125 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 28 | 28
126 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 34 | 42 |  | 8 | Engine problem
127 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 40 |  | 10 | Engine problem
128 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 160 | 148 | 150 | 160 | 50 |  | Gas shortage
129 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
130 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
131 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 212 | 250 | 300 | 154 |  | Gas shortage
132 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 24 | 35 | 15 |  | Fuel shortage
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
133 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
134 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 8 | 8 | 44 |  | Fuel shortage
135 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 25 | 50 | 94 |  | 10 | Engine problem
136 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
137 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 30 | 35 | 50 | 63 |  | Fuel shortage
138 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 35 | 55 | 58 |  | Fuel shortage
139 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 813 | 1161 | 950 | 1200 | 296
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 1392 | 1622 | 1611 | 2069 | 1513 | 83
140 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
141 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
142 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
143 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
144 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 45 | 34 | 113
145 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
146 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 35 | 70 | 115
147 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 35 | 0 | 30 | 0
148 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 189 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 400 | 250 | 442 | 398 | 125 | 189
| Total |  |  |  |  | 25339 | 24599 | 10299 | 11798 | 11557.6 | 14344 | 6353 | 2481
A. |  | 2023-10-28 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 11798 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 8411 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11798 | MW
3 | Day peak Generation : |  |  | 10299 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11398.71 | MW
4 | Evening peak Generation : |  |  | 11798 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 238.6589 | MKWHr | By Solar | 2.7458 | MKWHr
| By Gas : | 118.1487 | MKWHr |  | By Oil: | 13.1951 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 74.8707 | MKWHr |  | By Hydro: | 4.9694 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.05232 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6353 | MW | Dhaka | 4354.51 | 4354.51 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2481 | MW | Chittagong | 1215.9 | 1215.9 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 8834 | MW | Khulna | 1308.6 | 1308.6 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 937.45 | MMCFD |  |  | Rajshahi | 1084 | 1084 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 121058900.572 | ii) Oil : | Taka | 173121253.92 | Comilla | 1114 | 1114 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 521796290.1 | Total | Taka | 815976444.592 | Mymensingh | 863 | 863 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 487 | 487 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 900 | MW (W to E) at | 19:00 | hrs | Barisal | 333.7 | 333.7 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 870 | MW at | 19:30 | hrs | Rangpur | 638 | 638 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33°C |  |  | Total | 11398.71 | 11398.71 |  | 0
B. |  | 2023-10-29 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 33°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 13000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14344 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10800 | MW
4 | Reserve(Generation end) |  |  |  | 1344 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 262.9739 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8502 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.4531 | MKWHr. | ii) HVDC Flow at Peak Time |  | 802 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.2237 | MKWHr. | iii) Maximum HVDC Flow : |  | 897 | MW at | 11:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 103.27 |  | (b) Today: | 103.02 |  | (c) Rule Curve: |  | 108.7
.

## YesterdayGen
2023-10-28 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 415 | 342 |  | 0 | 170 | 146 | 0 | 0 | 0 | 277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 33 | 33 | 0 | 0 | 131 | 75 | 0 | 0 | 0 | 188 | 0 | 0 | 0 |  | 0 | 74 | 17 | 12 | 0 | 6 | 12 | 42 | 0 | 0 | 0 | 280 | 270 | 174 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 42 | 18 | 11 | 33 | 12 | 126 | 106 | 0 | 19 | 0 | 43 | 0 | 0 | 49 | 163 | 0 | 57 | 70 | 0 | 20 | 18 | 0 | 10 | 270 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 332 | 8 | 0 | 17 | 0 | 45 | 0 | 17 | 17 | 0 | 12 | 300 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 18 | 0 | 240 | 0 | 0 | 420 | 1 | 256 | 44 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 740 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 150 | 1013 | 0 | 0 |  | 5752 | 4065 | 9817 | 3363 | 896 | 1788 | 0 | 245 | 3101 | 206 | 0 | 91 | 126 | 0 | 1 | 0 | 103.37
2:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 416 | 342 |  | 0 | 170 | 148 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 33 | 0 | 0 | 131 | 75 | 0 | 0 | 0 | 188 | 0 | 0 | 0 |  | 0 | 74 | 17 | 12 | 0 | 6 | 12 | 42 | 0 | 0 | 0 | 280 | 270 | 176 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 11 | 33 | 12 | 124 | 106 | 0 | 19 | 0 | 43 | 0 | 0 | 49 | 130 | 0 | 40 | 83 | 0 | 20 | 18 | 0 | 10 | 265 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 17 | 0 | 332 | 8 | 0 | 17 | 0 | 45 | 0 | 17 | 17 | 0 | 12 | 310 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 18 | 0 | 230 | 0 | 0 | 420 | 2 | 260 | 94 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 150 | 913 | 0 | 0 |  | 5703 | 3803 | 9506 | 3293 | 896 | 1813 | 0 | 215 | 2866 | 206 | 0 | 91 | 124 | 0 | 2 | 0 | 103.35
3:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 368 | 252 |  | 0 | 170 | 145 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 33 | 0 | 0 | 130 | 75 | 0 | 0 | 0 | 188 | 0 | 0 | 0 |  | 0 | 74 | 17 | 12 | 0 | 6 | 12 | 42 | 0 | 0 | 0 | 280 | 270 | 177 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 0 | 33 | 12 | 122 | 106 | 0 | 19 | 0 | 43 | 0 | 0 | 49 | 130 | 0 | 40 | 83 | 0 | 20 | 18 | 0 | 10 | 260 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 17 | 0 | 332 | 8 | 0 | 17 | 0 | 45 | 0 | 17 | 17 | 0 | 12 | 305 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 18 | 0 | 230 | 0 | 0 | 420 | 2 | 258 | 40 | 0 |  | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 150 | 910 | 0 | 0 |  | 5483 | 3720 | 9203 | 3210 | 895 | 1641 | 0 | 215 | 2822 | 205 | 0 | 91 | 122 | 0 | 2 | 0 | 103.33
4:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 309 | 251 |  | 0 | 170 | 149 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 16 | 0 | 0 | 131 | 75 | 0 | 0 | 0 | 189 | 0 | 0 | 0 |  | 0 | 74 | 17 | 0 | 0 | 0 | 12 | 42 | 0 | 0 | 0 | 280 | 270 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 33 | 12 | 118 | 106 | 0 | 0 | 0 | 43 | 0 | 0 | 20 | 130 | 0 | 40 | 30 | 0 | 53 | 18 | 0 | 10 | 265 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 332 | 8 | 0 | 17 | 0 | 15 | 0 | 17 | 17 | 0 | 0 | 310 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 0 | 320 | 0 | 223 | 50 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 150 | 821 | 0 | 0 |  | 5126 | 3571 | 8697 | 3147 | 896 | 1517 | 0 | 125 | 2597 | 206 | 0 | 91 | 118 | 0 | 0 | 0 | 103.31
5:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 305 | 237 |  | 0 | 170 | 138 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 16 | 0 | 0 | 131 | 75 | 0 | 0 | 0 | 188 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 12 | 42 | 0 | 0 | 0 | 280 | 270 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 33 | 12 | 114 | 106 | 0 | 0 | 0 | 43 | 0 | 0 | 20 | 130 | 0 | 40 | 0 | 0 | 60 | 18 | 0 | 9 | 285 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 8 | 0 | 17 | 0 | 15 | 0 | 15 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 0 | 320 | 0 | 202 | 96 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 150 | 817 | 0 | 0 |  | 4993 | 3567 | 8560 | 3156 | 896 | 1526 | 0 | 72 | 2573 | 206 | 0 | 17 | 114 | 0 | 0 | 0 | 103.29
6:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 302 | 231 |  | 0 | 170 | 122 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 33 | 0 | 0 | 131 | 75 | 0 | 0 | 0 | 188 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 12 | 42 | 0 | 0 | 0 | 280 | 240 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 33 | 12 | 104 | 105 | 0 | 0 | 0 | 43 | 0 | 0 | 5 | 120 | 0 | 40 | 0 | 0 | 65 | 18 | 0 | 10 | 285 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 8 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 9 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 0 | 320 | 1 | 201 | 97 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 150 | 818 | 0 | 0 |  | 4864 | 3547 | 8411 | 3105 | 896 | 1460 | 0 | 49 | 2573 | 206 | 0 | 17 | 104 | 0 | 1 | 0 | 103.27
7:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 324 | 246 |  | 0 | 170 | 144 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 13 | 25 | 33 | 0 | 0 | 132 | 75 | 0 | 0 | 0 | 188 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 12 | 42 | 0 | 0 | 0 | 320 | 315 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 33 | 12 | 108 | 71 | 0 | 0 | 0 | 43 | 0 | 0 | 5 | 120 | 0 | 40 | 0 | 0 | 80 | 17 | 0 | 10 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 363 | 16 | 0 | 0 | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 8 | 0 | 0 | 0 | 17 | 4 | 0 | 0 | 250 | 0 | 0 | 320 | 1 | 201 | 100 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 180 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 354 | 3 | 150 | 818 | 23 | 0 |  | 5084 | 3610 | 8694 | 3247 | 896 | 1542 | 0 | 51 | 2573 | 207 | 0 | 17 | 108 | 52 | 1 | 0 | 103.25
8:00 | 0 | 0 | 132 | 0 | 0 | 0 | 0 | 341 | 281 |  | 0 | 170 | 148 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 13 | 25 | 33 | 0 | 0 | 132 | 75 | 0 | 0 | 0 | 188 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 12 | 17 | 0 | 0 | 0 | 300 | 290 | 189 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 18 | 8 | 33 | 12 | 114 | 32 | 0 | 0 | 1 | 43 | 0 | 0 | 5 | 120 | 0 | 40 | 0 | 0 | 90 | 17 | 0 | 10 | 310 | 16 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 10 | 10 | 0 | 0 | 0 | 362 | 35 | 0 | 0 | 2 | 15 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 23 | 0 | 0 | 0 | 17 | 12 | 0 | 0 | 250 | 0 | 0 | 325 | 0 | 199 | 100 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 600 | 180 | 0 | 0 | 1 | 31 | 0 | 0 | 0 | 355 | 13 | 150 | 819 | 75 | 0 |  | 5129 | 3778 | 8907 | 3192 | 896 | 1608 | 0 | 85 | 2618 | 207 | 0 | 17 | 114 | 170 | 0 | 0 | 103.24
9:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 380 | 281 |  | 0 | 200 | 150 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 33 | 2 | 0 | 132 | 75 | 0 | 0 | 0 | 208 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 12 | 1 | 0 | 0 | 0 | 280 | 270 | 175 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 8 | 33 | 12 | 116 | 33 | 0 | 14 | 2 | 43 | 0 | 0 | 5 | 163 | 0 | 40 | 0 | 0 | 100 | 17 | 0 | 9 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 19 | 0 | 17 | 15 | 12 | 0 | 0 | 335 | 56 | 17 | 0 | 1 | 45 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 33 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 250 | 0 | 0 | 325 | 0 | 196 | 82 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 610 | 180 | 0 | 0 | 3 | 55 | 0 | 0 | 0 | 357 | 22 | 150 | 822 | 125 | 0 |  | 5281 | 3885 | 9166 | 3181 | 896 | 1653 | 0 | 185 | 2630 | 207 | 0 | 17 | 116 | 281 | 0 | 0 | 103.23
10:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 398 | 281 |  | 0 | 200 | 150 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 32 | 8 | 0 | 132 | 75 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 12 | 1 | 0 | 0 | 0 | 280 | 270 | 175 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 8 | 33 | 12 | 120 | 33 | 0 | 14 | 2 | 43 | 0 | 0 | 5 | 163 | 0 | 40 | 0 | 0 | 107 | 17 | 0 | 9 | 275 | 8 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 18 | 12 | 0 | 0 | 336 | 45 | 17 | 0 | 4 | 45 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 46 | 0 | 0 | 0 | 17 | 28 | 0 | 0 | 250 | 0 | 0 | 325 | 0 | 197 | 100 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 600 | 180 | 0 | 0 | 4 | 71 | 0 | 0 | 0 | 357 | 29 | 150 | 820 | 165 | 0 |  | 5322 | 3941 | 9263 | 3205 | 896 | 1657 | 0 | 169 | 2619 | 207 | 0 | 17 | 120 | 373 | 0 | 0 | 103.22
11:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 413 | 307 |  | 0 | 225 | 152 | 0 | 0 | 0 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 33 | 32 | 8 | 0 | 132 | 75 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 12 | 1 | 0 | 0 | 0 | 300 | 270 | 163 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 18 | 8 | 33 | 12 | 132 | 33 | 0 | 14 | 2 | 43 | 0 | 0 | 45 | 163 | 0 | 30 | 0 | 0 | 125 | 17 | 0 | 9 | 310 | 8 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 20 | 12 | 0 | 0 | 376 | 45 | 17 | 2 | 4 | 65 | 0 | 0 | 0 | 0 | 12 | 310 | 0 | 51 | 0 | 0 | 0 | 17 | 30 | 2 | 1 | 250 | 0 | 0 | 324 | 1 | 199 | 100 | 0 |  | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 640 | 180 | 0 | 0 | 4 | 81 | 0 | 0 | 0 | 355 | 34 | 150 | 817 | 182 | 0 |  | 5679 | 4038 | 9717 | 3365 | 897 | 1823 | 0 | 206 | 2655 | 207 | 0 | 17 | 132 | 414 | 1 | 0 | 103.21
12:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 417 | 325 |  | 0 | 225 | 152 | 5 | 0 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 33 | 32 | 8 | 0 | 131 | 75 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 0 | 17 | 10 | 0 | 0 | 12 | 1 | 0 | 0 | 0 | 280 | 270 | 163 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 9 | 33 | 12 | 130 | 32 | 0 | 17 | 2 | 43 | 0 | 0 | 42 | 163 | 0 | 58 | 0 | 0 | 192 | 16 | 0 | 10 | 300 | 16 | 5 | 0 | 10 | 0 | 0 | 8 | 0 | 17 | 20 | 12 | 0 | 0 | 365 | 45 | 17 | 17 | 4 | 100 | 0 | 11 | 0 | 7 | 12 | 310 | 0 | 51 | 17 | 3 | 0 | 17 | 30 | 18 | 17 | 250 | 0 | 0 | 325 | 1 | 199 | 100 | 0 |  | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 700 | 220 | 0 | 0 | 5 | 84 | 0 | 0 | 0 | 354 | 35 | 150 | 813 | 189 | 0 |  | 5956 | 4343 | 10299 | 3541 | 897 | 2019 | 0 | 351 | 2711 | 206 | 0 | 17 | 130 | 426 | 1 | 0 | 103.2
13:00 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 413 | 327 |  | 0 | 225 | 145 | 9 | 0 | 5 | 251 | 0 | 0 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 11 | 33 | 16 | 8 | 0 | 130 | 75 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 17 | 12 | 0 | 0 | 12 | 1 | 0 | 0 | 0 | 280 | 240 | 168 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 9 | 33 | 12 | 148 | 32 | 0 | 17 | 2 | 42 | 0 | 0 | 42 | 70 | 0 | 58 | 0 | 0 | 178 | 16 | 0 | 10 | 310 | 16 | 5 | 0 | 42 | 0 | 0 | 28 | 0 | 17 | 19 | 12 | 1 | 3 | 365 | 68 | 17 | 17 | 4 | 100 | 0 | 17 | 0 | 21 | 12 | 310 | 0 | 49 | 17 | 17 | 0 | 17 | 28 | 17 | 19 | 230 | 0 | 0 | 325 | 4 | 193 | 90 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 810 | 220 | 0 | 0 | 4 | 78 | 0 | 0 | 0 | 353 | 32 | 150 | 848 | 175 | 0 |  | 5937 | 4444 | 10381 | 3492 | 896 | 1884 | 0 | 477 | 2849 | 205 | 0 | 29 | 148 | 397 | 4 | 0 | 103.19
14:00 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 379 | 273 |  | 0 | 225 | 150 | 8 | 51 | 15 | 253 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 12 | 33 | 30 | 8 | 0 | 130 | 75 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 3 | 24 | 17 | 12 | 0 | 0 | 12 | 1 | 0 | 0 | 0 | 280 | 240 | 185 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 9 | 33 | 12 | 148 | 31 | 0 | 16 | 2 | 42 | 0 | 0 | 43 | 70 | 0 | 61 | 0 | 0 | 188 | 16 | 0 | 10 | 265 | 16 | 5 | 0 | 76 | 0 | 0 | 28 | 0 | 17 | 16 | 12 | 17 | 26 | 343 | 79 | 30 | 17 | 3 | 80 | 17 | 17 | 0 | 28 | 12 | 310 | 0 | 41 | 17 | 34 | 0 | 17 | 23 | 18 | 34 | 230 | 17 | 0 | 325 | 5 | 193 | 94 | 0 |  | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 910 | 180 | 0 | 0 | 3 | 60 | 0 | 0 | 0 | 353 | 27 | 150 | 861 | 149 | 0 |  | 6066 | 4383 | 10449 | 3452 | 895 | 1688 | 0 | 690 | 2962 | 205 | 0 | 74 | 148 | 330 | 5 | 0 | 103.21
15:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 387 | 239 |  | 0 | 225 | 150 | 9 | 45 | 15 | 260 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 33 | 30 | 8 | 0 | 130 | 75 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 6 | 31 | 17 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 305 | 240 | 183 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 9 | 33 | 12 | 156 | 33 | 0 | 16 | 1 | 42 | 0 | 0 | 41 | 110 | 0 | 58 | 0 | 0 | 192 | 16 | 0 | 10 | 300 | 16 | 5 | 0 | 15 | 0 | 0 | 28 | 0 | 0 | 12 | 12 | 17 | 41 | 388 | 79 | 35 | 17 | 2 | 80 | 17 | 17 | 0 | 28 | 12 | 310 | 0 | 29 | 17 | 34 | 0 | 17 | 16 | 17 | 34 | 230 | 17 | 0 | 326 | 3 | 195 | 100 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 940 | 222 | 0 | 0 | 2 | 37 | 0 | 0 | 0 | 350 | 19 | 150 | 914 | 106 | 0 |  | 6154 | 4381 | 10535 | 3561 | 896 | 1731 | 0 | 629 | 3045 | 205 | 0 | 81 | 156 | 228 | 3 | 0 | 103.17
16:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 402 | 252 |  | 0 | 225 | 151 | 8 | 17 | 15 | 260 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 33 | 30 | 8 | 0 | 130 | 75 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 6 | 32 | 17 | 12 | 0 | 0 | 12 | 2 | 0 | 0 | 0 | 300 | 240 | 181 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 9 | 33 | 12 | 150 | 33 | 0 | 16 | 1 | 42 | 0 | 0 | 43 | 120 | 0 | 58 | 0 | 0 | 192 | 16 | 0 | 10 | 300 | 16 | 5 | 0 | 15 | 0 | 0 | 18 | 0 | 17 | 6 | 12 | 17 | 6 | 393 | 60 | 35 | 17 | 1 | 80 | 17 | 17 | 0 | 28 | 12 | 310 | 0 | 14 | 17 | 34 | 0 | 17 | 7 | 18 | 17 | 230 | 17 | 0 | 325 | 6 | 196 | 100 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 860 | 222 | 0 | 0 | 1 | 18 | 0 | 0 | 0 | 351 | 8 | 150 | 917 | 46 | 0 |  | 6071 | 4198 | 10269 | 3571 | 896 | 1749 | 0 | 537 | 2969 | 205 | 0 | 82 | 150 | 104 | 6 | 0 | 103.16
17:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 407 | 327 |  | 0 | 225 | 150 | 9 | 17 | 15 | 257 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 18 | 19 | 11 | 33 | 16 | 8 | 0 | 130 | 75 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 32 | 17 | 12 | 0 | 2 | 12 | 15 | 0 | 0 | 0 | 280 | 240 | 188 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 15 | 9 | 33 | 12 | 144 | 33 | 0 | 16 | 0 | 42 | 0 | 0 | 41 | 163 | 0 | 59 | 0 | 0 | 192 | 17 | 0 | 10 | 300 | 16 | 5 | 0 | 15 | 0 | 0 | 18 | 0 | 17 | 1 | 12 | 17 | 6 | 367 | 59 | 35 | 17 | 0 | 80 | 17 | 17 | 0 | 28 | 12 | 310 | 0 | 2 | 17 | 34 | 0 | 17 | 1 | 18 | 17 | 230 | 17 | 0 | 365 | 5 | 199 | 100 | 0 |  | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 840 | 222 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 352 | 1 | 150 | 918 | 6 | 0 |  | 6171 | 4098 | 10269 | 3519 | 895 | 1856 | 0 | 555 | 2994 | 205 | 0 | 82 | 144 | 14 | 5 | 0 | 103.15
18:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 406 | 327 |  | 0 | 225 | 154 | 8 | 22 | 15 | 260 | 0 | 0 | 9 | 8 | 75 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 18 | 19 | 12 | 33 | 30 | 10 | 0 | 130 | 75 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 6 | 33 | 19 | 12 | 0 | 19 | 12 | 15 | 0 | 0 | 0 | 355 | 240 | 179 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 3 | 16 | 8 | 33 | 12 | 158 | 33 | 0 | 16 | 0 | 43 | 0 | 0 | 45 | 163 | 0 | 56 | 0 | 0 | 192 | 17 | 0 | 10 | 310 | 16 | 5 | 0 | 42 | 0 | 0 | 38 | 0 | 27 | 0 | 12 | 17 | 28 | 399 | 77 | 70 | 17 | 0 | 150 | 17 | 17 | 17 | 28 | 12 | 310 | 0 | 0 | 24 | 34 | 0 | 17 | 0 | 41 | 28 | 230 | 53 | 0 | 490 | 8 | 200 | 100 | 0 |  | 896 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 130 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 15 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 19 | 0 | 9 | 15 | 107 | 0 | 0 | 35 | 920 | 222 | 0 | 13 | 0 | 0 | 32 | 0 | 0 | 350 | 0 | 150 | 1080 | 0 | 0 |  | 6864 | 4642 | 11506 | 3630 | 896 | 1840 | 0 | 1130 | 3360 | 205 | 0 | 279 | 158 | 0 | 8 | 0 | 103.14
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 420 | 327 |  | 0 | 225 | 152 | 8 | 52 | 15 | 260 | 0 | 0 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 18 | 19 | 12 | 33 | 30 | 25 | 0 | 130 | 75 | 0 | 0 | 3 | 215 | 0 | 0 | 0 |  | 6 | 66 | 34 | 12 | 0 | 19 | 12 | 20 | 0 | 0 | 0 | 280 | 240 | 188 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 16 | 16 | 9 | 33 | 12 | 158 | 33 | 0 | 16 | 0 | 43 | 0 | 0 | 42 | 163 | 0 | 57 | 0 | 0 | 191 | 18 | 0 | 10 | 270 | 16 | 2 | 0 | 15 | 0 | 0 | 64 | 0 | 82 | 0 | 12 | 17 | 66 | 367 | 87 | 34 | 17 | 0 | 150 | 17 | 17 | 17 | 37 | 12 | 310 | 17 | 0 | 35 | 34 | 0 | 17 | 0 | 90 | 35 | 230 | 17 | 0 | 602 | 2 | 193 | 63 | 0 |  | 802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 128 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 30 | 9 | 45 | 0 | 0 | 35 | 1210 | 222 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 352 | 0 | 150 | 1161 | 0 | 0 |  | 7022 | 4776 | 11798 | 3547 | 802 | 1780 | 0 | 1276 | 3838 | 205 | 0 | 190 | 158 | 0 | 2 | 0 | 103.11
19:30 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 424 | 335 |  | 0 | 225 | 152 | 8 | 25 | 15 | 260 | 0 | 0 | 9 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 18 | 19 | 12 | 33 | 30 | 8 | 0 | 132 | 75 | 0 | 0 | 8 | 208 | 0 | 0 | 0 |  | 6 | 66 | 34 | 12 | 0 | 19 | 12 | 17 | 0 | 0 | 0 | 280 | 240 | 193 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 15 | 9 | 33 | 12 | 150 | 43 | 0 | 19 | 0 | 43 | 0 | 0 | 42 | 163 | 0 | 57 | 0 | 0 | 191 | 18 | 0 | 10 | 272 | 16 | 2 | 0 | 15 | 0 | 0 | 37 | 0 | 72 | 0 | 12 | 17 | 6 | 367 | 89 | 34 | 34 | 0 | 150 | 17 | 17 | 17 | 38 | 12 | 310 | 17 | 0 | 35 | 34 | 0 | 17 | 0 | 71 | 35 | 230 | 17 | 0 | 612 | 2 | 196 | 73 | 0 |  | 802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 128 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 35 | 0 | 40 | 0 | 0 | 35 | 1244 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 150 | 1161 | 0 | 0 |  | 6909 | 4742 | 11651 | 3561 | 802 | 1799 | 0 | 1081 | 3884 | 207 | 0 | 165 | 150 | 0 | 2 | 0 | 0
20:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 422 | 334 |  | 0 | 225 | 153 | 8 | 17 | 0 | 260 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 18 | 19 | 12 | 33 | 30 | 8 | 0 | 132 | 75 | 0 | 0 | 8 | 208 | 0 | 0 | 0 |  | 6 | 66 | 34 | 12 | 0 | 19 | 12 | 20 | 0 | 0 | 0 | 280 | 240 | 199 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 16 | 9 | 33 | 12 | 152 | 51 | 0 | 19 | 0 | 43 | 0 | 0 | 42 | 163 | 0 | 57 | 0 | 0 | 191 | 18 | 0 | 10 | 270 | 16 | 2 | 0 | 0 | 0 | 0 | 24 | 0 | 73 | 0 | 12 | 17 | 0 | 367 | 89 | 34 | 34 | 0 | 120 | 17 | 17 | 17 | 38 | 12 | 310 | 17 | 0 | 17 | 34 | 0 | 17 | 0 | 62 | 35 | 230 | 17 | 0 | 613 | 2 | 198 | 87 | 0 |  | 802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 35 | 0 | 18 | 0 | 0 | 0 | 1244 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 150 | 1169 | 0 | 0 |  | 6820 | 4688 | 11508 | 3576 | 802 | 1814 | 0 | 894 | 3896 | 207 | 0 | 165 | 152 | 0 | 2 | 0 | 103.12
21:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 422 | 336 |  | 0 | 225 | 150 | 0 | 16 | 0 | 245 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 18 | 19 | 12 | 33 | 30 | 8 | 0 | 132 | 75 | 0 | 0 | 8 | 207 | 0 | 0 | 0 |  | 6 | 75 | 34 | 12 | 0 | 19 | 12 | 35 | 0 | 0 | 0 | 280 | 240 | 196 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 17 | 9 | 33 | 12 | 146 | 70 | 0 | 19 | 0 | 43 | 0 | 0 | 45 | 163 | 0 | 57 | 0 | 0 | 191 | 17 | 0 | 10 | 290 | 16 | 2 | 0 | 0 | 0 | 0 | 24 | 0 | 43 | 0 | 12 | 17 | 0 | 367 | 75 | 17 | 34 | 0 | 120 | 17 | 17 | 17 | 39 | 12 | 310 | 17 | 0 | 0 | 34 | 0 | 17 | 0 | 50 | 17 | 230 | 0 | 0 | 624 | 1 | 198 | 86 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 150 | 1169 | 0 | 0 |  | 6652 | 4581 | 11233 | 3574 | 896 | 1866 | 0 | 673 | 3745 | 207 | 0 | 125 | 146 | 0 | 1 | 0 | 103.11
22:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 421 | 261 |  | 0 | 225 | 148 | 0 | 0 | 0 | 244 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 18 | 19 | 12 | 33 | 30 | 0 | 0 | 132 | 75 | 0 | 0 | 8 | 208 | 0 | 0 | 0 |  | 6 | 75 | 34 | 12 | 0 | 19 | 12 | 37 | 0 | 0 | 0 | 280 | 240 | 193 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 17 | 10 | 33 | 12 | 146 | 70 | 0 | 19 | 0 | 43 | 0 | 0 | 45 | 163 | 0 | 57 | 0 | 0 | 191 | 18 | 0 | 10 | 280 | 16 | 2 | 0 | 0 | 0 | 0 | 24 | 0 | 17 | 0 | 12 | 17 | 0 | 367 | 69 | 17 | 34 | 0 | 120 | 17 | 17 | 17 | 39 | 12 | 300 | 17 | 0 | 0 | 34 | 0 | 17 | 0 | 36 | 17 | 230 | 0 | 0 | 612 | 1 | 196 | 40 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 150 | 1173 | 0 | 0 |  | 6375 | 4487 | 10862 | 3484 | 896 | 1744 | 0 | 603 | 3656 | 207 | 0 | 125 | 146 | 0 | 1 | 0 | 103.1
23:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 386 | 262 |  | 0 | 225 | 150 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 18 | 19 | 12 | 25 | 30 | 0 | 0 | 132 | 75 | 0 | 0 | 8 | 208 | 0 | 0 | 0 |  | 5 | 75 | 17 | 12 | 0 | 19 | 12 | 38 | 0 | 0 | 0 | 310 | 240 | 196 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 17 | 10 | 33 | 12 | 144 | 77 | 0 | 19 | 0 | 43 | 0 | 0 | 48 | 163 | 0 | 56 | 0 | 0 | 190 | 18 | 0 | 10 | 260 | 16 | 2 | 0 | 0 | 0 | 0 | 24 | 0 | 17 | 0 | 12 | 17 | 0 | 354 | 65 | 17 | 34 | 0 | 120 | 17 | 17 | 17 | 16 | 12 | 310 | 0 | 0 | 0 | 34 | 0 | 17 | 0 | 34 | 17 | 230 | 0 | 0 | 624 | 4 | 199 | 100 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 150 | 1078 | 0 | 0 |  | 6362 | 4241 | 10603 | 3472 | 896 | 1743 | 0 | 556 | 3473 | 207 | 0 | 108 | 144 | 0 | 4 | 0 | 103.09
24:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 345 | 261 |  | 0 | 225 | 151 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 18 | 19 | 12 | 25 | 30 | 0 | 0 | 132 | 75 | 0 | 0 | 8 | 208 | 0 | 0 | 0 |  | 3 | 66 | 17 | 12 | 0 | 8 | 12 | 36 | 0 | 0 | 0 | 280 | 240 | 190 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 17 | 8 | 33 | 12 | 140 | 77 | 0 | 19 | 0 | 43 | 0 | 0 | 45 | 163 | 0 | 56 | 0 | 0 | 190 | 18 | 0 | 10 | 315 | 14 | 2 | 0 | 0 | 0 | 0 | 24 | 0 | 17 | 0 | 12 | 17 | 0 | 330 | 65 | 17 | 34 | 0 | 120 | 17 | 17 | 17 | 16 | 12 | 310 | 0 | 0 | 0 | 34 | 0 | 17 | 0 | 34 | 17 | 230 | 0 | 0 | 624 | 6 | 200 | 83 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 150 | 1036 | 0 | 0 |  | 6267 | 4101 | 10368 | 3369 | 896 | 1776 | 0 | 543 | 3332 | 207 | 0 | 99 | 140 | 0 | 6 | 0 | 103.08
KWH | 0 | 0 | 3555344 | 0 | 0 | 0 | 0 | 9304060 | 698000 |  | 0 | 4875500 | 3546182 | 73920 | 184466 | 115564 | 5776348 | 0 | 0 | 54144 | 54144 | 284640 | 0 | 0 | 0 | 0 | 128520 | 77080 | 47980 | 404820 | 456000 | 282960 | 706680 | 680400 | 129010 | 0 | 3149416 | 1820000 | 0 | 0 | 45819 | 4878319 | 0 | 0 | 0 |  | 62160 | 839760 | 479474 | 165600 | 0 | 151200 | 284880 | 559680 | 0 | 0 | 0 | 7325600 | 6284000 | 4403000 | 0 | 0 | 0 | 0 | 0 | 776556 | 0 | 0 | 141154 | 408204 | 190620 | 814700 | 29520 | 3223680 | 1391040 | 0 | 322452 | 13850 | 1011000 | 0 | 0 | 803664 | 3296945 | 0 | 1226016 | 282240 | 0 | 1966570 | 400000 | 0 | 245160 | 9026000 | 368016 | 102816 | 0 | 371345 | 0 | 0 | 396000 | 0 | 458064 | 137700 | 234240 | 282720 | 194036 | 8588000 | 1166400 | 430080 | 409818 | 27480 | 1886836 | 218688 | 318653 | 196080 | 384720 | 215040 | 7412600 | 62400 | 351250 | 187200 | 486764 | 0 | 443520 | 203511 | 544320 | 329400 | 5828100 | 143855 | 0 | 10129090 | 52320 | 5083636 | 1785000 | 0 |  | 21453090 | 0 | 0 | 0 | 28800 | 0 | 0 | 0 | 0 | 0 | 18375 | 2445000 | 445200 | 0 | 0 | 0 | 0 | 0 | 0 | 70816 | 0 | 0 | 20008 | 0 | 49150 | 0 | 0 | 132966 | 0 | 0 | 4144700 | 0 | 0 | 3767045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6210836 | 115200 | 0 | 94944 | 23184 | 170275 | 0 | 41004 | 79296 | 20746900 | 4850700 | 0 | 26400 | 31740 | 466560 | 103872 | 0 | 0 | 8494545 | 225803 | 3687300 | 22584511 | 1246940 | 0 |  | 136883739 | 101775160 | 238658899 | 80747076 | 21453090 | 37401663 | 0 | 11307431 | 74870682 | 4969416 | 0 | 1887703 | 3223680 | 2745838 | 52320 | 0
Fuel Cost | 0 | 0 | 5190802.24 | 0 | 0 | 0 | 0 | 9769263 | 753840 |  | 0 | 5314295 | 3936262.02 | 826425.6 | 2444174.5 | 1531223 | 6469509.76 | 0 | 0 | 791585.28 | 761806.08 | 4614014.4 | 0 | 0 | 0 | 0 | 1634774.4 | 1040580 | 643411.8 | 303615 | 342000 | 0 | 0 | 0 | 2194460.1 | 0 | 850342.32 | 491400 | 0 | 0 | 749140.65 | 5073451.76 | 0 | 0 | 0 |  | 811188 | 14007196.8 | 8160647.48 | 2237256 | 0 | 1749384 | 361797.6 | 1863734.4 | 0 | 0 | 0 | 8131416 | 6849560 | 5107480 | 0 | 0 | 0 | 0 | 0 | 1296848.52 | 0 | 0 | 1898521.3 | 559239.48 | 142965 | 1425725 | 22140 | 23146022.4 | 1516233.6 | 0 | 438534.72 | 220769 | 1385070 | 0 | 0 | 1390338.72 | 3791486.75 | 0 | 2378471.04 | 643507.2 | 0 | 1986235.7 | 860000 | 0 | 485416.8 | 9026000 | 276012 | 78140.16 | 0 | 5068859.25 | 0 | 0 | 5338080 | 0 | 6344186.4 | 1609713 | 2417356.8 | 3861955.2 | 2574857.72 | 7900960 | 14183424 | 6218956.8 | 5184197.7 | 427588.8 | 22151454.64 | 2381512.32 | 3387281.39 | 2660805.6 | 4959040.8 | 2533171.2 | 6819592 | 808080 | 5075562.5 | 2375568 | 5539374.32 | 0 | 5792371.2 | 2431956.45 | 8148470.4 | 4338198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 64359270 | 0 | 0 | 0 | 299808 | 0 | 0 | 0 | 0 | 0 | 264048.75 | 2738400 | 863688 | 0 | 0 | 0 | 0 | 0 | 0 | 1107562.24 | 0 | 0 | 338335.28 | 0 | 829160.5 | 0 | 0 | 100655.262 | 0 | 0 | 35147056 | 0 | 0 | 4369772.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6148727.64 | 1548288 | 0 | 1123187.52 | 335008.8 | 2162492.5 | 0 | 453094.2 | 962653.44 | 172199270 | 4947714 | 0 | 195360 | 358979.4 | 5472748.8 | 1592357.76 | 0 | 0 | 77215414.05 | 0 | 44136981 | 193097569.05 | 0 | 0 |  | 298506289.07 | 622367602.392 | 920873891.462 | 80597041.522 | 64359270 | 40461859.05 | 0 | 144064337.22 | 521796290.1 | 1341742.32 | 0 | 29056916.7 | 23146022.4 | 16050412.15 | 0 | 0
Yesterday Day Peak | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 417 | 325 |  | 0 | 225 | 152 | 5 | 0 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 33 | 32 | 8 | 0 | 131 | 75 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 0 | 17 | 10 | 0 | 0 | 12 | 1 | 0 | 0 | 0 | 280 | 270 | 163 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 9 | 33 | 12 | 130 | 32 | 0 | 17 | 2 | 43 | 0 | 0 | 42 | 163 | 0 | 58 | 0 | 0 | 192 | 16 | 0 | 10 | 300 | 16 | 5 | 0 | 10 | 0 | 0 | 8 | 0 | 17 | 20 | 12 | 0 | 0 | 365 | 45 | 17 | 17 | 4 | 100 | 0 | 11 | 0 | 7 | 12 | 310 | 0 | 51 | 17 | 3 | 0 | 17 | 30 | 18 | 17 | 250 | 0 | 0 | 325 | 1 | 199 | 100 | 0 |  | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 700 | 220 | 0 | 0 | 5 | 84 | 0 | 0 | 0 | 354 | 35 | 150 | 813 | 189 | 0 |  | 10299 | DayPeak
Yesterday Evening Peak | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 420 | 327 |  | 0 | 225 | 152 | 8 | 52 | 15 | 260 | 0 | 0 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 18 | 19 | 12 | 33 | 30 | 25 | 0 | 130 | 75 | 0 | 0 | 3 | 215 | 0 | 0 | 0 | 0 | 6 | 66 | 34 | 12 | 0 | 19 | 12 | 20 | 0 | 0 | 0 | 280 | 240 | 188 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 16 | 16 | 9 | 33 | 12 | 158 | 33 | 0 | 16 | 0 | 43 | 0 | 0 | 42 | 163 | 0 | 57 | 0 | 0 | 191 | 18 | 0 | 10 | 270 | 16 | 2 | 0 | 15 | 0 | 0 | 64 | 0 | 82 | 0 | 12 | 17 | 66 | 367 | 87 | 34 | 17 | 0 | 150 | 17 | 17 | 17 | 37 | 12 | 310 | 17 | 0 | 35 | 34 | 0 | 17 | 0 | 90 | 35 | 230 | 17 | 0 | 602 | 2 | 193 | 63 | 0 |  | 802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 128 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 30 | 9 | 45 | 0 | 0 | 35 | 1210 | 222 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 352 | 0 | 150 | 1161 | 0 | 0 |  | 11798 | EvPeak
Forecast for Evening | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 412 | 330 |  | 0 | 225 | 150 | 8 | 97 | 15 | 300 | 0 | 0 | 8 | 8 | 149 | 45 | 0 | 0 | 0 | 17 | 35 | 55 | 18 | 19 | 13 | 33 | 33 | 25 | 0 | 130 | 75 | 0 | 0 | 17 | 215 | 0 | 0 | 0 |  | 12 | 70 | 34 | 12 | 0 | 19 | 12 | 20 | 0 | 0 | 0 | 300 | 260 | 200 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 30 | 52 | 18 | 11 | 33 | 12 | 166 | 45 | 0 | 19 | 0 | 43 | 0 | 0 | 42 | 163 | 0 | 62 | 0 | 0 | 190 | 18 | 0 | 10 | 300 | 16 | 2 | 0 | 130 | 0 | 0 | 100 | 0 | 136 | 0 | 12 | 17 | 150 | 400 | 85 | 88 | 17 | 0 | 270 | 17 | 17 | 17 | 78 | 12 | 310 | 17 | 0 | 35 | 34 | 0 | 35 | 0 | 90 | 55 | 250 | 163 | 0 | 600 | 10 | 180 | 100 | 0 |  | 902 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 40 | 60 | 16 | 130 | 25 | 110 | 0 | 0 | 0 | 30 | 16 | 94 | 28 | 42 | 40 | 8 | 35 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 74 | 0 | 50 | 32 | 113 | 0 | 0 | 55 | 1244 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 400 | 0 | 150 | 1200 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 400 | 330 | 0 | 0 | 225 | 150 | 8 | 85 | 15 | 250 | 0 | 0 | 8 | 8 | 16 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 13 | 33 | 33 | 8 | 0 | 130 | 75 | 0 | 0 | 8 | 210 |  | 0 | 0 | 0 | 6 | 40 | 17 | 12 | 0 | 6 | 12 | 10 | 0 | 0 | 0 | 275 | 250 | 190 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 11 | 33 | 12 | 143 | 30 | 0 | 16 | 1.6 | 43 | 0 | 0 | 42 | 163 | 0 | 50 | 0 | 0 | 180 | 17 | 0 | 10 | 300 | 16 | 2 | 0 | 80 | 0 | 0 | 66 | 0 | 17 | 20 | 12 | 17 | 6 | 400 | 40 | 35 | 17 | 5 | 100 | 17 | 17 | 17 | 28 | 12 | 300 | 0 | 50 | 17 | 17 | 0 | 17 | 35 | 18 | 55 | 250 | 35 |  | 480 | 10 | 180 | 100 | 0 |  | 902 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 28 | 34 | 30 | 8 | 24 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 53 | 0 | 35 | 15 | 34 | 0 | 8 | 35 | 800 | 220 |  | 38 | 6 | 100 | 70 | 0 |  | 350 | 30 | 150 | 950 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 364 | 262 | 0 | 0 | 170 | 147 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 13 | 25 | 31 | 0 | 0 | 131 | 75 | 0 | 0 | 3 | 195 | 0 | 0 | 0 | 0 | 2 | 0 | 17 | 0 | 0 | 0 | 12 | 9 | 0 | 0 | 0 | 270 | 240 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 33 | 12 | 104 | 34 | 0 | 19 | 1 | 43 | 0 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 190 | 17 | 0 | 10 | 280 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 10 | 0 | 0 | 0 | 364 | 57 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 22 | 0 | 0 | 0 | 17 | 12 | 0 | 0 | 240 | 0 | 0 | 320 | 0 | 200 | 76 | 0 | 0 | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 640 | 220 | 0 | 0 | 2 | 30 | 0 | 0 | 0 | 355 | 14 | 150 | 817 | 80 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
[22 empty] | 299565 | [26 empty] | 399366 | [49 empty] | 299523 |  | 299563 |  | 399588 |  | 299281 | 299229 | 299524 |  | 399747 |  |  |  |  | 399575 | 399337 | 399589 | [8 empty] | 399245 |  |  | 399274 |  | 399223 |  | 399630 | [12 empty] | 599468 | [32 empty] | 599787 |  | 499268 | 599634 | 43212 |  |  | 499720 | 599730 | [18 empty] | 292.3904
| Minimum Generation |  | 8411 | 6:00 | [202 empty] | 118148739
| Highest Generation |  | 11798 | 19:00 | [202 empty] | 118.1487 |  |  |  |  | 2.7458
| Day Peak Generation |  | 10299 | 12:00 | [202 empty] | 13195134
| Evening Peak Generation |  | 11798 | 19:00 | [202 empty] | 13.1951 |  |  | 37401663 |  | 4.9694
| HVDC Max Flow |  | 897 | 11:00 | [202 empty] | 21.4531 |  |  |  |  | 0.05232
| HVDC EvPeak Flow |  | 802 | 19:00 | [200 empty] | 238658899 |  | 3.2237 |  | 74.8707
| Load factor L.F |  | 84.29% | [166 empty] | 1275.5 | [36 empty] | 238.6589

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-10-29
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-10-28 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 10299 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 8502
Evening Peak Generation : |  |  | 11798 | MW Hour : | 19:00 | Available Max Generation : |  | 14344
E.P. Demand (at gen end) : |  |  | 11798 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 13000
Maximum Generation : |  |  | 11798 | MW Hour : | 19:00 | Reserve(Generation end) |  | 1344
Total Gen. (MKWH) : |  |  | 238.6589 | System Load Factor : | 84.29% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 870 | MW at | 19:30 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-10-29
Actual : |  | 103.02 | Ft.(MSL) , | Rule curve : | 108.7 | Ft.( MSL )
Gas Consumed : |  | Total = | 937.45 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 121058900.572
: |  |  | Coal : | 521796290.1 | Oil : | 173121253.92 | Total : | 815976444.592
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4534.2896 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1245.692 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1744.9061 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1516.5797 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1247.9061 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 928.0993 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 520.2585 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 433.5457 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 847.94 |  |  | 0 | 0%
Total |  | 0 |  | 13019.2171 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:08 | 14:05 | Khulna (C) S/S Bus Coupler Scheduled S/D Due to Annual Maintenance
08:16 | 11:24 | Gollamari 132/33kV S/S Tr-1 HT Scheduled S/D Due to 33 kv jumper change |  |  |  |  | 20.0MW load interruption.
08:17 | 11:25 | Gollamari 132/33kV S/S Tr-1 LT Scheduled S/D Due to 33 kv jumper change
08:17 | 11:26 | Gollamari 132/33kV S/S Tr-2 LT Scheduled S/D Due to 33 kv jumper change
08:18 | 11:25 | Gollamari 132/33kV S/S Tr-2 HT Scheduled S/D Due to 33 kv jumper change
08:20 | 15:11 | Saidpur 132/33kV S/S TR-4 (414T) LT Scheduled S/D Due to Annual Maintenance
08:20 | 15:26 | Palashbari 132/33kV S/S TR3-424T LT Scheduled S/D Due to Annual Maintenance
08:20 | 15:25 | Palashbari 132/33kV S/S TR3-424T HT Scheduled S/D Due to Annual Maintenance
08:21 | 15:10 | Saidpur 132/33kV S/S TR-4 (414T) HT Scheduled S/D Due to Annual Maintenance
08:23 | 10:12 | Barishal 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to For work on 33 kv bus by WZPDCL
08:24 | 10:11 | Barishal 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to For work on 33 kv bus by WZPDCL
08:25 |  | Sherpur 132/33kV S/S Transformer- 04 LT Scheduled S/D Due to Annual Maintenance
08:25 |  | Sherpur 132/33kV S/S Transformer- 04 HT Scheduled S/D Due to Annual Maintenance
08:32 | 16:37 | Panchagarh 132/33kV S/S T-3(A+B)(427T) LT Scheduled S/D Due to Annual Maintenance
08:32 | 16:35 | Panchagarh 132/33kV S/S T-3(A+B)(427T) HT Scheduled S/D Due to Anual maintance
08:34 | 08:44 | Barishal 132/33kV S/S T-1 (405T) LT Tripped showing Instant o/c , definite o/c, lockout -86 relays Due to Due to |  |  |  |  | 65.0MW load interruption.
operate section bus isolator
08:35 | 17:16 | Bhaluka-Mymensingh 132 kV Ckt-1 Scheduled S/D from Bhaluka 132/33kV end Due to
Annual Maintenance
08:35 |  | Tangail 132/33kV S/S Capacitor Bank-1 Scheduled S/D Due to Annual Maintenance
08:35 | 15:33 | Tangail 132/33kV S/S Capacitor Bank-2 Scheduled S/D Due to Annual Maintenance
08:44 | 15:45 | Rangpur 132/33kV S/S T-2 (404T) LT Scheduled S/D
08:46 | 20:19 | Haripur-Siddirganj 230kV Ckt-2 Scheduled S/D from Haripur 230/132kV end Due to From other end.
and from Siddhirganj 230/132kV end Due to Annual Maintenance work.
08:46 | 15:43 | Rangpur 132/33kV S/S T-2 (404T) HT Scheduled S/D
09:12 | 16:25 | Jamalpur 132/33kV S/S T-4 LT Scheduled S/D Due to Annual Maintenance Work.
09:12 | 16:25 | Jamalpur 132/33kV S/S T-4 HT Scheduled S/D Due to Annual Maintenance Work.
09:50 | 20:04 | Pabna- Shahjadpur 132kV Ckt-1 Forced S/D from Shahjadpur 132/33kV end Due to Shahjadpur-Pabna 132kv
Line CT Y-phase change.
09:50 | 20:04 | Pabna- Shahjadpur 132kV Ckt-1 Forced S/D from Shahjadpur 132/33kV end Due to
Shahjadpur-Pabna 132kv Line CT Y-phase change.
09:58 | 11:37 | Bhangura 132/33kV S/S Tr-1(403T) LT Tripped showing 132/33 kv power transformer-1 relays Due to |  |  |  |  | 5.0MW load interruption.
Bird in Incommer PT
09:58 | 12:46 | Bhangura 132/33kV S/S Tr-2(413T) LT Tripped showing 132/33 kv power transformer-2 relays.
10:05 | 20:14 | Pabna- Shahjadpur 132kV Ckt-1 Forced S/D from Pabna 132/33kV end Due to ALDC Instruction
for Shahjadpur S/S work.
10:21 | 13:40 | Saidpur 132/33kV S/S TR-2 (404T) LT Scheduled S/D Due to 33Kv T-2 and T-4 Bus coupler DS Maintenance.
10:22 | 13:39 | Saidpur 132/33kV S/S TR-2 (404T) HT Scheduled S/D Due to 33kv T-2 and T-4 Bus coupler DS.
10:38 |  | Kushiara CCPP 163 MW ST tripped.
10:54 | 12:44 | Bhangura 132/33kV S/S Tr-2(413T) HT Forced S/D Due to for working reason
12:00 |  | Day peak Generation = 10299 MW at 12:00 hrs.
14:13 |  | Kushiara CCPP 163 MW ST was sync.
16:10 | 16:30 | Jashore 132/33kV S/S T-1 LT Tripped showing OC,EF relays Due to WZPADCO 33 KV BISIC Feeder CT Blast. |  |  |  |  | 39.0MW load interruption.
16:32 | 17:05 | Madunaghat 132/33kV S/S T-1 33kV BUS Tripped showing REF-615 relays Due to Noapara 33kV Feeder Fault
19:00 |  | Evening Peak Gen. 11798 MW
| 20:14 | Pabna- Shahjadpur 132kV Ckt-1 is restored.
22:58 | 23:46 | Baroaulia-KSRM 132 kV Ckt-1 Tripped from Baroaulia 132/33kV end showing O/C operted, K-34, K-35 relays. |  |  |  |  | 10.0MW load interruption.
03:35 | 04:51 | Nawabganj 132/33kV S/S TR-2 LT Tripped showing Overcurrent Protection, Lockout Relay -1&2. relays
Due to Started phase-N, tripped phase-N, earth fault-1, Fault duration- 257ms, CB operation time-
74ms,Relay trip time- 178ms, Ia- 1.116 kA, Ib- 210.4 A, Ic-211.6A,
06:00 |  | Minimum generation 8502 MW.
06:48 |  | Bhangura 132/33kV S/S Tr-2(413T) HT Forced S/D |  |  |  |  | 4.0MW load interruption.
07:46 |  | Payra 400/132/33kV S/S 132/33 kV Transformer-04 LT Scheduled S/D Due to Anual maintenance
07:47 |  | Payra 400/132/33kV S/S 132/33 kV Transformer-04 HT Scheduled S/D Due to Anual maintenance
07:47 |  | Payra 400/132/33kV S/S 132/33 kV Transformer-04 HT Scheduled S/D Due to Anual maintenance
07:56 |  | Halishahar 132/33kV S/S 403T(TR-1) LT Scheduled S/D Due to Due to annual grid maintenance.
07:57 |  | Halishahar 132/33kV S/S 403T(TR-1) HT Scheduled S/D Due to Due to annual grid maintenance.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-10-28 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 180 | 3555344
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 420 | 9304060
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 327 | 698000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4875500 | GT-1 under S/D due to gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 8 | 73920 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 152 | 3546182 | GT-1 under S/D due to gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 52 | 184466 | Low demand.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 115564 | Low demand.
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 18 | 404820 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 9 | 54144 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 260 | 5776348 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 54144 | Low demand.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 128520 | Low demand.
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 48 | 284640 | Low demand.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 77080 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 47980 | Low demand.
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 31 | 738960 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 706680
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 30 | 680400
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 129010 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 15 | 371345 | Low demand.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 82 | 458064 | Low demand.
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 430080 | Low demand.
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 62400 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 187200 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 203511
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 329400 | Low demand.
| Meghnaghat Unique power |  | IPP | 586 | 0 | 63 | 1785000 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5422 | 2191 | 35262762
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 3 | 45819 | Low demand.
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 137700
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 151200
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 205 | 4969416
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 215 | 4878319
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 409818 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 66 | 839760 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 479474 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 12 | 165600 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 234240 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 12 | 284880 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 20 | 559680
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27480
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 150 | 1886836 | Low demand.
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 218688 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 318653 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 215040 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 34 | 486764 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 17 | 143855 | Low demand.
| SS Power I |  | SS Power | 1*612 | 612 | 602 | 10129090 | On test.
| Cox's Bazar Wind |  | IPP | 66 | 0 | 2 | 52320 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 193 | 5083636 | On test.
| Chattogram area Total |  |  |  | 3157 | 1659 | 31718268
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 188 | 4403000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7325600 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 240 | 6284000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 230 | 5828100 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 0 | 0 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 776556
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 66 | 194036 | Low demand.
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Under maint.
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 282720 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 408204 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 9 | 190620
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 158 | 3223680
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 814700
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 16 | 141154 | Low demand.
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 12 | 29520 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 196080 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 37 | 384720 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 443520 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 544320 | Fuel shortage
| Cumilla Area Total |  |  |  | 2896 | 1477 | 31470530
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 33 | 1391040 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 322452 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13850
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 64 | 396000 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 87 | 1166400 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 351250
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 62160 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 206 | 3703152
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1011000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3296945
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 42 | 803664
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 102816 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 57 | 1226016 | Gas shortage
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 0 | 282240 | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 191 | 1966570 | Engine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 400000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 368016 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 9026000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 367 | 8588000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 245160
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 310 | 7412600
| Sylhet Area Total |  |  |  | 2427 | 1489 | 34729027
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 802 | 21453090
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 28800 | Reserve
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 18375 | Low demand.
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 115200 | Reserve
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 9 | 23184 | Low demand.
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 466560
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | TG Test
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 352 | 8494545 | Engine problem
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 1171 | 30599754
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Transformer O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 23 | 445200 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 128 | 2445000 | ST Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1210 | 20746900
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 222 | 4850700
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 26400 | Transformer O/L
| Barisal 307 MW |  | IPP | 307*1 | 307 | 150 | 3687300 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1733 | 32201500
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 20008 | Reserve
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 148 | 3767045 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 212 | 6210836 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 49150 | Reserve
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 132966
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 25 | 70816 | Low demand.
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 30 | 94944 | Low demand.
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 79296 | Low demand.
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 31740
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1161 | 22584511
| Rajshahi Area Total |  |  |  | 3631 | 1622 | 33041312
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4144700 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 45 | 170275 | Low demand.
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 41004
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 35 | 103872 | Low demand.
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 225803
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1246940
| Rangpur Area Total |  |  |  | 950 | 250 | 5932594
| Total |  |  |  | 24599 | 11798 | 238658899
| Eastern Grid Total |  |  |  | 14516 | 7022 | 136883739
| Western Grid Total |  |  |  | 10083 | 4776 | 101775160
| National Grid Total |  |  |  | 24599 | 11798 | 238658899
*Data collected from respective power station over telephone.
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-10-28
| (a) ENTIRE EASTERN GRID : |  | 8034.41 | MW | (b) ENTIRE WESTERN GRID : |  | 3364.3 | MW
| i) Dhaka area |  | 4354.51 | MW | i) Khulna area |  | 1308.6 | MW
| ii) Chittagong area |  | 1215.9 | MW | ii) Rajshahi area |  | 1084 | MW
| iii) Comilla area |  | 1114 | MW | iii) Barisal area |  | 333.7 | MW
| iv) Mymensingh area |  | 863 | MW | iv) Rangpur area |  | 638 | MW
| v) Sylhet area |  | 487 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11398.71 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 27 | 18:30 | Kamrangirchar | 41.4 | 13:00 | Narinda | 55 | 12:00 | Sherpur | 108 | 18:00
2 | AKSML | 109 | 23:00 | Chowmuhani | 176 | 18:00 | Kaptai | N/A | N/A | Narshingdi | 165 | 18:30 | Shikalbaha | 29 | 23:00
3 | Aftabnagar | 32 | 18:30 | Chuadanga | 88 | 18:30 | Kazla | 88 | 13:00 | Natore | 109 | 18:00 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 67 | 13:00 | Coxsbazar | 124 | 18:00 | Keranigonj | 62 | 18:30 | Nawabganj | 33.3 | 19:30 | Shitalakhya | 98 | 12:00
5 | Agrabad | 82 | 15:00 | Cumilla(N) | 127 | 18:00 | Khagrachori | 22 | 19:00 | Netrakona | 98 | 19:30 | Sholosohor | 38 | 15:00
6 | Amnura | 43 | 18:00 | Cumilla(S) | 158 | 18:30 | Khulna | 86 | 18:30 | New | 72 | 12:00 | Shyampur | 154 | 12:00
7 | Ashuganj | 59 | 14:00 | Daudkandi | 130 | 19:00 | Khulshi | 163 | 19:00 | Niamatpur | 59 | 18:30 | Siddhirganj | 108 | 15:00
8 | BIPTC | N/A | N/A | Dhaka | 26 | 11:00 | Kishoreganj | 118 | 18:00 | Noapara | 45 | 18:00 | Sirajganj | 89 | 18:00
9 | BSRM | 138 | 18:30 | Dhamrai | 110 | 18:30 | Kodda | 249 | 15:00 | PHP | 3 | 15:00 | Sonargaon | 88 | 11:00
10 | Bagerhat | 73 | 18:30 | Dhanmondi | 104 | 13:00 | Kulaura | 44 | 18:00 | Pabna | 105 | 18:30 | Sreemongol | 61 | 18:00
11 | Bakulia | 88 | 18:30 | Dohazari | 56 | 18:00 | Kurigram | 54 | 18:00 | Palashbari | 82 | 18:30 | Sreepur | 59.5 | 18:30
12 | Banani | 34 | 11:00 | Faridpur | 115 | 18:00 | Kushtia | 116 | 18:00 | Panchagarh | 47 | 18:00 | Srinagar | 35.32 | 22:00
13 | Bangabhaban | 3 | 11:00 | Fatullah | 64 | 16:00 | Lalbag | 78 | 13:00 | Patuakhali | 78 | 22:00 | Sunamganj | 42 | 19:00
14 | Barapukuria | 51 | 18:00 | Fenchuganj | 37 | 18:00 | Lalmonirhat | 36 | 18:00 | Payra | 16 | 18:00 | Sylhet | 16 | 00:00
15 | Barguna | 14 | 00:00 | Feni | 97 | 18:00 | MI_Cement | 19 | 04:00 | Postogola | 51 | 18:00 | Sylhet-132 | 131 | 18:00
16 | Barishal | 89 | 18:30 | GPH | 96 | 02:00 | Madanganj | 29 | 18:30 | Purbachal | 18 | 18:00 | TK | 26.7 | 19:00
17 | Barishal-230 | 74 | 18:00 | Ghorashal | 60 | 19:30 | Madaripur | 74 | 18:00 | Purbasadipur | 93 | 18:30 | Tangail | 176 | 18:00
18 | Baroaulia | 67 | 14:00 | Goalpara | 30 | 13:00 | Madartek | 67.84 | 14:00 | Rahim | 40 | 13:00 | Thakurgaon | 68 | 18:00
19 | Baroirhat | 48 | 18:00 | Gollamari | 43 | 00:00 | Madunaghat | 45 | 19:00 | Rajbari | 52 | 18:00 | Tongi | 95 | 11:00
20 | Bashundhara | 138 | 18:00 | Gopalganj | 81.8 | 18:30 | Magura | 53 | 18:30 | Rajendrapur | 92 | 18:30 | Ullon | 36 | 19:30
21 | BashundharaCement | 7 | 12:00 | Gulshan | 84 | 12:00 | Mahasthangarh | 58 | 18:00 | Rajshahi | 119 | 18:30 | Uttara | 57 | 18:00
22 | Beanibazar | 56 | 18:00 | Halishahar | 66 | 16:00 | Manikganj | 88 | 18:30 | Rajshahi-230 | 28 | 18:30 | UttaraNew | 46 | 01:00
23 | Benapole | 48 | 18:00 | HaripurSBU | 136 | 16:00 | Maniknagar | 62 | 13:00 | Ramganj | 88 | 18:00 | Zigatola | 77 | 18:30
24 | Bhaluka | 128 | 17:00 | Hasnabad | 82 | 21:00 | Matarbari | 4 | 14:00 | Rampur | 27 | 18:30
25 | Bhandaria | 38 | 21:00 | Hathazari | 68 | 18:00 | Matuail | 70 | 10:00 | Rangamati | 17 | 18:00
26 | Bhangura | 19 | 00:00 | Ishurdi | 64 | 18:30 | Millgate | 90 | 12:00 | Rangpur | 112 | 18:00
27 | Bheramara(GK) | 49 | 18:00 | Jaldhaka | 53 | 18:00 | Mirpur | 116 | 18:00 | Ruppur | 3.4 | 10:00
28 | Bhulta | 229 | 19:00 | Jamalpur | 130 | 18:00 | Mirsorai | 4 | 16:00 | SSM | 0 | 00:00
29 | Bog-Sherpur | 48 | 18:00 | Jashore | 105 | 18:00 | Mirzapur | N/A | N/A | Saidpur | 82 | 18:30
30 | Bogura | 119 | 18:30 | Jhenaidah | 105 | 18:00 | Mithapukur | 42 | 18:00 | Satkhira | 96 | 18:00
31 | Borhanuddin | 42 | 21:00 | Joydebpur | 165 | 18:30 | Modern | 0 | 00:00 | Satmasjid | 91 | 13:00
32 | Brahmanbaria | 148 | 18:30 | Joypurhat | 42 | 18:00 | Mogbazar | 87.9 | 15:00 | Savar | 162 | 18:30
33 | Cantonment | 105 | 13:00 | Juldah | 22 | 12:00 | Mongla | 34 | 14:00 | SevenRings | 5.39 | 09:00
34 | Chandpur | 55 | 18:00 | KSRM | 26 | 14:00 | Motijheel | 26 | 12:00 | ShahCement | 36 | 00:00
35 | Chandraghona | 28 | 18:00 | Kabirpur | 241 | 18:30 | Munshiganj | 84 | 15:00 | Shahjadpur | 82 | 18:30
36 | Chapai | 53 | 18:30 | Kachua | 58 | 18:00 | Mymensingh | 178 | 18:30 | Shahjibazar | 101 | 21:00
37 | Charsaidpur | 26 | 16:00 | Kallyanpur | 99 | 12:00 | Naogaon | 103 | 18:30 | Shahmirpur | 34 | 01:00
38 | Chauddagram | 49 | 17:00 | Kalurghat | 32 | 12:00 | Narail | 44 | 18:00 | Shariatpur | 56 | 18:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-10-28 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 400 | 03:00 | 389 | 12:00 | Gopalganj | 409 | 03:00 | 399 | 13:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 389 | 03:00 | 370 | 13:00
| Bhulta | 401 | 03:00 | 392 | 12:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 408 | 03:00 | 398 | 16:00 | Payra | 416 | 05:00 | 408 | 20:00
| BIPTC | 399 | 04:00 | 392 | 18:00 | Rahanpur | 413 | 06:00 | 400 | 21:00
| Bogura | N/A | N/A | N/A | N/A | Rampal | 409 | 03:00 | 400 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 236 | 03:00 | 227 | 12:00 | Hasnabad | 235 | 04:00 | 228 | 10:00
| AKSML | 234 | 22:00 | 227 | 11:00 | Hathazari | 237 | 22:00 | 228 | 16:00
| Aminbazar | 238 | 03:00 | 230 | 11:00 | Ishurdi | 236 | 03:00 | 224 | 11:00
| Ashuganj | 237 | 06:00 | 231 | 12:00 | Jhenaidah | 229 | 03:00 | 217 | 12:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 238 | 03:00 | 229 | 12:00
| Baghabari | 229 | 02:00 | 223 | 11:00 | Keranigonj | 235 | 03:00 | 227 | 12:00
| Barapukuria | 226 | 03:00 | 217 | 21:00 | Khulna(S) | 235 | 03:00 | 225 | 12:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 238 | 06:00 | 232 | 18:00 | Maniknagar | 234 | 04:00 | 228 | 12:00
| Bheramara | 235 | 03:00 | 223 | 11:00 | Meghnaghat | 242 | 05:00 | 235 | 14:00
| Bhulta | 239 | 02:00 | 230 | 12:00 | Mirsorai | 235 | 22:00 | 227 | 10:00
| Bibiana | 235 | 02:00 | 228 | 16:00 | Rajshahi | 233 | 03:00 | 222 | 18:00
| BIPTC | 236 | 03:00 | 222 | 12:00 | Rampal | 234 | 03:00 | 225 | 12:00
| Bogura | 235 | 05:00 | 227 | 21:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 240 | 03:00 | 237 | 00:00 | Rampura | 236 | 05:00 | 229 | 12:00
| BSRM | 234 | 22:00 | 227 | 15:00 | Shikalbaha | 234 | 22:00 | 227 | 11:00
| Cumilla(N) | 233 | 05:00 | 228 | 12:00 | Shyampur | 235 | 03:00 | 227 | 12:00
| Fenchuganj | 239 | 09:00 | 232 | 12:00 | Siddhirganj | 236 | 08:00 | 231 | 10:00
| Ghorashal | 240 | 00:00 | 235 | 21:00 | Sirajgonj | 239 | 07:00 | 234 | 12:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 236 | 03:00 | 229 | 12:00
| GPH | 236 | 22:00 | 228 | 15:00 | Tongi | 235 | 04:00 | 224 | 11:00
| Haripur | 235 | 03:00 | 229 | 12:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 138 | 03:00 | 132 | 12:00 | Lalbag | 135 | 03:00 | 129 | 12:00
| Agargaon | 136 | 03:00 | 130 | 15:00 | Lalmonirhat | 133 | 06:00 | 127 | 12:00
| Agrabad | 135 | 22:00 | 130 | 10:00 | Madanganj | 137 | 23:00 | 129 | 11:00
| AKS | 134 | 22:00 | 129 | 14:00 | Madaripur | 132 | 06:00 | 129 | 12:00
| Aminbazar | 140 | 03:00 | 134 | 11:00 | Madartek | 137 | 03:00 | 131 | 12:00
| Amnura | 138 | 18:30 | 126 | 00:00 | Madunaghat | 137 | 03:00 | 132 | 11:00
| Ashuganj | 141 | 05:00 | 140 | 10:00 | Magura | 138 | 03:00 | 130 | 12:00
| Bagerhat | 135 | 06:00 | 127 | 18:00 | Mahasthangarh | 137 | 03:00 | 130 | 21:00
| Bakulia | 135 | 22:00 | 131 | 10:00 | Manikganj | 132 | 03:00 | 125 | 12:00
| Banani | 140 | 03:00 | 131 | 11:00 | Maniknagar | 138 | 02:00 | 133 | 11:00
| Bangabhaban | 138 | 06:00 | 132 | 12:00 | Matarbari | 130 | 01:00 | 125 | 18:00
| Barapukuria | 140 | 02:00 | 133 | 21:00 | Matuail | 133 | 06:00 | 128 | 16:00
| Barguna | 138 | 05:00 | 134 | 19:00 | Millgate | 141 | 05:00 | 131 | 12:00
| Barishal | 137 | 05:00 | 130 | 20:00 | Mirpur | 139 | 02:00 | 132 | 11:00
| Barishal-230 | 136 | 03:00 | 131 | 18:00 | Mirzapur | N/A | N/A | N/A | N/A
| Baroaulia | 136 | 18:30 | 131 | 14:00 | Mithapukur | 136 | 03:00 | 129 | 12:00
| Baroirhat | 129 | 09:00 | 123 | 00:00 | MI_Cement | 134 | 04:00 | 130 | 12:00
| Bashundhara | 140 | 02:00 | 131 | 12:00 | Modern | 137 | 22:00 | 131 | 10:00
| BashundharaCement | 133 | 04:00 | 129 | 11:00 | Mogbazar | 139 | 06:00 | 133 | 16:00
| Beanibazar | 129 | 07:00 | 125 | 18:00 | Mongla | 135 | 05:00 | 127 | 18:00
| Benapole | 137 | 02:00 | 127 | 12:00 | Motijheel | 138 | 06:00 | 132 | 12:00
| Bhaluka | 128 | 06:00 | 123 | 12:00 | Munshiganj | 134 | 03:00 | 129 | 12:00
| Bhandaria | 137 | 07:00 | 130 | 21:00 | Mymensingh | 135 | 09:00 | 121 | 12:00
| Bhangura | 142 | 03:00 | 134 | 12:00 | Naogaon | 134 | 05:00 | 126 | 21:00
| Bheramara | 136 | 03:00 | 129 | 11:00 | Narail | 138 | 06:00 | 129 | 12:00
| Bheramara(GK) | 135 | 04:00 | 128 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 125 | 06:00 | 120 | 12:00 | Narshingdi | 128 | 01:00 | 122 | 12:00
| Bog-Sherpur | 138 | 03:00 | 132 | 12:00 | Natore | 135 | 02:00 | 129 | 12:00
| Bogura | 138 | 05:00 | 132 | 12:00 | Nawabganj | 135 | 05:00 | 129 | 12:00
| Bogura-230 | 138 | 05:00 | 132 | 12:00 | Netrakona | 135 | 09:00 | 124 | 18:00
| Brahmanbaria | 128 | 03:00 | 120 | 18:00 | New | 139 | 07:00 | 131 | 12:00
| Cantonment | 136 | 03:00 | 130 | 12:00 | Niamatpur | 133 | 06:00 | 124 | 21:00
| Chandpur | 128 | 09:00 | 125 | 23:00 | Noapara | 137 | 06:00 | 128 | 23:00
| Chandraghona | 137 | 22:00 | 133 | 10:00 | Pabna | 141 | 05:00 | 129 | 12:00
| Chapai | 134 | 05:00 | 128 | 20:00 | Palashbari | 135 | 06:00 | 126 | 20:00
| Charsaidpur | 135 | 05:00 | 130 | 11:00 | Panchagarh | 134 | 03:00 | 124 | 12:00
| Chauddagram | 131 | 07:00 | 126 | 00:00 | Patuakhali | 138 | 01:00 | 135 | 19:00
| Chhatak | 129 | 05:00 | 125 | 00:00 | Payra | 140 | 04:00 | 137 | 19:00
| Chowmuhani | 126 | 09:00 | 117 | 00:00 | PHP | 129 | 08:00 | 124 | 00:00
| Chuadanga | 136 | 05:00 | 126 | 12:00 | Postogola | 137 | 04:00 | 131 | 12:00
| Coxsbazar | 128 | 22:00 | 120 | 18:00 | Purbachal | 141 | 02:00 | 131 | 12:00
| Cumilla(N) | 135 | 09:00 | 131 | 18:00 | Purbasadipur | 133 | 05:00 | 124 | 19:30
| Cumilla(S) | 134 | 09:00 | 125 | 13:00 | Rahanpur | 136 | 03:00 | 132 | 20:00
| Daudkandi | 125 | 06:00 | 120 | 00:00 | Rahim | 133 | 03:00 | 130 | 11:00
| Dhaka | 138 | 03:00 | 132 | 12:00 | Rajbari | 132 | 03:00 | 126 | 12:00
| Dhamrai | 136 | 03:00 | 128 | 12:00 | Rajendrapur | 132 | 19:00 | 125 | 12:00
| Dhanmondi | 133 | 03:00 | 129 | 12:00 | Rajshahi | 136 | 06:00 | 128 | 12:00
| Dohazari | 135 | 22:00 | 131 | 09:00 | Rajshahi-230 | 137 | 03:00 | 126 | 18:00
| Faridpur | 131 | 04:00 | 126 | 12:00 | Ramganj | 125 | 10:00 | 115 | 00:00
| Fatullah | 137 | 04:00 | 132 | 11:00 | Rampur | 135 | 21:00 | 130 | 10:00
| Fenchuganj | 134 | 09:00 | 130 | 18:00 | Rampura | 137 | 02:00 | 132 | 11:00
| Feni | 128 | 09:00 | 124 | 00:00 | Rangamati | 137 | 22:00 | 132 | 11:00
| Ghorashal | 141 | 01:00 | 138 | 16:00 | Rangpur | 135 | 06:00 | 126 | 19:30
| Goalpara | 138 | 03:00 | 130 | 12:00 | Ruppur | 138 | 03:00 | 131 | 12:00
| Gollamari | 137 | 03:00 | 131 | 12:00 | Saidpur | 135 | 05:00 | 126 | 20:00
| Gopalganj | 133 | 03:00 | 127 | 12:00 | Satkhira | 135 | 05:00 | 127 | 18:00
| Gopalganj-400 | 132 | 03:00 | 127 | 13:00 | Satmasjid | 136 | 03:00 | 130 | 11:00
| Gulshan | 137 | 05:00 | 131 | 12:00 | Savar | 138 | 19:00 | 131 | 12:00
| Halishahar | 135 | 01:00 | 130 | 10:00 | SevenRings | 142 | 06:00 | 136 | 11:00
| Haripur | 133 | 03:00 | 130 | 11:00 | ShahCement | 135 | 05:00 | 130 | 11:00
| HaripurSBU | 133 | 03:00 | 130 | 11:00 | Shahjadpur | 142 | 06:00 | 140 | 00:00
| Hasnabad | 137 | 06:00 | 132 | 11:00 | Shahjibazar | 128 | 08:00 | 122 | 19:30
| Hathazari | 137 | 18:30 | 132 | 15:00 | Shahmirpur | 135 | 21:00 | 130 | 01:00
| Ishurdi | 139 | 03:00 | 132 | 11:00 | Shariatpur | 132 | 04:00 | 127 | 15:00
| Jaldhaka | 135 | 06:00 | 124 | 21:00 | Sherpur | 133 | 18:30 | 120 | 01:00
| Jamalpur | 136 | 18:30 | 124 | 00:00 | Shikalbaha | 126 | 22:00 | 120 | 11:00
| Jashore | 136 | 05:00 | 127 | 12:00 | Shikalbaha-230 | 137 | 23:00 | 132 | 11:00
| Jhenaidah | 140 | 06:00 | 131 | 12:00 | Shitalakhya | 134 | 04:00 | 130 | 12:00
| Jhenaidah-230 | 141 | 03:00 | 132 | 12:00 | Sholosohor | 136 | 22:00 | 131 | 11:00
| Joydebpur | 138 | 18:30 | 131 | 11:00 | Shyampur | 136 | 08:00 | 131 | 12:00
| Joypurhat | 134 | 04:00 | 126 | 13:00 | Shyampur-230 | 137 | 05:00 | 132 | 11:00
| Juldah | 137 | 22:00 | 132 | 10:00 | Siddhirganj | 134 | 05:00 | 129 | 16:00
| Kabirpur | 137 | 07:00 | 127 | 16:00 | Sirajganj | 138 | 06:00 | 132 | 12:00
| Kachua | 130 | 18:30 | 123 | 00:00 | Sonargaon | 132 | 09:00 | 126 | 00:00
| Kaliakoir | 136 | 03:00 | 130 | 12:00 | Sreemongol | 129 | 08:00 | 124 | 20:00
| Kallyanpur | 140 | 06:00 | 134 | 12:00 | Sreepur | 130 | 03:00 | 125 | 12:00
| Kalurghat | 138 | 22:00 | 132 | 10:00 | Srinagar | 135 | 05:00 | 130 | 11:00
| Kamrangirchar | 139 | 03:00 | 129 | 16:00 | SSM | 140 | 21:00 | 134 | 10:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 128 | 07:00 | 123 | 00:00
| Kazla | 137 | 02:00 | 131 | 13:00 | Sylhet | 130 | 07:00 | 128 | 00:00
| Keranigonj | 136 | 05:00 | 130 | 12:00 | Sylhet-132 | 130 | 03:00 | 128 | 00:00
| Khagrachori | 136 | 03:00 | 132 | 15:00 | Tangail | 132 | 09:00 | 127 | 07:00
| Khulna | 137 | 06:00 | 130 | 12:00 | Thakurgaon | 132 | 04:00 | 121 | 20:00
| Khulna(S) | 138 | 06:00 | 131 | 12:00 | TK | 136 | 22:00 | 132 | 11:00
| Khulshi | 135 | 22:00 | 130 | 10:00 | Tongi | 141 | 04:00 | 133 | 11:00
| Kishoreganj | 134 | 06:00 | 130 | 00:00 | Ullon | 137 | 01:00 | 131 | 12:00
| Kodda | 137 | 18:30 | 124 | 11:00 | Uttara | 140 | 03:00 | 132 | 12:00
| KSRM | 136 | 18:30 | 131 | 10:00 | UttaraNew | 140 | 02:00 | 133 | 11:00
| Kulaura | 132 | 03:00 | 129 | 17:00 | Zigatola | 135 | 04:00 | 129 | 13:00
| Kurigram | 133 | 03:00 | 124 | 21:00
| Kushtia | 137 | 06:00 | 130 | 12:00

## L-Curve
Date | 2023-10-28
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 950 | 6267 | 4101 | 10368 |  |  |  | QF-LDC-11
0:30 | 1065 | 6009.5 | 4083 | 10092.5 | Date: | 2023-10-28
1:00 | 1180 | 5752 | 4065 | 9817
1:30 | 1165 | 5727.5 | 3934 | 9661.5
2:00 | 1150 | 5703 | 3803 | 9506
2:30 | 1145 | 5593 | 3761.5 | 9354.5 | [5 empty] | Gen. at Eve. Peak | 11798 | 11798 MW (19:00 )
3:00 | 1140 | 5483 | 3720 | 9203 | [6 empty] | 19:00
3:30 | 1095 | 5304.5 | 3645.5 | 8950 | [5 empty] | Gen. at Day Peak | 10299 | 10299 MW (12:00 )
4:00 | 1050 | 5126 | 3571 | 8697 | [6 empty] | 12:00
4:30 | 1045 | 5059.5 | 3569 | 8628.5 | [5 empty] | Highest Generation | 11798
5:00 | 1040 | 4993 | 3567 | 8560 | [6 empty] | 19:00
5:30 | 1050 | 4928.5 | 3557 | 8485.5
6:00 | 1060 | 4864 | 3547 | 8411
6:30 | 980 | 4974 | 3578.5 | 8552.5
7:00 | 900 | 5084 | 3610 | 8694
7:30 | 935 | 5106.5 | 3694 | 8800.5
8:00 | 970 | 5129 | 3778 | 8907
8:30 | 1070 | 5205 | 3831.5 | 9036.5
9:00 | 1170 | 5281 | 3885 | 9166
9:30 | 1250 | 5301.5 | 3913 | 9214.5
10:00 | 1330 | 5322 | 3941 | 9263
10:30 | 1330 | 5500.5 | 3989.5 | 9490
11:00 | 1330 | 5679 | 4038 | 9717
11:30 | 1335 | 5817.5 | 4190.5 | 10008
12:00 | 1340 | 5956 | 4343 | 10299
12:30 | 1315 | 5946.5 | 4393.5 | 10340
13:00 | 1290 | 5937 | 4444 | 10381
13:30 | 1245 | 6001.5 | 4413.5 | 10415
14:00 | 1200 | 6066 | 4383 | 10449
14:30 | 1225 | 6110 | 4382 | 10492
15:00 | 1250 | 6154 | 4381 | 10535
15:30 | 1270 | 6112.5 | 4289.5 | 10402
16:00 | 1290 | 6071 | 4198 | 10269
16:30 | 1180 | 6121 | 4148 | 10269
17:00 | 1070 | 6171 | 4098 | 10269
17:30 | 1025 | 6517.5 | 4370 | 10887.5
18:00 | 980 | 6864 | 4642 | 11506
18:30 | 940 | 6943 | 4709 | 11652
19:00 | 900 | 7022 | 4776 | 11798
19:30 | 870 | 6909 | 4742 | 11651
20:00 | 890 | 6820 | 4688 | 11508 |  |  |  | Executive Engineer
20:30 | 935 | 6736 | 4634.5 | 11370.5 |  |  |  | Network Operation Division
21:00 | 980 | 6652 | 4581 | 11233
21:30 | 990 | 6513.5 | 4534 | 11047.5
22:00 | 1000 | 6375 | 4487 | 10862 |  |  |  |  | Page 6 of 7
22:30 | 985 | 6368.5 | 4364 | 10732.5
23:00 | 970 | 6362 | 4241 | 10603
23:30 | 960 | 6314.5 | 4171 | 10485.5
24:00 | 950 | 6267 | 4101 | 10368
11798 MW (19:00 )
10299 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-10-28 |  | Energy |  | 238658899
QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3369 | 896 | 1776 | 0 | 543 | 3332 | 207 | 0 | 99 | 140 | 0 | 6 | 0
0:30 | 3366 | 896 | 1782 | 0 | 394 | 3216.5 | 206.5 | 0 | 95 | 133 | 0 | 3.5 | 0 |  | Date: | 43765
1:00 | 3363 | 896 | 1788 | 0 | 245 | 3101 | 206 | 0 | 91 | 126 | 0 | 1 | 0
1:30 | 3328 | 896 | 1800.5 | 0 | 230 | 2983.5 | 206 | 0 | 91 | 125 | 0 | 1.5 | 0 | [8 empty] | Total Energy | 238.6589 | 238.6589 | Total Energy Gen 238.659 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 238.659 MKWHr
2:00 | 3293 | 896 | 1813 | 0 | 215 | 2866 | 206 | 0 | 91 | 124 | 0 | 2 | 0 | [8 empty] | Energy not Served | 0 | 0
2:30 | 3251.5 | 895.5 | 1727 | 0 | 215 | 2844 | 205.5 | 0 | 91 | 123 | 0 | 2 | 0 | [8 empty] | Energy Requirement | 238.6589 | 238.6589
3:00 | 3210 | 895 | 1641 | 0 | 215 | 2822 | 205 | 0 | 91 | 122 | 0 | 2 | 0
3:30 | 3178.5 | 895.5 | 1579 | 0 | 170 | 2709.5 | 205.5 | 0 | 91 | 120 | 0 | 1 | 0 | [7 empty] | Shortage
4:00 | 3147 | 896 | 1517 | 0 | 125 | 2597 | 206 | 0 | 91 | 118 | 0 | 0 | 0
4:30 | 3151.5 | 896 | 1521.5 | 0 | 98.5 | 2585 | 206 | 0 | 54 | 116 | 0 | 0 | 0
5:00 | 3156 | 896 | 1526 | 0 | 72 | 2573 | 206 | 0 | 17 | 114 | 0 | 0 | 0
5:30 | 3130.5 | 896 | 1493 | 0 | 60.5 | 2573 | 206 | 0 | 17 | 109 | 0 | 0.5 | 0
6:00 | 3105 | 896 | 1460 | 0 | 49 | 2573 | 206 | 0 | 17 | 104 | 0 | 1 | 0
6:30 | 3176 | 896 | 1501 | 0 | 50 | 2573 | 206.5 | 0 | 17 | 106 | 26 | 1 | 0 | [6 empty] | Coal
7:00 | 3247 | 896 | 1542 | 0 | 51 | 2573 | 207 | 0 | 17 | 108 | 52 | 1 | 0
7:30 | 3219.5 | 896 | 1575 | 0 | 68 | 2595.5 | 207 | 0 | 17 | 111 | 111 | 0.5 | 0 | [5 empty] | Oil
8:00 | 3192 | 896 | 1608 | 0 | 85 | 2618 | 207 | 0 | 17 | 114 | 170 | 0 | 0
8:30 | 3186.5 | 896 | 1630.5 | 0 | 135 | 2624 | 207 | 0 | 17 | 115 | 225.5 | 0 | 0
9:00 | 3181 | 896 | 1653 | 0 | 185 | 2630 | 207 | 0 | 17 | 116 | 281 | 0 | 0
9:30 | 3193 | 896 | 1655 | 0 | 177 | 2624.5 | 207 | 0 | 17 | 118 | 327 | 0 | 0
10:00 | 3205 | 896 | 1657 | 0 | 169 | 2619 | 207 | 0 | 17 | 120 | 373 | 0 | 0
10:30 | 3285 | 896.5 | 1740 | 0 | 187.5 | 2637 | 207 | 0 | 17 | 126 | 393.5 | 0.5 | 0
11:00 | 3365 | 897 | 1823 | 0 | 206 | 2655 | 207 | 0 | 17 | 132 | 414 | 1 | 0
11:30 | 3453 | 897 | 1921 | 0 | 278.5 | 2683 | 206.5 | 0 | 17 | 131 | 420 | 1 | 0
12:00 | 3541 | 897 | 2019 | 0 | 351 | 2711 | 206 | 0 | 17 | 130 | 426 | 1 | 0
12:30 | 3516.5 | 896.5 | 1951.5 | 0 | 414 | 2780 | 205.5 | 0 | 23 | 139 | 411.5 | 2.5 | 0
13:00 | 3492 | 896 | 1884 | 0 | 477 | 2849 | 205 | 0 | 29 | 148 | 397 | 4 | 0
13:30 | 3492 | 896 | 1884 | 0 | 477 | 2849 | 205 | 0 | 29 | 148 | 397 | 4 | 0
14:00 | 3492 | 896 | 1884 | 0 | 477 | 2849 | 205 | 0 | 29 | 148 | 397 | 4 | 0
14:30 | 3526.5 | 896 | 1807.5 | 0 | 553 | 2947 | 205 | 0 | 55 | 152 | 312.5 | 3.5 | 0
15:00 | 3561 | 896 | 1731 | 0 | 629 | 3045 | 205 | 0 | 81 | 156 | 228 | 3 | 0
15:30 | 3566 | 896 | 1740 | 0 | 583 | 3007 | 205 | 0 | 81.5 | 153 | 166 | 4.5 | 0
16:00 | 3571 | 896 | 1749 | 0 | 537 | 2969 | 205 | 0 | 82 | 150 | 104 | 6 | 0
16:30 | 3545 | 895.5 | 1802.5 | 0 | 546 | 2981.5 | 205 | 0 | 82 | 147 | 59 | 5.5 | 0
17:00 | 3519 | 895 | 1856 | 0 | 555 | 2994 | 205 | 0 | 82 | 144 | 14 | 5 | 0
17:30 | 3574.5 | 895.5 | 1848 | 0 | 842.5 | 3177 | 205 | 0 | 180.5 | 151 | 7 | 6.5 | 0
18:00 | 3630 | 896 | 1840 | 0 | 1130 | 3360 | 205 | 0 | 279 | 158 | 0 | 8 | 0
18:30 | 3588.5 | 849 | 1810 | 0 | 1203 | 3599 | 205 | 0 | 234.5 | 158 | 0 | 5 | 0
19:00 | 3547 | 802 | 1780 | 0 | 1276 | 3838 | 205 | 0 | 190 | 158 | 0 | 2 | 0
19:30 | 3561 | 802 | 1799 | 0 | 1081 | 3884 | 207 | 0 | 165 | 150 | 0 | 2 | 0
20:00 | 3576 | 802 | 1814 | 0 | 894 | 3896 | 207 | 0 | 165 | 152 | 0 | 2 | 0
20:30 | 3575 | 849 | 1840 | 0 | 783.5 | 3820.5 | 207 | 0 | 145 | 149 | 0 | 1.5 | 0
21:00 | 3574 | 896 | 1866 | 0 | 673 | 3745 | 207 | 0 | 125 | 146 | 0 | 1 | 0
21:30 | 3529 | 896 | 1805 | 0 | 638 | 3700.5 | 207 | 0 | 125 | 146 | 0 | 1 | 0
22:00 | 3484 | 896 | 1744 | 0 | 603 | 3656 | 207 | 0 | 125 | 146 | 0 | 1 | 0
22:30 | 3478 | 896 | 1743.5 | 0 | 579.5 | 3564.5 | 207 | 0 | 116.5 | 145 | 0 | 2.5 | 0
23:00 | 3472 | 896 | 1743 | 0 | 556 | 3473 | 207 | 0 | 108 | 144 | 0 | 4 | 0
23:30 | 3420.5 | 896 | 1759.5 | 0 | 549.5 | 3402.5 | 207 | 0 | 103.5 | 142 | 0 | 5 | 0 |  | Max Temp. in Dhaka |  | 33°C
24:00 | 3369 | 896 | 1776 | 0 | 543 | 3332 | 207 | 0 | 99 | 140 | 0 | 6 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 238.659 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 238.659 MKWHr
Note on W13: Author:

## Generation
g | 2023-10-28
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 131 | 131 | 130 | 131 | 131 | 131 | 132 | 132 | 132 | 132 | 132 | 131 | 130 | 130 | 130 | 130 | 130 | 130 |  | 130 | 132 | 132 | 132 | 132 | 132 | 132 | 3149416
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1820000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [19 empty] | 3 | 8 | 8 | 8 | 8 | 8 | 8 | 45819
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 3 | 10 | 15 | 18 | 20 | 20 | 19 | 16 | 12 | 6 | 1 | [9 empty] | 137700
6 | Sikalbaha 225MW CCPP (Gas) | 188 | 188 | 188 | 189 | 188 | 188 | 188 | 188 | 208 | 215 | 218 | 215 | 218 | 217 | 216 | 217 | 218 | 217 |  | 215 | 208 | 208 | 207 | 208 | 208 | 208 | 4878319
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 19 |  | 34 | 34 | 34 | 34 | 34 | 17 | 17 | 479474
12 | Hathazari 100 MW peaking PP | 74 | 74 | 74 | 74 | 0 | [8 empty] | 24 | 31 | 32 | 32 | 33 |  | 66 | 66 | 66 | 75 | 75 | 75 | 66 | 839760
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 |  |  |  |  | 0 | 2 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 34 | 34 | 34 | 34 | 34 | 34 | 409818
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 277 | 250 | 250 | 235 | 235 | 235 | 175 | 175 | 175 | 175 | 253 | 254 | 251 | 253 | 260 | 260 | 257 | 260 |  | 260 | 260 | 260 | 245 | 244 | 240 | 240 | 5776348
18 | Kodda 300 MW PP Unit-2 (Summit) | [10 empty] | 0 | 10 | 42 | 76 | 15 | 15 | 15 | 42 |  | 15 | 15 | 0 |  |  |  |  | 371345
19 | Ashuganj 195 MW PP (APSCL-United) | [26 empty] | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 132 | 130 | 130 | 130 | 150 | 170 | 170 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 130 | 130 | 130 | 3555344
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 420 | 420 | 420 | 320 | 320 | 320 | 320 | 325 | 325 | 325 | 324 | 325 | 325 | 325 | 326 | 325 | 365 | 490 |  | 602 | 612 | 613 | 624 | 612 | 624 | 624 | 10129090
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP
33 | Ashuganj 225 MW CCPP | 174 | 176 | 177 | 184 | 193 | 152 | 196 | 189 | 175 | 175 | 163 | 163 | 168 | 185 | 183 | 181 | 188 | 179 |  | 188 | 193 | 199 | 196 | 193 | 196 | 190 | 4403000
34 | Ashuganj 450 MW CCPP(South) | 270 | 270 | 270 | 270 | 270 | 240 | 315 | 290 | 270 | 270 | 270 | 270 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 6284000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 320 | 300 | 280 | 280 | 300 | 280 | 280 | 280 | 305 | 300 | 280 | 355 |  | 280 | 280 | 280 | 280 | 280 | 310 | 280 | 7325600
| Ashuganj 420 MW CCPP(East) | 240 | 230 | 230 | 230 | 230 | 230 | 250 | 250 | 250 | 250 | 250 | 250 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5828100
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 415 | 416 | 368 | 309 | 305 | 302 | 324 | 341 | 380 | 398 | 413 | 417 | 413 | 379 | 387 | 402 | 407 | 406 |  | 420 | 424 | 422 | 422 | 421 | 386 | 345 | 9304060
| Meghnaghat Unique power | 44 | 94 | 40 | 50 | 96 | 97 | 100 | 100 | 82 | 100 | 100 | 100 | 90 | 94 | 100 | 100 | 100 | 100 |  | 63 | 73 | 87 | 86 | 40 | 100 | 83 | 1785000
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 200 | 200 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4875500
41 | Haripur 360 MW CCPP(HPL) | 342 | 342 | 252 | 251 | 237 | 231 | 246 | 281 | 281 | 281 | 307 | 325 | 327 | 273 | 239 | 252 | 327 | 327 |  | 327 | 335 | 334 | 336 | 261 | 262 | 261 | 698000
42 | RPCL 210MW CCPP | 106 | 106 | 106 | 106 | 106 | 105 | 71 | 32 | 33 | 33 | 33 | 32 | 32 | 31 | 33 | 33 | 33 | 33 |  | 33 | 43 | 51 | 70 | 70 | 77 | 77 | 1391040
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 8 | 23 | 33 | 46 | 51 | 51 | 49 | 41 | 29 | 14 | 2 | 0 | [8 empty] | 351250
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 42 | 42 | 42 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1011000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 57 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 30 | 58 | 58 | 61 | 58 | 58 | 59 | 56 |  | 57 | 57 | 57 | 57 | 57 | 56 | 56 | 1226016
48 | Shahjibazar 86 MW PP (Shahjibazar) | 70 | 83 | 83 | 30 | 0 | [21 empty] | 282240
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 20 | 20 | 20 | 53 | 60 | 65 | 80 | 90 | 100 | 107 | 125 | 192 | 178 | 188 | 192 | 192 | 192 | 192 |  | 191 | 191 | 191 | 191 | 191 | 190 | 190 | 1966570
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 16 | 16 | 16 | 17 | 17 |  | 18 | 18 | 18 | 17 | 18 | 18 | 18 | 400000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 9 | 10 | 10 | 10 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 245160
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 102816
55 | Fenchugonj 51 MW PP (Barakatullah)
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 14 | 368016
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 265 | 260 | 265 | 285 | 285 | 300 | 310 | 290 | 275 | 310 | 300 | 310 | 265 | 300 | 300 | 300 | 310 |  | 270 | 272 | 270 | 290 | 280 | 260 | 315 | 9026000
| Bibiyana South 400 MW | 300 | 310 | 305 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 |  | 310 | 310 | 310 | 310 | 300 | 310 | 310 | 7412600
58 | Nababganj 55 MW PP (Southern power ) | [17 empty] | 17 |  | 17 | 17 | 17 | 0 |  |  |  | 47980
59 | Tangail Palli Power Gen 22 MW | [13 empty] | 3 | 6 | 6 |  | 6 |  | 6 | 6 | 6 | 6 | 6 | 5 | 3 | 62160
60 | Barabkunda 22 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 284880
61 | Narshingdi 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 404820
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 0 |  |  |  |  | 14 | 14 | 14 | 17 | 17 | 16 | 16 | 16 | 16 | 16 |  | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 322452
63 | Impoprt (Tripura) | 126 | 124 | 122 | 118 | 114 | 104 | 108 | 114 | 116 | 120 | 132 | 130 | 148 | 148 | 156 | 150 | 144 | 158 |  | 158 | 150 | 152 | 146 | 146 | 144 | 140 | 3223680
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 17 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 15 | 15 |  | 20 | 17 | 20 | 35 | 37 | 38 | 36 | 559680
65 | Feni 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 15 | 16 |  | 16 | 15 | 16 | 17 | 17 | 17 | 17 | 408204
66 | Feni 11 MW PP (Doreen) | 11 | 11 |  | 11 | 11 | 11 | 0 | 8 | 8 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 8 |  | 9 | 9 | 9 | 9 | 10 | 10 | 8 | 190620
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 814700
68 | Cumilla 25 MW PP (Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 29520
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456000
70 | Summit Madhabdi | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 13 | 12 | 12 | 12 | 12 | 11 | 12 | 12 | 12 | 11 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 282960
71 | Maona 33 MW PP(Summit) | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 706680
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 16 | 16 | 33 | 33 | 33 | 33 | 32 | 32 | 32 | 16 | 30 | 30 | 30 | 16 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 680400
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 17 | 17 | 17 | 17 | 0 | [12 empty] | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 196080
| Chowmuhani 113 MW | [5 empty] | 9 | 0 |  |  |  | 0 | 7 | 21 | 28 | 28 | 28 | 28 | 28 |  | 37 | 38 | 38 | 39 | 39 | 16 | 16 | 384720
| Manikgonj 162MW PP(MPGL) | [10 empty] | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 24 |  | 35 | 35 | 17 |  |  |  |  | 187200
77 | Siddhirganj 100 PP(Dutch Bangla) | [11 empty] | 0 | 1 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 0 |  |  |  |  | 54144
78 | Gazipur 52 MW PP | [7 empty] | 0 | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 |  | 25 | 8 | 8 | 8 | 0 |  |  | 129010
79 | Kodda 150 MW PP | [12 empty] | 5 | 16 | 16 | 16 | 16 | 75 |  | 48 | 48 | 48 | 16 | 16 | 16 | 16 | 284640
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 42 | 0 | [15 empty] | 3 |  | 16 | 8 | 8 | 8 | 8 | 8 | 8 | 141154
| Gazipur 100 MW PP | [7 empty] | 0 | 17 | 17 | 17 | 17 | 17 | 30 | 35 | 35 | 35 | 70 |  | 34 | 34 | 34 | 17 | 17 | 17 | 17 | 430080
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 1 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 27480
| Jodiac Power | [12 empty] | 0 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 218688
| Karnaphuli Power Ltd. | 17 | 17 | 17 | 17 | 15 | [5 empty] | 0 | 11 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 318653
82 | Madanganj 102 PP(Summit) | [13 empty] | 51 | 45 | 17 | 17 | 22 |  | 52 | 25 | 17 | 16 |  |  |  | 184466
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit) | 146 | 148 | 145 | 149 | 138 | 122 | 144 | 148 | 150 | 150 | 152 | 152 | 145 | 150 | 150 | 151 | 150 | 154 |  | 152 | 152 | 153 | 150 | 148 | 150 | 151 | 3546182
87 | Meghnaghat 100 MW(IEL) | [10 empty] | 0 | 5 | 9 | 8 | 9 | 8 | 9 | 8 |  | 8 | 8 | 8 | 0 |  |  |  | 73920
| Meghnaghat 104 MW PP (OPCL) | [19 empty] | 17 | 17 | 17 | 17 | 17 |  |  | 62400
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 12 | 12 | 12 | 0 | [6 empty] | 0 | 10 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 165600
92 | Fenchuganj 44 MW (Energyprima) | 49 | 49 | 49 | 20 | 20 | 5 | 5 | 5 | 5 | 5 | 45 | 42 | 42 | 43 | 41 | 43 | 41 | 45 |  | 42 | 42 | 42 | 45 | 45 | 48 | 45 | 803664
93 | Ashuganj 51 MW PP (Midland) | 10 | 10 | 10 | 0 |  |  |  | 2 | 10 | 10 | 19 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 776556
94 | Gagnagar 102 MW PP (Digital Power) | [13 empty] | 8 | 8 | 8 | 8 | 8 |  | 8 | 0 | [5 empty] | 54144
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 0 | [12 empty] | 2 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 8 | 151200
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 | [15 empty] | 0
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [12 empty] | 5 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | [5 empty] | 115564
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 17 |  | 35 | 35 | 35 |  |  |  |  | 77080
101 | Kushiara 163 MW CCPP (KP) | 163 | 130 | 130 | 130 | 130 | 120 | 120 | 120 | 163 | 163 | 163 | 163 | 70 | 70 | 110 | 120 | 163 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3296945
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 13850
103 | Kamalaghat 54 MW PP(Banco Energy) | [16 empty] | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 128520
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 0 | [5 empty] | 3 | 8 | 19 | 8 | 8 | 8 | 28 | 28 | 28 | 18 | 18 | 38 |  | 64 | 37 | 24 | 24 | 24 | 24 | 24 | 396000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 10 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 17 | 17 | 27 |  | 82 | 72 | 73 | 43 | 17 | 17 | 17 | 458064
115 | Juldah 100 MW PP Unit-3 (Acorn) | 0 | 12 | 12 | 0 |  |  |  |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 234240
116 | Chandpur 200 MW (Desh energy) | 17 | 17 | 17 | 17 | 0 | [7 empty] | 1 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 282720
117 | Ashuganj 150 MW PP (Midland) | [12 empty] | 3 | 26 | 41 | 6 | 6 | 28 |  | 66 | 6 | [5 empty] | 194036
118 | Bibiyana-III 400 MW CCPP | 332 | 332 | 332 | 332 | 330 | 332 | 363 | 362 | 335 | 336 | 376 | 365 | 365 | 343 | 388 | 393 | 367 | 399 |  | 367 | 367 | 367 | 367 | 367 | 354 | 330 | 8588000
| Jamalpur 115 MW PP (United) | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 35 | 56 | 45 | 45 | 45 | 68 | 79 | 79 | 60 | 59 | 77 |  | 87 | 89 | 89 | 75 | 69 | 65 | 65 | 1166400
| Anwara 300 MW PP (United) | 45 | 45 | 45 | 15 | 15 | 15 | 15 | 15 | 45 | 45 | 65 | 100 | 100 | 80 | 80 | 80 | 80 | 150 |  | 150 | 150 | 120 | 120 | 120 | 120 | 120 | 1886836
| Juldah unit-2 (Acorn) | 12 | 12 | 12 | 0 | [5 empty] | 0 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 215040
| Anlima Energy Ltd. | 17 | 17 | 17 | 17 | 0 | [6 empty] | 3 | 17 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 486764
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 443520
| Spectra Solar Plant Ltd. | [6 empty] | 4 | 12 | 22 | 28 | 30 | 30 | 28 | 23 | 16 | 7 | 1 | [9 empty] | 203511
| Chandpur 115(Doreen) | 18 | 18 | 18 | 0 | [5 empty] | 0 | 2 | 18 | 17 | 18 | 17 | 18 | 18 | 41 |  | 90 | 71 | 62 | 50 | 36 | 34 | 34 | 544320
| Kanchan Purbachal Power Generation Ltd. | [9 empty] | 0 | 1 | 17 | 19 | 34 | 34 | 17 | 17 | 28 |  | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 329400
| Mirsharai 150 MW (Oil) | [13 empty] | 17 | 17 | 17 | 17 | 53 |  | 17 | 17 | 17 |  |  |  |  | 143855
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 1 | 2 | 2 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 4 | 5 | 3 | 6 | 5 | 8 |  | 2 | 2 | 2 | 1 | 1 | 4 | 6 | 52320
| Matarbari 2*600 MW (CPGCL) | 256 | 260 | 258 | 223 | 202 | 201 | 201 | 199 | 196 | 197 | 199 | 199 | 193 | 193 | 195 | 196 | 199 | 200 |  | 193 | 196 | 198 | 198 | 196 | 199 | 200 | 5083636
120 | Eastern Zone Total | 5752 | 5703 | 5483 | 5126 | 4993 | 4864 | 5084 | 5129 | 5281 | 5322 | 5679 | 5956 | 5937 | 6066 | 6154 | 6071 | 6171 | 6864 |  | 7022 | 6909 | 6820 | 6652 | 6375 | 6362 | 6267 | 136883739
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [17 empty] | 16 |  | 0 | [6 empty] | 28800
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [12 empty] | 0 | 0 |  |  |  | 19 | [8 empty] | 115200
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 0 | 10 | 31 | 55 | 71 | 81 | 84 | 78 | 60 | 37 | 18 | 3 | 0 | [8 empty] | 466560
131 | Rampal 1320 MW (BIFPCL) | 352 | 353 | 354 | 353 | 354 | 354 | 354 | 355 | 357 | 357 | 355 | 354 | 353 | 353 | 350 | 351 | 352 | 350 |  | 352 | 351 | 352 | 354 | 355 | 352 | 352 | 8494545
132 | United Payra Power Ltd. | [11 empty] | 0 | [5 empty] | 13 |  | 0 | [6 empty] | 26400
133 | Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 220 | 180 | 222 | 222 | 222 | 222 |  | 222 | 222 | 222 | 222 | 220 | 180 | 180 | 4850700
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [26 empty] | 0
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3687300
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 128 | 128 | 130 | 128 | 100 | 100 | 100 | 2445000
140 | Bhola 33 MW PP (Venture) | 22 | 20 | 20 | 20 | 19 | 18 | 15 | 15 | 12 | 13 | 12 | 16 | 18 | 17 | 17 | 18 | 18 | 23 |  | 23 | 23 | 23 | 23 | 23 | 22 | 21 | 445200
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 8 |  | 8 | 8 | [5 empty] | 18375
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [17 empty] | 15 |  | 9 | [6 empty] | 23184
146 | Bheramara HVDC | 896 | 896 | 895 | 896 | 896 | 896 | 896 | 896 | 896 | 896 | 897 | 897 | 896 | 895 | 896 | 896 | 895 | 896 |  | 802 | 802 | 802 | 896 | 896 | 896 | 896 | 21453090
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 740 | 600 | 560 | 560 | 560 | 560 | 560 | 600 | 610 | 600 | 640 | 700 | 810 | 910 | 940 | 860 | 840 | 920 |  | 1210 | 1244 | 1244 | 1080 | 1000 | 900 | 800 | 20746900
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4144700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 3 | 4 | 4 | 5 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 31740
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 161 | 160 | 140 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 160 | 172 | 163 | 158 | 154 | 154 | 153 |  | 148 | 148 | 148 | 148 | 148 | 148 | 150 | 3767045
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 270 | 270 | 250 | 200 | 200 | 180 | 210 | 250 | 270 | 270 | 300 | 414 | 375 | 309 | 266 | 255 | 234 | 195 |  | 212 | 214 | 214 | 230 | 241 | 234 | 235 | 6210836
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [26 empty] | 0
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 | [10 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 132966
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [17 empty] | 15 | [8 empty] | 20008
168 | Santahar 50 MW Peaking PP | [17 empty] | 37 | [8 empty] | 49150
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | [12 empty] | 7 |  |  |  |  | 47 |  | 25 | 0 | [5 empty] | 70816
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [17 empty] | 9 |  | 30 | 35 | 35 |  |  |  |  | 94944
172 | Confidence Power Bogura Unit-1 113 MW | [17 empty] | 35 |  | 35 | 35 | 0 |  |  |  |  | 79296
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 5 | 107 |  | 45 | 40 | 18 |  |  |  |  | 170275
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 2 | 3 | 6 | 6 | 6 | 6 | 6 | 4 | 2 | 0 | [9 empty] | 41004
178 | Energypac Power Venture Thakurgaon Ltd. | [17 empty] | 32 |  | 35 | 0 | 0 |  |  |  |  | 103872
| Intraco Solar 30 MW | [6 empty] | 3 | 13 | 22 | 29 | 34 | 35 | 32 | 27 | 19 | 8 | 1 | [9 empty] | 225803
| Adani Power Jharkhanda Ltd | 1013 | 913 | 910 | 821 | 817 | 818 | 818 | 819 | 822 | 820 | 817 | 813 | 848 | 861 | 914 | 917 | 918 | 1080 |  | 1161 | 1161 | 1169 | 1169 | 1173 | 1078 | 1036 | 22584511
178 | Teesta Solar Limited | [6 empty] | 23 | 75 | 125 | 165 | 182 | 189 | 175 | 149 | 106 | 46 | 6 | [9 empty] | 1246940