## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-10-30 | Monday
|  | Date (day): | 2023-10-30 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11986.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14532 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-10-29 | 2023-10-30 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 180 | 180 | 180 | 180
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  |  | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 386 | 374 | 400 | 412
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 330 | 327 | 330 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | GT-1 under S/D due to Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 4 | 8 | 8 | 8 | 92 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 152 | 150 | 150 | 150 | 185 |  | GT-1 under S/D due to Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 45 | 95 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 5 | 15 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 10 | 45 | 30 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 15 | 15 | 16 | 16 |  | 6 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 9 | 8 | 8 | 92 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 235 | 222 | 0 | 220 |  | 115
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 8 | 8 | 8 | 94 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 0 | 17 | 37 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 98 | 16 | 132 | 17 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 0 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 0 | 55
| Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
25 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 31 | 29 | 31 | 31 |  | 49 | Engine problem
26 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25
27 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 30 | 30 | 30 | 30
28 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 25 | 8 | 25 | 27 |  | Fuel shortage
29 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
30 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 38 | 85 | 80 | 130 | 170 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
31 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 76 | 17 | 135 | 14 |  | Fuel shortage
32 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 70 | 35 | 88 |  | 17 | Engine problem
33 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 1 | 0 | 17 | 87 |  | Fuel shortage
34 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 35 | 17 | 35 | 127 |  | Fuel shortage
35 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 32 | 0 | 35 | 0
36 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 33 | 35 | 35 | 55
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 98 | 51 | 100 | 100
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 5763 | 5422 | 1972 | 2240 | 1879 | 2627 | 1761 | 947
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
38 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 8 | 8 | 17 | 8 |  | Fuel shortage
39 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 19 | 6 | 18 | 32 |  | Fuel shortage
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 207 | 206 | 205 | 205 |  | 25 | Engine problem
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 213 | 210 | 210 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 17 | 17 | 88 |  | Fuel shortage
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 3 | 63 | 40 | 65 | 33 |  | Fuel shortage
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 17 | 17 |  | 85 | Engine problem
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 12 | 12 | 12 | 12 | 10 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 14 | 10 | 20
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 70 | 170 | 65 | 245 | 55 |  | Fuel shortage
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 17 | 17 | 93 |  | Fuel shortage
55 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
56 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 27 | 17 | 34 | 82 |  | Fuel shortage
57 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 17 | 53 | 35 | 163
58 | SS Power I |  | Coal | SS Power | 1*612 | 612 | 612 | 500 | 624 | 600 | 600 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 4 | 4 | 10 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 192 | 141 | 600 | 600 |  |  | On test.
| Chattogram area Total |  |  |  |  | 3217 | 3157 | 1360 | 1672 | 1947 | 2308 | 990 | 440
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 198 | 193 | 190 | 200 | 21 |  | Gas shortage
60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 280 | 280 | 280 |  |  | FGMO
61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 240 | 240 | 275 | 275 |  |  | FGMO
62 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 240 | 240 | 250 | 250 | 150 |  | Gas shortage
63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 0 | 0 | 0 | 45 |  | Gas shortage
| Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortae
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 33 | 109 | 150 | 150
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 30
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 15 | 18 | 17 | 17 | 183 |  | Fuel shortage
70 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 12 | 17 | 18 | 18 |  | 4 | Engine problem
71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 140 | 154 | 143 | 166
72 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 7 | 52 | 52 | 52
74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 0 | 12 | 12 | 12 |  | 13 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 17 | 0 | 0 | 97 | 17 | Fuel shortage & Engine problem
76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 28 | 77 | 28 | 75 | 38 |  | Fuel shortage
77 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 35 |  | 19 | Engine problem
78 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 18 | 83 | 17 | 94 | 21 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2896 | 1337 | 1601 | 1544 | 1749 | 750 | 216
79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 34 | 33 | 30 | 45 | 157 |  | Gas shortage
80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 16 | 16 | 19 |  | 3 | Engine problem
| Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 38 | 18 | 66 | 100 | 100 |  | Fuel shortage
83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 60 | 40 | 85 | 30 |  | Fuel shortage
84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 55 | 0 | 50 | 0
85 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 212 | 133 | 209.6 | 255 | 157 | 3
86 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 41 | 43 | 43 |  | 27 | Machine problem.
87 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Under maint.
88 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
89 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
90 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0
91 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 42 | 42 | 42 | 42
92 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 2 | 2 | 2 |  | 9 | Engine problem
93 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 62 | 62 | 62
94 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 0 | 0 | 0 | 86 |  | Gas shortage
95 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 191 | 188 | 190 | 190 |  | 41 | Machine problem
97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 16 | 17 | 17 | 18
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 16 | 16 | 16 | 9 |  | Gas shortage
99 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 280 | 280 | 300 |  |  | FGMO
100 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 376 | 376 | 377 | 400 |  |  | FGMO
101 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
102 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 300 | 310 | 300 | 310
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1482 | 1507 | 1502 | 1556 | 95 | 597
103 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 896 | 896 | 902 | 902
104 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 16 | 49 | 65 | 50 |  | Fuel shortage
105 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 29 | 0 | 40 |  | 14 | Engine problem
106 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
107 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 | 49 |  | Fuel shortage
108 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
109 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 0 | 16 | 24 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
110 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 5 | 18 | 53 | 74 | 31 |  | Fuel shortage
111 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 15 | 32 | 73 |  | Fuel shortage
112 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 79 | 0 | 100 | 0
113 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0
114 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 353 | 333 | 350 | 350 | 267 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 1333 | 1315 | 1469 | 1539 | 1150 | 14
115 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 16 | 110
116 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 19 | 22 | 21 | 25 |  | 15 | Engine problem
117 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 126 | 122 | 130 | 130 |  | 64 | ST under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 780 | 680 | 800 | 1244
119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 38 | 150
121 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 150 | 150 | 150 | 150 | 157 |  | Coal shortage
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1295 | 1211 | 1375 | 2029 | 157 | 79
122 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
123 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 30 | 22 |  | Fuel shortage
124 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 16 |  | 55 | Engine problem
125 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 28 | 28
126 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 8 | 34 | 42 |  | 8 | Engine problem
127 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 30 | 40 |  | 10 | Engine problem
128 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 142 | 152 | 150 | 160 | 50 |  | Gas shortage
129 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
130 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
131 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 229 | 201 | 250 | 300 | 154 |  | Gas shortage
132 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 24 | 35 | 15 |  | Fuel shortage
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
133 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
134 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 43 | 8 | 8 | 44 |  | Fuel shortage
135 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 55 | 50 | 94 |  | 10 | Engine problem
136 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
137 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 43 | 35 | 50 | 63 |  | Fuel shortage
138 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 55 | 35 | 57 | 56 |  | Fuel shortage
139 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 907 | 1135 | 950 | 1200 | 296
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 1294 | 1781 | 1611 | 2071 | 1511 | 83
140 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
141 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
142 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
143 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
144 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 108 | 42 | 113
145 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0 | 0 | 8 | 0
146 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 87 | 70 | 115
147 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 35 | 0 | 30 | 0
148 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 185 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 390 | 365 | 450 | 398 | 125 | 189
| Total |  |  |  |  | 25339 | 24599 | 10675 | 11825 | 11986.6 | 14532 | 6696 | 2568
A. |  | 2023-10-29 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 11825 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 8502 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11825 | MW
3 | Day peak Generation : |  |  | 10675 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11641.65 | MW
4 | Evening peak Generation : |  |  | 11825 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 247.7287 | MKWHr | By Solar | 2.7147 | MKWHr
| By Gas : | 123.748 | MKWHr |  | By Oil: | 16.1556 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 75.6737 | MKWHr |  | By Hydro: | 4.8719 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.10896 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6696 | MW | Dhaka | 4437.75 | 4437.75 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2568 | MW | Chittagong | 1232.5 | 1232.5 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 9264 | MW | Khulna | 1340 | 1340 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 943.74 | MMCFD |  |  | Rajshahi | 1092.4 | 1092.4 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 126416801.616 | ii) Oil : | Taka | 211337152.73 | Comilla | 1075 | 1075 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 522991571.96 | Total | Taka | 860745526.306 | Mymensingh | 927 | 927 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 482 | 482 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 1046 | MW (W to E) at | 18:00 | hrs | Barisal | 331 | 331 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 980 | MW at | 5:00 | hrs | Rangpur | 724 | 724 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 32.5°C |  |  | Total | 11641.65 | 11641.65 |  | 0
B. |  | 2023-10-30 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 32.5°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 13000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14532 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 11000 | MW
4 | Reserve(Generation end) |  |  |  | 1532 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 272.3445 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8476 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.3484 | MKWHr. | ii) HVDC Flow at Peak Time |  | 896 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.1075 | MKWHr. | iii) Maximum HVDC Flow : |  | 896 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 103.02 |  | (b) Today: | 102.66 |  | (c) Rule Curve: |  | 108.7
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-10-29 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 344 | 262 |  | 0 | 225 | 147 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 30 | 0 | 0 | 131 | 75 | 0 | 0 | 8 | 209 | 0 | 0 | 0 |  | 0 | 50 | 17 | 12 | 0 | 6 | 12 | 31 | 0 | 0 | 0 | 280 | 240 | 193 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 17 | 8 | 33 | 12 | 130 | 77 | 0 | 19 | 0 | 43 | 0 | 0 | 45 | 163 | 0 | 57 | 0 | 0 | 190 | 18 | 0 | 10 | 270 | 16 | 2 | 0 | 0 | 0 | 0 | 24 | 0 | 17 | 0 | 12 | 17 | 0 | 332 | 65 | 17 | 34 | 0 | 50 | 17 | 17 | 17 | 17 | 12 | 300 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 18 | 17 | 230 | 0 | 0 | 624 | 6 | 200 | 40 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 150 | 915 | 0 | 0 |  | 5996 | 3976 | 9972 | 3358 | 896 | 1679 | 0 | 419 | 3211 | 206 | 0 | 67 | 130 | 0 | 6 | 0 | 103.07
2:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 344 | 261 |  | 0 | 225 | 149 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 30 | 0 | 0 | 130 | 75 | 0 | 0 | 8 | 202 | 0 | 0 | 0 |  | 0 | 0 | 17 | 12 | 0 | 6 | 12 | 40 | 0 | 0 | 0 | 280 | 240 | 200 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 17 | 8 | 33 | 12 | 126 | 77 | 0 | 19 | 0 | 43 | 0 | 0 | 45 | 130 | 0 | 57 | 0 | 0 | 191 | 18 | 0 | 10 | 260 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 12 | 17 | 0 | 332 | 24 | 0 | 34 | 0 | 15 | 0 | 17 | 0 | 9 | 12 | 310 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 18 | 17 | 230 | 0 | 0 | 540 | 8 | 194 | 35 | 0 |  | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 150 | 905 | 0 | 0 |  | 5606 | 3899 | 9505 | 3363 | 895 | 1607 | 0 | 252 | 3032 | 205 | 0 | 17 | 126 | 0 | 8 | 0 | 103.06
3:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 344 | 262 |  | 0 | 225 | 148 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 32 | 0 | 0 | 130 | 75 | 0 | 0 | 8 | 201 | 0 | 0 | 0 |  | 0 | 0 | 17 | 12 | 0 | 6 | 12 | 39 | 0 | 0 | 0 | 280 | 240 | 202 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 17 | 8 | 33 | 12 | 120 | 86 | 0 | 19 | 0 | 43 | 0 | 0 | 5 | 130 | 0 | 57 | 0 | 0 | 190 | 18 | 0 | 10 | 270 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 332 | 24 | 0 | 34 | 0 | 16 | 0 | 17 | 0 | 0 | 12 | 310 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 18 | 0 | 230 | 0 | 0 | 430 | 10 | 200 | 65 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 640 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 150 | 828 | 0 | 0 |  | 5449 | 3757 | 9206 | 3374 | 896 | 1618 | 0 | 193 | 2773 | 205 | 0 | 17 | 120 | 0 | 10 | 0 | 103.05
4:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 344 | 238 |  | 0 | 190 | 146 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 32 | 0 | 0 | 130 | 75 | 0 | 0 | 8 | 201 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 5 | 12 | 40 | 0 | 0 | 0 | 280 | 240 | 208 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 17 | 8 | 33 | 12 | 120 | 86 | 0 | 19 | 0 | 43 | 0 | 0 | 5 | 120 | 0 | 40 | 0 | 0 | 190 | 18 | 0 | 10 | 265 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 334 | 0 | 0 | 34 | 0 | 16 | 0 | 17 | 0 | 0 | 12 | 310 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 18 | 0 | 230 | 0 | 0 | 380 | 12 | 199 | 96 | 0 |  | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 150 | 822 | 0 | 0 |  | 5246 | 3566 | 8812 | 3277 | 895 | 1533 | 0 | 139 | 2614 | 205 | 0 | 17 | 120 | 0 | 12 | 0 | 103.04
5:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 307 | 237 |  | 0 | 170 | 145 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 32 | 0 | 0 | 130 | 75 | 0 | 0 | 8 | 195 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 12 | 35 | 0 | 0 | 0 | 280 | 240 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 33 | 12 | 114 | 86 | 0 | 19 | 0 | 43 | 0 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 190 | 18 | 0 | 10 | 285 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 0 | 320 | 10 | 200 | 100 | 0 |  | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 150 | 815 | 0 | 0 |  | 5026 | 3517 | 8543 | 3235 | 895 | 1499 | 0 | 41 | 2527 | 205 | 0 | 17 | 114 | 0 | 10 | 0 | 103.03
6:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 304 | 236 |  | 0 | 170 | 147 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 13 | 25 | 32 | 0 | 0 | 130 | 75 | 0 | 0 | 8 | 195 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 12 | 40 | 0 | 0 | 0 | 280 | 240 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 33 | 12 | 106 | 75 | 0 | 19 | 0 | 43 | 0 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 190 | 18 | 0 | 10 | 290 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 230 | 0 | 0 | 320 | 7 | 200 | 90 | 0 |  | 894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 150 | 817 | 0 | 0 |  | 4970 | 3532 | 8502 | 3205 | 894 | 1499 | 0 | 25 | 2544 | 205 | 0 | 17 | 106 | 0 | 7 | 0 | 103.02
7:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 307 | 262 |  | 0 | 170 | 146 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 13 | 25 | 32 | 0 | 0 | 131 | 75 | 0 | 0 | 8 | 196 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 12 | 36 | 0 | 0 | 0 | 270 | 330 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 33 | 12 | 104 | 37 | 0 | 19 | 0 | 43 | 0 | 0 | 0 | 163 | 0 | 40 | 0 | 0 | 190 | 17 | 0 | 10 | 300 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 364 | 16 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 7 | 0 | 0 | 0 | 17 | 3 | 0 | 0 | 230 | 0 | 0 | 320 | 6 | 198 | 100 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530 | 220 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 354 | 4 | 150 | 820 | 24 | 0 |  | 5111 | 3762 | 8873 | 3235 | 896 | 1769 | 0 | 45 | 2542 | 206 | 0 | 17 | 104 | 53 | 6 | 0 | 103.01
8:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 364 | 262 |  | 0 | 170 | 147 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 13 | 25 | 31 | 0 | 0 | 131 | 75 | 0 | 0 | 3 | 195 | 0 | 0 | 0 |  | 2 | 0 | 17 | 0 | 0 | 0 | 12 | 9 | 0 | 0 | 0 | 270 | 240 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 33 | 12 | 104 | 34 | 0 | 19 | 1 | 43 | 0 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 190 | 17 | 0 | 10 | 280 | 0 | 2 | 0 | 0 | 0 | 0 | 19 | 0 | 17 | 10 | 0 | 0 | 0 | 364 | 57 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 22 | 0 | 0 | 0 | 17 | 12 | 0 | 0 | 240 | 0 | 0 | 320 | 0 | 200 | 76 | 0 |  | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 640 | 220 | 0 | 0 | 2 | 30 | 0 | 0 | 0 | 355 | 14 | 150 | 817 | 80 | 0 |  | 5080 | 3939 | 9019 | 3245 | 895 | 1613 | 0 | 115 | 2652 | 206 | 0 | 17 | 104 | 172 | 0 | 0 | 103
9:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 396 | 332 |  | 0 | 225 | 150 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 19 | 12 | 25 | 31 | 2 | 0 | 132 | 75 | 0 | 0 | 8 | 204 | 0 | 0 | 0 |  | 6 | 0 | 17 | 0 | 0 | 3 | 12 | 3 | 0 | 0 | 0 | 270 | 240 | 203 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 14 | 8 | 33 | 12 | 114 | 34 | 0 | 19 | 2 | 43 | 0 | 0 | 10 | 120 | 0 | 40 | 0 | 0 | 190 | 17 | 0 | 10 | 275 | 0 | 2 | 0 | 0 | 0 | 0 | 19 | 0 | 17 | 15 | 3 | 0 | 0 | 367 | 57 | 17 | 17 | 3 | 30 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 36 | 0 | 0 | 0 | 17 | 20 | 0 | 0 | 240 | 0 | 0 | 360 | 0 | 190 | 89 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 710 | 220 | 0 | 0 | 3 | 52 | 0 | 0 | 0 | 353 | 24 | 150 | 823 | 130 | 0 |  | 5511 | 4078 | 9589 | 3393 | 896 | 1709 | 0 | 196 | 2756 | 207 | 0 | 33 | 114 | 285 | 0 | 0 | 102.99
10:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 382 | 305 |  | 0 | 180 | 150 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 19 | 12 | 25 | 30 | 8 | 0 | 132 | 75 | 0 | 0 | 8 | 204 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 6 | 12 | 3 | 0 | 0 | 0 | 280 | 240 | 203 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 14 | 8 | 25 | 12 | 122 | 34 | 0 | 19 | 2 | 43 | 0 | 0 | 10 | 140 | 0 | 58 | 0 | 0 | 191 | 17 | 0 | 10 | 280 | 0 | 2 | 0 | 0 | 0 | 0 | 28 | 0 | 17 | 18 | 12 | 0 | 0 | 376 | 56 | 30 | 17 | 4 | 30 | 0 | 0 | 0 | 0 | 12 | 310 | 0 | 35 | 0 | 2 | 0 | 17 | 26 | 3 | 5 | 240 | 0 | 0 | 360 | 1 | 189 | 95 | 0 |  | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 710 | 180 | 0 | 0 | 4 | 68 | 0 | 0 | 0 | 353 | 30 | 150 | 833 | 165 | 0 |  | 5588 | 4094 | 9682 | 3433 | 895 | 1622 | 0 | 269 | 2765 | 207 | 0 | 16 | 122 | 352 | 1 | 0 | 102.98
11:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 383 | 330 |  | 0 | 225 | 152 | 0 | 15 | 0 | 235 | 0 | 0 | 3 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 19 | 12 | 25 | 30 | 8 | 0 | 132 | 75 | 0 | 0 | 8 | 212 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 280 | 240 | 204 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 14 | 8 | 33 | 12 | 126 | 34 | 0 | 19 | 2 | 43 | 0 | 0 | 37 | 163 | 0 | 57 | 0 | 0 | 191 | 17 | 0 | 10 | 300 | 0 | 2 | 0 | 15 | 0 | 0 | 28 | 0 | 17 | 19 | 12 | 2 | 0 | 376 | 66 | 35 | 17 | 4 | 66 | 0 | 14 | 0 | 7 | 12 | 300 | 0 | 29 | 0 | 17 | 0 | 17 | 31 | 18 | 17 | 240 | 0 | 0 | 450 | 3 | 190 | 97 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 740 | 180 | 0 | 0 | 5 | 77 | 0 | 0 | 0 | 352 | 35 | 150 | 872 | 181 | 0 |  | 6010 | 4180 | 10190 | 3440 | 896 | 1769 | 0 | 426 | 2924 | 207 | 0 | 16 | 126 | 383 | 3 | 0 | 102.97
12:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 386 | 330 |  | 0 | 225 | 152 | 4 | 45 | 5 | 235 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 19 | 12 | 25 | 30 | 8 | 0 | 132 | 75 | 0 | 0 | 8 | 213 | 0 | 0 | 0 |  | 6 | 3 | 0 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 280 | 240 | 198 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 7 | 12 | 8 | 33 | 0 | 140 | 34 | 0 | 18 | 2 | 43 | 0 | 0 | 42 | 163 | 0 | 59 | 0 | 0 | 191 | 16 | 0 | 10 | 280 | 0 | 2 | 0 | 38 | 0 | 0 | 38 | 0 | 17 | 20 | 12 | 15 | 33 | 376 | 59 | 34 | 17 | 4 | 70 | 17 | 17 | 17 | 28 | 12 | 300 | 0 | 55 | 17 | 17 | 0 | 17 | 32 | 18 | 33 | 240 | 17 | 0 | 500 | 4 | 192 | 98 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 220 | 0 | 0 | 5 | 79 | 0 | 0 | 0 | 353 | 35 | 150 | 907 | 185 | 0 |  | 6363 | 4312 | 10675 | 3456 | 896 | 1819 | 0 | 648 | 3052 | 207 | 0 | 36 | 140 | 417 | 4 | 0 | 102.96
13:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 408 | 300 |  | 0 | 225 | 150 | 8 | 60 | 15 | 235 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 19 | 11 | 25 | 30 | 8 | 0 | 132 | 75 | 0 | 0 | 8 | 217 | 0 | 0 | 0 |  | 6 | 40 | 0 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 280 | 240 | 196 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 27 | 15 | 8 | 33 | 0 | 142 | 32 | 0 | 18 | 2 | 40 | 0 | 0 | 42 | 130 | 0 | 59 | 0 | 0 | 191 | 16 | 0 | 10 | 285 | 0 | 2 | 0 | 60 | 0 | 0 | 38 | 0 | 17 | 19 | 12 | 17 | 56 | 376 | 69 | 35 | 17 | 4 | 70 | 17 | 17 | 17 | 26 | 12 | 300 | 0 | 25 | 17 | 30 | 0 | 17 | 29 | 18 | 35 | 240 | 53 | 0 | 500 | 6 | 137 | 81 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 13 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 900 | 220 | 0 | 0 | 5 | 73 | 0 | 0 | 0 | 353 | 33 | 150 | 1017 | 162 | 0 |  | 6416 | 4481 | 10897 | 3461 | 896 | 1715 | 0 | 782 | 3227 | 207 | 0 | 109 | 142 | 352 | 6 | 0 | 102.95
14:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 411 | 303 |  | 0 | 225 | 153 | 9 | 64 | 15 | 232 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 19 | 11 | 25 | 30 | 8 | 0 | 131 | 75 | 0 | 0 | 8 | 216 | 0 | 0 | 0 |  | 6 | 40 | 17 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 280 | 240 | 194 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 43 | 14 | 8 | 33 | 0 | 146 | 32 | 0 | 16 | 2 | 40 | 0 | 0 | 42 | 163 | 0 | 58 | 0 | 0 | 191 | 16 | 0 | 10 | 290 | 0 | 2 | 0 | 60 | 0 | 0 | 38 | 0 | 17 | 16 | 12 | 17 | 68 | 377 | 69 | 35 | 17 | 3 | 70 | 17 | 17 | 17 | 28 | 12 | 300 | 0 | 41 | 17 | 34 | 0 | 17 | 25 | 18 | 35 | 240 | 53 | 0 | 500 | 5 | 136 | 100 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 17 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 650 | 180 | 0 | 0 | 4 | 58 | 0 | 0 | 0 | 340 | 27 | 150 | 1025 | 141 | 0 |  | 6538 | 4221 | 10759 | 3455 | 896 | 1731 | 0 | 906 | 2971 | 206 | 0 | 126 | 146 | 317 | 5 | 0 | 102.97
15:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 406 | 330 |  | 0 | 225 | 152 | 9 | 78 | 15 | 228 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 19 | 11 | 25 | 30 | 8 | 0 | 131 | 75 | 0 | 0 | 8 | 216 | 0 | 0 | 0 |  | 6 | 40 | 17 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 280 | 240 | 195 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 43 | 14 | 8 | 33 | 12 | 140 | 32 | 0 | 16 | 1 | 42 | 0 | 0 | 41 | 163 | 0 | 60 | 0 | 0 | 188 | 16 | 0 | 10 | 315 | 8 | 2 | 0 | 55 | 0 | 0 | 38 | 0 | 17 | 11 | 12 | 17 | 72 | 379 | 69 | 35 | 17 | 2 | 70 | 17 | 17 | 17 | 28 | 12 | 310 | 7 | 24 | 17 | 34 | 0 | 17 | 18 | 17 | 35 | 240 | 53 | 0 | 502 | 4 | 180 | 100 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 17 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 600 | 180 | 0 | 0 | 2 | 40 | 0 | 0 | 0 | 333 | 19 | 150 | 1012 | 101 | 0 |  | 6632 | 4082 | 10714 | 3460 | 896 | 1758 | 0 | 959 | 2947 | 206 | 0 | 126 | 140 | 218 | 4 | 0 | 102.93
16:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 408 | 260 |  | 0 | 225 | 153 | 8 | 95 | 15 | 225 | 0 | 0 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 19 | 7 | 25 | 30 | 8 | 0 | 131 | 75 | 0 | 0 | 8 | 216 | 0 | 0 | 0 |  | 6 | 47 | 16 | 12 | 0 | 7 | 12 | 2 | 0 | 0 | 0 | 280 | 240 | 195 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 43 | 16 | 8 | 33 | 12 | 140 | 32 | 0 | 16 | 1 | 42 | 0 | 0 | 41 | 130 | 0 | 60 | 0 | 0 | 188 | 16 | 0 | 10 | 290 | 16 | 2 | 0 | 49 | 0 | 0 | 18 | 0 | 17 | 6 | 12 | 18 | 85 | 377 | 59 | 35 | 17 | 1 | 70 | 17 | 17 | 17 | 28 | 12 | 310 | 16 | 16 | 17 | 17 | 0 | 17 | 10 | 18 | 35 | 240 | 17 | 0 | 558 | 2 | 138 | 100 | 0 |  | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 17 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 600 | 180 | 0 | 0 | 1 | 19 | 0 | 0 | 0 | 334 | 8 | 150 | 1012 | 46 | 0 |  | 6441 | 3968 | 10409 | 3412 | 895 | 1642 | 0 | 930 | 2962 | 206 | 0 | 112 | 140 | 108 | 2 | 0 | 102.92
17:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 384 | 276 |  | 0 | 225 | 151 | 9 | 85 | 15 | 224 | 0 | 0 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 15 | 19 | 7 | 33 | 30 | 8 | 0 | 131 | 75 | 0 | 0 | 8 | 216 | 0 | 0 | 0 |  | 6 | 62 | 17 | 12 | 0 | 14 | 12 | 2 | 0 | 0 | 0 | 280 | 240 | 191 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 52 | 17 | 8 | 33 | 12 | 134 | 32 | 0 | 16 | 0 | 42 | 0 | 0 | 42 | 130 | 0 | 61 | 0 | 0 | 188 | 17 | 0 | 10 | 300 | 16 | 2 | 0 | 46 | 0 | 0 | 18 | 0 | 17 | 0 | 12 | 34 | 89 | 377 | 60 | 35 | 17 | 0 | 97 | 17 | 17 | 17 | 58 | 12 | 310 | 0 | 1 | 17 | 17 | 0 | 17 | 1 | 19 | 35 | 240 | 17 | 0 | 624 | 4 | 134 | 71 | 0 |  | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 80 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 43 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 17 | 0 | 35 | 3 | 20 | 0 | 0 | 35 | 600 | 180 | 0 | 2 | 0 | 3 | 0 | 0 | 0 | 333 | 1 | 150 | 1011 | 6 | 0 |  | 6545 | 3971 | 10516 | 3395 | 895 | 1642 | 0 | 1074 | 3022 | 206 | 0 | 132 | 134 | 12 | 4 | 0 | 102.91
18:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 374 | 327 |  | 0 | 225 | 150 | 8 | 95 | 15 | 222 | 0 | 0 | 9 | 8 | 98 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 15 | 19 | 10 | 25 | 30 | 25 | 0 | 131 | 75 | 0 | 0 | 8 | 210 | 0 | 0 | 0 |  | 6 | 63 | 34 | 12 | 0 | 19 | 12 | 14 | 0 | 0 | 0 | 280 | 240 | 193 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 52 | 17 | 8 | 33 | 12 | 154 | 33 | 0 | 16 | 0 | 41 | 0 | 0 | 42 | 163 | 0 | 62 | 0 | 0 | 188 | 17 | 0 | 10 | 280 | 16 | 2 | 0 | 85 | 0 | 0 | 18 | 0 | 76 | 0 | 12 | 18 | 109 | 376 | 60 | 70 | 17 | 0 | 170 | 17 | 17 | 17 | 77 | 12 | 310 | 1 | 0 | 35 | 27 | 0 | 17 | 0 | 83 | 35 | 240 | 53 | 0 | 624 | 4 | 141 | 51 | 0 |  | 896 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 29 | 0 | 8 | 122 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 8 | 40 | 43 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 18 | 0 | 43 | 15 | 108 | 0 | 0 | 55 | 680 | 220 | 0 | 17 | 0 | 0 | 87 | 0 | 0 | 333 | 0 | 150 | 1135 | 0 | 0 |  | 7153 | 4672 | 11825 | 3466 | 896 | 1756 | 0 | 1700 | 3233 | 206 | 0 | 410 | 154 | 0 | 4 | 0 | 102.9
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 423 | 327 |  | 0 | 225 | 152 | 9 | 48 | 15 | 223 | 0 | 0 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 15 | 19 | 12 | 33 | 30 | 8 | 0 | 131 | 75 | 0 | 0 | 0 | 210 | 0 | 0 | 0 |  | 6 | 75 | 17 | 12 | 0 | 19 | 12 | 2 | 0 | 0 | 0 | 280 | 240 | 190 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 15 | 8 | 33 | 12 | 142 | 34 | 0 | 19 | 0 | 43 | 0 | 0 | 48 | 163 | 0 | 62 | 0 | 0 | 188 | 17 | 0 | 10 | 260 | 16 | 2 | 0 | 15 | 0 | 0 | 65 | 0 | 112 | 0 | 12 | 18 | 50 | 376 | 89 | 35 | 17 | 0 | 170 | 17 | 17 | 17 | 55 | 12 | 300 | 16 | 0 | 17 | 34 | 0 | 17 | 0 | 72 | 30 | 240 | 34 | 0 | 623 | 5 | 143 | 35 | 0 |  | 895 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 2 | 0 | 8 | 122 | 21 | 16 | 0 | 0 | 0 | 28 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 34 | 0 | 35 | 15 | 34 | 0 | 0 | 0 | 960 | 220 | 0 | 17 | 0 | 0 | 54 | 0 | 0 | 332 | 0 | 150 | 1170 | 0 | 0 |  | 6880 | 4686 | 11566 | 3516 | 895 | 1714 | 0 | 1327 | 3548 | 206 | 0 | 213 | 142 | 0 | 5 | 0 | 102.84
19:30 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 396 | 327 |  | 0 | 225 | 151 | 0 | 17 | 15 | 222 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 15 | 19 | 12 | 33 | 30 | 0 | 0 | 131 | 75 | 0 | 0 | 0 | 209 | 0 | 0 | 0 |  | 6 | 82 | 17 | 12 | 0 | 19 | 12 | 2 | 0 | 0 | 0 | 280 | 240 | 188 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 15 | 8 | 32 | 12 | 146 | 67 | 0 | 19 | 0 | 43 | 0 | 0 | 48 | 163 | 0 | 62 | 0 | 0 | 191 | 17 | 0 | 10 | 300 | 16 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 88 | 0 | 12 | 18 | 0 | 377 | 89 | 17 | 17 | 0 | 170 | 17 | 17 | 17 | 24 | 12 | 310 | 16 | 0 | 0 | 34 | 0 | 17 | 0 | 72 | 34 | 240 | 17 | 0 | 653 | 2 | 148 | 100 | 0 |  | 895 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 130 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208 | 17 | 0 | 0 | 15 | 34 | 0 | 0 | 0 | 1060 | 220 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 335 | 0 | 150 | 1178 | 0 | 0 |  | 6754 | 4654 | 11408 | 3539 | 895 | 1825 | 0 | 953 | 3694 | 206 | 0 | 148 | 146 | 0 | 2 | 0 | 102.86
20:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 396 | 327 |  | 0 | 225 | 152 | 0 | 17 | 15 | 220 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 15 | 19 | 12 | 33 | 30 | 0 | 0 | 131 | 75 | 0 | 0 | 0 | 209 | 0 | 0 | 0 |  | 6 | 81 | 17 | 12 | 0 | 19 | 12 | 2 | 0 | 0 | 0 | 280 | 240 | 186 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 15 | 8 | 25 | 12 | 142 | 100 | 0 | 19 | 0 | 43 | 0 | 0 | 48 | 163 | 0 | 58 | 0 | 0 | 189 | 17 | 0 | 10 | 280 | 16 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 79 | 0 | 12 | 18 | 0 | 377 | 65 | 17 | 17 | 0 | 170 | 17 | 17 | 17 | 24 | 12 | 310 | 16 | 0 | 0 | 34 | 0 | 17 | 0 | 72 | 34 | 240 | 17 | 0 | 646 | 2 | 142 | 44 | 0 |  | 895 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 17 | 0 | 0 | 4 | 20 | 0 | 0 | 0 | 1080 | 220 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 333 | 0 | 150 | 1166 | 0 | 0 |  | 6644 | 4647 | 11291 | 3547 | 895 | 1778 | 0 | 887 | 3687 | 206 | 0 | 147 | 142 | 0 | 2 | 0 | 102.86
21:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 395 | 333 |  | 0 | 225 | 150 | 0 | 17 | 0 | 220 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 19 | 12 | 33 | 30 | 0 | 0 | 131 | 75 | 0 | 0 | 0 | 195 | 0 | 0 | 0 |  | 6 | 81 | 17 | 12 | 0 | 19 | 12 | 2 | 0 | 0 | 0 | 280 | 240 | 185 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 15 | 8 | 25 | 12 | 138 | 95 | 0 | 19 | 0 | 43 | 0 | 0 | 49 | 163 | 0 | 62 | 0 | 0 | 191 | 17 | 0 | 10 | 270 | 16 | 2 | 0 | 0 | 0 | 0 | 24 | 0 | 35 | 0 | 12 | 18 | 0 | 376 | 65 | 17 | 17 | 0 | 170 | 17 | 17 | 17 | 28 | 12 | 310 | 17 | 0 | 0 | 34 | 0 | 17 | 0 | 62 | 17 | 240 | 0 | 0 | 640 | 5 | 143 | 73 | 0 |  | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 150 | 1171 | 0 | 0 |  | 6511 | 4619 | 11130 | 3531 | 895 | 1806 | 0 | 692 | 3727 | 206 | 0 | 130 | 138 | 0 | 5 | 0 | 102.84
22:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 400 | 302 |  | 0 | 225 | 148 | 0 | 8 | 0 | 220 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 19 | 12 | 33 | 30 | 0 | 0 | 131 | 75 | 0 | 0 | 0 | 195 | 0 | 0 | 0 |  | 6 | 81 | 17 | 12 | 0 | 19 | 12 | 5 | 0 | 0 | 0 | 280 | 240 | 186 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 8 | 25 | 12 | 134 | 95 | 0 | 19 | 0 | 43 | 0 | 0 | 49 | 130 | 0 | 60 | 0 | 0 | 191 | 17 | 0 | 10 | 270 | 16 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 30 | 0 | 12 | 18 | 0 | 376 | 65 | 17 | 17 | 0 | 80 | 17 | 17 | 17 | 28 | 12 | 310 | 0 | 0 | 0 | 34 | 0 | 17 | 0 | 53 | 17 | 240 | 0 | 0 | 512 | 4 | 144 | 46 | 0 |  | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 150 | 1165 | 0 | 0 |  | 6084 | 4602 | 10686 | 3491 | 895 | 1710 | 0 | 529 | 3603 | 206 | 0 | 114 | 134 | 0 | 4 | 0 | 102.82
23:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 359 | 303 |  | 0 | 225 | 147 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 19 | 12 | 33 | 30 | 0 | 0 | 131 | 75 | 0 | 0 | 0 | 195 | 0 | 0 | 0 |  | 6 | 75 | 17 | 12 | 0 | 19 | 12 | 12 | 0 | 0 | 0 | 280 | 240 | 190 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 8 | 25 | 12 | 134 | 95 | 0 | 19 | 0 | 43 | 0 | 0 | 49 | 130 | 0 | 57 | 0 | 0 | 191 | 17 | 0 | 10 | 280 | 16 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 0 | 12 | 17 | 0 | 377 | 65 | 17 | 17 | 0 | 80 | 17 | 17 | 17 | 28 | 12 | 310 | 0 | 0 | 0 | 34 | 0 | 17 | 0 | 53 | 17 | 240 | 0 | 0 | 495 | 3 | 144 | 100 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 150 | 1061 | 0 | 0 |  | 6053 | 4381 | 10434 | 3459 | 896 | 1780 | 0 | 490 | 3358 | 206 | 0 | 108 | 134 | 0 | 3 | 0 | 102.8
24:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 352 | 302 |  | 0 | 225 | 150 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 19 | 12 | 33 | 30 | 0 | 0 | 131 | 75 | 0 | 0 | 0 | 173 | 0 | 0 | 0 |  | 0 | 66 | 17 | 12 | 0 | 6 | 12 | 14 | 0 | 0 | 0 | 280 | 240 | 195 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 8 | 25 | 12 | 128 | 95 | 0 | 19 | 0 | 43 | 0 | 0 | 49 | 130 | 0 | 57 | 0 | 0 | 190 | 18 | 0 | 9 | 280 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 12 | 17 | 0 | 377 | 45 | 0 | 17 | 0 | 80 | 17 | 17 | 0 | 29 | 12 | 310 | 0 | 0 | 0 | 34 | 0 | 17 | 0 | 53 | 17 | 240 | 0 | 0 | 495 | 6 | 145 | 75 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 980 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 150 | 1054 | 0 | 0 |  | 5893 | 4326 | 10219 | 3419 | 896 | 1739 | 0 | 410 | 3332 | 206 | 0 | 83 | 128 | 0 | 6 | 0 | 102.78
KWH | 0 | 0 | 3560031 | 0 | 0 | 0 | 0 | 9062400 | 7022000 |  | 0 | 4976000 | 3609745 | 64320 | 568030 | 147761 | 5223093 | 0 | 0 | 66240 | 72144 | 389280 | 0 | 0 | 0 | 0 | 102600 | 64552 | 94880 | 367056 | 456000 | 275760 | 648700 | 715000 | 108149 | 0 | 3055909 | 1816000 | 0 | 0 | 154720 | 4889029 | 0 | 0 | 0 |  | 101280 | 801408 | 354175 | 197400 | 0 | 218880 | 292272 | 367680 | 0 | 0 | 0 | 7154900 | 6039000 | 4793000 | 0 | 0 | 0 | 0 | 0 | 747352 | 0 | 0 | 334627 | 372024 | 185400 | 758500 | 258500 | 3107520 | 1314240 | 0 | 424944 | 14000 | 1007000 | 0 | 0 | 718992 | 3543463 | 0 | 1296576 | 0 | 0 | 4856890 | 400000 | 0 | 251100 | 6891000 | 218352 | 48384 | 0 | 514364 | 0 | 0 | 511200 | 0 | 596448 | 140670 | 246720 | 294240 | 567054 | 8783000 | 1246800 | 495360 | 434909 | 28199 | 1658509 | 263977 | 334544 | 233700 | 505680 | 229440 | 7389400 | 72960 | 307060 | 172800 | 479236 | 0 | 443520 | 205714 | 680640 | 456120 | 5863000 | 274327 | 0 | 11699999 | 108960 | 4181818 | 1694545 | 0 |  | 21348363 | 0 | 0 | 0 | 50880 | 0 | 0 | 0 | 44160 | 0 | 23250 | 2483000 | 448000 | 17664 | 0 | 0 | 0 | 24493 | 0 | 89200 | 0 | 60887 | 40208 | 103291 | 45086 | 0 | 0 | 214668 | 0 | 0 | 4121800 | 0 | 0 | 3750009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5521672 | 195360 | 0 | 253536 | 46512 | 181046 | 0 | 984 | 216672 | 20112600 | 4856345 | 0 | 40800 | 35100 | 516960 | 169536 | 0 | 0 | 8290909 | 232438 | 3687300 | 23579273 | 1233560 | 0 |  | 145693171 | 102035562 | 247728733 | 83100128 | 21348363 | 40647894 | 0 | 14093238 | 75673699 | 4871909 | 0 | 2062337 | 3107520 | 2714685 | 108960 | 0
Fuel Cost | 0 | 0 | 5197645.26 | 0 | 0 | 0 | 0 | 9515520 | 7583760 |  | 0 | 5423840 | 4006816.95 | 719097.6 | 7526397.5 | 1957833.25 | 5849864.16 | 0 | 0 | 968428.8 | 1015066.08 | 6310228.8 | 0 | 0 | 0 | 0 | 1305072 | 871452 | 1272340.8 | 275292 | 342000 | 0 | 0 | 0 | 1839614.49 | 0 | 825095.43 | 490320 | 0 | 0 | 2529672 | 5084590.16 | 0 | 0 | 0 |  | 1321704 | 13367485.44 | 6028058.5 | 2666874 | 0 | 2532441.6 | 371185.44 | 1224374.4 | 0 | 0 | 0 | 7941939 | 6582510 | 5559880 | 0 | 0 | 0 | 0 | 0 | 1248077.84 | 0 | 0 | 4500733.15 | 509672.88 | 139050 | 1327375 | 193875 | 22311993.6 | 1432521.6 | 0 | 577923.84 | 223160 | 1379590 | 0 | 0 | 1243856.16 | 4074982.45 | 0 | 2515357.44 | 0 | 0 | 4905458.9 | 860000 | 0 | 497178 | 6891000 | 163764 | 36771.84 | 0 | 7021068.6 | 0 | 0 | 6890976 | 0 | 8260804.8 | 1644432.3 | 2546150.4 | 4019318.4 | 7524806.58 | 8080360 | 15161088 | 7162905.6 | 5501598.85 | 438776.44 | 19470895.66 | 2874709.53 | 3556202.72 | 3171309 | 6518215.2 | 2702803.2 | 6798248 | 944832 | 4437017 | 2192832 | 5453705.68 | 0 | 5792371.2 | 2458282.3 | 10189180.8 | 6007100.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 64045089 | 0 | 0 | 0 | 529660.8 | 0 | 0 | 0 | 795321.6 | 0 | 334102.5 | 2780960 | 869120 | 192537.6 | 0 | 0 | 0 | 410747.61 | 0 | 1395088 | 0 | 1008288.72 | 679917.28 | 1407856.33 | 760600.82 | 0 | 0 | 162503.676 | 0 | 0 | 34952864 | 0 | 0 | 4350010.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5466455.28 | 2625638.4 | 0 | 2999330.88 | 672098.4 | 2299284.2 | 0 | 10873.2 | 2630398.08 | 166934580 | 4953471.9 | 0 | 301920 | 396981 | 6063940.8 | 2598986.88 | 0 | 0 | 75364362.81 | 0 | 44136981 | 201602784.15 | 0 | 0 |  | 330358732.02 | 633732755.356 | 964091487.376 | 82933868.636 | 64045089 | 43482932.98 | 0 | 181589704.68 | 522991571.96 | 1315415.43 | 0 | 29747448.05 | 22311993.6 | 15673463.04 | 0 | 0
Yesterday Day Peak | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 386 | 330 |  | 0 | 225 | 152 | 4 | 45 | 5 | 235 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 19 | 12 | 25 | 30 | 8 | 0 | 132 | 75 | 0 | 0 | 8 | 213 | 0 | 0 | 0 |  | 6 | 3 | 0 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 280 | 240 | 198 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 7 | 12 | 8 | 33 | 0 | 140 | 34 | 0 | 18 | 2 | 43 | 0 | 0 | 42 | 163 | 0 | 59 | 0 | 0 | 191 | 16 | 0 | 10 | 280 | 0 | 2 | 0 | 38 | 0 | 0 | 38 | 0 | 17 | 20 | 12 | 15 | 33 | 376 | 59 | 34 | 17 | 4 | 70 | 17 | 17 | 17 | 28 | 12 | 300 | 0 | 55 | 17 | 17 | 0 | 17 | 32 | 18 | 33 | 240 | 17 | 0 | 500 | 4 | 192 | 98 | 0 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 220 | 0 | 0 | 5 | 79 | 0 | 0 | 0 | 353 | 35 | 150 | 907 | 185 | 0 |  | 10675 | DayPeak
Yesterday Evening Peak | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 374 | 327 |  | 0 | 225 | 150 | 8 | 95 | 15 | 222 | 0 | 0 | 9 | 8 | 98 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 15 | 19 | 10 | 25 | 30 | 25 | 0 | 131 | 75 | 0 | 0 | 8 | 210 | 0 | 0 | 0 | 0 | 6 | 63 | 34 | 12 | 0 | 19 | 12 | 14 | 0 | 0 | 0 | 280 | 240 | 193 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 52 | 17 | 8 | 33 | 12 | 154 | 33 | 0 | 16 | 0 | 41 | 0 | 0 | 42 | 163 | 0 | 62 | 0 | 0 | 188 | 17 | 0 | 10 | 280 | 16 | 2 | 0 | 85 | 0 | 0 | 18 | 0 | 76 | 0 | 12 | 18 | 109 | 376 | 60 | 70 | 17 | 0 | 170 | 17 | 17 | 17 | 77 | 12 | 310 | 1 | 0 | 35 | 27 | 0 | 17 | 0 | 83 | 35 | 240 | 53 | 0 | 624 | 4 | 141 | 51 | 0 |  | 896 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 29 | 0 | 8 | 122 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 8 | 40 | 43 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 18 | 0 | 43 | 15 | 108 | 0 | 0 | 55 | 680 | 220 | 0 | 17 | 0 | 0 | 87 | 0 | 0 | 333 | 0 | 150 | 1135 | 0 | 0 |  | 11825 | EvPeak
Forecast for Evening | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 412 | 330 |  | 0 | 225 | 150 | 8 | 100 | 15 | 220 | 0 | 0 | 8 | 8 | 132 | 45 | 0 | 0 | 0 | 17 | 35 | 55 | 16 | 19 | 12 | 25 | 30 | 25 | 0 | 130 | 75 | 0 | 0 | 17 | 215 | 0 | 0 | 0 |  | 6 | 65 | 17 | 12 | 0 | 18 | 12 | 20 | 0 | 0 | 0 | 280 | 275 | 200 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 30 | 52 | 18 | 11 | 33 | 12 | 166 | 45 | 0 | 19 | 0 | 43 | 0 | 0 | 42 | 163 | 0 | 62 | 0 | 0 | 190 | 18 | 0 | 10 | 300 | 16 | 2 | 0 | 130 | 0 | 0 | 100 | 0 | 135 | 0 | 12 | 17 | 150 | 400 | 85 | 88 | 17 | 0 | 245 | 17 | 17 | 0 | 75 | 12 | 310 | 17 | 0 | 35 | 34 | 0 | 35 | 0 | 94 | 55 | 250 | 163 | 0 | 600 | 10 | 600 | 100 | 0 |  | 902 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 40 | 60 | 16 | 130 | 25 | 110 | 0 | 0 | 0 | 30 | 16 | 94 | 28 | 42 | 40 | 8 | 35 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 74 | 0 | 50 | 32 | 113 | 0 | 0 | 57 | 1244 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 350 | 0 | 150 | 1200 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 400 | 330 | 0 | 0 | 225 | 150 | 8 | 100 | 15 | 0 | 0 | 0 | 8 | 8 | 16 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 19 | 12 | 25 | 30 | 8 | 0 | 130 | 75 | 0 | 0 | 8 | 210 |  | 0 | 0 | 0 | 6 | 40 | 17 | 12 | 0 | 6 | 12 | 10 | 0 | 0 | 0 | 280 | 275 | 190 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 11 | 33 | 12 | 143 | 30 | 0 | 16 | 1.6 | 43 | 0 | 0 | 42 | 163 | 0 | 62 | 0 | 0 | 190 | 17 | 0 | 10 | 280 | 16 | 2 | 0 | 80 | 0 | 0 | 66 | 0 | 17 | 20 | 12 | 17 | 150 | 377 | 40 | 35 | 17 | 5 | 65 | 17 | 17 | 0 | 28 | 12 | 300 | 0 | 50 | 17 | 17 | 0 | 17 | 35 | 17 | 35 | 250 | 35 |  | 600 | 10 | 600 | 100 | 0 |  | 902 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 28 | 34 | 30 | 8 | 24 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 53 | 0 | 35 | 15 | 42 | 0 | 8 | 35 | 800 | 220 |  | 38 | 6 | 100 | 70 | 0 |  | 350 | 30 | 150 | 950 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 392 | 273 | 0 | 0 | 225 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 19 | 12 | 25 | 30 | 0 | 0 | 131 | 75 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 12 | 7 | 0 | 0 | 0 | 280 | 275 | 160 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 18 | 8 | 25 | 12 | 104 | 34 | 0 | 19 | 1 | 43 | 0 | 0 | 20 | 120 | 0 | 62 | 0 | 0 | 190 | 17 | 0 | 10 | 280 | 0 | 2 | 0 | 0 | 0 | 0 | 19 | 0 | 13 | 11 | 1 | 0 | 0 | 377 | 56 | 17 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 9 | 0 | 0 | 0 | 17 | 12 | 0 | 0 | 240 | 0 | 0 | 385 | 3 | 137 | 83 | 0 | 0 | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 660 | 220 | 0 | 0 | 2 | 31 | 0 | 0 | 0 | 339 | 15 | 150 | 1010 | 83 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
[22 empty] | 299565 | [26 empty] | 399366 | [49 empty] | 299523 |  | 299563 |  | 399588 |  | 299281 | 299229 | 299524 |  | 399747 |  |  |  |  | 399575 | 399337 | 399589 | [8 empty] | 399245 |  |  | 399274 |  | 399223 |  | 399630 | [12 empty] | 599468 | [32 empty] | 599787 |  | 499268 | 599634 | 43212 |  |  | 499720 | 599730 | [18 empty] | 292.3904
| Minimum Generation |  | 8502 | 6:00 | [202 empty] | 123748022
| Highest Generation |  | 11825 | 18:00 | [202 empty] | 123.748 |  |  |  |  | 2.7147
| Day Peak Generation |  | 10675 | 12:00 | [202 empty] | 16155575
| Evening Peak Generation |  | 11825 | 18:00 | [202 empty] | 16.1556 |  |  | 40647894 |  | 4.8719
| HVDC Max Flow |  | 896 | 1:00 | [202 empty] | 21.3484 |  |  |  |  | 0.10896
| HVDC EvPeak Flow |  | 896 | 18:00 | [200 empty] | 247728733 |  | 3.1075 |  | 75.6737
| Load factor L.F |  | 87.29% | [166 empty] | 1275.5 | [36 empty] | 247.7287

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-10-30
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-10-29 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 10675 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 8476
Evening Peak Generation : |  |  | 11825 | MW Hour : | 18:00 | Available Max Generation : |  | 14532
E.P. Demand (at gen end) : |  |  | 11825 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 13000
Maximum Generation : |  |  | 11825 | MW Hour : | 18:00 | Reserve(Generation end) |  | 1532
Total Gen. (MKWH) : |  |  | 247.7287 | System Load Factor : | 87.29% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 980 | MW at | 5:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-10-30
Actual : |  | 102.66 | Ft.(MSL) , | Rule curve : | 108.7 | Ft.( MSL )
Gas Consumed : |  | Total = | 943.74 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 126416801.616
: |  |  | Coal : | 522991571.96 | Oil : | 211337152.73 | Total : | 860745526.306
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4372.6492 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1200.296 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1681.0207 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1460.7805 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1202.1318 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 893.9104 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 501.2489 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 417.5625 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 816.683 |  |  | 0 | 0%
Total |  | 0 |  | 12546.2832 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
8:06 | 14:05 | Khulna (C) S/S Bus Coupler Scheduled S/D Due to Yearly Maintenance.
8:14 | 17:23 | Madaripur 132/33kV S/S T1-405T LT Scheduled S/D Due to Annual Maintenance.
8:15 | 17:22 | Madaripur 132/33kV S/S T1-405T HT Scheduled S/D Due to Annual maintenance.
8:22 | 14:40 | Panchagarh 132/33kV S/S T-3(A+B)(427T) LT Scheduled S/D Due to Annual Maintenance.
8:22 | 14:39 | Panchagarh 132/33kV S/S T-3(A+B)(427T) HT Scheduled S/D Due to Annual Maintenance.
8:26 | 14:55 | Saidpur 132/33kV S/S TR-5 (434T) LT Scheduled S/D Due to Annual Maintenance work.
8:27 | 14:54 | Saidpur 132/33kV S/S TR-5 (434T) HT Scheduled S/D Due to Annual maintenance work.
8:30 | 14:38 | Palashbari 132/33kV S/S TR4-434T HT Scheduled S/D Due to Annual Maintenance.
8:30 | 14:40 | Palashbari 132/33kV S/S TR4-434T LT Scheduled S/D Due to Annual Maintenance.
8:40 | 16:44 | Bhaluka-Mymensingh 132 kV Ckt-1 Scheduled S/D from Mymensingh 132/33kV end Due to S/D due to Annual maintenance
and from Bhaluka 132/33kV end Due to Annual maintanance.
8:53 | 16:27 | Khagrachori 132/33kV S/S TR-1 HT Scheduled S/D Due to Annual Maintenance.
9:05 | 17:09 | Jamalpur 132/33kV S/S T-4 HT Scheduled S/D Due to Annual maintenance work.
9:05 | 17:09 | Jamalpur 132/33kV S/S T-4 LT Scheduled S/D Due to Annual maintenance work.
9:10 | 14:41 | Rangpur 132/33kV S/S T-2 (404T) LT Scheduled S/D Due to Annual Maintenance.
9:12 | 14:40 | Rangpur 132/33kV S/S T-2 (404T) HT Scheduled S/D Due to Annual Maintenance.
9:31 | 10:09 | Bhangura 132/33kV S/S Tr-1(403T) HT Forced S/D. |  |  |  |  | 12.0MW load interrup.
- | 10:07 | Bhangura 132/33kV S/S Tr-2(413T) HT is restored.
12:00 | - | Day peak Generation is 10675MW
12:05 | 17:01 | Jamalpur 132/33kV S/S T-3 HT Forced S/D Due to 33 KV T3 & T4 bus coupler maintenance work by jamalpur pbs. |  |  |  |  | 15.0MW load interrup.
12:05 | 17:01 | Jamalpur 132/33kV S/S T-3 LT Forced S/D Due to 33 KV T3 & T4 bus coupler maintenance work by jamalpur pbs. |  |  |  |  | 15.0MW load interrup.
14:49 | 17:57 | HVDC Bheramera-Ishwardi 230kV Ckt-4 Project Work S/D from BIPTC end Due to could not shutdown properly due to problem in
line isolator and from Ishurdi 230/132kV end Due to Project work.
14:49 | 17:38 | Hasnabad 230/132kV S/S AUTO TR-2 HT Scheduled S/D Due to DS - 211 (132kV) maintenance.
14:49 | 17:38 | Hasnabad 230/132kV S/S AUTO TR-2 LT Scheduled S/D Due to DS - 211(132kV) maintenance.
- | 14:50 | Halishahar 132/33kV S/S 403T(TR-1) HT is restored.
14:54 | 17:55 | HVDC Bheramera- Ishwardi 230kV Ckt-3 Project Work S/D from Ishurdi 230/132kV end Due to Project work.
15:50 | - | Hasnabad 132/33kV S/S 132kV Main Bus Forced S/D Due to Auto TR -2 Main bus B phase finger burn out.
15:52 | 17:55 | HVDC Bheramera- Ishwardi 230kV Ckt-3 Project Work S/D from BIPTC end.
17:35 | 17:55 | Rangpur 132/33kV S/S Rangpur-Teesta Solar-2 Forced S/D Due to Maintenance work.
18:00 | - | Evening peak generation 11825 MW.
19:08 | 21:35 | Mymensingh 132/33kV S/S Transformer-2 (414T) LT Scheduled S/D Due to TR-3 X-F S/D due to 33KV Digharkanda(Bypass)
Feeder R-Phase Bus -T Clamp Red hot Maintenance.
19:08 | 21:34 | Mymensingh 132/33kV S/S Transformer-3 (424T) HT Scheduled S/D Due to TR-3 X-F S/D due to 33KV Digharkanda(Bypass)
Feeder R-Phase Bus -T Clamp Red hot Maintenance.
- | 20:43 | Payra 400/132/33kV S/S 132/33 kV Transformer-04 HT is restored.
- | 20:44 | Payra 400/132/33kV S/S 132/33 kV Transformer-04 LT is restored.
5:20 | - | Siddhirganj CCPP 335MW was shutdown due to GT inlet air filter cleaning.
6:00 | - | Min. Gen. 8476 MW
7:11 | - | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) LT Scheduled S/D Due to Annual maintenance.
7:12 | - | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) HT Scheduled S/D Due to Annual maintenance.
7:17 | - | Chauddagram-Feni 132 kV Ckt-1 Scheduled S/D from Chauddagram 132/33kV end Due to Yearly Maintenance and from
Feni 132/33kV end Due to Annual Maintenance.
7:38 | - | Siddhirganj 230/132kV S/S 335MW EGCB 2 Scheduled S/D Due to annual maintenance.
7:52 | - | Sholosohor 132/33kV S/S TRAFO-01 LT Scheduled S/D Due to Annual Maintenance.
7:52 | - | Sholosohor 132/33kV S/S TRAFO-01 HT Scheduled S/D Due to Annual Maintenance.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-10-29 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 180 | 3560031
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 374 | 9062400 | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 327 | 7022000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4976000 | GT-1 under S/D due to gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 8 | 64320 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 150 | 3609745 | GT-1 under S/D due to gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 95 | 568030 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 147761 | Low demand.
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 15 | 367056 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 9 | 66240 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 222 | 5223093 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 72144 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 102600 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 98 | 389280 | Low demand.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 64552 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 94880 | Engine problem
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 29 | 731760 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 648700 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 30 | 715000
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 108149 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 85 | 514364 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 76 | 596448 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 495360 | Fuel shortage
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 1 | 72960 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 172800 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 205714
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 456120 | Fuel shortage
| Meghnaghat Unique power |  | IPP | 586 | 0 | 51 | 1694545 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5422 | 2240 | 41802052
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 8 | 154720 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 140670
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 218880
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 206 | 4871909
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 210 | 4889029
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 434909 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 63 | 801408 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 354175 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 12 | 197400 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 246720 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 12 | 292272 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 14 | 367680
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 28199
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 170 | 1658509 | Low demand.
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 263977 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 334544 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 229440 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 27 | 479236 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 53 | 274327 | Engine problem
| SS Power I |  | SS Power | 1*612 | 612 | 624 | 11699999 | On test.
| Cox's Bazar Wind |  | IPP | 66 | 0 | 4 | 108960 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 141 | 4181818 | On test.
| Chattogram area Total |  |  |  | 3157 | 1672 | 32228781
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 193 | 4793000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7154900 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 240 | 6039000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 240 | 5863000 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 0 | 0 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 747352
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 109 | 567054 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Under maint.
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 18 | 294240 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 372024 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 185400
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 154 | 3107520
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 758500
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 334627
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 12 | 258500 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 233700 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 77 | 505680 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 443520 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 83 | 680640 | Fuel shortage
| Cumilla Area Total |  |  |  | 2896 | 1601 | 32338657
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 33 | 1314240 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 424944 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14000
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 18 | 511200 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 60 | 1246800 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 307060
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 101280 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 133 | 3919524
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 41 | 1007000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3543463
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 42 | 718992
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 48384 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1296576 | Gas shortage
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 0 | 0 | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 188 | 4856890 | Engine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 400000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 218352 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 6891000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 376 | 8783000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 251100
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 310 | 7389400
| Sylhet Area Total |  |  |  | 2427 | 1507 | 35404157
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 896 | 21348363
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 50880 | Low demand.
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 29 | 44160
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 23250 | Low demand.
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 18 | 195360 | Low demand.
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 46512 | Low demand.
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 516960
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | TG Test
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 333 | 8290909 | Engine problem
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 1315 | 30516394
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 17664 | Transformer O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 22 | 448000 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 122 | 2483000 | ST Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 680 | 20112600
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4856345
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 40800 | Transformer O/L
| Barisal 307 MW |  | IPP | 307*1 | 307 | 150 | 3687300 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1211 | 31645709
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 24493 | Reserve
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 60887 | Reserve
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 40208 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 152 | 3750009 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 201 | 5521672 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 45086 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 214668
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 103291
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 55 | 89200 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 43 | 253536 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 55 | 216672 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 35100
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1135 | 23579273
| Rajshahi Area Total |  |  |  | 3631 | 1781 | 33934095
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4121800 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 108 | 181046 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 984
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 87 | 169536
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 232438
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1233560
| Rangpur Area Total |  |  |  | 950 | 365 | 5939364
| Total |  |  |  | 24599 | 11825 | 247728733
| Eastern Grid Total |  |  |  | 14516 | 7153 | 145693171
| Western Grid Total |  |  |  | 10083 | 4672 | 102035562
| National Grid Total |  |  |  | 24599 | 11825 | 247728733
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-10-29
| (a) ENTIRE EASTERN GRID : |  | 8154.25 | MW | (b) ENTIRE WESTERN GRID : |  | 3487.4 | MW
| i) Dhaka area |  | 4437.75 | MW | i) Khulna area |  | 1340 | MW
| ii) Chittagong area |  | 1232.5 | MW | ii) Rajshahi area |  | 1092.4 | MW
| iii) Comilla area |  | 1075 | MW | iii) Barisal area |  | 331 | MW
| iv) Mymensingh area |  | 927 | MW | iv) Rangpur area |  | 724 | MW
| v) Sylhet area |  | 482 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11641.65 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 26 | 18:00 | Kamrangirchar | 49.8 | 13:00 | Narinda | 56 | 13:00 | Sherpur | 110 | 18:30
2 | AKSML | 100 | 04:00 | Chowmuhani | 170 | 18:00 | Kaptai | N/A | N/A | Narshingdi | 158 | 21:00 | Shikalbaha | 32 | 00:00
3 | Aftabnagar | 30 | 13:00 | Chuadanga | 82 | 18:30 | Kazla | 74 | 01:00 | Natore | 106 | 18:00 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 79 | 13:00 | Coxsbazar | 113 | 18:00 | Keranigonj | 72 | 18:00 | Nawabganj | 31.6 | 21:00 | Shitalakhya | 98.6 | 12:00
5 | Agrabad | 68 | 13:00 | Cumilla(N) | 123 | 18:00 | Khagrachori | 22 | 18:30 | Netrakona | 104 | 18:30 | Sholosohor | 40 | 18:00
6 | Amnura | 43 | 18:30 | Cumilla(S) | 154 | 18:00 | Khulna | 86 | 18:30 | New | 72 | 12:00 | Shyampur | 150 | 10:00
7 | Ashuganj | 60 | 23:00 | Daudkandi | 129 | 19:30 | Khulshi | 147 | 18:00 | Niamatpur | 59 | 18:00 | Siddhirganj | 108 | 15:00
8 | BIPTC | N/A | N/A | Dhaka | 38 | 11:00 | Kishoreganj | 120 | 18:00 | Noapara | 39 | 18:00 | Sirajganj | 88 | 18:00
9 | BSRM | 140 | 00:00 | Dhamrai | 108 | 15:00 | Kodda | 261 | 18:30 | PHP | 3 | 20:00 | Sonargaon | 83 | 19:30
10 | Bagerhat | 71 | 18:00 | Dhanmondi | 110.3 | 13:00 | Kulaura | 38 | 18:00 | Pabna | 92 | 18:00 | Sreemongol | 53 | 19:00
11 | Bakulia | 90 | 18:30 | Dohazari | 48 | 18:00 | Kurigram | 54 | 18:00 | Palashbari | 90 | 18:00 | Sreepur | 61 | 18:00
12 | Banani | 42 | 13:00 | Faridpur | 115 | 18:00 | Kushtia | 110 | 18:00 | Panchagarh | 44 | 18:00 | Srinagar | 32.8 | 21:00
13 | Bangabhaban | 12 | 10:00 | Fatullah | 64 | 13:00 | Lalbag | 79 | 13:00 | Patuakhali | 73 | 18:00 | Sunamganj | 44 | 18:00
14 | Barapukuria | 51 | 18:00 | Fenchuganj | 34 | 18:00 | Lalmonirhat | 37 | 18:00 | Payra | 15 | 18:00 | Sylhet | 12 | 18:00
15 | Barguna | 14 | 00:00 | Feni | 87 | 18:00 | MI_Cement | 19.4 | 17:00 | Postogola | 48 | 13:00 | Sylhet-132 | 123 | 18:00
16 | Barishal | 87 | 18:00 | GPH | 95 | 18:00 | Madanganj | 40 | 12:00 | Purbachal | 18 | 18:00 | TK | 25.5 | 18:00
17 | Barishal-230 | 70 | 18:00 | Ghorashal | 57 | 18:30 | Madaripur | 68 | 18:00 | Purbasadipur | 95 | 18:00 | Tangail | 173 | 18:30
18 | Baroaulia | 63 | 00:00 | Goalpara | 30 | 12:00 | Madartek | 61.02 | 13:00 | Rahim | 42 | 12:00 | Thakurgaon | 70 | 18:00
19 | Baroirhat | 46 | 18:00 | Gollamari | 38 | 12:00 | Madunaghat | 48 | 19:00 | Rajbari | 52 | 18:00 | Tongi | 93 | 16:00
20 | Bashundhara | 140 | 18:00 | Gopalganj | 83 | 18:00 | Magura | 54 | 18:00 | Rajendrapur | 92 | 18:30 | Ullon | 35 | 18:00
21 | BashundharaCement | 7 | 07:00 | Gulshan | 96 | 12:00 | Mahasthangarh | 56 | 18:00 | Rajshahi | 112 | 18:30 | Uttara | 62 | 12:00
22 | Beanibazar | 58 | 18:00 | Halishahar | 101 | 15:00 | Manikganj | 82 | 18:00 | Rajshahi-230 | 27 | 18:30 | UttaraNew | 40 | 18:00
23 | Benapole | 48 | 18:00 | HaripurSBU | 146 | 12:00 | Maniknagar | 72 | 13:00 | Ramganj | 80 | 18:00 | Zigatola | 77 | 13:00
24 | Bhaluka | 144 | 18:30 | Hasnabad | 82 | 12:00 | Matarbari | 7 | 20:00 | Rampur | 26 | 18:00
25 | Bhandaria | 36 | 20:00 | Hathazari | 61 | 13:00 | Matuail | 69 | 13:00 | Rangamati | 16 | 18:00
26 | Bhangura | 25 | 18:00 | Ishurdi | 59 | 18:00 | Millgate | 90 | 12:00 | Rangpur | 102 | 18:00
27 | Bheramara(GK) | 47 | 18:00 | Jaldhaka | 56 | 18:00 | Mirpur | 114 | 18:00 | Ruppur | 5.6 | 11:00
28 | Bhulta | 236 | 21:00 | Jamalpur | 143 | 18:30 | Mirsorai | 4 | 09:00 | SSM | 0 | 00:00
29 | Bog-Sherpur | 48 | 18:00 | Jashore | 106 | 18:00 | Mirzapur | 0 | 10:00 | Saidpur | 85 | 18:00
30 | Bogura | 119 | 18:00 | Jhenaidah | 102 | 18:00 | Mithapukur | 40 | 18:00 | Satkhira | 95 | 18:00
31 | Borhanuddin | 40 | 20:00 | Joydebpur | 159 | 12:00 | Modern | 0 | 00:00 | Satmasjid | 91 | 14:00
32 | Brahmanbaria | 143 | 19:30 | Joypurhat | 39 | 19:00 | Mogbazar | 89.6 | 15:00 | Savar | 160 | 15:00
33 | Cantonment | 104 | 14:00 | Juldah | 22 | 00:00 | Mongla | 36 | 09:00 | SevenRings | 9.23 | 02:00
34 | Chandpur | 51 | 18:00 | KSRM | 28 | 16:00 | Motijheel | 32 | 13:00 | ShahCement | 28 | 13:00
35 | Chandraghona | 27 | 18:00 | Kabirpur | 258 | 12:00 | Munshiganj | 76 | 00:00 | Shahjadpur | 78 | 18:00
36 | Chapai | 51 | 20:00 | Kachua | 54 | 18:00 | Mymensingh | 178 | 13:00 | Shahjibazar | 103 | 21:00
37 | Charsaidpur | 27 | 15:00 | Kallyanpur | 93 | 18:00 | Naogaon | 103 | 18:30 | Shahmirpur | 37.4 | 00:00
38 | Chauddagram | 45 | 18:00 | Kalurghat | 36 | 12:00 | Narail | 45 | 18:00 | Shariatpur | 55 | 18:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-10-29 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 400 | 06:00 | 389 | 10:00 | Gopalganj | 409 | 06:00 | 399 | 12:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 385 | 01:00 | 376 | 11:00
| Bhulta | 401 | 01:00 | 392 | 11:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 408 | 17:00 | 399 | 11:00 | Payra | 415 | 05:00 | 409 | 19:30
| BIPTC | 399 | 03:00 | 395 | 00:00 | Rahanpur | 412 | 04:00 | 400 | 19:30
| Bogura | N/A | N/A | N/A | N/A | Rampal | 409 | 04:00 | 400 | 13:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 236 | 06:00 | 227 | 11:00 | Hasnabad | 235 | 04:00 | 227 | 12:00
| AKSML | 233 | 20:00 | 228 | 10:00 | Hathazari | 236 | 18:00 | 229 | 12:00
| Aminbazar | 238 | 04:00 | 229 | 12:00 | Ishurdi | 235 | 03:00 | 223 | 11:00
| Ashuganj | 236 | 01:00 | 231 | 11:00 | Jhenaidah | 230 | 03:00 | 216 | 12:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 237 | 03:00 | 230 | 11:00
| Baghabari | 230 | 01:00 | 222 | 12:00 | Keranigonj | 234 | 02:00 | 226 | 12:00
| Barapukuria | 226 | 04:00 | 217 | 21:00 | Khulna(S) | 234 | 03:00 | 224 | 19:30
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 237 | 04:00 | 232 | 19:30 | Maniknagar | 235 | 04:00 | 228 | 11:00
| Bheramara | 235 | 01:00 | 222 | 11:00 | Meghnaghat | 242 | 01:00 | 236 | 13:00
| Bhulta | 237 | 01:00 | 231 | 11:00 | Mirsorai | 236 | 00:00 | 228 | 11:00
| Bibiana | 235 | 17:00 | 229 | 12:00 | Rajshahi | 234 | 02:00 | 220 | 19:30
| BIPTC | 236 | 03:00 | 222 | 11:00 | Rampal | 234 | 02:00 | 226 | 11:00
| Bogura | 235 | 04:00 | 225 | 19:30 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 241 | 17:00 | 237 | 10:00 | Rampura | 235 | 02:00 | 229 | 11:00
| BSRM | 235 | 18:00 | 229 | 10:00 | Shikalbaha | 234 | 18:30 | 228 | 06:00
| Cumilla(N) | 234 | 18:00 | 228 | 12:00 | Shyampur | 235 | 06:00 | 228 | 11:00
| Fenchuganj | 238 | 20:00 | 234 | 02:00 | Siddhirganj | 236 | 18:00 | 231 | 11:00
| Ghorashal | 240 | 08:00 | 235 | 00:00 | Sirajgonj | 240 | 02:00 | 234 | 19:30
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 236 | 06:00 | 229 | 11:00
| GPH | 235 | 18:00 | 229 | 10:00 | Tongi | 234 | 05:00 | 227 | 09:00
| Haripur | 235 | 18:00 | 230 | 11:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 137 | 01:00 | 131 | 10:00 | Lalbag | 135 | 05:00 | 129 | 11:00
| Agargaon | 136 | 02:00 | 130 | 11:00 | Lalmonirhat | 131 | 18:00 | 126 | 12:00
| Agrabad | 135 | 17:00 | 132 | 09:00 | Madanganj | 134 | 17:00 | 129 | 09:00
| AKS | 134 | 18:00 | 129 | 12:00 | Madaripur | 132 | 17:00 | 129 | 03:00
| Aminbazar | 141 | 04:00 | 134 | 11:00 | Madartek | 136 | 01:00 | 130 | 11:00
| Amnura | 137 | 17:00 | 126 | 19:30 | Madunaghat | 137 | 18:00 | 132 | 10:00
| Ashuganj | 140 | 00:00 | 138 | 12:00 | Magura | 138 | 05:00 | 130 | 12:00
| Bagerhat | 134 | 03:00 | 128 | 21:00 | Mahasthangarh | 137 | 03:00 | 129 | 12:00
| Bakulia | 136 | 22:00 | 132 | 11:00 | Manikganj | 133 | 18:30 | 125 | 12:00
| Banani | 140 | 06:00 | 132 | 11:00 | Maniknagar | 138 | 06:00 | 133 | 11:00
| Bangabhaban | 137 | 05:00 | 132 | 12:00 | Matarbari | 130 | 03:00 | 126 | 19:30
| Barapukuria | 140 | 04:00 | 133 | 21:00 | Matuail | 133 | 05:00 | 128 | 11:00
| Barguna | 139 | 08:00 | 135 | 19:30 | Millgate | 139 | 01:00 | 132 | 11:00
| Barishal | 136 | 05:00 | 133 | 18:00 | Mirpur | 139 | 03:00 | 132 | 12:00
| Barishal-230 | 136 | 06:00 | 132 | 19:30 | Mirzapur | 132 | 17:00 | 128 | 12:00
| Baroaulia | 136 | 17:00 | 132 | 11:00 | Mithapukur | 135 | 01:00 | 128 | 21:00
| Baroirhat | 131 | 18:00 | 127 | 00:00 | MI_Cement | 135 | 18:00 | 130 | 10:00
| Bashundhara | 140 | 03:00 | 130 | 11:00 | Modern | 136 | 18:30 | 132 | 10:00
| BashundharaCement | 134 | 17:00 | 129 | 09:00 | Mogbazar | 137 | 00:00 | 131 | 11:00
| Beanibazar | 129 | 07:00 | 126 | 11:00 | Mongla | 133 | 06:00 | 126 | 22:00
| Benapole | 136 | 05:00 | 128 | 13:00 | Motijheel | 137 | 05:00 | 133 | 11:00
| Bhaluka | 129 | 02:00 | 122 | 20:00 | Munshiganj | 134 | 05:00 | 129 | 11:00
| Bhandaria | 137 | 06:00 | 132 | 00:00 | Mymensingh | 136 | 00:00 | 118 | 07:00
| Bhangura | 141 | 01:00 | 132 | 18:00 | Naogaon | 134 | 01:00 | 125 | 12:00
| Bheramara | 136 | 01:00 | 129 | 11:00 | Narail | 138 | 01:00 | 129 | 19:30
| Bheramara(GK) | 136 | 02:00 | 129 | 11:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 125 | 18:00 | 119 | 11:00 | Narshingdi | 129 | 06:00 | 121 | 11:00
| Bog-Sherpur | 138 | 03:00 | 131 | 12:00 | Natore | 136 | 01:00 | 129 | 11:00
| Bogura | 139 | 06:00 | 131 | 21:00 | Nawabganj | 135 | 03:00 | 129 | 11:00
| Bogura-230 | 138 | 04:00 | 131 | 12:00 | Netrakona | 135 | 00:00 | 123 | 18:00
| Brahmanbaria | 128 | 07:00 | 121 | 19:30 | New | 139 | 00:00 | 132 | 11:00
| Cantonment | 136 | 03:00 | 130 | 11:00 | Niamatpur | 131 | 02:00 | 121 | 12:00
| Chandpur | 133 | 18:00 | 124 | 00:00 | Noapara | 137 | 06:00 | 129 | 12:00
| Chandraghona | 137 | 17:00 | 134 | 10:00 | Pabna | 138 | 01:00 | 130 | 12:00
| Chapai | 133 | 01:00 | 128 | 20:00 | Palashbari | 136 | 03:00 | 127 | 12:00
| Charsaidpur | 136 | 17:00 | 130 | 09:00 | Panchagarh | 134 | 03:00 | 122 | 12:00
| Chauddagram | 134 | 17:00 | 127 | 11:00 | Patuakhali | 138 | 09:00 | 136 | 00:00
| Chhatak | 130 | 07:00 | 125 | 18:30 | Payra | 140 | 06:00 | 138 | 12:00
| Chowmuhani | 130 | 17:00 | 122 | 03:00 | PHP | 132 | 18:00 | 126 | 11:00
| Chuadanga | 137 | 05:00 | 127 | 12:00 | Postogola | 136 | 04:00 | 132 | 10:00
| Coxsbazar | 128 | 08:00 | 123 | 19:30 | Purbachal | 140 | 06:00 | 131 | 11:00
| Cumilla(N) | 136 | 18:00 | 132 | 11:00 | Purbasadipur | 134 | 05:00 | 123 | 21:00
| Cumilla(S) | 135 | 17:00 | 126 | 16:00 | Rahanpur | 136 | 04:00 | 133 | 00:00
| Daudkandi | 132 | 17:00 | 119 | 12:00 | Rahim | 133 | 06:00 | 129 | 12:00
| Dhaka | 137 | 01:00 | 131 | 11:00 | Rajbari | 132 | 03:00 | 126 | 12:00
| Dhamrai | 134 | 01:00 | 129 | 11:00 | Rajendrapur | 134 | 18:30 | 123 | 13:00
| Dhanmondi | 134 | 00:00 | 127.7 | 12:00 | Rajshahi | 136 | 06:00 | 128 | 12:00
| Dohazari | 134 | 17:00 | 131 | 05:00 | Rajshahi-230 | 135 | 00:00 | 125 | 18:30
| Faridpur | 132 | 05:00 | 128 | 11:00 | Ramganj | 129 | 18:00 | 121 | 06:00
| Fatullah | 136 | 04:00 | 132 | 10:00 | Rampur | 135 | 00:00 | 131 | 14:00
| Fenchuganj | 133 | 07:00 | 131 | 00:00 | Rampura | 137 | 02:00 | 130 | 11:00
| Feni | 131 | 18:30 | 126 | 02:00 | Rangamati | 136 | 18:00 | 133 | 11:00
| Ghorashal | 140 | 08:00 | 137 | 16:00 | Rangpur | 132 | 18:00 | 127 | 21:00
| Goalpara | 138 | 03:00 | 132 | 11:00 | Ruppur | 139 | 01:00 | 131 | 12:00
| Gollamari | 137 | 03:00 | 132 | 11:00 | Saidpur | 136 | 05:00 | 125 | 21:00
| Gopalganj | 133 | 03:00 | 128 | 12:00 | Satkhira | 135 | 03:00 | 128 | 18:00
| Gopalganj-400 | 132 | 06:00 | 128 | 11:00 | Satmasjid | 136 | 04:00 | 130 | 11:00
| Gulshan | 135 | 03:00 | 130 | 11:00 | Savar | 137 | 06:00 | 132 | 11:00
| Halishahar | 135 | 19:00 | 131 | 16:00 | SevenRings | 141 | 01:00 | 137 | 10:00
| Haripur | 133 | 02:00 | 129 | 12:00 | ShahCement | 136 | 17:00 | 130 | 10:00
| HaripurSBU | 133 | 06:00 | 129 | 12:00 | Shahjadpur | 140 | 00:00 | 136 | 11:00
| Hasnabad | 136 | 18:00 | 132 | 10:00 | Shahjibazar | 128 | 07:00 | 122 | 23:00
| Hathazari | 137 | 09:00 | 133 | 03:00 | Shahmirpur | 135 | 17:00 | 131 | 10:00
| Ishurdi | 139 | 01:00 | 132 | 12:00 | Shariatpur | 132 | 04:00 | 128 | 12:00
| Jaldhaka | 135 | 05:00 | 124 | 20:00 | Sherpur | 134 | 01:00 | 111 | 07:00
| Jamalpur | 136 | 01:00 | 115 | 07:00 | Shikalbaha | 125 | 18:00 | 120 | 11:00
| Jashore | 136 | 05:00 | 128 | 13:00 | Shikalbaha-230 | 137 | 18:30 | 133 | 11:00
| Jhenaidah | 139 | 05:00 | 132 | 12:00 | Shitalakhya | 135 | 18:00 | 130 | 10:00
| Jhenaidah-230 | 141 | 03:00 | 132 | 11:00 | Sholosohor | 136 | 19:00 | 132 | 10:00
| Joydebpur | 138 | 18:00 | 131 | 08:00 | Shyampur | 136 | 04:00 | 132 | 11:00
| Joypurhat | 134 | 03:00 | 125 | 12:00 | Shyampur-230 | 136 | 01:00 | 132 | 10:00
| Juldah | 136 | 18:30 | 131 | 15:00 | Siddhirganj | 134 | 05:00 | 129 | 11:00
| Kabirpur | 135 | 06:00 | 127 | 07:00 | Sirajganj | 138 | 01:00 | 130 | 12:00
| Kachua | 133 | 18:00 | 126 | 00:00 | Sonargaon | 131 | 06:00 | 127 | 01:00
| Kaliakoir | 138 | 18:00 | 130 | 07:00 | Sreemongol | 129 | 08:00 | 125 | 23:00
| Kallyanpur | 140 | 02:00 | 134 | 11:00 | Sreepur | 138 | 05:00 | 125 | 19:30
| Kalurghat | 136 | 20:00 | 133 | 10:00 | Srinagar | 135 | 05:00 | 129 | 11:00
| Kamrangirchar | 139 | 02:00 | 129 | 11:00 | SSM | 140 | 00:00 | 135 | 07:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 127 | 06:00 | 123 | 18:00
| Kazla | 137 | 06:00 | 132 | 11:00 | Sylhet | 130 | 01:00 | 128 | 11:00
| Keranigonj | 135 | 03:00 | 129 | 12:00 | Sylhet-132 | 130 | 07:00 | 128 | 15:00
| Khagrachori | 136 | 19:00 | 133 | 12:00 | Tangail | 134 | 01:00 | 127 | 18:00
| Khulna | 137 | 06:00 | 130 | 21:00 | Thakurgaon | 134 | 03:00 | 120 | 12:00
| Khulna(S) | 138 | 03:00 | 132 | 11:00 | TK | 136 | 19:00 | 133 | 03:00
| Khulshi | 134 | 18:00 | 130 | 10:00 | Tongi | 139 | 01:00 | 134 | 10:00
| Kishoreganj | 135 | 06:00 | 130 | 11:00 | Ullon | 137 | 01:00 | 130 | 11:00
| Kodda | 138 | 18:00 | 125 | 12:00 | Uttara | 139 | 03:00 | 132 | 11:00
| KSRM | 137 | 20:00 | 132 | 11:00 | UttaraNew | 139 | 01:00 | 132 | 12:00
| Kulaura | 131 | 03:00 | 130 | 00:00 | Zigatola | 135 | 06:00 | 129 | 13:00
| Kurigram | 132 | 06:00 | 124 | 21:00
| Kushtia | 137 | 05:00 | 130 | 11:00

## L-Curve
Date | 2023-10-29
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1110 | 5893 | 4326 | 10219 |  |  |  | QF-LDC-11
0:30 | 1055 | 5944.5 | 4151 | 10095.5 | Date: | 2023-10-29
1:00 | 1000 | 5996 | 3976 | 9972
1:30 | 995 | 5801 | 3937.5 | 9738.5
2:00 | 990 | 5606 | 3899 | 9505
2:30 | 995 | 5527.5 | 3828 | 9355.5 | [5 empty] | Gen. at Eve. Peak | 11825 | 11825 MW (18:00 )
3:00 | 1000 | 5449 | 3757 | 9206 | [6 empty] | 18:00
3:30 | 1005 | 5347.5 | 3661.5 | 9009 | [5 empty] | Gen. at Day Peak | 10675 | 10675 MW (12:00 )
4:00 | 1010 | 5246 | 3566 | 8812 | [6 empty] | 12:00
4:30 | 995 | 5136 | 3541.5 | 8677.5 | [5 empty] | Highest Generation | 11825
5:00 | 980 | 5026 | 3517 | 8543 | [6 empty] | 18:00
5:30 | 990 | 4998 | 3524.5 | 8522.5
6:00 | 1000 | 4970 | 3532 | 8502
6:30 | 1005 | 5040.5 | 3647 | 8687.5
7:00 | 1010 | 5111 | 3762 | 8873
7:30 | 1040 | 5095.5 | 3850.5 | 8946
8:00 | 1070 | 5080 | 3939 | 9019
8:30 | 1105 | 5295.5 | 4008.5 | 9304
9:00 | 1140 | 5511 | 4078 | 9589
9:30 | 1205 | 5549.5 | 4086 | 9635.5
10:00 | 1270 | 5588 | 4094 | 9682
10:30 | 1230 | 5799 | 4137 | 9936
11:00 | 1190 | 6010 | 4180 | 10190
11:30 | 1195 | 6186.5 | 4246 | 10432.5
12:00 | 1200 | 6363 | 4312 | 10675
12:30 | 1195 | 6389.5 | 4396.5 | 10786
13:00 | 1190 | 6416 | 4481 | 10897
13:30 | 1228 | 6477 | 4351 | 10828
14:00 | 1266 | 6538 | 4221 | 10759
14:30 | 1258 | 6585 | 4151.5 | 10736.5
15:00 | 1250 | 6632 | 4082 | 10714
15:30 | 1160 | 6536.5 | 4025 | 10561.5
16:00 | 1070 | 6441 | 3968 | 10409
16:30 | 1030 | 6493 | 3969.5 | 10462.5
17:00 | 990 | 6545 | 3971 | 10516
17:30 | 1018 | 6849 | 4321.5 | 11170.5
18:00 | 1046 | 7153 | 4672 | 11825
18:30 | 1033 | 7016.5 | 4679 | 11695.5
19:00 | 1020 | 6880 | 4686 | 11566
19:30 | 1014 | 6754 | 4654 | 11408
20:00 | 1030 | 6644 | 4647 | 11291 |  |  |  | Executive Engineer
20:30 | 1045 | 6577.5 | 4633 | 11210.5 |  |  |  | Network Operation Division
21:00 | 1060 | 6511 | 4619 | 11130
21:30 | 1065 | 6297.5 | 4610.5 | 10908
22:00 | 1070 | 6084 | 4602 | 10686 |  |  |  |  | Page 6 of 7
22:30 | 1075 | 6068.5 | 4491.5 | 10560
23:00 | 1080 | 6053 | 4381 | 10434
23:30 | 1095 | 5973 | 4353.5 | 10326.5
24:00 | 1110 | 5893 | 4326 | 10219
11825 MW (18:00 )
10675 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-10-29 |  | Energy |  | 247728733
[15 empty] | 43766 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3419 | 896 | 1739 | 0 | 410 | 3332 | 206 | 0 | 83 | 128 | 0 | 6 | 0
0:30 | 3388.5 | 896 | 1709 | 0 | 414.5 | 3271.5 | 206 | 0 | 75 | 129 | 0 | 6 | 0 |  |  | Date: | 43766
1:00 | 3358 | 896 | 1679 | 0 | 419 | 3211 | 206 | 0 | 67 | 130 | 0 | 6 | 0
1:30 | 3360.5 | 895.5 | 1643 | 0 | 335.5 | 3121.5 | 205.5 | 0 | 42 | 128 | 0 | 7 | 0 | [8 empty] | Total Energy | 247.7287 | 247.7287 | Total Energy Gen 247.729 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 247.729 MKWHr
2:00 | 3363 | 895 | 1607 | 0 | 252 | 3032 | 205 | 0 | 17 | 126 | 0 | 8 | 0 | [8 empty] | Energy not Served | 0 | 0
2:30 | 3368.5 | 895.5 | 1612.5 | 0 | 222.5 | 2902.5 | 205 | 0 | 17 | 123 | 0 | 9 | 0 | [8 empty] | Energy Requirement | 247.7287 | 247.7287
3:00 | 3374 | 896 | 1618 | 0 | 193 | 2773 | 205 | 0 | 17 | 120 | 0 | 10 | 0
3:30 | 3325.5 | 895.5 | 1575.5 | 0 | 166 | 2693.5 | 205 | 0 | 17 | 120 | 0 | 11 | 0
4:00 | 3277 | 895 | 1533 | 0 | 139 | 2614 | 205 | 0 | 17 | 120 | 0 | 12 | 0
4:30 | 3256 | 895 | 1516 | 0 | 90 | 2570.5 | 205 | 0 | 17 | 117 | 0 | 11 | 0
5:00 | 3235 | 895 | 1499 | 0 | 41 | 2527 | 205 | 0 | 17 | 114 | 0 | 10 | 0
5:30 | 3220 | 894.5 | 1499 | 0 | 33 | 2535.5 | 205 | 0 | 17 | 110 | 0 | 8.5 | 0
6:00 | 3205 | 894 | 1499 | 0 | 25 | 2544 | 205 | 0 | 17 | 106 | 0 | 7 | 0
6:30 | 3220 | 895 | 1634 | 0 | 35 | 2543 | 205.5 | 0 | 17 | 105 | 26.5 | 6.5 | 0 | [7 empty] | Coal
7:00 | 3235 | 896 | 1769 | 0 | 45 | 2542 | 206 | 0 | 17 | 104 | 53 | 6 | 0
7:30 | 3240 | 895.5 | 1691 | 0 | 80 | 2597 | 206 | 0 | 17 | 104 | 112.5 | 3 | 0 | [6 empty] | Oil
8:00 | 3245 | 895 | 1613 | 0 | 115 | 2652 | 206 | 0 | 17 | 104 | 172 | 0 | 0
8:30 | 3319 | 895.5 | 1661 | 0 | 155.5 | 2704 | 206.5 | 0 | 25 | 109 | 228.5 | 0 | 0
9:00 | 3393 | 896 | 1709 | 0 | 196 | 2756 | 207 | 0 | 33 | 114 | 285 | 0 | 0
9:30 | 3413 | 895.5 | 1665.5 | 0 | 232.5 | 2760.5 | 207 | 0 | 24.5 | 118 | 318.5 | 0.5 | 0
10:00 | 3433 | 895 | 1622 | 0 | 269 | 2765 | 207 | 0 | 16 | 122 | 352 | 1 | 0
10:30 | 3436.5 | 895.5 | 1695.5 | 0 | 347.5 | 2844.5 | 207 | 0 | 16 | 124 | 367.5 | 2 | 0
11:00 | 3440 | 896 | 1769 | 0 | 426 | 2924 | 207 | 0 | 16 | 126 | 383 | 3 | 0
11:30 | 3448 | 896 | 1794 | 0 | 537 | 2988 | 207 | 0 | 26 | 133 | 400 | 3.5 | 0
12:00 | 3456 | 896 | 1819 | 0 | 648 | 3052 | 207 | 0 | 36 | 140 | 417 | 4 | 0
12:30 | 3458.5 | 896 | 1767 | 0 | 715 | 3139.5 | 207 | 0 | 72.5 | 141 | 384.5 | 5 | 0
13:00 | 3461 | 896 | 1715 | 0 | 782 | 3227 | 207 | 0 | 109 | 142 | 352 | 6 | 0
13:30 | 3461 | 896 | 1715 | 0 | 782 | 3227 | 207 | 0 | 109 | 142 | 352 | 6 | 0
14:00 | 3461 | 896 | 1715 | 0 | 782 | 3227 | 207 | 0 | 109 | 142 | 352 | 6 | 0
14:30 | 3460.5 | 896 | 1736.5 | 0 | 870.5 | 3087 | 206.5 | 0 | 117.5 | 141 | 285 | 5 | 0
15:00 | 3460 | 896 | 1758 | 0 | 959 | 2947 | 206 | 0 | 126 | 140 | 218 | 4 | 0
15:30 | 3436 | 895.5 | 1700 | 0 | 944.5 | 2954.5 | 206 | 0 | 119 | 140 | 163 | 3 | 0
16:00 | 3412 | 895 | 1642 | 0 | 930 | 2962 | 206 | 0 | 112 | 140 | 108 | 2 | 0
16:30 | 3403.5 | 895 | 1642 | 0 | 1002 | 2992 | 206 | 0 | 122 | 137 | 60 | 3 | 0
17:00 | 3395 | 895 | 1642 | 0 | 1074 | 3022 | 206 | 0 | 132 | 134 | 12 | 4 | 0
17:30 | 3430.5 | 895.5 | 1699 | 0 | 1387 | 3127.5 | 206 | 0 | 271 | 144 | 6 | 4 | 0
18:00 | 3466 | 896 | 1756 | 0 | 1700 | 3233 | 206 | 0 | 410 | 154 | 0 | 4 | 0
18:30 | 3491 | 895.5 | 1735 | 0 | 1513.5 | 3390.5 | 206 | 0 | 311.5 | 148 | 0 | 4.5 | 0
19:00 | 3516 | 895 | 1714 | 0 | 1327 | 3548 | 206 | 0 | 213 | 142 | 0 | 5 | 0
19:30 | 3539 | 895 | 1825 | 0 | 953 | 3694 | 206 | 0 | 148 | 146 | 0 | 2 | 0
20:00 | 3547 | 895 | 1778 | 0 | 887 | 3687 | 206 | 0 | 147 | 142 | 0 | 2 | 0
20:30 | 3539 | 895 | 1792 | 0 | 789.5 | 3707 | 206 | 0 | 138.5 | 140 | 0 | 3.5 | 0
21:00 | 3531 | 895 | 1806 | 0 | 692 | 3727 | 206 | 0 | 130 | 138 | 0 | 5 | 0
21:30 | 3511 | 895 | 1758 | 0 | 610.5 | 3665 | 206 | 0 | 122 | 136 | 0 | 4.5 | 0
22:00 | 3491 | 895 | 1710 | 0 | 529 | 3603 | 206 | 0 | 114 | 134 | 0 | 4 | 0
22:30 | 3475 | 895.5 | 1745 | 0 | 509.5 | 3480.5 | 206 | 0 | 111 | 134 | 0 | 3.5 | 0
23:00 | 3459 | 896 | 1780 | 0 | 490 | 3358 | 206 | 0 | 108 | 134 | 0 | 3 | 0
23:30 | 3439 | 896 | 1759.5 | 0 | 450 | 3345 | 206 | 0 | 95.5 | 131 | 0 | 4.5 | 0 |  |  | Max Temp. in Dhaka |  | 32.5°C
24:00 | 3419 | 896 | 1739 | 0 | 410 | 3332 | 206 | 0 | 83 | 128 | 0 | 6 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 247.729 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 247.729 MKWHr
Note on W13: Author:

## Generation
g | 2023-10-29
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 131 | 130 | 130 | 130 | 130 | 130 | 131 | 131 | 132 | 132 | 132 | 132 | 132 | 131 | 131 | 131 | 131 | 131 |  | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 3055909
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1816000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 3 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 0 | [5 empty] | 0 | 154720
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 5 | 10 | 15 | 18 | 19 | 20 | 19 | 16 | 11 | 6 | 0 | [9 empty] | 140670
6 | Sikalbaha 225MW CCPP (Gas) | 209 | 202 | 201 | 201 | 195 | 195 | 196 | 195 | 204 | 204 | 212 | 213 | 217 | 216 | 216 | 216 | 216 | 210 |  | 210 | 209 | 209 | 195 | 195 | 195 | 173 | 4889029
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 |  |  |  | 17 | 17 | 16 | 17 | 34 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 354175
12 | Hathazari 100 MW peaking PP | 50 | [10 empty] | 3 | 40 | 40 | 40 | 47 | 62 | 63 |  | 75 | 82 | 81 | 81 | 81 | 75 | 66 | 801408
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 34 | 34 | 34 | 34 |  |  |  |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 434909
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 234 | 227 | 227 | 180 | 180 | 150 | 150 | 155 | 234 | 235 | 235 | 235 | 235 | 232 | 228 | 225 | 224 | 222 |  | 223 | 222 | 220 | 220 | 220 | 220 | 213 | 5223093
18 | Kodda 300 MW PP Unit-2 (Summit) | [10 empty] | 15 | 38 | 60 | 60 | 55 | 49 | 46 | 85 |  | 15 | 0 | [5 empty] | 514364
19 | Ashuganj 195 MW PP (APSCL-United) | [25 empty] | 0 | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 150 | 150 | 180 | 180 | 180 | 180 | 130 | 130 | 180 |  | 180 | 180 | 180 | 180 | 130 | 130 | 130 | 3560031
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 624 | 540 | 430 | 380 | 320 | 320 | 320 | 320 | 360 | 360 | 450 | 500 | 500 | 500 | 502 | 558 | 624 | 624 |  | 623 | 653 | 646 | 640 | 512 | 495 | 495 | 11699999
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP
33 | Ashuganj 225 MW CCPP | 193 | 200 | 202 | 208 | 213 | 215 | 188 | 200 | 203 | 203 | 204 | 198 | 196 | 194 | 195 | 195 | 191 | 193 |  | 190 | 188 | 186 | 185 | 186 | 190 | 195 | 4793000
34 | Ashuganj 450 MW CCPP(South) | 240 | 240 | 240 | 240 | 240 | 240 | 330 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 6039000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 270 | 270 | 270 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 7154900
| Ashuganj 420 MW CCPP(East) | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 5863000
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 344 | 344 | 344 | 344 | 307 | 304 | 307 | 364 | 396 | 382 | 383 | 386 | 408 | 411 | 406 | 408 | 384 | 374 |  | 423 | 396 | 396 | 395 | 400 | 359 | 352 | 9062400
| Meghnaghat Unique power | 40 | 35 | 65 | 96 | 100 | 90 | 100 | 76 | 89 | 95 | 97 | 98 | 81 | 100 | 100 | 100 | 71 | 51 |  | 35 | 100 | 44 | 73 | 46 | 100 | 75 | 1694545
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 190 | 170 | 170 | 170 | 170 | 225 | 180 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4976000
41 | Haripur 360 MW CCPP(HPL) | 262 | 261 | 262 | 238 | 237 | 236 | 262 | 262 | 332 | 305 | 330 | 330 | 300 | 303 | 330 | 260 | 276 | 327 |  | 327 | 327 | 327 | 333 | 302 | 303 | 302 | 7022000
42 | RPCL 210MW CCPP | 77 | 77 | 86 | 86 | 86 | 75 | 37 | 34 | 34 | 34 | 34 | 34 | 32 | 32 | 32 | 32 | 32 | 33 |  | 34 | 67 | 100 | 95 | 95 | 95 | 95 | 1314240
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 7 | 22 | 36 | 35 | 29 | 55 | 25 | 41 | 24 | 16 | 1 | 0 | [8 empty] | 307060
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 40 | 40 | 42 | 42 | 42 | 41 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1007000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 57 | 57 | 57 | 40 | 40 | 40 | 40 | 40 | 40 | 58 | 57 | 59 | 59 | 58 | 60 | 60 | 61 | 62 |  | 62 | 62 | 58 | 62 | 60 | 57 | 57 | 1296576
48 | Shahjibazar 86 MW PP (Shahjibazar) | [25 empty] | 0 | 0
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 190 | 191 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 191 | 191 | 191 | 191 | 191 | 188 | 188 | 188 | 188 |  | 188 | 191 | 189 | 191 | 191 | 191 | 190 | 4856890
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 16 | 16 | 16 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 400000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 251100
54 | Hobiganj 11 MW PP Cofidence-E | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 48384
55 | Fenchugonj 51 MW PP (Barakatullah)
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | [10 empty] | 8 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 218352
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 260 | 270 | 265 | 285 | 290 | 300 | 280 | 275 | 280 | 300 | 280 | 285 | 290 | 315 | 290 | 300 | 280 |  | 260 | 300 | 280 | 270 | 270 | 280 | 280 | 6891000
| Bibiyana South 400 MW | 300 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 300 | 300 | 300 | 300 | 310 | 310 | 310 | 310 |  | 300 | 310 | 310 | 310 | 310 | 310 | 310 | 7389400
58 | Nababganj 55 MW PP (Southern power ) | [14 empty] | 0 | 17 | 17 | 35 |  | 17 | 0 |  |  |  |  | 0 | 94880
59 | Tangail Palli Power Gen 22 MW | [7 empty] | 2 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 0 | 101280
60 | Barabkunda 22 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 292272
61 | Narshingdi 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 16 | 16 | 16 | 16 | 367056
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 16 | 16 | 16 | 16 | 16 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 424944
63 | Impoprt (Tripura) | 130 | 126 | 120 | 120 | 114 | 106 | 104 | 104 | 114 | 122 | 126 | 140 | 142 | 146 | 140 | 140 | 134 | 154 |  | 142 | 146 | 142 | 138 | 134 | 134 | 128 | 3107520
64 | Malancha, Ctg. EPZ (United) | 31 | 40 | 39 | 40 | 35 | 40 | 36 | 9 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 14 |  | 2 | 2 | 2 | 2 | 5 | 12 | 14 | 367680
65 | Feni 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 14 | 14 | 14 | 14 | 12 | 15 | 14 | 14 | 16 | 17 | 17 |  | 15 | 15 | 15 | 15 | 18 | 18 | 18 | 372024
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 185400
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 32 | 25 | 25 | 25 | 25 | 25 | 758500
68 | Cumilla 25 MW PP (Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 0 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 258500
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456000
70 | Summit Madhabdi | 12 | 12 | 12 | 12 | 12 | 13 | 13 | 13 | 12 | 12 | 12 | 12 | 11 | 11 | 11 | 7 | 7 | 10 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 275760
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 25 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 648700
72 | Rupganj 33 MW PP(Summit) | 30 | 30 | 32 | 32 | 32 | 32 | 32 | 31 | 31 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 715000
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 17 | [10 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 233700
| Chowmuhani 113 MW | 17 | 9 | 0 | [7 empty] | 7 | 28 | 26 | 28 | 28 | 28 | 58 | 77 |  | 55 | 24 | 24 | 28 | 28 | 28 | 29 | 505680
| Manikgonj 162MW PP(MPGL) | [11 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 35 |  | 17 | 0 | [5 empty] | 172800
77 | Siddhirganj 100 PP(Dutch Bangla) | [10 empty] | 3 | 8 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 0 | [5 empty] | 66240
78 | Gazipur 52 MW PP | [8 empty] | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 25 |  | 8 | 0 | [5 empty] | 108149
79 | Kodda 150 MW PP | [8 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 98 |  | 32 | 32 | 32 | 32 | 16 | 16 | 0 | 389280
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | [10 empty] | 7 | 27 | 43 | 43 | 43 | 52 | 52 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 334627
| Gazipur 100 MW PP | 17 | [7 empty] | 17 | 30 | 35 | 34 | 35 | 35 | 35 | 35 | 35 | 70 |  | 35 | 17 | 17 | 17 | 17 | 17 | 0 | 495360
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 1 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 28199
| Jodiac Power | 17 | [9 empty] | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 263977
| Karnaphuli Power Ltd. | 17 | 17 | 17 | 17 | [6 empty] | 14 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 334544
82 | Madanganj 102 PP(Summit) | [10 empty] | 15 | 45 | 60 | 64 | 78 | 95 | 85 | 95 |  | 48 | 17 | 17 | 17 | 8 | 0 | 0 | 568030
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 147 | 149 | 148 | 146 | 145 | 147 | 146 | 147 | 150 | 150 | 152 | 152 | 150 | 153 | 152 | 153 | 151 | 150 |  | 152 | 151 | 152 | 150 | 148 | 147 | 150 | 3609745
87 | Meghnaghat 100 MW(IEL) | [11 empty] | 4 | 8 | 9 | 9 | 8 | 9 | 8 |  | 9 | 0 | [5 empty] | 64320
| Meghnaghat 104 MW PP (OPCL) | [14 empty] | 7 | 16 |  | 1 |  | 16 | 16 | 16 | 17 |  |  | 0 | 72960
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 12 | 12 | 12 | [6 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 197400
92 | Fenchuganj 44 MW (Energyprima) | 45 | 45 | 5 | 5 | 0 | 0 |  |  | 10 | 10 | 37 | 42 | 42 | 42 | 41 | 41 | 42 | 42 |  | 48 | 48 | 48 | 49 | 49 | 49 | 49 | 718992
93 | Ashuganj 51 MW PP (Midland) | 51 | 5 | 5 | 5 |  |  |  |  | 1 | 10 | 30 | 51 | 51 | 51 | 43 | 43 | 43 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 747352
94 | Gagnagar 102 MW PP (Digital Power) | [10 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 0 |  |  |  |  | 0 | 72144
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 5 |  |  |  |  | 3 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 14 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 6 | 218880
96 | Chattogram 108 MW PP (ECPV) | [20 empty] | 0 |  |  |  |  | 0 | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [11 empty] | 5 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 0 |  |  | 0 | 147761
100 | Manikganj 55 MW PP (Northern) | [19 empty] | 35 | 17 | 17 | 0 |  |  | 0 | 64552
101 | Kushiara 163 MW CCPP (KP) | 163 | 130 | 130 | 120 | 120 | 120 | 163 | 120 | 120 | 140 | 163 | 163 | 130 | 163 | 163 | 130 | 130 | 163 |  | 163 | 163 | 163 | 163 | 130 | 130 | 130 | 3543463
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 14000
103 | Kamalaghat 54 MW PP(Banco Energy) | [16 empty] | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 102600
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 24 | [5 empty] | 0 | 19 | 19 | 28 | 28 | 38 | 38 | 38 | 38 | 18 | 18 | 18 |  | 65 | 45 | 45 | 24 | 8 | 8 | 0 | 511200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | 0 |  |  | 0 | 4 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 76 |  | 112 | 88 | 79 | 35 | 30 | 17 | 17 | 596448
115 | Juldah 100 MW PP Unit-3 (Acorn) | 12 | 12 | 12 | 12 |  |  |  |  | 3 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 246720
116 | Chandpur 200 MW (Desh energy) | 17 | 17 | [8 empty] | 2 | 15 | 17 | 17 | 17 | 18 | 34 | 18 |  | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 294240
117 | Ashuganj 150 MW PP (Midland) | [11 empty] | 33 | 56 | 68 | 72 | 85 | 89 | 109 |  | 50 | 0 |  |  |  |  | 0 | 567054
118 | Bibiyana-III 400 MW CCPP | 332 | 332 | 332 | 334 | 346 | 357 | 364 | 364 | 367 | 376 | 376 | 376 | 376 | 377 | 379 | 377 | 377 | 376 |  | 376 | 377 | 377 | 376 | 376 | 377 | 377 | 8783000
| Jamalpur 115 MW PP (United) | 65 | 24 | 24 | 0 |  | 0 | 16 | 57 | 57 | 56 | 66 | 59 | 69 | 69 | 69 | 59 | 60 | 60 |  | 89 | 89 | 65 | 65 | 65 | 65 | 45 | 1246800
| Anwara 300 MW PP (United) | 50 | 15 | 16 | 16 | 16 | 0 |  |  | 30 | 30 | 66 | 70 | 70 | 70 | 70 | 70 | 97 | 170 |  | 170 | 170 | 170 | 170 | 80 | 80 | 80 | 1658509
| Juldah unit-2 (Acorn) | 12 | 12 | 12 | 12 | [5 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 229440
| Anlima Energy Ltd. | 17 | 17 | 17 | [6 empty] | 2 | 17 | 17 | 30 | 34 | 34 | 17 | 17 | 27 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 479236
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 443520
| Spectra Solar Plant Ltd. | [6 empty] | 3 | 12 | 20 | 26 | 31 | 32 | 29 | 25 | 18 | 10 | 1 | 0 | [8 empty] | 205714
| Chandpur 115(Doreen) | 18 | 18 | 18 | 18 | [5 empty] | 3 | 18 | 18 | 18 | 18 | 17 | 18 | 19 | 83 |  | 72 | 72 | 72 | 62 | 53 | 53 | 53 | 680640
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 0 | [6 empty] | 5 | 17 | 33 | 35 | 35 | 35 | 35 | 35 | 35 |  | 30 | 34 | 34 | 17 | 17 | 17 | 17 | 456120
| Mirsharai 150 MW (Oil) | [11 empty] | 17 | 53 | 53 | 53 | 17 | 17 | 53 |  | 34 | 17 | 17 | 0 |  |  | 0 | 274327
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 6 | 8 | 10 | 12 | 10 | 7 | 6 | 0 | 0 | 1 | 3 | 4 | 6 | 5 | 4 | 2 | 4 | 4 |  | 5 | 2 | 2 | 5 | 4 | 3 | 6 | 108960
| Matarbari 2*600 MW (CPGCL) | 200 | 194 | 200 | 199 | 200 | 200 | 198 | 200 | 190 | 189 | 190 | 192 | 137 | 136 | 180 | 138 | 134 | 141 |  | 143 | 148 | 142 | 143 | 144 | 144 | 145 | 4181818
120 | Eastern Zone Total | 5996 | 5606 | 5449 | 5246 | 5026 | 4970 | 5111 | 5080 | 5511 | 5588 | 6010 | 6363 | 6416 | 6538 | 6632 | 6441 | 6545 | 7153 |  | 6880 | 6754 | 6644 | 6511 | 6084 | 6053 | 5893 | 145693171
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [17 empty] | 16 |  | 16 | 16 | 16 | 0 |  |  | 0 | 50880
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 4 | 29 |  | 2 | 0 | [5 empty] | 44160
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [11 empty] | 5 | 13 | 17 | 17 | 17 | 17 | 18 |  | 34 | 17 | 17 | 17 |  |  |  | 195360
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 9 | 30 | 52 | 68 | 77 | 79 | 73 | 58 | 40 | 19 | 3 | 0 | [8 empty] | 516960
131 | Rampal 1320 MW (BIFPCL) | 352 | 353 | 355 | 353 | 352 | 367 | 354 | 355 | 353 | 353 | 352 | 353 | 353 | 340 | 333 | 334 | 333 | 333 |  | 332 | 335 | 333 | 333 | 342 | 338 | 338 | 8290909
132 | United Payra Power Ltd. | [16 empty] | 2 | 17 |  | 17 | 0 | [5 empty] | 40800
133 | Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 220 | 220 | 180 | 180 | 220 | 220 | 180 | 180 | 180 | 180 | 220 |  | 220 | 220 | 220 | 222 | 222 | 222 | 200 | 4856345
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [19 empty] | 16 | 0 |  |  |  |  | 0 | 17664
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3687300
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 122 | 126 | 126 | 126 | 100 | 100 | 80 | 80 | 80 | 122 |  | 122 | 130 | 122 | 122 | 124 | 130 | 124 | 2483000
140 | Bhola 33 MW PP (Venture) | 20 | 19 | 19 | 18 | 17 | 16 | 16 | 15 | 13 | 16 | 15 | 19 | 19 | 20 | 18 | 19 | 17 | 22 |  | 21 | 20 | 22 | 22 | 22 | 21 | 20 | 448000
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 8 |  | 8 | 8 | 0 |  |  |  | 0 | 23250
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [16 empty] | 3 | 15 |  | 15 | 15 | 4 | 0 |  |  | 0 | 46512
146 | Bheramara HVDC | 896 | 895 | 896 | 895 | 895 | 894 | 896 | 895 | 896 | 895 | 896 | 896 | 896 | 896 | 896 | 895 | 895 | 896 |  | 895 | 895 | 895 | 895 | 895 | 896 | 896 | 21348363
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 800 | 720 | 640 | 540 | 520 | 520 | 530 | 640 | 710 | 710 | 740 | 780 | 900 | 650 | 600 | 600 | 600 | 680 |  | 960 | 1060 | 1080 | 1120 | 1120 | 1000 | 980 | 20112600
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4121800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 28 | 0 | [5 empty] | 24493
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 2 | 3 | 4 | 5 | 5 | 5 | 4 | 2 | 1 | 0 | [9 empty] | 35100
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 150 | 151 | 151 | 130 | 130 | 130 | 135 | 159 | 140 | 140 | 140 | 142 | 152 | 152 | 152 | 151 | 152 | 152 |  | 151 | 151 | 151 | 150 | 151 | 152 | 152 | 3750009
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 235 | 248 | 260 | 220 | 200 | 200 | 346 | 304 | 261 | 243 | 230 | 229 | 202 | 194 | 181 | 189 | 195 | 201 |  | 200 | 208 | 234 | 236 | 230 | 230 | 234 | 5521672
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [26 empty] | 0
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 214668
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern) | [13 empty] | 8 | 42 | 8 | 8 | 8 | [7 empty] | 0 | 60887
167 | Katakhali 50 MW Peaking PP | [17 empty] | 40 | [8 empty] | 40208
168 | Santahar 50 MW Peaking PP | [17 empty] | 38 | [7 empty] | 0 | 45086
169 | Natore 52 MW PP (Rajlanka) | [13 empty] | 8 | 8 | 8 | 43 | 43 | [8 empty] | 103291
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 55 |  | 25 | 0 |  |  |  |  | 0 | 89200
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [12 empty] | 5 | 35 | 35 | 35 | 35 | 43 |  | 35 | 0 |  |  |  |  | 0 | 253536
172 | Confidence Power Bogura Unit-1 113 MW | [13 empty] | 35 | 35 | 35 | 35 | 55 |  | 0 | [5 empty] | 0 | 216672
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 20 | 108 |  | 34 | 34 | 20 | 0 |  |  | 0 | 181046
177 | Sympa Solar Power 8MW | [16 empty] | 0 | [9 empty] | 984
178 | Energypac Power Venture Thakurgaon Ltd. | [17 empty] | 87 |  | 54 | 36 | 36 | 0 |  |  | 0 | 169536
| Intraco Solar 30 MW | [6 empty] | 4 | 14 | 24 | 30 | 35 | 35 | 33 | 27 | 19 | 8 | 1 | 0 | [8 empty] | 232438
| Adani Power Jharkhanda Ltd | 915 | 905 | 828 | 822 | 815 | 817 | 820 | 817 | 823 | 833 | 872 | 907 | 1017 | 1025 | 1012 | 1012 | 1011 | 1135 |  | 1170 | 1178 | 1166 | 1171 | 1165 | 1061 | 1054 | 23579273
178 | Teesta Solar Limited | [6 empty] | 24 | 80 | 130 | 165 | 181 | 185 | 162 | 141 | 101 | 46 | 6 | 0 | [8 empty] | 1233560