## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-10-31 | Tuesday
|  | Date (day): | 2023-10-31 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12643.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14555 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-10-30 | 2023-10-31 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 160 | 180 | 180 | 180
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  |  | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 414 | 376 | 400 | 412
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 330 | 322 | 330 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 170 | 225 | 225 | 225 |  | GT-1 under S/D due to Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 4 | 8 | 8 | 8 | 92 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 152 | 120 | 150 | 150 | 185 |  | GT-1 under S/D due to Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 72 | 95 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 15 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 13 | 45 | 10 | 45 | 30 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 11 | 15 | 16 | 16 |  | 6 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 9 | 9 | 8 | 8 | 92 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 30 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 8 | 8 | 8 | 94 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 0 | 17 | 37 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 82 | 16 | 132 | 17 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 0 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 0 | 55
| Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
25 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 30 | 30 | 31 | 31 |  | 49 | Engine problem
26 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
27 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 24 | 26 | 30 | 30
28 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 25 | 8 | 25 | 27 |  | Fuel shortage
29 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
30 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 80 | 108 | 80 | 130 | 170 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
31 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 41 | 17 | 135 | 14 |  | Fuel shortage
32 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 88 | 35 | 88 |  | 17 | Engine problem
33 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 6 | 0 | 0 | 17 | 87 |  | Fuel shortage
34 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 35 | 17 | 35 | 127 |  | Fuel shortage
35 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 31 | 0 | 35 | 0
36 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 35 | 35 | 55
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 388 | 200 | 100 | 100
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 38 | 0 | 0
| Dhaka area Total |  |  |  |  | 5763 | 5422 | 2133 | 2191 | 1917 | 2750 | 1761 | 832
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
38 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 5 | 8 | 17 | 8 |  | Fuel shortage
39 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 2 | 19 | 6 | 19 | 31 |  | Fuel shortage
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 208 | 160 | 162 | 162 |  | 68 | Engine problem
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 202 | 202 | 210 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 17 | 17 | 88 |  | Fuel shortage
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 6 | 82 | 40 | 65 | 33 |  | Fuel shortage
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 34 | 17 | 34 |  | 68 | Engine problem
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 12 | 12 | 12 | 12 | 10 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 0 | 7 | 20
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 88 | 220 | 65 | 245 | 55 |  | Fuel shortage
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 17 | 17 | 93 |  | Fuel shortage
55 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
56 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 34 | 82 |  | Fuel shortage
57 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 36 | 36 | 35 | 163
58 | SS Power I |  | Coal | SS Power | 1*612 | 612 | 612 | 321 | 415 | 600 | 600 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 4 | 0 | 10 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 257 | 257 | 300 | 300 |  |  | On test.
| Chattogram area Total |  |  |  |  | 3217 | 3157 | 1281 | 1546 | 1601 | 1983 | 989 | 466
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 168 | 179 | 190 | 200 | 21 |  | Gas shortage
60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 315 | 280 | 280 | 80 |  | Gas shortage
61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 240 | 240 | 275 | 275 | 85 |  | Gas shortage
62 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 240 | 240 | 240 | 240 | 160 |  | Gas shortage
63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 0 | 0 | 0 | 45 |  | Gas shortage
| Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortae
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 50 | 100 | 150 | 150
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 30
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 17 | 17 | 17 | 183 |  | Fuel shortage
70 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 18 | 18 | 18 |  | 4 | Engine problem
71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 127 | 146 | 143 | 166
72 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 24 | 33 | 33
73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 28 | 43 | 52 | 52
74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 17 | 17 | 17 | 80 | 17 | Fuel shortage & Engine problem
76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 17 | 87 | 28 | 88 | 25 |  | Fuel shortage
77 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 35 |  | 19 | Engine problem
78 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 18 | 94 | 17 | 94 | 21 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2896 | 1332 | 1608 | 1551 | 1769 | 895 | 216
79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 33 | 34 | 34 | 45 | 157 |  | Gas shortage
80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 16 | 19 |  | 3 | Engine problem
| Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 28 | 95 | 66 | 100 | 100 |  | Fuel shortage
83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 89 | 90 | 40 | 85 | 30 |  | Fuel shortage
84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 53 | 0 | 50 | 0
85 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 230 | 244 | 213.6 | 255 | 157 | 3
86 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 0 | 0 |  | 70 | Machine problem.
87 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 28 | 20 | 40 | 40 |  | 50 | Under maint.
88 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
89 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
90 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0
91 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 45 | 42 | 42 | 42
92 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 2 | 2 | 2 |  | 9 | Engine problem
93 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 55 | 62 | 62
94 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 0 | 0 | 0 | 86 |  | Gas shortage
95 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 201 | 200 | 200 | 200 |  | 31 | Machine problem
97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 17 | 17
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 16 | 16 | 16 | 9 |  | Gas shortage
99 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 290 | 290 | 300 |  |  | FGMO
100 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 403 | 404 | 400 | 400 |  |  | FGMO
101 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
102 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 300 | 300 | 300 | 310
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1525 | 1519 | 1542 | 1562 | 95 | 590
103 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 901 | 775 | 902 | 902
104 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 19 | 49 | 65 | 50 |  | Fuel shortage
105 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 40 |  | 14 | Engine problem
106 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
107 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 | 49 |  | Fuel shortage
108 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
109 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 16 | 24 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
110 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 5 | 17 | 53 | 53 | 52 |  | Fuel shortage
111 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 32 | 15 | 32 | 73 |  | Fuel shortage
112 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 85 | 0 | 100 | 0
113 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0
114 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 336 | 407 | 570 | 570 | 47 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 1327 | 1250 | 1689 | 1738 | 951 | 14
115 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 16 | 110
116 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 20 | 22 | 21 | 25 |  | 15 | Engine problem
117 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 130 | 130 | 130 | 130 |  | 64 | ST under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 600 | 960 | 1244 | 1244
119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 222 | 220 | 220
120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 16 | 38 | 150
121 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 150 | 150 | 150 | 150 | 157 |  | Coal shortage
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1120 | 1500 | 1819 | 2029 | 157 | 79
122 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
123 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 30 | 22 |  | Fuel shortage
124 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 16 |  | 55 | Engine problem
125 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 28 | 28
126 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 8 | 34 | 42 |  | 8 | Engine problem
127 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 39 | 30 | 40 |  | 10 | Engine problem
128 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 149 | 145 | 150 | 160 | 50 |  | Gas shortage
129 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
130 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
131 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 154 | 161 | 250 | 300 | 114 |  | Gas shortage
132 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 24 | 35 | 15 |  | Fuel shortage
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
133 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 0 | 11 | 11
134 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 10 | 8 | 8 | 44 |  | Fuel shortage
135 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 32 | 50 | 94 |  | 10 | Engine problem
136 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
137 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 6 | 49 | 35 | 50 | 63 |  | Fuel shortage
138 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 55 | 35 | 57 | 56 |  | Fuel shortage
139 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1110 | 1217 | 1200 | 1200 | 296
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 1470 | 1754 | 1861 | 2071 | 1471 | 83
140 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
141 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
142 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
143 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
144 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 110 | 42 | 113
145 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
146 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 85 | 70 | 115
147 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0
148 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 193 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 405 | 365 | 450 | 398 | 125 | 189
| Total |  |  |  |  | 25339 | 24599 | 10823 | 11977 | 12643.6 | 14555 | 6601 | 2472
A. |  | 2023-10-30 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 11977 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 8476 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11977 | MW
3 | Day peak Generation : |  |  | 10823 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11770.39 | MW
4 | Evening peak Generation : |  |  | 11977 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 249.6547 | MKWHr | By Solar | 2.8035 | MKWHr
| By Gas : | 122.6122 | MKWHr |  | By Oil: | 19.2145 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 75.7349 | MKWHr |  | By Hydro: | 4.5158 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.10032 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6601 | MW | Dhaka | 4567.89 | 4567.89 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2472 | MW | Chittagong | 1198.5 | 1198.5 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 9073 | MW | Khulna | 1350.7 | 1350.7 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 920.49 | MMCFD |  |  | Rajshahi | 1128.8 | 1128.8 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 121770106.038 | ii) Oil : | Taka | 249947363.28 | Comilla | 1057 | 1057 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 533725029.67 | Total | Taka | 905442498.988 | Mymensingh | 930 | 930 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 450 | 450 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 940 | MW (W to E) at | 18:00 | hrs | Barisal | 326.5 | 326.5 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 940 | MW at | 18:00 | hrs | Rangpur | 761 | 761 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31.6°C |  |  | Total | 11770.39 | 11770.39 |  | 0
B. |  | 2023-10-31 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 32.5°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14555 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10800 | MW
4 | Reserve(Generation end) |  |  |  | 2555 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 250.1342 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8643 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.6553 | MKWHr. | ii) HVDC Flow at Peak Time |  | 775 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.0182 | MKWHr. | iii) Maximum HVDC Flow : |  | 901 | MW at | 4:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 102.66 |  | (b) Today: | 102.39 |  | (c) Rule Curve: |  | 108.7
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-10-30 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 351 | 302 |  | 0 | 225 | 146 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 19 | 12 | 33 | 30 | 0 | 0 | 131 | 75 | 0 | 0 | 0 | 174 | 0 | 0 | 0 |  | 0 | 50 | 17 | 12 | 0 | 6 | 12 | 10 | 0 | 0 | 0 | 280 | 240 | 200 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 8 | 25 | 12 | 122 | 95 | 0 | 19 | 0 | 43 | 0 | 0 | 49 | 130 | 0 | 57 | 0 | 0 | 190 | 18 | 0 | 10 | 280 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 12 | 17 | 0 | 377 | 0 | 0 | 17 | 0 | 16 | 0 | 17 | 0 | 12 | 12 | 310 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 35 | 17 | 240 | 0 | 0 | 496 | 6 | 144 | 92 | 0 |  | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 820 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 150 | 867 | 0 | 0 |  | 5709 | 4006 | 9715 | 3431 | 900 | 1766 | 0 | 232 | 2985 | 206 | 0 | 67 | 122 | 0 | 6 | 0 | 102.76
2:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 351 | 284 |  | 0 | 225 | 145 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 19 | 12 | 25 | 30 | 0 | 0 | 131 | 75 | 0 | 0 | 0 | 174 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 6 | 12 | 10 | 0 | 0 | 0 | 280 | 240 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 25 | 12 | 118 | 95 | 0 | 19 | 0 | 43 | 0 | 0 | 49 | 130 | 0 | 40 | 0 | 0 | 190 | 18 | 0 | 10 | 270 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 377 | 0 | 0 | 17 | 0 | 16 | 0 | 17 | 0 | 9 | 12 | 310 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 18 | 17 | 240 | 0 | 0 | 540 | 6 | 145 | 63 | 0 |  | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 640 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 150 | 826 | 0 | 0 |  | 5488 | 3791 | 9279 | 3395 | 899 | 1669 | 0 | 158 | 2811 | 206 | 0 | 17 | 118 | 0 | 6 | 0 | 102.74
3:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 319 | 257 |  | 0 | 225 | 149 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 19 | 12 | 25 | 32 | 0 | 0 | 131 | 75 | 0 | 0 | 0 | 174 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 6 | 12 | 16 | 0 | 0 | 0 | 280 | 240 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 25 | 12 | 116 | 100 | 0 | 19 | 0 | 43 | 0 | 0 | 10 | 130 | 0 | 40 | 0 | 0 | 190 | 18 | 0 | 10 | 290 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 364 | 0 | 0 | 17 | 0 | 16 | 0 | 17 | 0 | 0 | 12 | 310 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 18 | 17 | 240 | 0 | 0 | 460 | 6 | 145 | 90 | 0 |  | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 150 | 828 | 0 | 0 |  | 5339 | 3622 | 8961 | 3298 | 899 | 1594 | 0 | 132 | 2693 | 206 | 0 | 17 | 116 | 0 | 6 | 0 | 102.72
4:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 307 | 256 |  | 0 | 225 | 152 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 19 | 12 | 25 | 32 | 0 | 0 | 131 | 75 | 0 | 0 | 0 | 174 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 12 | 20 | 0 | 0 | 0 | 280 | 240 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 25 | 12 | 110 | 100 | 0 | 19 | 0 | 43 | 0 | 0 | 0 | 130 | 0 | 40 | 0 | 0 | 190 | 18 | 0 | 10 | 280 | 8 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 240 | 0 | 0 | 430 | 7 | 147 | 76 | 0 |  | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 150 | 827 | 0 | 0 |  | 5118 | 3582 | 8700 | 3237 | 901 | 1566 | 0 | 33 | 2623 | 206 | 0 | 17 | 110 | 0 | 7 | 0 | 102.7
5:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 307 | 257 |  | 0 | 225 | 150 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 19 | 12 | 25 | 32 | 0 | 0 | 131 | 75 | 0 | 0 | 0 | 175 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 20 | 0 | 0 | 0 | 280 | 270 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 25 | 12 | 110 | 100 | 0 | 19 | 0 | 43 | 0 | 0 | 0 | 130 | 0 | 40 | 0 | 0 | 190 | 18 | 0 | 10 | 300 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 240 | 0 | 0 | 355 | 8 | 147 | 100 | 0 |  | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 150 | 828 | 0 | 0 |  | 4940 | 3577 | 8517 | 3123 | 900 | 1648 | 0 | 17 | 2505 | 206 | 0 | 0 | 110 | 0 | 8 | 0 | 102.68
6:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 307 | 258 |  | 0 | 225 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 19 | 12 | 25 | 32 | 0 | 0 | 131 | 75 | 0 | 0 | 0 | 174 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 21 | 0 | 0 | 0 | 280 | 280 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 25 | 12 | 104 | 100 | 0 | 19 | 0 | 43 | 0 | 0 | 0 | 130 | 0 | 40 | 0 | 0 | 190 | 18 | 0 | 10 | 310 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 240 | 0 | 0 | 355 | 6 | 145 | 100 | 0 |  | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 150 | 827 | 0 | 0 |  | 4904 | 3572 | 8476 | 3084 | 900 | 1650 | 0 | 17 | 2509 | 206 | 0 | 0 | 104 | 0 | 6 | 0 | 102.66
7:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 340 | 342 |  | 0 | 225 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 19 | 12 | 25 | 32 | 0 | 0 | 131 | 75 | 0 | 0 | 0 | 175 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 36 | 0 | 0 | 0 | 300 | 280 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 25 | 12 | 98 | 84 | 0 | 19 | 0 | 43 | 0 | 0 | 0 | 130 | 0 | 40 | 0 | 0 | 190 | 17 | 0 | 10 | 320 | 0 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 1 | 2 | 0 | 0 | 0 | 401 | 10 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 6 | 0 | 0 | 0 | 17 | 4 | 0 | 0 | 240 | 0 | 0 | 355 | 6 | 147 | 100 | 0 |  | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 4 | 150 | 905 | 27 | 0 |  | 5082 | 3758 | 8840 | 3124 | 900 | 1819 | 0 | 36 | 2607 | 206 | 0 | 0 | 98 | 44 | 6 | 0 | 102.64
8:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 392 | 273 |  | 0 | 225 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 19 | 12 | 25 | 30 | 0 | 0 | 131 | 75 | 0 | 0 | 0 | 176 | 0 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 12 | 7 | 0 | 0 | 0 | 280 | 275 | 160 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 18 | 8 | 25 | 12 | 104 | 34 | 0 | 19 | 1 | 43 | 0 | 0 | 20 | 120 | 0 | 62 | 0 | 0 | 190 | 17 | 0 | 10 | 280 | 0 | 2 | 0 | 0 | 0 | 0 | 19 | 0 | 13 | 11 | 1 | 0 | 0 | 377 | 56 | 17 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 9 | 0 | 0 | 0 | 17 | 12 | 0 | 0 | 240 | 0 | 0 | 385 | 3 | 137 | 83 | 0 |  | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 660 | 220 | 0 | 0 | 2 | 31 | 0 | 0 | 0 | 339 | 15 | 150 | 1010 | 83 | 0 |  | 5142 | 4102 | 9244 | 3222 | 899 | 1651 | 0 | 124 | 2851 | 206 | 0 | 16 | 104 | 168 | 3 | 0 | 102.72
9:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 382 | 273 |  | 0 | 225 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 19 | 12 | 25 | 30 | 8 | 0 | 132 | 35 | 0 | 0 | 0 | 177 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 12 | 2 | 0 | 0 | 0 | 280 | 260 | 155 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 18 | 8 | 25 | 12 | 106 | 34 | 0 | 19 | 1 | 43 | 0 | 0 | 20 | 120 | 0 | 61 | 0 | 0 | 191 | 17 | 0 | 9 | 300 | 0 | 2 | 0 | 0 | 0 | 0 | 19 | 0 | 17 | 15 | 12 | 0 | 0 | 400 | 59 | 35 | 17 | 2 | 49 | 0 | 6 | 0 | 0 | 0 | 300 | 0 | 33 | 0 | 0 | 0 | 17 | 21 | 0 | 0 | 240 | 0 | 0 | 399 | 3 | 139 | 100 | 0 |  | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 700 | 220 | 0 | 0 | 3 | 54 | 0 | 0 | 0 | 338 | 24 | 150 | 1024 | 133 | 0 |  | 5260 | 4244 | 9504 | 3139 | 900 | 1718 | 0 | 245 | 2920 | 167 | 0 | 16 | 106 | 290 | 3 | 0 | 102.6
10:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 393 | 330 |  | 0 | 225 | 153 | 0 | 5 | 1 | 0 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 12 | 25 | 30 | 8 | 0 | 132 | 35 | 0 | 0 | 0 | 177 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 12 | 2 | 0 | 0 | 0 | 280 | 260 | 161 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 12 | 122 | 35 | 0 | 19 | 2 | 33 | 0 | 0 | 39 | 163 | 0 | 60 | 0 | 0 | 198 | 17 | 0 | 10 | 300 | 0 | 2 | 0 | 0 | 0 | 0 | 19 | 0 | 17 | 12 | 12 | 0 | 0 | 403 | 55 | 35 | 17 | 4 | 65 | 0 | 17 | 0 | 0 | 12 | 300 | 0 | 24 | 0 | 1 | 0 | 17 | 27 | 0 | 0 | 240 | 0 | 0 | 374 | 4 | 196 | 394 | 0 |  | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 540 | 180 | 0 | 0 | 4 | 71 | 0 | 0 | 0 | 334 | 31 | 150 | 1029 | 167 | 0 |  | 5779 | 4059 | 9838 | 3097 | 899 | 2097 | 0 | 295 | 2793 | 167 | 0 | 16 | 122 | 348 | 4 | 0 | 102.59
11:00 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 413 | 330 |  | 0 | 225 | 150 | 0 | 26 | 15 | 0 | 0 | 0 | 5 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 19 | 11 | 33 | 24 | 8 | 0 | 133 | 35 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 6 | 0 | 2 | 0 | 0 | 0 | 12 | 2 | 0 | 0 | 0 | 280 | 260 | 163 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 4 | 17 | 8 | 25 | 12 | 130 | 35 | 0 | 19 | 1 | 33 | 0 | 0 | 48 | 163 | 0 | 59 | 0 | 0 | 202 | 17 | 0 | 10 | 305 | 0 | 2 | 0 | 3 | 0 | 0 | 28 | 0 | 17 | 19 | 12 | 4 | 5 | 403 | 77 | 35 | 17 | 3 | 87 | 6 | 17 | 0 | 0 | 12 | 300 | 0 | 20 | 0 | 17 | 0 | 17 | 31 | 7 | 24 | 240 | 0 | 0 | 328 | 1 | 234 | 393 | 0 |  | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 560 | 180 | 0 | 0 | 5 | 78 | 0 | 0 | 0 | 337 | 35 | 150 | 1108 | 189 | 0 |  | 6051 | 4177 | 10228 | 3205 | 899 | 2076 | 0 | 457 | 2887 | 168 | 0 | 18 | 130 | 387 | 1 | 0 | 102.58
12:00 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 414 | 330 |  | 0 | 225 | 152 | 4 | 72 | 15 | 0 | 0 | 0 | 9 | 8 | 16 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 19 | 11 | 33 | 24 | 8 | 0 | 133 | 75 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 6 | 6 | 17 | 12 | 0 | 2 | 12 | 0 | 0 | 0 | 0 | 280 | 240 | 168 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 28 | 17 | 8 | 25 | 12 | 127 | 33 | 0 | 19 | 2 | 0 | 28 | 0 | 45 | 163 | 0 | 58 | 0 | 0 | 201 | 17 | 0 | 10 | 290 | 8 | 2 | 0 | 80 | 0 | 0 | 28 | 0 | 17 | 20 | 12 | 17 | 50 | 403 | 89 | 35 | 17 | 4 | 88 | 17 | 17 | 17 | 17 | 12 | 300 | 6 | 53 | 17 | 17 | 0 | 17 | 31 | 18 | 35 | 240 | 36 | 0 | 321 | 4 | 257 | 388 | 0 |  | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 5 | 0 | 6 | 0 | 0 | 0 | 6 | 35 | 600 | 220 | 0 | 0 | 5 | 85 | 0 | 0 | 0 | 336 | 36 | 150 | 1110 | 193 | 0 |  | 6501 | 4322 | 10823 | 3235 | 901 | 2048 | 0 | 846 | 2944 | 208 | 0 | 75 | 127 | 435 | 4 | 0 | 102.57
13:00 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 411 | 330 |  | 0 | 225 | 152 | 9 | 78 | 15 | 0 | 0 | 0 | 9 | 8 | 16 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 19 | 11 | 33 | 24 | 8 | 0 | 132 | 75 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 6 | 57 | 17 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 280 | 240 | 175 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 38 | 17 | 8 | 25 | 12 | 128 | 31 | 0 | 19 | 2 | 0 | 29 | 0 | 45 | 163 | 0 | 55 | 0 | 0 | 201 | 17 | 0 | 10 | 300 | 16 | 2 | 0 | 76 | 0 | 0 | 38 | 0 | 19 | 18 | 12 | 17 | 88 | 403 | 77 | 35 | 17 | 4 | 70 | 17 | 17 | 17 | 56 | 12 | 300 | 16 | 13 | 17 | 17 | 0 | 17 | 29 | 18 | 35 | 240 | 36 | 0 | 321 | 6 | 256 | 373 | 0 |  | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 35 | 0 | 0 | 0 | 6 | 35 | 670 | 220 | 0 | 0 | 4 | 80 | 0 | 0 | 0 | 339 | 34 | 150 | 1113 | 181 | 0 |  | 6622 | 4417 | 11039 | 3232 | 899 | 2071 | 0 | 980 | 3019 | 207 | 0 | 126 | 128 | 371 | 6 | 0 | 102.56
14:00 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 389 | 300 |  | 0 | 170 | 146 | 8 | 78 | 15 | 0 | 0 | 0 | 9 | 8 | 16 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 28 | 8 | 0 | 131 | 75 | 0 | 0 | 0 | 203 | 0 | 0 | 0 |  | 6 | 59 | 17 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 280 | 240 | 180 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 43 | 17 | 8 | 25 | 12 | 130 | 32 | 0 | 19 | 2 | 0 | 20 | 0 | 45 | 163 | 0 | 57 | 0 | 0 | 201 | 16 | 0 | 10 | 285 | 16 | 2 | 0 | 48 | 0 | 0 | 37 | 0 | 17 | 7 | 12 | 17 | 100 | 379 | 80 | 35 | 17 | 3 | 88 | 17 | 17 | 17 | 57 | 12 | 300 | 17 | 40 | 17 | 17 | 0 | 17 | 24 | 18 | 35 | 240 | 36 | 0 | 321 | 6 | 260 | 332 | 0 |  | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 35 | 0 | 0 | 0 | 5 | 35 | 720 | 220 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 339 | 29 | 150 | 1065 | 152 | 0 |  | 6449 | 4365 | 10814 | 3185 | 899 | 1919 | 0 | 988 | 3025 | 206 | 0 | 128 | 130 | 328 | 6 | 0 | 102.58
15:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 402 | 312 |  | 0 | 170 | 120 | 13 | 78 | 15 | 0 | 0 | 0 | 9 | 8 | 16 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 28 | 8 | 0 | 130 | 75 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 6 | 62 | 17 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 280 | 240 | 178 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 43 | 17 | 8 | 25 | 12 | 130 | 34 | 0 | 19 | 1 | 0 | 20 | 0 | 48 | 163 | 0 | 55 | 0 | 0 | 201 | 17 | 0 | 10 | 310 | 16 | 2 | 0 | 48 | 0 | 0 | 37 | 0 | 17 | 11 | 12 | 17 | 95 | 404 | 80 | 35 | 17 | 2 | 88 | 17 | 17 | 17 | 57 | 12 | 300 | 2 | 28 | 17 | 17 | 0 | 17 | 17 | 17 | 35 | 240 | 36 | 0 | 320 | 4 | 257 | 301 | 0 |  | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 35 | 0 | 18 | 0 | 5 | 35 | 800 | 220 | 0 | 0 | 1 | 46 | 35 | 0 | 0 | 337 | 22 | 150 | 1110 | 102 | 0 |  | 6451 | 4451 | 10902 | 3241 | 899 | 1885 | 0 | 1028 | 3144 | 205 | 0 | 131 | 130 | 235 | 4 | 0 | 102.54
16:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 413 | 310 |  | 0 | 170 | 120 | 17 | 80 | 15 | 0 | 0 | 0 | 9 | 8 | 32 | 46 | 0 | 0 | 0 | 0 | 0 | 17 | 10 | 19 | 11 | 33 | 28 | 8 | 0 | 130 | 75 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 6 | 64 | 17 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 280 | 240 | 175 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 43 | 17 | 8 | 25 | 12 | 140 | 34 | 0 | 19 | 0 | 0 | 20 | 0 | 42 | 163 | 0 | 55 | 0 | 0 | 200 | 17 | 0 | 10 | 300 | 8 | 2 | 0 | 30 | 0 | 0 | 37 | 0 | 17 | 6 | 12 | 17 | 80 | 404 | 80 | 35 | 17 | 1 | 88 | 17 | 17 | 17 | 58 | 12 | 300 | 0 | 12 | 17 | 17 | 0 | 17 | 8 | 18 | 35 | 240 | 17 | 0 | 320 | 3 | 255 | 186 | 40 |  | 898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 35 | 0 | 34 | 0 | 3 | 35 | 760 | 220 | 0 | 0 | 1 | 22 | 35 | 0 | 0 | 343 | 9 | 150 | 1126 | 48 | 0 |  | 6341 | 4353 | 10694 | 3250 | 898 | 1790 | 0 | 1044 | 3124 | 205 | 0 | 130 | 140 | 110 | 3 | 0 | 102.53
17:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 409 | 310 |  | 0 | 170 | 120 | 13 | 80 | 15 | 0 | 0 | 0 | 9 | 8 | 32 | 46 | 0 | 0 | 0 | 17 | 17 | 17 | 15 | 19 | 11 | 33 | 28 | 8 | 0 | 84 | 75 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 6 | 64 | 17 | 12 | 0 | 10 | 12 | 0 | 0 | 0 | 0 | 280 | 240 | 178 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 43 | 18 | 8 | 24 | 12 | 134 | 34 | 0 | 19 | 0 | 0 | 20 | 0 | 44 | 130 | 0 | 51 | 0 | 0 | 200 | 17 | 0 | 10 | 310 | 16 | 2 | 0 | 30 | 0 | 0 | 37 | 0 | 17 | 0 | 12 | 17 | 83 | 404 | 80 | 35 | 17 | 0 | 105 | 17 | 17 | 17 | 58 | 12 | 300 | 0 | 1 | 17 | 17 | 0 | 17 | 1 | 37 | 35 | 240 | 17 | 0 | 345 | 3 | 255 | 175 | 40 |  | 898 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 17 | 0 | 35 | 15 | 56 | 0 | 1 | 55 | 760 | 180 | 0 | 0 | 0 | 3 | 40 | 0 | 0 | 329 | 1 | 150 | 1120 | 3 | 0 |  | 6338 | 4275 | 10613 | 3220 | 898 | 1718 | 0 | 1212 | 3129 | 159 | 0 | 130 | 134 | 10 | 3 | 0 | 102.52
18:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 376 | 322 |  | 0 | 170 | 120 | 8 | 95 | 15 | 0 | 0 | 0 | 9 | 8 | 82 | 45 | 0 | 0 | 0 | 35 | 35 | 17 | 15 | 19 | 11 | 33 | 26 | 25 | 0 | 85 | 75 | 0 | 0 | 5 | 202 | 0 | 0 | 0 |  | 6 | 82 | 34 | 12 | 0 | 19 | 12 | 0 | 0 | 0 | 0 | 315 | 240 | 179 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 43 | 18 | 8 | 24 | 12 | 146 | 34 | 0 | 19 | 0 | 0 | 20 | 0 | 42 | 163 | 0 | 55 | 0 | 0 | 200 | 17 | 0 | 10 | 290 | 16 | 2 | 0 | 108 | 0 | 0 | 95 | 0 | 41 | 0 | 12 | 17 | 100 | 404 | 90 | 88 | 17 | 0 | 220 | 17 | 17 | 17 | 87 | 12 | 300 | 0 | 0 | 35 | 17 | 0 | 17 | 0 | 94 | 35 | 240 | 36 | 0 | 415 | 0 | 257 | 200 | 38 |  | 775 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 8 | 39 | 10 | 38 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 17 | 0 | 49 | 32 | 110 | 0 | 0 | 55 | 960 | 222 | 0 | 16 | 0 | 0 | 85 | 0 | 0 | 407 | 0 | 150 | 1217 | 0 | 0 |  | 7108 | 4869 | 11977 | 3252 | 775 | 1811 | 0 | 1914 | 3576 | 160 | 0 | 343 | 146 | 0 | 0 | 0 | 102.51
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 409 | 317 |  | 0 | 170 | 120 | 9 | 95 | 15 | 0 | 0 | 0 | 9 | 8 | 98 | 34 | 0 | 0 | 0 | 35 | 35 | 17 | 15 | 19 | 12 | 33 | 26 | 25 | 0 | 86 | 75 | 0 | 0 | 17 | 194 | 0 | 0 | 0 |  | 6 | 49 | 34 | 12 | 0 | 19 | 12 | 0 | 0 | 0 | 0 | 280 | 240 | 187 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 25 | 18 | 8 | 24 | 12 | 138 | 34 | 0 | 19 | 0 | 0 | 20 | 0 | 47 | 163 | 0 | 60 | 0 | 0 | 200 | 17 | 0 | 10 | 280 | 16 | 2 | 0 | 60 | 0 | 0 | 93 | 0 | 128 | 0 | 12 | 18 | 100 | 403 | 90 | 88 | 17 | 0 | 195 | 17 | 17 | 17 | 87 | 12 | 300 | 0 | 0 | 35 | 17 | 0 | 17 | 0 | 95 | 35 | 240 | 17 | 0 | 450 | 2 | 262 | 130 | 31 |  | 774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 130 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 8 | 38 | 8 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 17 | 0 | 50 | 0 | 70 | 0 | 0 | 55 | 1120 | 220 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 401 | 0 | 150 | 1217 | 0 | 0 |  | 7021 | 4930 | 11951 | 3266 | 774 | 1732 | 0 | 1794 | 3770 | 161 | 0 | 314 | 138 | 0 | 2 | 0 | 102.48
19:30 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 408 | 317 |  | 0 | 225 | 120 | 9 | 95 | 15 | 0 | 0 | 0 | 9 | 8 | 64 | 22 | 0 | 0 | 0 | 35 | 35 | 17 | 15 | 19 | 11 | 33 | 26 | 25 | 0 | 86 | 75 | 0 | 0 | 17 | 196 | 0 | 0 | 0 |  | 6 | 49 | 34 | 12 | 0 | 19 | 12 | 0 | 0 | 0 | 0 | 315 | 240 | 178 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 25 | 18 | 8 | 24 | 12 | 136 | 43 | 0 | 19 | 0 | 0 | 20 | 0 | 48 | 163 | 0 | 60 | 0 | 0 | 200 | 17 | 0 | 10 | 320 | 16 | 2 | 0 | 15 | 0 | 0 | 93 | 0 | 135 | 0 | 12 | 17 | 12 | 404 | 90 | 50 | 17 | 0 | 195 | 17 | 17 | 17 | 87 | 12 | 300 | 17 | 0 | 35 | 34 | 0 | 17 | 0 | 95 | 35 | 240 | 17 | 0 | 450 | 3 | 262 | 150 | 0 |  | 832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 8 | 32 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 10 | 0 | 50 | 0 | 34 | 0 | 0 | 55 | 1080 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 401 | 0 | 150 | 1157 | 0 | 0 |  | 6964 | 4754 | 11718 | 3302 | 832 | 1818 | 0 | 1568 | 3670 | 161 | 0 | 228 | 136 | 0 | 3 | 0 | 0
20:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 409 | 319 |  | 0 | 225 | 145 | 9 | 95 | 15 | 0 | 0 | 0 | 9 | 8 | 64 | 25 | 0 | 0 | 0 | 35 | 35 | 17 | 15 | 19 | 12 | 33 | 26 | 25 | 0 | 86 | 75 | 0 | 0 | 17 | 195 | 0 | 0 | 0 |  | 6 | 49 | 34 | 12 | 0 | 19 | 12 | 2 | 0 | 0 | 0 | 280 | 240 | 177 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 25 | 18 | 8 | 24 | 12 | 130 | 64 | 0 | 19 | 0 | 0 | 20 | 0 | 46 | 163 | 0 | 57 | 0 | 0 | 200 | 17 | 0 | 10 | 290 | 16 | 2 | 0 | 15 | 0 | 0 | 93 | 0 | 130 | 0 | 12 | 17 | 28 | 403 | 90 | 50 | 17 | 0 | 195 | 17 | 17 | 17 | 88 | 12 | 300 | 11 | 0 | 35 | 34 | 0 | 17 | 0 | 95 | 35 | 240 | 17 | 0 | 450 | 3 | 260 | 120 | 0 |  | 832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 8 | 32 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 17 | 0 | 50 | 0 | 34 | 0 | 0 | 55 | 1100 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 401 | 0 | 150 | 1152 | 0 | 0 |  | 6914 | 4777 | 11691 | 3284 | 832 | 1786 | 0 | 1584 | 3683 | 161 | 0 | 228 | 130 | 0 | 3 | 0 | 102.49
21:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 407 | 328 |  | 0 | 225 | 151 | 8 | 46 | 15 | 0 | 0 | 0 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 16 | 19 | 12 | 33 | 26 | 8 | 0 | 87 | 75 | 0 | 0 | 17 | 195 | 0 | 0 | 0 |  | 6 | 49 | 34 | 12 | 0 | 19 | 12 | 4 | 0 | 0 | 0 | 280 | 240 | 181 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 8 | 33 | 12 | 132 | 86 | 0 | 19 | 0 | 0 | 40 | 0 | 48 | 163 | 0 | 57 | 0 | 0 | 205 | 17 | 0 | 10 | 290 | 16 | 2 | 0 | 15 | 0 | 0 | 45 | 0 | 90 | 0 | 12 | 17 | 12 | 402 | 70 | 17 | 17 | 0 | 170 | 17 | 17 | 17 | 90 | 12 | 300 | 17 | 0 | 17 | 34 | 0 | 17 | 0 | 74 | 35 | 240 | 17 | 0 | 450 | 2 | 260 | 142 | 0 |  | 898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 1080 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 150 | 1161 | 0 | 0 |  | 6625 | 4733 | 11358 | 3342 | 898 | 1846 | 0 | 1140 | 3672 | 162 | 0 | 164 | 132 | 0 | 2 | 0 | 102.48
22:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 406 | 337 |  | 0 | 225 | 149 | 9 | 17 | 0 | 0 | 0 | 0 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 18 | 19 | 12 | 33 | 28 | 8 | 0 | 87 | 75 | 0 | 0 | 17 | 191 | 0 | 0 | 0 |  | 6 | 49 | 34 | 12 | 0 | 19 | 12 | 3 | 0 | 0 | 0 | 280 | 240 | 188 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 8 | 33 | 12 | 128 | 86 | 0 | 19 | 0 | 0 | 39 | 0 | 48 | 163 | 0 | 60 | 0 | 0 | 203 | 17 | 0 | 10 | 280 | 16 | 2 | 0 | 0 | 0 | 0 | 18 | 0 | 66 | 0 | 12 | 17 | 10 | 402 | 70 | 17 | 17 | 0 | 155 | 17 | 17 | 17 | 87 | 12 | 300 | 0 | 0 | 17 | 34 | 0 | 17 | 0 | 72 | 17 | 240 | 17 | 0 | 495 | 5 | 262 | 137 | 0 |  | 898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 940 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 150 | 1118 | 0 | 0 |  | 6485 | 4496 | 10981 | 3348 | 898 | 1846 | 0 | 922 | 3540 | 162 | 0 | 132 | 128 | 0 | 5 | 0 | 102.47
23:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 406 | 337 |  | 0 | 225 | 143 | 9 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 33 | 31 | 0 | 0 | 87 | 75 | 0 | 0 | 8 | 192 | 0 | 0 | 0 |  | 6 | 49 | 34 | 12 | 0 | 19 | 12 | 12 | 0 | 0 | 0 | 280 | 240 | 189 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 8 | 33 | 12 | 128 | 87 | 0 | 19 | 0 | 0 | 39 | 0 | 49 | 163 | 0 | 60 | 0 | 0 | 204 | 17 | 0 | 10 | 270 | 16 | 2 | 0 | 0 | 0 | 0 | 18 | 0 | 45 | 0 | 12 | 17 | 0 | 402 | 55 | 0 | 17 | 0 | 123 | 17 | 17 | 17 | 85 | 12 | 300 | 0 | 0 | 0 | 34 | 0 | 17 | 0 | 37 | 17 | 240 | 17 | 0 | 495 | 6 | 264 | 143 | 0 |  | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 17 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 900 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 150 | 1120 | 0 | 0 |  | 6246 | 4405 | 10651 | 3356 | 899 | 1845 | 0 | 647 | 3508 | 162 | 0 | 100 | 128 | 0 | 6 | 0 | 102.46
24:00 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 406 | 337 |  | 0 | 225 | 144 | 8 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 33 | 31 | 0 | 0 | 87 | 75 | 0 | 0 | 8 | 189 | 0 | 0 | 0 |  | 6 | 49 | 17 | 12 | 0 | 6 | 12 | 12 | 0 | 0 | 0 | 280 | 240 | 188 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 8 | 33 | 12 | 120 | 87 | 0 | 19 | 0 | 0 | 39 | 0 | 49 | 163 | 0 | 57 | 0 | 0 | 204 | 17 | 0 | 10 | 300 | 16 | 2 | 0 | 0 | 0 | 0 | 19 | 0 | 17 | 0 | 12 | 17 | 0 | 402 | 55 | 0 | 17 | 0 | 65 | 17 | 17 | 17 | 44 | 12 | 300 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 18 | 17 | 240 | 17 | 0 | 495 | 6 | 262 | 150 | 0 |  | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 860 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 150 | 1117 | 0 | 0 |  | 6074 | 4339 | 10413 | 3350 | 899 | 1888 | 0 | 443 | 3462 | 162 | 0 | 83 | 120 | 0 | 6 | 0 | 102.45
KWH | 0 | 0 | 3794875 | 0 | 0 | 0 | 0 | 9345030 | 7320000 |  | 0 | 4929500 | 3417716 | 124800 | 828648 | 187056 | 933173 | 0 | 0 | 92160 | 102960 | 488160 | 317695 | 0 | 0 | 0 | 129960 | 112376 | 122156 | 309672 | 456000 | 276840 | 744900 | 686900 | 169440 | 0 | 2863767 | 1652000 | 0 | 0 | 93043 | 4472178 | 0 | 0 | 0 |  | 99120 | 766968 | 388053 | 160680 | 0 | 191040 | 298224 | 248160 | 0 | 0 | 0 | 7204400 | 6189000 | 4409000 | 0 | 0 | 0 | 0 | 0 | 755040 | 0 | 0 | 401371 | 424982 | 175500 | 639700 | 294300 | 3018240 | 1423680 | 0 | 436464 | 13000 | 338400 | 348480 | 0 | 839088 | 3622500 | 0 | 1289088 | 0 | 0 | 4993700 | 396000 | 0 | 248040 | 7191000 | 256800 | 48536 | 0 | 607200 | 0 | 0 | 696000 | 0 | 726768 | 133515 | 242880 | 271200 | 762763 | 9379000 | 1306800 | 598080 | 342909 | 28199 | 1964618 | 263789 | 349598 | 221160 | 883680 | 224640 | 7275000 | 72960 | 288000 | 260640 | 377618 | 0 | 443160 | 201949 | 702720 | 509040 | 5940900 | 314472 | 0 | 9578181 | 100320 | 5134545 | 4080454 | 106363 |  | 21655272 | 0 | 0 | 0 | 36480 | 0 | 0 | 0 | 0 | 6912 | 1500 | 2679000 | 426300 | 0 | 0 | 0 | 0 | 0 | 0 | 91248 | 0 | 20215 | 133931 | 29434 | 71154 | 0 | 0 | 197964 | 0 | 0 | 4143600 | 0 | 0 | 3626927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4984727 | 137760 | 0 | 482304 | 54144 | 398947 | 0 | 42602 | 444576 | 19847000 | 5158691 | 0 | 40800 | 31140 | 550080 | 346752 | 0 | 0 | 8567273 | 236416 | 3687300 | 24777042 | 1278560 | 0 |  | 145468680 | 104186051 | 249654731 | 79284613 | 21655272 | 43327579 | 0 | 16953640 | 75734941 | 4515767 | 0 | 2260898 | 3018240 | 2803461 | 100320 | 0
Fuel Cost | 0 | 0 | 5540517.5 | 0 | 0 | 0 | 0 | 9812281.5 | 7905600 |  | 0 | 5373155 | 3793664.76 | 1395264 | 10979586 | 2478492 | 1045153.76 | 0 | 0 | 1347379.2 | 1448647.2 | 7913073.6 | 2929147.9 | 0 | 0 | 0 | 1653091.2 | 1517076 | 1638111.96 | 232254 | 342000 | 0 | 0 | 0 | 2882174.4 | 0 | 773217.09 | 446040 | 0 | 0 | 1521253.05 | 4651065.12 | 0 | 0 | 0 |  | 1293516 | 12793026.24 | 6604662.06 | 2170786.8 | 0 | 2210332.8 | 378744.48 | 826372.8 | 0 | 0 | 0 | 7996884 | 6746010 | 5114440 | 0 | 0 | 0 | 0 | 0 | 1260916.8 | 0 | 0 | 5398439.95 | 582225.34 | 131625 | 1119475 | 220725 | 21670963.2 | 1551811.2 | 0 | 593591.04 | 207220 | 463608 | 459993.6 | 0 | 1451622.24 | 4165875 | 0 | 2500830.72 | 0 | 0 | 5043637 | 851400 | 0 | 491119.2 | 7191000 | 192600 | 36887.36 | 0 | 8288280 | 0 | 0 | 9382080 | 0 | 10065736.8 | 1560790.35 | 2506521.6 | 3704592 | 10121865.01 | 8628680 | 15890688 | 8648236.8 | 4337798.85 | 438776.44 | 23064615.32 | 2872662.21 | 3716226.74 | 3001141.2 | 11390635.2 | 2646259.2 | 6693000 | 944832 | 4161600 | 3307521.6 | 4297292.84 | 0 | 5787669.6 | 2413290.55 | 10519718.4 | 6704056.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 64965816 | 0 | 0 | 0 | 379756.8 | 0 | 0 | 0 | 0 | 124416 | 21555 | 3000480 | 827022 | 0 | 0 | 0 | 0 | 0 | 0 | 1427118.72 | 0 | 334760.4 | 2264773.21 | 401185.42 | 1200367.98 | 0 | 0 | 149858.748 | 0 | 0 | 35137728 | 0 | 0 | 4207235.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4934879.73 | 1851494.4 | 0 | 5705656.32 | 782380.8 | 5066626.9 | 0 | 470752.1 | 5397152.64 | 164730100 | 5261864.82 | 0 | 301920 | 352193.4 | 6452438.4 | 5315708.16 | 0 | 0 | 77876511.57 | 0 | 44136981 | 211843709.1 | 0 | 0 |  | 354433153.58 | 654922442.938 | 1009355596.518 | 78287013.688 | 64965816 | 43483092.35 | 0 | 217619925.47 | 533725029.67 | 1219257.09 | 0 | 32327437.81 | 21670963.2 | 16057061.24 | 0 | 0
Yesterday Day Peak | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 414 | 330 |  | 0 | 225 | 152 | 4 | 72 | 15 | 0 | 0 | 0 | 9 | 8 | 16 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 19 | 11 | 33 | 24 | 8 | 0 | 133 | 75 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 6 | 6 | 17 | 12 | 0 | 2 | 12 | 0 | 0 | 0 | 0 | 280 | 240 | 168 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 28 | 17 | 8 | 25 | 12 | 127 | 33 | 0 | 19 | 2 | 0 | 28 | 0 | 45 | 163 | 0 | 58 | 0 | 0 | 201 | 17 | 0 | 10 | 290 | 8 | 2 | 0 | 80 | 0 | 0 | 28 | 0 | 17 | 20 | 12 | 17 | 50 | 403 | 89 | 35 | 17 | 4 | 88 | 17 | 17 | 17 | 17 | 12 | 300 | 6 | 53 | 17 | 17 | 0 | 17 | 31 | 18 | 35 | 240 | 36 | 0 | 321 | 4 | 257 | 388 | 0 |  | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 5 | 0 | 6 | 0 | 0 | 0 | 6 | 35 | 600 | 220 | 0 | 0 | 5 | 85 | 0 | 0 | 0 | 336 | 36 | 150 | 1110 | 193 | 0 |  | 10823 | DayPeak
Yesterday Evening Peak | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 376 | 322 |  | 0 | 170 | 120 | 8 | 95 | 15 | 0 | 0 | 0 | 9 | 8 | 82 | 45 | 0 | 0 | 0 | 35 | 35 | 17 | 15 | 19 | 11 | 33 | 26 | 25 | 0 | 85 | 75 | 0 | 0 | 5 | 202 | 0 | 0 | 0 | 0 | 6 | 82 | 34 | 12 | 0 | 19 | 12 | 0 | 0 | 0 | 0 | 315 | 240 | 179 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 43 | 18 | 8 | 24 | 12 | 146 | 34 | 0 | 19 | 0 | 0 | 20 | 0 | 42 | 163 | 0 | 55 | 0 | 0 | 200 | 17 | 0 | 10 | 290 | 16 | 2 | 0 | 108 | 0 | 0 | 95 | 0 | 41 | 0 | 12 | 17 | 100 | 404 | 90 | 88 | 17 | 0 | 220 | 17 | 17 | 17 | 87 | 12 | 300 | 0 | 0 | 35 | 17 | 0 | 17 | 0 | 94 | 35 | 240 | 36 | 0 | 415 | 0 | 257 | 200 | 38 |  | 775 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 8 | 39 | 10 | 38 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 17 | 0 | 49 | 32 | 110 | 0 | 0 | 55 | 960 | 222 | 0 | 16 | 0 | 0 | 85 | 0 | 0 | 407 | 0 | 150 | 1217 | 0 | 0 |  | 11977 | EvPeak
Forecast for Evening | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 412 | 330 |  | 0 | 225 | 150 | 8 | 100 | 15 | 335 | 0 | 0 | 8 | 8 | 132 | 45 | 0 | 0 | 0 | 17 | 35 | 55 | 16 | 19 | 12 | 33 | 30 | 25 | 0 | 87 | 75 | 0 | 0 | 17 | 215 | 0 | 0 | 0 |  | 6 | 65 | 34 | 12 | 0 | 19 | 12 | 20 | 0 | 0 | 0 | 280 | 275 | 200 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 30 | 52 | 18 | 11 | 33 | 12 | 166 | 45 | 0 | 19 | 0 | 0 | 40 | 0 | 42 | 163 | 0 | 62 | 0 | 0 | 200 | 17 | 0 | 10 | 300 | 16 | 2 | 0 | 130 | 0 | 0 | 100 | 0 | 135 | 0 | 12 | 17 | 150 | 400 | 85 | 88 | 17 | 0 | 245 | 17 | 17 | 17 | 88 | 12 | 310 | 17 | 0 | 35 | 34 | 0 | 35 | 0 | 94 | 55 | 240 | 163 | 0 | 600 | 10 | 300 | 100 | 0 |  | 902 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 40 | 60 | 16 | 130 | 25 | 110 | 0 | 0 | 0 | 30 | 16 | 94 | 28 | 42 | 40 | 8 | 35 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 53 | 0 | 50 | 32 | 113 | 0 | 0 | 57 | 1244 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 570 | 0 | 150 | 1200 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 400 | 330 | 0 | 0 | 225 | 150 | 8 | 100 | 15 | 30 | 0 | 0 | 8 | 8 | 16 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 19 | 12 | 33 | 30 | 8 | 0 | 87 | 75 | 0 | 0 | 8 | 210 |  | 0 | 0 | 0 | 6 | 40 | 17 | 12 | 0 | 6 | 12 | 7 | 0 | 0 | 0 | 280 | 275 | 190 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 11 | 33 | 12 | 143 | 34 | 0 | 16 | 1.6 | 0 | 40 | 0 | 42 | 163 | 0 | 62 | 0 | 0 | 200 | 17 | 0 | 10 | 290 | 16 | 2 | 0 | 80 | 0 | 0 | 66 | 0 | 17 | 20 | 12 | 17 | 150 | 400 | 40 | 35 | 17 | 5 | 65 | 17 | 17 | 17 | 28 | 12 | 300 | 0 | 50 | 17 | 17 | 0 | 17 | 35 | 17 | 35 | 240 | 35 |  | 600 | 10 | 300 | 100 | 0 |  | 902 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 28 | 34 | 30 | 8 | 24 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 53 | 0 | 35 | 15 | 42 | 0 | 8 | 35 | 1244 | 220 |  | 38 | 6 | 100 | 70 | 0 |  | 570 | 30 | 150 | 1200 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 345 | 291 | 0 | 0 | 170 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 11 | 33 | 30 | 0 | 0 | 86 | 75 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 2 | 0 | 17 | 0 | 0 | 6 | 12 | 2 | 0 | 0 | 0 | 280 | 300 | 171 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 18 | 8 | 33 | 12 | 106 | 34 | 0 | 19 | 1 | 0 | 38 | 0 | 30 | 130 | 0 | 62 | 0 | 0 | 203 | 17 | 0 | 10 | 290 | 16 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 13 | 9 | 12 | 0 | 0 | 402 | 75 | 8 | 17 | 2 | 16 | 9 | 17 | 0 | 0 | 12 | 300 | 0 | 23 | 0 | 0 | 0 | 17 | 12 | 0 | 0 | 240 | 0 | 0 | 326 | 0 | 257 | 130 | 0 | 0 | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 640 | 180 | 0 | 0 | 2 | 33 | 0 | 0 | 0 | 407 | 15 | 150 | 915 | 82 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
[22 empty] | 299565 | [26 empty] | 399366 | [49 empty] | 299523 |  | 299563 |  | 399588 |  | 299281 | 299229 | 299524 |  | 399747 |  |  |  |  | 399575 | 399337 | 399589 | [8 empty] | 399245 |  |  | 399274 |  | 399223 |  | 399630 | [12 empty] | 599468 | [32 empty] | 599787 |  | 499268 | 599634 | 43212 |  |  | 499720 | 599730 | [18 empty] | 292.3904
| Minimum Generation |  | 8476 | 6:00 | [202 empty] | 122612192
| Highest Generation |  | 11977 | 18:00 | [202 empty] | 122.6122 |  |  |  |  | 2.8035
| Day Peak Generation |  | 10823 | 12:00 | [202 empty] | 19214538
| Evening Peak Generation |  | 11977 | 18:00 | [202 empty] | 19.2145 |  |  | 43327579 |  | 4.5158
| HVDC Max Flow |  | 901 | 4:00 | [202 empty] | 21.6553 |  |  |  |  | 0.10032
| HVDC EvPeak Flow |  | 775 | 18:00 | [200 empty] | 249654731 |  | 3.0182 |  | 75.7349
| Load factor L.F |  | 86.85% | [166 empty] | 1275.5 | [36 empty] | 249.6547

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-10-31
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-10-30 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 10823 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 8643
Evening Peak Generation : |  |  | 11977 | MW Hour : | 18:00 | Available Max Generation : |  | 14555
E.P. Demand (at gen end) : |  |  | 11977 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 12000
Maximum Generation : |  |  | 11977 | MW Hour : | 18:00 | Reserve(Generation end) |  | 2555
Total Gen. (MKWH) : |  |  | 249.6547 | System Load Factor : | 86.85% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 940 | MW at | 18:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-10-31
Actual : |  | 102.39 | Ft.(MSL) , | Rule curve : | 108.7 | Ft.( MSL )
Gas Consumed : |  | Total = | 920.49 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 121770106.038
: |  |  | Coal : | 533725029.67 | Oil : | 249947363.28 | Total : | 905442498.988
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4049.3685 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1109.504 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1553.2499 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1349.182 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1110.5832 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 825.5327 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 463.2298 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 385.5962 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 754.1689 |  |  | 0 | 0%
Total |  | 0 |  | 11600.4152 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
8:18 | 18:02 | Hasnabad 230/132kV S/S AUTO TR-1 LT Scheduled S/D Due to Due to Tan Delta test and Others test.
8:19 | 17:48 | Hasnabad 230/132kV S/S AUTO TR-1 HT Scheduled S/D Due to Due to Tan Delta test and Others test.
8:22 | 17:18 | Madaripur 132/33kV S/S T1-405T LT Scheduled S/D Due to Annual maintenance.
8:23 | 17:18 | Madaripur 132/33kV S/S T1-405T HT Scheduled S/D Due to Annual maintenance.
8:28 | 14:27 | Saidpur 132/33kV S/S TR-5 (434T) LT Scheduled S/D Due to Annual maintanance.
8:29 | 14:26 | Saidpur 132/33kV S/S TR-5 (434T) HT Scheduled S/D Due to Annual maintanance.
8:30 | 14:22 | Palashbari 132/33kV S/S TR4-434T LT Scheduled S/D Due to Annual Maintenance.
8:30 | 14:20 | Palashbari 132/33kV S/S TR4-434T HT Scheduled S/D Due to Annual Maintenance.
8:36 | 15:31 | Bhaluka-Mymensingh 132 kV Ckt-1 Scheduled S/D from Mymensingh 132/33kV end Due to Annual maintenance work and from
Bhaluka 132/33kV end Due to Annual maintenance.
8:39 | 16:57 | Madunaghat-TKCL 132kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end Due to For annual deadline checking.
8:59 | 16:48 | Goalpara 132/33kV S/S Bus 1 Scheduled S/D Due to Shutdown for Annual Maintenance works.
9:31 | 16:25 | Haripur-Siddirganj 132kV Ckt-2 Scheduled S/D from Haripur 230/132kV end Due to Annual maintenance.
9:32 | 16:25 | Haripur-Siddirganj 230kV Ckt-2 Scheduled S/D from Siddhirganj 132/33kV end Due to Annual Maintenance in Haripur Sub-station.
No load shed occurred . Load share by Haripur ckt-1.
9:50 | - | Kishoreganj 132/33kV S/S Tr-3 (424T) LT Scheduled S/D Due to Annual maintenance.
9:50 | 15:34 | Kishoreganj 132/33kV S/S Tr-3 (424T) HT Scheduled S/D Due to Annual Maintenance.
9:54 | 20:31 | Payra 400/132/33kV S/S 132/33 kV Transformer-04 LT Scheduled S/D Due to anual maintenance.
9:55 | 20:29 | Payra 400/132/33kV S/S 132/33 kV Transformer-04 HT Scheduled S/D Due to Anual maintenance.
10:02 | 16:44 | Daudkandi-Sonargaon 132 kV Ckt-1 Scheduled S/D from Daudkandi 132/33kV end Due to SCADA maintenance work at Sonargaon
substation and from Sonargaon 132/33kV end Due to SCADA integration purpose.
10:05 | 15:35 | Thakurgaon 132/33kV S/S RPC Scheduled S/D Due to ANNUAL MAINTENANCE.
10:33 | 17:26 | HVDC Bheramera- Ishwardi 230kV Ckt-3 Project Work S/D from Ishurdi 230/132kV end Due to Ruppur- Bogura project work.
10:35 | 17:39 | HVDC Bheramera-Ishwardi 230kV Ckt-4 Project Work S/D from Ishurdi 230/132kV end Due to Ruppur- Bogura project work.
10:39 | 12:09 | Naogaon 132/33kV S/S T-1 LT Scheduled S/D Due to T-1 132kv CT(YPH) HEAT SPOT MAINTENANCE.
10:40 | 12:08 | Naogaon 132/33kV S/S T-1 HT Scheduled S/D Due to T-1 132kv CT(YPH) HEAT SPOT MAINTENANCE.
10:40 | 16:28 | Cumilla(N)-Shahjibazar 230 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to Relay test.
10:42 | 16:27 | Bibiyana-Shahjibazar 230 kV Ckt-1 Scheduled S/D from Bibiana 400/230kV end Due to AM.
11:04 | 17:24 | HVDC Bheramera- Ishwardi 230kV Ckt-3 Project Work S/D from BIPTC end.
11:18 | 17:31 | Rampal 400/230kV S/S ICT-2 LT Project Work S/D Due to Oil Leakage Maintenance.
11:18 | 17:08 | Rampal 400/230kV S/S ICT-2 HT Project Work S/D Due to Oil Leakage Maintenance.
11:45 | 17:38 | HVDC Bheramera-Ishwardi 230kV Ckt-4 Project Work S/D from BIPTC end.
12:00 | - | Day peak generation: 10823 MW
- | 14:28 | Sholosohor 132/33kV S/S TRAFO-01 LT is restored.
- | 14:28 | Sholosohor 132/33kV S/S TRAFO-01 HT is restored.
14:59 | - | Rampura 230/132kV S/S Aux Transformer-02 LT Project Work S/D Due to 300/400 MVA new transformer commissioning and interin work.
14:59 | - | Rampura 230/132kV S/S Aux Transformer-02 HT Project Work S/D Due to 300/400 MVA new transformer commissioning and interin work.
- | 15:12 | Meghnaghat Summit-2 GT was sync. at 15:12 hrs.
15:16 | - | Rampura 230/132kV S/S 132 kV Busbar-2 Project Work S/D Due to 300/400 MVA new transformer commissioning and interin work.
- | 15:46 | Chauddagram-Feni 132 kV Ckt-1 is restored.
- | 16:02 | Sherpur 132/33kV S/S Transformer- 04 HT is restored.
- | 16:03 | Sherpur 132/33kV S/S Transformer- 04 LT is restored.
- | 16:05 | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) HT is restored.
- | 16:06 | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) LT is restored.
17:29 | 18:09 | Mymensingh 132/33kV S/S 50 MW Solar Plant Scheduled S/D Due to Multifunction meter replacement work.
19:27 | 20:42 | Bhangura 132/33kV S/S Tr-1(403T) LT Forced S/D. |  |  |  |  | 8.0MW load interrup.
19:33 | 20:41 | Bhangura 132/33kV S/S Tr-1(403T) HT Forced S/D. |  |  |  |  | 8.0MW load interrup.
7:10 | - | Payra 400/132/33kV S/S 132/33 kV Transformer-04 LT Scheduled S/D Due to Annual Maintenance work.
7:11 | - | Payra 400/132/33kV S/S 132/33 kV Transformer-04 HT Scheduled S/D Due to Annual Maintenance work.
7:22 | - | Chauddagram-Feni 132 kV Ckt-1 Scheduled S/D from Feni 132/33kV end Due to AMS-2023-24.
7:32 | - | Baroaulia-Khulshi 132 kV Ckt-1 Scheduled S/D from Baroaulia 132/33kV end Due to Loop and T clamp hange.
7:47 | - | Chauddagram-Feni 132 kV Ckt-1 Scheduled S/D from Chauddagram 132/33kV end Due to Annual maintenance.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-10-30 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 180 | 3794875
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 376 | 9345030 | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 322 | 7320000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 170 | 4929500 | GT-1 under S/D due to gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 8 | 124800 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 120 | 3417716 | GT-1 under S/D due to gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 95 | 828648 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 187056 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 45 | 317695 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 15 | 309672 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 9 | 92160 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 933173 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 102960 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 129960 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 82 | 488160 | Low demand.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 112376 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 122156 | Low demand.
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 30 | 732840 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 744900 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 26 | 686900 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 169440 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 108 | 607200 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 41 | 726768 | Low demand.
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 598080 | Fuel shortage
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 72960 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 260640 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 201949
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 509040 | Fuel shortage
| Meghnaghat Unique power |  | IPP | 586 | 0 | 200 | 4080454 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 38 | 106363 | On test.
| Dhaka area Total |  |  |  | 5422 | 2191 | 42053471
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 5 | 93043 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 133515
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 191040 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 160 | 4515767
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 202 | 4472178
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 342909 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 82 | 766968 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 388053 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 12 | 160680 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 242880 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 12 | 298224 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 0 | 248160
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 28199
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 220 | 1964618 | Low demand.
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 263789 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 349598 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 224640 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 377618 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 36 | 314472 | Engine problem
| SS Power I |  | SS Power | 1*612 | 612 | 415 | 9578181 | On test.
| Cox's Bazar Wind |  | IPP | 66 | 0 | 0 | 100320 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 257 | 5134545 | On test.
| Chattogram area Total |  |  |  | 3157 | 1546 | 30189397
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 179 | 4409000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 315 | 7204400 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 240 | 6189000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 240 | 5940900 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 0 | 0 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 755040
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 100 | 762763 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Under maint.
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 271200 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 424982 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 175500 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 146 | 3018240
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 24 | 639700 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 401371 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 12 | 294300 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 221160 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 87 | 883680 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 443160 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 94 | 702720 | Fuel shortage
| Cumilla Area Total |  |  |  | 2896 | 1608 | 32737116
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 34 | 1423680 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 436464 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13000
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 95 | 696000 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 90 | 1306800 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 288000
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 99120 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 244 | 4263064
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 338400 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 20 | 348480 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3622500
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 42 | 839088 | Engine problem
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 48536 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 55 | 1289088 | Gas shortage
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 0 | 0 | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 200 | 4993700 | Engine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 396000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 256800 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7191000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 404 | 9379000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 248040
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 300 | 7275000
| Sylhet Area Total |  |  |  | 2427 | 1519 | 36225632
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 775 | 21655272
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 19 | 36480 | Low demand.
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 6912 | Reserve
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 1500 | Reserve
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 137760 | Low demand.
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 32 | 54144 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 550080
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | TG Test
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 407 | 8567273 | Engine problem
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 1250 | 31009421
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Transformer O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 22 | 426300 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 130 | 2679000 | ST Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 960 | 19847000
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 222 | 5158691
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 16 | 40800 | Transformer O/L
| Barisal 307 MW |  | IPP | 307*1 | 307 | 150 | 3687300 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1500 | 31839091
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 20215 | Low demand.
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 39 | 133931 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 145 | 3626927 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 161 | 4984727 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 71154 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 0 | 197964 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 10 | 29434 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 32 | 91248 | Low demand.
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 49 | 482304 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 55 | 444576 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 31140
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1217 | 24777042
| Rajshahi Area Total |  |  |  | 3631 | 1754 | 34890662
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4143600 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 110 | 398947
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 42602
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 85 | 346752 | Low demand.
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 236416
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1278560
| Rangpur Area Total |  |  |  | 950 | 365 | 6446877
| Total |  |  |  | 24599 | 11977 | 249654731
| Eastern Grid Total |  |  |  | 14516 | 7108 | 145468680
| Western Grid Total |  |  |  | 10083 | 4869 | 104186051
| National Grid Total |  |  |  | 24599 | 11977 | 249654731
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-10-30
| (a) ENTIRE EASTERN GRID : |  | 8203.39 | MW | (b) ENTIRE WESTERN GRID : |  | 3567 | MW
| i) Dhaka area |  | 4567.89 | MW | i) Khulna area |  | 1350.7 | MW
| ii) Chittagong area |  | 1198.5 | MW | ii) Rajshahi area |  | 1128.8 | MW
| iii) Comilla area |  | 1057 | MW | iii) Barisal area |  | 326.5 | MW
| iv) Mymensingh area |  | 930 | MW | iv) Rangpur area |  | 761 | MW
| v) Sylhet area |  | 450 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11770.39 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 27 | 18:00 | Kamrangirchar | 51.3 | 13:00 | Narinda | 71 | 12:00 | Sherpur | 116 | 18:00
2 | AKSML | 107.8 | 12:00 | Chowmuhani | 164 | 19:00 | Kaptai | N/A | N/A | Narshingdi | 160 | 18:30 | Shikalbaha | 26 | 18:30
3 | Aftabnagar | 32 | 13:00 | Chuadanga | 87 | 18:00 | Kazla | 100 | 13:00 | Natore | 109 | 18:00 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 84 | 13:00 | Coxsbazar | 103 | 21:00 | Keranigonj | 72 | 18:30 | Nawabganj | 33 | 21:00 | Shitalakhya | 98.6 | 16:00
5 | Agrabad | 68 | 18:00 | Cumilla(N) | 122 | 18:00 | Khagrachori | 22 | 18:00 | Netrakona | 97 | 18:00 | Sholosohor | 44 | 16:00
6 | Amnura | 43 | 18:30 | Cumilla(S) | 146 | 18:00 | Khulna | 86 | 19:00 | New | 74.6 | 12:00 | Shyampur | 122 | 00:00
7 | Ashuganj | 62 | 00:00 | Daudkandi | 124 | 20:00 | Khulshi | 170 | 18:30 | Niamatpur | 60 | 13:00 | Siddhirganj | 110 | 16:00
8 | BIPTC | N/A | N/A | Dhaka | 22 | 11:00 | Kishoreganj | 116 | 19:00 | Noapara | 39 | 18:00 | Sirajganj | 94 | 18:00
9 | BSRM | 184 | 18:00 | Dhamrai | 118 | 18:30 | Kodda | 268 | 10:00 | PHP | 3 | 09:00 | Sonargaon | 94 | 16:00
10 | Bagerhat | 70 | 18:00 | Dhanmondi | 117 | 13:00 | Kulaura | 42 | 18:00 | Pabna | 97 | 19:30 | Sreemongol | 57 | 18:30
11 | Bakulia | 90 | 18:30 | Dohazari | 70 | 20:00 | Kurigram | 58 | 18:00 | Palashbari | 100 | 18:00 | Sreepur | 60 | 18:30
12 | Banani | 46 | 13:00 | Faridpur | 117 | 18:00 | Kushtia | 108 | 18:00 | Panchagarh | 47 | 18:00 | Srinagar | 34.6 | 20:00
13 | Bangabhaban | 12 | 10:00 | Fatullah | 62 | 12:00 | Lalbag | 89 | 18:00 | Patuakhali | 73 | 20:00 | Sunamganj | 45 | 18:00
14 | Barapukuria | 52 | 18:00 | Fenchuganj | 34 | 18:00 | Lalmonirhat | 39 | 18:00 | Payra | 15 | 18:00 | Sylhet | 12 | 00:00
15 | Barguna | 16 | 18:00 | Feni | 98 | 18:00 | MI_Cement | 19.7 | 12:00 | Postogola | 52 | 13:00 | Sylhet-132 | 132 | 18:00
16 | Barishal | 84 | 13:00 | GPH | 98 | 13:00 | Madanganj | 37 | 00:00 | Purbachal | 19 | 12:00 | TK | 23 | 00:00
17 | Barishal-230 | 70 | 18:00 | Ghorashal | 53 | 18:00 | Madaripur | 70 | 18:00 | Purbasadipur | 96 | 18:30 | Tangail | 180 | 18:30
18 | Baroaulia | 62 | 11:00 | Goalpara | 30 | 13:00 | Madartek | 53.63 | 21:00 | Rahim | 33 | 01:00 | Thakurgaon | 71 | 18:00
19 | Baroirhat | 41 | 22:00 | Gollamari | 38 | 18:00 | Madunaghat | 43 | 18:00 | Rajbari | 54 | 18:00 | Tongi | 104 | 12:00
20 | Bashundhara | 147 | 13:00 | Gopalganj | 81.8 | 18:30 | Magura | 55 | 18:00 | Rajendrapur | 94 | 18:30 | Ullon | 35 | 21:00
21 | BashundharaCement | 7 | 07:00 | Gulshan | 106 | 12:00 | Mahasthangarh | 56 | 18:00 | Rajshahi | 115 | 18:00 | Uttara | 72 | 16:00
22 | Beanibazar | 56 | 18:00 | Halishahar | 118.5 | 15:00 | Manikganj | 91 | 18:00 | Rajshahi-230 | 28 | 19:00 | UttaraNew | 48 | 18:00
23 | Benapole | 48 | 18:00 | HaripurSBU | 156 | 13:00 | Maniknagar | 88 | 12:00 | Ramganj | 84 | 18:00 | Zigatola | 79 | 13:00
24 | Bhaluka | 144 | 19:00 | Hasnabad | 74 | 15:00 | Matarbari | 8 | 19:00 | Rampur | 28 | 18:30
25 | Bhandaria | 38 | 22:00 | Hathazari | 59 | 18:30 | Matuail | 70 | 12:00 | Rangamati | 16 | 18:00
26 | Bhangura | 26 | 18:00 | Ishurdi | 62 | 18:00 | Millgate | 90 | 15:00 | Rangpur | 119 | 18:30
27 | Bheramara(GK) | 49 | 18:00 | Jaldhaka | 58 | 18:00 | Mirpur | 115 | 18:30 | Ruppur | 6 | 11:00
28 | Bhulta | 233 | 19:00 | Jamalpur | 129 | 18:00 | Mirsorai | 2 | 00:00 | SSM | 1 | 21:00
29 | Bog-Sherpur | 50 | 18:00 | Jashore | 111 | 18:00 | Mirzapur | 0 | 00:00 | Saidpur | 88 | 18:00
30 | Bogura | 130 | 18:30 | Jhenaidah | 101 | 18:00 | Mithapukur | 36 | 08:00 | Satkhira | 93 | 18:00
31 | Borhanuddin | 40 | 19:30 | Joydebpur | 165 | 18:30 | Modern | 0 | 00:00 | Satmasjid | 96 | 19:00
32 | Brahmanbaria | 135 | 19:00 | Joypurhat | 43 | 18:30 | Mogbazar | 99.8 | 15:00 | Savar | 166 | 17:00
33 | Cantonment | 123 | 18:00 | Juldah | 22 | 14:00 | Mongla | 30 | 01:00 | SevenRings | 5.16 | 17:00
34 | Chandpur | 54 | 20:00 | KSRM | 25 | 14:00 | Motijheel | 33 | 11:00 | ShahCement | 27 | 03:00
35 | Chandraghona | 26 | 18:00 | Kabirpur | 250 | 18:30 | Munshiganj | 79 | 18:00 | Shahjadpur | 78 | 18:00
36 | Chapai | 55 | 18:30 | Kachua | 56 | 18:30 | Mymensingh | 168 | 19:00 | Shahjibazar | 102 | 18:00
37 | Charsaidpur | 28 | 12:00 | Kallyanpur | 96 | 18:00 | Naogaon | 106 | 18:30 | Shahmirpur | 41 | 03:00
38 | Chauddagram | 48 | 18:00 | Kalurghat | 36 | 15:00 | Narail | 43 | 18:00 | Shariatpur | 54 | 18:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-10-30 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 400 | 04:00 | 387 | 12:00 | Gopalganj | 409 | 05:00 | 397 | 18:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 385 | 18:30 | 373 | 12:00
| Bhulta | 400 | 03:00 | 390 | 10:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 408 | 20:00 | 398 | 15:00 | Payra | 416 | 06:00 | 409 | 18:00
| BIPTC | 400 | 04:00 | 393 | 12:00 | Rahanpur | 414 | 06:00 | 400 | 11:00
| Bogura | N/A | N/A | N/A | N/A | Rampal | 410 | 04:00 | 399 | 18:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 236 | 04:00 | 226 | 11:00 | Hasnabad | 234 | 04:00 | 226 | 12:00
| AKSML | 236 | 18:00 | 228 | 04:00 | Hathazari | 236 | 19:30 | 226 | 09:00
| Aminbazar | 236 | 01:00 | 228 | 12:00 | Ishurdi | 235 | 03:00 | 220 | 12:00
| Ashuganj | 236 | 06:00 | 229 | 11:00 | Jhenaidah | 230 | 04:00 | 217 | 12:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 236 | 04:00 | 228 | 12:00
| Baghabari | 230 | 05:00 | 218 | 12:00 | Keranigonj | 234 | 03:00 | 226 | 11:00
| Barapukuria | 223 | 18:30 | 217 | 11:00 | Khulna(S) | 235 | 04:00 | 222 | 18:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 237 | 03:00 | 232 | 12:00 | Maniknagar | 233 | 02:00 | 225 | 11:00
| Bheramara | 235 | 17:00 | 223 | 12:00 | Meghnaghat | 241 | 01:00 | 236 | 15:00
| Bhulta | 238 | 04:00 | 229 | 10:00 | Mirsorai | 233 | 00:00 | 228 | 14:00
| Bibiana | 234 | 02:00 | 228 | 15:00 | Rajshahi | 233 | 03:00 | 221 | 10:00
| BIPTC | 236 | 17:00 | 223 | 12:00 | Rampal | 234 | 04:00 | 226 | 14:00
| Bogura | 235 | 06:00 | 223 | 11:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 241 | 02:00 | 237 | 10:00 | Rampura | 235 | 02:00 | 227 | 10:00
| BSRM | 234 | 20:00 | 228 | 11:00 | Shikalbaha | 235 | 22:00 | 226 | 11:00
| Cumilla(N) | 233 | 18:30 | 226 | 11:00 | Shyampur | 235 | 04:00 | 227 | 11:00
| Fenchuganj | 237 | 08:00 | 233 | 13:00 | Siddhirganj | 236 | 03:00 | 228 | 11:00
| Ghorashal | 235 | 00:00 | 232 | 10:00 | Sirajgonj | 241 | 04:00 | 231 | 12:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 235 | 04:00 | 227 | 12:00
| GPH | 233 | 19:00 | 227 | 15:00 | Tongi | 233 | 19:30 | 223 | 12:00
| Haripur | 234 | 03:00 | 227 | 11:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 137 | 04:00 | 130 | 11:00 | Lalbag | 134 | 03:00 | 128 | 11:00
| Agargaon | 136 | 03:00 | 130 | 11:00 | Lalmonirhat | 133 | 05:00 | 124 | 12:00
| Agrabad | 135 | 19:00 | 129 | 11:00 | Madanganj | 135 | 20:00 | 127 | 10:00
| AKS | 134 | 21:00 | 128 | 10:00 | Madaripur | 131 | 00:00 | 128 | 13:00
| Aminbazar | 140 | 01:00 | 134 | 12:00 | Madartek | 137 | 04:00 | 129 | 11:00
| Amnura | 137 | 04:00 | 127 | 11:00 | Madunaghat | 136 | 19:00 | 131 | 10:00
| Ashuganj | 140 | 00:00 | 138 | 15:00 | Magura | 141 | 04:00 | 130 | 18:00
| Bagerhat | 135 | 06:00 | 125 | 18:00 | Mahasthangarh | 137 | 04:00 | 128 | 12:00
| Bakulia | 137 | 18:30 | 130 | 11:00 | Manikganj | 134 | 18:30 | 126 | 11:00
| Banani | 138 | 03:00 | 132 | 10:00 | Maniknagar | 137 | 05:00 | 129 | 12:00
| Bangabhaban | 136 | 02:00 | 129 | 12:00 | Matarbari | 130 | 17:00 | 125 | 15:00
| Barapukuria | 138 | 18:30 | 132 | 12:00 | Matuail | 133 | 06:00 | 128 | 10:00
| Barguna | 139 | 06:00 | 135 | 18:00 | Millgate | 138 | 20:00 | 131 | 10:00
| Barishal | 136 | 04:00 | 132 | 12:00 | Mirpur | 139 | 04:00 | 132 | 12:00
| Barishal-230 | 136 | 04:00 | 132 | 12:00 | Mirzapur | 135 | 18:00 | 128 | 12:00
| Baroaulia | 137 | 21:00 | 130 | 11:00 | Mithapukur | 136 | 04:00 | 126 | 12:00
| Baroirhat | 130 | 22:00 | 125 | 10:00 | MI_Cement | 135 | 05:00 | 129 | 10:00
| Bashundhara | 139 | 03:00 | 130 | 11:00 | Modern | 135 | 00:00 | 130 | 09:00
| BashundharaCement | 135 | 20:00 | 127 | 10:00 | Mogbazar | 137 | 02:00 | 130 | 11:00
| Beanibazar | 128 | 03:00 | 124 | 18:00 | Mongla | 134 | 02:00 | 127 | 12:00
| Benapole | 138 | 03:00 | 126 | 18:00 | Motijheel | 136 | 02:00 | 129 | 12:00
| Bhaluka | 127 | 05:00 | 122 | 11:00 | Munshiganj | 134 | 03:00 | 129 | 11:00
| Bhandaria | 137 | 07:00 | 132 | 18:00 | Mymensingh | 137 | 20:00 | 121 | 13:00
| Bhangura | 141 | 04:00 | 132 | 12:00 | Naogaon | 134 | 06:00 | 123 | 11:00
| Bheramara | 136 | 03:00 | 128 | 12:00 | Narail | 139 | 04:00 | 129 | 18:00
| Bheramara(GK) | 136 | 06:00 | 128 | 10:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 124 | 05:00 | 118 | 10:00 | Narshingdi | 128 | 05:00 | 120 | 12:00
| Bog-Sherpur | 138 | 02:00 | 130 | 11:00 | Natore | 135 | 06:00 | 128 | 12:00
| Bogura | 138 | 05:00 | 130 | 11:00 | Nawabganj | 134 | 04:00 | 128 | 11:00
| Bogura-230 | 138 | 06:00 | 129 | 11:00 | Netrakona | 136 | 19:00 | 125 | 01:00
| Brahmanbaria | 127 | 07:00 | 121 | 19:30 | New | 139 | 18:30 | 131 | 12:00
| Cantonment | 136 | 04:00 | 129 | 11:00 | Niamatpur | 133 | 02:00 | 121 | 11:00
| Chandpur | 134 | 17:00 | 121 | 10:00 | Noapara | 137 | 05:00 | 128 | 18:00
| Chandraghona | 137 | 20:00 | 131 | 10:00 | Pabna | 138 | 04:00 | 128 | 12:00
| Chapai | 133 | 04:00 | 128 | 12:00 | Palashbari | 132 | 18:30 | 126 | 12:00
| Charsaidpur | 135 | 20:00 | 129 | 12:00 | Panchagarh | 134 | 04:00 | 117 | 12:00
| Chauddagram | 134 | 20:00 | 125 | 10:00 | Patuakhali | 138 | 06:00 | 134 | 08:00
| Chhatak | 129 | 05:00 | 125 | 18:00 | Payra | 140 | 01:00 | 138 | 13:00
| Chowmuhani | 131 | 22:00 | 119 | 10:00 | PHP | 132 | 17:00 | 124 | 10:00
| Chuadanga | 138 | 06:00 | 126 | 18:00 | Postogola | 137 | 20:00 | 131 | 10:00
| Coxsbazar | 128 | 13:00 | 124 | 00:00 | Purbachal | 138 | 01:00 | 129 | 12:00
| Cumilla(N) | 136 | 17:00 | 129 | 10:00 | Purbasadipur | 133 | 05:00 | 120 | 12:00
| Cumilla(S) | 135 | 20:00 | 125 | 18:00 | Rahanpur | 135 | 06:00 | 132 | 11:00
| Daudkandi | 131 | 20:00 | 123 | 10:00 | Rahim | 133 | 03:00 | 128 | 12:00
| Dhaka | 136 | 00:00 | 130 | 12:00 | Rajbari | 132 | 03:00 | 125 | 18:00
| Dhamrai | 134 | 05:00 | 127 | 12:00 | Rajendrapur | 136 | 19:00 | 123 | 15:00
| Dhanmondi | 133 | 03:00 | 127 | 10:00 | Rajshahi | 136 | 04:00 | 128 | 12:00
| Dohazari | 134 | 21:00 | 128 | 11:00 | Rajshahi-230 | 136 | 03:00 | 126 | 11:00
| Faridpur | 132 | 05:00 | 126 | 12:00 | Ramganj | 132 | 18:30 | 118 | 10:00
| Fatullah | 137 | 20:00 | 131 | 11:00 | Rampur | 136 | 18:30 | 130 | 11:00
| Fenchuganj | 133 | 07:00 | 130 | 18:00 | Rampura | 136 | 02:00 | 130 | 10:00
| Feni | 132 | 19:00 | 125 | 10:00 | Rangamati | 136 | 18:30 | 130 | 10:00
| Ghorashal | 140 | 06:00 | 136 | 00:00 | Rangpur | 133 | 02:00 | 125 | 11:00
| Goalpara | 139 | 04:00 | 130 | 12:00 | Ruppur | 138 | 06:00 | 130 | 10:00
| Gollamari | 137 | 03:00 | 130 | 11:00 | Saidpur | 135 | 06:00 | 125 | 12:00
| Gopalganj | 133 | 03:00 | 127 | 12:00 | Satkhira | 136 | 05:00 | 126 | 18:00
| Gopalganj-400 | 131 | 02:00 | 120 | 00:00 | Satmasjid | 136 | 04:00 | 129 | 12:00
| Gulshan | 136 | 03:00 | 129 | 12:00 | Savar | 138 | 04:00 | 132 | 12:00
| Halishahar | 136 | 22:00 | 129 | 10:00 | SevenRings | 141 | 20:00 | 138 | 14:00
| Haripur | 133 | 03:00 | 128 | 12:00 | ShahCement | 135 | 20:00 | 129 | 12:00
| HaripurSBU | 133 | 03:00 | 128 | 12:00 | Shahjadpur | 143 | 04:00 | 138 | 12:00
| Hasnabad | 136 | 01:00 | 131 | 13:00 | Shahjibazar | 126 | 06:00 | 122 | 00:00
| Hathazari | 138 | 19:30 | 131 | 09:00 | Shahmirpur | 135 | 19:30 | 129 | 11:00
| Ishurdi | 139 | 03:00 | 130 | 12:00 | Shariatpur | 132 | 02:00 | 127 | 15:00
| Jaldhaka | 133 | 06:00 | 123 | 12:00 | Sherpur | 137 | 20:00 | 120 | 01:00
| Jamalpur | 139 | 19:30 | 120 | 02:00 | Shikalbaha | 125 | 18:30 | 120 | 09:00
| Jashore | 135 | 03:00 | 127 | 12:00 | Shikalbaha-230 | 137 | 22:00 | 132 | 05:00
| Jhenaidah | 140 | 06:00 | 131 | 12:00 | Shitalakhya | 135 | 05:00 | 129 | 10:00
| Jhenaidah-230 | 141 | 03:00 | 131 | 18:00 | Sholosohor | 136 | 21:00 | 130 | 11:00
| Joydebpur | 139 | 18:30 | 132 | 10:00 | Shyampur | 137 | 20:00 | 130 | 09:00
| Joypurhat | 134 | 05:00 | 123 | 12:00 | Shyampur-230 | 137 | 04:00 | 132 | 10:00
| Juldah | 135 | 00:00 | 131 | 09:00 | Siddhirganj | 133 | 04:00 | 128 | 10:00
| Kabirpur | 137 | 03:00 | 127 | 15:00 | Sirajganj | 138 | 05:00 | 128 | 11:00
| Kachua | 134 | 17:00 | 122 | 10:00 | Sonargaon | 131 | 08:00 | 127 | 16:00
| Kaliakoir | 137 | 19:30 | 130 | 12:00 | Sreemongol | 129 | 08:00 | 124 | 15:00
| Kallyanpur | 140 | 06:00 | 134 | 11:00 | Sreepur | 129 | 03:00 | 124 | 12:00
| Kalurghat | 136 | 18:30 | 131 | 10:00 | Srinagar | 134 | 04:00 | 129 | 12:00
| Kamrangirchar | 138 | 01:00 | 129 | 11:00 | SSM | 140 | 19:30 | 132 | 11:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 127 | 06:00 | 121 | 18:00
| Kazla | 135 | 01:00 | 128 | 13:00 | Sylhet | 129 | 00:00 | 128 | 11:00
| Keranigonj | 139 | 11:00 | 129 | 12:00 | Sylhet-132 | 130 | 04:00 | 128 | 12:00
| Khagrachori | 136 | 21:00 | 131 | 11:00 | Tangail | 134 | 20:00 | 127 | 12:00
| Khulna | 137 | 04:00 | 129 | 12:00 | Thakurgaon | 134 | 18:30 | 117 | 12:00
| Khulna(S) | 138 | 03:00 | 130 | 18:00 | TK | 137 | 21:00 | 132 | 09:00
| Khulshi | 135 | 21:00 | 128 | 10:00 | Tongi | 140 | 19:30 | 133 | 12:00
| Kishoreganj | 135 | 06:00 | 129 | 14:00 | Ullon | 133 | 02:00 | 128 | 11:00
| Kodda | 137 | 18:30 | 124 | 12:00 | Uttara | 140 | 04:00 | 133 | 11:00
| KSRM | 137 | 18:30 | 131 | 10:00 | UttaraNew | 140 | 03:00 | 132 | 14:00
| Kulaura | 132 | 08:00 | 128 | 18:00 | Zigatola | 134 | 03:00 | 128 | 12:00
| Kurigram | 133 | 04:00 | 124 | 12:00
| Kushtia | 137 | 01:00 | 129 | 12:00

## L-Curve
Date | 2023-10-30
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1170 | 6074 | 4339 | 10413 |  |  |  | QF-LDC-11
0:30 | 1140 | 5891.5 | 4172.5 | 10064 | Date: | 2023-10-30
1:00 | 1110 | 5709 | 4006 | 9715
1:30 | 1100 | 5598.5 | 3898.5 | 9497
2:00 | 1090 | 5488 | 3791 | 9279
2:30 | 1100 | 5413.5 | 3706.5 | 9120 | [5 empty] | Gen. at Eve. Peak | 11977 | 11977 MW (18:00 )
3:00 | 1110 | 5339 | 3622 | 8961 | [6 empty] | 18:00
3:30 | 1105 | 5228.5 | 3602 | 8830.5 | [5 empty] | Gen. at Day Peak | 10823 | 10823 MW (12:00 )
4:00 | 1100 | 5118 | 3582 | 8700 | [6 empty] | 12:00
4:30 | 1127 | 5029 | 3579.5 | 8608.5 | [5 empty] | Highest Generation | 11977
5:00 | 1154 | 4940 | 3577 | 8517 | [6 empty] | 18:00
5:30 | 1147 | 4922 | 3574.5 | 8496.5
6:00 | 1140 | 4904 | 3572 | 8476
6:30 | 1065 | 4993 | 3665 | 8658
7:00 | 990 | 5082 | 3758 | 8840
7:30 | 1165 | 5112 | 3930 | 9042
8:00 | 1340 | 5142 | 4102 | 9244
8:30 | 1390 | 5201 | 4173 | 9374
9:00 | 1440 | 5260 | 4244 | 9504
9:30 | 1425 | 5519.5 | 4151.5 | 9671
10:00 | 1410 | 5779 | 4059 | 9838
10:30 | 1345 | 5915 | 4118 | 10033
11:00 | 1280 | 6051 | 4177 | 10228
11:30 | 1235 | 6276 | 4249.5 | 10525.5
12:00 | 1190 | 6501 | 4322 | 10823
12:30 | 1175 | 6561.5 | 4369.5 | 10931
13:00 | 1160 | 6622 | 4417 | 11039
13:30 | 1135 | 6535.5 | 4391 | 10926.5
14:00 | 1110 | 6449 | 4365 | 10814
14:30 | 1198 | 6450 | 4408 | 10858
15:00 | 1286 | 6451 | 4451 | 10902
15:30 | 1252 | 6396 | 4402 | 10798
16:00 | 1218 | 6341 | 4353 | 10694
16:30 | 1217 | 6339.5 | 4314 | 10653.5
17:00 | 1216 | 6338 | 4275 | 10613
17:30 | 1078 | 6723 | 4572 | 11295
18:00 | 940 | 7108 | 4869 | 11977
18:30 | 965 | 7064.5 | 4899.5 | 11964
19:00 | 990 | 7021 | 4930 | 11951
19:30 | 1020 | 6964 | 4754 | 11718
20:00 | 992 | 6914 | 4777 | 11691 |  |  |  | Executive Engineer
20:30 | 1039 | 6769.5 | 4755 | 11524.5 |  |  |  | Network Operation Division
21:00 | 1086 | 6625 | 4733 | 11358
21:30 | 1093 | 6555 | 4614.5 | 11169.5
22:00 | 1100 | 6485 | 4496 | 10981 |  |  |  |  | Page 6 of 7
22:30 | 1110 | 6365.5 | 4450.5 | 10816
23:00 | 1120 | 6246 | 4405 | 10651
23:30 | 1145 | 6160 | 4372 | 10532
24:00 | 1170 | 6074 | 4339 | 10413
11977 MW (18:00 )
10823 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-10-30 |  | Energy |  | 249654731
QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3350 | 899 | 1888 | 0 | 443 | 3462 | 162 | 0 | 83 | 120 | 0 | 6 | 0
0:30 | 3390.5 | 899.5 | 1827 | 0 | 337.5 | 3223.5 | 184 | 0 | 75 | 121 | 0 | 6 | 0 |  | Date: | 43767
1:00 | 3431 | 900 | 1766 | 0 | 232 | 2985 | 206 | 0 | 67 | 122 | 0 | 6 | 0
1:30 | 3413 | 899.5 | 1717.5 | 0 | 195 | 2898 | 206 | 0 | 42 | 120 | 0 | 6 | 0 | [7 empty] | Total Energy | 249.6547 | 249.6547 | Total Energy Gen 249.655 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 249.655 MKWHr
2:00 | 3395 | 899 | 1669 | 0 | 158 | 2811 | 206 | 0 | 17 | 118 | 0 | 6 | 0 | [7 empty] | Energy not Served | 0 | 0
2:30 | 3346.5 | 899 | 1631.5 | 0 | 145 | 2752 | 206 | 0 | 17 | 117 | 0 | 6 | 0 | [7 empty] | Energy Requirement | 249.6547 | 249.6547
3:00 | 3298 | 899 | 1594 | 0 | 132 | 2693 | 206 | 0 | 17 | 116 | 0 | 6 | 0
3:30 | 3267.5 | 900 | 1580 | 0 | 82.5 | 2658 | 206 | 0 | 17 | 113 | 0 | 6.5 | 0
4:00 | 3237 | 901 | 1566 | 0 | 33 | 2623 | 206 | 0 | 17 | 110 | 0 | 7 | 0
4:30 | 3180 | 900.5 | 1607 | 0 | 25 | 2564 | 206 | 0 | 8.5 | 110 | 0 | 7.5 | 0
5:00 | 3123 | 900 | 1648 | 0 | 17 | 2505 | 206 | 0 | 0 | 110 | 0 | 8 | 0
5:30 | 3103.5 | 900 | 1649 | 0 | 17 | 2507 | 206 | 0 | 0 | 107 | 0 | 7 | 0
6:00 | 3084 | 900 | 1650 | 0 | 17 | 2509 | 206 | 0 | 0 | 104 | 0 | 6 | 0
6:30 | 3104 | 900 | 1734.5 | 0 | 26.5 | 2558 | 206 | 0 | 0 | 101 | 22 | 6 | 0 | [6 empty] | Coal
7:00 | 3124 | 900 | 1819 | 0 | 36 | 2607 | 206 | 0 | 0 | 98 | 44 | 6 | 0
7:30 | 3173 | 899.5 | 1735 | 0 | 80 | 2729 | 206 | 0 | 8 | 101 | 106 | 4.5 | 0 | [5 empty] | Oil
8:00 | 3222 | 899 | 1651 | 0 | 124 | 2851 | 206 | 0 | 16 | 104 | 168 | 3 | 0
8:30 | 3180.5 | 899.5 | 1684.5 | 0 | 184.5 | 2885.5 | 186.5 | 0 | 16 | 105 | 229 | 3 | 0
9:00 | 3139 | 900 | 1718 | 0 | 245 | 2920 | 167 | 0 | 16 | 106 | 290 | 3 | 0
9:30 | 3118 | 899.5 | 1907.5 | 0 | 270 | 2856.5 | 167 | 0 | 16 | 114 | 319 | 3.5 | 0
10:00 | 3097 | 899 | 2097 | 0 | 295 | 2793 | 167 | 0 | 16 | 122 | 348 | 4 | 0
10:30 | 3151 | 899 | 2086.5 | 0 | 376 | 2840 | 167.5 | 0 | 17 | 126 | 367.5 | 2.5 | 0
11:00 | 3205 | 899 | 2076 | 0 | 457 | 2887 | 168 | 0 | 18 | 130 | 387 | 1 | 0
11:30 | 3220 | 900 | 2062 | 0 | 651.5 | 2915.5 | 188 | 0 | 46.5 | 128.5 | 411 | 2.5 | 0
12:00 | 3235 | 901 | 2048 | 0 | 846 | 2944 | 208 | 0 | 75 | 127 | 435 | 4 | 0
12:30 | 3233.5 | 900 | 2059.5 | 0 | 913 | 2981.5 | 207.5 | 0 | 100.5 | 127.5 | 403 | 5 | 0
13:00 | 3232 | 899 | 2071 | 0 | 980 | 3019 | 207 | 0 | 126 | 128 | 371 | 6 | 0
13:30 | 3232 | 899 | 2071 | 0 | 980 | 3019 | 207 | 0 | 126 | 128 | 371 | 6 | 0
14:00 | 3232 | 899 | 2071 | 0 | 980 | 3019 | 207 | 0 | 126 | 128 | 371 | 6 | 0
14:30 | 3236.5 | 899 | 1978 | 0 | 1004 | 3081.5 | 206 | 0 | 128.5 | 129 | 303 | 5 | 0
15:00 | 3241 | 899 | 1885 | 0 | 1028 | 3144 | 205 | 0 | 131 | 130 | 235 | 4 | 0
15:30 | 3245.5 | 898.5 | 1837.5 | 0 | 1036 | 3134 | 205 | 0 | 130.5 | 135 | 172.5 | 3.5 | 0
16:00 | 3250 | 898 | 1790 | 0 | 1044 | 3124 | 205 | 0 | 130 | 140 | 110 | 3 | 0
16:30 | 3235 | 898 | 1754 | 0 | 1128 | 3126.5 | 182 | 0 | 130 | 137 | 60 | 3 | 0
17:00 | 3220 | 898 | 1718 | 0 | 1212 | 3129 | 159 | 0 | 130 | 134 | 10 | 3 | 0
17:30 | 3236 | 836.5 | 1764.5 | 0 | 1563 | 3352.5 | 159.5 | 0 | 236.5 | 140 | 5 | 1.5 | 0
18:00 | 3252 | 775 | 1811 | 0 | 1914 | 3576 | 160 | 0 | 343 | 146 | 0 | 0 | 0
18:30 | 3259 | 774.5 | 1771.5 | 0 | 1854 | 3673 | 160.5 | 0 | 328.5 | 142 | 0 | 1 | 0
19:00 | 3266 | 774 | 1732 | 0 | 1794 | 3770 | 161 | 0 | 314 | 138 | 0 | 2 | 0
19:30 | 3302 | 832 | 1818 | 0 | 1568 | 3670 | 161 | 0 | 228 | 136 | 0 | 3 | 0
20:00 | 3284 | 832 | 1786 | 0 | 1584 | 3683 | 161 | 0 | 228 | 130 | 0 | 3 | 0
20:30 | 3313 | 865 | 1816 | 0 | 1362 | 3677.5 | 161.5 | 0 | 196 | 131 | 0 | 2.5 | 0
21:00 | 3342 | 898 | 1846 | 0 | 1140 | 3672 | 162 | 0 | 164 | 132 | 0 | 2 | 0
21:30 | 3345 | 898 | 1846 | 0 | 1031 | 3606 | 162 | 0 | 148 | 130 | 0 | 3.5 | 0
22:00 | 3348 | 898 | 1846 | 0 | 922 | 3540 | 162 | 0 | 132 | 128 | 0 | 5 | 0
22:30 | 3352 | 898.5 | 1845.5 | 0 | 784.5 | 3524 | 162 | 0 | 116 | 128 | 0 | 5.5 | 0
23:00 | 3356 | 899 | 1845 | 0 | 647 | 3508 | 162 | 0 | 100 | 128 | 0 | 6 | 0
23:30 | 3353 | 899 | 1866.5 | 0 | 545 | 3485 | 162 | 0 | 91.5 | 124 | 0 | 6 | 0 |  | Max Temp. in Dhaka |  | 31.6°C
24:00 | 3350 | 899 | 1888 | 0 | 443 | 3462 | 162 | 0 | 83 | 120 | 0 | 6 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 249.655 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 249.655 MKWHr
Note on W13: Author:

## Generation
g | 2023-10-30
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 132 | 132 | 133 | 133 | 132 | 131 | 130 | 130 | 84 | 85 |  | 86 | 86 | 86 | 87 | 87 | 87 | 87 | 2863767
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 35 | 35 | 35 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1652000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 5 |  | 17 | 17 | 17 | 17 | 17 | 8 | 8 | 93043
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 2 | 11 | 15 | 12 | 19 | 20 | 18 | 7 | 11 | 6 | 0 | [9 empty] | 133515
6 | Sikalbaha 225MW CCPP (Gas) | 174 | 174 | 174 | 174 | 175 | 174 | 175 | 176 | 177 | 177 | 204 | 202 | 202 | 203 | 202 | 202 | 202 | 202 |  | 194 | 196 | 195 | 195 | 191 | 192 | 189 | 4472178
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 17 | 17 | 17 | 0 |  |  | 0 | 0 | 0 | 2 | 17 | 17 | 17 | 17 | 17 | 17 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 17 | 388053
12 | Hathazari 100 MW peaking PP | 50 | 0 | [5 empty] | 0 | 0 |  |  | 6 | 57 | 59 | 62 | 64 | 64 | 82 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 766968
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 0 |  |  |  |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 342909
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 214 | 213 | 210 | 170 | 36 | 0 | [19 empty] | 0 | 933173
18 | Kodda 300 MW PP Unit-2 (Summit) | [10 empty] | 3 | 80 | 76 | 48 | 48 | 30 | 30 | 108 |  | 60 | 15 | 15 | 15 | 0 |  | 0 | 607200
19 | Ashuganj 195 MW PP (APSCL-United) | [25 empty] | 0 | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 200 | 130 | 130 | 160 | 160 | 160 | 163 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 3794875
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 496 | 540 | 460 | 430 | 355 | 355 | 355 | 385 | 399 | 374 | 328 | 321 | 321 | 321 | 320 | 320 | 345 | 415 |  | 450 | 450 | 450 | 450 | 495 | 495 | 495 | 9578181
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP
33 | Ashuganj 225 MW CCPP | 200 | 197 | 206 | 204 | 201 | 189 | 156 | 160 | 155 | 161 | 163 | 168 | 175 | 180 | 178 | 175 | 178 | 179 |  | 187 | 178 | 177 | 181 | 188 | 189 | 188 | 4409000
34 | Ashuganj 450 MW CCPP(South) | 240 | 240 | 240 | 240 | 270 | 280 | 280 | 275 | 260 | 260 | 260 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 6189000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 300 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 315 |  | 280 | 315 | 280 | 280 | 280 | 280 | 280 | 7204400
| Ashuganj 420 MW CCPP(East) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 5940900
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 351 | 351 | 319 | 307 | 307 | 307 | 340 | 392 | 382 | 393 | 413 | 414 | 411 | 389 | 402 | 413 | 409 | 376 |  | 409 | 408 | 409 | 407 | 406 | 406 | 406 | 9345030
| Meghnaghat Unique power | 92 | 63 | 90 | 76 | 100 | 100 | 100 | 83 | 100 | 394 | 393 | 388 | 373 | 332 | 301 | 186 | 175 | 200 |  | 130 | 150 | 120 | 142 | 137 | 143 | 150 | 4080454
| Summit Meghanghat-2 589 MW(Gas) | [15 empty] | 40 | 40 | 38 |  | 31 | 0 | [5 empty] | 106363
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 170 | 170 | 170 | 170 | 170 |  | 170 | 225 | 225 | 225 | 225 | 225 | 225 | 4929500
41 | Haripur 360 MW CCPP(HPL) | 302 | 284 | 257 | 256 | 257 | 258 | 342 | 273 | 273 | 330 | 330 | 330 | 330 | 300 | 312 | 310 | 310 | 322 |  | 317 | 317 | 319 | 328 | 337 | 337 | 337 | 7320000
42 | RPCL 210MW CCPP | 95 | 95 | 100 | 100 | 100 | 100 | 84 | 34 | 34 | 35 | 35 | 33 | 31 | 32 | 34 | 34 | 34 | 34 |  | 34 | 43 | 64 | 86 | 86 | 87 | 87 | 1423680
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 6 | 9 | 33 | 24 | 20 | 53 | 13 | 40 | 28 | 12 | 1 | 0 | [8 empty] | 288000
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 33 | 33 | 0 | [14 empty] | 338400
45 | Fenchugonj CCPP Phase-2 | [11 empty] | 28 | 29 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 40 | 39 | 39 | 39 | 348480
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 57 | 40 | 40 | 40 | 40 | 40 | 40 | 62 | 61 | 60 | 59 | 58 | 55 | 57 | 55 | 55 | 51 | 55 |  | 60 | 60 | 57 | 57 | 60 | 60 | 57 | 1289088
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 191 | 198 | 202 | 201 | 201 | 201 | 201 | 200 | 200 | 200 |  | 200 | 200 | 200 | 205 | 203 | 204 | 204 | 4993700
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 396000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 248040
54 | Hobiganj 11 MW PP Cofidence-E | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 48536
55 | Fenchugonj 51 MW PP (Barakatullah)
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 8 | 0 |  |  | 0 | 0 |  |  | 8 | 16 | 16 | 16 | 8 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 256800
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 270 | 290 | 280 | 300 | 310 | 320 | 280 | 300 | 300 | 305 | 290 | 300 | 285 | 310 | 300 | 310 | 290 |  | 280 | 320 | 290 | 290 | 280 | 270 | 300 | 7191000
| Bibiyana South 400 MW | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7275000
58 | Nababganj 55 MW PP (Southern power ) | [15 empty] | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 0 | 0 | 122156
59 | Tangail Palli Power Gen 22 MW | 0 | [6 empty] | 1 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 99120
60 | Barabkunda 22 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 298224
61 | Narshingdi 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 13 | 11 | 11 | 0 |  | 10 | 15 | 15 |  | 15 | 15 | 15 | 16 | 18 | 18 | 18 | 309672
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 436464
63 | Impoprt (Tripura) | 122 | 118 | 116 | 110 | 110 | 104 | 98 | 104 | 106 | 122 | 130 | 127 | 128 | 130 | 130 | 140 | 134 | 146 |  | 138 | 136 | 130 | 132 | 128 | 128 | 120 | 3018240
64 | Malancha, Ctg. EPZ (United) | 10 | 10 | 16 | 20 | 20 | 21 | 36 | 7 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2 | 4 | 3 | 12 | 12 | 248160
65 | Feni 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 424982
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 175500
67 | Jangalia 33 MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 24 |  | 24 | 24 | 24 | 33 | 33 | 33 | 33 | 639700
68 | Cumilla 25 MW PP (Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 294300
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456000
70 | Summit Madhabdi | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 12 | 11 | 12 | 12 | 12 | 12 | 12 | 276840
71 | Maona 33 MW PP(Summit) | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 744900
72 | Rupganj 33 MW PP(Summit) | 30 | 30 | 32 | 32 | 32 | 32 | 32 | 30 | 30 | 30 | 24 | 24 | 24 | 28 | 28 | 28 | 28 | 26 |  | 26 | 26 | 26 | 26 | 28 | 31 | 31 | 686900
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | [11 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 221160
| Chowmuhani 113 MW | 12 | 9 | 0 |  |  |  |  | 0 |  |  |  | 17 | 56 | 57 | 57 | 58 | 58 | 87 |  | 87 | 87 | 88 | 90 | 87 | 85 | 44 | 883680
| Manikgonj 162MW PP(MPGL) | [11 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 35 |  | 35 | 35 | 35 | 17 | 17 | 0 |  | 260640
77 | Siddhirganj 100 PP(Dutch Bangla) | [10 empty] | 5 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 0 |  | 92160
78 | Gazipur 52 MW PP | [8 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 25 |  | 25 | 25 | 25 | 8 | 8 | 0 |  | 169440
79 | Kodda 150 MW PP | [7 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 82 |  | 98 | 64 | 64 | 32 | 32 | 0 | 0 | 488160
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | [9 empty] | 4 | 28 | 38 | 43 | 43 | 43 | 43 | 43 |  | 25 | 25 | 25 | 8 | 8 | 8 | 8 | 401371
| Gazipur 100 MW PP | [7 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 88 |  | 88 | 50 | 50 | 17 | 17 | 0 | 0 | 598080
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 2 | 4 | 3 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 28199
| Jodiac Power | [10 empty] | 6 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 263789
| Karnaphuli Power Ltd. | 17 | 17 | 17 | 0 |  |  |  |  | 6 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 349598
82 | Madanganj 102 PP(Summit) | [9 empty] | 5 | 26 | 72 | 78 | 78 | 78 | 80 | 80 | 95 |  | 95 | 95 | 95 | 46 | 17 | 17 | 17 | 828648
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [11 empty] | 13 | 33 | 33 | 36 | 46 | 46 | 45 |  | 34 | 22 | 25 | 0 |  |  | 0 | 317695
86 | Meghnaghat CCPP ( Summit) | 146 | 145 | 149 | 152 | 150 | 151 | 152 | 151 | 153 | 153 | 150 | 152 | 152 | 146 | 120 | 120 | 120 | 120 |  | 120 | 120 | 145 | 151 | 149 | 143 | 144 | 3417716
87 | Meghnaghat 100 MW(IEL) | [11 empty] | 4 | 9 | 8 | 13 | 17 | 13 | 8 |  | 9 | 9 | 9 | 8 | 9 | 9 | 8 | 124800
| Meghnaghat 104 MW PP (OPCL) | [11 empty] | 6 | 16 | 17 | 2 | 0 |  |  |  |  | 17 | 11 | 17 | 0 |  |  | 72960
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 12 | 0 | [9 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 160680
92 | Fenchuganj 44 MW (Energyprima) | 49 | 49 | 10 | 0 |  |  |  | 20 | 20 | 39 | 48 | 45 | 45 | 45 | 48 | 42 | 44 | 42 |  | 47 | 48 | 46 | 48 | 48 | 49 | 49 | 839088
93 | Ashuganj 51 MW PP (Midland) | 51 | 0 | [5 empty] | 9 | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 755040
94 | Gagnagar 102 MW PP (Digital Power) | [9 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 0 |  | 102960
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 0 | [6 empty] | 0 | 2 | 6 | 6 | 6 | 6 | 10 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 6 | 191040
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 | [14 empty] | 0 | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [9 empty] | 1 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 0 |  | 0 | 187056
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 17 | 35 |  | 35 | 35 | 35 | 17 | 0 |  | 0 | 112376
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 120 | 120 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 130 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3622500
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 1 | 2 | 2 | 2 | 1 | 0 | 0 | [9 empty] | 13000
103 | Kamalaghat 54 MW PP(Banco Energy) | [16 empty] | 17 | 35 |  | 35 | 35 | 35 | 17 | 17 | 0 | 0 | 129960
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [5 empty] | 0 | 8 | 19 | 19 | 19 | 28 | 28 | 38 | 37 | 37 | 37 | 37 | 95 |  | 93 | 93 | 93 | 45 | 18 | 18 | 19 | 696000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 0 |  |  |  |  | 1 | 13 | 17 | 17 | 17 | 17 | 19 | 17 | 17 | 17 | 17 | 41 |  | 128 | 135 | 130 | 90 | 66 | 45 | 17 | 726768
115 | Juldah 100 MW PP Unit-3 (Acorn) | 12 | 12 | 12 | 0 |  |  |  | 1 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 242880
116 | Chandpur 200 MW (Desh energy) | 17 | [9 empty] | 4 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 271200
117 | Ashuganj 150 MW PP (Midland) | [10 empty] | 5 | 50 | 88 | 100 | 95 | 80 | 83 | 100 |  | 100 | 12 | 28 | 12 | 10 | 0 | 0 | 762763
118 | Bibiyana-III 400 MW CCPP | 377 | 377 | 364 | 365 | 365 | 365 | 401 | 377 | 400 | 403 | 403 | 403 | 403 | 379 | 404 | 404 | 404 | 404 |  | 403 | 404 | 403 | 402 | 402 | 402 | 402 | 9379000
| Jamalpur 115 MW PP (United) | [5 empty] | 0 | 10 | 56 | 59 | 55 | 77 | 89 | 77 | 80 | 80 | 80 | 80 | 90 |  | 90 | 90 | 90 | 70 | 70 | 55 | 55 | 1306800
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | 0 | 0 | 0 | 0 | 49 | 65 | 87 | 88 | 70 | 88 | 88 | 88 | 105 | 220 |  | 195 | 195 | 195 | 170 | 155 | 123 | 65 | 1964618
| Juldah unit-2 (Acorn) | 12 | 12 | 12 | [6 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 224640
| Anlima Energy Ltd. | 17 | 17 | [7 empty] | 1 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 34 | 34 | 34 | 34 | 34 | 17 | 377618
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 443160
| Spectra Solar Plant Ltd. | [6 empty] | 4 | 12 | 21 | 27 | 31 | 31 | 29 | 24 | 17 | 8 | 1 | 0 | [8 empty] | 201949
| Chandpur 115(Doreen) | 35 | 18 | 18 | [7 empty] | 7 | 18 | 18 | 18 | 17 | 18 | 37 | 94 |  | 95 | 95 | 95 | 74 | 72 | 37 | 18 | 702720
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 0 |  |  |  | 0 | 0 | 0 | 24 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 509040
| Mirsharai 150 MW (Oil) | [11 empty] | 36 | 36 | 36 | 36 | 17 | 17 | 36 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 314472
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 6 | 6 | 6 | 7 | 8 | 6 | 6 | 3 | 3 | 4 | 1 | 4 | 6 | 6 | 4 | 3 | 3 | 0 |  | 2 | 3 | 3 | 2 | 5 | 6 | 6 | 100320
| Matarbari 2*600 MW (CPGCL) | 144 | 145 | 145 | 147 | 147 | 145 | 147 | 137 | 139 | 196 | 234 | 257 | 256 | 260 | 257 | 255 | 255 | 257 |  | 262 | 262 | 260 | 260 | 262 | 264 | 262 | 5134545
120 | Eastern Zone Total | 5709 | 5488 | 5339 | 5118 | 4940 | 4904 | 5082 | 5142 | 5260 | 5779 | 6051 | 6501 | 6622 | 6449 | 6451 | 6341 | 6338 | 7108 |  | 7021 | 6964 | 6914 | 6625 | 6485 | 6246 | 6074 | 145468680
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [16 empty] | 16 | 19 |  | 0 | [5 empty] | 0 | 36480
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [26 empty] | 0
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [11 empty] | 5 |  |  |  |  | 17 | 17 |  | 17 | 10 | 17 | 17 | 17 | 17 | 0 | 137760
130 | Mongla Orion 100 MW Solar PP | [7 empty] | 31 | 54 | 71 | 78 | 85 | 80 | 66 | 46 | 22 | 3 | 0 | [8 empty] | 550080
131 | Rampal 1320 MW (BIFPCL) | 338 | 340 | 340 | 339 | 335 | 342 | 340 | 339 | 338 | 334 | 337 | 336 | 339 | 339 | 337 | 343 | 329 | 407 |  | 401 | 401 | 401 | 401 | 405 | 409 | 408 | 8567273
132 | United Payra Power Ltd. | [7 empty] | 0 | [9 empty] | 16 |  | 0 | [6 empty] | 40800
133 | Bhola Nutan Biddut BD LTD (GAS) | 200 | 200 | 200 | 200 | 200 | 200 | 220 | 220 | 220 | 180 | 180 | 220 | 220 | 220 | 220 | 220 | 180 | 222 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5158691
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [25 empty] | 0 | 0
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3687300
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 130 | 122 | 80 | 80 | 80 | 80 | 80 | 130 | 130 | 80 | 80 | 130 | 122 | 126 | 130 | 130 | 92 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 2679000
140 | Bhola 33 MW PP (Venture) | 19 | 18 | 17 | 17 | 16 | 15 | 14 | 13 | 13 | 14 | 16 | 20 | 20 | 20 | 20 | 18 | 14 | 22 |  | 21 | 21 | 22 | 21 | 21 | 21 | 20 | 426300
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [25 empty] | 0 | 1500
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 8 | 0 | [5 empty] | 6912
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [16 empty] | 15 | 32 | [7 empty] | 0 | 54144
146 | Bheramara HVDC | 900 | 899 | 899 | 901 | 900 | 900 | 900 | 899 | 900 | 899 | 899 | 901 | 899 | 899 | 899 | 898 | 898 | 775 |  | 774 | 832 | 832 | 898 | 898 | 899 | 899 | 21655272
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 820 | 640 | 600 | 560 | 520 | 520 | 540 | 660 | 700 | 540 | 560 | 600 | 670 | 720 | 800 | 760 | 760 | 960 |  | 1120 | 1080 | 1100 | 1080 | 940 | 900 | 860 | 19847000
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4143600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 2 | 3 | 4 | 5 | 5 | 4 | 0 | 1 | 1 | 0 | [9 empty] | 31140
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 152 | 153 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 137 | 150 | 149 | 146 | 146 | 145 | 145 | 145 | 145 |  | 145 | 145 | 145 | 145 | 145 | 146 | 150 | 3626927
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 252 | 265 | 200 | 200 | 240 | 230 | 270 | 240 | 240 | 236 | 203 | 154 | 182 | 177 | 160 | 160 | 164 | 161 |  | 172 | 173 | 173 | 193 | 202 | 201 | 207 | 4984727
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 197964
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 8 |  | 8 | 8 | 8 | 0 |  |  |  | 20215
167 | Katakhali 50 MW Peaking PP | [17 empty] | 39 |  | 38 | 32 | 32 | 32 | 0 |  |  | 133931
168 | Santahar 50 MW Peaking PP | [17 empty] | 38 |  | 38 | 0 | [5 empty] | 71154
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 10 |  | 8 | 8 | 8 |  |  |  | 0 | 29434
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 32 |  | 32 | 32 | 32 |  |  |  | 0 | 91248
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [11 empty] | 6 | 35 | 35 | 35 | 35 | 35 | 49 |  | 50 | 50 | 50 | 35 | 35 | 0 | 0 | 482304
172 | Confidence Power Bogura Unit-1 113 MW | [11 empty] | 35 | 35 | 35 | 35 | 35 | 55 | 55 |  | 55 | 55 | 55 | 35 | 0 |  | 0 | 444576
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [14 empty] | 18 | 34 | 56 | 110 |  | 70 | 34 | 34 | 34 | 34 | 11 | 0 | 398947
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 2 | 4 | 6 | 6 | 6 | 6 | 5 | 5 | 3 | 1 | [9 empty] | 42602
178 | Energypac Power Venture Thakurgaon Ltd. | [14 empty] | 35 | 35 | 40 | 85 |  | 75 | 35 | 35 |  |  |  | 0 | 346752
| Intraco Solar 30 MW | [6 empty] | 4 | 15 | 24 | 31 | 35 | 36 | 34 | 29 | 22 | 9 | 1 | [9 empty] | 236416
| Adani Power Jharkhanda Ltd | 867 | 826 | 828 | 827 | 828 | 827 | 905 | 1010 | 1024 | 1029 | 1108 | 1110 | 1113 | 1065 | 1110 | 1126 | 1120 | 1217 |  | 1217 | 1157 | 1152 | 1161 | 1118 | 1120 | 1117 | 24777042
178 | Teesta Solar Limited | [6 empty] | 27 | 83 | 133 | 167 | 189 | 193 | 181 | 152 | 102 | 48 | 3 | [9 empty] | 1278560