## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-11-12 | Sunday
|  | Date (day): | 2023-11-12 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11759.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13667 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-11-11 | 2023-11-12 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 170 | 180 | 180 | 180 |  | 190 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 51 | 74 | 80 | 80 | 28 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 355 | 334 | 395 | 400 | 12 |  | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 167 | 154 | 150 | 150 | 210 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | GT-1 under S/D due to Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 20 | 8 | 50 | 50 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 138 | 152 | 150 | 150 | 185 |  | GT-1 under S/D due to Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 34 | 95 | 95
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 25 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 25 | 50 | 50 | 25 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 12 | 14 | 18 | 18 |  | 4 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 1 | 50 | 17 | 50 | 50 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 251 | 224 | 260 | 260 | 165 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 91 | 91 | 91 | 11 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 0 | 17 | 37 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 32 | 16 | 132 | 17 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 0 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 0 | 55
| Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
25 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 30 | 30 | 31 | 31 |  | 49 | Engine problem
26 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
27 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
28 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 18 | 8 | 25 | 27 |  | Fuel shortage
29 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
30 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 49 | 80 | 130 | 170 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
31 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 51 | 17 | 80 | 69 |  | Fuel shortage
32 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 0 | 105
33 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 2 | 51 | 17 | 51 | 53 |  | Fuel shortage
34 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 35 | 17 | 35 | 127 |  | Fuel shortage
35 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 31 | 0 | 35 | 0
36 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 35 | 17 | 35 | 20 |  | Fuel shortage
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 5763 | 5422 | 1516 | 2060 | 2030 | 2603 | 1907 | 1011
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
38 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 16 | 8 | 17 | 8 |  | Fuel shortage
39 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 24 | 26 | 6 | 26 | 24 |  | Fuel shortage
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 132 | 132 | 132 | 132 |  | 98 | Engine problem
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 141 | 141 | 141 | 141 |  |  | Gas shortage
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 24 | 17 | 17 | 17 | 88 |  | Fuel shortage
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 16 | 8 | 17 | 81 |  | Fuel shortage
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 17 | 0 | 17 | 102 |  | Fuel shortage
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 12 | 12 | 12 | 12 | 10 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 0 | 20 | 30
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 85 | 240 | 100 | 260 | 40 |  | Fuel shortage
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 5 | 17 | 17 | 17 | 37 |  | Fuel shortage
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 35 | 19 | 17 | 19 | 91 |  | Fuel shortage
55 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
56 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 34 | 82 |  | Fuel shortage
57 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 15 | 17 | 17 | 17
58 | SS Power I |  | Coal | SS Power | 1*612 | 612 | 612 | 312 | 325 | 325 | 325
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 0 | 3 | 10 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 204 | 201 | 300 | 300 |  |  | On test.
| Chattogram area Total |  |  |  |  | 3217 | 3157 | 1083 | 1252 | 1208 | 1427 | 1115 | 428
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 186 | 158 | 180 | 190 | 31 |  | Gas shortage
60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 275 | 280 | 280 | 280 | 80 |  | Gas shortage
61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 240 | 240 | 280 | 280 | 80 |  | Gas shortage
62 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 230 | 230 | 300 | 300 | 100 |  | Gas shortage
63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 0 | 0 | 0
| Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortae
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 26 | 51 | 51 | 51
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 60 | 12 | 140
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 17 | 17 | 17 | 183 |  | Fuel shortage
70 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 16 | 18 | 18 |  | 4 | Engine problem
71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 124 | 130 | 128 | 140
72 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 28 | 52 | 52
74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 6 | 12 | 12 | 12 |  | 13 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 17 | 17 | 52 | 62 |  | Fuel shortage
76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 57 | 28 | 58 | 55 |  | Fuel shortage
77 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 17 | 17 | 17 |  | 37 | Engine problem
78 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 4 | 88 | 34 | 95 | 20 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2896 | 1149 | 1444 | 1469 | 1745 | 806 | 217
79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 97 | 99 | 100 | 100 | 102 |  | Gas shortage
80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 18 | 18 | 18 |  | 4 | Engine problem
| Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 8 | 93 | 84 | 100 | 100 |  | Fuel shortage
83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 8 | 85 | 40 | 85 | 30 |  | Fuel shortage
84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 49 | 0 | 50 | 0
85 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 170 | 301 | 299.6 | 309 | 102 | 4
86 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 42 | 42 | 42 |  | 28 | Machine problem.
87 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Engine problem
88 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
89 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
90 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 42 | 50 | 45 | 50
91 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0
92 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 2 | 2 |  | 9 | Engine problem
93 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 62 | 60 | 62
94 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 0 | 0 | 0 | 86 |  | Gas shortage
95 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 202 | 205 | 205 | 205 |  | 26 | Machine problem
97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 16 | 17 | 17 | 17
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 16 | 16 | 16 | 9 |  | Gas shortage
99 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 285 | 290 | 300 |  |  | FGMO
100 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 403 | 402 | 400 | 400 |  |  | FGMO
101 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
102 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 250 | 260 | 230 | 260 |  | 123 | ST under maint.
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1329 | 1354 | 1317 | 1364 | 258 | 706
103 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 911 | 912 | 919 | 801
104 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 16 | 0 | 16 | 99 |  | Fuel shortage
105 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 50 |  | 4 | Engine problem
106 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
107 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 75 | 34 |  | Fuel shortage
108 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
109 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 | 40 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
110 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 13 | 50 | 83 | 22 |  | Fuel shortage
111 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 32 | 15 | 32 | 73 |  | Fuel shortage
112 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 72 | 0 | 100 | 0
113 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0
114 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 345 | 455 | 400 | 570 |  | 617
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 1328 | 1428 | 1484 | 1627 | 924 | 621
115 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 12 | 16 | 110
116 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 14 | 23 | 21 | 25 |  | 15 | Engine problem
117 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 130 | 120 | 130 | 130 |  | 64 | ST under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 590 | 900 | 1244 | 1244
119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 38 | 150
121 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 140 | 140 | 140 | 185 | 122 |  | Coal shortage
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1094 | 1469 | 1809 | 2064 | 122 | 79
122 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
123 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 35 | 17 |  | Fuel shortage
124 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 20 |  | 51 | Engine problem
125 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 28 | 28
126 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 34 | 42 |  | 8 | Engine problem
127 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 40 |  | 10 | Engine problem
128 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
129 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
130 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
131 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 414 | 250 | 414
132 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 24 | 38 | 12 |  | Fuel shortage
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
133 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
134 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 8 | 52
135 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 40 | 85 |  | 19 | Engine problem
136 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
137 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 45 | 35 | 50 | 63 |  | Fuel shortage
138 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 35 | 55
139 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 922 | 1155 | 1200 | 1300
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 1352 | 1660 | 1701 | 2170 | 1113 | 88
140 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
141 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
142 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
143 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
144 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 34 | 34 | 113
145 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
146 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 35 | 70 | 75 | 40 |  | Fuel shotage
147 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 30 | 0
148 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 183 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 393 | 239 | 442 | 358 | 165 | 189
| Total |  |  |  |  | 25339 | 24599 | 9414 | 11207 | 11759.6 | 13667 | 6512 | 3343
A. |  | 2023-11-11 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 11207 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 7369 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11207 | MW
3 | Day peak Generation : |  |  | 9414 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10993.81 | MW
4 | Evening peak Generation : |  |  | 11207 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 222.6957 | MKWHr | By Solar | 2.5808 | MKWHr
| By Gas : | 111.2036 | MKWHr |  | By Oil: | 11.7995 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 71.2172 | MKWHr |  | By Hydro: | 3.0128 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.05376 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6512 | MW | Dhaka | 4348.61 | 4348.61 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3343 | MW | Chittagong | 1143.6 | 1143.6 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 9855 | MW | Khulna | 1197.8 | 1197.8 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 870.73 | MMCFD |  |  | Rajshahi | 1005.8 | 1005.8 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 114369595.874 | ii) Oil : | Taka | 149963522.51 | Comilla | 988 | 988 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 512916895.33 | Total | Taka | 777250013.714 | Mymensingh | 896 | 896 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 437 | 437 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 420 | MW (W to E) at | 18:00 | hrs | Barisal | 297 | 297 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 350 | MW at | 19:00 | hrs | Rangpur | 680 | 680 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31.6°C |  |  | Total | 10993.81 | 10993.81 |  | 0
B. |  | 2023-11-12 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 31.6°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13667 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10200 | MW
4 | Reserve(Generation end) |  |  |  | 1867 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 234.4793 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7754 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.0785 | MKWHr. | ii) HVDC Flow at Peak Time |  | 912 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.7494 | MKWHr. | iii) Maximum HVDC Flow : |  | 918 | MW at | 22:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 100.07 |  | (b) Today: | 99.9 |  | (c) Rule Curve: |  | 107.9
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-11-11 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 170 | 0 | 6 | 0 | 316 | 245 |  | 0 | 225 | 112 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 19 | 12 | 33 | 25 | 0 | 0 | 92 | 40 | 0 | 0 | 0 | 132 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 42 | 0 | 0 | 0 | 280 | 270 | 169 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 18 | 10 | 17 | 12 | 102 | 104 | 0 | 0 | 0 | 42 | 0 | 5 | 0 | 0 | 0 | 40 | 0 | 0 | 205 | 18 | 0 | 0 | 260 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 376 | 0 | 0 | 17 | 0 | 15 | 0 | 17 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 250 | 0 | 0 | 320 | 6 | 198 | 0 | 0 |  | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 140 | 828 | 0 | 0 |  | 4783 | 3594 | 8377 | 3135 | 911 | 1400 | 0 | 78 | 2613 | 132 | 0 | 0 | 102 | 0 | 6 | 0 | 100.09
2:00 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 303 | 255 |  | 0 | 225 | 112 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 13 | 33 | 25 | 0 | 0 | 92 | 40 | 0 | 0 | 0 | 128 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 280 | 270 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 98 | 104 | 0 | 0 | 0 | 42 | 0 | 5 | 0 | 0 | 0 | 40 | 0 | 0 | 205 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 320 | 10 | 203 | 0 | 0 |  | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 140 | 818 | 0 | 0 |  | 4532 | 3474 | 8006 | 2978 | 912 | 1328 | 0 | 0 | 2548 | 132 | 0 | 0 | 98 | 0 | 10 | 0 | 100.09
3:00 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 302 | 215 |  | 0 | 170 | 114 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 13 | 33 | 25 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 280 | 230 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 102 | 83 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 205 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 321 | 10 | 203 | 0 | 0 |  | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 140 | 815 | 0 | 0 |  | 4231 | 3416 | 7647 | 2815 | 912 | 1195 | 0 | 0 | 2521 | 92 | 0 | 0 | 102 | 0 | 10 | 0 | 100.08
4:00 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 292 | 205 |  | 0 | 170 | 115 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 13 | 33 | 25 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 290 | 230 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 102 | 84 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 205 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 320 | 7 | 204 | 0 | 0 |  | 627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 140 | 815 | 0 | 0 |  | 4219 | 3158 | 7377 | 2800 | 627 | 1200 | 0 | 0 | 2549 | 92 | 0 | 0 | 102 | 0 | 7 | 0 | 100.08
5:00 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 289 | 205 |  | 0 | 170 | 114 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 13 | 25 | 25 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 315 | 230 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 100 | 87 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 205 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 320 | 6 | 205 | 0 | 0 |  | 531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 140 | 818 | 0 | 0 |  | 4291 | 3078 | 7369 | 2837 | 531 | 1229 | 0 | 0 | 2574 | 92 | 0 | 0 | 100 | 0 | 6 | 0 | 100.07
6:00 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 295 | 205 |  | 0 | 170 | 113 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 12 | 25 | 25 | 0 | 0 | 92 | 40 | 0 | 0 | 0 | 133 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 280 | 270 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 12 | 90 | 87 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 205 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 320 | 3 | 203 | 0 | 0 |  | 531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 140 | 815 | 0 | 0 |  | 4392 | 3101 | 7493 | 2909 | 531 | 1260 | 0 | 0 | 2568 | 132 | 0 | 0 | 90 | 0 | 3 | 0 | 100.07
7:00 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 350 | 218 |  | 0 | 170 | 117 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 12 | 25 | 25 | 0 | 0 | 92 | 40 | 0 | 0 | 0 | 141 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 41 | 0 | 0 | 0 | 325 | 360 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 33 | 12 | 96 | 103 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 205 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 4 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 250 | 0 | 0 | 320 | 2 | 206 | 0 | 0 |  | 531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 180 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 380 | 3 | 140 | 811 | 17 | 0 |  | 4753 | 3223 | 7976 | 3220 | 531 | 1390 | 0 | 0 | 2567 | 132 | 0 | 0 | 96 | 38 | 2 | 0 | 100.06
8:00 | 0 | 0 | 0 | 170 | 0 | 32 | 0 | 392 | 188 |  | 0 | 170 | 121 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 12 | 25 | 25 | 0 | 0 | 92 | 40 | 0 | 0 | 0 | 141 | 0 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 280 | 270 | 175 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 15 | 10 | 33 | 12 | 98 | 104 | 0 | 0 | 1 | 42 | 0 | 25 | 0 | 0 | 0 | 40 | 0 | 0 | 205 | 17 | 0 | 10 | 285 | 0 | 5 | 0 | 0 | 0 | 0 | 24 | 0 | 9 | 9 | 0 | 0 | 0 | 343 | 35 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 9 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 322 | 0 | 202 | 0 | 0 |  | 626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 590 | 220 | 0 | 0 | 2 | 25 | 0 | 0 | 0 | 374 | 11 | 140 | 817 | 69 | 0 |  | 4779 | 3519 | 8298 | 3174 | 626 | 1444 | 0 | 69 | 2615 | 132 | 0 | 0 | 98 | 140 | 0 | 0 | 100.04
9:00 | 0 | 0 | 0 | 170 | 0 | 12 | 0 | 392 | 187 |  | 0 | 170 | 122 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19 | 0 | 25 | 8 | 0 | 0 | 92 | 40 | 0 | 0 | 0 | 141 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 0 | 10 | 2 | 0 | 0 | 0 | 280 | 240 | 183 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 15 | 10 | 33 | 12 | 100 | 104 | 0 | 0 | 2 | 43 | 0 | 10 | 0 | 0 | 0 | 40 | 0 | 0 | 205 | 17 | 0 | 10 | 275 | 0 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 15 | 4 | 0 | 0 | 335 | 69 | 0 | 2 | 3 | 50 | 0 | 2 | 0 | 0 | 12 | 200 | 0 | 32 | 0 | 4 | 0 | 0 | 22 | 0 | 0 | 230 | 0 | 0 | 322 | 0 | 190 | 0 | 0 |  | 845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 560 | 180 | 0 | 0 | 3 | 45 | 0 | 0 | 0 | 378 | 22 | 140 | 814 | 118 | 0 |  | 4704 | 3621 | 8325 | 2997 | 845 | 1210 | 0 | 186 | 2574 | 132 | 0 | 16 | 100 | 265 | 0 | 0 | 100.05
10:00 | 0 | 0 | 0 | 170 | 0 | 12 | 0 | 373 | 206 |  | 0 | 170 | 123 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 19 | 12 | 0 | 25 | 0 | 0 | 92 | 40 | 0 | 0 | 0 | 141 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 6 | 10 | 0 | 0 | 0 | 0 | 300 | 240 | 198 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 15 | 10 | 33 | 12 | 112 | 100 | 0 | 0 | 2 | 43 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 203 | 17 | 0 | 10 | 270 | 16 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 18 | 12 | 0 | 0 | 337 | 8 | 0 | 17 | 4 | 65 | 0 | 17 | 0 | 0 | 12 | 200 | 0 | 41 | 0 | 17 | 0 | 0 | 26 | 0 | 0 | 230 | 0 | 0 | 320 | 0 | 201 | 0 | 0 |  | 845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 520 | 180 | 0 | 0 | 4 | 61 | 0 | 0 | 0 | 351 | 30 | 140 | 816 | 153 | 0 |  | 4791 | 3617 | 8408 | 3032 | 845 | 1212 | 0 | 197 | 2518 | 132 | 0 | 16 | 112 | 344 | 0 | 0 | 100.05
11:00 | 0 | 0 | 0 | 170 | 0 | 12 | 0 | 334 | 201 |  | 0 | 170 | 134 | 0 | 0 | 0 | 253 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 19 | 11 | 0 | 25 | 0 | 0 | 92 | 40 | 0 | 0 | 0 | 140 | 0 | 0 | 0 |  | 6 | 0 | 14 | 12 | 0 | 14 | 12 | 0 | 0 | 0 | 0 | 290 | 240 | 192 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 15 | 10 | 33 | 12 | 114 | 98 | 0 | 0 | 2 | 43 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 203 | 17 | 0 | 10 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 19 | 12 | 0 | 0 | 387 | 8 | 0 | 17 | 4 | 65 | 0 | 26 | 0 | 0 | 12 | 250 | 0 | 47 | 0 | 17 | 0 | 0 | 31 | 0 | 0 | 230 | 0 | 0 | 312 | 1 | 201 | 0 | 0 |  | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 520 | 220 | 0 | 0 | 5 | 70 | 0 | 0 | 0 | 349 | 34 | 140 | 818 | 177 | 0 |  | 5019 | 3873 | 8892 | 3216 | 911 | 1369 | 0 | 214 | 2510 | 132 | 0 | 30 | 114 | 395 | 1 | 0 | 100.04
12:00 | 0 | 0 | 0 | 170 | 0 | 51 | 0 | 355 | 167 |  | 0 | 225 | 138 | 0 | 0 | 0 | 251 | 0 | 0 | 1 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 19 | 11 | 25 | 25 | 0 | 0 | 92 | 40 | 0 | 0 | 0 | 141 | 0 | 0 | 0 |  | 6 | 0 | 17 | 12 | 0 | 24 | 12 | 0 | 0 | 0 | 0 | 275 | 240 | 186 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 15 | 10 | 33 | 6 | 124 | 97 | 0 | 0 | 2 | 43 | 0 | 42 | 0 | 0 | 0 | 58 | 0 | 0 | 202 | 16 | 0 | 10 | 300 | 0 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 20 | 12 | 0 | 0 | 403 | 8 | 0 | 24 | 4 | 85 | 5 | 35 | 0 | 0 | 12 | 250 | 2 | 49 | 0 | 17 | 0 | 0 | 31 | 4 | 0 | 230 | 15 | 0 | 312 | 0 | 204 | 0 | 0 |  | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 590 | 220 | 0 | 0 | 5 | 72 | 0 | 0 | 0 | 345 | 34 | 140 | 922 | 183 | 0 |  | 5247 | 4167 | 9414 | 3231 | 911 | 1607 | 0 | 272 | 2683 | 132 | 0 | 48 | 124 | 406 | 0 | 0 | 100.04
13:00 | 0 | 0 | 0 | 170 | 0 | 75 | 0 | 336 | 161 |  | 0 | 225 | 146 | 0 | 17 | 0 | 244 | 0 | 0 | 14 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 19 | 11 | 33 | 25 | 0 | 0 | 92 | 40 | 0 | 0 | 0 | 141 | 0 | 0 | 0 |  | 6 | 0 | 17 | 12 | 0 | 27 | 12 | 2 | 0 | 0 | 0 | 280 | 240 | 187 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 13 | 10 | 33 | 12 | 130 | 95 | 0 | 0 | 2 | 40 | 0 | 44 | 0 | 0 | 0 | 40 | 0 | 0 | 201 | 17 | 0 | 10 | 300 | 0 | 5 | 0 | 18 | 0 | 0 | 8 | 0 | 17 | 18 | 12 | 1 | 10 | 403 | 8 | 0 | 34 | 4 | 103 | 17 | 35 | 0 | 0 | 12 | 255 | 36 | 21 | 12 | 17 | 0 | 0 | 30 | 27 | 0 | 230 | 22 | 0 | 312 | 0 | 201 | 0 | 0 |  | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 2 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 830 | 220 | 0 | 0 | 5 | 66 | 0 | 0 | 0 | 345 | 31 | 140 | 1022 | 171 | 0 |  | 5442 | 4427 | 9869 | 3205 | 910 | 1602 | 0 | 461 | 3020 | 132 | 0 | 55 | 130 | 354 | 0 | 0 | 100.03
14:00 | 0 | 0 | 0 | 170 | 0 | 74 | 0 | 305 | 163 |  | 0 | 225 | 146 | 0 | 50 | 10 | 247 | 0 | 0 | 40 | 58 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 19 | 11 | 33 | 25 | 0 | 0 | 92 | 40 | 0 | 0 | 0 | 141 | 0 | 0 | 0 |  | 6 | 0 | 17 | 12 | 0 | 26 | 12 | 0 | 0 | 0 | 0 | 275 | 240 | 187 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 33 | 12 | 130 | 92 | 0 | 0 | 2 | 43 | 0 | 44 | 0 | 0 | 0 | 40 | 0 | 0 | 201 | 17 | 0 | 10 | 260 | 16 | 5 | 0 | 47 | 0 | 0 | 8 | 0 | 17 | 15 | 12 | 16 | 10 | 372 | 8 | 0 | 34 | 3 | 105 | 17 | 35 | 0 | 28 | 12 | 235 | 68 | 31 | 18 | 17 | 0 | 0 | 25 | 48 | 0 | 230 | 25 | 0 | 311 | 0 | 192 | 0 | 0 |  | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 9 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 840 | 180 | 0 | 0 | 4 | 53 | 0 | 0 | 0 | 349 | 26 | 140 | 977 | 144 | 0 |  | 5549 | 4157 | 9706 | 3066 | 909 | 1413 | 0 | 711 | 2979 | 132 | 0 | 58 | 130 | 308 | 0 | 0 | 100.04
15:00 | 0 | 0 | 0 | 170 | 0 | 71 | 0 | 322 | 163 |  | 0 | 225 | 149 | 0 | 48 | 15 | 238 | 0 | 0 | 27 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 19 | 11 | 33 | 25 | 0 | 0 | 92 | 40 | 0 | 0 | 0 | 141 | 0 | 0 | 0 |  | 6 | 0 | 17 | 12 | 0 | 26 | 12 | 0 | 0 | 0 | 0 | 315 | 240 | 170 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 12 | 10 | 33 | 12 | 134 | 91 | 0 | 15 | 1 | 41 | 0 | 20 | 0 | 0 | 0 | 40 | 0 | 0 | 203 | 17 | 0 | 10 | 300 | 16 | 5 | 0 | 47 | 0 | 0 | 8 | 0 | 17 | 11 | 12 | 0 | 10 | 404 | 8 | 0 | 34 | 2 | 103 | 17 | 35 | 0 | 27 | 12 | 235 | 61 | 25 | 17 | 17 | 0 | 0 | 18 | 35 | 0 | 230 | 0 | 0 | 310 | 2 | 197 | 0 | 0 |  | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 17 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 740 | 220 | 0 | 0 | 2 | 35 | 0 | 0 | 0 | 347 | 16 | 140 | 918 | 99 | 0 |  | 5514 | 4067 | 9581 | 3205 | 910 | 1527 | 0 | 619 | 2822 | 132 | 0 | 17 | 134 | 213 | 2 | 0 | 100.02
16:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 352 | 159 |  | 0 | 225 | 148 | 0 | 17 | 15 | 230 | 0 | 0 | 9 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 19 | 11 | 25 | 25 | 0 | 0 | 92 | 40 | 0 | 0 | 0 | 141 | 0 | 0 | 0 |  | 3 | 0 | 17 | 12 | 0 | 26 | 12 | 0 | 0 | 0 | 0 | 320 | 240 | 154 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 16 | 10 | 33 | 12 | 126 | 93 | 0 | 18 | 0 | 41 | 0 | 49 | 0 | 0 | 0 | 60 | 0 | 0 | 201 | 17 | 0 | 10 | 305 | 16 | 5 | 0 | 47 | 0 | 0 | 8 | 0 | 17 | 5 | 12 | 0 | 10 | 404 | 8 | 0 | 34 | 1 | 103 | 17 | 35 | 0 | 37 | 12 | 255 | 17 | 5 | 0 | 17 | 0 | 0 | 8 | 36 | 0 | 230 | 0 | 0 | 310 | 2 | 198 | 0 | 0 |  | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 740 | 220 | 0 | 0 | 1 | 14 | 0 | 0 | 0 | 349 | 8 | 140 | 921 | 43 | 0 |  | 5455 | 4078 | 9533 | 3269 | 909 | 1663 | 0 | 500 | 2828 | 132 | 0 | 17 | 126 | 87 | 2 | 0 | 100.02
17:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 346 | 154 |  | 0 | 180 | 152 | 3 | 17 | 15 | 229 | 0 | 0 | 12 | 40 | 32 | 15 | 0 | 0 | 0 | 17 | 5 | 17 | 14 | 19 | 12 | 25 | 25 | 8 | 0 | 92 | 40 | 0 | 0 | 3 | 141 | 0 | 0 | 0 |  | 6 | 2 | 17 | 12 | 0 | 26 | 12 | 0 | 0 | 0 | 0 | 280 | 240 | 151 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 1 | 16 | 10 | 33 | 12 | 124 | 98 | 0 | 18 | 0 | 40 | 0 | 50 | 0 | 0 | 0 | 40 | 0 | 0 | 205 | 17 | 0 | 10 | 290 | 16 | 5 | 0 | 47 | 0 | 0 | 28 | 0 | 17 | 0 | 12 | 11 | 23 | 371 | 46 | 0 | 34 | 0 | 105 | 17 | 35 | 17 | 38 | 12 | 235 | 24 | 1 | 17 | 17 | 0 | 6 | 1 | 48 | 21 | 230 | 23 | 0 | 310 | 2 | 202 | 0 | 0 |  | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 2 | 0 | 16 | 32 | 35 | 0 | 0 | 35 | 790 | 180 | 0 | 19 | 0 | 1 | 10 | 0 | 0 | 346 | 1 | 140 | 967 | 3 | 0 |  | 5600 | 4069 | 9669 | 3111 | 911 | 1462 | 0 | 921 | 2925 | 132 | 0 | 74 | 124 | 7 | 2 | 0 | 100.01
18:00 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 334 | 154 |  | 0 | 225 | 152 | 20 | 34 | 25 | 224 | 0 | 0 | 50 | 91 | 32 | 25 | 0 | 0 | 0 | 17 | 35 | 55 | 14 | 19 | 11 | 25 | 25 | 18 | 0 | 92 | 40 | 0 | 0 | 16 | 141 | 0 | 0 | 0 |  | 6 | 16 | 17 | 12 | 0 | 26 | 12 | 0 | 0 | 0 | 0 | 280 | 240 | 158 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 28 | 16 | 10 | 33 | 12 | 130 | 99 | 0 | 18 | 0 | 42 | 0 | 50 | 0 | 0 | 0 | 62 | 0 | 0 | 205 | 17 | 0 | 10 | 285 | 16 | 5 | 0 | 49 | 0 | 0 | 93 | 0 | 51 | 0 | 12 | 17 | 60 | 402 | 85 | 0 | 17 | 0 | 240 | 17 | 19 | 17 | 57 | 12 | 260 | 51 | 0 | 35 | 17 | 0 | 17 | 0 | 88 | 35 | 230 | 17 | 0 | 325 | 3 | 201 | 0 | 0 |  | 912 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 23 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 13 | 0 | 45 | 32 | 34 | 0 | 0 | 35 | 900 | 220 | 0 | 54 | 0 | 0 | 35 | 0 | 0 | 455 | 0 | 140 | 1155 | 0 | 0 |  | 6411 | 4796 | 11207 | 3221 | 912 | 1658 | 0 | 1723 | 3346 | 132 | 0 | 82 | 130 | 0 | 3 | 0 | 100.01
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 340 | 151 |  | 0 | 225 | 155 | 49 | 50 | 30 | 224 | 0 | 0 | 62 | 49 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 14 | 19 | 12 | 25 | 25 | 25 | 0 | 92 | 40 | 0 | 0 | 17 | 141 | 0 | 0 | 0 |  | 6 | 16 | 17 | 12 | 0 | 26 | 12 | 3 | 0 | 0 | 0 | 280 | 240 | 168 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 16 | 10 | 25 | 12 | 124 | 95 | 0 | 18 | 0 | 42 | 0 | 50 | 0 | 0 | 0 | 62 | 0 | 0 | 204 | 17 | 0 | 10 | 280 | 16 | 5 | 0 | 15 | 0 | 0 | 65 | 0 | 80 | 0 | 12 | 17 | 50 | 402 | 85 | 0 | 17 | 0 | 245 | 17 | 19 | 17 | 57 | 12 | 260 | 65 | 0 | 17 | 17 | 0 | 17 | 0 | 95 | 17 | 230 | 17 | 0 | 325 | 0 | 202 | 0 | 0 |  | 801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 1040 | 220 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 452 | 0 | 140 | 1163 | 0 | 0 |  | 6299 | 4716 | 11015 | 3233 | 801 | 1656 | 0 | 1511 | 3492 | 132 | 0 | 66 | 124 | 0 | 0 | 0 | 99.99
19:30 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 340 | 152 |  | 0 | 225 | 156 | 25 | 17 | 15 | 223 | 0 | 0 | 48 | 49 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 18 | 19 | 12 | 25 | 25 | 25 | 0 | 92 | 40 | 0 | 0 | 17 | 141 | 0 | 0 | 0 |  | 6 | 16 | 17 | 12 | 0 | 26 | 12 | 2 | 0 | 0 | 0 | 280 | 240 | 170 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 16 | 10 | 25 | 12 | 122 | 95 | 0 | 18 | 0 | 43 | 0 | 50 | 0 | 0 | 0 | 62 | 0 | 0 | 204 | 18 | 0 | 10 | 270 | 16 | 5 | 0 | 15 | 0 | 0 | 25 | 0 | 81 | 0 | 12 | 17 | 6 | 402 | 65 | 0 | 17 | 0 | 248 | 17 | 17 | 17 | 57 | 12 | 260 | 72 | 0 | 17 | 17 | 0 | 17 | 0 | 95 | 17 | 230 | 17 | 0 | 325 | 0 | 201 | 0 | 0 |  | 881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 17 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 1050 | 220 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 442 | 0 | 140 | 1166 | 0 | 0 |  | 6113 | 4729 | 10842 | 3232 | 881 | 1584 | 0 | 1331 | 3494 | 132 | 0 | 66 | 122 | 0 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 340 | 150 |  | 0 | 225 | 157 | 35 | 22 | 15 | 224 | 0 | 0 | 37 | 24 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 18 | 19 | 12 | 25 | 25 | 8 | 0 | 92 | 40 | 0 | 0 | 17 | 141 | 0 | 0 | 0 |  | 6 | 16 | 17 | 12 | 0 | 26 | 12 | 2 | 0 | 0 | 0 | 280 | 240 | 170 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 16 | 10 | 25 | 12 | 122 | 95 | 0 | 16 | 0 | 42 | 0 | 50 | 0 | 0 | 0 | 62 | 0 | 0 | 204 | 18 | 0 | 10 | 285 | 16 | 5 | 0 | 0 | 0 | 0 | 25 | 0 | 56 | 0 | 12 | 17 | 6 | 402 | 45 | 0 | 17 | 0 | 249 | 17 | 17 | 17 | 58 | 12 | 260 | 71 | 0 | 17 | 17 | 0 | 17 | 0 | 96 | 17 | 230 | 17 | 0 | 325 | 0 | 201 | 0 | 0 |  | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 17 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1040 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 448 | 0 | 140 | 1165 | 0 | 0 |  | 6029 | 4700 | 10729 | 3240 | 916 | 1598 | 0 | 1166 | 3489 | 132 | 0 | 66 | 122 | 0 | 0 | 0 | 100
21:00 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 340 | 152 |  | 0 | 225 | 157 | 0 | 14 | 15 | 224 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 18 | 19 | 12 | 25 | 25 | 8 | 0 | 92 | 40 | 0 | 0 | 17 | 131 | 0 | 0 | 0 |  | 6 | 16 | 17 | 12 | 0 | 26 | 10 | 2 | 0 | 0 | 0 | 280 | 240 | 170 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 16 | 10 | 33 | 12 | 126 | 95 | 0 | 18 | 0 | 42 | 0 | 50 | 0 | 0 | 0 | 62 | 0 | 0 | 204 | 18 | 0 | 10 | 295 | 16 | 5 | 0 | 0 | 0 | 0 | 25 | 0 | 53 | 0 | 12 | 17 | 0 | 402 | 45 | 17 | 17 | 0 | 124 | 17 | 17 | 17 | 58 | 12 | 260 | 71 | 0 | 0 | 17 | 0 | 17 | 0 | 75 | 17 | 230 | 17 | 0 | 325 | 0 | 202 | 0 | 0 |  | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1060 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 452 | 0 | 140 | 1167 | 0 | 0 |  | 5793 | 4739 | 10532 | 3238 | 917 | 1674 | 0 | 863 | 3516 | 132 | 0 | 66 | 126 | 0 | 0 | 0 | 99.99
22:00 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 339 | 153 |  | 0 | 225 | 158 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 18 | 19 | 12 | 25 | 25 | 0 | 0 | 92 | 40 | 0 | 0 | 17 | 131 | 0 | 0 | 0 |  | 0 | 16 | 17 | 12 | 0 | 26 | 10 | 12 | 0 | 0 | 0 | 280 | 240 | 170 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 16 | 10 | 33 | 12 | 124 | 95 | 0 | 18 | 0 | 42 | 0 | 50 | 0 | 0 | 0 | 62 | 0 | 0 | 204 | 18 | 0 | 10 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 35 | 0 | 12 | 17 | 0 | 402 | 28 | 0 | 17 | 0 | 123 | 17 | 17 | 0 | 58 | 12 | 260 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 72 | 0 | 230 | 17 | 0 | 312 | 0 | 203 | 0 | 0 |  | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 940 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 140 | 1061 | 0 | 0 |  | 5464 | 4477 | 9941 | 3241 | 918 | 1670 | 0 | 530 | 3276 | 132 | 0 | 50 | 124 | 0 | 0 | 0 | 99.98
23:00 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 340 | 153 |  | 0 | 225 | 157 | 0 | 0 | 0 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 25 | 0 | 0 | 92 | 40 | 0 | 0 | 8 | 131 | 0 | 0 | 0 |  | 0 | 16 | 0 | 12 | 0 | 26 | 10 | 12 | 0 | 0 | 0 | 280 | 240 | 170 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 16 | 10 | 33 | 12 | 122 | 98 | 0 | 18 | 0 | 42 | 0 | 50 | 0 | 0 | 0 | 60 | 0 | 0 | 204 | 18 | 0 | 10 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 12 | 17 | 0 | 402 | 25 | 0 | 17 | 0 | 124 | 17 | 17 | 0 | 51 | 12 | 260 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 35 | 0 | 230 | 0 | 0 | 300 | 0 | 204 | 0 | 0 |  | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 880 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 452 | 0 | 140 | 1001 | 0 | 0 |  | 5334 | 4294 | 9628 | 3246 | 917 | 1615 | 0 | 433 | 3147 | 132 | 0 | 16 | 122 | 0 | 0 | 0 | 99.97
24:00 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 339 | 151 |  | 0 | 225 | 158 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 25 | 0 | 0 | 92 | 40 | 0 | 0 | 8 | 131 | 0 | 0 | 0 |  | 0 | 16 | 0 | 12 | 0 | 6 | 10 | 14 | 0 | 0 | 0 | 280 | 240 | 164 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 16 | 10 | 33 | 12 | 114 | 99 | 0 | 0 | 0 | 42 | 0 | 50 | 0 | 0 | 0 | 62 | 0 | 0 | 204 | 18 | 0 | 10 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 12 | 17 | 0 | 401 | 16 | 0 | 17 | 0 | 80 | 17 | 17 | 0 | 9 | 12 | 260 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 18 | 0 | 230 | 0 | 0 | 300 | 2 | 202 | 0 | 0 |  | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 140 | 1017 | 0 | 0 |  | 5156 | 4176 | 9332 | 3222 | 917 | 1605 | 0 | 293 | 3031 | 132 | 0 | 16 | 114 | 0 | 2 | 0 | 99.96
KWH | 0 | 0 | 0 | 4252500 | 0 | 986909 | 0 | 8144890 | 4426000 |  | 0 | 4417300 | 3273862 | 109440 | 224495 | 155541 | 5581893 | 0 | 0 | 238080 | 293472 | 201600 | 36992 | 0 | 0 | 0 | 115920 | 134564 | 140690 | 239328 | 456000 | 279000 | 628900 | 614200 | 82080 | 0 | 2200800 | 812000 | 0 | 0 | 105269 | 3171935 | 0 | 0 | 0 |  | 79440 | 108432 | 195009 | 168120 | 0 | 340800 | 210816 | 370080 | 0 | 0 | 0 | 7283500 | 6140000 | 4142000 | 0 | 0 | 0 | 0 | 0 | 742532 | 0 | 0 | 93413 | 262332 | 178380 | 596800 | 278500 | 2749440 | 2229120 | 0 | 174096 | 13500 | 994000 | 0 | 616200 | 0 | 0 | 0 | 1164864 | 0 | 0 | 5117740 | 298000 | 0 | 171720 | 6994000 | 258480 | 89134 | 0 | 373855 | 0 | 0 | 352800 | 0 | 536256 | 135000 | 206400 | 169440 | 259272 | 8982000 | 538800 | 14400 | 387236 | 27242 | 1944545 | 228523 | 409817 | 79800 | 462000 | 189120 | 5698700 | 514560 | 273190 | 129600 | 270982 | 0 | 120240 | 206015 | 693120 | 123480 | 5886200 | 167272 | 0 | 7641817 | 53760 | 4952727 | 0 | 0 |  | 20078545 | 0 | 0 | 0 | 16320 | 0 | 0 | 0 | 0 | 0 | 0 | 2484000 | 433300 | 27264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211392 | 0 | 0 | 4132100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7760618 | 89760 | 0 | 145824 | 54144 | 162096 | 0 | 38385 | 62112 | 19264200 | 4962355 | 0 | 121200 | 34140 | 455040 | 125952 | 0 | 0 | 9338182 | 215865 | 3437300 | 22450909 | 1182410 | 0 |  | 125412277 | 97283413 | 222695690 | 76048700 | 20078545 | 35154876 | 0 | 11127234 | 71217235 | 3012800 | 0 | 672313 | 2749440 | 2580787 | 53760 | 0
Fuel Cost | 0 | 0 | 0 | 6336225 | 0 | 1312588.97 | 0 | 8552134.5 | 4780080 |  | 0 | 4814857 | 3633986.82 | 1223539.2 | 2974558.75 | 2060918.25 | 6251720.16 | 0 | 0 | 3480729.6 | 4129151.04 | 3267936 | 341066.24 | 0 | 0 | 0 | 1474502.4 | 1816614 | 1886652.9 | 179496 | 342000 | 0 | 0 | 0 | 1396180.8 | 0 | 594216 | 219240 | 0 | 0 | 1721148.15 | 3298812.4 | 0 | 0 | 0 |  | 1036692 | 1808645.76 | 3319053.18 | 2271301.2 | 0 | 3943056 | 267736.32 | 1232366.4 | 0 | 0 | 0 | 8084685 | 6692600 | 4804720 | 0 | 0 | 0 | 0 | 0 | 1240028.44 | 0 | 0 | 1256404.85 | 359394.84 | 133785 | 1044400 | 208875 | 19740979.2 | 2429740.8 | 0 | 236770.56 | 215190 | 1361780 | 0 | 1072188 | 0 | 0 | 0 | 2259836.16 | 0 | 0 | 5168917.4 | 640700 | 0 | 340005.6 | 6994000 | 193860 | 67741.84 | 0 | 5103120.75 | 0 | 0 | 4755744 | 0 | 7427145.6 | 1578150 | 2130048 | 2314550.4 | 3440539.44 | 8263440 | 6551808 | 208224 | 4898535.4 | 423885.52 | 22828958.3 | 2488615.47 | 4356354.71 | 1082886 | 5955180 | 2227833.6 | 5242804 | 6663552 | 3947595.5 | 1644624 | 3083775.16 | 0 | 1570334.4 | 2461879.25 | 10376006.4 | 1626231.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 60235635 | 0 | 0 | 0 | 169891.2 | 0 | 0 | 0 | 0 | 0 | 0 | 2782080 | 840602 | 297177.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160023.744 | 0 | 0 | 35040208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7683011.82 | 1206374.4 | 0 | 1725097.92 | 782380.8 | 2058619.2 | 0 | 424154.25 | 754039.68 | 159892860 | 5061602.1 | 0 | 896880 | 386123.4 | 5337619.2 | 1930844.16 | 0 | 0 | 84884074.38 | 0 | 41144481 | 191955271.95 | 0 | 0 |  | 267165629.23 | 605649051.804 | 872814681.034 | 75364278.724 | 60235635 | 39005317.15 | 0 | 141567887.57 | 512916895.33 | 813456 | 0 | 8395634.94 | 19740979.2 | 14774597.12 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 170 | 0 | 51 | 0 | 355 | 167 |  | 0 | 225 | 138 | 0 | 0 | 0 | 251 | 0 | 0 | 1 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 19 | 11 | 25 | 25 | 0 | 0 | 92 | 40 | 0 | 0 | 0 | 141 | 0 | 0 | 0 |  | 6 | 0 | 17 | 12 | 0 | 24 | 12 | 0 | 0 | 0 | 0 | 275 | 240 | 186 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 15 | 10 | 33 | 6 | 124 | 97 | 0 | 0 | 2 | 43 | 0 | 42 | 0 | 0 | 0 | 58 | 0 | 0 | 202 | 16 | 0 | 10 | 300 | 0 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 20 | 12 | 0 | 0 | 403 | 8 | 0 | 24 | 4 | 85 | 5 | 35 | 0 | 0 | 12 | 250 | 2 | 49 | 0 | 17 | 0 | 0 | 31 | 4 | 0 | 230 | 15 | 0 | 312 | 0 | 204 | 0 | 0 |  | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 590 | 220 | 0 | 0 | 5 | 72 | 0 | 0 | 0 | 345 | 34 | 140 | 922 | 183 | 0 |  | 9414 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 334 | 154 |  | 0 | 225 | 152 | 20 | 34 | 25 | 224 | 0 | 0 | 50 | 91 | 32 | 25 | 0 | 0 | 0 | 17 | 35 | 55 | 14 | 19 | 11 | 25 | 25 | 18 | 0 | 92 | 40 | 0 | 0 | 16 | 141 | 0 | 0 | 0 | 0 | 6 | 16 | 17 | 12 | 0 | 26 | 12 | 0 | 0 | 0 | 0 | 280 | 240 | 158 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 28 | 16 | 10 | 33 | 12 | 130 | 99 | 0 | 18 | 0 | 42 | 0 | 50 | 0 | 0 | 0 | 62 | 0 | 0 | 205 | 17 | 0 | 10 | 285 | 16 | 5 | 0 | 49 | 0 | 0 | 93 | 0 | 51 | 0 | 12 | 17 | 60 | 402 | 85 | 0 | 17 | 0 | 240 | 17 | 19 | 17 | 57 | 12 | 260 | 51 | 0 | 35 | 17 | 0 | 17 | 0 | 88 | 35 | 230 | 17 | 0 | 325 | 3 | 201 | 0 | 0 |  | 912 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 23 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 13 | 0 | 45 | 32 | 34 | 0 | 0 | 35 | 900 | 220 | 0 | 54 | 0 | 0 | 35 | 0 | 0 | 455 | 0 | 140 | 1155 | 0 | 0 |  | 11207 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 400 | 150 |  | 0 | 225 | 150 | 50 | 95 | 15 | 260 | 0 | 0 | 50 | 91 | 132 | 50 | 0 | 0 | 0 | 17 | 35 | 55 | 18 | 19 | 12 | 33 | 25 | 25 | 0 | 92 | 40 | 0 | 0 | 17 | 141 | 0 | 0 | 0 |  | 6 | 17 | 17 | 12 | 0 | 26 | 12 | 30 | 0 | 0 | 0 | 280 | 280 | 190 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 140 | 100 | 0 | 18 | 0 | 42 | 0 | 50 | 0 | 0 | 0 | 62 | 0 | 0 | 205 | 17 | 0 | 10 | 300 | 16 | 2 | 0 | 130 | 0 | 0 | 100 | 0 | 80 | 0 | 12 | 17 | 140 | 400 | 85 | 105 | 17 | 0 | 260 | 17 | 19 | 52 | 58 | 12 | 260 | 51 | 0 | 35 | 34 | 0 | 17 | 0 | 95 | 35 | 300 | 17 | 0 | 325 | 10 | 300 | 0 | 0 |  | 801 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 50 | 75 | 0 | 130 | 25 | 110 | 0 | 0 | 0 | 35 | 20 | 85 | 28 | 42 | 40 | 52 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 83 | 0 | 50 | 32 | 113 | 0 | 0 | 55 | 1244 | 220 | 0 | 150 | 0 | 0 | 75 | 0 | 0 | 570 | 0 | 185 | 1300 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 395 | 150 | 0 | 0 | 225 | 150 | 8 | 95 | 15 | 260 | 0 | 0 | 17 | 91 | 16 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 33 | 25 | 8 | 0 | 92 | 40 | 0 | 0 | 8 | 141 |  | 0 | 0 | 0 | 6 | 8 | 0 | 12 | 0 | 6 | 12 | 20 | 0 | 0 | 0 | 280 | 280 | 180 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 10 | 33 | 12 | 128 | 100 | 0 | 18 | 1.6 | 42 | 0 | 45 | 0 | 0 | 0 | 60 | 0 | 0 | 205 | 17 | 0 | 10 | 290 | 16 | 2 | 0 | 80 | 0 | 0 | 84 | 0 | 17 | 20 | 12 | 17 | 12 | 400 | 40 | 0 | 17 | 5 | 100 | 17 | 17 | 17 | 28 | 12 | 230 | 17 | 50 | 17 | 17 | 0 | 17 | 35 | 34 | 17 | 300 | 17 |  | 325 | 10 | 300 | 0 | 0 |  | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 28 | 34 | 30 | 8 | 24 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 50 | 0 | 35 | 15 | 34 | 0 | 8 | 35 | 1244 | 220 |  | 38 | 6 | 100 | 70 | 0 |  | 400 | 30 | 140 | 1200 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 63 | 0 | 354 | 152 | 0 | 0 | 225 | 148 | 0 | 0 | 0 | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 25 | 0 | 0 | 92 | 40 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 10 | 0 | 0 | 0 | 0 | 35 | 310 | 184 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 16 | 10 | 33 | 5 | 100 | 69 | 0 | 0 | 0 | 42 | 0 | 10 | 0 | 0 | 0 | 40 | 0 | 0 | 203 | 17 | 0 | 10 | 275 | 16 | 5 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 10 | 10 | 0 | 0 | 377 | 47 | 0 | 11 | 2 | 70 | 0 | 0 | 0 | 0 | 12 | 90 | 0 | 14 | 0 | 0 | 0 | 0 | 13 | 0 | 17 | 350 | 0 | 0 | 303 | 0 | 348 | 0 | 0 | 0 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 670 | 180 | 0 | 0 | 2 | 27 | 0 | 0 | 0 | 401 | 0 | 140 | 1010 | 68 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
[22 empty] | 299565 | [26 empty] | 399366 | 399587 | [8 empty] | 299280 | [26 empty] | 299755 | [12 empty] | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 |  | 399747 |  |  |  |  | 399575 | 399337 | 399589 | 299230 | [7 empty] | 399245 |  | 299282 | 399274 |  | 399223 |  | 399630 | [12 empty] | 599468 | [32 empty] | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 | [8 empty] | 599726 | [9 empty] | 292.3904
| Minimum Generation |  | 7369 | 5:00 | [202 empty] | 111203576
| Highest Generation |  | 11207 | 18:00 | [202 empty] | 111.2036 |  |  |  |  | 2.5808
| Day Peak Generation |  | 9414 | 12:00 | [202 empty] | 11799547
| Evening Peak Generation |  | 11207 | 18:00 | [202 empty] | 11.7995 |  |  | 35154876 |  | 3.0128
| HVDC Max Flow |  | 918 | 22:00 | [202 empty] | 20.0785 |  |  |  |  | 0.05376
| HVDC EvPeak Flow |  | 912 | 18:00 | [200 empty] | 222695690 |  | 2.7494 |  | 71.2172
| Load factor L.F |  | 82.8% | [166 empty] | 1275.5 | [36 empty] | 222.6957

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-11-12
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-11-11 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9414 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 7754
Evening Peak Generation : |  |  | 11207 | MW Hour : | 18:00 | Available Max Generation : |  | 13667
E.P. Demand (at gen end) : |  |  | 11207 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 11800
Maximum Generation : |  |  | 11207 | MW Hour : | 18:00 | Reserve(Generation end) |  | 1867
Total Gen. (MKWH) : |  |  | 222.6957 | System Load Factor : | 82.8% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 350 | MW at | 19:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-11-12
Actual : |  | 99.9 | Ft.(MSL) , | Rule curve : | 107.9 | Ft.( MSL )
Gas Consumed : |  | Total = | 870.73 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 114369595.874
: |  |  | Coal : | 512916895.33 | Oil : | 149963522.51 | Total : | 777250013.714
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4307.9931 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1182.1376 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1655.4666 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1438.4608 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1183.8221 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 880.2349 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 493.6451 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 411.1693 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 804.1802 |  |  | 0 | 0%
Total |  | 0 |  | 12357.1096 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:05 | 15:49 | Jashore 132/33kV S/S JH-1(L2) Scheduled S/D Due to Annual Maintanance
08:06 | 16:07 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-1 Scheduled S/D Due to Annual Maintenance
08:20 | 17:16 | Natore-Rajshahi 132kV Ckt-2 Scheduled S/D from Rajshahi 132/33kV end Due to Annual Maintenance and from Natore
132/33kV end Due to Yearly maintenance work.
08:21 | 15:30 | Gallamari- Khulna (S) 132kV Ckt-2 Scheduled S/D from Gollamari 132/33kV end Due to Annual Maintenance.
08:23 | 17:41 | Ishurdi-Pabna 132kV ckt Scheduled S/D from Pabna 132/33kV end Due to annual maintenence and from Ishurdi 132/33kV end
Due to A/M
08:23 | 16:39 | Amnura 132/33kV S/S T-3 (426T) HT Scheduled S/D Due to Annual maintenance
08:26 | 16:57 | Rangpur-Saidpur 132kV Ckt-1 Scheduled S/D from Saidpur 132/33kV end Due to Annual Maintenance and from Rangpur
132/33kV end Due to Annual Maintenances
08:27 | 15:07 | Tangail 132/33kV S/S Tr-1 HT Scheduled S/D Due to Annual Maintenance
08:27 | 15:08 | Tangail 132/33kV S/S Tr-1 LT Scheduled S/D Due to Annual Maintenance
08:28 |  | Amnura 132/33kV S/S T-3 (426T) LT Scheduled S/D Due to Annual maintenance
08:30 | 12:20 | Jamalpur 132/33kV S/S Bus-B Scheduled S/D Due to Annual maintenance
08:42 | 16:32 | Brahmanbaria 132/33kV S/S 401T LT Scheduled S/D Due to Annual maintenance
08:42 | 16:32 | Brahmanbaria 132/33kV S/S 401T HT Scheduled S/D Due to Annual maintenance
08:44 | 20:27 | Shyampur 230/132kV S/S Auto TR-1 LT Scheduled S/D Due to Annual maintenance
08:46 | 16:21 | Ashuganj-Sreepur 230 kV Ckt-1 Scheduled S/D from Ashuganj 230/132/33kV end Due to Annual maintenance work
08:48 | 13:40 | Kulaura 132/33kV S/S TR-1 HT Scheduled S/D Due to Annual maintenance
08:48 | 13:44 | Kulaura 132/33kV S/S TR-1 LT Scheduled S/D Due to Annual maintenance
08:51 | 16:01 | Ashuganj-Cumilla(N) 230 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to annual maintenance and
from Ashuganj 230/132/33kV end Due to Annual maintenance
09:03 | 14:54 | Rajendrapur 132/33kV S/S MTR-1 LT Scheduled S/D Due to
09:05 | 10:01 | Saidpur 132/33kV S/S BUS B Scheduled S/D Due to For 132kv RNP CKT-1 'B' Bus DS Maintenance.
09:05 | 14:52 | Rajendrapur 132/33kV S/S MTR-1 HT Scheduled S/D Due to Annual maintenance
09:05 | 11:14 | Kabirpur 132/33kV S/S XFR, T-3 HT Forced S/D Due to Shutdown taken by DPBS-1 due to 33 kV Radio feeder fault.
09:10 | 17:16 | Madanganj 132/33kV S/S GT-1 LT Scheduled S/D
09:14 | 17:08 | Madanganj 132/33kV S/S GT-1 HT Scheduled S/D
09:25 | 20:29 | Shyampur 230/132kV S/S Aux TR-1 LT Scheduled S/D Due to Annual maintenance
09:27 | 16:16 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-1 Scheduled S/D Due to Annual maintenance
09:27 | 20:26 | Shyampur 230/132kV S/S Auto TR-1 HT Scheduled S/D Due to Annual maintenance
09:29 | 20:29 | Shyampur 230/132kV S/S Aux TR-1 HT Scheduled S/D Due to Annual maintenance
09:39 |  | Gopalganj(N)-Rampal Ckt-2 Project Work S/D from Rampal 400/230kV end Due to NLDC REQUIREMENT.
12:00 |  | Day peak Generation : 9414 MW
12:25 | 15:25 | Jamalpur 132/33kV S/S Bus-A Scheduled S/D Due to Annual maintenance
| 15:40 | Khulna (C) S/S TR-1 425T HT is restored.
| 15:45 | Khulna (C) S/S TR-1 425T LT is restored.
| 16:57 | Rangpur-Saidpur 132kV Ckt-1 is restored.
| 17:15 | Mymensingh-Netrokona 132kV Ckt-2 is restored.
| 17:30 | Barishal 230/132kV S/S T-4 HT is restored.
| 17:31 | Hasnabad 132/33kV S/S 132/33kV 414 T-2 LT is restored.
| 17:31 | Hasnabad 132/33kV S/S 132/33kV 414 T-2 HT is restored.
| 17:32 | Barishal 230/132kV S/S T-4 LT is restored.
18:00 |  | Evening Peak Generation = 11207 MW.
18:02 |  | Lalbagh 132/33kV GT-2 transformer was switched on.
| 18:04 | Barishal 132/33kV S/S 132 kV Capacitor Bank is restored.
05:00 |  | Min. Gen. 7754 MW
05:49 |  | Ashuganj (N) CCPP ST was shut down due to generator bearing vibration high
06:10 | 07:35 | Dohazari 132/33kV S/S Power Transformer -T-2 HT Scheduled S/D Due to Redhot Maintenance by Keranihat PBS |  |  |  |  | 30.0MW Load interrup.
06:10 | 07:35 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Scheduled S/D Due to Redhot Maintenance by Keranihat PBS |  |  |  |  | 30.0MW Load interrup.
06:43 |  | Hasnabad 132/33kV S/S 132/33kV 414 T-2 LT Scheduled S/D Due
06:43 |  | Hasnabad 132/33kV S/S 132/33kV 414 T-2 HT Scheduled S/D Due
07:28 |  | Bagerhat-Mongla 132 kV Ckt-2 Scheduled S/D from Bagerhat 132/33kV end Due to Annual maintenance work and from Mongla
132/33kV end Due to Annual maintenance
07:42 |  | Khulna(S) 230/132kV S/S TR-1 LT Scheduled S/D Due to Annual maintenance
07:43 |  | Khulna(S) 230/132kV S/S TR-1 HT Scheduled S/D Due to Annual maintenance
07:48 |  | Barishal 230/132kV S/S T-4 LT Scheduled S/D Due to Annual maintenance
07:49 |  | Barishal 230/132kV S/S T-4 HT Scheduled S/D Due to Annual maintenance
07:53 |  | Jashore 132/33kV S/S JH-1(L2) Scheduled S/D Due to Annual maintenance
07:53 |  | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-1 Scheduled S/D Due to Annual maintenance
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-11-11 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4252500 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 74 | 986909 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 334 | 8144890 | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 154 | 4426000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4417300 | GT-1 under S/D due to gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 20 | 109440 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 152 | 3273862 | GT-1 under S/D due to gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 34 | 224495 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 25 | 155541 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 25 | 36992 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 14 | 239328 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 50 | 238080 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 224 | 5581893 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 91 | 293472 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 115920 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 201600 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 134564 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 140690
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 30 | 735000 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 628900
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 614200 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 18 | 82080 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 49 | 373855 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 51 | 536256 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 14400 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 51 | 514560 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 129600 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 206015
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 123480 | Fuel shortage
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5422 | 2060 | 36931822
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 16 | 105269 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 135000
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 26 | 340800 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 132 | 3012800 | Unit-2 under maint.
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 141 | 3171935
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 387236 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 16 | 108432 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 195009 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 12 | 168120 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 206400 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 12 | 210816 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 0 | 370080
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27242
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 240 | 1944545 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 228523 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 19 | 409817 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 189120 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 270982 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 17 | 167272 | Fuel shortage
| SS Power I |  | SS Power | 1*612 | 612 | 325 | 7641817 | Machine problem
| Cox's Bazar Wind |  | IPP | 66 | 0 | 3 | 53760 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 201 | 4952727 | On test.
| Chattogram area Total |  |  |  | 3157 | 1252 | 24297702
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 158 | 4142000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7283500 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 240 | 6140000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 230 | 5886200 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 0 | 0 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 742532
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 60 | 259272 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Under maint.
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 169440 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 262332 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 178380
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 130 | 2749440
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 596800
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 28 | 93413 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 12 | 278500 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 79800 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 57 | 462000 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 120240 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 88 | 693120 | Fuel shortage
| Cumilla Area Total |  |  |  | 2896 | 1444 | 30136969
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 99 | 2229120 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 174096 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13500
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 93 | 352800 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 85 | 538800 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 273190
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 79440 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 301 | 3660946
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 42 | 994000 | Under maint.
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 616200
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 89134 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1164864
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 0 | 0 | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 205 | 5117740 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 298000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 258480 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 6994000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 402 | 8982000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 171720
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 260 | 5698700 | ST U/M
| Sylhet Area Total |  |  |  | 2427 | 1354 | 30384838
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 912 | 20078545
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 16320 | High voltage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 13 | 89760 | High voltage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 32 | 54144 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 455040
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 455 | 9338182
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 1428 | 30031991
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 12 | 27264 | Low demand
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 23 | 433300 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 120 | 2484000 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 900 | 19264200
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4962355
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 121200 | High voltage
| Barisal 307 MW |  | IPP | 307*1 | 307 | 140 | 3437300 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1469 | 30729619
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 7760618
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 211392
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 45 | 145824 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 62112 | Low demand
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 34140
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1155 | 22450909
| Rajshahi Area Total |  |  |  | 3631 | 1660 | 30664995
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4132100 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 162096 | Low demand
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 38385
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 35 | 125952 | Low demand
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 215865
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1182410
| Rangpur Area Total |  |  |  | 950 | 239 | 5856808
| Total |  |  |  | 24599 | 11207 | 222695690
| Eastern Grid Total |  |  |  | 14516 | 6411 | 125412277
| Western Grid Total |  |  |  | 10083 | 4796 | 97283413
| National Grid Total |  |  |  | 24599 | 11207 | 222695690
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-11-11
| (a) ENTIRE EASTERN GRID : |  | 7813.21 | MW | (b) ENTIRE WESTERN GRID : |  | 3180.6 | MW
| i) Dhaka area |  | 4348.61 | MW | i) Khulna area |  | 1197.8 | MW
| ii) Chittagong area |  | 1143.6 | MW | ii) Rajshahi area |  | 1005.8 | MW
| iii) Comilla area |  | 988 | MW | iii) Barisal area |  | 297 | MW
| iv) Mymensingh area |  | 896 | MW | iv) Rangpur area |  | 680 | MW
| v) Sylhet area |  | 437 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10993.81 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 24 | 18:00 | Kamrangirchar | 38.1 | 13:00 | Narinda | 73 | 13:00 | Sherpur | 108 | 18:00
2 | AKSML | 100 | 14:00 | Chowmuhani | 142 | 18:00 | Kaptai | N/A | N/A | Narshingdi | 151 | 19:30 | Shikalbaha | 23 | 18:30
3 | Aftabnagar | 30 | 18:00 | Chuadanga | 73 | 18:00 | Kazla | 88 | 19:00 | Natore | 99 | 18:00 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 84 | 00:00 | Coxsbazar | 107 | 18:30 | Keranigonj | 60 | 18:00 | Nawabganj | 28.2 | 18:00 | Shitalakhya | 93.3 | 12:00
5 | Agrabad | 58 | 18:00 | Cumilla(N) | 114 | 18:00 | Khagrachori | 28 | 18:00 | Netrakona | 98 | 18:00 | Sholosohor | 39 | 15:00
6 | Amnura | 36 | 18:00 | Cumilla(S) | 134 | 15:00 | Khulna | 68 | 18:30 | New | 45.4 | 12:00 | Shyampur | 152 | 09:00
7 | Ashuganj | 52 | 00:00 | Daudkandi | 116 | 18:00 | Khulshi | 164 | 19:30 | Niamatpur | 51 | 18:00 | Siddhirganj | 110 | 18:00
8 | BIPTC | N/A | N/A | Dhaka | 24 | 12:00 | Kishoreganj | 118 | 18:00 | Noapara | 37 | 18:00 | Sirajganj | 75 | 18:30
9 | BSRM | 131 | 16:00 | Dhamrai | 108 | 16:00 | Kodda | 254 | 18:30 | PHP | 3 | 03:00 | Sonargaon | 97 | 18:00
10 | Bagerhat | 68 | 18:00 | Dhanmondi | 123 | 13:00 | Kulaura | 34 | 18:00 | Pabna | 87 | 18:00 | Sreemongol | 52 | 18:00
11 | Bakulia | 83 | 18:30 | Dohazari | 62 | 19:00 | Kurigram | 51 | 18:00 | Palashbari | 82 | 18:00 | Sreepur | 56 | 18:00
12 | Banani | 24 | 15:00 | Faridpur | 108 | 18:00 | Kushtia | 102 | 18:00 | Panchagarh | 41 | 18:00 | Srinagar | 30.35 | 21:00
13 | Bangabhaban | 6 | 11:00 | Fatullah | 64 | 12:00 | Lalbag | 72 | 21:00 | Patuakhali | 70 | 21:00 | Sunamganj | 39 | 18:00
14 | Barapukuria | 46 | 18:00 | Fenchuganj | 28 | 18:00 | Lalmonirhat | 34 | 18:00 | Payra | 14 | 00:00 | Sylhet | 16 | 18:00
15 | Barguna | 14 | 21:00 | Feni | 94 | 18:00 | MI_Cement | 19 | 00:00 | Postogola | 51 | 13:00 | Sylhet-132 | 104 | 18:00
16 | Barishal | 79 | 13:00 | GPH | 95 | 18:30 | Madanganj | 30 | 18:00 | Purbachal | 17 | 15:00 | TK | 23 | 19:00
17 | Barishal-230 | 62 | 18:00 | Ghorashal | 53 | 14:00 | Madaripur | 65 | 21:00 | Purbasadipur | 88 | 18:00 | Tangail | 172 | 18:00
18 | Baroaulia | 56 | 02:00 | Goalpara | 26 | 07:00 | Madartek | 74.29 | 19:30 | Rahim | 45 | 12:00 | Thakurgaon | 66 | 18:00
19 | Baroirhat | 38 | 18:00 | Gollamari | 42 | 13:00 | Madunaghat | 31 | 18:00 | Rajbari | 48 | 18:00 | Tongi | 112 | 15:00
20 | Bashundhara | 126 | 13:00 | Gopalganj | 77.8 | 18:00 | Magura | 44 | 18:00 | Rajendrapur | 100 | 18:00 | Ullon | 35 | 09:00
21 | BashundharaCement | 0 | 00:00 | Gulshan | 82 | 12:00 | Mahasthangarh | 50 | 18:00 | Rajshahi | 105 | 18:00 | Uttara | 55 | 18:00
22 | Beanibazar | 48 | 18:00 | Halishahar | 100 | 13:00 | Manikganj | 82 | 18:00 | Rajshahi-230 | 24 | 19:30 | UttaraNew | 45 | 18:00
23 | Benapole | 42 | 18:00 | HaripurSBU | 157 | 15:00 | Maniknagar | 60 | 13:00 | Ramganj | 88 | 20:00 | Zigatola | 87 | 18:30
24 | Bhaluka | 122 | 18:00 | Hasnabad | 82 | 18:00 | Matarbari | 17 | 19:00 | Rampur | 25 | 18:00
25 | Bhandaria | 38 | 21:00 | Hathazari | 64 | 18:30 | Matuail | 70.8 | 12:00 | Rangamati | 14 | 18:00
26 | Bhangura | 22 | 18:00 | Ishurdi | 59 | 18:00 | Millgate | 94 | 16:00 | Rangpur | 107 | 18:00
27 | Bheramara(GK) | 40 | 18:30 | Jaldhaka | 54 | 18:00 | Mirpur | 114 | 18:30 | Ruppur | 3.6 | 10:00
28 | Bhulta | 218 | 19:00 | Jamalpur | 119 | 18:00 | Mirsorai | 5 | 16:00 | SSM | 14 | 01:00
29 | Bog-Sherpur | 48 | 18:00 | Jashore | 103 | 13:00 | Mirzapur | 0 | 00:00 | Saidpur | 81 | 18:00
30 | Bogura | 121 | 19:00 | Jhenaidah | 91 | 18:30 | Mithapukur | 30 | 18:00 | Satkhira | 89 | 18:00
31 | Borhanuddin | 33 | 21:00 | Joydebpur | 137 | 18:00 | Modern | 0 | 00:00 | Satmasjid | 79 | 13:00
32 | Brahmanbaria | 124 | 18:00 | Joypurhat | 37 | 19:30 | Mogbazar | 92.9 | 13:00 | Savar | 152 | 18:00
33 | Cantonment | 112 | 18:00 | Juldah | 22 | 11:00 | Mongla | 26 | 12:00 | SevenRings | 7.3 | 04:00
34 | Chandpur | 52 | 18:00 | KSRM | 30 | 08:00 | Motijheel | 29 | 16:00 | ShahCement | 36 | 06:00
35 | Chandraghona | 24 | 18:00 | Kabirpur | 243 | 16:00 | Munshiganj | 78 | 13:00 | Shahjadpur | 70 | 18:30
36 | Chapai | 48 | 12:00 | Kachua | 40 | 18:00 | Mymensingh | 159 | 18:00 | Shahjibazar | 92 | 18:00
37 | Charsaidpur | 16 | 00:00 | Kallyanpur | 84 | 18:00 | Naogaon | 87 | 18:00 | Shahmirpur | 36 | 15:00
38 | Chauddagram | 41 | 18:00 | Kalurghat | 32 | 12:00 | Narail | 36 | 18:00 | Shariatpur | 52 | 14:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-11-11 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 403 | 06:00 | 41 | 17:00 | Gopalganj | 411 | 06:00 | 397 | 12:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 387 | 05:00 | 373 | 12:00
| Bhulta | 403 | 03:00 | 391 | 12:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 404 | 02:00 | 397 | 12:00 | Payra | 417 | 01:00 | 411 | 12:00
| BIPTC | 405 | 04:00 | 393 | 18:00 | Rahanpur | 414 | 02:00 | 401 | 18:30
| Bogura | N/A | N/A | N/A | N/A | Rampal | 413 | 03:00 | 400 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 238 | 06:00 | 227 | 16:00 | Hasnabad | 237 | 01:00 | 230 | 13:00
| AKSML | 227 | 18:00 | 216 | 04:00 | Hathazari | 229 | 19:00 | 220 | 12:00
| Aminbazar | 239 | 01:00 | 230 | 13:00 | Ishurdi | 236 | 01:00 | 224 | 11:00
| Ashuganj | 238 | 01:00 | 230 | 12:00 | Jhenaidah | 232 | 02:00 | 220 | 11:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 238 | 01:00 | 230 | 15:00
| Baghabari | 229 | 00:00 | 220 | 11:00 | Keranigonj | 237 | 06:00 | 227 | 12:00
| Barapukuria | 226 | 01:00 | 217 | 18:00 | Khulna(S) | 240 | 03:00 | 229 | 12:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 242 | 06:00 | 234 | 11:00 | Maniknagar | 237 | 02:00 | 228 | 12:00
| Bheramara | 235 | 01:00 | 222 | 11:00 | Meghnaghat | 242 | 00:00 | 239 | 07:00
| Bhulta | 240 | 03:00 | 230 | 12:00 | Mirsorai | 230 | 09:00 | 219 | 16:00
| Bibiana | 232 | 02:00 | 226 | 12:00 | Rajshahi | 236 | 02:00 | 221 | 11:00
| BIPTC | 237 | 01:00 | 222 | 11:00 | Rampal | 239 | 01:00 | 229 | 12:00
| Bogura | 235 | 01:00 | 227 | 13:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 244 | 06:00 | 240 | 08:00 | Rampura | 238 | 05:00 | 228 | 12:00
| BSRM | 230 | 18:00 | 220 | 03:00 | Shikalbaha | 225 | 18:30 | 212 | 04:00
| Cumilla(N) | 234 | 18:00 | 226 | 11:00 | Shyampur | 237 | 06:00 | 228 | 12:00
| Fenchuganj | 235 | 09:00 | 230 | 11:00 | Siddhirganj | 238 | 03:00 | 232 | 15:00
| Ghorashal | 240 | 00:00 | 240 | 00:00 | Sirajgonj | 239 | 00:00 | 232 | 12:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 234 | 06:00 | 226 | 12:00
| GPH | 227 | 18:00 | 215 | 03:00 | Tongi | 235 | 04:00 | 223 | 12:00
| Haripur | 236 | 03:00 | 228 | 12:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 138 | 01:00 | 130 | 12:00 | Lalbag | 137 | 06:00 | 130 | 11:00
| Agargaon | 138 | 06:00 | 131 | 12:00 | Lalmonirhat | 133 | 03:00 | 124 | 18:00
| Agrabad | 132 | 19:00 | 126 | 04:00 | Madanganj | 135 | 04:00 | 127 | 12:00
| AKS | 131 | 19:30 | 125 | 14:00 | Madaripur | 132 | 00:00 | 128 | 11:00
| Aminbazar | 140 | 02:00 | 132 | 15:00 | Madartek | 138 | 06:00 | 130 | 12:00
| Amnura | 138 | 01:00 | 130 | 11:00 | Madunaghat | 134 | 18:00 | 128 | 03:00
| Ashuganj | 142 | 07:00 | 139 | 12:00 | Magura | 141 | 00:00 | 132 | 12:00
| Bagerhat | 133 | 05:00 | 123 | 12:00 | Mahasthangarh | 137 | 00:00 | 130 | 12:00
| Bakulia | 134 | 19:00 | 128 | 04:00 | Manikganj | 132 | 09:00 | 125 | 15:00
| Banani | 138 | 01:00 | 129 | 11:00 | Maniknagar | 139 | 05:00 | 132 | 12:00
| Bangabhaban | 138 | 01:00 | 132 | 12:00 | Matarbari | 131 | 10:00 | 122 | 01:00
| Barapukuria | 140 | 01:00 | 132 | 18:00 | Matuail | 134.3 | 06:00 | 128 | 12:00
| Barguna | 136 | 09:00 | 131 | 20:00 | Millgate | 138 | 01:00 | 128 | 12:00
| Barishal | 137 | 04:00 | 127 | 21:00 | Mirpur | 138 | 05:00 | 129 | 12:00
| Barishal-230 | 137 | 00:00 | 132 | 12:00 | Mirzapur | 136 | 09:00 | 128 | 15:00
| Baroaulia | 134 | 19:00 | 126 | 04:00 | Mithapukur | 137 | 03:00 | 128 | 13:00
| Baroirhat | 132 | 20:00 | 124 | 03:00 | MI_Cement | 135.5 | 06:00 | 127 | 12:00
| Bashundhara | 139 | 03:00 | 130 | 11:00 | Modern | 133 | 19:00 | 127 | 02:00
| BashundharaCement | 135 | 04:00 | 127 | 12:00 | Mogbazar | 140 | 06:00 | 132 | 13:00
| Beanibazar | 129 | 00:00 | 127 | 11:00 | Mongla | 131 | 04:00 | 123 | 12:00
| Benapole | 139 | 04:00 | 125 | 12:00 | Motijheel | 138 | 01:00 | 132 | 12:00
| Bhaluka | 134 | 02:00 | 128 | 12:00 | Munshiganj | 135 | 04:00 | 127 | 12:00
| Bhandaria | 135 | 09:00 | 127 | 21:00 | Mymensingh | 138 | 09:00 | 126 | 12:00
| Bhangura | 142 | 01:00 | 124 | 00:00 | Naogaon | 135 | 01:00 | 127 | 12:00
| Bheramara | 137 | 01:00 | 130 | 11:00 | Narail | 141 | 04:00 | 133 | 18:00
| Bheramara(GK) | 137 | 01:00 | 130 | 11:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 124 | 05:00 | 118 | 11:00 | Narshingdi | 134 | 06:00 | 122 | 11:00
| Bog-Sherpur | 139 | 01:00 | 132 | 12:00 | Natore | 137 | 01:00 | 131 | 10:00
| Bogura | 139 | 03:00 | 133 | 12:00 | Nawabganj | 137 | 01:00 | 129 | 12:00
| Bogura-230 | 138 | 01:00 | 133 | 12:00 | Netrakona | 135 | 17:00 | 127 | 11:00
| Brahmanbaria | 129 | 05:00 | 124 | 12:00 | New | 138 | 03:00 | 129 | 12:00
| Cantonment | 138 | 06:00 | 130 | 12:00 | Niamatpur | 134 | 02:00 | 125 | 19:30
| Chandpur | 135 | 20:00 | 122 | 12:00 | Noapara | 137 | 05:00 | 126 | 13:00
| Chandraghona | 134 | 19:00 | 127 | 04:00 | Pabna | 139 | 01:00 | 129 | 11:00
| Chapai | 135 | 05:00 | 131 | 13:00 | Palashbari | 135 | 03:00 | 127 | 18:00
| Charsaidpur | 135 | 01:00 | 128 | 12:00 | Panchagarh | 132 | 02:00 | 120 | 13:00
| Chauddagram | 134 | 21:00 | 125 | 12:00 | Patuakhali | 136 | 17:00 | 131 | 20:00
| Chhatak | 130 | 07:00 | 127 | 12:00 | Payra | 136 | 06:00 | 133 | 12:00
| Chowmuhani | 131 | 19:30 | 123 | 11:00 | PHP | 132 | 19:30 | 124 | 02:00
| Chuadanga | 140 | 06:00 | 130 | 12:00 | Postogola | 137 | 01:00 | 129 | 12:00
| Coxsbazar | 127 | 09:00 | 122 | 00:00 | Purbachal | 139 | 01:00 | 129 | 12:00
| Cumilla(N) | 138 | 19:00 | 131 | 11:00 | Purbasadipur | 133 | 04:00 | 122 | 18:00
| Cumilla(S) | 137 | 19:00 | 126 | 13:00 | Rahanpur | 137 | 01:00 | 132 | 18:00
| Daudkandi | 130 | 06:00 | 124 | 12:00 | Rahim | 135 | 03:00 | 130 | 12:00
| Dhaka | 138 | 02:00 | 131 | 12:00 | Rajbari | 133 | 01:00 | 126 | 12:00
| Dhamrai | 136 | 01:00 | 128 | 16:00 | Rajendrapur | 131 | 10:00 | 124 | 16:00
| Dhanmondi | 135 | 05:00 | 127 | 12:00 | Rajshahi | 138 | 02:00 | 128 | 11:00
| Dohazari | 132 | 09:00 | 126 | 04:00 | Rajshahi-230 | 138 | 01:00 | 128 | 13:00
| Faridpur | 133 | 03:00 | 126 | 12:00 | Ramganj | 132 | 20:00 | 120 | 00:00
| Fatullah | 138 | 06:00 | 128 | 12:00 | Rampur | 132 | 19:00 | 125 | 05:00
| Fenchuganj | 133 | 07:00 | 130 | 11:00 | Rampura | 139 | 05:00 | 132 | 12:00
| Feni | 131 | 19:00 | 125 | 02:00 | Rangamati | 133 | 09:00 | 127 | 03:00
| Ghorashal | 142 | 00:00 | 137 | 12:00 | Rangpur | 136 | 03:00 | 125 | 18:00
| Goalpara | 135 | 01:00 | 127 | 11:00 | Ruppur | 139 | 00:00 | 134 | 10:00
| Gollamari | 134 | 01:00 | 126 | 12:00 | Saidpur | 135 | 06:00 | 125 | 18:00
| Gopalganj | 132 | 01:00 | 125 | 12:00 | Satkhira | 133 | 01:00 | 124 | 12:00
| Gopalganj-400 | 132 | 01:00 | 124 | 05:00 | Satmasjid | 137 | 06:00 | 131 | 12:00
| Gulshan | 138 | 01:00 | 132 | 12:00 | Savar | 142 | 19:30 | 129 | 12:00
| Halishahar | 133 | 19:00 | 126 | 12:00 | SevenRings | 144 | 06:00 | 136 | 12:00
| Haripur | 135 | 03:00 | 128 | 12:00 | ShahCement | 135 | 01:00 | 128 | 12:00
| HaripurSBU | 135 | 03:00 | 130 | 12:00 | Shahjadpur | 143 | 00:00 | 136 | 11:00
| Hasnabad | 136 | 01:00 | 129 | 12:00 | Shahjibazar | 129 | 05:00 | 125 | 16:00
| Hathazari | 135 | 18:30 | 128 | 12:00 | Shahmirpur | 133 | 08:00 | 128 | 00:00
| Ishurdi | 140 | 01:00 | 133 | 11:00 | Shariatpur | 133 | 03:00 | 126 | 12:00
| Jaldhaka | 135 | 03:00 | 123 | 18:00 | Sherpur | 136 | 18:30 | 120 | 12:00
| Jamalpur | 137 | 18:00 | 120 | 07:00 | Shikalbaha | 123 | 19:00 | 116 | 04:00
| Jashore | 139 | 15:00 | 124 | 12:00 | Shikalbaha-230 | 134 | 19:30 | 128 | 03:00
| Jhenaidah | 141 | 04:00 | 134 | 11:00 | Shitalakhya | 136 | 19:00 | 127 | 12:00
| Jhenaidah-230 | 143 | 01:00 | 135 | 11:00 | Sholosohor | 133 | 19:00 | 125 | 03:00
| Joydebpur | 142 | 05:00 | 134 | 11:00 | Shyampur | 138 | 05:00 | 125 | 22:00
| Joypurhat | 135 | 01:00 | 127 | 12:00 | Shyampur-230 | 138 | 06:00 | 129 | 12:00
| Juldah | 133 | 17:00 | 128 | 00:00 | Siddhirganj | 134 | 01:00 | 128 | 12:00
| Kabirpur | 136 | 07:00 | 124 | 16:00 | Sirajganj | 139 | 00:00 | 130 | 12:00
| Kachua | 135 | 18:00 | 124 | 02:00 | Sonargaon | 134 | 19:00 | 126 | 12:00
| Kaliakoir | 137 | 09:00 | 130 | 15:00 | Sreemongol | 130 | 03:00 | 126 | 11:00
| Kallyanpur | 138 | 01:00 | 131 | 12:00 | Sreepur | 134 | 00:00 | 128 | 12:00
| Kalurghat | 132 | 18:00 | 126 | 04:00 | Srinagar | 137 | 02:00 | 129 | 12:00
| Kamrangirchar | 137 | 01:00 | 128 | 12:00 | SSM | 136 | 19:00 | 131 | 04:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 128 | 07:00 | 124 | 18:00
| Kazla | 138 | 01:00 | 131 | 13:00 | Sylhet | 130 | 05:00 | 128 | 11:00
| Keranigonj | 137 | 05:00 | 130 | 12:00 | Sylhet-132 | 130 | 00:00 | 128 | 11:00
| Khagrachori | 133 | 09:00 | 127 | 03:00 | Tangail | 135 | 09:00 | 127 | 11:00
| Khulna | 133 | 03:00 | 126 | 12:00 | Thakurgaon | 132 | 02:00 | 121 | 12:00
| Khulna(S) | 134 | 01:00 | 127 | 12:00 | TK | 133 | 18:30 | 126 | 17:00
| Khulshi | 132 | 20:00 | 126 | 08:00 | Tongi | 139 | 04:00 | 131 | 12:00
| Kishoreganj | 138 | 02:00 | 134 | 12:00 | Ullon | 137 | 01:00 | 131 | 15:00
| Kodda | 140 | 01:00 | 121 | 16:00 | Uttara | 138 | 02:00 | 130 | 12:00
| KSRM | 133 | 19:00 | 127 | 03:00 | UttaraNew | 137 | 01:00 | 130 | 12:00
| Kulaura | 131 | 00:00 | 129 | 12:00 | Zigatola | 136 | 02:00 | 129 | 12:00
| Kurigram | 133 | 02:00 | 122 | 18:00
| Kushtia | 139 | 01:00 | 131 | 11:00

## L-Curve
Date | 2023-11-11
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 760 | 5156 | 4176 | 9332 |  |  |  | QF-LDC-11
0:30 | 865 | 4969.5 | 3885 | 8854.5 | Date: | 2023-11-11
1:00 | 970 | 4783 | 3594 | 8377
1:30 | 980 | 4657.5 | 3534 | 8191.5
2:00 | 990 | 4532 | 3474 | 8006
2:30 | 980 | 4381.5 | 3445 | 7826.5 | [5 empty] | Gen. at Eve. Peak | 11207 | 11207 MW (18:00 )
3:00 | 970 | 4231 | 3416 | 7647 | [6 empty] | 18:00
3:30 | 915 | 4225 | 3287 | 7512 | [5 empty] | Gen. at Day Peak | 9414 | 9414 MW (12:00 )
4:00 | 860 | 4219 | 3158 | 7377 | [6 empty] | 12:00
4:30 | 855 | 4255 | 3118 | 7373 | [5 empty] | Highest Generation | 11207
5:00 | 850 | 4291 | 3078 | 7369 | [6 empty] | 18:00
5:30 | 845 | 4341.5 | 3089.5 | 7431
6:00 | 840 | 4392 | 3101 | 7493
6:30 | 695 | 4572.5 | 3162 | 7734.5
7:00 | 550 | 4753 | 3223 | 7976
7:30 | 575 | 4766 | 3371 | 8137
8:00 | 600 | 4779 | 3519 | 8298
8:30 | 660 | 4741.5 | 3570 | 8311.5
9:00 | 720 | 4704 | 3621 | 8325
9:30 | 765 | 4747.5 | 3619 | 8366.5
10:00 | 810 | 4791 | 3617 | 8408
10:30 | 855 | 4905 | 3745 | 8650
11:00 | 900 | 5019 | 3873 | 8892
11:30 | 930 | 5133 | 4020 | 9153
12:00 | 960 | 5247 | 4167 | 9414
12:30 | 900 | 5344.5 | 4297 | 9641.5
13:00 | 840 | 5442 | 4427 | 9869
13:30 | 810 | 5495.5 | 4292 | 9787.5
14:00 | 780 | 5549 | 4157 | 9706
14:30 | 765 | 5531.5 | 4112 | 9643.5
15:00 | 750 | 5514 | 4067 | 9581
15:30 | 690 | 5484.5 | 4072.5 | 9557
16:00 | 630 | 5455 | 4078 | 9533
16:30 | 565 | 5527.5 | 4073.5 | 9601
17:00 | 500 | 5600 | 4069 | 9669
17:30 | 460 | 6005.5 | 4432.5 | 10438
18:00 | 420 | 6411 | 4796 | 11207
18:30 | 385 | 6355 | 4756 | 11111
19:00 | 350 | 6299 | 4716 | 11015
19:30 | 430 | 6113 | 4729 | 10842
20:00 | 470 | 6029 | 4700 | 10729 |  |  |  | Executive Engineer
20:30 | 500 | 5911 | 4719.5 | 10630.5 |  |  |  | Network Operation Division
21:00 | 530 | 5793 | 4739 | 10532
21:30 | 575 | 5628.5 | 4608 | 10236.5
22:00 | 620 | 5464 | 4477 | 9941 |  |  |  |  | Page 6 of 7
22:30 | 690 | 5399 | 4385.5 | 9784.5
23:00 | 760 | 5334 | 4294 | 9628
23:30 | 760 | 5245 | 4235 | 9480
24:00 | 760 | 5156 | 4176 | 9332
11207 MW (18:00 )
9414 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-11-11 |  | Energy |  | 222695690
[15 empty] | 43779 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3222 | 917 | 1605 | 0 | 293 | 3031 | 132 | 0 | 16 | 114 | 0 | 2 | 0
0:30 | 3178.5 | 914 | 1502.5 | 0 | 185.5 | 2822 | 132 | 0 | 8 | 108 | 0 | 4 | 0 |  |  | Date: | 43779
1:00 | 3135 | 911 | 1400 | 0 | 78 | 2613 | 132 | 0 | 0 | 102 | 0 | 6 | 0
1:30 | 3056.5 | 911.5 | 1364 | 0 | 39 | 2580.5 | 132 | 0 | 0 | 100 | 0 | 8 | 0 | [9 empty] | Total Energy | 222.6957 | 222.6957 | Total Energy Gen 222.696 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 222.696 MKWHr
2:00 | 2978 | 912 | 1328 | 0 | 0 | 2548 | 132 | 0 | 0 | 98 | 0 | 10 | 0 | [9 empty] | Energy not Served | 0 | 0
2:30 | 2896.5 | 912 | 1261.5 | 0 | 0 | 2534.5 | 112 | 0 | 0 | 100 | 0 | 10 | 0 | [9 empty] | Energy Requirement | 222.6957 | 222.6957
3:00 | 2815 | 912 | 1195 | 0 | 0 | 2521 | 92 | 0 | 0 | 102 | 0 | 10 | 0
3:30 | 2807.5 | 769.5 | 1197.5 | 0 | 0 | 2535 | 92 | 0 | 0 | 102 | 0 | 8.5 | 0 | [8 empty] | Shortage
4:00 | 2800 | 627 | 1200 | 0 | 0 | 2549 | 92 | 0 | 0 | 102 | 0 | 7 | 0
4:30 | 2818.5 | 579 | 1214.5 | 0 | 0 | 2561.5 | 92 | 0 | 0 | 101 | 0 | 6.5 | 0
5:00 | 2837 | 531 | 1229 | 0 | 0 | 2574 | 92 | 0 | 0 | 100 | 0 | 6 | 0
5:30 | 2873 | 531 | 1244.5 | 0 | 0 | 2571 | 112 | 0 | 0 | 95 | 0 | 4.5 | 0
6:00 | 2909 | 531 | 1260 | 0 | 0 | 2568 | 132 | 0 | 0 | 90 | 0 | 3 | 0
6:30 | 3064.5 | 531 | 1325 | 0 | 0 | 2567.5 | 132 | 0 | 0 | 93 | 19 | 2.5 | 0 | [7 empty] | Coal
7:00 | 3220 | 531 | 1390 | 0 | 0 | 2567 | 132 | 0 | 0 | 96 | 38 | 2 | 0
7:30 | 3197 | 578.5 | 1417 | 0 | 34.5 | 2591 | 132 | 0 | 0 | 97 | 89 | 1 | 0 | [6 empty] | Oil
8:00 | 3174 | 626 | 1444 | 0 | 69 | 2615 | 132 | 0 | 0 | 98 | 140 | 0 | 0
8:30 | 3085.5 | 735.5 | 1327 | 0 | 127.5 | 2594.5 | 132 | 0 | 8 | 99 | 202.5 | 0 | 0
9:00 | 2997 | 845 | 1210 | 0 | 186 | 2574 | 132 | 0 | 16 | 100 | 265 | 0 | 0
9:30 | 3014.5 | 845 | 1211 | 0 | 191.5 | 2546 | 132 | 0 | 16 | 106 | 304.5 | 0 | 0
10:00 | 3032 | 845 | 1212 | 0 | 197 | 2518 | 132 | 0 | 16 | 112 | 344 | 0 | 0
10:30 | 3124 | 878 | 1290.5 | 0 | 205.5 | 2514 | 132 | 0 | 23 | 113 | 369.5 | 0.5 | 0
11:00 | 3216 | 911 | 1369 | 0 | 214 | 2510 | 132 | 0 | 30 | 114 | 395 | 1 | 0
11:30 | 3223.5 | 911 | 1488 | 0 | 243 | 2596.5 | 132 | 0 | 39 | 119 | 400.5 | 0.5 | 0
12:00 | 3231 | 911 | 1607 | 0 | 272 | 2683 | 132 | 0 | 48 | 124 | 406 | 0 | 0
12:30 | 3218 | 910.5 | 1604.5 | 0 | 366.5 | 2851.5 | 132 | 0 | 51.5 | 127 | 380 | 0 | 0
13:00 | 3205 | 910 | 1602 | 0 | 461 | 3020 | 132 | 0 | 55 | 130 | 354 | 0 | 0
13:30 | 3205 | 910 | 1602 | 0 | 461 | 3020 | 132 | 0 | 55 | 130 | 354 | 0 | 0
14:00 | 3205 | 910 | 1602 | 0 | 461 | 3020 | 132 | 0 | 55 | 130 | 354 | 0 | 0
14:30 | 3205 | 910 | 1564.5 | 0 | 540 | 2921 | 132 | 0 | 36 | 132 | 283.5 | 1 | 0
15:00 | 3205 | 910 | 1527 | 0 | 619 | 2822 | 132 | 0 | 17 | 134 | 213 | 2 | 0
15:30 | 3237 | 909.5 | 1595 | 0 | 559.5 | 2825 | 132 | 0 | 17 | 130 | 150 | 2 | 0
16:00 | 3269 | 909 | 1663 | 0 | 500 | 2828 | 132 | 0 | 17 | 126 | 87 | 2 | 0
16:30 | 3190 | 910 | 1562.5 | 0 | 710.5 | 2876.5 | 132 | 0 | 45.5 | 125 | 47 | 2 | 0
17:00 | 3111 | 911 | 1462 | 0 | 921 | 2925 | 132 | 0 | 74 | 124 | 7 | 2 | 0
17:30 | 3166 | 911.5 | 1560 | 0 | 1322 | 3135.5 | 132 | 0 | 78 | 127 | 3.5 | 2.5 | 0
18:00 | 3221 | 912 | 1658 | 0 | 1723 | 3346 | 132 | 0 | 82 | 130 | 0 | 3 | 0
18:30 | 3227 | 856.5 | 1657 | 0 | 1617 | 3419 | 132 | 0 | 74 | 127 | 0 | 1.5 | 0
19:00 | 3233 | 801 | 1656 | 0 | 1511 | 3492 | 132 | 0 | 66 | 124 | 0 | 0 | 0
19:30 | 3232 | 881 | 1584 | 0 | 1331 | 3494 | 132 | 0 | 66 | 122 | 0 | 0 | 0
20:00 | 3240 | 916 | 1598 | 0 | 1166 | 3489 | 132 | 0 | 66 | 122 | 0 | 0 | 0
20:30 | 3239 | 916.5 | 1636 | 0 | 1014.5 | 3502.5 | 132 | 0 | 66 | 124 | 0 | 0 | 0
21:00 | 3238 | 917 | 1674 | 0 | 863 | 3516 | 132 | 0 | 66 | 126 | 0 | 0 | 0
21:30 | 3239.5 | 917.5 | 1672 | 0 | 696.5 | 3396 | 132 | 0 | 58 | 125 | 0 | 0 | 0
22:00 | 3241 | 918 | 1670 | 0 | 530 | 3276 | 132 | 0 | 50 | 124 | 0 | 0 | 0
22:30 | 3243.5 | 917.5 | 1642.5 | 0 | 481.5 | 3211.5 | 132 | 0 | 33 | 123 | 0 | 0 | 0
23:00 | 3246 | 917 | 1615 | 0 | 433 | 3147 | 132 | 0 | 16 | 122 | 0 | 0 | 0
23:30 | 3234 | 917 | 1610 | 0 | 363 | 3089 | 132 | 0 | 16 | 118 | 0 | 1 | 0 |  |  | Max Temp. in Dhaka |  | 31.6°C
24:00 | 3222 | 917 | 1605 | 0 | 293 | 3031 | 132 | 0 | 16 | 114 | 0 | 2 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 222.696 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 222.696 MKWHr
Note on W13: Author:

## Generation
g | 2023-11-11
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 |  | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 2200800
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 0 | 0 | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 812000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [16 empty] | 3 | 16 |  | 17 | 17 | 17 | 17 | 17 | 8 | 8 | 105269
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 4 | 9 | 15 | 18 | 19 | 20 | 18 | 15 | 11 | 5 | 0 | [9 empty] | 135000
6 | Sikalbaha 225MW CCPP (Gas) | 132 | 128 | 97 | 82 | 110 | 133 | 141 | 141 | 141 | 141 | 140 | 141 | 141 | 141 | 141 | 141 | 141 | 141 |  | 141 | 141 | 141 | 131 | 131 | 131 | 131 | 3171935
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [10 empty] | 14 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 195009
12 | Hathazari 100 MW peaking PP | [16 empty] | 2 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 108432
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | [7 empty] | 2 | 17 | 17 | 24 | 34 | 34 | 34 | 34 | 34 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 387236
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 159 | 160 | 253 | 251 | 244 | 247 | 238 | 230 | 229 | 224 |  | 224 | 223 | 224 | 224 | 228 | 231 | 233 | 5581893
18 | Kodda 300 MW PP Unit-2 (Summit) | [12 empty] | 18 | 47 | 47 | 47 | 47 | 49 |  | 15 | 15 |  |  |  |  | 0 | 373855
19 | Ashuganj 195 MW PP (APSCL-United) | [25 empty] | 0 | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4252500
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 320 | 320 | 321 | 320 | 320 | 320 | 320 | 322 | 322 | 320 | 312 | 312 | 312 | 311 | 310 | 310 | 310 | 325 |  | 325 | 325 | 325 | 325 | 312 | 300 | 300 | 7641817
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP
33 | Ashuganj 225 MW CCPP | 169 | 142 | 143 | 143 | 143 | 169 | 195 | 175 | 183 | 198 | 192 | 186 | 187 | 187 | 170 | 154 | 151 | 158 |  | 168 | 170 | 170 | 170 | 170 | 170 | 164 | 4142000
34 | Ashuganj 450 MW CCPP(South) | 270 | 270 | 230 | 230 | 230 | 270 | 360 | 270 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 6140000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 290 | 315 | 280 | 325 | 280 | 280 | 300 | 290 | 275 | 280 | 275 | 315 | 320 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 7283500
| Ashuganj 420 MW CCPP(East) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5886200
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 316 | 303 | 302 | 292 | 289 | 295 | 350 | 392 | 392 | 373 | 334 | 355 | 336 | 305 | 322 | 352 | 346 | 334 |  | 340 | 340 | 340 | 340 | 339 | 340 | 339 | 8144890
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 225 | 225 | 225 | 225 | 225 | 180 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4417300
41 | Haripur 360 MW CCPP(HPL) | 245 | 255 | 215 | 205 | 205 | 205 | 218 | 188 | 187 | 206 | 201 | 167 | 161 | 163 | 163 | 159 | 154 | 154 |  | 151 | 152 | 150 | 152 | 153 | 153 | 151 | 4426000
42 | RPCL 210MW CCPP | 104 | 104 | 83 | 84 | 87 | 87 | 103 | 104 | 104 | 100 | 98 | 97 | 95 | 92 | 91 | 93 | 98 | 99 |  | 95 | 95 | 95 | 95 | 95 | 98 | 99 | 2229120
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 4 | 9 | 32 | 41 | 47 | 49 | 21 | 31 | 25 | 5 | 1 | [9 empty] | 273190
44 | Fenchugonj CCPP Phase-1 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 43 | 43 | 43 | 43 | 40 | 43 | 41 | 41 | 40 | 42 |  | 42 | 43 | 42 | 42 | 42 | 42 | 42 | 994000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 58 | 58 | 40 | 40 | 40 | 60 | 40 | 62 |  | 62 | 62 | 62 | 62 | 62 | 60 | 62 | 1164864
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 203 | 203 | 202 | 201 | 201 | 203 | 201 | 205 | 205 |  | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 5117740
51 | Sylhet 20 MW GTPP | 18 | [6 empty] | 17 | 17 | 17 | 17 | 16 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 298000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 0 | [6 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 171720
54 | Hobiganj 11 MW PP Cofidence-E | 2 | [6 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 89134
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | [5 empty] | 25 | 10 |  |  | 42 | 44 | 44 | 20 | 49 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 616200
56 | Shahjahanulla 25 MW PP | 0 | [8 empty] | 16 | 16 |  |  | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 258480
57 | Bibiana-II 341 MW CCPP (Summit) | 260 | 260 | 265 | 280 | 310 | 300 | 300 | 285 | 275 | 270 | 300 | 300 | 300 | 260 | 300 | 305 | 290 | 285 |  | 280 | 270 | 285 | 295 | 280 | 290 | 280 | 6994000
| Bibiyana South 400 MW | 260 | 260 | 200 | 200 | 200 | 200 | 230 | 230 | 200 | 200 | 250 | 250 | 255 | 235 | 235 | 255 | 235 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 5698700
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 17 | 55 |  | 35 | 35 | 35 | 35 |  |  | 0 | 140690
59 | Tangail Palli Power Gen 22 MW | [7 empty] | 1 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 3 | 6 | 6 |  | 6 | 6 | 6 | 6 |  |  | 0 | 79440
60 | Barabkunda 22 MW PP (Regent) | 12 | 12 |  |  |  |  | 8 | 8 | 10 | 10 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 10 | 10 | 10 | 10 | 210816
61 | Narshingdi 22 MW PP (Doreen) | 15 | [7 empty] | 10 | 12 | 12 | 12 | 12 | 14 | 14 | 14 | 14 | 14 |  | 14 | 18 | 18 | 18 | 18 | 18 | 18 | 239328
62 | Tangail 22 MW PP (Doreen) | [14 empty] | 15 | 18 | 18 | 18 |  | 18 | 18 | 16 | 18 | 18 | 18 | 0 | 174096
63 | Impoprt (Tripura) | 102 | 98 | 102 | 102 | 100 | 90 | 96 | 98 | 100 | 112 | 114 | 124 | 130 | 130 | 134 | 126 | 124 | 130 |  | 124 | 122 | 122 | 126 | 124 | 122 | 114 | 2749440
64 | Malancha, Ctg. EPZ (United) | 42 | 22 | 12 | 12 | 12 | 27 | 41 | 16 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 |  | 3 | 2 | 2 | 2 | 12 | 12 | 14 | 370080
65 | Feni 22 MW PP (Doreen) | 18 |  |  |  |  | 13 | 12 | 15 | 15 | 15 | 15 | 15 | 13 | 0 | 12 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 262332
66 | Feni 11 MW PP (Doreen) | 10 | [6 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 178380
67 | Jangalia 33 MW PP (Summit) | 17 | [5 empty] | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 596800
68 | Cumilla 25 MW PP (Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 6 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 278500
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456000
70 | Summit Madhabdi | 12 | 13 | 13 | 13 | 13 | 12 | 12 | 12 | 0 | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 11 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 279000
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 0 | 0 | 25 | 33 | 33 | 33 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 628900
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 614200
73 | Ghorashal 108 MW PP (Regent) | 6 | [6 empty] | 32 | 12 | 12 | 12 | 51 | 75 | 74 | 71 | 70 | 75 | 74 |  | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 986909
| Feni Lanka Power | [16 empty] | 17 | 17 |  | 17 | 17 | 17 | 17 |  |  | 0 | 79800
| Chowmuhani 113 MW | [13 empty] | 28 | 27 | 37 | 38 | 57 |  | 57 | 57 | 58 | 58 | 58 | 51 | 9 | 462000
| Manikgonj 162MW PP(MPGL) | [12 empty] | 12 | 18 | 17 |  | 17 | 35 |  | 17 | 17 | 17 |  |  |  | 0 | 129600
77 | Siddhirganj 100 PP(Dutch Bangla) | [11 empty] | 1 | 14 | 40 | 27 | 9 | 12 | 50 |  | 62 | 48 | 37 |  |  |  | 0 | 238080
78 | Gazipur 52 MW PP | [16 empty] | 8 | 18 |  | 25 | 25 | 8 | 8 |  |  | 0 | 82080
79 | Kodda 150 MW PP | [8 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 0 |  | 32 | 32 |  | 16 | 16 | 16 | 16 |  |  | 0 | 201600
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 1 | 28 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 93413
| Gazipur 100 MW PP | [22 empty] | 17 |  |  | 0 | 14400
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 2 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 27242
| Jodiac Power | [11 empty] | 5 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 228523
| Karnaphuli Power Ltd. | 17 | [7 empty] | 2 | 17 | 26 | 35 | 35 | 35 | 35 | 35 | 35 | 19 |  | 19 | 17 | 17 | 17 | 17 | 17 | 17 | 409817
82 | Madanganj 102 PP(Summit) | [12 empty] | 17 | 50 | 48 | 17 | 17 | 34 |  | 50 | 17 | 22 | 14 |  |  | 0 | 224495
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [16 empty] | 15 | 25 | [7 empty] | 0 | 36992
86 | Meghnaghat CCPP ( Summit) | 112 | 112 | 114 | 115 | 114 | 113 | 117 | 121 | 122 | 123 | 134 | 138 | 146 | 146 | 149 | 148 | 152 | 152 |  | 155 | 156 | 157 | 157 | 158 | 157 | 158 | 3273862
87 | Meghnaghat 100 MW(IEL) | [16 empty] | 3 | 20 |  | 49 | 25 | 35 |  |  |  | 0 | 109440
| Meghnaghat 104 MW PP (OPCL) | [11 empty] | 2 | 36 | 68 | 61 | 17 | 24 | 51 |  | 65 | 72 | 71 | 71 | 17 |  | 0 | 514560
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [8 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 168120
92 | Fenchuganj 44 MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 5 | [6 empty] | 14 | 10 | 10 | 10 | 26 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 742532
94 | Gagnagar 102 MW PP (Digital Power) | [12 empty] | 16 | 58 | 8 | 8 | 40 | 91 |  | 49 | 49 | 24 | 8 |  |  | 0 | 293472
95 | Patenga 50MW PP (Baraka) | [9 empty] | 6 | 14 | 24 | 27 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 6 | 340800
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [13 empty] | 10 | 15 | 15 | 15 | 25 |  | 30 | 15 | 15 | 15 |  |  | 0 | 155541
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 5 | 35 |  | 35 | 35 | 35 | 35 |  |  | 0 | 134564
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [9 empty] | 13500
103 | Kamalaghat 54 MW PP(Banco Energy) | [16 empty] | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 115920
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [7 empty] | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 28 | 93 |  | 65 | 25 | 25 | 25 | 8 |  | 0 | 352800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 9 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 51 |  | 80 | 81 | 56 | 53 | 35 | 35 | 35 | 536256
115 | Juldah 100 MW PP Unit-3 (Acorn) | 12 | [7 empty] | 4 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 206400
116 | Chandpur 200 MW (Desh energy) | [12 empty] | 1 | 16 | 0 |  | 11 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 169440
117 | Ashuganj 150 MW PP (Midland) | [12 empty] | 10 | 10 | 10 | 10 | 23 | 60 |  | 50 | 6 | 6 |  |  |  | 0 | 259272
118 | Bibiyana-III 400 MW CCPP | 376 | 342 | 343 | 342 | 342 | 342 | 343 | 343 | 335 | 337 | 387 | 403 | 403 | 372 | 404 | 404 | 371 | 402 |  | 402 | 402 | 402 | 402 | 402 | 402 | 401 | 8982000
| Jamalpur 115 MW PP (United) | [7 empty] | 35 | 69 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 46 | 85 |  | 85 | 65 | 45 | 45 | 28 | 25 | 16 | 538800
| Anwara 300 MW PP (United) | 15 | [7 empty] | 50 | 65 | 65 | 85 | 103 | 105 | 103 | 103 | 105 | 240 |  | 245 | 248 | 249 | 124 | 123 | 124 | 80 | 1944545
| Juldah unit-2 (Acorn) | [8 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 189120
| Anlima Energy Ltd. | [8 empty] | 4 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 270982
| Bhairob 54.5 MW | 17 | [15 empty] | 6 | 17 |  | 17 | 17 | 17 | 17 |  |  | 0 | 120240
| Spectra Solar Plant Ltd. | [6 empty] | 3 | 11 | 22 | 26 | 31 | 31 | 30 | 25 | 18 | 8 | 1 | [9 empty] | 206015
| Chandpur 115(Doreen) | [11 empty] | 4 | 27 | 48 | 35 | 36 | 48 | 88 |  | 95 | 95 | 96 | 75 | 72 | 35 | 18 | 693120
| Kanchan Purbachal Power Generation Ltd. | [16 empty] | 21 | 35 |  | 17 | 17 | 17 | 17 |  |  | 0 | 123480
| Mirsharai 150 MW (Oil) | [11 empty] | 15 | 22 | 25 | 0 |  | 23 | 17 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 167272
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 6 | 10 | 10 | 7 | 6 | 3 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 2 | 2 | 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 53760
| Matarbari 2*600 MW (CPGCL) | 198 | 203 | 203 | 204 | 205 | 203 | 206 | 202 | 190 | 201 | 201 | 204 | 201 | 192 | 197 | 198 | 202 | 201 |  | 202 | 201 | 201 | 202 | 203 | 204 | 202 | 4952727
120 | Eastern Zone Total | 4783 | 4532 | 4231 | 4219 | 4291 | 4392 | 4753 | 4779 | 4704 | 4791 | 5019 | 5247 | 5442 | 5549 | 5514 | 5455 | 5600 | 6411 |  | 6299 | 6113 | 6029 | 5793 | 5464 | 5334 | 5156 | 125412277
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [17 empty] | 16 | [7 empty] | 0 | 16320
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [12 empty] | 2 | 9 | 17 |  | 2 | 13 |  | 17 | 17 | 17 |  |  |  | 0 | 89760
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 7 | 25 | 45 | 61 | 70 | 72 | 66 | 53 | 35 | 14 | 1 | [9 empty] | 455040
131 | Rampal 1320 MW (BIFPCL) | 377 | 377 | 372 | 380 | 381 | 380 | 380 | 374 | 378 | 351 | 349 | 345 | 345 | 349 | 347 | 349 | 346 | 455 |  | 452 | 442 | 448 | 452 | 450 | 452 | 402 | 9338182
132 | United Payra Power Ltd. | [16 empty] | 19 | 54 |  | 17 | 17 |  |  |  |  | 0 | 121200
133 | Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 180 | 180 | 220 | 220 | 220 | 180 | 220 | 220 | 180 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 4962355
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 12 |  | 16 | 16 |  |  |  |  | 0 | 27264
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3437300
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 100 | 130 | 130 | 130 | 80 | 120 | 124 | 80 | 120 |  | 128 | 120 | 130 | 130 | 130 | 130 | 130 | 2484000
140 | Bhola 33 MW PP (Venture) | 20 | 19 | 19 | 18 | 18 | 15 | 14 | 13 | 12 | 11 | 12 | 14 | 18 | 20 | 18 | 12 | 20 | 23 |  | 23 | 24 | 24 | 24 | 23 | 23 | 22 | 433300
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [16 empty] | 32 | 32 | [7 empty] | 0 | 54144
146 | Bheramara HVDC | 911 | 912 | 912 | 627 | 531 | 531 | 531 | 626 | 845 | 845 | 911 | 911 | 910 | 909 | 910 | 909 | 911 | 912 |  | 801 | 881 | 916 | 917 | 918 | 917 | 917 | 20078545
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 580 | 520 | 500 | 520 | 540 | 540 | 540 | 590 | 560 | 520 | 520 | 590 | 830 | 840 | 740 | 740 | 790 | 900 |  | 1040 | 1050 | 1040 | 1060 | 940 | 880 | 800 | 19264200
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4132100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 2 | 3 | 4 | 5 | 5 | 5 | 4 | 2 | 1 | 0 | [9 empty] | 34140
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 300 | 250 | 220 | 220 | 220 | 250 | 350 | 350 | 220 | 220 | 300 | 414 | 350 | 240 | 300 | 414 | 300 | 414 |  | 414 | 350 | 350 | 414 | 414 | 350 | 350 | 7760618
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 |  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 211392
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern) | [25 empty] | 0 | 0
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [26 empty] | 0
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [26 empty] | 0
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [16 empty] | 16 | 45 |  | 35 | 35 |  |  |  |  | 0 | 145824
172 | Confidence Power Bogura Unit-1 113 MW | [16 empty] | 35 | 35 | [7 empty] | 0 | 62112
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 35 | 34 |  | 34 | 35 | 34 | 34 |  |  | 0 | 162096
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 5 | 6 | 6 | 6 | 5 | 4 | 2 | 0 | [9 empty] | 38385
178 | Energypac Power Venture Thakurgaon Ltd. | [16 empty] | 10 | 35 |  | 35 | 35 | 35 |  |  |  | 0 | 125952
| Intraco Solar 30 MW | [6 empty] | 3 | 11 | 22 | 30 | 34 | 34 | 31 | 26 | 16 | 8 | 1 | [9 empty] | 215865
| Adani Power Jharkhanda Ltd | 828 | 818 | 815 | 815 | 818 | 815 | 811 | 817 | 814 | 816 | 818 | 922 | 1022 | 977 | 918 | 921 | 967 | 1155 |  | 1163 | 1166 | 1165 | 1167 | 1061 | 1001 | 1017 | 22450909
178 | Teesta Solar Limited | [6 empty] | 17 | 69 | 118 | 153 | 177 | 183 | 171 | 144 | 99 | 43 | 3 | [9 empty] | 1182410