## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2019-04-10 | Wednesday
|  | Date (day): | 2019-04-10 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12245 | MW |  |  | (b) At Evening Peak Hour : |  | 13779 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-04-09 | 2019-04-10 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 36 | 36 | 36 | 36 |  |  | Unit-1 under maint.
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 134 | 44 | 135 | 135 |  |  | On test.
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 142 | 50 | 100 | 100 |  |  | On test.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 190 | 120 | 190 | 190
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  |  | Under maint
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 78 | 78
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 50 | 108
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 355 | 343 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 0 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 238 | 337 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 280 | 380 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 92 | 92 |  | 8 | Engine problem
11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 280 | 250 | 305 | 305
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 13 | 0 | 19 | 19
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 80 | 87 | 150 | 218
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 120 | 20 | 150 | 215 |  | 2
0 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
21 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 0 | 102 | 102
22 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 6 | 6 | 48 | 48
23 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 0 | 54 | 54
24 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
25 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 18 | 0 | 55 | 55
26 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 0 | 55 | 55
27 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 51 | 51 |  | 57 | Engine problem
28 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 50 | 43 | 57 | 57 |  | 23 | Engine problem
29 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
30 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 29 | 12 | 33 | 33
31 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 8 | 0 | 51 | 51
32 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
33 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 200 | 300
34 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
35 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
36 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
37 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
| Dhaka area Total |  |  |  |  | 6034 | 5798 | 2020 | 1761 | 4529 | 4920 | 260 | 90
38 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 100 | 100 | 110 | 70 |  | Machine problem.
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Under maint
39 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 16 | 16 |  | 9 | Engine problem
40 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18.3 | 0 | 20 | 0
41 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 78 | 82 | 80 | 80 |  | 150 | Low water lavel
43 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
44 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 205 | 204 | 225 | 225 |  |  | FGMO
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under S/D
46 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 32 | 51 | 51 | 51
47 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 50 | 50
48 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 34 | 85 | 85
49 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 10 | 78 | 78 |  | 22 | Engine problem
50 | Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
51 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 0 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 10 | 7 | 20
52 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 45 | 50 | 105 | 105
| Chattogram area Total |  |  |  |  | 1761 | 1681 | 580.3 | 699 | 989 | 992 | 250 | 371
53 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Gas shortage
54 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 203 | 184 | 221 | 221 |  |  | FGMO
55 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 240 | 290 | 360 | 360
56 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 220 | 280 | 360 | 360
57 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 3 | 40 | 40
58 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 0 | 5 | 5 | 50 |  | Gas shortage
59 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage
60 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 8 | 26 | 100 | 95 |  | Gas Shortage
61 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 5 | 5 | 45 | 45 |  | 6 | Gas Shortage
62 | Midland 150MW |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 150 | 150
63 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
64 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 100 |  | 63 | Under maint. |  | 2019-09-04
66 | Chandpur Desh 200MW |  | HFO | IPP | 0 | 200 | 200 | 34 | 0 | 200 | 200
67 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 22
68 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 0 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 98 | 10 | 132 | 156
69 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 8 | 0 | 10 | 33
70 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
71 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 0 | 0 | 0 | 21
72 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 865 | 785 | 1717 | 2131 | 457 | 203
73 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 150 | 162 | 202 | 202
74 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 20
75 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 87 | 87 |  | 8 | Enjgine problem
76 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 1.7 | 0 | 2 | 0
77 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 0 | 0 | 200 | 200
78 | United Jamalpur PPL |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 112 | 112
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 151.7 | 162 | 603 | 621 | 0 | 8
79 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 60 | 60
80 | Fenchugonj CCPP-2 |  | Gas | PDB | !F71 | 104 | 90 | 42 | 60 | 60 | 60
81 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 0 | 163 | 163
82 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 176 | 167 | 200 | 270 |  |  | FGMO
83 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 5 | 51 | 51
84 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 5 | 5 | 44 | 44
85 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11
86 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 67 | 52 | 66 | 66 |  |  | FGMO
87 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 5 | 86 | 86
88 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 5 | 47 | 47
89 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 105 | 106 | 120 | 120
90 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | under maint.
91 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 7 | 6 | 46 | 46
92 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 8 | 25 | 25
93 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 290 | 341 | 341 |  |  | FGMO
| Bibiyana-3 285MW |  | Gas | PDB | 285 MW | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
94 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 822 | 749 | 1330 | 1400 | 0 | 20
95 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 46
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 842 | 637 | 860 | 958
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
96 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 115 | 115
97 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 9 | 0 | 35
98 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 |  |  | Reserve
99 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 80
100 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  |  | Under maint.
101 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
0 | Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
102 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
103 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 17 | 105 | 105
| Madhumati Power Plant |  | HFO | IPP | 100 MW | 0 | 0 | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  |  | 2223 | 2209 | 877 | 663 | 1120 | 1479 | 0 | 0
104 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 64 | 0 | 110 | 110
105 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 26
106 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 3 | 33 | 33
107 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 120 | 120 | 120 | 120
108 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 94 | 52 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 298 | 175 | 358 | 384 | 0 | 0
109 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 65 | 60 | 65 | 65 | 71
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 60 | 60 | 60 | 60 | 100
110 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
111 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 54
112 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 12 | 35 | 35 |  | 15 | Engine problem
113 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
114 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 40
115 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 163 | 169 | 200 | 200 |  |  | FGMO
116 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 154 | 160 | 225 | 225 |  |  | FGMO
117 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 131 | 165 | 176 | 220 | 220 |  | Gas shortage
118 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282 | 282 | 282 | 142 | 180 | 282 | 282 |  |  | ON test
119 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 30
120 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 3 | 22 | 22 | 22
121 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 3 | 10 | 17 | 17
122 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11
123 | Rajlanka 52 MW |  | HFO | IPP | 52 | 52 | 52 | 0 | 8 | 43 | 43 |  | 9 | Engine problem
124 | Chapainawabganj-100 MW |  | HFO | PDB | 104 | 104 | 104 | 25 | 0 | 100 | 100
125 | Paramount Baghabari |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Reserve
126 | Confidence CPBL-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 113 | 113 |  |  | On test
| Rajshahi Area Total |  |  |  |  | 1948 | 1938 | 746 | 846 | 1399 | 1617 | 391 | 24
127 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under overhauling
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  |  | under maint.
128 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 184 | 184 | 200 | 200 | 74
129 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
130 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 184 | 184 | 200 | 235 | 74 | 85
| Total |  |  |  |  | 18192 | 17649 | 6544 | 6024 | 12245 | 13779 | 1432 | 801
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6089.9177 | 5606 | 11395.3303 | 12822.8875
A. |  | 2019-04-09 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 7305.6 | MW at | 15:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 6168.04 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 6024 | MW
3 | Day peak Generation : |  |  | 6544 | MW at | 10:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 5606 | MW
4 | Evening peak Generation : |  |  | 6024 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 156.6237 | MKWHr | By Solar | 0.15021 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 114.3581 | MKWHr |  | By Oil: | 16.5811 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 4.0974 | MKWHr |  | By Hydro: | 1.7949 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1432 | MW | Dhaka | 2364 | 2364 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 801 | MW | Chittagong | 695 | 695 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2233 | MW | Khulna | 525 | 525 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 963.8 | MMCFD |  |  | Rajshahi | 667 | 667 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 76201355.38 | ii) Oil : | Taka | 157048872.43 | Comilla | 166 | 166 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 15815964 | Total | Taka | 249066191.81 | Mymensingh | 386 | 386 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.993 | MKWHr. | Sylhet | 268 | 268 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -130 | MW (E to W) at | 21:00 | hrs | Barisal | 65 | 65 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -420 | MW at | 19:00 | hrs | Rangpur | 470 | 470 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 29.2° C |  |  | Total | 5606 | 5606 |  | 0
B. |  | 2019-04-10 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 31.3° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13779 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7300 | MW
4 | Reserve(Generation end) |  |  |  | 4279 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 203.6691 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5019 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.936 | MKWHr. | ii) HVDC Flow at Peak Time |  | 637 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.7059 | MKWHr. | iii) Maximum HVDC Flow : |  | 843 | MW at | 15:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 84.41 |  | (b) Today: | 84.17 |  | (c) Rule Curve: |  | 86.2
.

## YesterdayGen
2019-04-09
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285MW | United Jamalpur PPL | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | Paramount Baghabari | Confidence CPBL-2 | Madhumati Power Plant | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 36 | 133 | 201 | 190 | 0 | 0 | 0 | 320 | 303 | 0 | 0 | 370 | 275 | 0 | 0 | 0 | 160 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 17 | 18 | 17 | 19 | 25 | 25 | 33 | 33 | 0 | 0 | 81 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 51 | 0 | 17 | 10 | 75 | 50 | 22 | 34 | 0 | 0 | 0 | 300 | 300 | 190 | 26 | 0 | 40 | 5 | 5 | 5 | 0 | 0 | 8 | 0 | 11 | 33 | 18 | 92 | 213 | 0 | 20 | 0 | 30 | 42 | 11 | 50 | 100 | 245 | 52 | 5 | 47 | 95 | 0 | 44 | 10 | 255 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 34 | 0 | 0 | 0 |  | 703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 2 | 0 | 120 | 25 | 80 | 0 | 60 | 60 | 0 | 0 | 25 | 0 | 0 | 0 | 8 | 0 | 3 | 17 | 8 | 0 | 0 | 184 | 0 | 0 | 157 | 0 | 147 | 0 | 95 | 0 | 151 | 0 | 102 | 0 | 0 | 0 | 0 |  | 5203 | 1979 | 7182 | 3785 | 703 | 1512 | 749 | 184 | 81 | 76 | 92 | 0 | 0 | 84.46
2:00 | 36 | 133 | 200 | 190 | 0 | 0 | 0 | 320 | 302 | 0 | 0 | 370 | 275 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 17 | 18 | 17 | 19 | 25 | 25 | 33 | 33 | 0 | 0 | 81 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 41 | 0 | 17 | 10 | 13 | 6 | 22 | 32 | 0 | 0 | 0 | 300 | 300 | 184 | 26 | 0 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 11 | 8 | 18 | 92 | 214 | 0 | 20 | 0 | 30 | 42 | 5 | 50 | 100 | 252 | 42 | 5 | 47 | 95 | 0 | 43 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 17 | 0 | 0 | 0 |  | 693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 120 | 24 | 80 | 0 | 50 | 60 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 3 | 17 | 8 | 0 | 0 | 184 | 0 | 0 | 157 | 0 | 146 | 0 | 95 | 0 | 151 | 0 | 107 | 0 | 0 | 0 | 0 |  | 4960 | 1933 | 6893 | 3687 | 693 | 1501 | 600 | 184 | 81 | 55 | 92 | 0 | 0 | 84.45
3:00 | 36 | 133 | 200 | 190 | 0 | 0 | 0 | 320 | 303 | 0 | 0 | 370 | 255 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 18 | 17 | 19 | 25 | 25 | 33 | 33 | 0 | 0 | 81 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 41 | 0 | 17 | 10 | 13 | 6 | 22 | 32 | 0 | 0 | 0 | 300 | 300 | 184 | 26 | 0 | 10 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 11 | 8 | 15 | 84 | 215 | 0 | 20 | 0 | 30 | 42 | 5 | 5 | 100 | 252 | 42 | 5 | 5 | 93 | 0 | 7 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 17 | 0 | 0 | 0 |  | 693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 120 | 22 | 80 | 0 | 50 | 60 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 184 | 0 | 0 | 156 | 0 | 146 | 0 | 95 | 0 | 151 | 0 | 106 | 0 | 0 | 0 | 0 |  | 4749 | 1913 | 6662 | 3652 | 693 | 1372 | 543 | 184 | 81 | 53 | 84 | 0 | 0 | 84.44
4:00 | 36 | 133 | 150 | 190 | 0 | 0 | 0 | 290 | 271 | 0 | 0 | 350 | 225 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 18 | 17 | 19 | 25 | 25 | 33 | 33 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 41 | 0 | 17 | 10 | 13 | 6 | 22 | 34 | 0 | 0 | 0 | 280 | 280 | 184 | 26 | 0 | 10 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 11 | 8 | 12 | 84 | 215 | 0 | 0 | 0 | 30 | 42 | 5 | 5 | 100 | 188 | 43 | 5 | 5 | 94 | 0 | 7 | 0 | 271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 17 | 0 | 0 | 0 |  | 693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 120 | 23 | 64 | 0 | 50 | 60 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 184 | 0 | 0 | 158 | 0 | 150 | 0 | 95 | 0 | 149 | 0 | 122 | 0 | 0 | 0 | 0 |  | 4463 | 1909 | 6372 | 3451 | 693 | 1340 | 497 | 184 | 79 | 44 | 84 | 0 | 0 | 84.43
5:00 | 36 | 134 | 150 | 190 | 0 | 0 | 0 | 280 | 262 | 0 | 0 | 320 | 265 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 18 | 17 | 19 | 25 | 25 | 33 | 33 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 24 | 0 | 17 | 10 | 13 | 6 | 22 | 34 | 0 | 0 | 0 | 260 | 260 | 184 | 26 | 0 | 10 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 11 | 8 | 12 | 80 | 182 | 0 | 0 | 0 | 30 | 42 | 5 | 5 | 100 | 188 | 43 | 5 | 5 | 102 | 0 | 7 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 17 | 0 | 0 | 0 |  | 693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 22 | 64 | 0 | 50 | 60 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 184 | 0 | 0 | 156 | 0 | 147 | 0 | 96 | 0 | 148 | 0 | 117 | 0 | 0 | 0 | 0 |  | 4306 | 1896 | 6202 | 3371 | 693 | 1285 | 470 | 184 | 77 | 42 | 80 | 0 | 0 | 84.42
6:00 | 36 | 134 | 150 | 190 | 0 | 0 | 0 | 282 | 262 | 0 | 0 | 320 | 250 | 0 | 0 | 0 | 120 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 17 | 18 | 17 | 19 | 25 | 25 | 33 | 33 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 28 | 0 | 17 | 10 | 14 | 10 | 22 | 36 | 0 | 0 | 0 | 260 | 260 | 184 | 26 | 0 | 10 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 11 | 8 | 12 | 80 | 185 | 0 | 0 | 0 | 30 | 42 | 5 | 5 | 100 | 189 | 40 | 5 | 5 | 94 | 0 | 7 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 50 | 30 | 0 | 0 | 0 |  | 693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 21 | 32 | 0 | 50 | 60 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 11 | 0 | 0 | 184 | 0 | 0 | 133 | 0 | 136 | 0 | 96 | 0 | 131 | 0 | 117 | 0 | 0 | 0 | 0 |  | 4353.04 | 1815 | 6168.04 | 3309 | 693 | 1301 | 482 | 184 | 77 | 42 | 80 | 0.04 | 0 | 84.41
7:00 | 36 | 134 | 100 | 190 | 0 | 0 | 0 | 277 | 232 | 0 | 0 | 280 | 270 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 17 | 18 | 17 | 16 | 25 | 25 | 33 | 33 | 3 | 0 | 77 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 32 | 0 | 17 | 10 | 44 | 50 | 22 | 36 | 0 | 0 | 0 | 240 | 230 | 188 | 26 | 0 | 10 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 80 | 148 | 0 | 0 | 0 | 30 | 42 | 5 | 5 | 100 | 188 | 56 | 5 | 5 | 85 | 0 | 7 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74 | 100 | 70 | 0 | 0 | 0 |  | 842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 20 | 32 | 0 | 50 | 60 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 11 | 0 | 0 | 184 | 0 | 0 | 133 | 0 | 135 | 0 | 96 | 0 | 130 | 0 | 118 | 0 | 0 | 0 | 0 |  | 4296.74 | 1962 | 6258.74 | 3158 | 842 | 1206 | 669 | 184 | 77 | 42 | 80 | 0.74 | 0 | 84.4
8:00 | 36 | 134 | 100 | 190 | 0 | 0 | 0 | 260 | 233 | 0 | 0 | 280 | 285 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 17 | 18 | 17 | 16 | 25 | 25 | 33 | 33 | 8 | 0 | 77 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 32 | 0 | 17 | 10 | 46 | 50 | 22 | 8 | 0 | 0 | 0 | 240 | 220 | 203 | 26 | 0 | 10 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 80 | 150 | 0 | 0 | 0 | 30 | 42 | 5 | 5 | 100 | 188 | 40 | 5 | 5 | 102 | 0 | 7 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 34 | 0 | 0 | 0 |  | 842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 19 | 32 | 0 | 50 | 60 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 11 | 0 | 0 | 184 | 0 | 0 | 135 | 0 | 130 | 0 | 96 | 0 | 130 | 0 | 165 | 0 | 0 | 0 | 0 |  | 4259 | 2005 | 6264 | 3147 | 842 | 1235 | 655 | 184 | 77 | 42 | 80 | 2 | 0 | 84.39
9:00 | 36 | 134 | 100 | 190 | 0 | 0 | 0 | 300 | 232 | 0 | 0 | 280 | 275 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 17 | 18 | 17 | 13 | 25 | 25 | 33 | 33 | 13 | 0 | 78 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 0 | 32 | 0 | 17 | 10 | 45 | 50 | 22 | 4 | 0 | 0 | 0 | 240 | 195 | 223 | 26 | 0 | 10 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 11 | 8 | 0 | 96 | 150 | 0 | 0 | 0.1 | 30 | 42 | 5 | 5 | 100 | 174 | 66 | 5 | 5 | 103 | 0 | 7 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 100 | 34 | 0 | 0 | 0 |  | 842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 19 | 64 | 0 | 60 | 65 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 11 | 0 | 0 | 184 | 0 | 0 | 147 | 0 | 148 | 0 | 95 | 0 | 130 | 0 | 144 | 35 | 0 | 0 | 0 |  | 4355.5 | 2095 | 6450.5 | 3240 | 842 | 1238 | 716 | 184 | 78 | 42 | 96 | 14.5 | 0 | 84.38
10:00 | 36 | 134 | 142 | 190 | 0 | 0 | 0 | 355 | 238 | 0 | 0 | 280 | 280 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 17 | 18 | 17 | 13 | 25 | 25 | 0 | 29 | 8 | 0 | 78 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 32 | 0 | 17 | 10 | 45 | 50 | 22 | 3 | 0 | 0 | 0 | 240 | 220 | 203 | 26 | 0 | 10 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 11 | 8 | 0 | 98 | 150 | 0 | 0 | 1.7 | 30 | 42 | 5 | 5 | 100 | 176 | 67 | 5 | 0 | 105 | 0 | 7 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.3 | 100 | 34 | 0 | 0 | 0 |  | 842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 20 | 64 | 0 | 60 | 65 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 0 | 0 | 184 | 0 | 0 | 163 | 0 | 154 | 0 | 94 | 0 | 131 | 0 | 142 | 35 | 0 | 0 | 0 |  | 4439 | 2105 | 6544 | 3331 | 842 | 1226 | 723 | 184 | 78 | 42 | 98 | 20 | 0 | 84.37
11:00 | 36 | 134 | 100 | 190 | 0 | 0 | 0 | 360 | 251 | 0 | 0 | 300 | 250 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 17 | 18 | 17 | 0 | 25 | 0 | 25 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 32 | 0 | 17 | 20 | 60 | 50 | 22 | 2 | 0 | 0 | 0 | 260 | 220 | 158 | 26 | 0 | 10 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 8 | 8 | 0 | 98 | 150 | 0 | 0 | 2.4 | 30 | 42 | 5 | 5 | 0 | 173 | 40 | 5 | 5 | 97 | 0 | 7 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 100 | 34 | 0 | 0 | 0 |  | 842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 20 | 48 | 0 | 60 | 65 | 0 | 0 | 25 | 0 | 24 | 0 | 0 | 0 | 3 | 3 | 11 | 0 | 0 | 183 | 0 | 0 | 165 | 0 | 155 | 0 | 94 | 0 | 140 | 0 | 165 | 17 | 0 | 17 | 0 |  | 4068.4 | 2157 | 6225.4 | 3067 | 842 | 1176 | 717 | 183 | 78 | 42 | 98 | 22.4 | 0 | 84.36
12:00 | 36 | 133 | 100 | 120 | 0 | 0 | 0 | 300 | 257 | 0 | 0 | 300 | 280 | 0 | 0 | 0 | 20 | 0 | 75 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 6 | 0 | 18 | 17 | 0 | 25 | 0 | 25 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 18 | 212 | 0 | 0 | 0 | 0 | 32 | 0 | 17 | 40 | 90 | 50 | 22 | 4 | 0 | 0 | 0 | 240 | 220 | 177 | 26 | 0 | 10 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 8 | 8 | 0 | 52 | 150 | 0 | 0 | 2.6 | 30 | 42 | 8 | 5 | 0 | 177 | 68 | 5 | 5 | 110 | 0 | 7 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.3 | 100 | 60 | 0 | 0 | 0 |  | 842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 20 | 48 | 0 | 60 | 60 | 0 | 0 | 25 | 0 | 24 | 0 | 0 | 0 | 3 | 3 | 11 | 0 | 0 | 183 | 0 | 0 | 162 | 0 | 152 | 0 | 95 | 0 | 155 | 0 | 163 | 17 | 0 | 0 | 0 |  | 4115.9 | 2143 | 6258.9 | 3028 | 842 | 1186 | 824 | 183 | 79 | 42 | 52 | 22.9 | 0 | 84.35
13:00 | 36 | 134 | 100 | 120 | 0 | 0 | 0 | 356 | 308 | 0 | 0 | 350 | 270 | 0 | 0 | 0 | 20 | 0 | 108 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 6 | 17 | 18 | 17 | 13 | 25 | 0 | 33 | 17 | 0 | 0 | 80 | 0 | 0 | 0 | 25 | 204 | 0 | 0 | 0 | 0 | 51 | 0 | 17 | 40 | 102 | 50 | 22 | 4 | 0 | 0 | 0 | 300 | 250 | 189 | 26 | 0 | 10 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 64 | 150 | 0 | 0 | 2.5 | 30 | 42 | 8 | 5 | 0 | 173 | 62 | 5 | 5 | 98 | 0 | 8 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.5 | 100 | 70 | 0 | 0 | 0 |  | 842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 21 | 48 | 0 | 60 | 60 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 0 | 0 | 185 | 0 | 0 | 203 | 0 | 168 | 0 | 96 | 0 | 171 | 0 | 195 | 17 | 0 | 0 | 0 |  | 4507 | 2217 | 6724 | 3282 | 842 | 1352 | 855 | 185 | 80 | 42 | 64 | 22 | 0 | 84.34
14:00 | 36 | 134 | 100 | 120 | 0 | 0 | 0 | 359 | 307 | 0 | 0 | 370 | 280 | 0 | 0 | 0 | 20 | 0 | 108 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 6 | 17 | 18 | 17 | 0 | 25 | 0 | 33 | 29 | 0 | 0 | 80 | 0 | 0 | 0 | 25 | 215 | 0 | 0 | 0 | 0 | 51 | 0 | 17 | 40 | 105 | 50 | 22 | 7 | 0 | 0 | 0 | 280 | 250 | 200 | 26 | 0 | 10 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 80 | 171 | 0 | 0 | 2.2 | 30 | 42 | 8 | 5 | 0 | 171 | 67 | 5 | 5 | 118 | 0 | 5 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.2 | 100 | 70 | 0 | 0 | 0 |  | 842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 24 | 64 | 0 | 60 | 60 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 0 | 0 | 185 | 0 | 0 | 190 | 0 | 155 | 0 | 97 | 0 | 172 | 0 | 190 | 35 | 0 | 0 | 0 |  | 4590.4 | 2225 | 6815.4 | 3305 | 842 | 1360 | 902 | 185 | 80 | 42 | 80 | 19.4 | 0 | 84.33
15:00 | 36 | 134 | 100 | 120 | 0 | 0 | 0 | 351 | 329 | 0 | 0 | 430 | 280 | 0 | 0 | 0 | 110 | 0 | 142 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 6 | 17 | 18 | 17 | 16 | 25 | 15 | 33 | 29 | 12 | 0 | 80 | 0 | 0 | 0 | 25 | 204 | 0 | 0 | 0 | 0 | 51 | 0 | 17 | 10 | 105 | 50 | 0 | 2 | 0 | 0 | 0 | 320 | 300 | 183 | 26 | 0 | 10 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 92 | 207 | 0 | 0 | 1.7 | 60 | 42 | 8 | 5 | 0 | 255 | 64 | 5 | 5 | 93 | 0 | 5 | 10 | 280 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.9 | 100 | 70 | 0 | 0 | 4 |  | 843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 22 | 64 | 0 | 60 | 60 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 5 | 0 | 0 | 184 | 0 | 0 | 194 | 0 | 189 | 0 | 98 | 0 | 172 | 0 | 250 | 35 | 0 | 0 | 0 |  | 4978.6 | 2327 | 7305.6 | 3665 | 843 | 1496 | 888 | 184 | 80 | 42 | 92 | 15.6 | 0 | 84.32
16:00 | 36 | 133 | 100 | 190 | 0 | 0 | 0 | 327 | 278 | 0 | 0 | 340 | 280 | 0 | 0 | 0 | 110 | 0 | 80 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 6 | 17 | 18 | 17 | 16 | 25 | 23 | 33 | 29 | 26 | 0 | 80 | 0 | 20 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 24 | 0 | 17 | 10 | 12 | 38 | 22 | 6 | 0 | 0 | 0 | 300 | 270 | 184 | 26 | 0 | 10 | 5 | 5 | 5 | 0 | 0 | 0 | 18 | 0 | 8 | 8 | 92 | 208 | 0 | 0 | 0.3 | 60 | 42 | 8 | 5 | 0 | 253 | 51 | 5 | 5 | 96 | 0 | 6 | 10 | 251 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 20 | 70 | 0 | 0 | 7 |  | 843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 18 | 64 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 11 | 0 | 0 | 184 | 0 | 0 | 175 | 0 | 175 | 0 | 96 | 0 | 159 | 0 | 200 | 35 | 0 | 0 | 0 |  | 4585.3 | 2203 | 6788.3 | 3623 | 843 | 1272 | 668 | 184 | 80 | 17 | 92 | 9.3 |  | 84.31
17:00 | 36 | 133 | 102 | 190 | 0 | 0 | 0 | 325 | 258 | 0 | 0 | 300 | 250 | 0 | 0 | 0 | 110 | 0 | 70 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 6 | 17 | 18 | 17 | 16 | 25 | 23 | 33 | 29 | 34 | 0 | 80 | 0 | 50 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 32 | 0 | 21 | 10 | 12 | 24 | 22 | 6 | 0 | 0 | 0 | 250 | 250 | 182 | 26 | 0 | 10 | 5 | 5 | 5 | 0 | 0 | 0 | 22 | 0 | 8 | 8 | 96 | 145 | 0 | 0 | 0 | 60 | 60 | 8 | 5 | 0 | 224 | 40 | 5 | 5 | 94 | 0 | 5 | 10 | 245 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 20 | 70 | 0 | 0 | 7 |  | 842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 120 | 17 | 64 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 155 | 0 | 147 | 0 | 41 | 0 | 152 | 0 | 160 | 35 | 0 | 0 | 0 |  | 4338.2 | 2055 | 6393.2 | 3404 | 842 | 1106 | 640 | 184 | 80 | 39 | 96 | 2.2 | 0 | 84.3
18:00 | 36 | 64 | 35 | 190 | 0 | 0 | 0 | 280 | 218 | 0 | 0 | 300 | 210 | 0 | 0 | 0 | 40 | 0 | 60 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 6 | 17 | 18 | 0 | 16 | 0 | 23 | 0 | 29 | 0 | 0 | 60 | 0 | 70 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 50 | 0 | 34 | 10 | 12 | 24 | 22 | 6 | 0 | 0 | 0 | 220 | 220 | 150 | 26 | 0 | 10 | 5 | 5 | 5 | 0 | 0 | 0 | 22 | 0 | 8 | 8 | 92 | 144 | 0 | 0 | 0 | 30 | 60 | 8 | 5 | 0 | 171 | 17 | 5 | 5 | 39 | 0 | 6 | 10 | 165 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 20 | 70 | 0 | 0 | 0 |  | 842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 100 | 20 | 48 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 156 | 0 | 135 | 0 | 14 | 0 | 130 | 0 | 160 | 35 | 0 | 0 | 0 |  | 3561.1 | 1989 | 5550.1 | 2802 | 842 | 963 | 528 | 184 | 60 | 79 | 92 | 0.1 | 0 | 84.29
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.5
19:00 | 36 | 34 | 40 | 120 | 0 | 0 | 0 | 250 | 257 | 0 | 0 | 350 | 200 | 0 | 0 | 0 | 20 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 70 | 0 | 1 | 203 | 0 | 0 | 0 | 0 | 51 | 0 | 17 | 10 | 17 | 33 | 22 | 6 | 0 | 0 | 0 | 240 | 210 | 151 | 8 | 0 | 2 | 0 | 5 | 5 | 0 | 0 | 0 | 22 | 8 | 8 | 0 | 118 | 145 | 0 | 0 | 0 | 30 | 60 | 8 | 5 | 0 | 164 | 40 | 5 | 5 | 68 | 0 | 5 | 10 | 160 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 66 | 0 | 0 | 0 |  | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 120 | 28 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 140 | 0 | 135 | 0 | 52 | 0 | 130 | 0 | 165 | 35 | 0 | 0 | 0 |  | 3536 | 1430 | 4966 | 2623 | 337 | 1074 | 505 | 184 | 80 | 45 | 118 | 0 | 0 | 84.28
19:30 | 36 | 35 | 50 | 120 | 0 | 0 | 0 | 380 | 305 | 0 | 0 | 350 | 250 | 0 | 0 | 0 | 20 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 80 | 0 | 90 | 0 | 8 | 227 | 0 | 0 | 0 | 0 | 51 | 0 | 19 | 10 | 32 | 50 | 22 | 10 | 0 | 0 | 0 | 260 | 250 | 182 | 8 | 0 | 2 | 0 | 5 | 5 | 0 | 0 | 0 | 22 | 8 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 30 | 60 | 8 | 5 | 0 | 175 | 40 | 5 | 5 | 67 | 0 | 6 | 10 | 315 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 |  | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 120 | 26 | 16 | 0 | 50 | 60 | 0 | 0 | 0 | 12 | 0 | 0 | 1 | 0 | 22 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 164 | 0 | 159 | 0 | 51 | 0 | 135 | 0 | 140 | 28 | 0 | 0 | 0 |  | 3940 | 1538 | 5478 | 3005 | 336 | 1276 | 544 | 184 | 80 | 53 | 0 | 0 | 0 | 0
20:00 | 36 | 44 | 50 | 120 | 0 | 0 | 0 | 358 | 338 | 0 | 0 | 380 | 250 | 0 | 0 | 0 | 20 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 0 | 33 | 0 | 0 | 0 | 82 | 0 | 90 | 0 | 8 | 217 | 0 | 0 | 0 | 0 | 51 | 0 | 34 | 10 | 31 | 50 | 22 | 13 | 0 | 0 | 0 | 290 | 280 | 181 | 8 | 0 | 2 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 30 | 60 | 5 | 5 | 0 | 175 | 40 | 5 | 5 | 109 | 0 | 6 | 10 | 280 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 |  | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 120 | 2 | 0 | 0 | 50 | 60 | 0 | 0 | 0 | 12 | 0 | 0 | 8 | 0 | 22 | 5 | 0 | 0 | 0 | 184 | 0 | 0 | 170 | 0 | 163 | 0 | 52 | 0 | 154 | 0 | 160 | 17 | 0 | 0 | 0 |  | 4098 | 1570 | 5668 | 3138 | 362 | 1306 | 533 | 184 | 82 | 63 | 0 | 0 | 0 | 84.27
21:00 | 36 | 44 | 50 | 120 | 0 | 0 | 0 | 343 | 337 | 0 | 0 | 380 | 250 | 0 | 0 | 0 | 20 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 18 | 33 | 12 | 0 | 0 | 82 | 0 | 100 | 0 | 8 | 204 | 0 | 0 | 0 | 0 | 51 | 0 | 34 | 10 | 50 | 50 | 0 | 10 | 0 | 0 | 0 | 290 | 280 | 184 | 8 | 0 | 3 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 162 | 0 | 0 | 0 | 30 | 60 | 5 | 5 | 0 | 167 | 52 | 5 | 5 | 106 | 0 | 6 | 10 | 290 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 |  | 637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 120 | 3 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 12 | 0 | 0 | 8 | 0 | 22 | 10 | 0 | 0 | 0 | 184 | 0 | 0 | 169 | 0 | 160 | 0 | 52 | 0 | 165 | 0 | 180 | 17 | 0 | 0 | 0 |  | 4156 | 1868 | 6024 | 3168 | 637 | 1338 | 562 | 184 | 82 | 43 | 10 | 0 | 0 | 84.26
22:00 | 36 | 44 | 50 | 120 | 0 | 0 | 0 | 331 | 335 | 0 | 0 | 380 | 220 | 0 | 0 | 0 | 20 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 25 | 33 | 28 | 0 | 0 | 82 | 0 | 100 | 0 | 8 | 216 | 0 | 0 | 0 | 0 | 40 | 0 | 17 | 10 | 19 | 29 | 22 | 10 | 0 | 0 | 0 | 250 | 250 | 202 | 8 | 0 | 3 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 163 | 0 | 0 | 0 | 30 | 60 | 5 | 5 | 0 | 170 | 52 | 5 | 5 | 122 | 0 | 6 | 10 | 270 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 |  | 637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 6 | 0 | 0 | 60 | 65 | 0 | 0 | 0 | 12 | 0 | 0 | 8 | 0 | 22 | 12 | 0 | 0 | 0 | 185 | 0 | 0 | 160 | 0 | 152 | 0 | 52 | 0 | 157 | 0 | 180 | 0 | 0 | 0 | 0 |  | 3968 | 1828 | 5796 | 3110 | 637 | 1321 | 422 | 185 | 82 | 17 | 22 | 0 | 0 | 84.25
23:00 | 36 | 44 | 50 | 120 | 0 | 0 | 0 | 334 | 336 | 0 | 0 | 380 | 220 | 0 | 0 | 0 | 20 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 16 | 25 | 32 | 28 | 28 | 0 | 0 | 82 | 0 | 100 | 0 | 8 | 202 | 0 | 0 | 0 | 0 | 41 | 0 | 17 | 10 | 19 | 19 | 22 | 24 | 0 | 0 | 0 | 250 | 250 | 190 | 8 | 0 | 36 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 170 | 0 | 0 | 0 | 30 | 60 | 5 | 5 | 0 | 167 | 68 | 5 | 47 | 113 | 0 | 6 | 10 | 265 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 |  | 843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 6 | 0 | 0 | 60 | 65 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 22 | 13 | 0 | 0 | 0 | 184 | 0 | 0 | 162 | 0 | 153 | 0 | 51 | 0 | 158 | 0 | 183 | 0 | 0 | 0 | 0 |  | 4059 | 2026 | 6085 | 3154 | 843 | 1376 | 399 | 184 | 82 | 17 | 30 | 0 | 0 | 84.24
24:00 | 36 | 44 | 50 | 120 | 0 | 0 | 0 | 325 | 338 | 0 | 0 | 380 | 230 | 0 | 0 | 0 | 20 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 10 | 25 | 32 | 28 | 28 | 0 | 0 | 82 | 0 | 100 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 51 | 0 | 17 | 0 | 0 | 0 | 22 | 24 | 0 | 0 | 0 | 250 | 250 | 196 | 8 | 0 | 40 | 0 | 5 | 5 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 38 | 170 | 0 | 0 | 0 | 30 | 60 | 5 | 5 | 0 | 167 | 56 | 5 | 5 | 93 | 0 | 6 | 10 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 7 | 0 | 0 | 60 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 10 | 0 | 0 | 0 | 184 | 0 | 0 | 158 | 0 | 149 | 0 | 51 | 0 | 154 | 0 | 184 | 0 | 0 | 0 | 0 |  | 3898 | 1988 | 5886 | 3114 | 843 | 1321 | 287 | 184 | 82 | 17 | 38 | 0 | 0 | 84.23
KWH | 870000 | 2768400 | 3678000 | 3921750 | 0 | 9409 | 0 | 7813120 | 6747000 | 0 | 0 | 8158125 | 6185745 | 0 | 0 | 0 | 2059128 | 0 | 2065000 | 0 | 0 | 195264 | 0 | 0 | 0 | 0 | 163584 | 250200 | 321304 | 314000 | 254448 | 575000 | 460440 | 651900 | 616900 | 139116 | 0 | 1794933 | 0 | 700000 | 0 | 144783 | 4858997 | 0 | 0 | 0 | 0 | 966240 | 0 | 465217 | 359880 | 1029120 | 861120 | 472080 | 389280 | 0 | 0 | 0 | 6768000 | 6304500 | 4473000 | 602181 | 0 | 334872 | 100320 | 120000 | 207136 | 0 | 0 | 9389 | 96840 | 111240 | 202700 | 128770 | 1705920 | 4052000 | 0 | 59832 | 12650 | 805000 | 1162938 | 162600 | 210000 | 1130596 | 4498000 | 1209000 | 193920 | 360000 | 2364160 | 0 | 286800 | 114480 | 6701500 | 484560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137565 | 1880640 | 987840 | 0 | 0 | 57600 |  | 17936000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139200 | 70528 | 0 | 2871000 | 419300 | 1121280 | 4432 | 1314000 | 1470000 | 0 | 0 | 369748 | 51390 | 35583 | 0 | 52320 | 0 | 193920 | 128304 | 131670 | 0 | 0 | 4097400 | 0 | 0 | 4134536 | 0 | 3831273 | 0 | 1934209 | 0 | 3789664 | 0 | 3826320 | 394080 | 0 | 11520 | 0 |  | 108296032 | 48327677 | 156623709 | 82362718 | 17936000 | 31995400 | 15531998 | 4097400 | 1794933 | 1049125 | 1705920 | 150215 | 0
Fuel Cost | 748200 | 2380824 | 3163080 | 3372705 | 0 | 7621.29 | 0 | 4766003.2 | 4115670 | 0 | 0 | 5465943.75 | 93961466.55 | 0 | 0 | 0 | 1338433.2 | 0 | 2292150 | 0 | 0 | 1286789.76 | 0 | 0 | 0 | 0 | 1091105.28 | 1783926 | 2008150 | 1968780 | 190836 | 431250 | 0 | 0 | 0 | 1316037.36 | 0 | 0 | 0 | 770000 | 0 | 1371095.01 | 3206938.02 | 0 | 0 | 0 | 0 | 8493249.6 | 0 | 4526561.41 | 2227657.2 | 6648115.2 | 5631724.8 | 401268 | 0 | 0 | 0 | 0 | 4196160 | 4350105 | 3131100 | 415504.89 | 0 | 224364.24 | 86275.2 | 110400 | 169851.52 | 0 | 0 | 69666.38 | 74566.8 | 83430 | 156079 | 96577.5 | 11668492.8 | 3039000 | 0 | 46070.64 | 0 | 837200 | 1209455.52 | 156096 | 189000 | 881864.88 | 3148600 | 1378260 | 207494.4 | 396000 | 2695142.4 | 0 | 266724 | 106466.4 | 4288960 | 363420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9226425.6 | 0 | 0 | 0 |  | 91473600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1567392 | 830819.84 | 0 | 1980990 | 415107 | 8297472 | 149269.76 | 1379700 | 1543500 | 0 | 0 | 3312942.08 | 444523.5 | 316688.7 | 0 | 519014.4 | 0 | 213312 | 120605.76 | 99674.19 | 0 | 0 | 15815964 | 0 | 0 | 2811484.48 | 0 | 2681891.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 218234333.8 | 133973950.81 | 352208284.61 | 58588458.29 | 91473600 | 17612897.09 | 146661887.34 | 15815964 | 0 | 10386985.09 | 11668492.8 | 0 | 0
Yesterday Day Peak | 36 | 134 | 142 | 190 | 0 | 0 | 0 | 355 | 238 | 0 | 0 | 280 | 280 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 17 | 18 | 17 | 13 | 25 | 25 | 0 | 29 | 8 | 0 | 78 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 32 | 0 | 17 | 10 | 45 | 50 | 22 | 3 | 0 | 0 | 0 | 240 | 220 | 203 | 26 | 0 | 10 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 11 | 8 | 0 | 98 | 150 | 0 | 0 | 1.7 | 30 | 42 | 5 | 5 | 100 | 176 | 67 | 5 | 0 | 105 | 0 | 7 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.3 | 100 | 34 | 0 | 0 | 0 |  | 842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 20 | 64 | 0 | 60 | 65 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 0 | 0 | 184 | 0 | 0 | 163 | 0 | 154 | 0 | 94 | 0 | 131 | 0 | 142 | 35 | 0 | 0 | 0 |  | 6544 | DayPeak
Yesterday Evening Peak | 36 | 44 | 50 | 120 | 0 | 0 | 0 | 343 | 337 | 0 | 0 | 380 | 250 | 0 | 0 | 0 | 20 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 18 | 33 | 12 | 0 | 0 | 82 | 0 | 100 | 0 | 8 | 204 | 0 | 0 | 0 | 0 | 51 | 0 | 34 | 10 | 50 | 50 | 0 | 10 | 0 | 0 | 0 | 290 | 280 | 184 | 8 | 0 | 3 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 162 | 0 | 0 | 0 | 30 | 60 | 5 | 5 | 0 | 167 | 52 | 5 | 5 | 106 | 0 | 6 | 10 | 290 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 |  | 637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 120 | 3 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 12 | 0 | 0 | 8 | 0 | 22 | 10 | 0 | 0 | 0 | 184 | 0 | 0 | 169 | 0 | 160 | 0 | 52 | 0 | 165 | 0 | 180 | 17 | 0 | 0 | 0 |  | 6024 | EvPeak
Forecast for Evening | 36 | 135 | 100 | 190 | 0 | 108 | 78 | 412 | 360 | 110 | 0 | 450 | 305 | 92 | 100 | 55 | 215 | 0 | 218 | 100 | 100 | 102 | 149 | 100 | 51 | 0 | 48 | 54 | 55 | 55 | 19 | 25 | 32 | 33 | 33 | 51 | 0 | 80 | 0 | 110 | 0 | 16 | 225 | 0 | 0 | 0 | 0 | 51 | 50 | 85 | 78 | 105 | 50 | 22 | 20 | 0 | 0 | 0 | 360 | 360 | 221 | 100 | 100 | 40 | 5 | 5 | 45 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 156 | 202 | 87 | 20 | 0 | 60 | 60 | 51 | 44 | 163 | 270 | 66 | 86 | 47 | 120 | 0 | 46 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 112 |  | 958 | 46 | 0 | 0 | 115 | 0 | 0 | 0 | 35 | 80 | 40 | 120 | 33 | 110 | 26 | 60 | 65 | 50 | 54 | 100 | 35 | 50 | 40 | 43 | 30 | 22 | 17 | 11 | 0 | 0 | 200 | 17 | 18 | 200 | 0 | 225 | 0 | 95 | 100 | 220 | 0 | 282 | 105 | 0 | 113 | 0
Forecast for Day | 36 | 135 | 100 | 190 | 0 | 50 | 78 | 412 | 360 | 110 | 0 | 450 | 305 | 92 | 100 | 55 | 150 | 0 | 150 | 100 | 100 | 102 | 149 | 100 | 51 | 0 | 48 | 54 | 55 | 55 | 19 | 25 | 32 | 33 | 33 | 51 | 0 | 80 | 0 | 100 | 0 | 16 | 225 | 0 | 0 | 0 | 0 | 51 | 50 | 85 | 78 | 105 | 50 | 22 | 7 | 0 | 0 | 0 | 360 | 360 | 221 | 26 | 0 | 40 | 5 | 5 | 45 | 0 | 0 | 52 | 0 | 11 | 10 | 0 | 132 | 202 | 87 | 0 | 2 | 60 | 60 | 51 | 44 | 163 | 200 | 66 | 86 | 47 | 120 | 0 | 46 | 10 | 341 | 25 | 11 | 100 | 200 | 200 | 100 | 200 | 100 | 149 | 20 | 100 | 200 | 150 | 0 | 112 |  | 860 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 120 | 33 | 110 | 0 | 60 | 65 | 0 | 0 | 100 | 35 | 50 |  | 43 | 0 | 22 | 17 | 11 | 0 | 0 | 200 | 0 | 0 | 200 | 0 | 225 | 0 | 95 | 0 | 176 | 0 | 282 | 105 | 0 | 113 | 0
Generation at 08:00(Today) | 36 | 43 | 50 | 120 | 0 | 0 | 0 | 323 | 257 | 0 | 0 | 320 | 230 | 0 | 0 | 0 | 20 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 30 | 24 | 29 | 0 | 0 | 80 | 0 | 100 | 0 | 0 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 22 | 15 | 0 | 0 | 0 | 250 | 250 | 202 | 26 | 0 | 10 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 58 | 170 | 0 | 0 | 1 | 30 | 60 | 5 | 5 | 0 | 168 | 68 | 5 | 5 | 95 | 0 | 6 | 10 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.26 | 0 | 0 | 0 | 0 | 0 | 0 | 846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 7 | 0 | 0 | 60 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 5 | 0 | 0 | 184 | 0 | 0 | 135 | 0 | 150 | 0 | 41 | 0 | 120 | 0 | 180 | 0 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 6168.04 | 6:00
| Highest Generation |  | 7305.6 | 15:00
| Day Peak Generation |  | 6544 | 10:00
| Evening Peak Generation |  | 6024 | 21:00
| HVDC Max Flow |  | 843 | 15:00
| HVDC EvPeak Flow |  | 637 | 21:00
| Load factor L.F |  | 89.33%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-04-10
Till now the maximum generation is : - |  |  | 11623 MW | 19:30 | Hrs on | 2018-09-19
The Summary of Yesterday's |  | 2019-04-09 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6544 | MW Hour : | 10:00 | Min. Gen. at | 5:00 | 5019 | MW
Evening Peak Generation : |  | 6024 | MW Hour : | 21:00 | Available Max Generation : |  | 13779 | MW
E.P. Demand (at gen end) : |  | 6024 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 9500 | MW
Maximum Generation : |  | 7305.6 | MW Hour : | 15:00 | Reserve(Generation end) |  | 4279 | MW
Total Gen. (MKWH) : |  | 156.6237 | System Load Factor : | 89.33% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -420 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-04-10
Actual : | 84.17 | Ft.(MSL) , | Rule curve : | 86.2 | Ft.( MSL )
Gas Consumed : | Total = | 963.8 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 76201355.38
|  | Coal : | 15815964 | Oil : | 157048872.43 | Total : | 249066191.81
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3302.6346 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1118.4 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1001.2157 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 904.3869 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 817.4445 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 659.637 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 374.8571 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 169.9981 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 508.716 |  |  | 0 | 0%
Total | 0 |  | 8857.2899 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1.2 |  | 7) Raozan #02.
|  |  |  | 2) Khulna ST 110 MW |  | 8) Haripur SBU-1,2
|  |  |  | 3) Ghorasal Max 78 MW |  | 9) Ghorashal Unit-1
|  |  |  | 4) Bheramara 410 MW. |  | 10) Sikalbaha ST 60 MW
|  |  |  | 5) Siddhirganj ST |  | 11) Sikalbaha Peaking GT
6) Ashuganj #3,4,5
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) After maintenance Siddhirganj 132/33 kV T-1 was switched on at 09:10.
b) Thakurgaon 132/33 kV T-1 & T-1 transformer tripped at 09:05 from 33 kV side due to 33 kV feeder fault and |  |  |  | About 15 MW power interruption occurred under Thakurgaon S/S areas
were switched on at 09:40. |  |  |  | from 09:05 to 09:40
c) Kishoreganj 132/33 kV T2 transformer was shut down from 11:35 to 11:45 due to 33 kV bus fault.
d) After maintenance Feni-Baroierhat 132 Ckt-2 was switched on at 12:49
e) Ghorasal- Ishwardi 230 kV Ckt-1 tripped at 11:25 from Ghorasal end showing distance R phase and was switched on at 11:54.
f) Hathazari-Kaptai 132 kV Ckt-1 was shut down from 11:46 to 12:58 for clean uf right of way.
g) Rajshahi-Natore 132 kV Ckt-1 was shut down from 10:52 to 11:56 for red hot maintenance at Rajshahi end
h) Rajshahi 132/33 kV T2 transformer was shut down from 10:28 to 14:35 due to 33 kV CB terminal red hot. |  |  |  | About 10 MW power interruption occurred under Rajshahi S/S areas
from 10:28 to 14:35
i) Bhulta 132/33 kV T1 transformer tripped at 11:21 showing VAJ,HVPH relay and was switched on at 11:32.
j) Daudkandi-Cumilla(N) 132 kV Ckt-1 tripped 11:41 from both end showing dist Z1,B phase relay at Daudkandi end
& directional O/C B phase relay at Cumilla(N) end and was switched on at 11:54.
k) Siddhirganj 335 MW CCPP was shut down from 10:18 to 11:14 STG commissioning work.
l) Halishahar 132/33 kV T1 transformer was shut down from 13:10 to 14:10 for checking CB test. |  |  |  | About 35 MW power interruption occurred under Halishahar S/S areas
from 13:10 to 14:10
m) After maint Raozan # 01 was synchronized at 15:41.
n) Narsingdi 132 kV Bus-2 was shut down from 14:12 to 16:46 due to red hot.
o) Bogura- Sirajganj 132 kV Ckt-1 tripped at 16:20 from Bogura end showing distance ABC phase, Z1 fault and
was switched on at 16:41.
p) Baghabari 100 MW tripped at 18:15 and was switched on at 19:27.
q) Madanganj- Sitalakhya 132 kV Ckt tripped at 18:15 from Madanganj end showing distance A phase relay and
was switched on at 19:35.
r) Haripur- Ullon (Maniknagar-2)132 kV Ckt tripped at 18:17 from Haripur end showing Z1,R phase relay and was
switched on at 18:31 again Haripur- Ullon 132 kV Ckt tripped at 19:44 from both end showing Z1,B(RYB) phase
relay at Haripur end and Z1,B phase at Ullon end and was switched on at 19:53.
s) Siddhirganj- Ullon 132 kV Ckt tripped at 18:18 from both end showing dist Z1,B phase relay at Ullon end and |  |  |  | About 70 MW power interruption occurred under Dhanmondi S/S areas
dist Z1,(C-N) phase relay at Siddhirganj end and was switched 18:38. |  |  |  | from 18:18 to 18:38
t) Feni-Chowmohoni 132 kV Ckt was shut down from 21:20 to due to23:08 emergency maintenance.
u) Haripur-Shyampur (N)132 kV Ckt tripped at 18:12 from Haripur end showing Z1,A-N relay at haripur end &
dist Z1,r phase pick up at Shyampur end and was switched 18:42.
v) Shyampur(O)-Shyampur (N) 132 kV Ckt tripped at 18:12 from Shyampur(N) end showing 86 lock out and was switched 18:43.
w) Feni-Cumilla(N) 132 kV Ckt-2 tripped at 19:29 from Cumilla(N) end showing dist A-phase and was switched on at 19:32.
x) Feni-Baroierhat 132 kV Ckt-2 was shut down from19:38 to 01:39 Feni end due to TCSR problem.
y) Magbazar-Rampura 132 kV Ckt-1,2 tripped at 18:07 from Magbazar end due to bus bar protection operated |  |  |  | About 102 MW power interruption occurred under Magbazar S/S areas
and was switched on at 18:44. |  |  |  | from 18:07 to 18:44
z) Ashuganj-Bhulta 400 kV Ckt was shut down since at 22:47 Bhulta end due to red hot maint
AA) Magura 33 kV bus was S/D from 07:04 to 07:32 due to 33 kV feeder fault. |  |  |  | About 18 MW power interruption occurred under Magura S/S areas
from 07:04 to 07:32(10/04/2019)

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-04-09 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 36 | 870000 | Unit-1 under maint.
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 44 | 2768400 | On test
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 50 | 3678000 | On test
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 120 | 3921750 | Bad Weather.
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 0 | 0
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 0 | 9409 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 343 | 7813120 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 0 | 0 | Reserve
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 337 | 6747000 | Frequency control
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 380 | 8158125 | Bad Weather.
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 250 | 6185745 | Bad Weather.
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 254448 | Tripped at 18:10
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 87 | 2065000 | FGMO
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 0 | Reserve
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 20 | 2059128 | Bad Weather.
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 0 | 195264 | Reserve
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 6 | 163584
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 0 | 250200 | Reserve
25 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 0 | 321304 | Reserve
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 0 | 314000 | Reserve
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Reserve
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 43 | 1035440 | Bad Weather.
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 651900
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 12 | 616900 | Bad Weather.
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 0 | 139116 | Reserve
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
34 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
35 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
36 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
37 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
38 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 0 | 0 | Reserve
| Dhaka area Total |  |  |  | 5798 | 1761 | 48217833
39 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 100 | 700000 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 8 | 144783 | Low demand
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 137565
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 50 | 861120
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 82 | 1794933 | Low water lavel
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4858997 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under S/D
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 966240
47 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
48 | Dohazari Peaking |  | PDB | 6*17 | 102 | 34 | 465217 | Low demand
49 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 359880 | Low demand
| Juldah 100 MW Unit-3 |  | IPP | 0 | 100 | 100 | 1880640
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 472080 | Bad Weather.
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 10 | 389280
51 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 50 | 1029120 | Low demand
| Chattogram area Total |  |  |  | 1681 | 699 | 14059855
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 184 | 4473000 | FGMO
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 290 | 6768000 | Bad Weather.
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 280 | 6304500 | Bad Weather.
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 3 | 334872 | Gas shortage
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 0 | 100320 | Bad Weather.
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 8 | 602181 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 5 | 207136 | Gas shortage
| Midland 150MW |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
61 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
62 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
63 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
| Chandpur Desh 200MW |  | IPP | 0 | 200 | 0 | 987840 | Reserve
64 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 0 | 96840 | Tripped due to Bad weather.
65 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 111240 | Tripped due to Bad weather.
** | Tripura |  | Imported power | 0 | 160 | 10 | 1705920 | Bad Weather.
66 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 0 | 202700 | Tripped due to Bad weather.
67 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 0 | 9389 | Reserve
68 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 0 | 128770 | Bad Weather.
69 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 785 | 22152708
70 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 162 | 4052000 | Bad Weather.
71 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 0 | 59832 | Bad Weather.
72 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 0 | 0 | Bad Weather.
73 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 12650
74 | United Mymensingh PPL |  | IPP | 200 | 200 | 0 | 0 | Reserve
| United Jamalpur PPL |  | IPP | 115 MW | 115 | 0 | 57600 | Reserve
| Mymensingh Area Total |  |  |  | 637 | 162 | 4182082
75 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 30 | 805000
76 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1162938
77 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 0 | 1130596 | Bad Weather.
78 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 167 | 4498000 | Frequency control
79 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 5 | 162600 | Bad Weather.
80 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 5 | 210000 | Bad Weather.
81 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Bad Weather.
82 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 52 | 1209000 | FGMO
83 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 5 | 193920 | Frequency control
84 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 5 | 360000 | Bad Weather.
85 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 106 | 2364160 | FGMO
86 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
87 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 6 | 286800 | Bad Weather.
88 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 8 | 484560 | Bad Weather.
89 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 290 | 6701500 | FGMO
| Bibiyana-3 285MW |  | PDB | 285 MW | 0 | 0 | 0 | On test
90 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 114480
| Sylhet Area Total |  |  |  | 1549 | 749 | 19683554
91 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 637 | 17936000
92 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
93 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Bad Weather.
94 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 9 | 139200
95 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
96 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 0 | 70528 | Bad Weather.
97 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
98 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
99 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
| Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 17 | 394080 | Low demand
| Madhumati Power Plant |  | IPP | 100 MW | 0 | 0 | 0 | on test.
| Khulna Area Total |  |  |  | 2209 | 663 | 18539808
100 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 0 | 1121280 | Reserve
101 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 4432 | Reserve
102 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 3 | 419300 | Bad Weather.
103 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 120 | 2871000 | ST under maintenance
104 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 52 | 1934209 | Bad Weather.
| Barisal Area Total |  |  |  | 462 | 175 | 6350221
105 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 60 | 1470000 | Gas shortage
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 60 | 1314000 | Gas shortage
106 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
107 | Bera Peaking |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
108 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 12 | 51390 | Low demand
109 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 35583 | Reserve
110 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
111 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 169 | 4134536 | FGMO
112 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 160 | 3831273 | FGMO
113 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 165 | 3789664 | FGMO
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282 | 282 | 180 | 3826320 | Frequency control
114 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
115 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 193920
116 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 10 | 128304 | Bad Weather.
117 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 0 | 131670 | Tripped due to Bad weather.
118 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 8 | 52320 | Bad Weather.
119 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 0 | 369748 | Reserve
| Paramount Baghabari |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
| Confidence CPBL-2 |  | IPP | 113 MW | 113 | 0 | 11520 | Reserve
| Rajshahi Area Total |  |  |  | 1938 | 846 | 19340248
120 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
121 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 184 | 4097400
122 | Rangpur GT |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
123 | Saidpur GT |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
| Rangpur Area Total |  |  |  | 484 | 184 | 4097400
| Total |  |  |  | 17649 | 6024 | 156623709
| Eastern Grid Total |  |  |  | 12556 | 4156 | 108296032
| Western Grid Total |  |  |  | 5093 | 1868 | 48327677
| National Grid Total |  |  |  | 17649 | 6024 | 156623709
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2019-04-09 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 3879 | MW | (b) ENTIRE WESTERN GRID : |  |  | 1727 | MW
i) Dhaka area |  |  | 2364 | MW | i) Khulna area |  |  | 525 | MW
ii) Chittagong area |  |  | 695 | MW | ii) Rajshahi area |  |  | 667 | MW
iii) Comilla area |  |  | 166 | MW | iii) Barisal area |  |  | 65 | MW
iv) Mymensingh area |  |  | 386 | MW | iv) Rangpur area |  |  | 470 | MW
v) Sylhet area |  |  | 268 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 5606 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 84 | 300 | Netrokona | 49 | 2100 | Central s/s | 57 | 100
Munsiganj | 79 | 100 | Jamalpur | 62 | 100 | Noapara | 57 | 100
Sonargaon | 70 | 1800 | Sherpur | 40 | 100 | Jessore | 102 | 1400
Shyampur | 166 | 1000 | Srimongal | 27 | 1830 | Jhenida | 70 | 1930
Bhulta | 156 | 1000 | Shahjibazar | 71 | 2200 | Bottail | 80 | 100
Madanganj | 53 | 1000 | Fenchuganj | 18 | 2100 | G.K Project | 30 | 100
Shitalakhya | 112 | 1500 | Kulawara | 21 | 2100 | Faridpur | 102 | 100
Rahim steel | 28 | 1300 | Sylhet | 94 | 1830 | Madaripur | 75 | 100
Matuail | 86 | 1000 | Chatak | 19 | 1900 | Gopalganj | 46 | 100
Ghorasal | 47 | 100 | Sunamganj | 19 | 1900 | Bagerhat | 55 | 1830
Narsingdi | 97 | 100 | Biani Bazar | 34 | 1830 | Mongla | 34 | 1100
Haripur (SBU) | 96 | 900 | Comilla (S) | 120 | 1830 | Satkhira | 60 | 100
Ullon | 56 | 1400 | Comilla(N) | 72 | 1800 | Gallamari | 50 | 1300
Hasnabad | 140 | 400 | Chandpur | 77 | 1830 | Magura | 30 | 100
Magbazar | 115 | 1000 | Feni | 91 | 1830 | Chuadanga | 55 | 100
Maniknagar | 96 | 1000 | Chowmuhani | 132 | 1900 | Barisal | 98 | 1830
Bangabhaban | 28 | 1000 | Ashuganj | 31 | 800 | Patuakhali | 65 | 1930
Narinda | 76 | 1000 | Daudkandi | 68 | 1800 | Bhandaria | 28 | 100
Dhanmondi | 93 | 1000 | B.Baria | 68 | 2100 | Ishurdi | 32 | 1930
Lalbag | 83 | 1800 | Ramganj | 38 | 1830 | Ruppur Paromanobik | 1 | 100
Madartek | 35 | 2100 | Madunaghat | 54 | 1830 | Natore | 73 | 2000
Mirpur | 78 | 1500 | Hathazari | 65 | 1930 | Bogra | 141 | 700
Kalyanpur | 69 | 1400 | Khulshi | 194 | 1500 | Noagaon | 76 | 2000
Gulshan | 102 | 1000 | Halishahar | 142 | 1500 | Rajshahi | 109 | 1930
Uttara | 44 | 1800 | Baraulia | 152 | 1700 | C.Nawabganj | 58 | 700
Uttara(New) | 12 | 900 | Sikalbaha | 37 | 1900 | Amnura | 26 | 1900
Kamrangirchar | 66 | 1100 | Dohazari | 88 | 2100 | Pabna | 71 | 1500
Savar | 119 | 1000 | Cox'sbazar | 77 | 2100 | Shahjadpur | 75 | 900
Bhasantec | 124 | 1000 | Chandraghona | 23 | 2000 | Serajganj | 76 | 1500
Agargaon | 44 | 1000 | Kaptai | 2.8 | 700 | Niyamatpur | 44 | 2000
Satmosjid | 73 | 1800 | A. Khaer Stl. | 0 | 100 | Joypurhat | 32 | 100
Tongi | 104 | 1600 | Bakulia | 88 | 1500 | Mohastangor | 6 | 100
Kabirpur | 170 | 1700 | Julda | 0 | 0 | Rangpur | 104 | 1930
Basundhara | 98 | 1000 | TK chemical | 3 | 1300 | Lalmonirhat | 73 | 2000
Manikganj | 62 | 100 | Modern Steel | 14 | 1200 | Saidpur | 85 | 1930
Joydevpur | 172 | 1700 | Shahmirpur | 28 | 1500 | Purbasadipur | 74 | 1900
New Tongi | 95 | 1000 | Khagrachhari | 11 | 1100 | Thakurgaon | 58 | 1930
Kodda | 172 | 800 | Matarbari | 25 | 1930 | Palashbari | 57 | 100
Dhamrai | 32 | 2200 | Baroiar Hat | 14 | 1300 | Barapukuria | 31 | 1930
Valuka | 55 | 1500 | Rangamati | 10 | 1830 | Panchagar | 32 | 2000
Tangail | 100 | 1500 | Abul Khair 230 | 137 | 200 | Joldhaka | 10 | 100
Mymensing | 122 | 100 | BSRM | 139 | 1500
Kishorganj | 56 | 2300 | Goalpara | 28 | 1300
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-04-09
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 402 | 6:00 | 390 | 15:00 | Kaliakoir | 393 | 18:30 | 374 | 16:00
Bheramara | 403 | 19:30 | 388 | 24:00 | Bhulta | 409 | 18:30 | 391 | 10:00
Ashuganj(N) | 408 | 4:00 | 394 | 10:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 238 | 1:00 | 235 | 7:00 | Hathazari | 221 | 21:00 | 205 | 9:00
Ishurdi | 237 | 17:00 | 230 | 7:00 | Megnaghat | 236 | 18:30 | 228 | 9:00
Ashuganj | 244 | 19:00 | 235 | 10:00 | Fenchuganj | 240 | 2:00 | 233 | 12:00
Serajganj | 235 | 3:00 | 230 | 12:00 | Siddhirganj | 236 | 18:30 | 224 | 10:00
Baghabari | 232 | 17:00 | 225 | 12:00 | Maniknagar | 236 | 19:00 | 223 | 15:00
Barapukuria | 235 | 8:00 | 224 | 19:30 | Old Airport | 235 | 18:30 | 222 | 10:00
Bogra | 233 | 16:00 | 224 | 13:00 | Barisal | 242 | 4:00 | 231 | 18:30
Khulna South | 231 | 18:00 | 215 | 12:00 | AKSML | 222 | 21:00 | 205 | 15:00
Rampura | 230 | 4:00 | 223 | 10:00 | BSRM | 226 | 21:00 | 208 | 10:00
Haripur | 230 | 18:30 | 222 | 10:00 | Bibiyana | 240 | 4:00 | 232 | 11:00
Hasnabad | 233 | 19:00 | 222 | 10:00 | Bhulta | 233 | 19:00 | 224 | 10:00
Aminbazar | 234 | 19:00 | 223 | 15:00 | Ashuganj (S) | 242 | 18:30 | 234 | 10:00
Tongi | 229 | 18:30 | 220 | 10:00 | Kaliakoir | 238 | 18:30 | 225 | 16:00
Comilla (N) | 242 | 19:00 | 229 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 137 | 1830 | 130 | 1000 | Madanhat | 137 | 2100 | 127 | 1000
Munsiganj | 139 | 1830 | 128 | 1000 | Hathazari | 135 | 2100 | 125 | 900
Megnaghat | 137 | 1830 | 129 | 900 | Khulshi | 132 | 2100 | 122 | 1000
Shyampur | 138 | 1830 | 128 | 1000 | Halishahar | 130 | 300 | 125 | 1000
Bhulta | 135 | 1830 | 125 | 1500 | Baraulia | 133 | 2100 | 123 | 1000
Madanganj | 137 | 1830 | 126 | 1100 | Sikalbaha | 135 | 2100 | 126 | 1830
Shitalakhya | 139 | 1830 | 126 | 1000 | Dohazari | 135 | 2200 | 124 | 1830
Rahim steal | 137 | 1830 | 130 | 1000 | Cox'sbazar | 130 | 1300 | 118 | 1830
Matuail | 136 | 1830 | 129 | 1500 | Chandraghona | 135 | 2100 | 126 | 1000
Ghorasal | 140 | 700 | 138 | 100 | Kaptai | 130 | 100 | 130 | 200
Narsinghdi | 142 | 1830 | 128 | 1500 | A. Khaer Stl. | 134 | 2100 | 124 | 1000
Haripur (SBU) | 138 | 1830 | 131 | 1500 | Bakulia | 133 | 2100 | 124 | 1000
Ullon | 141 | 1830 | 138 | 600 | Julda | 132 | 1300 | 126 | 1000
Hasnabad | 138 | 1830 | 128 | 1000 | TK Chemical | 137 | 2200 | 126 | 1100
Magbazar | 141 | 1830 | 131 | 1000 | Modern Steel | 134 | 2100 | 123 | 1000
Maniknagar | 140 | 1830 | 132 | 1000 | Shahmirpur | 132 | 700 | 125 | 1000
Bangabhaban | 134 | 600 | 125 | 1500 | Khagrachhari | 135 | 2100 | 125 | 1000
Narinda | 138 | 600 | 131 | 1000 | Matarbari | 132 | 1300 | 119 | 1830
Dhanmondi | 141 | 1830 | 138 | 600 | Baroiar Hat | 135 | 1300 | 127 | 900
Lalbag | 134 | 600 | 125 | 1500 | Rangamati | 133 | 1400 | 125 | 1000
Madartek | 138 | 600 | 131 | 1000 | Goalpara | 137 | 1800 | 125 | 1200
Mirpur | 139 | 1830 | 129 | 1000 | Central s/s | 137 | 1800 | 125 | 1200
Kalyanpur | 140 | 1830 | 131 | 1000 | Noapara | 133 | 1800 | 121 | 1200
Gulshan | 141 | 1830 | 131 | 1000 | Jessore | 130 | 1800 | 118 | 1200
Uttara | 138 | 1830 | 127 | 1700 | Jhenida | 135 | 1800 | 120 | 1200
Uttara New | 137 | 1830 | 128 | 1000 | Bottail | 137 | 1700 | 126 | 1300
Kamrangirchar | 139 | 1830 | 125 | 1000 | G.K.Project | 141 | 1700 | 133 | 1400
Savar | 138 | 1830 | 128 | 1000 | Faridpur | 136 | 1930 | 125 | 1300
Bhasantec | 143 | 1830 | 133 | 1000 | Madaripur | 138 | 1930 | 127 | 1300
Agargaon | 142 | 1830 | 134 | 1000 | Gopalganj | 141 | 1930 | 125 | 700
Satmosjid | 143 | 1830 | 134 | 1000 | Bagerhat | 139 | 1930 | 124 | 1200
Tongi | 136 | 1800 | 130 | 1600 | Mongla | 137 | 1930 | 124 | 1200
Kabirpur | 138 | 1800 | 129 | 1500 | Satkhira | 137 | 1800 | 125 | 1200
Basundhara | 138 | 1830 | 127 | 1000 | Gallamari | 138 | 1930 | 125 | 1200
Manikganj | 138 | 2100 | 132 | 1200 | Magura | 137 | 1800 | 118 | 1200
Joydevpur | 143 | 1600 | 134 | 100 | Chuadanga | 134 | 1800 | 116 | 1200
New Tongi | 139 | 1830 | 129 | 1600 | Barisal | 141 | 2000 | 133 | 1400
Kodda | 145 | 1800 | 130 | 400 | Patuakhali | 139 | 2000 | 130 | 1300
Dhamrai | 139 | 1830 | 130 | 1500 | Bhandaria | 138 | 1930 | 127 | 1200
Valuka | 140 | 1800 | 122 | 1500 | Ishurdi | 140 | 1700 | 133 | 1300
Tangail | 142 | 1830 | 130 | 1500 | Ruppur Paromanobik | 139 | 200 | 133 | 1500
Mymensing | 141 | 1800 | 132 | 100 | Natore | 139 | 1600 | 129 | 1300
Kishorganj | 140 | 1000 | 133 | 1500 | Bogra | 142 | 1600 | 134 | 1300
Netrokona | 141 | 1800 | 130 | 1500 | Noagaon | 140 | 1600 | 128 | 1300
Jamalpur | 140 | 1800 | 127 | 100 | Rajshahi | 137 | 1600 | 125 | 1200
Sherpur | 140 | 1800 | 125 | 1500 | C.Nawabganj | 134 | 1600 | 120 | 1300
Srimongal | 140 | 700 | 137 | 1600 | Amnura | 136 | 1600 | 122 | 1200
Shahjibazar | 140 | 1100 | 135 | 1600 | Pabna | 135 | 1700 | 129 | 700
Fenchuganj | 137 | 1800 | 135 | 1200 | Shahjadpur | 144 | 1700 | 136 | 1000
Khulawara | 137 | 1930 | 135 | 900 | Serajganj | 140 | 1700 | 132 | 1200
Sylhet | 136 | 100 | 134 | 1600 | Niyamatpur | 143 | 1600 | 127 | 1200
Chatak | 137 | 400 | 134 | 1400 | Joypurhat | 143 | 1600 | 129 | 1300
Sunamganj | 136 | 100 | 133 | 1700 | Mohastangor | 140 | 1600 | 132 | 1300
Biani Bazar | 137 | 1100 | 133 | 2100 | Rangpur | 135 | 900 | 120 | 1900
Comilla(s) | 135 | 1930 | 124 | 900 | Lalmonirhat | 137 | 600 | 115 | 1900
Comilla(n) | 144 | 1900 | 134 | 900 | Saidpur | 135 | 500 | 116 | 1900
Chandpur | 140 | 1300 | 125 | 1100 | Purbasadipur | 135 | 500 | 120 | 1900
Feni | 138 | 2200 | 124 | 1000 | Thakurgaon | 134 | 600 | 110 | 1900
Chowmuhani | 136 | 2100 | 125 | 700 | Palashbari | 137 | 600 | 125 | 1900
Ashuganj | 144 | 1900 | 139 | 2300 | Barapukuria | 135 | 800 | 124 | 1930
Daudkandi | 139 | 2000 | 128 | 1000 | Panchagar | 132 | 500 | 106 | 1900
B.Baria | 142 | 1830 | 134 | 2200 | Joldhaka | 134 | 600 | 118 | 1900

## L-Curve
Date | 2019-04-09
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 300 | 3898 | 1988 | 5886 |  |  |  | QF-LDC-12
0:30 | 320 | 4550.5 | 1983.5 | 6534 | Date: | 2019-04-09
1:00 | 340 | 5203 | 1979 | 7182
1:30 | 300 | 5081.5 | 1956 | 7037.5
2:00 | 260 | 4960 | 1933 | 6893
2:30 | 210 | 4854.5 | 1923 | 6777.5 | [5 empty] | Gen. at Eve. Peak | 6024 | 6024 MW (21:00 )
3:00 | 160 | 4749 | 1913 | 6662 | [6 empty] | 21:00
3:30 | 135 | 4606 | 1911 | 6517 | [5 empty] | Gen. at Day Peak | 6544 | 6544 MW (10:00 )
4:00 | 110 | 4463 | 1909 | 6372 | [6 empty] | 10:00
4:30 | 85 | 4384.5 | 1902.5 | 6287 | [5 empty] | Highest Generation | 7305.6
5:00 | 60 | 4306 | 1896 | 6202 | [6 empty] | 15:00
5:30 | 100 | 4329.52 | 1855.5 | 6185.02
6:00 | 140 | 4353.04 | 1815 | 6168.04
6:30 | 150 | 4324.89 | 1888.5 | 6213.39
7:00 | 160 | 4296.74 | 1962 | 6258.74
7:30 | 240 | 4277.87 | 1983.5 | 6261.37
8:00 | 320 | 4259 | 2005 | 6264
8:30 | 360 | 4307.25 | 2050 | 6357.25
9:00 | 400 | 4355.5 | 2095 | 6450.5
9:30 | 395 | 4397.25 | 2100 | 6497.25
10:00 | 390 | 4439 | 2105 | 6544
10:30 | 370 | 4253.7 | 2131 | 6384.7
11:00 | 350 | 4068.4 | 2157 | 6225.4
11:30 | 292.5 | 4092.15 | 2150 | 6242.15
12:00 | 235 | 4115.9 | 2143 | 6258.9
12:30 | 202.5 | 4311.45 | 2180 | 6491.45
13:00 | 170 | 4507 | 2217 | 6724
13:30 | 205 | 4548.7 | 2221 | 6769.7
14:00 | 240 | 4590.4 | 2225 | 6815.4
14:30 | 330 | 4784.5 | 2276 | 7060.5
15:00 | 420 | 4978.6 | 2327 | 7305.6
15:30 | 495 | 4781.95 | 2265 | 7046.95
16:00 | 570 | 4585.3 | 2203 | 6788.3
16:30 | 615 | 4461.75 | 2129 | 6590.75
17:00 | 660 | 4338.2 | 2055 | 6393.2
17:30 | 510 | 3949.65 | 2022 | 5971.65
18:00 | 360 | 3561.1 | 1989 | 5550.1
18:30 | 390 | 3548.55 | 1709.5 | 5258.05
19:00 | 420 | 3536 | 1430 | 4966
19:30 | 280 | 3940 | 1538 | 5478
20:00 | 250 | 4098 | 1570 | 5668 |  |  |  | Executive Engineer
20:30 | 190 | 4127 | 1719 | 5846 |  |  |  | Network Operation Division
21:00 | 130 | 4156 | 1868 | 6024
21:30 | 105 | 4062 | 1848 | 5910
22:00 | 80 | 3968 | 1828 | 5796 |  |  |  |  | Page 6 of 7
22:30 | 170 | 4013.5 | 1927 | 5940.5
23:00 | 260 | 4059 | 2026 | 6085
23:30 | 280 | 3978.5 | 2007 | 5985.5
24:00 | 300 | 3898 | 1988 | 5886
6024 MW (21:00 )
6544 MW (10:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-04-09 |  | Energy | 156623709
[10 empty] | 2019-04-09 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3114 | 843 | 1321 | 287 | 184 | 82 | 17 | 0 | 38
0:30 | 3449.5 | 773 | 1416.5 | 518 | 184 | 81.5 | 46.5 | 0 | 65 | Date: | 2019-04-09
1:00 | 3785 | 703 | 1512 | 749 | 184 | 81 | 76 | 0 | 92
1:30 | 3736 | 698 | 1506.5 | 674.5 | 184 | 81 | 65.5 | 0 | 92 | [7 empty] | Total Energy | 156.6237 | Total Energy Gen 156.624 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 156.624 MKWHr
2:00 | 3687 | 693 | 1501 | 600 | 184 | 81 | 55 | 0 | 92 | [7 empty] | Energy not Served | 0
2:30 | 3669.5 | 693 | 1436.5 | 571.5 | 184 | 81 | 54 | 0 | 88 | [7 empty] | Energy Requirement | 156.6237
3:00 | 3652 | 693 | 1372 | 543 | 184 | 81 | 53 | 0 | 84
3:30 | 3551.5 | 693 | 1356 | 520 | 184 | 80 | 48.5 | 0 | 84 | [6 empty] | Shortage
4:00 | 3451 | 693 | 1340 | 497 | 184 | 79 | 44 | 0 | 84
4:30 | 3411 | 693 | 1312.5 | 483.5 | 184 | 78 | 43 | 0 | 82
5:00 | 3371 | 693 | 1285 | 470 | 184 | 77 | 42 | 0 | 80
5:30 | 3340 | 693 | 1293 | 476 | 184 | 77 | 42 | 0 | 80
6:00 | 3309 | 693 | 1301 | 482 | 184 | 77 | 42 | 0 | 80
6:30 | 3233.5 | 767.5 | 1253.5 | 575.5 | 184 | 77 | 42 | 0 | 80 |  |  |  |  | Coal
7:00 | 3158 | 842 | 1206 | 669 | 184 | 77 | 42 | 0 | 80
7:30 | 3152.5 | 842 | 1220.5 | 662 | 184 | 77 | 42 | 0 | 80 |  |  |  | Oil |  |  |  | ,
8:00 | 3147 | 842 | 1235 | 655 | 184 | 77 | 42 | 0 | 80
8:30 | 3193.5 | 842 | 1236.5 | 685.5 | 184 | 77.5 | 42 | 0 | 88
9:00 | 3240 | 842 | 1238 | 716 | 184 | 78 | 42 | 0 | 96
9:30 | 3285.5 | 842 | 1232 | 719.5 | 184 | 78 | 42 | 0 | 97
10:00 | 3331 | 842 | 1226 | 723 | 184 | 78 | 42 | 0 | 98
10:30 | 3199 | 842 | 1201 | 720 | 183.5 | 78 | 42 | 0 | 98
11:00 | 3067 | 842 | 1176 | 717 | 183 | 78 | 42 | 0 | 98
11:30 | 3047.5 | 842 | 1181 | 770.5 | 183 | 78.5 | 42 | 0 | 75
12:00 | 3028 | 842 | 1186 | 824 | 183 | 79 | 42 | 0 | 52
12:30 | 3155 | 842 | 1269 | 839.5 | 184 | 79.5 | 42 | 0 | 58
13:00 | 3282 | 842 | 1352 | 855 | 185 | 80 | 42 | 0 | 64
13:30 | 3282 | 842 | 1352 | 855 | 185 | 80 | 42 | 0 | 64
14:00 | 3282 | 842 | 1352 | 855 | 185 | 80 | 42 | 0 | 64
14:30 | 3473.5 | 842.5 | 1424 | 871.5 | 184.5 | 80 | 42 | 0 | 78
15:00 | 3665 | 843 | 1496 | 888 | 184 | 80 | 42 | 0 | 92
15:30 | 3644 | 843 | 1384 | 778 | 184 | 80 | 29.5 | 0 | 92
16:00 | 3623 | 843 | 1272 | 668 | 184 | 80 | 17 | 0 | 92
16:30 | 3513.5 | 842.5 | 1189 | 654 | 184 | 80 | 28 | 0 | 94
17:00 | 3404 | 842 | 1106 | 640 | 184 | 80 | 39 | 0 | 96
17:30 | 3103 | 842 | 1034.5 | 584 | 184 | 70 | 59 | 0 | 94
18:00 | 2802 | 842 | 963 | 528 | 184 | 60 | 79 | 0 | 92
18:30 | 2712.5 | 589.5 | 1018.5 | 516.5 | 184 | 70 | 62 | 0 | 105
19:00 | 2623 | 337 | 1074 | 505 | 184 | 80 | 45 | 0 | 118
19:30 | 3005 | 336 | 1276 | 544 | 184 | 80 | 53 | 0 | 0
20:00 | 3138 | 362 | 1306 | 533 | 184 | 82 | 63 | 0 | 0
20:30 | 3153 | 499.5 | 1322 | 547.5 | 184 | 82 | 53 | 0 | 5
21:00 | 3168 | 637 | 1338 | 562 | 184 | 82 | 43 | 0 | 10
21:30 | 3139 | 637 | 1329.5 | 492 | 184.5 | 82 | 30 | 0 | 16
22:00 | 3110 | 637 | 1321 | 422 | 185 | 82 | 17 | 0 | 22
22:30 | 3132 | 740 | 1348.5 | 410.5 | 184.5 | 82 | 17 | 0 | 26
23:00 | 3154 | 843 | 1376 | 399 | 184 | 82 | 17 | 0 | 30
23:30 | 3134 | 843 | 1348.5 | 343 | 184 | 82 | 17 | 0 | 34 | Max Temp. in Dhaka |  | 29.2° C
24:00 | 3114 | 843 | 1321 | 287 | 184 | 82 | 17 | 0 | 38
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 156.624 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 156.624 MKWHr
Note on W13: Author:

## Generation
2019-04-09
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 81 | 81 | 81 | 79 | 77 | 77 | 77 | 77 | 78 | 78 | 78 | 79 | 80 | 80 | 80 | 80 | 80 | 60 |  | 80 | 80 | 82 | 82 | 82 | 82 | 82 | 1794933
2 | Kaptai Unit-4 & 5
3 | Chattogram ST-1 (Raozan) | [15 empty] | 20 | 50 | 70 |  | 70 | 90 | 90 | 100 | 100 | 100 | 100 | 700000
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | [10 empty] | 0 | 18 | 25 | 25 | 25 | 0 | 0 | 0 |  | 1 | 8 | 8 | 8 | 8 | 8 | 0 | 144783
| Teknaf Solartech 20MW | [5 empty] | 0.04 | 0.74 | 2 | 14.4 | 18.3 | 20 | 20.3 | 19.5 | 17.2 | 13.9 | 9 | 2.2 | 0.1 |  | 0 | [6 empty] | 137565
6 | Sikalbaha 225MW (Gas) | 201 | 203 | 203 | 203 | 203 | 204 | 203 | 204 | 196 | 205 | 203 | 212 | 204 | 215 | 204 | 203 | 185 | 189 |  | 203 | 227 | 217 | 204 | 216 | 202 | 203 | 4858997
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 21 | 34 |  | 17 | 19 | 34 | 34 | 17 | 17 | 17 | 465217
12 | Hathazari peaking
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 70 | 80 | 80 | 80 | 80 | 70 | 80 | 80 | 80 | 80 | 60 | 75 | 108 | 108 | 142 | 80 | 70 | 60 |  | 87 | 87 | 87 | 87 | 36 | 37 | 37 | 2065000
17 | Siddhirganj CCPP-335 MW | 160 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 0 | 20 | 20 | 20 | 110 | 110 | 110 | 40 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 2059128
18 | Summit Gazipur -2
19 | Ashuganj 195MW Modular | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 602181
20 | Ghorasal ST: Unit-1,2 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 870000
21 | Ghorasal GT: Unit-3 | 133 | 133 | 133 | 133 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 133 | 134 | 134 | 134 | 133 | 133 | 64 |  | 34 | 35 | 44 | 44 | 44 | 44 | 44 | 2768400
22 | Ghorasal GT: Unit-4 | 201 | 200 | 200 | 150 | 150 | 150 | 100 | 100 | 100 | 142 | 100 | 100 | 100 | 100 | 100 | 100 | 102 | 35 |  | 40 | 50 | 50 | 50 | 50 | 50 | 50 | 3678000
23 | Ghorasal ST: Unit-5 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 120 | 120 | 120 | 120 | 190 | 190 | 190 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3921750
24
25 | Ghorasal ST: Unit-7
26
28 | Ashuganj ST: Unit- 3
29 | Ashuganj ST: Unit- 4
30 | Ashuganj ST: Unit- 5
32 | Ashuganj Engines TSK | 40 | 40 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 2 | 2 | 2 | 3 | 3 | 36 | 40 | 334872
33 | Ashuganj CCPP 225 MW | 190 | 184 | 184 | 184 | 184 | 184 | 188 | 203 | 223 | 203 | 158 | 177 | 189 | 200 | 183 | 184 | 182 | 150 |  | 151 | 182 | 181 | 184 | 202 | 190 | 196 | 4473000
34 | Ashuganj CCPP(South) | 300 | 300 | 300 | 280 | 260 | 260 | 230 | 220 | 195 | 220 | 220 | 220 | 250 | 250 | 300 | 270 | 250 | 220 |  | 210 | 250 | 280 | 280 | 250 | 250 | 250 | 6304500
| Ashuganj CCPP(North) | 300 | 300 | 300 | 280 | 260 | 260 | 240 | 240 | 240 | 240 | 260 | 240 | 300 | 280 | 320 | 300 | 250 | 220 |  | 240 | 260 | 290 | 290 | 250 | 250 | 250 | 6768000
35 | Ashuganj (Precision) 55MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 0 | [6 empty] | 100320
36 | Chandpur CCPP
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 320 | 320 | 320 | 290 | 280 | 282 | 277 | 260 | 300 | 355 | 360 | 300 | 356 | 359 | 351 | 327 | 325 | 280 |  | 250 | 380 | 358 | 343 | 331 | 334 | 325 | 7813120
40 | Meghnaghat CCPP 450MW | 370 | 370 | 370 | 350 | 320 | 320 | 280 | 280 | 280 | 280 | 300 | 300 | 350 | 370 | 430 | 340 | 300 | 300 |  | 350 | 350 | 380 | 380 | 380 | 380 | 380 | 8158125
41 | Haripur Power CCPP 360MW | 303 | 302 | 303 | 271 | 262 | 262 | 232 | 233 | 232 | 238 | 251 | 257 | 308 | 307 | 329 | 278 | 258 | 218 |  | 257 | 305 | 338 | 337 | 335 | 336 | 338 | 6747000
42 | Mymensingh RPCL 210MW | 213 | 214 | 215 | 215 | 182 | 185 | 148 | 150 | 150 | 150 | 150 | 150 | 150 | 171 | 207 | 208 | 145 | 144 |  | 145 | 144 | 144 | 162 | 163 | 170 | 170 | 4052000
43 | Haripur NEPC 110MW
44 | Fenchugonj CCPP-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 60 | 60 | 60 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 805000
45 | Fenchugonj CCPP-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1162938
46 | Shajibazar 330 MW | 245 | 252 | 252 | 188 | 188 | 189 | 188 | 188 | 174 | 176 | 173 | 177 | 173 | 171 | 255 | 253 | 224 | 171 |  | 164 | 175 | 175 | 167 | 170 | 167 | 167 | 4498000
47 | Shahjibazar GT: Unit- 8, 9 | 52 | 42 | 42 | 43 | 43 | 40 | 56 | 40 | 66 | 67 | 40 | 68 | 62 | 67 | 64 | 51 | 40 | 17 |  | 40 | 40 | 40 | 52 | 52 | 68 | 56 | 1209000
48 | Shahjibazar 86MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 193920
49 | Shahjibazar (EPL) 50MW | 47 | 47 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 47 | 5 | 360000
50 | Sylhet GT 150 MW | 95 | 95 | 93 | 94 | 102 | 94 | 85 | 102 | 103 | 105 | 97 | 110 | 98 | 118 | 93 | 96 | 94 | 39 |  | 68 | 67 | 109 | 106 | 122 | 113 | 93 | 2364160
51 | Sylhet GT 20 MW
52 | Sylhet (EPL) 50MW | 44 | 43 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 5 | 5 | 6 | 5 | 6 |  | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 286800
53 | Sylhet (Desh) 10MW | 10 | 0 | [12 empty] | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 114480
54 | Hobiganj 11MW
55 | Fenchugonj (Barakatullah) 51MW | 11 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 162600
56 | Shahjahanulla 25 MW | 25 | 0 | [12 empty] | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 484560
57 | Summit Bibiana- 2 | 255 | 260 | 270 | 271 | 260 | 275 | 250 | 260 | 290 | 280 | 270 | 270 | 300 | 290 | 280 | 251 | 245 | 165 |  | 160 | 315 | 280 | 290 | 270 | 265 | 270 | 6701500
58 | Southern 55MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 |  | 0 | [6 empty] | 314000
59 | Sikalbaha (Energis) | 51 | 41 | 41 | 41 | 24 | 28 | 32 | 32 | 32 | 32 | 32 | 32 | 51 | 51 | 51 | 24 | 32 | 50 |  | 51 | 51 | 51 | 51 | 40 | 41 | 51 | 966240
60 | Barabkunda (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 22 | 22 | 22 |  | 22 | 22 | 22 | 0 | 22 | 22 | 22 | 472080
61 | Narshingdi (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 13 | 13 | 0 | 0 | 13 | 0 | 16 | 16 | 16 | 16 |  | 0 | 0 | 0 |  | 0 | 16 | 10 | 254448
62 | Tangail (Doreen) 22MW | 20 | 20 | 20 | 0 | [22 empty] | 59832
63 | Tripura | 92 | 92 | 84 | 84 | 80 | 80 | 80 | 80 | 96 | 98 | 98 | 52 | 64 | 80 | 92 | 92 | 96 | 92 |  | 118 | 0 | 0 | 10 | 22 | 30 | 38 | 1705920
64 | Malancha, Ctg. EPZ (United) | 34 | 32 | 32 | 34 | 34 | 36 | 36 | 8 | 4 | 3 | 2 | 4 | 4 | 7 | 2 | 6 | 6 | 6 |  | 6 | 10 | 13 | 10 | 10 | 24 | 24 | 389280
65 | Feni (Doreen) 22MW | [15 empty] | 18 | 22 | 22 |  | 22 | 22 | 0 | 0 |  | 0 | 16 | 96840
66 | Feni, Mohipal (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 0 | 11 | 11 | 8 | 8 | 0 | 0 |  |  |  | 0 |  | 8 | 8 | 0 | 0 |  |  |  | 111240
67 | Jangalia (Summit) 33MW | 33 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 0 | 0 |  |  |  |  | 202700
68 | Summit Cumilla 25MW | 18 | 18 | 15 | 12 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 8 | 8 | 8 |  | 0 | 0 | 0 |  |  |  |  | 128770
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 |  | 0 | 0 | 25 | 25 | 25 | 25 | 25 | 575000
70 | Summit Madhabdi | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 0 | 0 |  | 15 | 23 | 23 | 23 |  | 0 | 0 | 0 | 18 | 25 | 32 | 32 | 460440
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 0 |  | 0 | 2 | 33 | 33 | 33 | 28 | 28 | 651900
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 29 | 0 | 0 | 17 | 29 | 29 | 29 | 29 | 29 |  | 0 | 0 | 0 | 12 | 28 | 28 | 28 | 616900
73 | Ghorashal (Regent) | [26 empty] | 9409
76 | Siddhirganj (Desh)
77 | Siddhirganj (Dutch Bangla)
78 | Gazipur (RPCL) | [6 empty] | 3 | 8 | 13 | 8 | 0 | 0 | 0 |  | 12 | 26 | 34 | 0 |  | 0 | [6 empty] | 139116
79 | Kodda 149MW
80 | Jamalpur 95MW
81 | Lakdhanvi 52 MW | 8 | 0 | [24 empty] | 9389
82 | Madanganj 102MW
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj (Powerpac) 100MW
86 | Meghnaghat CCPP(Summit) | 275 | 275 | 255 | 225 | 265 | 250 | 270 | 285 | 275 | 280 | 250 | 280 | 270 | 280 | 280 | 280 | 250 | 210 |  | 200 | 250 | 250 | 250 | 220 | 220 | 230 | 6185745
87 | Meghnaghat (IEL)
88 | Ghorashal 78MW (MAX)
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 40 | 40 | 40 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 359880
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 210000
93 | Ashuganj (Midland) 51MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 207136
94 | Gagnagar (Orion) | [8 empty] | 0 | 7 | 7 | 24 | 24 | 24 | 24 | 24 | 24 | 8 |  | 0 | [6 empty] | 195264
95 | Patenga 50MW | 50 | 6 | 6 | 6 | 6 | 10 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 38 | 24 | 24 |  | 33 | 50 | 50 | 50 | 29 | 19 | 0 | 861120
96 | Chattogram ECPV 108 MW | 75 | 13 | 13 | 13 | 13 | 14 | 44 | 46 | 45 | 45 | 60 | 90 | 102 | 105 | 105 | 12 | 12 | 12 |  | 17 | 32 | 31 | 50 | 19 | 19 | 0 | 1029120
97 | Katpotti 51 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 163584
98 | Bosila 108MW
99 | Madanganj-55 MW | [20 empty] | 0
100 | Northern 55 MW | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 0 | 0 | 0 |  |  |  |  | 321304
101 | Kushiara 163 MW CCPP GT | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 0 | 0 | 0 | [13 empty] | 1130596
102 | Sarishabari (Solar) | [7 empty] | 0 | 0.1 | 1.7 | 2.4 | 2.6 | 2.5 | 2.2 | 1.7 | 0.3 | 0 | 0 | [8 empty] | 12650
103 | Banco Energy 54MW | 17 | 17 | 0 | 0 | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 17 | 17 | 17 | 17 | 17 | 17 |  | 0 | 0 | 0 |  |  |  |  | 250200
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW
115 | Juldah 100 MW Unit-3 | 100 | 100 | 80 | 80 | 30 | 50 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 20 | 20 | 20 |  | 70 | 80 | 90 | 100 | 70 | 70 | 0 | 1880640
116 | Chandpur Desh 200MW | 34 | 17 | 17 | 17 | 17 | 30 | 70 | 34 | 34 | 34 | 34 | 60 | 70 | 70 | 70 | 70 | 70 | 70 |  | 66 | 0 | 0 |  |  | 0 |  | 987840
117 | Midland 150MW
118 | Bibiyana-3 285MW
| United Jamalpur PPL | [14 empty] | 4 | 7 | 7 | 0 |  | 0 | [6 empty] | 57600
120 | Eastern Zone Total | 5203 | 4960 | 4749 | 4463 | 4306 | 4353.04 | 4296.74 | 4259 | 4355.5 | 4439 | 4068.4 | 4115.9 | 4507 | 4590.4 | 4978.6 | 4585.3 | 4338.2 | 3561.1 |  | 3536 | 3940 | 4098 | 4156 | 3968 | 4059 | 3898 | 108296032
121
122 | o
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | 32 | 13 | 11 | 2 | 0 | [14 empty] | 28 | 34 | 29 | 9 | 0 |  |  | 139200
Khulna CCPP 225MW
129 | Labon Chora 105 MW | [7 empty] | 0 | 35 | 35 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 |  | 35 | 28 | 17 | 17 | 0 |  |  | 394080
130
131
132
133
| Summit Barisal 110 MW | 80 | 80 | 80 | 64 | 64 | 32 | 32 | 32 | 64 | 64 | 48 | 48 | 48 | 64 | 64 | 64 | 64 | 48 |  | 16 | 16 | 0 |  |  |  |  | 1121280
136 | Barisal GT: Unit-1, 2 | [26 empty] | 4432
137 | Bhola Aggreko 95MW | 95 | 95 | 95 | 95 | 96 | 96 | 96 | 96 | 95 | 94 | 94 | 95 | 96 | 97 | 98 | 96 | 41 | 14 |  | 52 | 51 | 52 | 52 | 52 | 51 | 51 | 1934209
| Bhola CCPP 194MW | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 100 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2871000
140 | Bhola (Venture) 33MW | 25 | 24 | 22 | 23 | 22 | 21 | 20 | 19 | 19 | 20 | 20 | 20 | 21 | 24 | 22 | 18 | 17 | 20 |  | 28 | 26 | 2 | 3 | 6 | 6 | 7 | 419300
141 | Bangla Trak Noapara
142 | Noapara (KZA) 40MW
143 | Gopalganj Peaking | 2 | 0 | [14 empty] | 18 | 45 |  | 0 | [6 empty] | 70528
144 | Bheramara GT-1,2,3
145 | Madhumati Power Plant
146 | Bheramara HVDC | 703 | 693 | 693 | 693 | 693 | 693 | 842 | 842 | 842 | 842 | 842 | 842 | 842 | 842 | 843 | 843 | 842 | 842 |  | 337 | 336 | 362 | 637 | 637 | 843 | 843 | 17936000
147 | Bheramara 360 MW
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 183 | 183 | 185 | 185 | 184 | 184 | 184 | 184 |  | 184 | 184 | 184 | 184 | 185 | 184 | 184 | 4097400
153 | Baghabari GT 71MW | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 65 | 65 | 65 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 65 | 65 | 65 | 1470000
156 | Baghabari GT 100MW | 60 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 0 | 50 | 50 | 60 | 60 | 60 | 60 | 1314000
Baghabari Peaking 50MW
157 | Sirajgonj Unit-1 225MW (Gas) | 157 | 157 | 156 | 158 | 156 | 133 | 133 | 135 | 147 | 163 | 165 | 162 | 203 | 190 | 194 | 175 | 155 | 156 |  | 140 | 164 | 170 | 169 | 160 | 162 | 158 | 4134536
158 | Sirajgonj Unit-1 225MW (Oil)
| Sirajgonj Unit-2 225MW (Gas) | 147 | 146 | 146 | 150 | 147 | 136 | 135 | 130 | 148 | 154 | 155 | 152 | 168 | 155 | 189 | 175 | 147 | 135 |  | 135 | 159 | 163 | 160 | 152 | 153 | 149 | 3831273
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas) | 151 | 151 | 151 | 149 | 148 | 131 | 130 | 130 | 130 | 131 | 140 | 155 | 171 | 172 | 172 | 159 | 152 | 130 |  | 130 | 135 | 154 | 165 | 157 | 158 | 154 | 3789664
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas) | 102 | 107 | 106 | 122 | 117 | 117 | 118 | 165 | 144 | 142 | 165 | 163 | 195 | 190 | 250 | 200 | 160 | 160 |  | 165 | 140 | 160 | 180 | 180 | 183 | 184 | 3826320
161 | Bera Peaking
162 | Bogra (GBB) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 0 | 0 |  |  | 22 | 22 | 22 | 22 | 22 | 3 | 193920
163 | Bogra (EPL) | 17 | 17 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 0 | 0 |  |  |  | 0 | 5 | 10 | 12 | 13 | 10 | 128304
164 | Ullapara (Summit) | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 0 | 11 | 11 | 0 | 0 | 5 | 11 | 0 | 0 | [7 empty] | 0 | 131670
165 | Amnura 50MW | [20 empty] | 12 | 12 | 12 | 12 | 6 | 0 | 51390
166 | Katakhali (Northern) | [10 empty] | 24 | 24 | 0 | 0 | 0 | [11 empty] | 35583
167 | Katakhali Peaking
168 | Santahar Peaking
169 | Rajlanka 52 MW | 8 | 0 | [18 empty] | 1 | 8 | 8 | 8 | 0 | 0 | 52320
170 | Chapainawabganj-100 MW | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 0 | [9 empty] | 369748
171 | Paramount Baghabari
172 | Confidence CPBL-2 | [10 empty] | 17 | 0 | 0 | [13 empty] | 11520
173 | Rangpur GT
175 | Saidpur GT
176
177
178
178 | Western Zone Total | 1979 | 1933 | 1913 | 1909 | 1896 | 1815 | 1962 | 2005 | 2095 | 2105 | 2157 | 2143 | 2217 | 2225 | 2327 | 2203 | 2055 | 1989 |  | 1430 | 1538 | 1570 | 1868 | 1828 | 2026 | 1988 | 48327677