## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-11-25 | Saturday
|  | Date (day): | 2023-11-25 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11388.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13049 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-11-24 | 2023-11-25 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 65 | 39 | 77 | 77 | 31 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 335 | 400 | 412 | 412
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 260 | 337 | 330 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 180 | 225 | 225 | 225 | 225 |  | GT-1 under S/D due to Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 92 | 100 |  |  | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 85 | 85 |  | 17 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 15 | 30 | 25 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 30 | 40 | 35 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 9 | 18 | 18 |  | 4 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 92 | 92 |  | 8 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 230 | 335 | 335 | 335 | 0
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 0 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 0 | 16 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 0 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 5 | 0 | 35 | 20 |  | Fuel shortage
| Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
25 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 31 | 27 | 31 | 31 |  | 49 | Engine problem
26 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
27 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 32 | 33 | 33 | 33
28 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 8 | 8 | 25 | 27 |  | Fuel shortage
29 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
30 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 80 | 130 | 170 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
31 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 20 | 18 | 100 | 49 |  | Fuel shortage
32 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 30 | 105
33 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 0 | 26 | 88 | 16 |  | Fuel shortage
34 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 17 | 17 | 35 | 127 |  | Fuel shortage
35 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 32 | 0 | 35 | 0
36 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 17 | 35 | 20 |  | Fuel shortage
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 5763 | 5422 | 1419 | 1694 | 2335 | 2893 | 1515 | 1018
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
38 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 0 | 8 | 17 | 8 |  | Fuel shortage
39 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 6 | 6 | 10 | 40 |  | Fuel shortage
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 46 | 46 | 184 |  | Low water lavel
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 210 | 212 | 212
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 17 | 17 | 88 |  | Fuel shortage
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 40 | 64 | 34 |  | Fuel shortage
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 | 102 |  | Fuel shortage
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 12 | 12 | 12 | 88 |  | Fuel shortage
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 12 | 12 | 88 |  | Fuel shortage
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 12 | 12 | 12 | 12 | 10 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 30 | 30 | 10 | 25
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 260 | 260 | 40 |  | Fuel shortage+Engine problem
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 8 | 17 | 17 | 37 |  | Fuel shortage
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 17 | 17 | 93 |  | Fuel shortage
55 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 12 | 12 | 88 |  | Fuel shortage
56 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 17 | 99 |  | Fuel shortage
57 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Fuel shortage
58 | SS Power I |  | Coal | SS Power | 1*612 | 612 | 612 | 358 | 480 | 400 | 500
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 0 | 0 | 10 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 3217 | 3157 | 726 | 882 | 1133 | 1260 | 1450 | 330
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 0 | 0 |  | 221 | Under maint.
60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 305 | 320 | 320 | 40 |  | Gas shortage
61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
62 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 350 | 395 | 395 | 395 | 5
63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 47 | 48 | 51 | 51
| Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 0 | 10 | 10 | 40 | 40 |  |  | Contract Expired
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 55 | 158 | 55 | 102 | 93 |  | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 10 | 34 | 51 | 51
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 150 | 150
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 14 | 17 | 17 | 17 | 183 |  | Fuel shortage
70 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 16 | 18 | 18 |  | 4 | Engine problem
71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 88 | 108 | 128 | 140
72 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 6 | 8 | 10 | 10 |  | 15 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 37 | 32 | 28 | 65 | 48 |  | Fuel shortage
77 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 0 | 17 | 17 |  | 37 | Engine problem
78 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 18 | 41 | 36 | 72 | 43 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2896 | 975 | 1216 | 1526 | 1658 | 412 | 800
79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 75 | 85 | 80 | 90 | 112 |  | Gas shortage
80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Contract Expired
| Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 29 | 93 | 84 | 104 | 96 |  | Fuel shortage
83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 8 | 47 | 56 | 85 | 30 |  | Fuel shortage
84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 52 | 0 | 50 | 0
85 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 166 | 225 | 277.6 | 285 | 112 | 22
86 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
87 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 28 | 28 | 28 | 28 |  | 62 | Engine problem
88 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
89 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
90 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
91 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 18 | 41 | 44 | 44
92 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 5 | 5 | 5 |  | 6 | Engine problem
93 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 |  | 66 | GT-8 Under maint.
94 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 40 | 40 | 40 | 40 | 46 |  | Gas shortage
95 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 196 | 195 | 200 | 200 |  | 31 | Machine problem
97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 16 | 17 | 17 | 17
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 16 | 16 | 16 | 9 |  | Gas shortage
99 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 300 | 310 | 310 |  |  | FGMO
100 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 400 | 401 | 400 | 400
101 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
102 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 390 | 395 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1451 | 1491 | 1513 | 1513 | 269 | 622
103 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 447 | 209 | 453 | 453
104 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 32 | 48 | 67 |  | Fuel shortage
105 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 50
106 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
107 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 70 | 39 |  | Fuel shortage
108 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
109 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 16 | 24 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
110 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105
111 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 15 | 32 | 73 |  | Fuel shortage
112 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 66 | 0 | 100 | 0
113 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0
114 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 351 | 502 | 450 | 550
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 864 | 711 | 1155 | 1324 | 859 | 0
115 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 16 | 110
116 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 15 | 16 | 21 | 25 |  | 15 | Engine problem
117 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 80 | 50 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 820 | 890 | 1000 | 1220
119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 110 | 110 | 110 | 110 |  | 110 | GT-1 Under maint.
120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 12 | 0 | 150
121 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 150 | 230 | 150 | 150 | 157 |  | Coal shortage
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1175 | 1308 | 1427 | 1895 | 157 | 189
122 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
123 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 35 | 17 |  | Fuel shortage
124 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 20 |  | 51 | Engine problem
125 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 28 | 28
126 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 34 | 42 |  | 8 | Engine problem
127 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 40 |  | 10 | Engine problem
128 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
129 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
130 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
131 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 230 | 414 | 380 | 414
132 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 38 | 12 |  | Fuel shortage
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
133 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
134 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
135 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 40 | 85 |  | 19 | Engine problem
136 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
137 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 12 | 35 | 50 | 63 |  | Fuel shortage
138 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 20 | 35 | 113
139 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 827 | 820 | 850 | 900
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 1073 | 1277 | 1501 | 1828 | 1113 | 88
140 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
141 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
142 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
143 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
144 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 3 | 70 | 113 | 113
145 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
146 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 17 | 70 | 110
147 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 27 | 0 | 30 | 0
148 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 161 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 366 | 257 | 521 | 393 | 125 | 189
| Total |  |  |  |  | 25339 | 24599 | 8215 | 9061 | 11388.6 | 13049 | 6012 | 3258
A. |  | 2023-11-24 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 9061 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 7277 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9061 | MW
3 | Day peak Generation : |  |  | 8215 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8783.06 | MW
4 | Evening peak Generation : |  |  | 9061 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 194.9203 | MKWHr | By Solar | 2.3642 | MKWHr
| By Gas : | 110.3464 | MKWHr |  | By Oil: | 3.9781 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 63.0258 | MKWHr |  | By Hydro: | 1.1384 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.024 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6012 | MW | Dhaka | 3146.56 | 3146.56 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3258 | MW | Chittagong | 976.9 | 976.9 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 9270 | MW | Khulna | 1056.9 | 1056.9 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 796.38 | MMCFD |  |  | Rajshahi | 892.4 | 892.4 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 111968923.72 | ii) Oil : | Taka | 51291613.49 | Comilla | 761 | 761 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 474882716.39 | Total | Taka | 638143253.6 | Mymensingh | 693 | 693 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 362 | 362 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 420 | MW (W to E) at | 18:00 | hrs | Barisal | 255.3 | 255.3 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 300 | MW at | 19:30 | hrs | Rangpur | 639 | 639 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 29.2°C |  |  | Total | 8783.06 | 8783.06 |  | 0
B. |  | 2023-11-25 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 29.2°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13049 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8200 | MW
4 | Reserve(Generation end) |  |  |  | 2849 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 219.4224 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6700 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.8276 | MKWHr. | ii) HVDC Flow at Peak Time |  | 209 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.2157 | MKWHr. | iii) Maximum HVDC Flow : |  | 917 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 98.68 |  | (b) Today: | 98.58 |  | (c) Rule Curve: |  | 106.6
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-11-24 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 372 | 307 |  | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 11 | 25 | 33 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 10 | 0 | 0 | 0 | 280 | 0 | 0 | 102 | 0 | 51 | 39 | 0 | 51 | 0 | 0 | 0 | 15 | 11 | 33 | 8 | 104 | 103 | 0 | 0 | 0 | 43 | 28 | 0 | 44 | 0 | 0 | 0 | 40 | 0 | 200 | 18 | 0 | 10 | 285 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 368 | 0 | 0 | 0 | 0 |  | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 150 | 823 | 0 | 0 |  | 4819 | 3432 | 8251 | 3133 | 917 | 1614 | 0 | 23 | 2368 | 92 | 0 | 0 | 104 | 0 | 0 | 0 | 98.71
2:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 372 | 307 |  | 0 | 225 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 11 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 18 | 0 | 0 | 0 | 295 | 0 | 0 | 45 | 0 | 5 | 36 | 0 | 5 | 0 | 0 | 0 | 15 | 11 | 33 | 8 | 96 | 103 | 0 | 0 | 0 | 43 | 28 | 0 | 5 | 0 | 0 | 0 | 40 | 0 | 200 | 18 | 0 | 10 | 295 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 345 | 0 | 0 | 0 | 0 |  | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 150 | 818 | 0 | 0 |  | 4399 | 3455 | 7854 | 3002 | 916 | 1454 | 0 | 0 | 2340 | 46 | 0 | 0 | 96 | 0 | 0 | 0 | 98.71
3:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 372 | 307 |  | 0 | 225 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 11 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 29 | 0 | 0 | 0 | 290 | 0 | 0 | 45 | 0 | 5 | 38 | 0 | 5 | 0 | 0 | 0 | 15 | 11 | 33 | 8 | 98 | 104 | 0 | 0 | 0 | 43 | 28 | 0 | 5 | 0 | 0 | 0 | 40 | 0 | 200 | 18 | 0 | 10 | 275 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 345 | 0 | 0 | 0 | 0 |  | 726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 150 | 822 | 0 | 0 |  | 4380 | 3272 | 7652 | 2988 | 726 | 1446 | 0 | 0 | 2348 | 46 | 0 | 0 | 98 | 0 | 0 | 0 | 98.7
4:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 372 | 307 |  | 0 | 225 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 11 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 29 | 0 | 0 | 0 | 280 | 0 | 0 | 45 | 0 | 5 | 38 | 0 | 5 | 0 | 0 | 0 | 15 | 11 | 33 | 8 | 98 | 104 | 0 | 0 | 0 | 43 | 28 | 0 | 5 | 0 | 0 | 0 | 40 | 0 | 201 | 18 | 0 | 10 | 285 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 345 | 2 | 0 | 0 | 0 |  | 585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 150 | 820 | 0 | 0 |  | 4381 | 3057 | 7438 | 2977 | 585 | 1386 | 0 | 0 | 2344 | 46 | 0 | 0 | 98 | 0 | 2 | 0 | 98.7
5:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 339 | 282 |  | 0 | 170 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 11 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 27 | 0 | 0 | 0 | 280 | 0 | 0 | 45 | 0 | 5 | 36 | 0 | 5 | 0 | 0 | 0 | 15 | 11 | 33 | 8 | 96 | 104 | 0 | 0 | 0 | 43 | 28 | 0 | 5 | 0 | 0 | 0 | 10 | 0 | 201 | 18 | 0 | 10 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 345 | 3 | 0 | 0 | 0 |  | 585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 150 | 827 | 0 | 0 |  | 4220 | 3057 | 7277 | 2926 | 585 | 1276 | 0 | 0 | 2345 | 46 | 0 | 0 | 96 | 0 | 3 | 0 | 98.69
6:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 333 | 282 |  | 0 | 170 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 11 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 30 | 0 | 0 | 0 | 280 | 0 | 0 | 45 | 0 | 5 | 38 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 33 | 8 | 90 | 105 | 0 | 0 | 0 | 43 | 28 | 0 | 5 | 0 | 0 | 0 | 10 | 0 | 201 | 18 | 0 | 10 | 300 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 345 | 6 | 0 | 0 | 0 |  | 686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 150 | 823 | 0 | 0 |  | 4223 | 3194 | 7417 | 2917 | 686 | 1331 | 0 | 0 | 2341 | 46 | 0 | 0 | 90 | 0 | 6 | 0 | 98.68
7:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 338 | 280 |  | 0 | 170 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 11 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 30 | 0 | 0 | 0 | 370 | 0 | 0 | 45 | 0 | 51 | 40 | 0 | 24 | 0 | 0 | 0 | 9 | 11 | 33 | 8 | 82 | 104 | 0 | 0 | 0 | 43 | 28 | 0 | 5 | 0 | 0 | 0 | 10 | 0 | 201 | 17 | 0 | 10 | 295 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 3 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 340 | 0 | 0 | 345 | 6 | 0 | 0 | 0 |  | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 110 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 353 | 1 | 150 | 827 | 10 | 0 |  | 4504 | 2933 | 7437 | 3186 | 372 | 1375 | 0 | 0 | 2345 | 46 | 0 | 0 | 82 | 25 | 6 | 0 | 98.68
8:00 | 0 | 0 | 0 | 180 | 0 | 60 | 0 | 389 | 337 |  | 0 | 225 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 11 | 17 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 30 | 0 | 0 | 0 | 280 | 0 | 0 | 102 | 0 | 51 | 40 | 0 | 51 | 0 | 0 | 0 | 13 | 11 | 33 | 8 | 78 | 86 | 0 | 0 | 1 | 43 | 28 | 0 | 25 | 0 | 0 | 0 | 40 | 0 | 202 | 17 | 0 | 10 | 285 | 16 | 5 | 0 | 0 | 0 | 0 | 7 | 0 | 1 | 10 | 0 | 0 | 0 | 354 | 16 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 18 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 395 | 0 | 0 | 345 | 3 | 0 | 0 | 0 |  | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 520 | 110 | 0 | 0 | 1 | 21 | 0 | 0 | 0 | 353 | 8 | 150 | 825 | 52 | 0 |  | 4803 | 3001 | 7804 | 3192 | 326 | 1648 | 0 | 24 | 2363 | 46 | 0 | 0 | 78 | 124 | 3 | 0 | 98.68
9:00 | 0 | 0 | 0 | 180 | 0 | 60 | 0 | 352 | 263 |  | 0 | 225 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 0 | 17 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 30 | 0 | 0 | 0 | 280 | 0 | 0 | 55 | 0 | 51 | 39 | 0 | 10 | 0 | 0 | 0 | 16 | 11 | 33 | 8 | 80 | 72 | 0 | 0 | 1 | 43 | 28 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 201 | 17 | 0 | 10 | 260 | 16 | 4 | 0 | 0 | 0 | 0 | 24 | 0 | 17 | 15 | 0 | 0 | 0 | 353 | 16 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 31 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 250 | 0 | 0 | 332 | 0 | 0 | 0 | 0 |  | 446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 520 | 110 | 0 | 0 | 3 | 48 | 0 | 0 | 0 | 353 | 9 | 150 | 829 | 100 | 0 |  | 4402 | 3094 | 7496 | 2905 | 446 | 1379 | 0 | 57 | 2354 | 46 | 0 | 0 | 80 | 229 | 0 | 0 | 98.67
10:00 | 0 | 0 | 0 | 180 | 0 | 22 | 0 | 334 | 227 |  | 0 | 180 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 0 | 17 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 30 | 0 | 0 | 0 | 280 | 0 | 0 | 55 | 0 | 47 | 30 | 0 | 10 | 0 | 0 | 0 | 16 | 11 | 33 | 6 | 72 | 72 | 0 | 0 | 2 | 43 | 28 | 0 | 10 | 0 | 0 | 0 | 10 | 0 | 198 | 17 | 0 | 10 | 260 | 16 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 18 | 0 | 0 | 0 | 338 | 8 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 43 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 250 | 0 | 0 | 325 | 0 | 0 | 0 | 0 |  | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 530 | 110 | 0 | 0 | 4 | 57 | 0 | 0 | 0 | 354 | 15 | 150 | 829 | 143 | 0 |  | 4193 | 3146 | 7339 | 2872 | 447 | 1197 | 0 | 33 | 2358 | 46 | 0 | 0 | 72 | 314 | 0 | 0 | 98.67
11:00 | 0 | 0 | 0 | 180 | 0 | 22 | 0 | 335 | 227 |  | 0 | 180 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 11 | 17 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 3 | 12 | 30 | 0 | 0 | 0 | 275 | 0 | 0 | 55 | 0 | 47 | 8 | 0 | 10 | 0 | 0 | 0 | 16 | 11 | 25 | 6 | 80 | 75 | 0 | 0 | 2 | 43 | 28 | 0 | 10 | 0 | 0 | 0 | 40 | 0 | 197 | 17 | 0 | 10 | 290 | 8 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 19 | 0 | 0 | 0 | 329 | 8 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 12 | 0 | 370 | 0 | 49 | 0 | 2 | 0 | 0 | 25 | 7 | 0 | 250 | 0 | 0 | 325 | 0 | 0 | 0 | 0 |  | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 620 | 110 | 0 | 0 | 5 | 67 | 0 | 0 | 0 | 354 | 34 | 150 | 826 | 165 | 0 |  | 4272 | 3286 | 7558 | 2854 | 447 | 1234 | 0 | 61 | 2445 | 46 | 0 | 16 | 80 | 375 | 0 | 0 | 98.66
12:00 | 0 | 0 | 0 | 180 | 0 | 65 | 0 | 335 | 260 |  | 0 | 180 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 11 | 25 | 32 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 12 | 30 | 0 | 0 | 0 | 280 | 0 | 0 | 55 | 0 | 47 | 10 | 0 | 10 | 0 | 0 | 0 | 16 | 11 | 33 | 6 | 88 | 75 | 0 | 0 | 2 | 43 | 28 | 0 | 18 | 0 | 0 | 0 | 40 | 0 | 196 | 16 | 0 | 10 | 300 | 8 | 2 | 0 | 0 | 0 | 0 | 29 | 0 | 17 | 20 | 0 | 14 | 0 | 400 | 8 | 0 | 0 | 5 | 0 | 0 | 17 | 0 | 37 | 0 | 390 | 0 | 52 | 0 | 17 | 0 | 0 | 32 | 18 | 0 | 350 | 0 | 0 | 358 | 0 | 0 | 0 | 0 |  | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 820 | 110 | 0 | 0 | 5 | 66 | 0 | 0 | 0 | 351 | 27 | 150 | 827 | 161 | 0 |  | 4737 | 3478 | 8215 | 3068 | 447 | 1333 | 0 | 166 | 2676 | 46 | 0 | 16 | 88 | 375 | 0 | 0 | 98.66
13:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 407 | 330 |  | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 7 | 25 | 32 | 8 | 0 | 46 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 12 | 30 | 0 | 0 | 0 | 280 | 0 | 0 | 102 | 0 | 47 | 10 | 0 | 25 | 0 | 0 | 0 | 16 | 11 | 33 | 6 | 98 | 74 | 0 | 0 | 2 | 43 | 28 | 0 | 37 | 0 | 0 | 0 | 40 | 0 | 196 | 17 | 0 | 10 | 285 | 16 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 17 | 15 | 0 | 19 | 0 | 354 | 8 | 0 | 0 | 2 | 0 | 0 | 17 | 0 | 36 | 0 | 370 | 0 | 50 | 0 | 17 | 0 | 0 | 28 | 18 | 0 | 393 | 0 | 0 | 403 | 0 | 0 | 0 | 0 |  | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 6 | 0 | 5 | 0 | 800 | 110 | 0 | 0 | 4 | 72 | 0 | 0 | 0 | 354 | 15 | 150 | 829 | 153 | 0 |  | 5151 | 3678 | 8829 | 3264 | 447 | 1709 | 0 | 197 | 2706 | 46 | 0 | 16 | 98 | 346 | 0 | 0 | 98.65
14:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 354 | 280 |  | 0 | 225 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 7 | 25 | 12 | 8 | 0 | 46 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 12 | 30 | 0 | 0 | 0 | 280 | 0 | 0 | 102 | 0 | 46 | 10 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 8 | 98 | 73 | 0 | 0 | 2 | 43 | 26 | 0 | 37 | 0 | 0 | 0 | 40 | 0 | 196 | 17 | 0 | 10 | 265 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 15 | 0 | 19 | 0 | 354 | 8 | 0 | 0 | 3 | 0 | 0 | 17 | 0 | 39 | 0 | 350 | 0 | 41 | 0 | 17 | 0 | 0 | 23 | 18 | 0 | 280 | 0 | 0 | 354 | 0 | 0 | 0 | 0 |  | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 6 | 0 | 4 | 0 | 560 | 110 | 0 | 0 | 4 | 54 | 0 | 0 | 0 | 355 | 5 | 150 | 826 | 141 | 0 |  | 4705 | 3209 | 7914 | 2869 | 447 | 1568 | 0 | 163 | 2415 | 46 | 0 | 16 | 98 | 292 | 0 | 0 | 98.66
15:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 331 | 240 |  | 0 | 170 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 20 | 7 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 30 | 0 | 0 | 0 | 280 | 0 | 0 | 102 | 0 | 46 | 10 | 0 | 10 | 0 | 0 | 0 | 16 | 11 | 33 | 8 | 84 | 75 | 0 | 0 | 1 | 43 | 26 | 0 | 10 | 0 | 0 | 0 | 40 | 0 | 196 | 17 | 0 | 10 | 280 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 11 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 9 | 0 | 350 | 0 | 29 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 230 | 0 | 0 | 320 | 1 | 0 | 0 | 0 |  | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 6 | 0 | 3 | 0 | 540 | 109 | 0 | 0 | 2 | 37 | 0 | 0 | 0 | 354 | 16 | 150 | 830 | 95 | 0 |  | 4256 | 3071 | 7327 | 2800 | 447 | 1334 | 0 | 40 | 2364 | 46 | 0 | 0 | 84 | 211 | 1 | 0 | 98.64
16:00 | 0 | 0 | 0 | 180 | 0 | 39 | 0 | 339 | 246 |  | 0 | 170 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 20 | 7 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 0 | 0 | 0 | 315 | 0 | 0 | 55 | 0 | 47 | 10 | 0 | 10 | 0 | 0 | 0 | 16 | 11 | 33 | 8 | 88 | 72 | 0 | 0 | 0 | 43 | 26 | 0 | 10 | 0 | 0 | 0 | 40 | 0 | 196 | 17 | 0 | 10 | 300 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 5 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 10 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 260 | 0 | 0 | 325 | 3 | 0 | 0 | 0 |  | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 6 | 0 | 2 | 0 | 560 | 109 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 354 | 7 | 150 | 829 | 35 | 0 |  | 4222 | 3056 | 7278 | 2887 | 447 | 1325 | 0 | 14 | 2388 | 46 | 0 | 0 | 88 | 80 | 3 | 0 | 98.64
17:00 | 0 | 0 | 0 | 180 | 0 | 39 | 0 | 358 | 337 |  | 0 | 225 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 9 | 20 | 7 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 |  | 0 | 0 | 0 | 8 | 0 | 6 | 12 | 18 | 0 | 0 | 0 | 310 | 0 | 0 | 55 | 0 | 47 | 10 | 0 | 18 | 0 | 0 | 0 | 16 | 11 | 33 | 8 | 96 | 84 | 0 | 0 | 0 | 43 | 26 | 0 | 10 | 0 | 0 | 0 | 40 | 0 | 196 | 17 | 0 | 10 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 3 | 0 | 12 | 4 | 0 | 333 | 4 | 0 | 2 | 0 | 15 | 0 | 3 | 0 | 3 | 0 | 350 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 5 | 0 | 300 | 0 | 0 | 340 | 1 | 0 | 0 | 0 |  | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 620 | 109 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 353 | 0 | 150 | 824 | 2 | 0 |  | 4553 | 3029 | 7582 | 2975 | 447 | 1423 | 0 | 134 | 2457 | 46 | 0 | 0 | 96 | 3 | 1 | 0 | 98.63
18:00 | 0 | 0 | 0 | 180 | 0 | 39 | 0 | 400 | 337 |  | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 5 | 9 | 20 | 7 | 25 | 33 | 8 | 0 | 46 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 0 | 6 | 12 | 30 | 0 | 0 | 0 | 305 | 0 | 0 | 158 | 0 | 48 | 10 | 0 | 34 | 0 | 0 | 0 | 16 | 11 | 33 | 8 | 108 | 85 | 0 | 0 | 0 | 43 | 28 | 0 | 41 | 0 | 0 | 0 | 40 | 0 | 195 | 17 | 0 | 10 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 93 | 0 | 20 | 0 | 12 | 17 | 0 | 401 | 47 | 0 | 17 | 0 | 15 | 8 | 17 | 0 | 32 | 0 | 395 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 41 | 0 | 395 | 0 | 0 | 480 | 0 | 0 | 0 | 0 |  | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 12 | 0 | 70 | 0 | 0 | 20 | 890 | 110 | 0 | 12 | 0 | 0 | 17 | 0 | 0 | 502 | 0 | 230 | 820 | 0 | 0 |  | 5508 | 3553 | 9061 | 3293 | 209 | 1764 | 0 | 549 | 3092 | 46 | 0 | 0 | 108 | 0 | 0 | 0 | 98.63
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 39 | 0 | 408 | 306 |  | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 9 | 20 | 17 | 25 | 33 | 8 | 0 | 46 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 0 | 6 | 12 | 30 | 0 | 0 | 0 | 305 | 0 | 0 | 158 | 0 | 47 | 14 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 8 | 104 | 85 | 0 | 0 | 0 | 43 | 28 | 0 | 47 | 0 | 0 | 0 | 40 | 0 | 198 | 17 | 0 | 10 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 93 | 0 | 35 | 0 | 12 | 17 | 0 | 402 | 47 | 35 | 17 | 0 | 65 | 17 | 17 | 0 | 36 | 0 | 400 | 11 | 0 | 17 | 17 | 0 | 6 | 0 | 54 | 0 | 395 | 0 | 0 | 480 | 0 | 0 | 0 | 0 |  | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 900 | 110 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 180 | 824 | 0 | 0 |  | 5662 | 3385 | 9047 | 3320 | 209 | 1697 | 0 | 713 | 2958 | 46 | 0 | 0 | 104 | 0 | 0 | 0 | 0
19:30 | 0 | 0 | 0 | 180 | 0 | 39 | 0 | 413 | 319 |  | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 20 | 17 | 25 | 33 | 8 | 0 | 46 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 0 | 6 | 12 | 30 | 0 | 0 | 0 | 335 | 0 | 0 | 158 | 0 | 46 | 30 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 8 | 100 | 88 | 0 | 0 | 0 | 43 | 28 | 0 | 44 | 0 | 0 | 0 | 40 | 0 | 198 | 18 | 0 | 10 | 335 | 16 | 5 | 0 | 0 | 0 | 0 | 72 | 0 | 35 | 0 | 12 | 17 | 0 | 403 | 16 | 35 | 17 | 0 | 65 | 17 | 17 | 0 | 36 | 0 | 391 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 54 | 0 | 395 | 0 | 0 | 480 | 1 | 0 | 0 | 0 |  | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 880 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 180 | 824 | 0 | 0 |  | 5692 | 3268 | 8960 | 3341 | 209 | 1777 | 0 | 539 | 2947 | 46 | 0 | 0 | 100 | 0 | 1 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 39 | 0 | 414 | 331 |  | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 17 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 0 | 6 | 12 | 30 | 0 | 0 | 0 | 305 | 0 | 0 | 158 | 0 | 47 | 29 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 8 | 108 | 97 | 0 | 0 | 0 | 43 | 28 | 0 | 47 | 0 | 0 | 0 | 40 | 0 | 198 | 18 | 0 | 10 | 285 | 16 | 5 | 0 | 0 | 0 | 0 | 55 | 0 | 35 | 0 | 12 | 17 | 0 | 400 | 16 | 17 | 17 | 0 | 65 | 17 | 17 | 0 | 36 | 0 | 390 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 54 | 0 | 395 | 0 | 0 | 470 | 0 | 0 | 0 | 0 |  | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 800 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 180 | 832 | 0 | 0 |  | 5553 | 3428 | 8981 | 3318 | 405 | 1787 | 0 | 462 | 2855 | 46 | 0 | 0 | 108 | 0 | 0 | 0 | 98.62
21:00 | 0 | 0 | 0 | 180 | 0 | 39 | 0 | 414 | 311 |  | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 12 | 20 | 18 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 0 | 6 | 12 | 30 | 0 | 0 | 0 | 315 | 0 | 0 | 102 | 0 | 47 | 32 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 8 | 106 | 97 | 0 | 0 | 0 | 43 | 28 | 0 | 47 | 0 | 0 | 0 | 38 | 0 | 198 | 18 | 0 | 10 | 310 | 16 | 5 | 0 | 0 | 0 | 0 | 55 | 0 | 20 | 0 | 12 | 17 | 0 | 402 | 16 | 17 | 17 | 0 | 30 | 17 | 17 | 0 | 26 | 0 | 400 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 35 | 0 | 393 | 0 | 0 | 450 | 0 | 0 | 0 | 0 |  | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 150 | 824 | 0 | 0 |  | 5435 | 3369 | 8804 | 3351 | 447 | 1738 | 0 | 348 | 2768 | 46 | 0 | 0 | 106 | 0 | 0 | 0 | 0
22:00 | 0 | 0 | 0 | 180 | 0 | 39 | 0 | 409 | 306 |  | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 12 | 20 | 18 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 0 | 6 | 12 | 31 | 0 | 0 | 0 | 305 | 0 | 0 | 102 | 0 | 47 | 31 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 8 | 110 | 98 | 0 | 0 | 0 | 43 | 28 | 0 | 47 | 0 | 0 | 0 | 38 | 0 | 199 | 18 | 0 | 10 | 275 | 16 | 5 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 0 | 12 | 17 | 0 | 401 | 19 | 17 | 17 | 0 | 15 | 17 | 17 | 0 | 9 | 0 | 390 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 17 | 0 | 395 | 0 | 0 | 453 | 0 | 0 | 0 | 0 |  | 477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 150 | 821 | 0 | 0 |  | 5310 | 3332 | 8642 | 3329 | 477 | 1634 | 0 | 278 | 2768 | 46 | 0 | 0 | 110 | 0 | 0 | 0 | 98.61
23:00 | 0 | 0 | 0 | 180 | 0 | 39 | 0 | 406 | 307 |  | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 20 | 18 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 12 | 31 | 0 | 0 | 0 | 285 | 0 | 0 | 102 | 0 | 47 | 31 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 8 | 194 | 103 | 0 | 0 | 0 | 43 | 28 | 0 | 47 | 0 | 0 | 0 | 5 | 0 | 200 | 18 | 0 | 10 | 265 | 16 | 5 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 12 | 19 | 0 | 401 | 0 | 0 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 350 | 0 | 0 | 440 | 0 | 0 | 0 | 0 |  | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 740 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 150 | 826 | 0 | 0 |  | 5130 | 3228 | 8358 | 3277 | 447 | 1591 | 0 | 121 | 2682 | 46 | 0 | 0 | 194 | 0 | 0 | 0 | 98.6
24:00 | 0 | 0 | 0 | 180 | 0 | 39 | 0 | 393 | 307 |  | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 19 | 18 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 5 | 12 | 32 | 0 | 0 | 0 | 280 | 0 | 0 | 55 | 0 | 46 | 31 | 0 | 5 | 0 | 0 | 0 | 16 | 11 | 33 | 8 | 94 | 103 | 0 | 0 | 0 | 43 | 28 | 0 | 5 | 0 | 0 | 0 | 5 | 0 | 202 | 17 | 0 | 10 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 350 | 0 | 0 | 400 | 0 | 0 | 0 | 0 |  | 446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 150 | 823 | 0 | 0 |  | 4791 | 3171 | 7962 | 3256 | 446 | 1471 | 0 | 59 | 2590 | 46 | 0 | 0 | 94 | 0 | 0 | 0 | 98.6
KWH | 0 | 0 | 0 | 4394250 | 0 | 960772 | 0 | 8988670 | 7008000 |  | 0 | 4851600 | 0 | 0 | 0 | 0 | 6675439 | 0 | 0 | 0 | 0 | 57120 | 0 | 0 | 0 | 0 | 104400 | 34951 | 29831 | 297144 | 480000 | 254160 | 590200 | 783900 | 42240 | 0 | 1138440 | 0 | 0 | 0 | 0 | 4882036 | 0 | 0 | 0 |  | 0 | 0 | 0 | 59400 | 0 | 68160 | 288624 | 626880 | 0 | 0 | 0 | 7473600 | 0 | 0 | 1990545 | 0 | 917064 | 617760 | 0 | 792256 | 0 | 0 | 0 | 343372 | 233280 | 785800 | 194390 | 2215680 | 2095680 | 0 | 0 | 12350 | 1016000 | 704400 | 0 | 614880 | 0 | 0 | 0 | 800640 | 0 | 4019250 | 413000 | 0 | 253620 | 6981500 | 357168 | 85752 | 0 | 0 | 0 | 0 | 619200 | 0 | 302976 | 134055 | 90240 | 202560 | 0 | 8879000 | 223200 | 83520 | 122109 | 22801 | 193200 | 95795 | 198218 | 0 | 362880 | 0 | 9053600 | 14400 | 292380 | 31680 | 199473 | 0 | 99360 | 182303 | 325440 | 0 | 7901100 | 0 | 0 | 9016362 | 24000 | 0 | 0 | 0 |  | 11827636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1659000 | 356300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238410 | 0 | 0 | 4136400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7863490 | 0 | 0 | 69696 | 0 | 186816 | 0 | 34309 | 55776 | 17313100 | 2623882 | 0 | 58800 | 32280 | 441360 | 46656 | 0 | 0 | 8909091 | 146247 | 3774500 | 19876364 | 1066090 | 0 |  | 114204056 | 80716203 | 194920259 | 74004289 | 11827636 | 36342125 | 0 | 3920977 | 63025817 | 1138440 | 0 | 57120 | 2215680 | 2364175 | 24000 | 0
Fuel Cost | 0 | 0 | 0 | 6547432.5 | 0 | 1277826.76 | 0 | 9438103.5 | 7568640 |  | 0 | 5288244 | 0 | 0 | 0 | 0 | 7476491.68 | 0 | 0 | 0 | 0 | 925915.2 | 0 | 0 | 0 | 0 | 1327968 | 471838.5 | 400033.71 | 222858 | 360000 | 0 | 0 | 0 | 718502.4 | 0 | 307378.8 | 0 | 0 | 0 | 0 | 5077317.44 | 0 | 0 | 0 |  | 0 | 0 | 0 | 802494 | 0 | 788611.2 | 366552.48 | 2087510.4 | 0 | 0 | 0 | 8295696 | 0 | 0 | 2567803.05 | 0 | 1036282.32 | 920462.4 | 0 | 1323067.52 | 0 | 0 | 0 | 470419.64 | 174960 | 1375150 | 145792.5 | 15908582.4 | 2284291.2 | 0 | 0 | 196859 | 1391920 | 929808 | 0 | 1063742.4 | 0 | 0 | 0 | 1825459.2 | 0 | 4059442.5 | 887950 | 0 | 502167.6 | 6981500 | 267876 | 65171.52 | 0 | 0 | 0 | 0 | 8346816 | 0 | 4196217.6 | 1567102.95 | 931276.8 | 2766969.6 | 0 | 8168680 | 2714112 | 1207699.2 | 1544678.85 | 354783.56 | 2268168 | 1043207.55 | 2107057.34 | 0 | 4677523.2 | 0 | 8329312 | 186480 | 4224891 | 402019.2 | 2270002.74 | 0 | 1297641.6 | 2178520.85 | 4871836.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 35482908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1858080 | 691222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180476.37 | 0 | 0 | 35076672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7784855.1 | 0 | 0 | 824503.68 | 0 | 2372563.2 | 0 | 379114.45 | 677120.64 | 143698730 | 2676359.64 | 0 | 435120 | 365086.8 | 5177152.8 | 715236.48 | 0 | 0 | 80983637.19 | 0 | 45180765 | 169942912.2 | 0 | 0 |  | 169783118.66 | 534502515.55 | 704285634.21 | 69410063.65 | 35482908 | 42558860.07 | 0 | 50365698.29 | 474882716.39 | 307378.8 | 0 | 925915.2 | 15908582.4 | 14443511.41 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 65 | 0 | 335 | 260 |  | 0 | 180 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 11 | 25 | 32 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 12 | 30 | 0 | 0 | 0 | 280 | 0 | 0 | 55 | 0 | 47 | 10 | 0 | 10 | 0 | 0 | 0 | 16 | 11 | 33 | 6 | 88 | 75 | 0 | 0 | 2 | 43 | 28 | 0 | 18 | 0 | 0 | 0 | 40 | 0 | 196 | 16 | 0 | 10 | 300 | 8 | 2 | 0 | 0 | 0 | 0 | 29 | 0 | 17 | 20 | 0 | 14 | 0 | 400 | 8 | 0 | 0 | 5 | 0 | 0 | 17 | 0 | 37 | 0 | 390 | 0 | 52 | 0 | 17 | 0 | 0 | 32 | 18 | 0 | 350 | 0 | 0 | 358 | 0 | 0 | 0 | 0 |  | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 820 | 110 | 0 | 0 | 5 | 66 | 0 | 0 | 0 | 351 | 27 | 150 | 827 | 161 | 0 |  | 8215 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 39 | 0 | 400 | 337 |  | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 5 | 9 | 20 | 7 | 25 | 33 | 8 | 0 | 46 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 6 | 12 | 30 | 0 | 0 | 0 | 305 | 0 | 0 | 158 | 0 | 48 | 10 | 0 | 34 | 0 | 0 | 0 | 16 | 11 | 33 | 8 | 108 | 85 | 0 | 0 | 0 | 43 | 28 | 0 | 41 | 0 | 0 | 0 | 40 | 0 | 195 | 17 | 0 | 10 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 93 | 0 | 20 | 0 | 12 | 17 | 0 | 401 | 47 | 0 | 17 | 0 | 15 | 8 | 17 | 0 | 32 | 0 | 395 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 41 | 0 | 395 | 0 | 0 | 480 | 0 | 0 | 0 | 0 |  | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 12 | 0 | 70 | 0 | 0 | 20 | 890 | 110 | 0 | 12 | 0 | 0 | 17 | 0 | 0 | 502 | 0 | 230 | 820 | 0 | 0 |  | 9061 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 77 | 0 | 412 | 330 |  | 0 | 225 | 0 | 100 | 85 | 30 | 335 | 0 | 0 | 92 | 100 | 149 | 40 | 0 | 0 | 0 | 35 | 35 | 35 | 18 | 20 | 11 | 33 | 33 | 25 | 0 | 46 | 0 | 0 | 0 | 17 | 212 | 0 | 0 | 0 |  | 6 | 64 | 0 | 12 | 0 | 10 | 12 | 25 | 0 | 0 | 0 | 320 | 0 | 0 | 102 | 0 | 51 | 40 | 0 | 51 | 0 | 0 | 52 | 18 | 11 | 33 | 10 | 140 | 90 | 0 | 0 | 0 | 43 | 28 | 0 | 44 | 0 | 0 | 0 | 40 | 0 | 200 | 17 | 0 | 10 | 310 | 16 | 5 | 0 | 130 | 0 | 0 | 104 | 0 | 100 | 0 | 12 | 17 | 150 | 400 | 85 | 105 | 17 | 0 | 260 | 17 | 17 | 114 | 65 | 12 | 400 | 88 | 0 | 35 | 17 | 0 | 17 | 0 | 72 | 35 | 395 | 0 | 0 | 500 | 10 | 0 | 0 | 0 |  | 453 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 50 | 70 | 16 | 130 | 25 | 110 | 0 | 0 | 0 | 35 | 20 | 85 | 28 | 42 | 40 | 52 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 105 | 0 | 50 | 32 | 113 | 0 | 0 | 113 | 1220 | 110 | 0 | 150 | 0 | 0 | 110 | 0 | 0 | 550 | 0 | 150 | 900 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 77 | 0 | 412 | 330 | 0 | 0 | 225 | 0 | 92 | 85 | 15 | 335 | 0 | 0 | 92 | 100 | 16 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 20 | 11 | 33 | 33 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 212 |  | 0 | 0 | 0 | 6 | 40 | 0 | 12 | 0 | 6 | 12 | 10 | 0 | 0 | 0 | 320 | 0 | 0 | 55 | 0 | 51 | 40 | 0 | 51 | 0 | 0 | 52 | 18 | 11 | 33 | 10 | 128 | 80 | 0 | 0 | 1.6 | 43 | 28 | 0 | 44 | 0 | 0 | 0 | 40 | 0 | 200 | 17 | 0 | 10 | 310 | 16 | 5 | 0 | 80 | 0 | 0 | 84 | 0 | 18 | 20 | 12 | 17 | 150 | 400 | 56 | 30 | 17 | 5 | 260 | 17 | 17 | 114 | 28 | 12 | 400 | 26 | 50 | 17 | 17 | 0 | 17 | 35 | 36 | 17 | 395 | 0 |  | 400 | 10 | 0 | 0 | 0 |  | 453 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 28 | 34 | 30 | 52 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 105 | 0 | 35 | 15 | 113 | 0 | 8 | 35 | 1000 | 110 |  | 0 | 6 | 100 | 70 | 0 |  | 450 | 30 | 150 | 850 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 26 | 0 | 372 | 308 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 18 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 10 | 0 | 0 | 0 | 310 | 0 | 0 | 8 | 0 | 47 | 10 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 33 | 8 | 92 | 104 | 0 | 0 | 1 | 43 | 28 | 0 | 31 | 0 | 0 | 0 | 37 | 0 | 203 | 17 | 0 | 10 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 9 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 385 | 0 | 0 | 368 | 11 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 113 | 0 | 1 | 0 | 620 | 110 | 0 | 0 | 1 | 26 | 0 | 0 | 0 | 352 | 11 | 140 | 821 | 56 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
[8 empty] | 299430 | [13 empty] | 299565 | [26 empty] | 399366 | 399587 | [8 empty] | 299280 | [26 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 |  | 399747 |  |  |  | 399575 |  | 399337 | 399589 | 299230 | [7 empty] | 399245 |  | 299282 | 399274 |  | 399223 |  | 399630 | [12 empty] | 599468 | [32 empty] | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 | [8 empty] | 599726 | [9 empty] | 292.3904
| Minimum Generation |  | 7277 | 5:00 | [202 empty] | 110346414
| Highest Generation |  | 9061 | 18:00 | [202 empty] | 110.3464 |  |  |  |  | 2.3642
| Day Peak Generation |  | 8215 | 12:00 | [202 empty] | 3978097
| Evening Peak Generation |  | 9061 | 18:00 | [202 empty] | 3.9781 |  |  | 36342125 |  | 1.1384
| HVDC Max Flow |  | 917 | 1:00 | [202 empty] | 11.8276 |  |  |  |  | 0.024
| HVDC EvPeak Flow |  | 209 | 18:00 | [200 empty] | 194920259 |  | 2.2157 |  | 63.0258
| Load factor L.F |  | 89.63% | [166 empty] | 1275.5 | [36 empty] | 194.9203

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-11-25
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-11-24 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 8215 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6700
Evening Peak Generation : |  |  | 9061 | MW Hour : | 18:00 | Available Max Generation : |  | 13049
E.P. Demand (at gen end) : |  |  | 9061 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 10200
Maximum Generation : |  |  | 9061 | MW Hour : | 18:00 | Reserve(Generation end) |  | 2849
Total Gen. (MKWH) : |  |  | 194.9203 | System Load Factor : | 89.63% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 300 | MW at | 19:30 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-11-25
Actual : |  | 98.58 | Ft.(MSL) , | Rule curve : | 106.6 | Ft.( MSL )
Gas Consumed : |  | Total = | 796.38 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 111968923.72
: |  |  | Coal : | 474882716.39 | Oil : | 51291613.49 | Total : | 638143253.6
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3693.7597 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1009.6328 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1412.702 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1226.4236 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1009.8797 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 750.3172 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 421.4087 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 350.4332 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 685.4034 |  |  | 0 | 0%
Total |  | 0 |  | 10559.9605 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:07 | 11:27 | Bogura 132/33kV S/S Transformer-3 HT Forced S/D Due to Red hot to Auxiliary DS.
08:20 |  | Summit Power Madhabdi Control Room Shutdown
08:47 |  | Maniknagar 132/33kV S/S Motijheel Ckt-2 Scheduled S/D Due to Annual Maintenance schedule 2023-24.
09:37 |  | Matuail 132/33kV S/S 132/33 kV GT-1 HT Scheduled S/D Due to Schedule maintenance work
09:37 |  | 132/33 kV GT-1 HV side and LV side of Matuail Grid Substation were opened as scheduled shut down.
10:09 |  | Haripur- Rahim Steel 132 kV circuit scheduled S/D is taken due to the changing of LA in Rahim Steel side.
10:29 | 10:42 | Shariatpur 132/33kV S/S T2-416T LT Forced S/D Due to Maintenance by PBS | [5 empty] | 10 MW load interrup.
| 10:29 | Chandpur 115(Doreen) Syncronized
10:29 | 10:41 | Shariatpur 132/33kV S/S T2-416T HT Forced S/D Due to Maintenance by PBS
| 10:30 | Summit Power Madhabdi Control Room Syncronized
| 10:32 | Chowmuhani 113 MW Syncronized
| 10:35 | Karnaphuli Power Ltd. Syncronized
| 10:36 | Anlima Energy Ltd. Syncronized
| 10:36 | Kodda 150 MW PP B-R Syncronized
| 10:45 | Patenga 50MW PP (Baraka) Syncronized
| 11:01 | Chandpur 200MW (Desh energy) Syncronized
| 11:05 | Bogura 132/33kV S/S 132KV Bus-B is restored.
| 11:07 | Keranigonj 230/132/33kV S/S TR-2 HT is restored.
| 11:08 | Keranigonj 230/132/33kV S/S TR-2 LT is restored.
11:12 |  | Khulna (C) S/S Tr-2 415 T LT Scheduled S/D Due to For Oil Centrifuging
11:13 |  | Khulna (C) S/S Tr-2 415 T HT Scheduled S/D Due to For Oil Centrifuging .
| 11:50 | Rangpur 113 MW PP (Confidence) Syncronized
12:00 |  | Haripur- Rahim Steel 132 kV circuit is restored after scheduled S/D.
| 12:20 | Gazipur 52 MW PP Syncronized
| 12:34 | Joydebpur-Kodda B 132 kV Ckt-2 is restored.
| 12:34 | Joydebpur-Kodda B 132 kV Ckt-1 is restored.
14:28 |  | Kodda 150 MW PP B-R Shutdown
| 14:29 | Mirpur 132/33kV S/S T1 HT is restored.
| 14:29 | Mirpur 132/33kV S/S T1 LT is restored.
14:43 |  | Gazipur 52 MW PP Shutdown
14:44 |  | Bhola 225 MW CCPP Syncronized with remarks:- GT-2
14:44 |  | Jamalpur 115 MW PP (United) Shutdown
14:45 |  | Anlima Energy Ltd. Shutdown
14:46 |  | Karnaphuli Power Ltd. Shutdown
14:47 |  | Patenga 50MW PP (Baraka) Shutdown
14:51 |  | Chandpur 200MW (Desh energy) Shutdown
14:57 |  | Chandpur 115(Doreen) Shutdown
15:02 |  | Kodda 149 MW PP Unit-1 (Summit) Shutdown
15:25 |  | Chowmuhani 113 MW Shutdown
| 15:38 | Kishoreganj 132/33kV S/S Tr-3 (424T) HT is restored.
| 15:50 | Chowmuhani-Feni 132 kV Ckt-2 is restored.
| 15:50 | Kishoreganj 132/33kV S/S Tr-2 (414T) LT is restored.
| 15:50 | Kishoreganj 132/33kV S/S Tr-2 (414T) HT is restored.
| 16:12 | Barishal 132/33kV S/S T-1 (405T) HT is restored.
| 16:14 | Barishal 132/33kV S/S T-1 (405T) LT is restored.
| 16:24 | Anlima Energy Ltd. Syncronized
| 16:25 | Maniknagar 132/33kV S/S Motijheel Ckt-2 is restored.
| 16:26 | Anlima Energy Ltd. Syncronized
| 16:27 | Anwara 300 MW PP (United) Syncronized
| 16:28 | Patenga 50MW PP (Baraka) Syncronized
| 16:28 | Chandpur 200MW (Desh energy) Syncronized
| 16:31 | Chandpur 115(Doreen) Syncronized
| 16:32 | Kaptai 7 MW Solar PP Shutdown
| 16:35 | Juldah 100 MW PP Unit-3 (Acorn) Syncronized
| 16:37 | Kodda 149 MW PP Unit-1 (Summit) Syncronized
| 16:37 | Jamalpur 115 MW PP (United) Syncronized
| 16:38 | Juldah 100 MW Unit-1 (Acorn) Syncronized
| 16:40 | Chowmuhani 113 MW Syncronized
| 16:43 | Kamalaghat 54 MW PP(Banco Energy) Syncronized
| 16:43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) Syncronized
| 16:45 | Baghabari-Sirajganj 132 kV Ckt-1 is restored.
| 16:45 | Karnaphuli Power Ltd. Syncronized
| 16:46 | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-2 is restored.
| 16:47 | Sirajganj 132/33kV S/S Sherpur-2 is restored.
16:50 |  | Sarishabari 3 MW Solar Plant Shutdown
| 17:00 | Ghorasal- Ishwardi 230 kV Ckt-1 is restored.
| 17:01 | Gazipur 52 MW PP Syncronized
| 17:10 | Hobiganj 11MW PP Cofidence-E Syncronized
17:10 |  | Teknaf 20MW PP (Solartech) Shutdown
17:13 |  | Sirajgonj 6.55 MW Solar Shutdown
17:14 |  | Teesta Solar Limited Shutdown
17:15 |  | Sympa Solar Power 8 MW Shutdown
17:15 | 18:06 | Kishoreganj 132/33kV S/S Tr-1 (404T) LT Forced S/D Due to 33 kv T3 Bus coupler DS Sparking problem | [5 empty] | 9 MW load interrup.
17:15 | 18:06 | Kishoreganj 132/33kV S/S Tr-1 (404T) HT Forced S/D Due to 33 kv T3 Bus coupler DS Sparking problem
17:20 |  | Spectra Solar Plant Ltd. Shutdown
17:22 |  | Mongla Orion 100 MW Solar PP Shutdown
| 17:25 | Jodiac Power Syncronized
| 17:25 | Bagura 113 MW PP (Confidence)-2 Syncronized
| 17:27 | Energypac Power Venture Thakurgaon Ltd. Syncronized
17:27 |  | Sutiakhali 50 MW Solar PP Shutdown
| 17:32 | United Payra Power Ltd. Syncronized
| 17:39 | Confidence Power Bogura Unit-1 113 MW Syncronized
17:40 |  | Intraco Solar 30 MW Shutdown
| 17:40 | Manikgonj 162MW PP(MPGL) Syncronized
| 17:45 | Manikganj 55 MW PP (Northern) Syncronized
| 17:46 | Nababganj 55 MW PP (Southern power ) Syncronized
| 17:46 | Nababganj 55 MW PP (Southern power ) Syncronized
| 18:02 | Meghnaghat 104 MW PP (OPCL) Syncronized
| 18:06 | Kishoreganj 132/33kV S/S Tr-1 (404T) LT is restored.
| 18:23 | Gazipur 100 MW PP Syncronized
| 18:30 | Bhairob 54.5 MW Syncronized
| 18:46 | Nababganj 55 MW PP (Southern power ) Syncronized
19:00 |  | Energypac Power Venture Thakurgaon Ltd. Shutdown
19:02 |  | Narshingdi 22 MW PP (Doreen) Tripped
19:13 |  | Meghnaghat 104 MW PP (OPCL) Shutdown
19:21 |  | Confidence Power Bogura Unit-1 113 MW Shutdown
19:29 |  | Manikgonj 162MW PP(MPGL) Shutdown
19:29 |  | United Payra Power Ltd. Shutdown
19:29 |  | Bagura 113 MW PP (Confidence)-2 Shutdown
19:32 |  | Nababganj 55 MW PP (Southern power ) Shutdown
19:53 |  | Gazipur 52 MW PP Shutdown
19:58 |  | Manikganj 55 MW PP (Northern) Shutdown
| 20:16 | Narshingdi 22 MW PP (Doreen) Syncronized
20:30 |  | Rangpur 113 MW PP (Confidence) Shutdown
20:56 | 21:36 | Madaripur 132/33kV S/S T1-405T HT Forced S/D Due to WZ 33 kv bus Ds fault maintenance | [5 empty] | 17 MW load interrup.
20:56 | 21:37 | Madaripur 132/33kV S/S T1-405T LT Forced S/D Due to WZ 33 KV Bus DS fault maintenance
| 21:39 | Matuail 132/33kV S/S 132/33 kV GT-1 HT is restored.
22:18 |  | Anwara 300 MW PP (United) Shutdown
22:19 |  | Juldah 100 MW Unit-1 (Acorn) Shutdown
22:33 |  | Gazipur 100 MW PP Shutdown
22:33 |  | Kamalaghat 54 MW PP(Banco Energy) Shutdown
22:38 |  | Kodda 149 MW PP Unit-1 (Summit) Shutdown
22:39 |  | Jamalpur 115 MW PP (United) Shutdown
22:50 |  | Chowmuhani 113 MW Shutdown
22:52 |  | Jodiac Power Shutdown
22:58 |  | Chandpur 115(Doreen) Shutdown
23:47 |  | Juldah 100 MW PP Unit-3 (Acorn) Shutdown
23:47 |  | Mymensingh 200 MW PP (United) Shutdown
23:55 |  | Anlima Energy Ltd. Shutdown
23:55 |  | Sikalbaha 105 MW PP (Baraka Sikalbaha) Shutdown
00:04 |  | Patenga 50MW PP (Baraka) Shutdown
00:31 |  | Chandpur 200MW (Desh energy) Shutdown
00:34 |  | Karnaphuli Power Ltd. Shutdown
00:44 |  | Ghorashal 108 MW PP (Regent) Shutdown
00:50 |  | Ashuganj 195 MW PP (APSCL-United) Shutdown
| 05:33 | Rangpur 113 MW PP (Confidence) Syncronized
| 05:35 | Ashuganj 195 MW PP (APSCL-United) Syncronized
| 06:07 | Teknaf 20MW PP (Solartech) Syncronized
| 06:11 | Kaptai 7 MW Solar PP Syncronized
| 06:13 | Sutiakhali 50 MW Solar PP Syncronized
| 06:17 | Mongla Orion 100 MW Solar PP Syncronized
| 06:18 | Spectra Solar Plant Ltd. Syncronized
| 06:21 | Intraco Solar 30 MW Syncronized
| 06:23 | Sirajgonj 6.55 MW Solar Syncronized
| 06:25 | Sympa Solar Power 8 MW Syncronized
| 06:30 | Teesta Solar Limited Syncronized
| 06:30 | Sarishabari 3 MW Solar Plant Syncronized
06:38 |  | Chowmuhani-Feni 132 kV Ckt-1 Project Work S/D from Feni 132/33kV end.
| 06:43 | Mymensingh 200 MW PP (United) Syncronized
| 06:44 | Ghorashal 108 MW PP (Regent) Syncronized
07:05 |  | Feni 22MW PP (Doreen) Forced Shutdown with remarks:- On request of BPDB
07:06 |  | Ghorasal- Ishwardi 230 kV Ckt-1 Scheduled S/D from Ishurdi 230/132kV end Due to annual maintanance
07:10 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) LT Scheduled S/D
07:11 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) HT Scheduled S/D Due to Annual maintenance
07:12 |  | Sirajganj 132/33kV S/S Sherpur-2 Project Work S/D Due to Tower erection of 68 MW solar power plant.
07:12 |  | Narshingdi 22 MW PP (Doreen) Tripped

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-11-24 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4394250
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 39 | 960772 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 400 | 8988670
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 337 | 7008000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4851600 | GT-1 under S/D due to gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | GT-1 under S/D due to gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 9 | 297144 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 6675439
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 104400 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 57120 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 34951 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 5 | 29831 | High Voltage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 27 | 734160 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 590200 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 783900
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 42240 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 20 | 302976 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 83520 | Reserve
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 14400 | Reserve
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 31680 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 182303
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Reserve
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5422 | 1694 | 36167556
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 0 | Reserve
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 134055
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 6 | 68160 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1138440 | Unit-2 under maint.
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 210 | 4882036
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 122109 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 12 | 59400 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 90240 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 12 | 288624 | Fuel shortage
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 30 | 626880
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 22801
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 193200 | Low demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 8 | 95795 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 198218 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 199473 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 0 | 0 | Fuel shortage
| SS Power I |  | SS Power | 1*612 | 612 | 480 | 9016362
| Cox's Bazar Wind |  | IPP | 66 | 0 | 0 | 24000 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 3157 | 882 | 17159793
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 0 | Under maint.
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 305 | 7473600 | Under maint.
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 395 | 7901100
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 48 | 917064
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 0 | 10 | 617760 | Gas shortage
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 158 | 1990545 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 34 | 792256
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Under maint.
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 202560 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 343372 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 233280
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 108 | 2215680
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 785800
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 8 | 194390 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 32 | 362880 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 99360 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 41 | 325440 | Fuel shortage
| Cumilla Area Total |  |  |  | 2896 | 1216 | 24455087
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 85 | 2095680 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Contract Expired
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12350
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 93 | 619200 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 47 | 223200 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 292380
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 225 | 3242810
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1016000
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 28 | 704400 | Engine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 41 | 614880 | Gas shortage
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 85752 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under maint.
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 40 | 800640 | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 195 | 4019250 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 413000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 357168 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 6981500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 401 | 8879000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 253620
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 395 | 9053600
| Sylhet Area Total |  |  |  | 2427 | 1491 | 33178810
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 209 | 11827636
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 0 | Reserve
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Reserve
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Reserve
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 441360
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 502 | 8909091
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 711 | 21178087
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 16 | 356300 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 50 | 1659000 | ST Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 890 | 17313100
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 110 | 2623882 | GT-1 Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 12 | 58800 | Low demand
| Barisal 307 MW |  | IPP | 307*1 | 307 | 230 | 3774500 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1308 | 25785582
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 7863490 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 238410
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 12 | 69696 | Low demand
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 20 | 55776 | Low demand
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 32280
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 820 | 19876364
| Rajshahi Area Total |  |  |  | 3631 | 1277 | 28136016
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4136400 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 186816 | Low demand
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 34309
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 17 | 46656 | Low demand
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 146247
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1066090
| Rangpur Area Total |  |  |  | 950 | 257 | 5616518
| Total |  |  |  | 24599 | 9061 | 194920259
| Eastern Grid Total |  |  |  | 14516 | 5508 | 114204056
| Western Grid Total |  |  |  | 10083 | 3553 | 80716203
| National Grid Total |  |  |  | 24599 | 9061 | 194920259
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-11-24
| (a) ENTIRE EASTERN GRID : |  | 5939.46 | MW | (b) ENTIRE WESTERN GRID : |  | 2843.6 | MW
| i) Dhaka area |  | 3146.56 | MW | i) Khulna area |  | 1056.9 | MW
| ii) Chittagong area |  | 976.9 | MW | ii) Rajshahi area |  | 892.4 | MW
| iii) Comilla area |  | 761 | MW | iii) Barisal area |  | 255.3 | MW
| iv) Mymensingh area |  | 693 | MW | iv) Rangpur area |  | 639 | MW
| v) Sylhet area |  | 362 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8783.06 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 19 | 00:00 | Kamrangirchar | 36 | 00:00 | Narinda | 32 | 13:00 | Sherpur | 92 | 18:00
2 | AKSML | 101.2 | 01:00 | Chowmuhani | 124 | 20:00 | Kaptai | N/A | N/A | Narshingdi | 133 | 20:00 | Shikalbaha | 18 | 00:00
3 | Aftabnagar | 26 | 13:00 | Chuadanga | 66 | 18:00 | Kazla | 74 | 13:00 | Natore | 86 | 18:00 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 64 | 13:00 | Coxsbazar | 91 | 18:00 | Keranigonj | 56 | 11:00 | Nawabganj | 33.4 | 21:00 | Shitalakhya | 61.5 | 00:00
5 | Agrabad | 40 | 18:00 | Cumilla(N) | 89 | 18:00 | Khagrachori | 20 | 18:30 | Netrakona | 91 | 18:00 | Sholosohor | 25 | 00:00
6 | Amnura | 32 | 18:00 | Cumilla(S) | 110 | 22:00 | Khulna | 68 | 13:00 | New | 40.8 | 00:00 | Shyampur | 148 | 00:00
7 | Ashuganj | 52 | 00:00 | Daudkandi | 104 | 20:00 | Khulshi | 122 | 00:00 | Niamatpur | 45 | 18:00 | Siddhirganj | 80 | 12:00
8 | BIPTC | N/A | N/A | Dhaka | 14 | 12:00 | Kishoreganj | 106 | 18:30 | Noapara | 25.5 | 19:30 | Sirajganj | 65 | 18:00
9 | BSRM | 138 | 23:00 | Dhamrai | 76 | 13:00 | Kodda | 182 | 12:00 | PHP | 8 | 08:00 | Sonargaon | 91 | 02:00
10 | Bagerhat | 63 | 18:00 | Dhanmondi | 77 | 13:00 | Kulaura | 28 | 18:00 | Pabna | 72 | 18:00 | Sreemongol | 46 | 18:00
11 | Bakulia | 60 | 00:00 | Dohazari | 60 | 18:30 | Kurigram | 50 | 18:00 | Palashbari | 76 | 18:00 | Sreepur | 38 | 00:00
12 | Banani | 0 | 00:00 | Faridpur | 93 | 19:30 | Kushtia | 92 | 18:00 | Panchagarh | 43 | 18:00 | Srinagar | 29 | 13:00
13 | Bangabhaban | 4 | 10:00 | Fatullah | 49 | 00:00 | Lalbag | 71 | 00:00 | Patuakhali | 56.9 | 21:00 | Sunamganj | 34 | 18:00
14 | Barapukuria | 40 | 18:00 | Fenchuganj | 23 | 19:00 | Lalmonirhat | 37 | 10:00 | Payra | 20 | 21:00 | Sylhet | 14 | 12:00
15 | Barguna | 12 | 00:00 | Feni | 73 | 19:00 | MI_Cement | 19.4 | 15:00 | Postogola | 37 | 00:00 | Sylhet-132 | 85 | 17:00
16 | Barishal | 69 | 21:00 | GPH | 93 | 14:00 | Madanganj | 29 | 13:00 | Purbachal | 14 | 12:00 | TK | 17.6 | 00:00
17 | Barishal-230 | 58 | 13:00 | Ghorashal | 47 | 00:00 | Madaripur | 61 | 22:00 | Purbasadipur | 90 | 18:00 | Tangail | 136 | 18:00
18 | Baroaulia | 80 | 00:00 | Goalpara | 26 | 13:00 | Madartek | 61.29 | 13:00 | Rahim | 47 | 00:00 | Thakurgaon | 67 | 18:00
19 | Baroirhat | 26 | 19:00 | Gollamari | 34 | 13:00 | Madunaghat | 33 | 18:00 | Rajbari | 42 | 18:00 | Tongi | 73 | 00:00
20 | Bashundhara | 121 | 13:00 | Gopalganj | 63.9 | 18:00 | Magura | 39 | 18:00 | Rajendrapur | 66 | 00:00 | Ullon | 34 | 12:00
21 | BashundharaCement | 0 | 00:00 | Gulshan | 62 | 13:00 | Mahasthangarh | 48 | 18:00 | Rajshahi | 88 | 19:30 | Uttara | 45 | 12:00
22 | Beanibazar | 42 | 18:30 | Halishahar | 60 | 19:30 | Manikganj | 67 | 00:00 | Rajshahi-230 | 21 | 20:00 | UttaraNew | 39 | 12:00
23 | Benapole | 38 | 18:00 | HaripurSBU | 121 | 00:00 | Maniknagar | 44 | 12:00 | Ramganj | 66 | 19:30 | Zigatola | 72 | 13:00
24 | Bhaluka | 98 | 13:00 | Hasnabad | 68 | 12:00 | Matarbari | 18 | 18:00 | Rampur | 28 | 00:00
25 | Bhandaria | 32 | 20:00 | Hathazari | 44 | 18:00 | Matuail | 47 | 00:00 | Rangamati | 12 | 18:00
26 | Bhangura | 20 | 18:00 | Ishurdi | 43 | 20:00 | Millgate | 62 | 11:00 | Rangpur | 95 | 18:30
27 | Bheramara(GK) | 35 | 18:00 | Jaldhaka | 55 | 18:00 | Mirpur | 92 | 12:00 | Ruppur | 4.8 | 11:00
28 | Bhulta | 211 | 00:00 | Jamalpur | 113 | 18:00 | Mirsorai | 3.5 | 18:00 | SSM | 8 | 03:00
29 | Bog-Sherpur | 46 | 18:00 | Jashore | 86 | 18:00 | Mirzapur | 15 | 18:30 | Saidpur | 66 | 18:00
30 | Bogura | 102 | 18:00 | Jhenaidah | 83 | 18:00 | Mithapukur | 78 | 16:00 | Satkhira | 81 | 18:00
31 | Borhanuddin | 34 | 20:00 | Joydebpur | 109 | 00:00 | Modern | 0 | 00:00 | Satmasjid | 73 | 13:00
32 | Brahmanbaria | 106 | 20:00 | Joypurhat | 40 | 18:00 | Mogbazar | 77.1 | 11:00 | Savar | 126 | 12:00
33 | Cantonment | 102 | 13:00 | Juldah | 18 | 00:00 | Mongla | 25 | 12:00 | SevenRings | 9.55 | 03:00
34 | Chandpur | 42 | 19:00 | KSRM | 33.5 | 02:00 | Motijheel | 23 | 18:30 | ShahCement | 20 | 12:00
35 | Chandraghona | 23 | 12:00 | Kabirpur | 178 | 00:00 | Munshiganj | 74 | 13:00 | Shahjadpur | 57 | 18:00
36 | Chapai | 43 | 11:00 | Kachua | 47 | 19:00 | Mymensingh | 147 | 18:00 | Shahjibazar | 84 | 18:30
37 | Charsaidpur | 23 | 01:00 | Kallyanpur | 60 | 13:00 | Naogaon | 85 | 18:00 | Shahmirpur | 22 | 00:00
38 | Chauddagram | 35 | 18:00 | Kalurghat | 20 | 00:00 | Narail | 32 | 18:00 | Shariatpur | 48 | 21:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-11-24 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 408 | 09:00 | 394 | 12:00 | Gopalganj | 411 | 08:00 | 403 | 12:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | N/A | N/A | N/A | N/A
| Bhulta | 415 | 08:00 | 406 | 12:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 410 | 22:00 | 400 | 01:00 | Payra | 418 | 08:00 | 412 | 12:00
| BIPTC | 409 | 19:00 | 396 | 00:00 | Rahanpur | 406 | 03:00 | 399 | 17:00
| Bogura | N/A | N/A | N/A | N/A | Rampal | 411 | 06:00 | 403 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 237 | 08:00 | 231 | 00:00 | Hasnabad | 238 | 19:00 | 233 | 00:00
| AKSML | 229 | 14:00 | 223 | 23:00 | Hathazari | 229 | 09:00 | 222 | 16:00
| Aminbazar | 236 | 08:00 | 230 | 12:00 | Ishurdi | 235 | 05:00 | 226 | 12:00
| Ashuganj | 236 | 06:00 | 228 | 01:00 | Jhenaidah | 234 | 03:00 | 225 | 13:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | N/A | N/A | N/A | N/A
| Baghabari | 230 | 19:00 | 223 | 12:00 | Keranigonj | 237 | 08:00 | 230 | 00:00
| Barapukuria | 226 | 05:00 | 222 | 19:30 | Khulna(S) | 241 | 03:00 | 228 | 14:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 242 | 04:00 | 238 | 13:00 | Maniknagar | 239 | 08:00 | 234 | 00:00
| Bheramara | 236 | 08:00 | 226 | 12:00 | Meghnaghat | 242 | 14:00 | 239 | 00:00
| Bhulta | 240 | 08:00 | 235 | 12:00 | Mirsorai | 231 | 09:00 | 222 | 00:00
| Bibiana | 234 | 13:00 | 228 | 00:00 | Rajshahi | 236 | 08:00 | 225 | 12:00
| BIPTC | 235 | 08:00 | 224 | 12:00 | Rampal | 237 | 03:00 | 230 | 12:00
| Bogura | 234 | 19:00 | 228 | 12:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 245 | 04:00 | 242 | 00:00 | Rampura | 237 | 04:00 | 233 | 00:00
| BSRM | 231 | 08:00 | 222 | 00:00 | Shikalbaha | 224 | 09:00 | 220 | 00:00
| Cumilla(N) | 235 | 08:00 | 230 | 00:00 | Shyampur | 238 | 08:00 | 232 | 00:00
| Fenchuganj | 237 | 09:00 | 231 | 01:00 | Siddhirganj | 240 | 18:00 | 237 | 00:00
| Ghorashal | 240 | 15:00 | 230 | 01:00 | Sirajgonj | 240 | 19:00 | 234 | 12:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 235 | 08:00 | 229 | 12:00
| GPH | 229 | 09:00 | 221 | 00:00 | Tongi | 235 | 07:00 | 230 | 00:00
| Haripur | 238 | 08:00 | 233 | 00:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 135 | 08:00 | 131 | 11:00 | Lalbag | 136 | 09:00 | 132 | 00:00
| Agargaon | 139 | 08:00 | 135 | 00:00 | Lalmonirhat | 132 | 02:00 | 126 | 17:00
| Agrabad | 135 | 08:00 | 130 | 00:00 | Madanganj | 135 | 08:00 | 131 | 00:00
| AKS | 133 | 09:00 | 129 | 00:00 | Madaripur | 132 | 05:00 | 130 | 11:00
| Aminbazar | 139 | 08:00 | 135 | 12:00 | Madartek | 134 | 08:00 | 130 | 11:00
| Amnura | 137 | 06:00 | 128 | 12:00 | Madunaghat | 135 | 08:00 | 130 | 00:00
| Ashuganj | 140 | 00:00 | 136 | 13:00 | Magura | 137 | 04:00 | 131 | 12:00
| Bagerhat | 132 | 09:00 | 125 | 18:00 | Mahasthangarh | 137 | 04:00 | 132 | 12:00
| Bakulia | 134 | 07:00 | 130 | 23:00 | Manikganj | 132 | 13:00 | 124 | 00:00
| Banani | 137 | 08:00 | 130 | 04:00 | Maniknagar | 137 | 08:00 | 134 | 00:00
| Bangabhaban | 137 | 22:00 | 133 | 00:00 | Matarbari | 124 | 14:00 | 106 | 18:00
| Barapukuria | 136 | 05:00 | 132 | 19:30 | Matuail | 135.7 | 09:00 | 132 | 00:00
| Barguna | 135 | 04:00 | 133 | 00:00 | Millgate | 137 | 06:00 | 133 | 00:00
| Barishal | 137 | 04:00 | 130 | 12:00 | Mirpur | 139 | 08:00 | 134 | 12:00
| Barishal-230 | 138 | 05:00 | 135 | 00:00 | Mirzapur | 133 | 09:00 | 128 | 07:00
| Baroaulia | 135 | 09:00 | 131 | 12:00 | Mithapukur | 138 | 05:00 | 129 | 11:00
| Baroirhat | 132 | 08:00 | 127 | 00:00 | MI_Cement | 136 | 09:00 | 132 | 00:00
| Bashundhara | 138 | 08:00 | 132 | 12:00 | Modern | 133 | 06:00 | 130 | 00:00
| BashundharaCement | 135 | 08:00 | 131 | 00:00 | Mogbazar | 135 | 08:00 | 124 | 17:00
| Beanibazar | 131 | 07:00 | 129 | 00:00 | Mongla | 131 | 08:00 | 126 | 18:00
| Benapole | 135 | 06:00 | 127 | 13:00 | Motijheel | 137 | 22:00 | 133 | 00:00
| Bhaluka | 135 | 08:00 | 129 | 12:00 | Munshiganj | 136 | 19:00 | 132 | 00:00
| Bhandaria | 135 | 08:00 | 130 | 22:00 | Mymensingh | 136 | 18:00 | 126 | 13:00
| Bhangura | 141 | 04:00 | 137 | 12:00 | Naogaon | 134 | 02:00 | 129 | 12:00
| Bheramara | 136 | 06:00 | 131 | 12:00 | Narail | 137 | 03:00 | 130 | 12:00
| Bheramara(GK) | 136 | 06:00 | 131 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 130 | 17:00 | 123 | 00:00 | Narshingdi | 133 | 09:00 | 125 | 00:00
| Bog-Sherpur | 137 | 03:00 | 133 | 11:00 | Natore | 137 | 06:00 | 132 | 12:00
| Bogura | 139 | 04:00 | 133 | 12:00 | Nawabganj | 137 | 08:00 | 133 | 00:00
| Bogura-230 | 137 | 04:00 | 133 | 12:00 | Netrakona | 135 | 19:00 | 128 | 16:00
| Brahmanbaria | 131 | 07:00 | 126 | 23:00 | New | 138 | 19:00 | 133 | 11:00
| Cantonment | 138 | 05:00 | 134 | 12:00 | Niamatpur | 134 | 02:00 | 128 | 12:00
| Chandpur | 134 | 19:00 | 123 | 00:00 | Noapara | 135 | 06:00 | 129 | 12:00
| Chandraghona | 135 | 06:00 | 131 | 00:00 | Pabna | 138 | 03:00 | 132 | 13:00
| Chapai | 132 | 04:00 | 130 | 11:00 | Palashbari | 132 | 14:00 | 129 | 12:00
| Charsaidpur | 136 | 08:00 | 133 | 00:00 | Panchagarh | 132 | 05:00 | 120 | 09:00
| Chauddagram | 134 | 18:00 | 127 | 00:00 | Patuakhali | 135 | 05:00 | 133 | 00:00
| Chhatak | 131 | 00:00 | 129 | 11:00 | Payra | 136 | 03:00 | 134 | 00:00
| Chowmuhani | 131 | 17:00 | 122 | 14:00 | PHP | 132 | 08:00 | 126 | 00:00
| Chuadanga | 136 | 05:00 | 128 | 12:00 | Postogola | 138 | 09:00 | 134 | 00:00
| Coxsbazar | 126 | 09:00 | 107 | 18:00 | Purbachal | 139 | 09:00 | 132 | 12:00
| Cumilla(N) | 137 | 20:00 | 132 | 00:00 | Purbasadipur | 132 | 03:00 | 124 | 12:00
| Cumilla(S) | 136 | 19:00 | 130 | 00:00 | Rahanpur | 135 | 03:00 | 132 | 17:00
| Daudkandi | 134 | 07:00 | 129 | 00:00 | Rahim | 135 | 05:00 | 132 | 00:00
| Dhaka | 135 | 08:00 | 131 | 00:00 | Rajbari | 133 | 03:00 | 129 | 00:00
| Dhamrai | 134 | 05:00 | 131 | 00:00 | Rajendrapur | 133 | 14:00 | 125 | 00:00
| Dhanmondi | 136 | 08:00 | 133 | 00:00 | Rajshahi | 137 | 06:00 | 131 | 12:00
| Dohazari | 134 | 06:00 | 130 | 18:30 | Rajshahi-230 | 137 | 04:00 | 128 | 08:00
| Faridpur | 133 | 09:00 | 130 | 00:00 | Ramganj | 132 | 18:30 | 123 | 00:00
| Fatullah | 137 | 08:00 | 133 | 00:00 | Rampur | 135 | 09:00 | 130 | 01:00
| Fenchuganj | 135 | 08:00 | 132 | 00:00 | Rampura | 135 | 04:00 | 131 | 11:00
| Feni | 130 | 05:00 | 127 | 00:00 | Rangamati | 135 | 08:00 | 130 | 00:00
| Ghorashal | 144 | 08:00 | 139 | 01:00 | Rangpur | 132 | 04:00 | 127 | 12:00
| Goalpara | 134 | 03:00 | 130 | 12:00 | Ruppur | 138 | 08:00 | 132 | 12:00
| Gollamari | 134 | 06:00 | 130 | 12:00 | Saidpur | 133 | 05:00 | 126 | 19:30
| Gopalganj | 132 | 03:00 | 128 | 12:00 | Satkhira | 132 | 03:00 | 125 | 18:00
| Gopalganj-400 | 132 | 04:00 | 129 | 00:00 | Satmasjid | 139 | 08:00 | 131 | 17:00
| Gulshan | 135 | 06:00 | 132 | 00:00 | Savar | 138 | 18:30 | 132 | 12:00
| Halishahar | 135 | 09:00 | 130 | 16:00 | SevenRings | 143 | 08:00 | 138 | 13:00
| Haripur | 135 | 05:00 | 132 | 00:00 | ShahCement | 136 | 08:00 | 133 | 00:00
| HaripurSBU | 135 | 05:00 | 132 | 00:00 | Shahjadpur | 142 | 03:00 | 139 | 12:00
| Hasnabad | 138 | 18:30 | 135 | 00:00 | Shahjibazar | 133 | 07:00 | 127 | 23:00
| Hathazari | 135 | 05:00 | 130 | 03:00 | Shahmirpur | 134 | 09:00 | 130 | 00:00
| Ishurdi | 139 | 07:00 | 134 | 12:00 | Shariatpur | 132 | 03:00 | 129 | 12:00
| Jaldhaka | 132 | 05:00 | 125 | 08:00 | Sherpur | 136 | 18:00 | 120 | 15:00
| Jamalpur | 139 | 18:00 | 123 | 07:00 | Shikalbaha | 124 | 08:00 | 120 | 16:00
| Jashore | 134 | 04:00 | 128 | 12:00 | Shikalbaha-230 | 136 | 09:00 | 132 | 00:00
| Jhenaidah | 139 | 02:00 | 132 | 12:00 | Shitalakhya | 136 | 09:00 | 132 | 00:00
| Jhenaidah-230 | 138 | 03:00 | 132 | 13:00 | Sholosohor | 135 | 08:00 | 130 | 00:00
| Joydebpur | 142 | 05:00 | 124 | 00:00 | Shyampur | 137 | 17:00 | 134 | 00:00
| Joypurhat | 135 | 05:00 | 129 | 12:00 | Shyampur-230 | 137 | 08:00 | 133 | 00:00
| Juldah | 135 | 08:00 | 130 | 00:00 | Siddhirganj | 135 | 02:00 | 132 | 00:00
| Kabirpur | 135 | 07:00 | 128 | 07:00 | Sirajganj | 138 | 02:00 | 133 | 12:00
| Kachua | 135 | 19:00 | 126 | 00:00 | Sonargaon | 135 | 17:00 | 128 | 08:00
| Kaliakoir | N/A | N/A | N/A | N/A | Sreemongol | 131 | 06:00 | 129 | 00:00
| Kallyanpur | 139 | 03:00 | 135 | 12:00 | Sreepur | 135 | 08:00 | 131 | 00:00
| Kalurghat | 134 | 09:00 | 130 | 00:00 | Srinagar | 137 | 08:00 | 133 | 00:00
| Kamrangirchar | 138 | 09:00 | 132 | 12:00 | SSM | 138 | 07:00 | 135 | 01:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 130 | 04:00 | 128 | 00:00
| Kazla | 137 | 09:00 | 134 | 00:00 | Sylhet | 132 | 07:00 | 130 | 00:00
| Keranigonj | 137 | 08:00 | 132 | 00:00 | Sylhet-132 | 131 | 08:00 | 130 | 00:00
| Khagrachori | 135 | 09:00 | 130 | 00:00 | Tangail | 133 | 18:30 | 127 | 01:00
| Khulna | 133 | 08:00 | 128 | 12:00 | Thakurgaon | 132 | 04:00 | 122 | 19:30
| Khulna(S) | 134 | 03:00 | 129 | 12:00 | TK | 135 | 08:00 | 123 | 02:00
| Khulshi | 133 | 09:00 | 129 | 00:00 | Tongi | 138 | 07:00 | 134 | 00:00
| Kishoreganj | 136 | 01:00 | 130 | 18:30 | Ullon | 134 | 08:00 | 130 | 12:00
| Kodda | 136 | 13:00 | 123 | 00:00 | Uttara | 138 | 09:00 | 132 | 12:00
| KSRM | 135 | 09:00 | 129 | 02:00 | UttaraNew | 137 | 08:00 | 132 | 12:00
| Kulaura | 132 | 00:00 | 131 | 12:00 | Zigatola | 136 | 09:00 | 132 | 00:00
| Kurigram | 131 | 05:00 | 125 | 21:00
| Kushtia | 136 | 04:00 | 131 | 12:00

## L-Curve
Date | 2023-11-24
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 868 | 4791 | 3171 | 7962 |  |  |  | QF-LDC-11
0:30 | 822 | 4805 | 3301.5 | 8106.5 | Date: | 2023-11-24
1:00 | 776 | 4819 | 3432 | 8251
1:30 | 778 | 4609 | 3443.5 | 8052.5
2:00 | 780 | 4399 | 3455 | 7854
2:30 | 770 | 4389.5 | 3363.5 | 7753 | [5 empty] | Gen. at Eve. Peak | 9061 | 9061 MW (18:00 )
3:00 | 760 | 4380 | 3272 | 7652 | [6 empty] | 18:00
3:30 | 753 | 4380.5 | 3164.5 | 7545 | [5 empty] | Gen. at Day Peak | 8215 | 8215 MW (12:00 )
4:00 | 746 | 4381 | 3057 | 7438 | [6 empty] | 12:00
4:30 | 723 | 4300.5 | 3057 | 7357.5 | [5 empty] | Highest Generation | 9061
5:00 | 700 | 4220 | 3057 | 7277 | [6 empty] | 18:00
5:30 | 660 | 4221.5 | 3125.5 | 7347
6:00 | 620 | 4223 | 3194 | 7417
6:30 | 590 | 4363.5 | 3063.5 | 7427
7:00 | 560 | 4504 | 2933 | 7437
7:30 | 538 | 4653.5 | 2967 | 7620.5
8:00 | 516 | 4803 | 3001 | 7804
8:30 | 678 | 4602.5 | 3047.5 | 7650
9:00 | 840 | 4402 | 3094 | 7496
9:30 | 926 | 4297.5 | 3120 | 7417.5
10:00 | 1012 | 4193 | 3146 | 7339
10:30 | 995 | 4232.5 | 3216 | 7448.5
11:00 | 978 | 4272 | 3286 | 7558
11:30 | 965 | 4504.5 | 3382 | 7886.5
12:00 | 952 | 4737 | 3478 | 8215
12:30 | 881 | 4944 | 3578 | 8522
13:00 | 810 | 5151 | 3678 | 8829
13:30 | 805 | 4928 | 3443.5 | 8371.5
14:00 | 800 | 4705 | 3209 | 7914
14:30 | 800 | 4480.5 | 3140 | 7620.5
15:00 | 800 | 4256 | 3071 | 7327
15:30 | 813 | 4239 | 3063.5 | 7302.5
16:00 | 826 | 4222 | 3056 | 7278
16:30 | 803 | 4387.5 | 3042.5 | 7430
17:00 | 780 | 4553 | 3029 | 7582
17:30 | 600 | 5030.5 | 3291 | 8321.5
18:00 | 420 | 5508 | 3553 | 9061
18:30 | 367 | 5585 | 3469 | 9054
19:00 | 314 | 5662 | 3385 | 9047
19:30 | 300 | 5692 | 3268 | 8960
20:00 | 340 | 5553 | 3428 | 8981 |  |  |  | Executive Engineer
20:30 | 440 | 5494 | 3398.5 | 8892.5 |  |  |  | Network Operation Division
21:00 | 540 | 5435 | 3369 | 8804
21:30 | 548 | 5372.5 | 3350.5 | 8723
22:00 | 556 | 5310 | 3332 | 8642 |  |  |  |  | Page 6 of 7
22:30 | 673 | 5220 | 3280 | 8500
23:00 | 790 | 5130 | 3228 | 8358
23:30 | 829 | 4960.5 | 3199.5 | 8160
24:00 | 868 | 4791 | 3171 | 7962
9061 MW (18:00 )
8215 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-11-24 |  | Energy |  | 194920259
QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3256 | 446 | 1471 | 0 | 59 | 2590 | 46 | 0 | 0 | 94 | 0 | 0 | 0
0:30 | 3194.5 | 681.5 | 1542.5 | 0 | 41 | 2479 | 69 | 0 | 0 | 99 | 0 | 0 | 0 |  | Date: | 43792
1:00 | 3133 | 917 | 1614 | 0 | 23 | 2368 | 92 | 0 | 0 | 104 | 0 | 0 | 0
1:30 | 3067.5 | 916.5 | 1534 | 0 | 11.5 | 2354 | 69 | 0 | 0 | 100 | 0 | 0 | 0 | [8 empty] | Total Energy | 194.9203 | 194.9203 | Total Energy Gen 194.920 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 194.920 MKWHr
2:00 | 3002 | 916 | 1454 | 0 | 0 | 2340 | 46 | 0 | 0 | 96 | 0 | 0 | 0 | [8 empty] | Energy not Served | 0 | 0
2:30 | 2995 | 821 | 1450 | 0 | 0 | 2344 | 46 | 0 | 0 | 97 | 0 | 0 | 0 | [8 empty] | Energy Requirement | 194.9203 | 194.9203
3:00 | 2988 | 726 | 1446 | 0 | 0 | 2348 | 46 | 0 | 0 | 98 | 0 | 0 | 0
3:30 | 2982.5 | 655.5 | 1416 | 0 | 0 | 2346 | 46 | 0 | 0 | 98 | 0 | 1 | 0 | [7 empty] | Shortage
4:00 | 2977 | 585 | 1386 | 0 | 0 | 2344 | 46 | 0 | 0 | 98 | 0 | 2 | 0
4:30 | 2951.5 | 585 | 1331 | 0 | 0 | 2344.5 | 46 | 0 | 0 | 97 | 0 | 2.5 | 0
5:00 | 2926 | 585 | 1276 | 0 | 0 | 2345 | 46 | 0 | 0 | 96 | 0 | 3 | 0
5:30 | 2921.5 | 635.5 | 1303.5 | 0 | 0 | 2343 | 46 | 0 | 0 | 93 | 0 | 4.5 | 0
6:00 | 2917 | 686 | 1331 | 0 | 0 | 2341 | 46 | 0 | 0 | 90 | 0 | 6 | 0
6:30 | 3051.5 | 529 | 1353 | 0 | 0 | 2343 | 46 | 0 | 0 | 86 | 12.5 | 6 | 0 | [6 empty] | Coal
7:00 | 3186 | 372 | 1375 | 0 | 0 | 2345 | 46 | 0 | 0 | 82 | 25 | 6 | 0
7:30 | 3189 | 349 | 1511.5 | 0 | 12 | 2354 | 46 | 0 | 0 | 80 | 74.5 | 4.5 | 0 | [5 empty] | Oil
8:00 | 3192 | 326 | 1648 | 0 | 24 | 2363 | 46 | 0 | 0 | 78 | 124 | 3 | 0
8:30 | 3048.5 | 386 | 1513.5 | 0 | 40.5 | 2358.5 | 46 | 0 | 0 | 79 | 176.5 | 1.5 | 0
9:00 | 2905 | 446 | 1379 | 0 | 57 | 2354 | 46 | 0 | 0 | 80 | 229 | 0 | 0
9:30 | 2888.5 | 446.5 | 1288 | 0 | 45 | 2356 | 46 | 0 | 0 | 76 | 271.5 | 0 | 0
10:00 | 2872 | 447 | 1197 | 0 | 33 | 2358 | 46 | 0 | 0 | 72 | 314 | 0 | 0
10:30 | 2863 | 447 | 1215.5 | 0 | 47 | 2401.5 | 46 | 0 | 8 | 76 | 344.5 | 0 | 0
11:00 | 2854 | 447 | 1234 | 0 | 61 | 2445 | 46 | 0 | 16 | 80 | 375 | 0 | 0
11:30 | 2961 | 447 | 1283.5 | 0 | 113.5 | 2560.5 | 46 | 0 | 16 | 84 | 375 | 0 | 0
12:00 | 3068 | 447 | 1333 | 0 | 166 | 2676 | 46 | 0 | 16 | 88 | 375 | 0 | 0
12:30 | 3166 | 447 | 1521 | 0 | 181.5 | 2691 | 46 | 0 | 16 | 93 | 360.5 | 0 | 0
13:00 | 3264 | 447 | 1709 | 0 | 197 | 2706 | 46 | 0 | 16 | 98 | 346 | 0 | 0
13:30 | 3264 | 447 | 1709 | 0 | 197 | 2706 | 46 | 0 | 16 | 98 | 346 | 0 | 0
14:00 | 3264 | 447 | 1709 | 0 | 197 | 2706 | 46 | 0 | 16 | 98 | 346 | 0 | 0
14:30 | 3032 | 447 | 1521.5 | 0 | 118.5 | 2535 | 46 | 0 | 8 | 91 | 278.5 | 0.5 | 0
15:00 | 2800 | 447 | 1334 | 0 | 40 | 2364 | 46 | 0 | 0 | 84 | 211 | 1 | 0
15:30 | 2843.5 | 447 | 1329.5 | 0 | 27 | 2376 | 46 | 0 | 0 | 86 | 145.5 | 2 | 0
16:00 | 2887 | 447 | 1325 | 0 | 14 | 2388 | 46 | 0 | 0 | 88 | 80 | 3 | 0
16:30 | 2931 | 447 | 1374 | 0 | 74 | 2422.5 | 46 | 0 | 0 | 92 | 41.5 | 2 | 0
17:00 | 2975 | 447 | 1423 | 0 | 134 | 2457 | 46 | 0 | 0 | 96 | 3 | 1 | 0
17:30 | 3134 | 328 | 1593.5 | 0 | 341.5 | 2774.5 | 46 | 0 | 0 | 102 | 1.5 | 0.5 | 0
18:00 | 3293 | 209 | 1764 | 0 | 549 | 3092 | 46 | 0 | 0 | 108 | 0 | 0 | 0
18:30 | 3306.5 | 209 | 1730.5 | 0 | 631 | 3025 | 46 | 0 | 0 | 106 | 0 | 0 | 0
19:00 | 3320 | 209 | 1697 | 0 | 713 | 2958 | 46 | 0 | 0 | 104 | 0 | 0 | 0
19:30 | 3341 | 209 | 1777 | 0 | 539 | 2947 | 46 | 0 | 0 | 100 | 0 | 1 | 0
20:00 | 3318 | 405 | 1787 | 0 | 462 | 2855 | 46 | 0 | 0 | 108 | 0 | 0 | 0
20:30 | 3334.5 | 426 | 1762.5 | 0 | 405 | 2811.5 | 46 | 0 | 0 | 107 | 0 | 0 | 0
21:00 | 3351 | 447 | 1738 | 0 | 348 | 2768 | 46 | 0 | 0 | 106 | 0 | 0 | 0
21:30 | 3340 | 462 | 1686 | 0 | 313 | 2768 | 46 | 0 | 0 | 108 | 0 | 0 | 0
22:00 | 3329 | 477 | 1634 | 0 | 278 | 2768 | 46 | 0 | 0 | 110 | 0 | 0 | 0
22:30 | 3303 | 462 | 1612.5 | 0 | 199.5 | 2725 | 46 | 0 | 0 | 152 | 0 | 0 | 0
23:00 | 3277 | 447 | 1591 | 0 | 121 | 2682 | 46 | 0 | 0 | 194 | 0 | 0 | 0
23:30 | 3266.5 | 446.5 | 1531 | 0 | 90 | 2636 | 46 | 0 | 0 | 144 | 0 | 0 | 0 |  | Max Temp. in Dhaka |  | 29.2°C
24:00 | 3256 | 446 | 1471 | 0 | 59 | 2590 | 46 | 0 | 0 | 94 | 0 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 194.920 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 194.920 MKWHr
Note on W13: Author:

## Generation
g | 2023-11-24
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 92 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1138440
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 4 | 10 | 15 | 18 | 19 | 20 | 15 | 15 | 11 | 5 | 0 | [9 empty] | 134055
6 | Sikalbaha 225MW CCPP (Gas) | 202 | 200 | 202 | 201 | 201 | 201 | 201 | 201 | 201 | 212 | 210 | 215 | 213 | 213 | 212 | 213 | 210 | 210 |  | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 4882036
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [25 empty] | 0 | 0
12 | Hathazari 100 MW peaking PP | [26 empty] | 0
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [16 empty] | 2 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 122109
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 280 | 230 | 230 | 230 | 230 | 250 | 250 | 250 | 230 | 230 | 230 | 230 | 335 | 240 | 240 | 240 | 270 | 335 |  | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 6675439
18 | Kodda 300 MW PP Unit-2 (Summit) | [25 empty] | 0 | 0
19 | Ashuganj 195 MW PP (APSCL-United) | 102 | 45 | 45 | 45 | 45 | 45 | 45 | 102 | 55 | 55 | 55 | 55 | 102 | 102 | 102 | 55 | 55 | 158 |  | 158 | 158 | 158 | 102 | 102 | 102 | 55 | 1990545
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4394250
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 368 | 345 | 345 | 345 | 345 | 345 | 345 | 345 | 332 | 325 | 325 | 358 | 403 | 354 | 320 | 325 | 340 | 480 |  | 480 | 480 | 470 | 450 | 453 | 440 | 400 | 9016362
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 51 | 5 | 5 | 5 | 5 | 5 | 51 | 51 | 51 | 47 | 47 | 47 | 47 | 46 | 46 | 47 | 47 | 48 |  | 47 | 46 | 47 | 47 | 47 | 47 | 46 | 917064
33 | Ashuganj 225 MW CCPP
34 | Ashuganj 450 MW CCPP(South) | [25 empty] | 0 | 0
| Ashuganj 450 MW CCPP(North) | 280 | 295 | 290 | 280 | 280 | 280 | 370 | 280 | 280 | 280 | 275 | 280 | 280 | 280 | 280 | 315 | 310 | 305 |  | 305 | 335 | 305 | 315 | 305 | 285 | 280 | 7473600
| Ashuganj 420 MW CCPP(East) | 350 | 300 | 300 | 300 | 280 | 280 | 340 | 395 | 250 | 250 | 250 | 350 | 393 | 280 | 230 | 260 | 300 | 395 |  | 395 | 395 | 395 | 393 | 395 | 350 | 350 | 7901100
35 | Ashuganj 55 MW PP (Precision) | 39 | 36 | 38 | 38 | 36 | 38 | 40 | 40 | 39 | 30 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 14 | 30 | 29 | 32 | 31 | 31 | 31 | 617760
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 372 | 372 | 372 | 372 | 339 | 333 | 338 | 389 | 352 | 334 | 335 | 335 | 407 | 354 | 331 | 339 | 358 | 400 |  | 408 | 413 | 414 | 414 | 409 | 406 | 393 | 8988670
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 170 | 170 | 170 | 225 | 225 | 180 | 180 | 180 | 225 | 225 | 170 | 170 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4851600
41 | Haripur 360 MW CCPP(HPL) | 307 | 307 | 307 | 307 | 282 | 282 | 280 | 337 | 263 | 227 | 227 | 260 | 330 | 280 | 240 | 246 | 337 | 337 |  | 306 | 319 | 331 | 311 | 306 | 307 | 307 | 7008000
42 | RPCL 210MW CCPP | 103 | 103 | 104 | 104 | 104 | 105 | 104 | 86 | 72 | 72 | 75 | 75 | 74 | 73 | 75 | 72 | 84 | 85 |  | 85 | 88 | 97 | 97 | 98 | 103 | 103 | 2095680
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 3 | 18 | 31 | 43 | 49 | 52 | 50 | 41 | 29 | 10 | 0 | [9 empty] | 292380
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1016000
45 | Fenchugonj CCPP Phase-2 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 26 | 26 | 26 | 26 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 704400
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86 MW PP (Shahjibazar) | 40 | 40 | 40 | 40 | 10 | 10 | 10 | 40 | 10 | 10 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 38 | 38 | 5 | 5 | 800640
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 200 | 200 | 200 | 201 | 201 | 201 | 201 | 202 | 201 | 198 | 197 | 196 | 196 | 196 | 196 | 196 | 196 | 195 |  | 198 | 198 | 198 | 198 | 199 | 200 | 202 | 4019250
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 18 | 18 | 18 | 18 | 18 | 17 | 413000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 253620
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 2 | 2 | 2 | [5 empty] | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 85752
55 | Fenchugonj 51 MW PP (Barakatullah) | [25 empty] | 0 | 0
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 16 | 16 | 16 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 357168
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 295 | 275 | 285 | 290 | 300 | 295 | 285 | 260 | 260 | 290 | 300 | 285 | 265 | 280 | 300 | 290 | 300 |  | 280 | 335 | 285 | 310 | 275 | 265 | 280 | 6981500
| Bibiyana South 400 MW | 370 | 370 | 370 | 370 | 370 | 380 | 380 | 390 | 370 | 370 | 370 | 390 | 370 | 350 | 350 | 350 | 350 | 395 |  | 400 | 391 | 390 | 400 | 390 | 400 | 400 | 9053600
58 | Nababganj 55 MW PP (Southern power ) | [17 empty] | 5 |  | 17 | 17 |  |  |  |  | 0 | 29831
59 | Tangail Palli Power Gen 22 MW | [25 empty] | 0 | 0
60 | Barabkunda 22 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 288624
61 | Narshingdi 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 9 | 9 | 9 | 9 |  | 9 |  |  | 12 | 12 | 12 | 13 | 297144
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 104 | 96 | 98 | 98 | 96 | 90 | 82 | 78 | 80 | 72 | 80 | 88 | 98 | 98 | 84 | 88 | 96 | 108 |  | 104 | 100 | 108 | 106 | 110 | 194 | 94 | 2215680
64 | Malancha, Ctg. EPZ (United) | 10 | 18 | 29 | 29 | 27 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 15 | 18 | 30 |  | 30 | 30 | 30 | 30 | 31 | 31 | 32 | 626880
65 | Feni 22 MW PP (Doreen) | 15 | 15 | 15 | 15 | 15 |  | 9 | 13 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 343372
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 233280
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 785800
68 | Cumilla 25 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 6 | 6 | 6 | 6 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 194390
69 | Summit Ashulia | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 480000
70 | Summit Madhabdi | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 0 | 11 | 11 | 7 | 7 | 7 | 7 | 7 | 7 |  | 17 | 17 | 17 | 18 | 18 | 18 | 18 | 254160
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 17 | 17 | 17 | 17 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 590200
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 32 | 12 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 783900
73 | Ghorashal 108 MW PP (Regent) | 74 | 12 | 12 | 12 | 12 | 12 | 12 | 60 | 60 | 22 | 22 | 65 | 75 | 72 | 72 | 39 | 39 | 39 |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 960772
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | [10 empty] | 12 | 37 | 36 | 39 | 9 |  | 3 | 32 |  | 36 | 36 | 36 | 26 | 9 |  | 0 | 362880
| Manikgonj 162MW PP(MPGL) | [17 empty] | 17 |  | 17 | [5 empty] | 0 | 31680
77 | Siddhirganj 100 PP(Dutch Bangla) | [25 empty] | 0 | 0
78 | Gazipur 52 MW PP | [12 empty] | 8 | 8 |  |  |  | 8 |  | 8 | 8 |  |  |  |  | 0 | 42240
79 | Kodda 150 MW PP | [10 empty] | 16 | 16 | 16 | 16 | [11 empty] | 0 | 57120
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [19 empty] | 35 | 35 | 17 | 17 | 17 |  | 0 | 83520
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 4 | 4 | 5 | 2 | 3 | 2 | 1 | [10 empty] | 22801
| Jodiac Power | [17 empty] | 8 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 95795
| Karnaphuli Power Ltd. | [10 empty] | 4 | 17 | 17 | 17 |  |  | 3 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 198218
82 | Madanganj 102 PP(Summit) | [25 empty] | 0 | 0
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [19 empty] | 11 | [5 empty] | 0 | 14400
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [16 empty] | 8 | 12 |  | 12 | 12 | 12 | 12 | 12 |  | 0 | 59400
92 | Fenchuganj 44 MW (Energyprima) | 44 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 44 | 10 | 10 | 18 | 37 | 37 | 10 | 10 | 10 | 41 |  | 47 | 44 | 47 | 47 | 47 | 47 | 5 | 614880
93 | Ashuganj 51 MW PP (Midland) | 51 | 5 | 5 | 5 | 5 | 5 | 24 | 51 | 10 | 10 | 10 | 10 | 25 | 51 | 10 | 10 | 18 | 34 |  | 51 | 51 | 51 | 51 | 51 | 51 | 5 | 792256
94 | Gagnagar 102 MW PP (Digital Power) | [25 empty] | 0 | 0
95 | Patenga 50MW PP (Baraka) | [10 empty] | 3 | 6 | 6 | 6 |  |  | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 5 | 68160
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 | [14 empty] | 0 | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [25 empty] | 0 | 0
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 17 |  | 17 | 17 |  |  |  |  | 0 | 34951
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 12350
103 | Kamalaghat 54 MW PP(Banco Energy) | [16 empty] | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 104400
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [7 empty] | 7 | 24 | 8 | 8 | 29 | 45 | 8 | 8 | 8 | 15 | 93 |  | 93 | 72 | 55 | 55 | 35 | 16 | 0 | 619200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 23 | [6 empty] | 1 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 3 | 20 |  | 35 | 35 | 35 | 20 | 17 |  | 0 | 302976
115 | Juldah 100 MW PP Unit-3 (Acorn) | [16 empty] | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 0 | 90240
116 | Chandpur 200 MW (Desh energy) | [11 empty] | 14 | 19 | 19 |  |  | 4 | 17 |  | 17 | 17 | 17 | 17 | 17 | 19 | 20 | 202560
117 | Ashuganj 150 MW PP (Midland) | [25 empty] | 0 | 0
118 | Bibiyana-III 400 MW CCPP | 363 | 365 | 353 | 352 | 354 | 354 | 401 | 354 | 353 | 338 | 329 | 400 | 354 | 354 | 323 | 338 | 333 | 401 |  | 402 | 403 | 400 | 402 | 401 | 401 | 401 | 8879000
| Jamalpur 115 MW PP (United) | [7 empty] | 16 | 16 | 8 | 8 | 8 | 8 | 8 |  |  | 4 | 47 |  | 47 | 16 | 16 | 16 | 19 |  | 0 | 223200
| Anwara 300 MW PP (United) | [16 empty] | 15 | 15 |  | 65 | 65 | 65 | 30 | 15 |  | 0 | 193200
| Juldah unit-2 (Acorn) | [25 empty] | 0 | 0
| Anlima Energy Ltd. | [10 empty] | 2 | 17 | 17 | 17 |  |  | 7 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 199473
| Bhairob 54.5 MW | [19 empty] | 6 | 17 | 17 | 17 | 17 | 17 | 17 | 99360
| Spectra Solar Plant Ltd. | [6 empty] | 2 | 11 | 18 | 25 | 25 | 32 | 28 | 23 | 15 | 5 | 0 | [9 empty] | 182303
| Chandpur 115(Doreen) | [10 empty] | 7 | 18 | 18 | 18 |  |  | 5 | 41 |  | 54 | 54 | 54 | 35 | 17 |  | 0 | 325440
| Kanchan Purbachal Power Generation Ltd. | [25 empty] | 0 | 0
Mirsharai 150 MW (Oil)
| Mirsharai 150 MW (Gas) | [25 empty] | 0 | 0
| Cox's Bazar Wind | 0 | 0 | 0 | 2 | 3 | 6 | 6 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 1 | 0 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 24000
Matarbari 2*600 MW (CPGCL)
120 | Eastern Zone Total | 4819 | 4399 | 4380 | 4381 | 4220 | 4223 | 4504 | 4803 | 4402 | 4193 | 4272 | 4737 | 5151 | 4705 | 4256 | 4222 | 4553 | 5508 |  | 5662 | 5692 | 5553 | 5435 | 5310 | 5130 | 4791 | 114204056
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
Khulna 115 PP MW (KPCL-2)
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [25 empty] | 0 | 0
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 5 | 21 | 48 | 57 | 67 | 66 | 72 | 54 | 37 | 15 | 1 | [9 empty] | 441360
131 | Rampal 1320 MW (BIFPCL) | 357 | 357 | 361 | 359 | 353 | 353 | 353 | 353 | 353 | 354 | 354 | 351 | 354 | 355 | 354 | 354 | 353 | 502 |  | 404 | 413 | 403 | 404 | 404 | 356 | 347 | 8909091
132 | United Payra Power Ltd. | [17 empty] | 12 |  | 35 | [5 empty] | 0 | 58800
133 | Bhola Nutan Biddut BD LTD (GAS) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 109 | 109 | 109 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2623882
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [25 empty] | 0 | 0
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 230 |  | 180 | 180 | 180 | 150 | 150 | 150 | 150 | 3774500
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 120 | 80 | 80 | 80 | 80 | 122 | 30 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1659000
140 | Bhola 33 MW PP (Venture) | 17 | 16 | 15 | 15 | 14 | 14 | 14 | 13 | 13 | 13 | 12 | 15 | 16 | 16 | 11 | 11 | 12 | 16 |  | 17 | 16 | 18 | 19 | 19 | 18 | 17 | 356300
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 917 | 916 | 726 | 585 | 585 | 686 | 372 | 326 | 446 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 209 |  | 209 | 209 | 405 | 447 | 477 | 447 | 446 | 11827636
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 520 | 520 | 530 | 620 | 820 | 800 | 560 | 540 | 560 | 620 | 890 |  | 900 | 880 | 800 | 770 | 770 | 740 | 700 | 17313100
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4136400
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 4 | 4 | 2 | 0 | 0 | [9 empty] | 32280
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 300 | 330 | 330 | 260 | 260 | 300 | 330 | 320 | 250 | 230 | 230 | 230 | 414 | 320 | 240 | 300 | 250 | 414 |  | 370 | 370 | 414 | 414 | 350 | 350 | 350 | 7863490
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 238410
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [17 empty] | 12 |  | 35 | [5 empty] | 0 | 69696
172 | Confidence Power Bogura Unit-1 113 MW | [17 empty] | 20 |  | 35 | [5 empty] | 0 | 55776
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [11 empty] | 3 | 6 | 6 | 6 | 6 | 30 | 70 |  | 35 | 35 | 35 |  |  |  | 0 | 186816
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 3 | 5 | 5 | 5 | 4 | 3 | 2 | 0 | [9 empty] | 34309
178 | Energypac Power Venture Thakurgaon Ltd. | [17 empty] | 17 | [7 empty] | 0 | 46656
| Intraco Solar 30 MW | [6 empty] | 1 | 8 | 9 | 15 | 34 | 27 | 15 | 5 | 16 | 7 | 0 | [9 empty] | 146247
| Adani Power Jharkhanda Ltd | 823 | 818 | 822 | 820 | 827 | 823 | 827 | 825 | 829 | 829 | 826 | 827 | 829 | 826 | 830 | 829 | 824 | 820 |  | 824 | 824 | 832 | 824 | 821 | 826 | 823 | 19876364
178 | Teesta Solar Limited | [6 empty] | 10 | 52 | 100 | 143 | 165 | 161 | 153 | 141 | 95 | 35 | 2 | [9 empty] | 1066090