## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-11-26 | Sunday
|  | Date (day): | 2023-11-26 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11429.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13406 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-11-25 | 2023-11-26 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 39 | 70 | 77 | 77 | 31 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 363 | 392 | 412 | 412
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 291 | 341 | 330 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 170 | 225 | 225 | 225 | 225 |  | GT-1 under S/D due to Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 13 | 92 | 100 |  |  | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 10 | 85 | 85 |  | 17 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 15 | 30 | 25 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 30 | 40 | 35 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 12 | 0 | 18 | 18 |  | 4 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 15 | 92 | 92 |  | 8 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 335 | 335 | 335 | 0
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 0 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 32 | 16 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 0 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 0 | 35 | 20 |  | Fuel shortage
| Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
25 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 31 | 32 | 38 | 38 |  | 42 | Engine problem
26 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
27 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
28 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 20 | 8 | 25 | 27 |  | Fuel shortage
29 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
30 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 40 | 80 | 130 | 170 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
31 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 0 | 18 | 100 | 49 |  | Fuel shortage
32 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 88 | 30 | 105
33 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 68 | 26 | 88 | 16 |  | Fuel shortage
34 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 72 | 17 | 35 | 127 |  | Fuel shortage
35 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 0 | 0 | 35 | 0
36 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 34 | 17 | 35 | 20 |  | Fuel shortage
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 5763 | 5422 | 1408 | 2127 | 2342 | 2900 | 1515 | 1011
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
38 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 11 | 8 | 17 | 8 |  | Fuel shortage
39 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 6 | 10 | 40 |  | Fuel shortage
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 46 | 46 | 184 |  | Low water lavel
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 214 | 212 | 212
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 17 | 17 | 88 |  | Fuel shortage
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 40 | 64 | 34 |  | Fuel shortage
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 | 102 |  | Fuel shortage
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 12 | 12 | 12 | 88 |  | Fuel shortage
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 12 | 12 | 88 |  | Fuel shortage
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 12 | 12 | 12 | 12 | 10 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 0 | 10 | 25
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 80 | 260 | 260 | 40 |  | Fuel shortage+Engine problem
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 17 | 17 | 17 | 37 |  | Fuel shortage
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 10 | 17 | 17 | 17 | 93 |  | Fuel shortage
55 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 12 | 12 | 88 |  | Fuel shortage
56 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 12 | 17 | 17 | 17 | 99 |  | Fuel shortage
57 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 18 | 17 | 0 | 0 | 163 |  | Fuel shortage
58 | SS Power I |  | Coal | SS Power | 1*612 | 612 | 612 | 400 | 500 | 400 | 500
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 1 | 4 | 10 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 300 |  |  | On test.
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 163 | 163 | 18 | 17 | 0 | 0
| Chattogram area Total |  |  |  |  | 3380 | 3320 | 757 | 1012 | 1133 | 1560 | 1450 | 330
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 0 | 0 |  | 221 | Under maint.
60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 280 | 320 | 320 | 40 |  | Gas shortage
61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
62 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 300 | 395 | 395 | 395 | 5
63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 47 | 46 | 51 | 51
| Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 0 | 41 | 42 | 40 | 40 |  |  | Contract Expired
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 102 | 55 | 102 | 93 |  | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 5 | 51 | 51 | 51
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 36 | 150 | 150
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 10 | 17 | 17 | 17 | 183 |  | Fuel shortage
70 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 7 | 16 | 18 | 18 |  | 4 | Engine problem
71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 116 | 104 | 128 | 140
72 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 31 | 52 | 52
74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 6 | 8 | 10 | 10 |  | 15 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 42 | 114 | 114
76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 46 | 28 | 65 | 48 |  | Fuel shortage
77 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
78 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 60 | 36 | 72 | 43 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2896 | 954 | 1337 | 1526 | 1658 | 412 | 800
79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 84 | 94 | 80 | 90 | 112 |  | Gas shortage
80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Contract Expired
| Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 16 | 112 | 84 | 104 | 96 |  | Fuel shortage
83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 8 | 56 | 56 | 85 | 30 |  | Fuel shortage
84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 47 | 0 | 50 | 0
85 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 157 | 268 | 277.6 | 285 | 112 | 22
86 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
87 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 26 | 26 | 28 | 28 |  | 62 | Engine problem
88 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
89 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
90 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
91 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 35 | 44 | 44
92 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 0 | 5 | 5 |  | 6 | Engine problem
93 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 |  | 66 | GT-8 Under maint.
94 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 40 | 40 | 40 | 46 |  | Gas shortage
95 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 196 | 197 | 200 | 200 |  | 31 | Machine problem
97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 16 | 17 | 17 | 17
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 16 | 16 | 16 | 9 |  | Gas shortage
99 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 305 | 310 | 310 |  |  | FGMO
100 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 402 | 402 | 400 | 400
101 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
102 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 390 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1461 | 1491 | 1513 | 1513 | 269 | 622
103 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 447 | 354 | 453 | 453
104 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 16 | 32 | 48 | 67 |  | Fuel shortage
105 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 50
106 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
107 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 70 | 39 |  | Fuel shortage
108 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
109 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 16 | 24 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
110 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105
111 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 15 | 32 | 73 |  | Fuel shortage
112 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 74 | 0 | 100 | 0
113 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0
114 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 352 | 604 | 450 | 550
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 873 | 991 | 1155 | 1324 | 859 | 0
115 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 16 | 110
116 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 14 | 18 | 21 | 25 |  | 15 | Engine problem
117 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 50 | 50 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 600 | 1190 | 1000 | 1220
119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 110 | 110 | 110 | 110 |  | 110 | GT-1 Under maint.
120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 45 | 0 | 150
121 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 140 | 200 | 150 | 200 | 107 |  | Coal shortage
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 914 | 1613 | 1427 | 1945 | 107 | 189
122 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
123 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 35 | 17 |  | Fuel shortage
124 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 20 |  | 51 | Engine problem
125 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 28 | 28
126 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 34 | 42 |  | 8 | Engine problem
127 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 40 |  | 10 | Engine problem
128 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
129 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
130 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
131 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 300 | 414 | 414 | 414
132 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 38 | 12 |  | Fuel shortage
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
133 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
134 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
135 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 40 | 85 |  | 19 | Engine problem
136 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
137 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 69 | 35 | 50 | 63 |  | Fuel shortage
138 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 100 | 35 | 113
139 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 822 | 819 | 850 | 900
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 1135 | 1410 | 1535 | 1828 | 1113 | 88
140 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
141 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
142 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
143 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
144 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 113 | 111 | 113 | 113
145 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
146 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 70 | 70 | 110
147 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 30 | 0
148 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 177 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 499 | 351 | 521 | 393 | 125 | 189
| Total |  |  |  |  | 25502 | 24762 | 8158 | 10600 | 11429.6 | 13406 | 5962 | 3251
A. |  | 2023-11-25 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 10583 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 6700 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10583 | MW
3 | Day peak Generation : |  |  | 8140 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10153.75 | MW
4 | Evening peak Generation : |  |  | 10583 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 202.6999 | MKWHr | By Solar | 2.3302 | MKWHr
| By Gas : | 109.4927 | MKWHr |  | By Oil: | 10.9787 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 66.1937 | MKWHr |  | By Hydro: | 1.115 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.13824 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5962 | MW | Dhaka | 3890.35 | 3890.35 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3251 | MW | Chittagong | 1072.8 | 1072.8 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 9213 | MW | Khulna | 1141.6 | 1141.6 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 814.34 | MMCFD |  |  | Rajshahi | 948 | 948 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 109498154.418 | ii) Oil : | Taka | 142127086.8 | Comilla | 887 | 887 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 501307483.42 | Total | Taka | 752932724.638 | Mymensingh | 812 | 812 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.0165 | MKWHr. | Sylhet | 413 | 413 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 330 | MW (W to E) at | 18:00 | hrs | Barisal | 282 | 282 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 216 | MW at | 22:00 | hrs | Rangpur | 707 | 707 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.1°C |  |  | Total | 10153.75 | 10153.75 |  | 0
B. |  | 2023-11-26 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 30.1°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13406 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9200 | MW
4 | Reserve(Generation end) |  |  |  | 2406 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 210.6868 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7092 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 10.0916 | MKWHr. | ii) HVDC Flow at Peak Time |  | 354 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.3597 | MKWHr. | iii) Maximum HVDC Flow : |  | 447 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 98.58 |  | (b) Today: | 98.5 |  | (c) Rule Curve: |  | 106.5
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-11-25 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 352 | 307 |  | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 18 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 32 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 10 | 16 | 0 | 5 | 0 | 0 | 0 | 16 | 11 | 33 | 8 | 94 | 104 | 0 | 0 | 0 | 43 | 28 | 0 | 5 | 0 | 0 | 0 | 5 | 0 | 202 | 18 | 0 | 10 | 275 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 350 | 0 | 0 | 375 | 3 | 0 | 0 | 0 |  | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 150 | 823 | 0 | 0 |  | 4445 | 3176 | 7621 | 3088 | 447 | 1356 | 0 | 17 | 2570 | 46 | 0 | 0 | 94 | 0 | 3 | 0 | 98.59
2:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 352 | 268 |  | 0 | 170 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 18 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 32 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 5 | 0 | 0 | 0 | 16 | 11 | 33 | 8 | 84 | 105 | 0 | 0 | 0 | 43 | 28 | 0 | 5 | 0 | 0 | 0 | 5 | 0 | 202 | 18 | 0 | 10 | 270 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 350 | 0 | 0 | 300 | 4 | 0 | 0 | 0 |  | 446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 150 | 817 | 0 | 0 |  | 4178 | 2968 | 7146 | 3010 | 446 | 1250 | 0 | 17 | 2289 | 46 | 0 | 0 | 84 | 0 | 4 | 0 | 98.59
3:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 340 | 267 |  | 0 | 170 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 18 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 32 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 5 | 0 | 0 | 0 | 16 | 11 | 33 | 8 | 78 | 105 | 0 | 0 | 0 | 43 | 28 | 0 | 5 | 0 | 0 | 0 | 5 | 0 | 202 | 18 | 0 | 10 | 275 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 285 | 0 | 0 | 295 | 6 | 0 | 0 | 0 |  | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 140 | 820 | 0 | 0 |  | 4042 | 2959 | 7001 | 2879 | 447 | 1253 | 0 | 17 | 2275 | 46 | 0 | 0 | 78 | 0 | 6 | 0 | 98.59
4:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 304 | 246 |  | 0 | 170 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 18 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 32 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 5 | 0 | 0 | 0 | 16 | 11 | 33 | 8 | 84 | 72 | 0 | 0 | 0 | 43 | 28 | 0 | 5 | 0 | 0 | 0 | 5 | 0 | 203 | 18 | 0 | 10 | 285 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 240 | 0 | 0 | 285 | 12 | 0 | 0 | 0 |  | 446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 140 | 827 | 0 | 0 |  | 3920 | 2918 | 6838 | 2766 | 446 | 1192 | 0 | 17 | 2275 | 46 | 0 | 0 | 84 | 0 | 12 | 0 | 98.58
5:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 304 | 247 |  | 0 | 170 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 18 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 32 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 5 | 0 | 0 | 0 | 16 | 11 | 8 | 8 | 90 | 72 | 0 | 0 | 0 | 43 | 28 | 0 | 5 | 0 | 0 | 0 | 5 | 0 | 203 | 18 | 0 | 10 | 270 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 240 | 0 | 0 | 285 | 12 | 0 | 0 | 0 |  | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 140 | 823 | 0 | 0 |  | 3834 | 2866 | 6700 | 2688 | 447 | 1128 | 0 | 17 | 2272 | 46 | 0 | 0 | 90 | 0 | 12 | 0 | 98.58
6:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 328 | 278 |  | 0 | 170 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 18 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 31 | 0 | 0 | 0 | 280 | 0 | 0 | 8 | 0 | 10 | 10 | 0 | 5 | 0 | 0 | 0 | 16 | 11 | 8 | 8 | 84 | 73 | 0 | 0 | 0 | 43 | 28 | 0 | 5 | 0 | 0 | 0 | 5 | 0 | 203 | 18 | 0 | 10 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 300 | 0 | 0 | 285 | 16 | 0 | 0 | 0 |  | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 500 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 140 | 820 | 0 | 0 |  | 4015 | 2952 | 6967 | 2813 | 447 | 1256 | 0 | 37 | 2268 | 46 | 0 | 0 | 84 | 0 | 16 | 0 | 98.58
7:00 | 0 | 0 | 0 | 180 | 0 | 10 | 0 | 349 | 309 |  | 0 | 225 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 18 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 29 | 0 | 0 | 0 | 310 | 0 | 0 | 8 | 0 | 37 | 10 | 0 | 5 | 0 | 0 | 0 | 16 | 11 | 17 | 8 | 82 | 104 | 0 | 0 | 0 | 43 | 28 | 0 | 5 | 0 | 0 | 0 | 5 | 0 | 203 | 17 | 0 | 10 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 4 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 3 | 0 | 0 | 0 | 17 | 2 | 0 | 0 | 340 | 0 | 0 | 303 | 18 | 0 | 0 | 0 |  | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | 520 | 110 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 353 | 2 | 140 | 821 | 9 | 0 |  | 4518 | 3106 | 7624 | 3180 | 447 | 1389 | 0 | 130 | 2307 | 46 | 0 | 0 | 82 | 25 | 18 | 0 | 98.57
8:00 | 0 | 0 | 0 | 180 | 0 | 26 | 0 | 372 | 308 |  | 0 | 225 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 18 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 10 | 0 | 0 | 0 | 310 | 0 | 0 | 8 | 0 | 47 | 10 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 33 | 8 | 92 | 104 | 0 | 0 | 1 | 43 | 28 | 0 | 31 | 0 | 0 | 0 | 37 | 0 | 203 | 17 | 0 | 10 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 9 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 385 | 0 | 0 | 368 | 11 | 0 | 0 | 0 |  | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 113 | 0 | 1 | 0 | 620 | 110 | 0 | 0 | 1 | 26 | 0 | 0 | 0 | 352 | 11 | 140 | 821 | 56 | 0 |  | 4745 | 3243 | 7988 | 3247 | 400 | 1444 | 0 | 154 | 2471 | 46 | 0 | 0 | 92 | 123 | 11 | 0 | 98.57
9:00 | 0 | 0 | 0 | 180 | 0 | 39 | 0 | 352 | 231 |  | 0 | 170 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 0 | 0 | 285 | 0 | 0 | 8 | 0 | 47 | 11 | 0 | 5 | 0 | 0 | 0 | 0 | 8 | 33 | 8 | 96 | 86 | 0 | 0 | 1 | 43 | 28 | 0 | 10 | 0 | 0 | 0 | 37 | 0 | 199 | 17 | 0 | 10 | 270 | 16 | 5 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 15 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 33 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 250 | 0 | 0 | 351 | 8 | 0 | 0 | 0 |  | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 113 | 0 | 3 | 0 | 560 | 110 | 0 | 0 | 3 | 54 | 0 | 0 | 0 | 352 | 18 | 140 | 821 | 107 | 0 |  | 4246 | 3143 | 7389 | 2903 | 375 | 1171 | 0 | 161 | 2394 | 46 | 0 | 0 | 96 | 235 | 8 | 0 | 98.57
10:00 | 0 | 0 | 0 | 180 | 0 | 39 | 0 | 333 | 230 |  | 0 | 170 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 0 | 0 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 8 | 0 | 47 | 36 | 0 | 5 | 0 | 0 | 0 | 0 | 8 | 33 | 6 | 104 | 85 | 0 | 0 | 2 | 43 | 28 | 0 | 10 | 0 | 0 | 0 | 37 | 0 | 199 | 17 | 0 | 10 | 280 | 16 | 2 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 18 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 43 | 0 | 0 | 0 | 17 | 0 | 0 | 23 | 250 | 3 | 0 | 326 | 8 | 0 | 0 | 0 |  | 389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 113 | 0 | 4 | 0 | 550 | 110 | 0 | 0 | 4 | 63 | 0 | 0 | 0 | 351 | 28 | 140 | 828 | 142 | 0 |  | 4230 | 3203 | 7433 | 2845 | 389 | 1196 | 0 | 169 | 2365 | 46 | 0 | 3 | 104 | 308 | 8 | 0 | 98.56
11:00 | 0 | 0 | 0 | 180 | 0 | 39 | 0 | 311 | 231 |  | 0 | 170 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 20 | 0 | 25 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 8 | 0 | 47 | 41 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 33 | 6 | 110 | 85 | 0 | 0 | 2 | 43 | 26 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 200 | 17 | 0 | 10 | 310 | 16 | 2 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 20 | 0 | 0 | 0 | 397 | 0 | 17 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 49 | 0 | 0 | 0 | 17 | 0 | 0 | 35 | 250 | 0 | 8 | 328 | 3 | 0 | 0 | 0 |  | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 113 | 0 | 5 | 0 | 560 | 110 | 0 | 0 | 5 | 74 | 0 | 0 | 0 | 351 | 33 | 140 | 828 | 169 | 0 |  | 4411 | 3446 | 7857 | 3010 | 447 | 1305 | 0 | 198 | 2377 | 46 | 0 | 0 | 110 | 361 | 3 | 0 | 98.56
12:00 | 0 | 0 | 0 | 180 | 0 | 39 | 0 | 363 | 291 |  | 0 | 170 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 20 | 11 | 0 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 8 | 0 | 47 | 41 | 0 | 5 | 0 | 0 | 0 | 7 | 11 | 33 | 6 | 116 | 84 | 0 | 0 | 2 | 43 | 26 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 196 | 16 | 0 | 10 | 290 | 8 | 2 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 20 | 0 | 10 | 0 | 402 | 8 | 17 | 0 | 4 | 0 | 0 | 10 | 0 | 8 | 0 | 390 | 0 | 47 | 0 | 12 | 0 | 17 | 0 | 0 | 0 | 300 | 0 | 18 | 400 | 1 | 0 | 0 | 0 |  | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 113 | 0 | 5 | 0 | 600 | 110 | 0 | 0 | 5 | 74 | 0 | 0 | 0 | 352 | 34 | 140 | 822 | 177 | 0 |  | 4719 | 3421 | 8140 | 3111 | 447 | 1356 | 0 | 211 | 2484 | 46 | 0 | 0 | 116 | 368 | 1 | 0 | 98.56
13:00 | 0 | 0 | 0 | 180 | 0 | 39 | 0 | 404 | 333 |  | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 17 | 33 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 8 | 0 | 45 | 41 | 0 | 24 | 0 | 0 | 0 | 14 | 11 | 33 | 6 | 112 | 99 | 0 | 0 | 2 | 43 | 26 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 196 | 17 | 0 | 10 | 290 | 16 | 2 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 18 | 0 | 19 | 0 | 399 | 8 | 35 | 0 | 4 | 0 | 0 | 17 | 0 | 9 | 0 | 400 | 0 | 48 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 393 | 0 | 18 | 439 | 0 | 0 | 0 | 0 |  | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 113 | 0 | 5 | 0 | 640 | 110 | 0 | 0 | 4 | 70 | 0 | 0 | 0 | 352 | 31 | 140 | 817 | 138 | 0 |  | 5105 | 3461 | 8566 | 3308 | 447 | 1524 | 0 | 251 | 2558 | 46 | 0 | 0 | 112 | 320 | 0 | 0 | 98.55
14:00 | 0 | 0 | 0 | 180 | 0 | 39 | 0 | 398 | 272 |  | 0 | 225 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 17 | 33 | 25 | 8 | 0 | 46 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 8 | 0 | 45 | 39 | 0 | 43 | 0 | 0 | 0 | 16 | 11 | 33 | 6 | 118 | 95 | 0 | 0 | 2 | 43 | 26 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 196 | 17 | 0 | 10 | 270 | 16 | 2 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 15 | 0 | 17 | 0 | 354 | 8 | 35 | 0 | 3 | 0 | 0 | 17 | 0 | 9 | 0 | 360 | 0 | 41 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 350 | 0 | 18 | 442 | 0 | 0 | 0 | 0 |  | 446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 113 | 0 | 5 | 0 | 760 | 110 | 0 | 0 | 3 | 57 | 0 | 0 | 0 | 352 | 25 | 140 | 818 | 146 | 0 |  | 4833 | 3518 | 8351 | 3096 | 446 | 1409 | 0 | 257 | 2682 | 46 | 0 | 0 | 118 | 297 | 0 | 0 | 98.56
15:00 | 0 | 0 | 0 | 180 | 0 | 36 | 0 | 350 | 271 |  | 0 | 225 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 20 | 17 | 33 | 25 | 8 | 0 | 46 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 8 | 0 | 45 | 38 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 6 | 112 | 95 | 0 | 0 | 1 | 43 | 26 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 196 | 17 | 0 | 10 | 300 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 11 | 0 | 17 | 0 | 357 | 8 | 35 | 0 | 2 | 0 | 0 | 17 | 0 | 9 | 0 | 360 | 0 | 29 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 350 | 0 | 27 | 440 | 0 | 0 | 0 | 0 |  | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 34 | 0 | 3 | 0 | 830 | 110 | 0 | 0 | 2 | 34 | 0 | 0 | 0 | 352 | 16 | 140 | 818 | 97 | 0 |  | 4783 | 3484 | 8267 | 3137 | 447 | 1402 | 0 | 178 | 2750 | 46 | 0 | 0 | 112 | 195 | 0 | 0 | 98.55
16:00 | 0 | 0 | 0 | 180 | 0 | 34 | 0 | 352 | 272 |  | 0 | 225 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 20 | 17 | 33 | 25 | 8 | 0 | 46 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 8 | 0 | 45 | 37 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 8 | 104 | 96 | 0 | 0 | 0 | 43 | 27 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 195 | 17 | 0 | 10 | 315 | 16 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 6 | 12 | 19 | 2 | 358 | 8 | 35 | 5 | 1 | 15 | 4 | 17 | 0 | 9 | 0 | 360 | 0 | 12 | 0 | 17 | 0 | 17 | 0 | 0 | 18 | 350 | 0 | 24 | 405 | 5 | 0 | 0 | 0 |  | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 5 | 0 | 15 | 0 | 34 | 0 | 1 | 30 | 850 | 110 | 0 | 8 | 1 | 15 | 0 | 0 | 0 | 350 | 6 | 140 | 816 | 37 | 0 |  | 4980 | 3536 | 8516 | 3237 | 447 | 1505 | 0 | 362 | 2731 | 46 | 0 | 0 | 104 | 79 | 5 | 0 | 98.54
17:00 | 0 | 0 | 0 | 180 | 0 | 39 | 0 | 351 | 271 |  | 0 | 225 | 0 | 4 | 0 | 6 | 300 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 0 | 20 | 17 | 33 | 25 | 8 | 0 | 46 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 5 | 0 | 0 | 12 | 0 | 10 | 12 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 55 | 0 | 45 | 41 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 6 | 97 | 96 | 0 | 0 | 0 | 43 | 26 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 195 | 17 | 0 | 10 | 300 | 16 | 0 | 0 | 10 | 0 | 0 | 110 | 0 | 0 | 0 | 12 | 17 | 15 | 358 | 20 | 88 | 17 | 0 | 45 | 17 | 17 | 17 | 31 | 0 | 390 | 17 | 0 | 35 | 17 | 0 | 17 | 0 | 14 | 34 | 350 | 0 | 15 | 405 | 3 | 0 | 0 | 0 |  | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 920 | 110 | 0 | 17 | 0 | 1 | 17 | 0 | 0 | 402 | 0 | 140 | 818 | 2 | 0 |  | 5313 | 3588 | 8901 | 3130 | 447 | 1510 | 0 | 810 | 2855 | 46 | 0 | 0 | 97 | 3 | 3 | 0 | 98.54
18:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 392 | 341 |  | 0 | 225 | 0 | 13 | 10 | 15 | 335 | 0 | 0 | 15 | 0 | 32 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 0 | 20 | 12 | 33 | 25 | 20 | 0 | 46 | 0 | 0 | 0 | 11 | 214 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 19 | 12 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 102 | 0 | 46 | 42 | 0 | 51 | 0 | 0 | 31 | 16 | 11 | 33 | 8 | 104 | 94 | 0 | 0 | 0 | 43 | 26 | 0 | 35 | 0 | 0 | 0 | 40 | 0 | 197 | 17 | 0 | 10 | 305 | 16 | 0 | 0 | 40 | 0 | 0 | 112 | 0 | 0 | 0 | 12 | 17 | 36 | 402 | 56 | 88 | 17 | 0 | 80 | 17 | 17 | 42 | 46 | 0 | 400 | 68 | 0 | 72 | 17 | 0 | 17 | 0 | 60 | 34 | 395 | 0 | 17 | 500 | 4 | 0 | 0 | 0 |  | 354 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 69 | 0 | 111 | 0 | 0 | 100 | 1190 | 110 | 0 | 45 | 0 | 0 | 70 | 0 | 0 | 604 | 0 | 200 | 819 | 0 | 0 |  | 6218 | 4365 | 10583 | 3282 | 354 | 1763 | 0 | 1515 | 3483 | 46 | 0 | 32 | 104 | 0 | 4 | 0 | 98.54
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 401 | 287 |  | 0 | 225 | 0 | 19 | 28 | 22 | 280 | 0 | 0 | 35 | 0 | 48 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 17 | 20 | 17 | 33 | 25 | 25 | 0 | 46 | 0 | 0 | 0 | 17 | 214 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 20 | 12 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 102 | 0 | 46 | 42 | 0 | 51 | 0 | 0 | 8 | 16 | 11 | 33 | 8 | 94 | 94 | 0 | 0 | 0 | 43 | 26 | 0 | 44 | 0 | 0 | 0 | 40 | 0 | 197 | 17 | 0 | 10 | 260 | 16 | 3 | 0 | 45 | 0 | 0 | 112 | 0 | 0 | 0 | 12 | 17 | 85 | 400 | 56 | 88 | 17 | 0 | 230 | 17 | 17 | 17 | 48 | 0 | 400 | 50 | 0 | 72 | 17 | 0 | 17 | 0 | 72 | 34 | 393 | 0 | 0 | 470 | 3 | 0 | 0 | 0 |  | 209 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 17 | 0 | 70 | 0 | 58 | 0 | 0 | 35 | 1120 | 109 | 0 | 82 | 0 | 0 | 54 | 0 | 0 | 617 | 0 | 200 | 820 | 0 | 0 |  | 6273 | 4024 | 10297 | 3232 | 209 | 1626 | 0 | 1642 | 3397 | 46 | 0 | 48 | 94 | 0 | 3 | 0 | 98.53
19:30 | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 382 | 277 |  | 0 | 225 | 0 | 9 | 17 | 25 | 285 | 0 | 0 | 8 | 0 | 48 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 17 | 20 | 17 | 33 | 25 | 25 | 0 | 46 | 0 | 0 | 0 | 17 | 213 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 20 | 12 | 3 | 0 | 0 | 0 | 280 | 0 | 0 | 55 | 0 | 46 | 42 | 0 | 51 | 0 | 0 | 8 | 16 | 11 | 33 | 8 | 102 | 94 | 0 | 0 | 0 | 43 | 26 | 0 | 44 | 0 | 0 | 0 | 40 | 0 | 198 | 18 | 0 | 10 | 290 | 16 | 5 | 0 | 45 | 0 | 0 | 112 | 0 | 0 | 0 | 12 | 17 | 96 | 402 | 35 | 88 | 17 | 0 | 230 | 17 | 17 | 17 | 48 | 0 | 400 | 32 | 0 | 72 | 17 | 0 | 17 | 0 | 72 | 34 | 350 | 0 | 0 | 450 | 1 | 0 | 0 | 0 |  | 209 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 17 | 0 | 70 | 0 | 34 | 0 | 0 | 35 | 1100 | 109 | 0 | 100 | 0 | 0 | 35 | 0 | 0 | 622 | 0 | 200 | 813 | 0 | 0 |  | 6110 | 3993 | 10103 | 3180 | 209 | 1602 | 0 | 1560 | 3355 | 46 | 0 | 48 | 102 | 0 | 1 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 381 | 277 |  | 0 | 225 | 0 | 9 | 24 | 25 | 280 | 0 | 0 | 9 | 0 | 48 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 17 | 20 | 17 | 33 | 25 | 25 | 0 | 46 | 0 | 0 | 0 | 17 | 213 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 20 | 12 | 5 | 0 | 0 | 0 | 280 | 0 | 0 | 55 | 0 | 46 | 43 | 0 | 51 | 0 | 0 | 8 | 16 | 11 | 33 | 8 | 100 | 95 | 0 | 0 | 0 | 43 | 26 | 0 | 44 | 0 | 0 | 0 | 40 | 0 | 199 | 18 | 0 | 10 | 270 | 16 | 5 | 0 | 45 | 0 | 0 | 121 | 0 | 1 | 0 | 12 | 17 | 98 | 400 | 35 | 88 | 17 | 0 | 100 | 17 | 17 | 17 | 48 | 0 | 400 | 17 | 0 | 72 | 17 | 0 | 17 | 0 | 72 | 34 | 350 | 0 | 0 | 400 | 2 | 0 | 0 | 0 |  | 301 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 17 | 0 | 70 | 0 | 34 | 0 | 0 | 35 | 1040 | 109 | 0 | 75 | 0 | 0 | 35 | 0 | 0 | 624 | 0 | 200 | 815 | 0 | 0 |  | 5929 | 3989 | 9918 | 3174 | 301 | 1586 | 0 | 1412 | 3249 | 46 | 0 | 48 | 100 | 0 | 2 | 0 | 98.53
21:00 | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 381 | 277 |  | 0 | 225 | 0 | 0 | 17 | 15 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 20 | 17 | 33 | 25 | 25 | 0 | 46 | 0 | 0 | 0 | 17 | 213 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 19 | 12 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 55 | 0 | 46 | 41 | 0 | 51 | 0 | 0 | 8 | 16 | 11 | 33 | 8 | 104 | 94 | 0 | 0 | 0 | 43 | 26 | 0 | 44 | 0 | 0 | 0 | 40 | 0 | 198 | 18 | 0 | 10 | 270 | 16 | 5 | 0 | 45 | 0 | 0 | 65 | 0 | 23 | 0 | 12 | 17 | 108 | 400 | 35 | 88 | 17 | 0 | 65 | 17 | 17 | 17 | 49 | 0 | 400 | 17 | 0 | 72 | 17 | 0 | 17 | 0 | 72 | 34 | 350 | 0 | 0 | 405 | 3 | 0 | 0 | 0 |  | 447 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 17 | 0 | 70 | 0 | 34 | 0 | 0 | 35 | 1020 | 110 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 438 | 0 | 200 | 817 | 0 | 0 |  | 5734 | 3866 | 9600 | 3172 | 447 | 1580 | 0 | 1182 | 3050 | 46 | 0 | 16 | 104 | 0 | 3 | 0 | 98.53
22:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 382 | 277 |  | 0 | 225 | 0 | 0 | 17 | 15 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 20 | 17 | 33 | 25 | 25 | 0 | 46 | 0 | 0 | 0 | 17 | 213 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 20 | 12 | 3 | 0 | 0 | 0 | 280 | 0 | 0 | 55 | 0 | 46 | 43 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 8 | 100 | 84 | 0 | 0 | 0 | 43 | 26 | 0 | 41 | 0 | 0 | 0 | 40 | 0 | 199 | 18 | 0 | 10 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 65 | 0 | 25 | 0 | 12 | 17 | 117 | 401 | 35 | 88 | 17 | 0 | 65 | 17 | 17 | 0 | 48 | 0 | 400 | 0 | 0 | 53 | 17 | 0 | 17 | 0 | 72 | 34 | 350 | 0 | 0 | 405 | 2 | 0 | 0 | 0 |  | 446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 35 | 0 | 22 | 0 | 0 | 35 | 940 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 200 | 817 | 0 | 0 |  | 5642 | 3622 | 9264 | 3165 | 446 | 1594 | 0 | 955 | 2940 | 46 | 0 | 16 | 100 | 0 | 2 | 0 | 98.52
23:00 | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 386 | 300 |  | 0 | 225 | 0 | 0 | 5 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 20 | 18 | 25 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 0 | 20 | 12 | 5 | 0 | 0 | 0 | 315 | 0 | 0 | 55 | 0 | 46 | 43 | 0 | 51 | 0 | 0 | 0 | 16 | 11 | 33 | 8 | 96 | 84 | 0 | 0 | 0 | 43 | 26 | 0 | 41 | 0 | 0 | 0 | 40 | 0 | 199 | 18 | 0 | 10 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 12 | 17 | 86 | 404 | 8 | 17 | 17 | 0 | 30 | 17 | 17 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 38 | 17 | 350 | 0 | 0 | 405 | 7 | 0 | 0 | 0 |  | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 930 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 200 | 822 | 0 | 0 |  | 5271 | 3586 | 8857 | 3330 | 447 | 1658 | 0 | 395 | 2878 | 46 | 0 | 0 | 96 | 0 | 7 | 0 | 98.52
24:00 | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 397 | 292 |  | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 18 | 25 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 0 | 9 | 12 | 8 | 0 | 0 | 0 | 310 | 0 | 0 | 55 | 0 | 46 | 43 | 0 | 5 | 0 | 0 | 0 | 16 | 11 | 33 | 8 | 92 | 87 | 0 | 0 | 0 | 43 | 28 | 0 | 41 | 0 | 0 | 0 | 40 | 0 | 203 | 18 | 0 | 10 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 403 | 12 | 0 | 0 | 0 |  | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 163 | 819 | 0 | 0 |  | 4985 | 3531 | 8516 | 3394 | 447 | 1618 | 0 | 97 | 2810 | 46 | 0 | 0 | 92 | 0 | 12 | 0 | 98.52
KWH | 0 | 0 | 0 | 4362750 | 0 | 808136 | 0 | 8753150 | 6748000 |  | 0 | 4838600 | 0 | 49920 | 84127 | 111083 | 6931994 | 0 | 0 | 60250 | 0 | 138720 | 0 | 0 | 0 | 0 | 129600 | 139998 | 135784 | 265464 | 480000 | 347760 | 635700 | 684900 | 165600 | 0 | 1115040 | 0 | 0 | 0 | 81142 | 5006317 | 0 | 0 | 0 |  | 38400 | 0 | 0 | 91440 | 0 | 131520 | 280224 | 293280 | 0 | 0 | 0 | 7328100 | 0 | 0 | 602182 | 0 | 873504 | 708960 | 0 | 727788 | 0 | 0 | 95434 | 281988 | 221940 | 736800 | 187080 | 2359680 | 2138880 | 0 | 0 | 11950 | 1015000 | 672600 | 0 | 361224 | 0 | 0 | 0 | 956160 | 0 | 5040900 | 410000 | 0 | 253980 | 6993000 | 373056 | 76432 | 0 | 278509 | 0 | 0 | 878400 | 0 | 66672 | 136350 | 104640 | 233760 | 553672 | 8971000 | 314400 | 692160 | 150545 | 24719 | 634800 | 142035 | 231672 | 123120 | 346080 | 0 | 9053700 | 166080 | 325380 | 354240 | 223309 | 0 | 416880 | 6641 | 417600 | 370800 | 8040000 | 0 | 135491 | 9065453 | 138240 | 0 | 0 | 0 |  | 10091636 | 0 | 0 | 0 | 82560 | 0 | 0 | 0 | 0 | 0 | 0 | 1508000 | 357700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17813 | 0 | 0 | 0 | 130644 | 0 | 0 | 4181900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8278327 | 96240 | 0 | 426336 | 0 | 1319798 | 0 | 34858 | 344064 | 19894500 | 2622000 | 0 | 267600 | 29700 | 472320 | 271872 | 0 | 0 | 9461818 | 204305 | 3806400 | 19783636 | 1083940 | 0 |  | 117931885 | 84767967 | 202699852 | 74943374 | 10091636 | 34549337 | 0 | 10839955 | 66193707 | 1115040 | 0 | 138720 | 2359680 | 2330163 | 138240 | 0
Fuel Cost | 0 | 0 | 0 | 6500497.5 | 0 | 1074820.88 | 0 | 9190807.5 | 7287840 |  | 0 | 5274074 | 0 | 558105.6 | 1114682.75 | 1471849.75 | 7763833.28 | 0 | 0 | 880855 | 0 | 2248651.2 | 0 | 0 | 0 | 0 | 1648512 | 1889973 | 1820863.44 | 199098 | 360000 | 0 | 0 | 0 | 2816856 | 0 | 301060.8 | 0 | 0 | 0 | 1326671.7 | 5206569.68 | 0 | 0 | 0 |  | 501120 | 0 | 0 | 1235354.4 | 0 | 1521686.4 | 355884.48 | 976622.4 | 0 | 0 | 0 | 8134191 | 0 | 0 | 776814.78 | 0 | 987059.52 | 1056350.4 | 0 | 1215405.96 | 0 | 0 | 1283587.3 | 386323.56 | 166455 | 1289400 | 140310 | 16942502.4 | 2331379.2 | 0 | 0 | 190483 | 1390550 | 887832 | 0 | 624917.52 | 0 | 0 | 0 | 2180044.8 | 0 | 5091309 | 881500 | 0 | 502880.4 | 6993000 | 279792 | 58088.32 | 0 | 3801647.85 | 0 | 0 | 11840832 | 0 | 923407.2 | 1593931.5 | 1079884.8 | 3193161.6 | 7347227.44 | 8253320 | 3823104 | 10008633.6 | 1904394.25 | 384627.64 | 7452552 | 1546761.15 | 2462673.36 | 1670738.4 | 4460971.2 | 0 | 8329404 | 2150736 | 4701741 | 4495305.6 | 2541256.42 | 0 | 5444452.8 | 79359.95 | 6251472 | 4883436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 30274908 | 0 | 0 | 0 | 859449.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1688960 | 693938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242791.19 | 0 | 0 | 0 | 98897.508 | 0 | 0 | 35462512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8195543.73 | 1293465.6 | 0 | 5043554.88 | 0 | 16761434.6 | 0 | 385180.9 | 4176936.96 | 165124350 | 2674440 | 0 | 1980240 | 335907 | 5540313.6 | 4167797.76 | 0 | 0 | 86007925.62 | 0 | 45562608 | 169150087.8 | 0 | 0 |  | 227941497.68 | 585721242.748 | 813662740.428 | 69971461.548 | 30274908 | 39526692.87 | 0 | 139878435.6 | 501307483.42 | 301060.8 | 0 | 2248651.2 | 16942502.4 | 13211544.59 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 39 | 0 | 363 | 291 |  | 0 | 170 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 20 | 11 | 0 | 25 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 8 | 0 | 47 | 41 | 0 | 5 | 0 | 0 | 0 | 7 | 11 | 33 | 6 | 116 | 84 | 0 | 0 | 2 | 43 | 26 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 196 | 16 | 0 | 10 | 290 | 8 | 2 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 20 | 0 | 10 | 0 | 402 | 8 | 17 | 0 | 4 | 0 | 0 | 10 | 0 | 8 | 0 | 390 | 0 | 47 | 0 | 12 | 0 | 17 | 0 | 0 | 0 | 300 | 0 | 18 | 400 | 1 | 0 | 0 | 0 |  | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 113 | 0 | 5 | 0 | 600 | 110 | 0 | 0 | 5 | 74 | 0 | 0 | 0 | 352 | 34 | 140 | 822 | 177 | 0 |  | 8140 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 392 | 341 |  | 0 | 225 | 0 | 13 | 10 | 15 | 335 | 0 | 0 | 15 | 0 | 32 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 0 | 20 | 12 | 33 | 25 | 20 | 0 | 46 | 0 | 0 | 0 | 11 | 214 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 12 | 0 | 19 | 12 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 102 | 0 | 46 | 42 | 0 | 51 | 0 | 0 | 31 | 16 | 11 | 33 | 8 | 104 | 94 | 0 | 0 | 0 | 43 | 26 | 0 | 35 | 0 | 0 | 0 | 40 | 0 | 197 | 17 | 0 | 10 | 305 | 16 | 0 | 0 | 40 | 0 | 0 | 112 | 0 | 0 | 0 | 12 | 17 | 36 | 402 | 56 | 88 | 17 | 0 | 80 | 17 | 17 | 42 | 46 | 0 | 400 | 68 | 0 | 72 | 17 | 0 | 17 | 0 | 60 | 34 | 395 | 0 | 17 | 500 | 4 | 0 | 0 | 0 |  | 354 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 69 | 0 | 111 | 0 | 0 | 100 | 1190 | 110 | 0 | 45 | 0 | 0 | 70 | 0 | 0 | 604 | 0 | 200 | 819 | 0 | 0 |  | 10583 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 77 | 0 | 412 | 330 |  | 0 | 225 | 0 | 100 | 85 | 30 | 335 | 0 | 0 | 92 | 100 | 149 | 40 | 0 | 0 | 0 | 35 | 35 | 35 | 18 | 20 | 18 | 33 | 33 | 25 | 0 | 46 | 0 | 0 | 0 | 17 | 212 | 0 | 0 | 0 |  | 6 | 64 | 0 | 12 | 0 | 10 | 12 | 25 | 0 | 0 | 0 | 320 | 0 | 0 | 102 | 0 | 51 | 40 | 0 | 51 | 0 | 0 | 52 | 18 | 11 | 33 | 10 | 140 | 90 | 0 | 0 | 0 | 43 | 28 | 0 | 44 | 0 | 0 | 0 | 40 | 0 | 200 | 17 | 0 | 10 | 310 | 16 | 5 | 0 | 130 | 0 | 0 | 104 | 0 | 100 | 0 | 12 | 17 | 150 | 400 | 85 | 105 | 17 | 0 | 260 | 17 | 17 | 114 | 65 | 12 | 400 | 88 | 0 | 35 | 17 | 0 | 17 | 0 | 72 | 35 | 395 | 0 | 0 | 500 | 10 | 300 | 0 | 0 |  | 453 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 50 | 70 | 16 | 130 | 25 | 110 | 0 | 0 | 0 | 35 | 20 | 85 | 28 | 42 | 40 | 52 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 105 | 0 | 50 | 32 | 113 | 0 | 0 | 113 | 1220 | 110 | 0 | 150 | 0 | 0 | 110 | 0 | 0 | 550 | 0 | 200 | 900 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 77 | 0 | 412 | 330 | 0 | 0 | 225 | 0 | 92 | 85 | 15 | 335 | 0 | 0 | 92 | 100 | 16 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 20 | 18 | 33 | 33 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 212 |  | 0 | 0 | 0 | 6 | 40 | 0 | 12 | 0 | 6 | 12 | 10 | 0 | 0 | 0 | 320 | 0 | 0 | 55 | 0 | 51 | 40 | 0 | 51 | 0 | 0 | 52 | 18 | 11 | 33 | 10 | 128 | 80 | 0 | 0 | 1.6 | 43 | 28 | 0 | 44 | 0 | 0 | 0 | 40 | 0 | 200 | 17 | 0 | 10 | 310 | 16 | 5 | 0 | 80 | 0 | 0 | 84 | 0 | 18 | 20 | 12 | 17 | 150 | 400 | 56 | 30 | 17 | 5 | 260 | 17 | 17 | 114 | 28 | 12 | 400 | 26 | 50 | 17 | 17 | 0 | 17 | 35 | 36 | 17 | 395 | 0 |  | 400 | 10 | 0 | 0 | 0 |  | 453 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 28 | 34 | 30 | 52 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 105 | 0 | 35 | 15 | 113 | 0 | 8 | 35 | 1000 | 110 |  | 0 | 6 | 100 | 70 | 0 |  | 450 | 30 | 150 | 850 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 396 | 267 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 18 | 25 | 25 | 2 | 0 | 46 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 10 | 0 | 0 | 0 | 280 | 0 | 0 | 55 | 0 | 46 | 6 | 0 | 43 | 0 | 0 | 0 | 16 | 11 | 33 | 8 | 90 | 70 | 0 | 0 | 1 | 43 | 28 | 0 | 40 | 0 | 0 | 0 | 40 | 0 | 200 | 17 | 0 | 10 | 295 | 8 | 5 | 0 | 0 | 0 | 0 | 56 | 0 | 3 | 10 | 0 | 2 | 0 | 398 | 37 | 17 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 19 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 393 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 860 | 109 | 0 | 0 | 1 | 28 | 0 | 0 | 0 | 355 | 12 | 150 | 814 | 76 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
[8 empty] | 299430 | [13 empty] | 299565 | [26 empty] | 399366 | 399587 | [8 empty] | 299280 | [26 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 |  | 399747 |  |  |  | 399575 |  | 399337 | 399589 | 299230 | [7 empty] | 399245 |  | 299282 | 399274 |  | 399223 |  | 399630 | [12 empty] | 599468 | [32 empty] | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 | [8 empty] | 599726 | [9 empty] | 292.3904
| Minimum Generation |  | 6700 | 5:00 | [202 empty] | 109492711
| Highest Generation |  | 10583 | 18:00 | [202 empty] | 109.4927 |  |  |  |  | 2.3302
| Day Peak Generation |  | 8140 | 12:00 | [202 empty] | 10978675
| Evening Peak Generation |  | 10583 | 18:00 | [202 empty] | 10.9787 |  |  | 34549337 |  | 1.115
| HVDC Max Flow |  | 447 | 1:00 | [202 empty] | 10.0916 |  |  |  |  | 0.13824
| HVDC EvPeak Flow |  | 354 | 18:00 | [200 empty] | 202699852 |  | 2.3597 |  | 66.1937
| Load factor L.F |  | 79.81% | [166 empty] | 1275.5 | [36 empty] | 202.6999

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-11-26
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-11-25 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 8140 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 7092
Evening Peak Generation : |  |  | 10583 | MW Hour : | 18:00 | Available Max Generation : |  | 13406
E.P. Demand (at gen end) : |  |  | 10583 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 11000
Maximum Generation : |  |  | 10583 | MW Hour : | 18:00 | Reserve(Generation end) |  | 2406
Total Gen. (MKWH) : |  |  | 202.6999 | System Load Factor : | 79.81% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 216 | MW at | 22:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-11-26
Actual : |  | 98.5 | Ft.(MSL) , | Rule curve : | 106.5 | Ft.( MSL )
Gas Consumed : |  | Total = | 814.34 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 109498154.418
: |  |  | Coal : | 501307483.42 | Oil : | 142127086.8 | Total : | 752932724.638
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3693.7597 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1009.6328 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1412.702 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1226.4236 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1009.8797 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 750.3172 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 421.4087 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 350.4332 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 685.4034 |  |  | 0 | 0%
Total |  | 0 |  | 10559.9605 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:00 |  | Spectra Solar Plant Ltd. Tripped
08:04 | 17:17 | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to Annual Maintenance
08:05 | 14:55 | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to Annual maintenace
08:07 |  | Mirpur 132/33kV S/S T1 HT Forced S/D Due to T-1 Transformer hydraulic pressure low, motor pump problem.
08:07 |  | Mirpur 132/33kV S/S T1 LT Forced S/D Due to T-1 Hydraulic pressure low.
08:10 | 15:47 | Patuakhali 132/33kV S/S 405T (T-1) LT Scheduled S/D Due to T- Transformer yearly maintenance
08:11 | 15:46 | Patuakhali 132/33kV S/S 405T (T-1) HT Scheduled S/D Due to T-1 Transformer & associate yearly maintenance work.
08:11 | 17:02 | Gollamari 132/33kV S/S E01 Gollamari-Gopalgonj Line - 1 Scheduled S/D Due to Annual Maintenance.
08:12 | 17:01 | Gopalganj 132/33kV S/S Gallamari-1 Scheduled S/D Due to Annual Maintenance
08:13 | 17:17 | Rajshahi 230/132/33kV S/S 230/132 kV ATR-01 (704T) LT Scheduled S/D Due to Annual Maintenance
08:13 | 16:40 | Bogura(New)-Naogaon 132 kV Ckt-1 Scheduled S/D from Bogura 230/132kV end. and from Naogaon 132/33kV end Due to Annual
maintenance
08:14 | 16:05 | Jhenaidah-Khulna 230kV Ckt-2 Scheduled S/D from Jhenaidah 230/132kV end Due to A/M works and from Khulna(S)
230/132kVend.
08:15 | 17:16 | Rajshahi 230/132/33kV S/S 230/132 kV ATR-01 (704T) HT Scheduled S/D Due to Annual Maintenance
08:15 | 10:38 | Feni 132/33kV S/S T-1(405T) LT Scheduled S/D Due to Maintenance work by BPDB |  |  |  |  | 25.0MW load interrup.
08:16 | 10:37 | Feni 132/33kV S/S T-1(405T) HT Scheduled S/D Due to Maintenance work by BPDB |  |  |  |  | 25.0MW load interrup.
08:20 |  | Summit Power Madhabdi Control Room Shutdown
08:25 | 16:15 | Barapukuria-Rangpur 132 kV Ckt-2 Scheduled S/D from Barapukuria 230/132/33kV end Due to Annual Maintenance and
from Rangpur 132/33kV end Due to Annual Maintenances
08:30 |  | Maona 33 MW PP(Summit) Forced Shutdown
08:31 |  | Feni 11 MW PP (Doreen) Syncronized
08:32 | 13:34 | Kishoreganj 132/33kV S/S Tr-2 (414T) HT Scheduled S/D Due to Annual maintenance of 33 kv T2 bus sec by PDB
08:32 | 13:34 | Kishoreganj 132/33kV S/S Tr-2 (414T) LT Scheduled S/D Due to Annual maintenance of 33 kv T2 bus sec by PDB
08:39 | 13:53 | Gopalganj 400/132kV S/S ATR-01 HT Scheduled S/D
08:39 | 13:53 | Gopalganj 400/132kV S/S ATR-01 LT Scheduled S/D
08:41 | 15:47 | Sherpur 132/33kV S/S Transformer- 02 LT Scheduled S/D Due to Annual Maintenance |  |  |  |  | 25.0MW load interrup.
08:41 | 15:45 | Sherpur 132/33kV S/S Transformer- 02 HT Scheduled S/D Due to Annual Maintenance |  |  |  |  | 25.0MW load interrup.
08:44 | 16:18 | Narshingdi 132/33kV S/S T-1 LT Scheduled S/D Due to For Annual Maintenance purpose.
08:45 | 16:17 | Narshingdi 132/33kV S/S T-1 HT Scheduled S/D Due to Annaul Maintenance purpose.
08:46 | 16:50 | Kulaura 132/33kV S/S TR-1 LT Scheduled S/D Due to Annual maintenance and C.T changed |  |  |  |  | 10.0MW load interrup.
08:47 | 16:49 | Kulaura 132/33kV S/S TR-1 HT Scheduled S/D Due to Annual maintenance and C.T changed |  |  |  |  | 10.0MW load interrup.
08:48 | 14:48 | Mongla 132/33kV S/S T-1 LT Scheduled S/D Due to Annual Maintenance of 33 KV Bus. |  |  |  |  | 10.0MW load interrup.
08:49 | 14:49 | Mongla 132/33kV S/S T-2 LT Scheduled S/D Due to Annual Maintenance of 33 KV Bus. |  |  |  |  | 10.0MW load interrup.
08:50 | 14:47 | Mongla 132/33kV S/S T-1 HT Scheduled S/D Due to Annual Maintenance of 33 KV Bus. |  |  |  |  | 10.0MW load interrup.
08:50 | 14:48 | Mongla 132/33kV S/S T-2 HT Scheduled S/D Due to Annual Maintenance of 33 KV Bus. |  |  |  |  | 10.0MW load interrup.
08:51 | 16:50 | Fenchuganj-Sreemangal 132kV Ckt-1 Scheduled S/D from Sreemongol 132/33kV end Due to For dead line checking.
08:52 | 17:19 | Bhaluka-Mymensingh 132 kV Ckt-1 Scheduled S/D from Bhaluka 132/33kV end Due to Dead Line Checking
08:54 | 17:17 | Sreepur 230/132/33kV S/S Sreepur-Valuka Ckt-1 Scheduled S/D Due to Annual Maintenance (Line)
08:58 | 16:30 | Bhulta-Haripur 132 kV Ckt-1 Scheduled S/D from Bhulta 132/33kV end Due to Annual Maintenance and from Haripur
230/132kV end Due to Work at Bhulta side.
09:02 | 16:51 | Fenchuganj-Sreemangal 132kV Ckt-1 Scheduled S/D from Fenchuganj 230/132/33kV end Due to Annual Maintenance by
Srmongal S/S
09:05 |  | Ullapara 11 MW PP (Summit) Tripped
09:23 |  | Narshingdi 22 MW PP (Doreen) Syncronized
09:24 | 14:11 | Noapara 132/33kV S/S BUS-B Scheduled S/D Due to Annual Maintenance..
09:25 | 15:52 | Kodda-Rajendrapur 132kV Ckt-1 Scheduled S/D from Rajendrapur 132/33kV end Due to Annual Maintenance and from
Kodda 132/33kV end Due to Annual Maintenance
09:26 |  | Kallyanpur 132/33kV S/S GT-1 (132kV) HT Scheduled S/D Due to centrifuging work
09:28 | 13:10 | Madanganj-Munsiganj 132 kV Ckt-1 Scheduled S/D from Madanganj 132/33kV end. and from Munshiganj 132/33kV end
Due to Annual maintenance
09:31 | 17:16 | Mymensingh RPCL -Mymensingh 132kV Ckt-1 Scheduled S/D from Mymensingh 132/33kV end Due to Annual maintenance work
09:32 | 14:44 | Khulna(S) 230/132kV S/S TR-1 LT Scheduled S/D Due to TAN-DELTA TEST.
09:33 | 14:44 | Khulna(S) 230/132kV S/S TR-1 HT Scheduled S/D Due to TAN-DELTA TEST.
09:41 | 15:55 | Fenchuganj-Kulaura 132 kV Ckt-1 Scheduled S/D from Fenchuganj 230/132/33kV end Due to Annual Maintenance by
Kulaura S/S and from Kulaura 132/33kV end Due to For annual maintenance.
09:55 |  | Mirsharai 150 MW Syncronized
09:59 | 12:25 | Savar 132/33kV S/S T-3 LT Scheduled S/D Due to Hot spot maintenance & Measurement of Bucholtz relay of 132/33 KV
Transformer-3.
09:59 | 12:25 | Savar 132/33kV S/S T-3 HT Scheduled S/D Due to Hot spot maintenance & Measurement of Bucholtz relay of 132/33 KV
Transformer-3
10:02 |  | Gazipur 100 MW PP Syncronized
10:05 |  | Maona 33 MW PP(Summit) Syncronized
10:14 |  | Fenchuganj 44MW (Energyprima) Shutdown
10:42 |  | Feni 11 MW PP (Doreen) Shutdown
11:00 |  | Chowmuhani 113 MW Syncronized
| 11:00 | Ishurdi 132/33kV S/S 132/33 kV T-2 HT is restored.
11:02 |  | Anlima Energy Ltd. Syncronized
11:04 | 11:17 | Keranigonj 230/132/33kV S/S Lalbagh-3 Tripped showing Distance Relay relays. |  |  |  |  | 81.0MW load interrup.
11:09 |  | Chandpur 200MW (Desh energy) Syncronized
11:12 | 12:44 | Sonargaon 132/33kV S/S Tr-1 LT Forced S/D Due to Corrective Maintenance at R Phase 33 Kv CT due to high temperature |  |  |  |  | 36.0MW load interrup.
11:13 | 12:38 | Sonargaon 132/33kV S/S Tr-1 HT Forced S/D Due to Corrective Maintenance at R Phase 33 Kv CT due to high temperature |  |  |  |  | 36.0MW load interrup.
11:16 |  | Karnaphuli Power Ltd. Syncronized
11:20 |  | Ullapara 11 MW PP (Summit) Syncronized
11:20 |  | Summit Power Madhabdi Control Room Syncronized
11:25 |  | Feni 11 MW PP (Doreen) Syncronized
11:33 |  | Jamalpur 115 MW PP (United) Syncronized
11:36 |  | Maona 33 MW PP(Summit) Tripped
| 11:43 | Chowmuhani-Feni 132 kV Ckt-1 is restored.
11:49 |  | Feni 22MW PP (Doreen) Syncronized
11:50 |  | Kanchan Purbachal Power Generation Ltd. Shutdown
12:06 |  | Hathazari 100 MW peaking PP Syncronized
12:16 |  | Maona 33 MW PP(Summit) Syncronized
12:32 |  | Hathazari 100 MW peaking PP Shutdown
13:03 |  | Gazipur 52 MW PP Syncronized
14:46 | 17:14 | Khulna(S) 230/132kV S/S TR-3 HT Scheduled S/D
14:46 | 17:15 | Khulna(S) 230/132kV S/S TR-3 LT Scheduled S/D
| 14:56 | Khulshi-Madunaghat 132kV Ckt-1 is restored.
14:57 |  | Hobiganj 11MW PP Cofidence-E Shutdown
| 14:57 | Sholosohor 132/33kV S/S Sholoshahar-Khulshi Ckt-1 is
restored.
15:17 |  | Juldah 100 MW Unit-1 (Acorn) Syncronized
15:18 |  | Kanchan Purbachal Power Generation Ltd. Syncronized
15:20 |  | Ashuganj 150MW PP (Midland) Syncronized
15:20 |  | Juldah 100 MW PP Unit-3 (Acorn) Syncronized
15:22 |  | Bagura 113 MW PP (Confidence)-2 Syncronized
15:23 |  | Confidence Power Bogura Unit-1 113 MW Syncronized
15:26 |  | Sikalbaha 105 MW PP (Baraka Sikalbaha) Syncronized
15:29 |  | United Payra Power Ltd. Syncronized
15:38 |  | Jodiac Power Syncronized
15:45 |  | Manikganj 55 MW PP (Northern) Syncronized
15:52 |  | Anwara 300 MW PP (United) Syncronized
15:55 |  | Rupsha 105 MW PP (Orion rupsha) Syncronized
16:01 |  | Tangail Palli Power Gen 22 MW Syncronized
16:01 |  | Siddhirganj 100 PP(Dutch Bangla) Syncronized
16:01 |  | Patenga 50MW PP (Baraka) Syncronized
16:04 |  | Manikgonj 162MW PP(MPGL) Syncronized
| 16:05 | Jhenaidah-Khulna 230kV Ckt-2 is restored.
16:07 |  | Meghnaghat 104 MW PP (OPCL) Syncronized
16:14 |  | Energypac Power Venture Thakurgaon Ltd. Syncronized
16:19 |  | Kodda 300 MW PP Unit-2 (Summit) Syncronized
16:21 |  | Chandpur 115(Doreen) Syncronized
16:22 |  | Meghnaghat 100 MW(IEL) Syncronized
| 16:23 | Barishal 132/33kV S/S T-1 (405T) HT is restored.
| 16:24 | Barishal 132/33kV S/S T-1 (405T) LT is restored.
16:28 |  | Kamalaghat 54 MW PP(Banco Energy) Syncronized
16:31 |  | Madanganj-55 MW PP(Summit) Syncronized
16:33 |  | Kaptai 7 MW Solar PP Shutdown
16:35 |  | Feni Lanka Power Syncronized
| 16:35 | Khulshi 132/33kV S/S 405T (T1) HT is restored.
16:36 |  | Narshingdi 22 MW PP (Doreen) Tripped
| 16:36 | Khulshi 132/33kV S/S 405T (T1) LT is restored.
| 16:50 | Sirajganj 132/33kV S/S Sherpur-2 is restored.
| 16:50 | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-2 is restored.
| 16:52 | Baghabari-Sirajganj 132 kV Ckt-1 is restored.
16:54 |  | Kaliakoir 400/230/132kV S/S 400kV Bus 2 Forced S/D Due to Emergency Maintenance.
17:01 |  | Jangalia 52 MW PP (Lakdanavi) Syncronized
17:02 |  | Sarishabari 3 MW Solar Plant Shutdown
17:08 |  | Raozan 25 MW PP Syncronized
| 17:08 | Barishal 230/132kV S/S T-4 HT is restored.
17:09 |  | Khulna 115 PP MW (KPCL-2) Syncronized
17:10 |  | Sirajgonj 6.55 MW Solar Shutdown
| 17:10 | Barishal 230/132kV S/S T-4 LT is restored.
17:10 |  | Teknaf 20MW PP (Solartech) Shutdown
17:12 |  | Spectra Solar Plant Ltd. Shutdown
| 17:14 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) HT is restored.
17:15 |  | Madanganj 102 PP(Summit) Syncronized
17:15 |  | Nababganj 55 MW PP (Southern power ) Syncronized
17:15 |  | Sympa Solar Power 8 MW Shutdown
17:15 |  | Teesta Solar Limited Shutdown
| 17:15 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) LT is restored.
17:17 |  | Mongla Orion 100 MW Solar PP Shutdown
17:27 |  | Sutiakhali 50 MW Solar PP Shutdown
17:33 | 18:10 | Ishurdi 230/132kV S/S 230/132 kV T-01 LT Tripped showing BBC relays.
17:33 | 18:10 | Ishurdi 230/132kV S/S 230/132 kV T-01 HT Tripped showing BBC relays.
17:40 |  | Intraco Solar 30 MW Shutdown

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-11-25 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4362750
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 70 | 808136 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 392 | 8753150 | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 341 | 6748000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4838600 | GT-1 under S/D due to gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 13 | 49920 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | GT-1 under S/D due to gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 10 | 84127 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 111083 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 265464 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 15 | 60250 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 6931994
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 129600 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 138720 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 139998 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 135784 | Low demand
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 32 | 827760 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 635700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 684900 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 20 | 165600 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 40 | 278509 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 66672 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 692160 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 68 | 166080 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 354240 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 6641
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 34 | 370800 | Fuel shortage
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5422 | 2127 | 37806638
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 11 | 81142 | Low demand
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 136350
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 131520 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1115040 | Unit-2 under maint.
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 214 | 5006317
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 150545 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 12 | 91440 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 104640 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 12 | 280224 | Fuel shortage
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 0 | 293280
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 24719
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 80 | 634800 | Low demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 142035 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 231672 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 223309 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 0 | 135491 | Fuel shortage
| SS Power I |  | SS Power | 1*612 | 612 | 500 | 9065453
| Cox's Bazar Wind |  | IPP | 66 | 0 | 4 | 138240 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 0 | 0 | On test.
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 163 | 17 | 135491
| Chattogram area Total |  |  |  | 3320 | 995 | 18121708
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 0 | Under maint.
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7328100 | Under maint.
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 395 | 8040000
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 46 | 873504
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 0 | 42 | 708960 | Gas shortage
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 102 | 602182 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 727788
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 36 | 553672 | Low demand
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Under maint.
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 233760 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 281988 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 221940
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 104 | 2359680
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 736800
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 31 | 95434 | Low demand
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 8 | 187080 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 42 | 123120 | Low demand
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 46 | 346080 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 416880 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 60 | 417600 | Fuel shortage
| Cumilla Area Total |  |  |  | 2896 | 1337 | 24254568
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 94 | 2138880 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Contract Expired
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11950
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 112 | 878400 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 56 | 314400 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 325380
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 38400 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 268 | 3707410
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1015000
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 26 | 672600 | Engine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 35 | 361224 | Gas shortage
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 76432 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under maint.
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 40 | 956160 | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 197 | 5040900 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 410000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 373056 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 6993000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 402 | 8971000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 253980
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9053700
| Sylhet Area Total |  |  |  | 2427 | 1491 | 34177052
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 354 | 10091636 | Block-1 under maintenance
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 82560 | Low demand
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Reserve
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 96240 | Low demand
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Reserve
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 472320
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 604 | 9461818
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 991 | 20204574
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 18 | 357700 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 50 | 1508000 | ST Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1190 | 19894500
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 110 | 2622000 | GT-1 Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 45 | 267600 | Low demand
| Barisal 307 MW |  | IPP | 307*1 | 307 | 200 | 3806400 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1613 | 28456200
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 8278327
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 130644
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 17813 | Reserve
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 69 | 426336 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 100 | 344064 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 29700
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 819 | 19783636
| Rajshahi Area Total |  |  |  | 3631 | 1410 | 29010520
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4181900 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 111 | 1319798 | Engine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 34858
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 70 | 271872 | Low demand
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 204305
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1083940
| Rangpur Area Total |  |  |  | 950 | 351 | 7096673
| Total |  |  |  | 24762 | 10583 | 202835343
| Eastern Grid Total |  |  |  | 14679 | 6218 | 118067376
| Western Grid Total |  |  |  | 10083 | 4365 | 84767967
| National Grid Total |  |  |  | 24762 | 10583 | 202835343
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-11-25
| (a) ENTIRE EASTERN GRID : |  | 7075.15 | MW | (b) ENTIRE WESTERN GRID : |  | 3078.6 | MW
| i) Dhaka area |  | 3890.35 | MW | i) Khulna area |  | 1141.6 | MW
| ii) Chittagong area |  | 1072.8 | MW | ii) Rajshahi area |  | 948 | MW
| iii) Comilla area |  | 887 | MW | iii) Barisal area |  | 282 | MW
| iv) Mymensingh area |  | 812 | MW | iv) Rangpur area |  | 707 | MW
| v) Sylhet area |  | 413 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10153.75 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 18 | 18:00 | Kamrangirchar | 38.1 | 13:00 | Narinda | 40 | 13:00 | Sherpur | 104 | 18:00
2 | AKSML | 109 | 16:00 | Chowmuhani | 124 | 20:00 | Kaptai | N/A | N/A | Narshingdi | 151 | 18:30 | Shikalbaha | 19 | 18:30
3 | Aftabnagar | 26 | 12:00 | Chuadanga | 73 | 18:00 | Kazla | 80 | 13:00 | Natore | 95 | 18:00 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 62 | 18:00 | Coxsbazar | 93 | 18:30 | Keranigonj | 56 | 12:00 | Nawabganj | 34.2 | 20:00 | Shitalakhya | 82.2 | 12:00
5 | Agrabad | 48 | 18:00 | Cumilla(N) | 102 | 21:00 | Khagrachori | 24 | 18:00 | Netrakona | 92 | 18:00 | Sholosohor | 38 | 15:00
6 | Amnura | 31 | 18:30 | Cumilla(S) | 117 | 14:00 | Khulna | 78 | 18:00 | New | 57 | 11:00 | Shyampur | 154 | 10:00
7 | Ashuganj | 56 | 18:30 | Daudkandi | 110 | 18:00 | Khulshi | 127 | 17:00 | Niamatpur | 48 | 18:00 | Siddhirganj | 96 | 11:00
8 | BIPTC | N/A | N/A | Dhaka | 24 | 13:00 | Kishoreganj | 102 | 18:00 | Noapara | 37.5 | 18:00 | Sirajganj | 79 | 19:30
9 | BSRM | 140 | 00:00 | Dhamrai | 116 | 18:00 | Kodda | 242 | 18:00 | PHP | 10 | 11:00 | Sonargaon | 88 | 23:00
10 | Bagerhat | 68 | 18:30 | Dhanmondi | 96 | 13:00 | Kulaura | 36 | 18:00 | Pabna | 80 | 18:00 | Sreemongol | 46 | 21:00
11 | Bakulia | 88 | 18:30 | Dohazari | 74 | 18:00 | Kurigram | 50 | 18:00 | Palashbari | 81 | 18:00 | Sreepur | 51 | 18:00
12 | Banani | 0 | 00:00 | Faridpur | 108 | 18:00 | Kushtia | 97 | 18:00 | Panchagarh | 42 | 18:00 | Srinagar | 28.43 | 20:00
13 | Bangabhaban | 5 | 09:00 | Fatullah | 55 | 12:00 | Lalbag | 80 | 11:00 | Patuakhali | 58.5 | 21:00 | Sunamganj | 35 | 18:00
14 | Barapukuria | 49 | 18:00 | Fenchuganj | 30 | 18:00 | Lalmonirhat | 35 | 18:00 | Payra | 20 | 18:30 | Sylhet | 16 | 18:30
15 | Barguna | 12 | 18:00 | Feni | 84 | 18:00 | MI_Cement | 19 | 08:00 | Postogola | 44 | 13:00 | Sylhet-132 | 96 | 18:00
16 | Barishal | 71 | 18:00 | GPH | 89 | 19:00 | Madanganj | 28 | 15:00 | Purbachal | 15 | 11:00 | TK | 17 | 14:00
17 | Barishal-230 | 62 | 18:00 | Ghorashal | 51 | 18:30 | Madaripur | 61 | 18:00 | Purbasadipur | 100 | 18:30 | Tangail | 140 | 18:30
18 | Baroaulia | 64 | 09:00 | Goalpara | 24 | 12:00 | Madartek | 57.28 | 18:30 | Rahim | 37 | 12:00 | Thakurgaon | 73 | 18:30
19 | Baroirhat | 32 | 18:30 | Gollamari | 35 | 18:30 | Madunaghat | 37 | 18:00 | Rajbari | 45 | 18:30 | Tongi | 87 | 11:00
20 | Bashundhara | 124 | 18:00 | Gopalganj | 67.8 | 18:30 | Magura | 46 | 18:00 | Rajendrapur | 78 | 18:00 | Ullon | 36 | 18:00
21 | BashundharaCement | 1 | 15:00 | Gulshan | 70 | 13:00 | Mahasthangarh | 50 | 18:00 | Rajshahi | 95 | 18:30 | Uttara | 48 | 12:00
22 | Beanibazar | 48 | 18:00 | Halishahar | 94 | 15:00 | Manikganj | 79 | 19:30 | Rajshahi-230 | 24 | 13:00 | UttaraNew | 41 | 13:00
23 | Benapole | 40 | 18:00 | HaripurSBU | 147 | 19:00 | Maniknagar | 50 | 13:00 | Ramganj | 78 | 21:00 | Zigatola | 78 | 19:00
24 | Bhaluka | 108 | 18:00 | Hasnabad | 61 | 18:00 | Matarbari | 18 | 18:00 | Rampur | 26 | 18:00
25 | Bhandaria | 34 | 18:00 | Hathazari | 50 | 18:00 | Matuail | 58 | 11:00 | Rangamati | 12 | 12:00
26 | Bhangura | 20 | 18:30 | Ishurdi | 55 | 18:00 | Millgate | 84 | 15:00 | Rangpur | 115 | 18:00
27 | Bheramara(GK) | 39 | 18:00 | Jaldhaka | 60 | 18:00 | Mirpur | 101 | 18:00 | Ruppur | 3.2 | 12:00
28 | Bhulta | 206 | 19:00 | Jamalpur | 120 | 18:00 | Mirsorai | 3.5 | 13:00 | SSM | 14 | 01:00
29 | Bog-Sherpur | 50 | 18:00 | Jashore | 94 | 18:00 | Mirzapur | 15 | 18:00 | Saidpur | 90 | 18:00
30 | Bogura | 107 | 18:00 | Jhenaidah | 90 | 18:00 | Mithapukur | 28 | 18:00 | Satkhira | 81 | 18:00
31 | Borhanuddin | 35 | 21:00 | Joydebpur | 145 | 17:00 | Modern | 0 | 00:00 | Satmasjid | 71 | 13:00
32 | Brahmanbaria | 115 | 18:00 | Joypurhat | 42 | 18:30 | Mogbazar | 72.1 | 12:00 | Savar | 128 | 18:30
33 | Cantonment | 110 | 13:00 | Juldah | 18 | 16:00 | Mongla | 22 | 00:00 | SevenRings | 5.15 | 15:00
34 | Chandpur | 45 | 20:00 | KSRM | 28 | 19:00 | Motijheel | 25 | 12:00 | ShahCement | 18 | 00:00
35 | Chandraghona | 21 | 18:00 | Kabirpur | 233 | 18:30 | Munshiganj | 70 | 13:00 | Shahjadpur | 70 | 18:30
36 | Chapai | 47 | 12:00 | Kachua | 48 | 20:00 | Mymensingh | 154 | 18:00 | Shahjibazar | 91 | 18:00
37 | Charsaidpur | 19 | 01:00 | Kallyanpur | 70 | 18:00 | Naogaon | 88 | 18:30 | Shahmirpur | 37 | 16:00
38 | Chauddagram | 38 | 21:00 | Kalurghat | 28 | 12:00 | Narail | 35 | 18:30 | Shariatpur | 49 | 19:30
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-11-25 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 406 | 05:00 | 391 | 12:00 | Gopalganj | 412 | 04:00 | 399 | 13:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 396 | 03:00 | 381 | 16:00
| Bhulta | 414 | 02:00 | 403 | 12:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 410 | 18:30 | 400 | 12:00 | Payra | 418 | 02:00 | 410 | 18:00
| BIPTC | 409 | 19:30 | 399 | 17:00 | Rahanpur | 408 | 18:30 | 399 | 12:00
| Bogura | N/A | N/A | N/A | N/A | Rampal | 412 | 02:00 | 398 | 18:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 239 | 05:00 | 228 | 12:00 | Hasnabad | 236 | 00:00 | 229 | 12:00
| AKSML | 228 | 19:00 | 217 | 12:00 | Hathazari | 227 | 18:30 | 218 | 12:00
| Aminbazar | 236 | 00:00 | 227 | 12:00 | Ishurdi | 237 | 05:00 | 224 | 12:00
| Ashuganj | 237 | 19:00 | 234 | 05:00 | Jhenaidah | 237 | 05:00 | 222 | 12:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 238 | 03:00 | 228 | 15:00
| Baghabari | 230 | 02:00 | 222 | 13:00 | Keranigonj | 239 | 05:00 | 227 | 16:00
| Barapukuria | 228 | 18:30 | 222 | 23:00 | Khulna(S) | 244 | 02:00 | 231 | 18:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 243 | 03:00 | 237 | 16:00 | Maniknagar | 239 | 04:00 | 231 | 16:00
| Bheramara | 237 | 05:00 | 224 | 12:00 | Meghnaghat | 242 | 04:00 | 238 | 15:00
| Bhulta | 241 | 04:00 | 231 | 15:00 | Mirsorai | 229 | 22:00 | 220 | 13:00
| Bibiana | 235 | 04:00 | 228 | 11:00 | Rajshahi | 237 | 18:30 | 222 | 12:00
| BIPTC | 237 | 05:00 | 222 | 12:00 | Rampal | 238 | 02:00 | 229 | 16:00
| Bogura | 235 | 04:00 | 227 | 12:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 244 | 00:00 | 240 | 15:00 | Rampura | 238 | 06:00 | 230 | 12:00
| BSRM | 230 | 05:00 | 221 | 12:00 | Shikalbaha | 226 | 19:30 | 216 | 15:00
| Cumilla(N) | 235 | 18:30 | 223 | 15:00 | Shyampur | 239 | 05:00 | 229 | 16:00
| Fenchuganj | 236 | 04:00 | 230 | 10:00 | Siddhirganj | 241 | 04:00 | 233 | 12:00
| Ghorashal | 240 | 00:00 | 235 | 15:00 | Sirajgonj | 240 | 05:00 | 233 | 15:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 235 | 05:00 | 227 | 11:00
| GPH | 228 | 19:00 | 217 | 12:00 | Tongi | 236 | 04:00 | 225 | 15:00
| Haripur | 238 | 20:00 | 231 | 12:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 135 | 03:00 | 128 | 12:00 | Lalbag | 138 | 05:00 | 130 | 12:00
| Agargaon | 140 | 03:00 | 133 | 12:00 | Lalmonirhat | 134 | 09:00 | 127 | 19:30
| Agrabad | 134 | 19:00 | 126 | 15:00 | Madanganj | 135 | 18:30 | 130 | 12:00
| AKS | 132 | 19:00 | 126 | 12:00 | Madaripur | 132 | 00:00 | 129 | 16:00
| Aminbazar | 139 | 00:00 | 134 | 12:00 | Madartek | 135 | 05:00 | 128 | 12:00
| Amnura | 139 | 05:00 | 128 | 12:00 | Madunaghat | 135 | 05:00 | 128 | 12:00
| Ashuganj | 140 | 03:00 | 134 | 13:00 | Magura | 138 | 05:00 | 130 | 12:00
| Bagerhat | 133 | 04:00 | 124 | 18:00 | Mahasthangarh | 138 | 05:00 | 131 | 12:00
| Bakulia | 134 | 20:00 | 128 | 12:00 | Manikganj | 132 | 05:00 | 124 | 16:00
| Banani | 138 | 19:00 | 129 | 13:00 | Maniknagar | 137 | 03:00 | 131 | 12:00
| Bangabhaban | 136 | 00:00 | 131 | 12:00 | Matarbari | 132 | 04:00 | 108 | 18:00
| Barapukuria | 137 | 03:00 | 132 | 23:00 | Matuail | 135.7 | 04:00 | 130 | 16:00
| Barguna | 137 | 18:30 | 133 | 17:00 | Millgate | 138 | 01:00 | 128 | 16:00
| Barishal | 139 | 05:00 | 129 | 17:00 | Mirpur | 139 | 02:00 | 133 | 14:00
| Barishal-230 | 139 | 04:00 | 134 | 13:00 | Mirzapur | 134 | 02:00 | 128 | 16:00
| Baroaulia | 134 | 19:00 | 127 | 15:00 | Mithapukur | 137 | 18:30 | 130 | 12:00
| Baroirhat | 134 | 18:30 | 125 | 16:00 | MI_Cement | 137 | 04:00 | 130.6 | 16:00
| Bashundhara | 138 | 02:00 | 129 | 12:00 | Modern | 134 | 19:00 | 128 | 12:00
| BashundharaCement | 135 | 18:30 | 130 | 12:00 | Mogbazar | 135 | 01:00 | 130 | 11:00
| Beanibazar | 130 | 02:00 | 128 | 14:00 | Mongla | 132 | 09:00 | 125 | 18:00
| Benapole | 138 | 04:00 | 126 | 13:00 | Motijheel | 137 | 03:00 | 131 | 12:00
| Bhaluka | 134 | 03:00 | 128 | 15:00 | Munshiganj | 136 | 04:00 | 130 | 12:00
| Bhandaria | 136 | 09:00 | 130 | 22:00 | Mymensingh | 138 | 20:00 | 117 | 17:00
| Bhangura | 142 | 02:00 | 135 | 11:00 | Naogaon | 135 | 18:30 | 124 | 12:00
| Bheramara | 138 | 05:00 | 130 | 12:00 | Narail | 139 | 05:00 | 130 | 16:00
| Bheramara(GK) | 137 | 04:00 | 129 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 128 | 22:00 | 117 | 15:00 | Narshingdi | 132 | 06:00 | 120 | 15:00
| Bog-Sherpur | 139 | 02:00 | 131 | 12:00 | Natore | 138 | 05:00 | 129 | 12:00
| Bogura | 140 | 18:30 | 132 | 12:00 | Nawabganj | 137 | 04:00 | 130 | 12:00
| Bogura-230 | 139 | 18:30 | 132 | 12:00 | Netrakona | 135 | 18:30 | 128 | 06:00
| Brahmanbaria | 130 | 08:00 | 123 | 15:00 | New | 138 | 01:00 | 130 | 12:00
| Cantonment | 140 | 05:00 | 133 | 12:00 | Niamatpur | 134 | 02:00 | 122 | 12:00
| Chandpur | 137 | 18:30 | 124 | 11:00 | Noapara | 135 | 04:00 | 128 | 12:00
| Chandraghona | 134 | 05:00 | 120 | 15:00 | Pabna | 140 | 05:00 | 131 | 12:00
| Chapai | 133 | 04:00 | 130 | 11:00 | Palashbari | 135 | 04:00 | 130 | 07:00
| Charsaidpur | 136 | 02:00 | 130 | 16:00 | Panchagarh | 134 | 05:00 | 121 | 12:00
| Chauddagram | 134 | 04:00 | 126 | 12:00 | Patuakhali | 137 | 19:00 | 133 | 14:00
| Chhatak | 131 | 00:00 | 128 | 17:00 | Payra | 136 | 03:00 | 134 | 12:00
| Chowmuhani | 133 | 19:00 | 122 | 12:00 | PHP | 134 | 19:00 | 124 | 16:00
| Chuadanga | 137 | 03:00 | 127 | 12:00 | Postogola | 138 | 20:00 | 133 | 11:00
| Coxsbazar | 125 | 09:00 | 113 | 02:00 | Purbachal | 139 | 04:00 | 128 | 16:00
| Cumilla(N) | 139 | 18:30 | 130 | 16:00 | Purbasadipur | 133 | 04:00 | 123 | 23:00
| Cumilla(S) | 138 | 18:30 | 128 | 12:00 | Rahanpur | 134 | 04:00 | 132 | 01:00
| Daudkandi | 135 | 18:30 | 128 | 12:00 | Rahim | 135 | 01:00 | 132 | 12:00
| Dhaka | 135 | 04:00 | 128 | 12:00 | Rajbari | 134 | 02:00 | 128 | 12:00
| Dhamrai | 135 | 02:00 | 126 | 12:00 | Rajendrapur | 133 | 05:00 | 122 | 15:00
| Dhanmondi | 136.5 | 05:00 | 132 | 12:00 | Rajshahi | 137 | 02:00 | 129 | 12:00
| Dohazari | 134 | 20:00 | 127 | 14:00 | Rajshahi-230 | 138 | 05:00 | 127 | 13:00
| Faridpur | 134 | 03:00 | 128 | 15:00 | Ramganj | 135 | 19:00 | 122 | 12:00
| Fatullah | 139 | 00:00 | 132 | 12:00 | Rampur | 134 | 05:00 | 127 | 13:00
| Fenchuganj | 134 | 06:00 | 131 | 15:00 | Rampura | 136 | 03:00 | 130 | 12:00
| Feni | 134 | 18:30 | 125 | 16:00 | Rangamati | 134 | 19:00 | 128 | 14:00
| Ghorashal | 142 | 18:00 | 135 | 15:00 | Rangpur | 134 | 04:00 | 127 | 17:00
| Goalpara | 136 | 03:00 | 129 | 18:00 | Ruppur | 138 | 00:00 | 132 | 12:00
| Gollamari | 135 | 01:00 | 129 | 12:00 | Saidpur | 134 | 04:00 | 126 | 23:00
| Gopalganj | 133 | 05:00 | 127 | 17:00 | Satkhira | 135 | 04:00 | 124 | 18:00
| Gopalganj-400 | 132 | 02:00 | 128 | 12:00 | Satmasjid | 139 | 05:00 | 132 | 16:00
| Gulshan | 135 | 06:00 | 129 | 12:00 | Savar | 138 | 01:00 | 132 | 12:00
| Halishahar | 135 | 20:00 | 126 | 15:00 | SevenRings | 143 | 19:00 | 135 | 11:00
| Haripur | 135 | 01:00 | 132 | 12:00 | ShahCement | 136 | 02:00 | 130 | 16:00
| HaripurSBU | 135 | 01:00 | 132 | 12:00 | Shahjadpur | 145 | 04:00 | 138 | 16:00
| Hasnabad | 138 | 01:00 | 133 | 11:00 | Shahjibazar | 133 | 14:00 | 124 | 15:00
| Hathazari | 135 | 07:00 | 129 | 02:00 | Shahmirpur | 134 | 19:00 | 128 | 14:00
| Ishurdi | 140 | 04:00 | 132 | 12:00 | Shariatpur | 134 | 05:00 | 128 | 15:00
| Jaldhaka | 133 | 04:00 | 125 | 23:00 | Sherpur | 137 | 20:00 | 121 | 00:00
| Jamalpur | 140 | 20:00 | 123 | 07:00 | Shikalbaha | 124 | 19:00 | 117 | 12:00
| Jashore | 135 | 03:00 | 127 | 13:00 | Shikalbaha-230 | 136 | 19:30 | 129 | 15:00
| Jhenaidah | 138 | 03:00 | 130 | 12:00 | Shitalakhya | 137 | 04:00 | 130.6 | 16:00
| Jhenaidah-230 | 140 | 05:00 | 131 | 12:00 | Sholosohor | 134 | 05:00 | 128 | 12:00
| Joydebpur | 142 | 22:00 | 131 | 12:00 | Shyampur | 137 | 20:00 | 131 | 12:00
| Joypurhat | 136 | 01:00 | 121 | 12:00 | Shyampur-230 | 138 | 05:00 | 131 | 16:00
| Juldah | 134 | 18:30 | 129 | 12:00 | Siddhirganj | 136 | 06:00 | 132 | 11:00
| Kabirpur | 135 | 00:00 | 125 | 15:00 | Sirajganj | 139 | 00:00 | 130 | 12:00
| Kachua | 138 | 18:30 | 125 | 13:00 | Sonargaon | 135 | 05:00 | 130 | 23:00
| Kaliakoir | 136 | 04:00 | 128 | 15:00 | Sreemongol | 132 | 08:00 | 127 | 12:00
| Kallyanpur | 139 | 01:00 | 133 | 16:00 | Sreepur | 135 | 05:00 | 130 | 11:00
| Kalurghat | 135 | 20:00 | 128 | 11:00 | Srinagar | 138 | 04:00 | 130 | 12:00
| Kamrangirchar | 139 | 03:00 | 130 | 16:00 | SSM | 138 | 07:00 | 130 | 12:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 130 | 08:00 | 127 | 17:00
| Kazla | 137 | 05:00 | 131 | 15:00 | Sylhet | 132 | 03:00 | 129 | 15:00
| Keranigonj | 138 | 03:00 | 130 | 16:00 | Sylhet-132 | 131 | 03:00 | 130 | 00:00
| Khagrachori | 134 | 19:00 | 128 | 12:00 | Tangail | 134 | 20:00 | 127 | 07:00
| Khulna | 132 | 00:00 | 127 | 18:00 | Thakurgaon | 134 | 05:00 | 122 | 12:00
| Khulna(S) | 136 | 03:00 | 129 | 12:00 | TK | 135 | 19:00 | 128 | 16:00
| Khulshi | 133 | 19:00 | 126 | 15:00 | Tongi | 140 | 04:00 | 131 | 15:00
| Kishoreganj | 135 | 19:00 | 125 | 17:00 | Ullon | 134 | 02:00 | 128 | 12:00
| Kodda | 140 | 20:00 | 122 | 16:00 | Uttara | 138 | 05:00 | 128 | 16:00
| KSRM | 134 | 19:00 | 127 | 12:00 | UttaraNew | 138 | 05:00 | 128 | 16:00
| Kulaura | 133 | 08:00 | 130 | 15:00 | Zigatola | 137 | 03:00 | 130 | 13:00
| Kurigram | 133 | 05:00 | 126 | 17:00
| Kushtia | 136 | 00:00 | 130 | 12:00

## L-Curve
Date | 2023-11-25
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 390 | 4985 | 3531 | 8516 |  |  |  | QF-LDC-11
0:30 | 400 | 4715 | 3353.5 | 8068.5 | Date: | 2023-11-25
1:00 | 410 | 4445 | 3176 | 7621
1:30 | 425 | 4311.5 | 3072 | 7383.5
2:00 | 440 | 4178 | 2968 | 7146
2:30 | 445 | 4110 | 2963.5 | 7073.5 | [5 empty] | Gen. at Eve. Peak | 10583 | 10583 MW (18:00 )
3:00 | 450 | 4042 | 2959 | 7001 | [6 empty] | 18:00
3:30 | 455 | 3981 | 2938.5 | 6919.5 | [5 empty] | Gen. at Day Peak | 8140 | 8140 MW (12:00 )
4:00 | 460 | 3920 | 2918 | 6838 | [6 empty] | 12:00
4:30 | 455 | 3877 | 2892 | 6769 | [5 empty] | Highest Generation | 10583
5:00 | 450 | 3834 | 2866 | 6700 | [6 empty] | 18:00
5:30 | 465 | 3924.5 | 2909 | 6833.5
6:00 | 480 | 4015 | 2952 | 6967
6:30 | 445 | 4266.5 | 3029 | 7295.5
7:00 | 410 | 4518 | 3106 | 7624
7:30 | 365 | 4631.5 | 3174.5 | 7806
8:00 | 320 | 4745 | 3243 | 7988
8:30 | 395 | 4495.5 | 3193 | 7688.5
9:00 | 470 | 4246 | 3143 | 7389
9:30 | 525 | 4238 | 3173 | 7411
10:00 | 580 | 4230 | 3203 | 7433
10:30 | 585 | 4320.5 | 3324.5 | 7645
11:00 | 590 | 4411 | 3446 | 7857
11:30 | 565 | 4565 | 3433.5 | 7998.5
12:00 | 540 | 4719 | 3421 | 8140
12:30 | 515 | 4912 | 3441 | 8353
13:00 | 490 | 5105 | 3461 | 8566
13:30 | 530 | 4969 | 3489.5 | 8458.5
14:00 | 570 | 4833 | 3518 | 8351
14:30 | 540 | 4808 | 3501 | 8309
15:00 | 510 | 4783 | 3484 | 8267
15:30 | 510 | 4881.5 | 3510 | 8391.5
16:00 | 510 | 4980 | 3536 | 8516
16:30 | 440 | 5146.5 | 3562 | 8708.5
17:00 | 370 | 5313 | 3588 | 8901
17:30 | 350 | 5765.5 | 3976.5 | 9742
18:00 | 330 | 6218 | 4365 | 10583
18:30 | 280 | 6245.5 | 4194.5 | 10440
19:00 | 230 | 6273 | 4024 | 10297
19:30 | 232 | 6110 | 3993 | 10103
20:00 | 264 | 5929 | 3989 | 9918 |  |  |  | Executive Engineer
20:30 | 242 | 5831.5 | 3927.5 | 9759 |  |  |  | Network Operation Division
21:00 | 220 | 5734 | 3866 | 9600
21:30 | 218 | 5688 | 3744 | 9432
22:00 | 216 | 5642 | 3622 | 9264 |  |  |  |  | Page 6 of 7
22:30 | 259 | 5456.5 | 3604 | 9060.5
23:00 | 302 | 5271 | 3586 | 8857
23:30 | 346 | 5128 | 3558.5 | 8686.5
24:00 | 390 | 4985 | 3531 | 8516
10583 MW (18:00 )
8140 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-11-25 |  | Energy |  | 202699852
[15 empty] | 43793 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3394 | 447 | 1618 | 0 | 97 | 2810 | 46 | 0 | 0 | 92 | 0 | 12 | 0
0:30 | 3241 | 447 | 1487 | 0 | 57 | 2690 | 46 | 0 | 0 | 93 | 0 | 7.5 | 0 |  |  | Date: | 43793
1:00 | 3088 | 447 | 1356 | 0 | 17 | 2570 | 46 | 0 | 0 | 94 | 0 | 3 | 0
1:30 | 3049 | 446.5 | 1303 | 0 | 17 | 2429.5 | 46 | 0 | 0 | 89 | 0 | 3.5 | 0 | [9 empty] | Total Energy | 202.6999 | 202.6999 | Total Energy Gen 202.700 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 202.700 MKWHr
2:00 | 3010 | 446 | 1250 | 0 | 17 | 2289 | 46 | 0 | 0 | 84 | 0 | 4 | 0 | [9 empty] | Energy not Served | 0 | 0
2:30 | 2944.5 | 446.5 | 1251.5 | 0 | 17 | 2282 | 46 | 0 | 0 | 81 | 0 | 5 | 0 | [9 empty] | Energy Requirement | 202.6999 | 202.6999
3:00 | 2879 | 447 | 1253 | 0 | 17 | 2275 | 46 | 0 | 0 | 78 | 0 | 6 | 0
3:30 | 2822.5 | 446.5 | 1222.5 | 0 | 17 | 2275 | 46 | 0 | 0 | 81 | 0 | 9 | 0 | [8 empty] | Shortage
4:00 | 2766 | 446 | 1192 | 0 | 17 | 2275 | 46 | 0 | 0 | 84 | 0 | 12 | 0
4:30 | 2727 | 446.5 | 1160 | 0 | 17 | 2273.5 | 46 | 0 | 0 | 87 | 0 | 12 | 0
5:00 | 2688 | 447 | 1128 | 0 | 17 | 2272 | 46 | 0 | 0 | 90 | 0 | 12 | 0
5:30 | 2750.5 | 447 | 1192 | 0 | 27 | 2270 | 46 | 0 | 0 | 87 | 0 | 14 | 0
6:00 | 2813 | 447 | 1256 | 0 | 37 | 2268 | 46 | 0 | 0 | 84 | 0 | 16 | 0
6:30 | 2996.5 | 447 | 1322.5 | 0 | 83.5 | 2287.5 | 46 | 0 | 0 | 83 | 12.5 | 17 | 0 | [7 empty] | Coal
7:00 | 3180 | 447 | 1389 | 0 | 130 | 2307 | 46 | 0 | 0 | 82 | 25 | 18 | 0
7:30 | 3213.5 | 423.5 | 1416.5 | 0 | 142 | 2389 | 46 | 0 | 0 | 87 | 74 | 14.5 | 0 | [6 empty] | Oil
8:00 | 3247 | 400 | 1444 | 0 | 154 | 2471 | 46 | 0 | 0 | 92 | 123 | 11 | 0
8:30 | 3075 | 387.5 | 1307.5 | 0 | 157.5 | 2432.5 | 46 | 0 | 0 | 94 | 179 | 9.5 | 0
9:00 | 2903 | 375 | 1171 | 0 | 161 | 2394 | 46 | 0 | 0 | 96 | 235 | 8 | 0
9:30 | 2874 | 382 | 1183.5 | 0 | 165 | 2379.5 | 46 | 0 | 1.5 | 100 | 271.5 | 8 | 0
10:00 | 2845 | 389 | 1196 | 0 | 169 | 2365 | 46 | 0 | 3 | 104 | 308 | 8 | 0
10:30 | 2927.5 | 418 | 1250.5 | 0 | 183.5 | 2371 | 46 | 0 | 1.5 | 107 | 334.5 | 5.5 | 0
11:00 | 3010 | 447 | 1305 | 0 | 198 | 2377 | 46 | 0 | 0 | 110 | 361 | 3 | 0
11:30 | 3060.5 | 447 | 1330.5 | 0 | 204.5 | 2430.5 | 46 | 0 | 0 | 113 | 364.5 | 2 | 0
12:00 | 3111 | 447 | 1356 | 0 | 211 | 2484 | 46 | 0 | 0 | 116 | 368 | 1 | 0
12:30 | 3209.5 | 447 | 1440 | 0 | 231 | 2521 | 46 | 0 | 0 | 114 | 344 | 0.5 | 0
13:00 | 3308 | 447 | 1524 | 0 | 251 | 2558 | 46 | 0 | 0 | 112 | 320 | 0 | 0
13:30 | 3308 | 447 | 1524 | 0 | 251 | 2558 | 46 | 0 | 0 | 112 | 320 | 0 | 0
14:00 | 3308 | 447 | 1524 | 0 | 251 | 2558 | 46 | 0 | 0 | 112 | 320 | 0 | 0
14:30 | 3222.5 | 447 | 1463 | 0 | 214.5 | 2654 | 46 | 0 | 0 | 112 | 257.5 | 0 | 0
15:00 | 3137 | 447 | 1402 | 0 | 178 | 2750 | 46 | 0 | 0 | 112 | 195 | 0 | 0
15:30 | 3187 | 447 | 1453.5 | 0 | 270 | 2740.5 | 46 | 0 | 0 | 108 | 137 | 2.5 | 0
16:00 | 3237 | 447 | 1505 | 0 | 362 | 2731 | 46 | 0 | 0 | 104 | 79 | 5 | 0
16:30 | 3183.5 | 447 | 1507.5 | 0 | 586 | 2793 | 46 | 0 | 0 | 100.5 | 41 | 4 | 0
17:00 | 3130 | 447 | 1510 | 0 | 810 | 2855 | 46 | 0 | 0 | 97 | 3 | 3 | 0
17:30 | 3206 | 400.5 | 1636.5 | 0 | 1162.5 | 3169 | 46 | 0 | 16 | 100.5 | 1.5 | 3.5 | 0
18:00 | 3282 | 354 | 1763 | 0 | 1515 | 3483 | 46 | 0 | 32 | 104 | 0 | 4 | 0
18:30 | 3257 | 281.5 | 1694.5 | 0 | 1578.5 | 3440 | 46 | 0 | 40 | 99 | 0 | 3.5 | 0
19:00 | 3232 | 209 | 1626 | 0 | 1642 | 3397 | 46 | 0 | 48 | 94 | 0 | 3 | 0
19:30 | 3180 | 209 | 1602 | 0 | 1560 | 3355 | 46 | 0 | 48 | 102 | 0 | 1 | 0
20:00 | 3174 | 301 | 1586 | 0 | 1412 | 3249 | 46 | 0 | 48 | 100 | 0 | 2 | 0
20:30 | 3173 | 374 | 1583 | 0 | 1297 | 3149.5 | 46 | 0 | 32 | 102 | 0 | 2.5 | 0
21:00 | 3172 | 447 | 1580 | 0 | 1182 | 3050 | 46 | 0 | 16 | 104 | 0 | 3 | 0
21:30 | 3168.5 | 446.5 | 1587 | 0 | 1068.5 | 2995 | 46 | 0 | 16 | 102 | 0 | 2.5 | 0
22:00 | 3165 | 446 | 1594 | 0 | 955 | 2940 | 46 | 0 | 16 | 100 | 0 | 2 | 0
22:30 | 3247.5 | 446.5 | 1626 | 0 | 675 | 2909 | 46 | 0 | 8 | 98 | 0 | 4.5 | 0
23:00 | 3330 | 447 | 1658 | 0 | 395 | 2878 | 46 | 0 | 0 | 96 | 0 | 7 | 0
23:30 | 3362 | 447 | 1638 | 0 | 246 | 2844 | 46 | 0 | 0 | 94 | 0 | 9.5 | 0 |  |  | Max Temp. in Dhaka |  | 30.1°C
24:00 | 3394 | 447 | 1618 | 0 | 97 | 2810 | 46 | 0 | 0 | 92 | 0 | 12 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 202.700 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 202.700 MKWHr
Note on W13: Author:

## Generation
g | 2023-11-25
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1115040
2 | Karnaphuli Hydro PP Unit-4 & 5 | [7 empty] | 0
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 11 |  | 17 | 17 | 17 | 17 | 17 |  |  | 81142
| Teknaf 20MW PP (Solartech) | [6 empty] | 4 | 9 | 15 | 18 | 20 | 20 | 18 | 15 | 11 | 6 | 0 | [9 empty] | 136350
6 | Sikalbaha 225MW CCPP (Gas) | 215 | 201 | 177 | 177 | 177 | 187 | 215 | 213 | 214 | 218 | 215 | 216 | 216 | 215 | 215 | 214 | 213 | 214 |  | 214 | 213 | 213 | 213 | 213 | 214 | 213 | 5006317
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [26 empty] | 0
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [15 empty] | 5 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 150545
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 280 | 280 | 250 | 250 | 250 | 250 | 321 | 336 | 280 | 240 | 280 | 280 | 335 | 260 | 260 | 290 | 300 | 335 |  | 280 | 285 | 280 | 280 | 280 | 334 | 335 | 6931994
18 | Kodda 300 MW PP Unit-2 (Summit) | [16 empty] | 10 | 40 |  | 45 | 45 | 45 | 45 |  |  |  | 278509
19 | Ashuganj 195 MW PP (APSCL-United) | 0 |  |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 55 | 102 |  | 102 | 55 | 55 | 55 | 55 | 55 | 55 | 602182
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4362750
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 375 | 300 | 295 | 285 | 285 | 285 | 303 | 368 | 351 | 326 | 328 | 400 | 439 | 442 | 440 | 405 | 405 | 500 |  | 470 | 450 | 400 | 405 | 405 | 405 | 403 | 9065453
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 10 | 10 | 10 | 10 | 10 | 10 | 37 | 47 | 47 | 47 | 47 | 47 | 45 | 45 | 45 | 45 | 45 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 873504
33 | Ashuganj 225 MW CCPP
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 265 | 280 | 310 | 310 | 285 | 280 | 270 | 345 | 280 | 280 | 295 | 340 | 304 | 280 |  | 280 | 280 | 280 | 280 | 280 | 315 | 310 | 7328100
| Ashuganj 420 MW CCPP(East) | 350 | 350 | 285 | 240 | 240 | 300 | 340 | 385 | 250 | 250 | 250 | 300 | 393 | 350 | 350 | 350 | 350 | 395 |  | 393 | 350 | 350 | 350 | 350 | 350 | 393 | 8040000
35 | Ashuganj 55 MW PP (Precision) | 16 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 36 | 41 | 41 | 41 | 39 | 38 | 37 | 41 | 42 |  | 42 | 42 | 43 | 41 | 43 | 43 | 43 | 708960
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 352 | 352 | 340 | 304 | 304 | 328 | 349 | 372 | 352 | 333 | 311 | 363 | 404 | 398 | 350 | 352 | 351 | 392 |  | 401 | 382 | 381 | 381 | 382 | 386 | 397 | 8753150
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 170 | 170 | 170 | 170 | 170 | 225 | 225 | 170 | 170 | 170 | 170 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4838600
41 | Haripur 360 MW CCPP(HPL) | 307 | 268 | 267 | 246 | 247 | 278 | 309 | 308 | 231 | 230 | 231 | 291 | 333 | 272 | 271 | 272 | 271 | 341 |  | 287 | 277 | 277 | 277 | 277 | 300 | 292 | 6748000
42 | RPCL 210MW CCPP | 104 | 105 | 105 | 72 | 72 | 73 | 104 | 104 | 86 | 85 | 85 | 84 | 99 | 95 | 95 | 96 | 96 | 94 |  | 94 | 94 | 95 | 94 | 84 | 84 | 87 | 2138880
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 3 | 17 | 33 | 43 | 49 | 47 | 48 | 41 | 29 | 12 | 0 | [9 empty] | 325380
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1015000
45 | Fenchugonj CCPP Phase-2 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 26 | 26 | 26 | 26 | 26 | 27 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 28 | 672600
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86 MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 37 | 37 | 37 | 70 | 78 | 78 | 78 | 40 | 80 | 43 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 956160
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 202 | 202 | 202 | 203 | 203 | 203 | 203 | 203 | 199 | 199 | 200 | 196 | 196 | 196 | 196 | 195 | 195 | 197 |  | 197 | 198 | 199 | 198 | 199 | 199 | 203 | 5040900
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 410000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 253980
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 2 | 2 | 2 | [5 empty] | 3 | 5 | 5 | 5 | 5 | 5 | 5 | 76432
55 | Fenchugonj 51 MW PP (Barakatullah) | [26 empty] | 0
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 373056
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 270 | 275 | 285 | 270 | 290 | 300 | 280 | 270 | 280 | 310 | 290 | 290 | 270 | 300 | 315 | 300 | 305 |  | 260 | 290 | 270 | 270 | 280 | 280 | 290 | 6993000
| Bibiyana South 400 MW | 370 | 340 | 340 | 340 | 340 | 340 | 380 | 380 | 380 | 390 | 400 | 390 | 400 | 360 | 360 | 360 | 390 | 400 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 9053700
58 | Nababganj 55 MW PP (Southern power ) | [17 empty] | 17 |  | 17 | 17 | 35 | 35 | 35 |  |  | 135784
59 | Tangail Palli Power Gen 22 MW | [16 empty] | 5 | 6 |  | 6 | 6 | 6 | 6 | 6 |  |  | 38400
60 | Barabkunda 22 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 280224
61 | Narshingdi 22 MW PP (Doreen) | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  |  | 10 | 12 | 12 | 10 | 10 | 14 | 17 |  |  |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 265464
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 94 | 84 | 78 | 84 | 90 | 84 | 82 | 92 | 96 | 104 | 110 | 116 | 112 | 118 | 112 | 104 | 97 | 104 |  | 94 | 102 | 100 | 104 | 100 | 96 | 92 | 2359680
64 | Malancha, Ctg. EPZ (United) | 32 | 32 | 32 | 32 | 32 | 31 | 29 | 10 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 3 | 5 | 0 | 3 | 5 | 8 | 293280
65 | Feni 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  |  |  | 7 | 14 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 281988
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 221940
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 33 | 8 | 8 | 17 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 736800
68 | Cumilla 25 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 6 | 6 | 6 | 6 | 6 | 6 | 8 | 6 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 187080
69 | Summit Ashulia | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 480000
70 | Summit Madhabdi | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  |  |  | 11 | 17 | 17 | 17 | 17 | 17 | 12 |  | 17 | 17 | 17 | 17 | 17 | 18 | 18 | 347760
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  |  | 25 |  | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 635700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 684900
73 | Ghorashal 108 MW PP (Regent) | 0 | [5 empty] | 10 | 26 | 39 | 39 | 39 | 39 | 39 | 39 | 36 | 34 | 39 | 70 |  | 67 | 67 | 67 | 67 | 70 | 67 | 67 | 808136
| Feni Lanka Power | [16 empty] | 17 | 42 |  | 17 | 17 | 17 | 17 |  |  |  | 123120
| Chowmuhani 113 MW | [11 empty] | 8 | 9 | 9 | 9 | 9 | 31 | 46 |  | 48 | 48 | 48 | 49 | 48 |  |  | 346080
| Manikgonj 162MW PP(MPGL) | [16 empty] | 35 | 72 |  | 72 | 72 | 72 | 72 | 53 |  |  | 354240
77 | Siddhirganj 100 PP(Dutch Bangla) | [16 empty] | 8 | 15 |  | 35 | 8 | 9 |  |  |  |  | 60250
78 | Gazipur 52 MW PP | [13 empty] | 8 | 8 | 8 | 8 | 20 |  | 25 | 25 | 25 | 25 | 25 |  |  | 165600
79 | Kodda 150 MW PP | [17 empty] | 32 |  | 48 | 48 | 48 | 16 | 16 |  |  | 138720
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [17 empty] | 31 |  | 8 | 8 | 8 | 8 |  |  |  | 95434
| Gazipur 100 MW PP | [10 empty] | 17 | 17 | 35 | 35 | 35 | 35 | 88 | 88 |  | 88 | 88 | 88 | 88 | 88 | 17 |  | 692160
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 1 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 24719
| Jodiac Power | [15 empty] | 4 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 |  | 142035
| Karnaphuli Power Ltd. | [11 empty] | 10 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 231672
82 | Madanganj 102 PP(Summit) | [17 empty] | 10 |  | 28 | 17 | 24 | 17 | 17 | 5 |  | 84127
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | [16 empty] | 4 | 13 |  | 19 | 9 | 9 |  |  |  |  | 49920
| Meghnaghat 104 MW PP (OPCL) | [16 empty] | 17 | 68 |  | 50 | 32 | 17 | 17 |  |  |  | 166080
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [15 empty] | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 91440
92 | Fenchuganj 44 MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 31 | 10 | 10 | 0 | 0 | 0 |  |  |  |  | 35 |  | 44 | 44 | 44 | 44 | 41 | 41 | 41 | 361224
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5 | 5 | 5 | 24 | 43 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 5 | 727788
94 | Gagnagar 102 MW PP (Digital Power) | [26 empty] | 0
95 | Patenga 50MW PP (Baraka) | [16 empty] | 10 | 19 |  | 20 | 20 | 20 | 19 | 20 | 20 | 9 | 131520
96 | Chattogram 108 MW PP (ECPV) | [26 empty] | 0
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [16 empty] | 6 | 15 |  | 22 | 25 | 25 | 15 | 15 |  |  | 111083
100 | Manikganj 55 MW PP (Northern) | [15 empty] | 17 | 17 | 35 |  | 35 | 35 | 35 |  |  |  |  | 139998
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [9 empty] | 11950
103 | Kamalaghat 54 MW PP(Banco Energy) | [16 empty] | 35 | 35 |  | 35 | 35 | 35 |  |  |  |  | 129600
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [6 empty] | 5 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 55 | 110 | 112 |  | 112 | 112 | 121 | 65 | 65 | 65 | 25 | 878400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [21 empty] | 1 | 23 | 25 |  |  | 66672
115 | Juldah 100 MW PP Unit-3 (Acorn) | [15 empty] | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 |  | 104640
116 | Chandpur 200 MW (Desh energy) | [11 empty] | 10 | 19 | 17 | 17 | 19 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 233760
117 | Ashuganj 150 MW PP (Midland) | [15 empty] | 2 | 15 | 36 |  | 85 | 96 | 98 | 108 | 117 | 86 |  | 553672
118 | Bibiyana-III 400 MW CCPP | 388 | 353 | 353 | 353 | 315 | 330 | 401 | 401 | 352 | 353 | 397 | 402 | 399 | 354 | 357 | 358 | 358 | 402 |  | 400 | 402 | 400 | 400 | 401 | 404 | 401 | 8971000
| Jamalpur 115 MW PP (United) | [11 empty] | 8 | 8 | 8 | 8 | 8 | 20 | 56 |  | 56 | 35 | 35 | 35 | 35 | 8 | 0 | 314400
| Anwara 300 MW PP (United) | [15 empty] | 15 | 45 | 80 |  | 230 | 230 | 100 | 65 | 65 | 30 |  | 634800
| Juldah unit-2 (Acorn) | [26 empty] | 0
| Anlima Energy Ltd. | [11 empty] | 12 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 223309
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  |  | 416880
| Spectra Solar Plant Ltd. | [6 empty] | 2 | [19 empty] | 6641
| Chandpur 115(Doreen) | [16 empty] | 14 | 60 |  | 72 | 72 | 72 | 72 | 72 | 38 |  | 417600
| Kanchan Purbachal Power Generation Ltd. | [7 empty] | 0 | 15 | 23 | 35 |  |  |  |  | 18 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 17 |  | 370800
| Mirsharai 150 MW (Oil) | [9 empty] | 3
| Mirsharai 150 MW (Gas) | [10 empty] | 8 | 18 | 18 | 18 | 27 | 24 | 15 | 17 | [8 empty] | 135491
| Cox's Bazar Wind | 3 | 4 | 6 | 12 | 12 | 16 | 18 | 11 | 8 | 8 | 3 | 1 | 0 | 0 | 0 | 5 | 3 | 4 |  | 3 | 1 | 2 | 3 | 2 | 7 | 12 | 138240
Matarbari 2*600 MW (CPGCL)
120 | Eastern Zone Total | 4445 | 4178 | 4042 | 3920 | 3834 | 4015 | 4518 | 4745 | 4246 | 4230 | 4411 | 4719 | 5105 | 4833 | 4783 | 4980 | 5313 | 6218 |  | 6273 | 6110 | 5929 | 5734 | 5642 | 5271 | 4985 | 117931885
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [17 empty] | 16 |  | 16 | 32 | 16 | 16 |  |  |  | 82560
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [15 empty] | 5 | 17 | 17 |  | 17 | 17 | 17 | 17 |  |  |  | 96240
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 5 | 26 | 54 | 63 | 74 | 74 | 70 | 57 | 34 | 15 | 1 | [9 empty] | 472320
131 | Rampal 1320 MW (BIFPCL) | 352 | 352 | 350 | 353 | 354 | 353 | 353 | 352 | 352 | 351 | 351 | 352 | 352 | 352 | 352 | 350 | 402 | 604 |  | 617 | 622 | 624 | 438 | 408 | 351 | 355 | 9461818
132 | United Payra Power Ltd. | [15 empty] | 8 | 17 | 45 |  | 82 | 100 | 75 | 17 |  |  |  | 267600
133 | Bhola Nutan Biddut BD LTD (GAS) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 109 | 109 | 109 | 110 | 109 | 109 | 110 | 2622000
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [26 empty] | 0
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 150 | 150 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 163 | 3806400
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 130 | 50 | 50 | 50 | 110 | 130 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 120 | 130 | 1508000
140 | Bhola 33 MW PP (Venture) | 16 | 15 | 14 | 14 | 14 | 14 | 13 | 14 | 12 | 11 | 11 | 14 | 16 | 15 | 13 | 13 | 15 | 18 |  | 19 | 19 | 20 | 20 | 20 | 18 | 18 | 357700
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [26 empty] | 0
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 447 | 446 | 447 | 446 | 447 | 447 | 447 | 400 | 375 | 389 | 447 | 447 | 447 | 446 | 447 | 447 | 447 | 354 |  | 209 | 209 | 301 | 447 | 446 | 447 | 447 | 10091636
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 700 | 500 | 500 | 500 | 500 | 500 | 520 | 620 | 560 | 550 | 560 | 600 | 640 | 760 | 830 | 850 | 920 | 1190 |  | 1120 | 1100 | 1040 | 1020 | 940 | 930 | 900 | 19894500
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4181900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 29700
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 350 | 350 | 350 | 300 | 250 | 320 | 350 | 350 | 250 | 250 | 300 | 300 | 350 | 300 | 300 | 350 | 350 | 414 |  | 370 | 370 | 370 | 370 | 370 | 414 | 414 | 8278327
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [6 empty] | 5 | 5 | 130644
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 8 | 8 | 8 |  |  |  |  | 17813
170 | Chapainawabganj 100 MW Peaking PP | [26 empty] | 0
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [15 empty] | 15 | 35 | 69 |  | 70 | 70 | 70 | 70 | 35 |  |  | 426336
172 | Confidence Power Bogura Unit-1 113 MW | [15 empty] | 30 | 35 | 100 |  | 35 | 35 | 35 | 35 | 35 |  |  | 344064
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [5 empty] | 20 | 108 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 34 | 34 | 34 | 111 |  | 58 | 34 | 34 | 34 | 22 |  |  | 1319798
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 5 | 5 | 3 | 1 | 0 | [9 empty] | 34858
178 | Energypac Power Venture Thakurgaon Ltd. | [16 empty] | 17 | 70 |  | 54 | 35 | 35 | 35 |  |  |  | 271872
| Intraco Solar 30 MW | [6 empty] | 2 | 11 | 18 | 28 | 33 | 34 | 31 | 25 | 16 | 6 | 0 | [9 empty] | 204305
| Adani Power Jharkhanda Ltd | 823 | 817 | 820 | 827 | 823 | 820 | 821 | 821 | 821 | 828 | 828 | 822 | 817 | 818 | 818 | 816 | 818 | 819 |  | 820 | 813 | 815 | 817 | 817 | 822 | 819 | 19783636
178 | Teesta Solar Limited | [6 empty] | 9 | 56 | 107 | 142 | 169 | 177 | 138 | 146 | 97 | 37 | 2 | [9 empty] | 1083940