## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:October 2023
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2023-10-01 |  | 2023-09-01 |  | 2022-10-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 14356 | 2023-10-11 | 14938 | 2023-09-16 | 12901 | 2022-10-10 | 15648 | 2023-04-19
|  |  | 20:00 |  | 21:00 |  | 20:00 |  | 21:00
2 | Minimum Generation (MW) | 8008 | 2023-10-06 | 9737 | 2023-09-22 | 2828 | 2022-10-25 | - | -
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 14356 | 2023-10-11 | 14938 | 2023-09-16 | 12901 | 2022-10-10 | 15648 | 2023-04-19
|  |  | 20:00 |  | 21:00 |  | 20:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 12530 | 2023-10-01 | 13849 | 2023-09-17 | 11274 | 2022-10-01 | 13415 | 2023-04-19
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 14470 | 2023-10-30 | 15370 | 2023-09-30 | 14300 | 2022-10-31 | 16096 | 2023-04-19
|  |  | 18:00 |  | 20:00 |  | 20:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 12963.6129 |  | 14065.4 |  | 11594.5161 |  | - | -
7 | Average Generation (MW) at Day Peak | 11283.7097 |  | 12351.2667 |  | 9760.6774 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 920 | 2023-10-11 | 940 | 2023-09-25 | 975 | 2022-10-04 | 956 | 27/3/2019
|  |  | 4:30 |  | 24':30 |  | 14:30 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 160 | 2023-10-01 | 174 | 2023-09-13 | 172 | 2022-10-10 | 194 | 12/06/19
|  |  | 15:00 |  | 23:00 |  | 19:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 244 | 2023-10-12 | 822 | 2023-09-05 | 4395 | 2022-10-04 | 4395 | 04/10/2022
|  |  | 19:00 |  | 21:00 |  | 21:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 13944 | 2023-10-12 | 14489 | 2023-09-05 | 8431 | 44838 | 13200 | 04/10/2022
|  | - | 19:30 | - | 21:00 | - | 0.875 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2023-10-13 | 0 | 2023-09-21 | 0 | 44858 | - | -
|  |  | 20:00 |  | 19:30 |  | 21:00 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 12852 | 2023-10-13 | 12861 | 2023-09-21 | 5652 | 2022-10-24 | - | -
|  |  | 20:00 |  | 19:30 |  | 21:00 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 469 | 2023-10-23 | 763 | 2023-09-06 | 1937 | 44844 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 11359 | 2023-10-23 | 12621 | 2023-09-06 | 10256 | 44844 | - | -
|  |  | 12:00 |  | 12:00 |  | 10:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2023-10-13 | 0 | 2023-09-21 | 0 | 44858 | - | -
|  |  | 12:00 |  | 12:00 |  | 9:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 10593 | 2023-10-13 | 11696 | 2023-09-21 | 8146 | 44858 | - | -
|  |  | 12:00 |  | 12:00 |  | 9:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 17 |  | 12 |  | 25 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 8 |  | 19 |  | 27 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 2096.5113 |  | 1674.6479 |  | 1483.1714 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 34.051 |  | 43.3331 |  | 135.2896 |  | - | -
22 | Net Generation of BPDB (MKWH) | 2062.4603 |  | 1631.3147 |  | 1347.8818 |  | - | -
23 | Net Generation of IPP (MKWH) | 4679.0652 |  | 4590.0003 |  | 4808.0999 |  | - | -
24 | Net Generation of REB (MKWH) | 117.5706 |  | 107.426 |  | 114.4586 |  | - | -
24 | Net Generation of Rental Power Plant (MKWH) | 198.4182 |  | 306.0719 |  | 308.6068 |  | - | -
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 7057.5143 |  | 6634.8128 |  | 6579.047 |  | 7842.9924 | April'22
26 | Energy Generation by Gas (MKWH) | 4220.4017 |  | 4256.6062 |  | 3736.515 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 47.9579 |  | 88.1703 |  | 205.5598 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 944.7542 |  | 1117.1117 |  | 1900.5833 |  | 2365.7466 | April'22
29 | Energy Generation by Hydro (MKWH) | 134.4035 |  | 135.9844 |  | 110.3709 |  | 104.66 | Sep-22
30 | Energy Generation by Solar (MKWH) | 72.0839 |  | 36.0858 |  | 41.0067 |  | 40.58 | March-22
31 | Energy Generation by Coal (MKWH) | 906.2581 |  | 1044.1876 |  | 720.3009 |  | 950.96 | Sep'22
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 723.4527 |  | 745.1102 |  | 755.5794 |  | 776.67 | August-22
33 | Monthly Load Factor (%) | 78.905 |  | 77.424 |  | 86.4057 |  | 92.62 | August-22

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:October 2023
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 14356 | 2023-10-11 | 20:00
Generation Period
| Dhaka | MW | 5004.86
| Chattogram | MW | 1268.5
| Cumilla | MW | 1329
| Mymensingh | MW | 1141
| Sylhet | MW | 503
a) | Total supply in East zone | MW | 9246.36
| Khulna | MW | 1720.7
| Barisal | MW | 433.5
| Rajshahi | MW | 1440.8
| Rangpur | MW | 881
b) | Total supply in West zone | MW | 4476
c) | Total supply in both zone ( a+b) | MW | 13722.36
Ref: | 27.21.0000.603.16.087.20.732 | Date: 22/11/2023
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:October 2023
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 600 | 2023-10-09 | 18:30
| b) Ishurdi end | MW | 318 | 2023-10-31 | 15:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 1050 | 2023-10-02 | 10:00
| b) Ishurdi end | MW | 120 | 2023-10-10 | 21:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 3.0058
| b) Ishurdi end | MKWH | 93.5356
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 90.7295
| b) Ishurdi end | MKWH | 2.9182
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 340 | 2023-10-09 | 20:00
| b)Serajganj end | MW | 640 | 2023-10-31 | 15:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 380 | 2023-10-09 | 9:00
| b)Sirajganj end | MW | 60 | 2023-10-09 | 24':00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 0.2647
| b)Sirajganj end | MKWH | 246.71
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 243.2546
| b)Sirajganj end | MKWH | 0.264
30 | Transmission loss of EWI /NO-2 | % | 1.399'%
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 2140 | 20.10.2023 | 0:30
|  | MW | 1424
| b) Aminbazar end | AMPS | -
|  | MW | -
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | -
|  | MW | -
| b) Aminbazar end | AMPS | 2100 | 20.10.2023 | 0:30
|  | MW | 1412
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 21944.832 | 20.10.23 | N/A
| a) Aminbazar end | MWh | - | -
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | - | - | N/A
| a) Aminbazar end | MWh | 21920.832 | 20.10.23
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MWh | 639704.45
| b) Aminbazar end (ckt-1 ) | MWh | -
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | -
| b) Aminbazar end (ckt-2 ) | MWh | 639264.001
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | 0.068852
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: October 2023
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) HT | 2023-10-06 03:27 | 2023-10-06 04:11 | 0:44 | E/O | Aminbazar & Agargaon ckt 1 & 2 Triped. | 234 | 171.6 | Power interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 01 | 2023-10-06 00:45 | 2023-10-06 03:15 | 2:30 | T | Due to 230kv bus coupler y phase CT fire hazard holl 230kv bus black out by 400kv ATR 2 and ATR 3 Trip at a time all 230 and 132 kv side power out also Aminbazar grid black out | 396 | 990 | Power interruption
Ashuganj 230/132/33kV Sub-Station | T-3 Kalabagan HT | 2023-10-19 10:29 | 2023-10-19 12:01 | 1:32 | T | Tripped showing dist.relay | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 HT | 2023-10-19 10:29 | 2023-10-19 11:45 | 1:16 | T | Tripped showing dist.relay | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-3 HT | 2023-10-29 12:05 | 2023-10-29 17:01 | 4:56 | E/O | 33 KV T3 & T4 bus coupler maintenance work by jamalpur pbs | 15 | 74 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | 33 kV T1 Bus | 2023-10-06 11:44 | 2023-10-06 12:44 | 1:00 | E/O | Due to emergency maint.work | 2 | 2 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-1 (404T) HT | 2023-10-06 11:42 | 2023-10-06 12:44 | 1:02 | E/O | emergency S/D by bpdb | 2 | 2.0667 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) LT | 2023-10-31 16:58 | 2023-10-31 17:02 | 0:04 | T | df/dt | 25 | 1.6667 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) LT | 2023-10-31 16:58 | 2023-10-31 17:02 | 0:04 | T | df/dt | 25 | 1.6667 | Power interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 01 LT | 2023-10-13 07:34 | 2023-10-13 08:15 | 0:41 | T | Bad weather & heavy rain. | 16 | 10.9333 | Power interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 02 HT | 2023-10-13 07:34 | 2023-10-13 07:34 | 0:00 | T | Bad weather & heavy rain. | 15 | 0 | Power interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-1 HT | 2023-10-23 14:56 | 2023-10-23 14:56 | 0:00 | E/O | Emergency shutdown | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-1 LT | 2023-10-05 15:37 | 2023-10-05 18:30 | 2:53 | T | Due to burning of 33kV CB of pbs feeder-1 | 37 | 106.6833 | Power interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-1 LT | 2023-10-06 00:46 | 2023-10-06 01:55 | 1:09 | T | Due to under frequency | 22 | 25.3 | Power interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-1 LT | 2023-10-23 14:56 | 2023-10-23 14:56 | 0:00 | E/O | Emergency shutdown | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-2 LT | 2023-10-05 15:37 | 2023-10-05 18:35 | 2:58 | T | Due to burning of CB of PBS 33 kV feeder-1 | 37 | 109.7667 | Power interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-2 LT | 2023-10-06 00:46 | 2023-10-06 01:53 | 1:07 | T | Due to under frequency | 22 | 24.5667 | Power interruption
|  |  | Total : | 21:56 |  | Unserved Energy: |  | 1520.25
Dhaka (South) Grid Circle :
Fatullah 132/33kV Grid Sub-Station | 132/33 kV GT-1 HT | 2023-10-10 14:27 | 2023-10-10 14:45 | 0:18 | T | Directional OC Trip 67 Trip | 57 | 17.1 | Power interruption
Fatullah 132/33kV Grid Sub-Station | 132/33 kV GT-1 HT | 2023-10-10 15:13 | 2023-10-10 15:18 | 0:05 | T | Directional OC Trip 67 Trip | 42 | 3.5 | Power interruption
Haripur 230/132kV Grid Sub-Station | Auto TR-1 HT | 2023-10-12 12:18 | 2023-10-12 13:56 | 1:38 | E/O | Red Hot Maintenance | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Auto TR-1 HT | 2023-10-16 12:42 | 2023-10-16 17:15 | 4:33 | E/O | High Temperature Junction Point Maintenance. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Auto TR-2 HT | 2023-10-12 01:19 | 2023-10-12 01:19 | 0:00 | T | Trip and firing. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Auto TR-2 LT | 2023-10-12 01:19 | 2023-10-12 01:19 | 0:00 | T | Trip and firing. | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 424 T-5 HT | 2023-10-14 16:22 | 2023-10-14 17:29 | 1:07 | T | Unknown | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 424 T-5 LT | 2023-10-01 10:50 | 2023-10-01 15:27 | 4:37 | E/O | 33kv Reserve bus Red phase D/S melt | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132kV Main Bus | 2023-10-29 15:50 | 2023-10-29 15:50 | 0:00 | E/O | Auto TR -2 Main bus B phase finger burn out. | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Bus-2 | 2023-10-03 11:49 | 2023-10-03 12:31 | 0:42 | T | Tripped showing Bus "2" BF & Bus PRO TC 1 OPER Bus "2" BF & Bus PRO TC 2 OPER relays. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 HT | 2023-10-13 07:25 | 2023-10-13 10:22 | 2:57 | T | PRV-2 Trip due to insert rain water at PRV box. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Transformer GT-1 HT | 2023-10-19 15:18 | 2023-10-19 19:35 | 4:17 | T | LA Failure(B-ph). | 46 | 197.0333 | Power interruption
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) HT | 2023-10-19 15:18 | 2023-10-19 16:17 | 0:59 | T | DPDC 132/33 kV LA fault. | 156 | 153.4 | Power interruption
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) HT | 2023-10-27 14:37 | 2023-10-27 15:48 | 1:11 | T | Due to Lightning Arrester (LA) Burst of Blue phase of 132 KV Kazla-1 Feeder, 230 KV Transformer-1 of Maniknagar S/S has been tripped. | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) HT | 2023-10-19 15:18 | 2023-10-19 16:40 | 1:22 | T | DPDC 132/33kv LA Fault | 156 | 213.2 | Power interruption
Munshiganj 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-10-03 06:50 | 2023-10-03 09:04 | 2:14 | E/O | 33KV Bus-1 Red Hot Maintenance by PBS | 25 | 55.8333 | Power interruption
Narshingdi 132/33kV Grid Sub-Station | T-3 HT | 2023-10-11 13:41 | 2023-10-11 13:46 | 0:05 | T | Tripp. | 40 | 3.3333 | Power interruption
Nawabganj 132/33kV Grid Sub-Station | TR-2 LT | 2023-10-12 23:01 | 2023-10-12 23:20 | 0:19 | T | Because of AGLA Feeder tripping. | 0 | 0 | No interruption
Nawabganj 132/33kV Grid Sub-Station | TR-2 LT | 2023-10-12 23:44 | 2023-10-13 13:28 | 13:44 | E/O | Sparking at TR-2 Low Voltage Side Bushing. | 0 | 0 | No interruption
Nawabganj 132/33kV Grid Sub-Station | TR-2 LT | 2023-10-29 03:35 | 2023-10-29 04:51 | 1:16 | T | Started phase-N, tripped phase-N, earth fault-1, Fault duration- 257ms, CB operation time- 74ms,Relay trip time- 178ms, Ia- 1.116 kA, Ib- 210.4 A, Ic-211.6A, | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 HT | 2023-10-05 23:41 | 2023-10-06 17:15 | 17:34 | T | 33kV NLDC Trafo Over current and Earth fault | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | NLDC Trafo LT | 2023-10-05 23:41 | 2023-10-05 23:41 | 0:00 | T | 33kV NLDC Trafo Over current and Earth fault | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | NLDC Trafo LT | 2023-10-10 09:35 | 2023-10-14 16:28 | 102:53 | T | Triped | 0.16 | 16.4613 | Power interruption
Rampura 230/132kV Grid Sub-Station | NLDC Trafo LT | 2023-10-23 16:02 | 2023-10-23 17:25 | 1:23 | T | UNKNOWN | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 HT | 2023-10-04 16:40 | 2023-10-04 17:35 | 0:55 | E/O | 33 KV MIEZ feeder work | 30 | 27.5 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2023-10-05 13:04 | 2023-10-05 14:15 | 1:11 | E/O | MIEZ Feeder's Heat Srink cable emergency maintenance work S/D taken by PBS under T-01 | 35 | 41.4167 | Power interruption
|  |  | Total : | 165:20 |  | Unserved Energy: |  | 728.778
Chattogram Grid Circle :
Baroaulia 132/33kV Grid Sub-Station | SASM HT | 2023-10-24 18:06 | 2023-10-24 19:52 | 1:46 | T |  | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | 413T(TR-2) HT | 2023-10-06 15:12 | 2023-10-07 14:58 | 23:46 | T | 132/33 TR-02 (44.1/63MVA) trip | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | 423T(TR-3) HT | 2023-10-26 16:53 | 2023-10-26 17:27 | 0:34 | E/O | Due to pdb emergency maintenance work. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | T-01 HT | 2023-10-07 23:05 | 2023-10-07 23:56 | 0:51 | E/O | Red hot maintenance by bpdb. | 18 | 15.3 | Power interruption
KSRM 132/33kV Grid Sub-Station | Transformer-01 HT | 2023-10-05 10:22 | 2023-10-05 11:48 | 1:26 | T | 33kV load side (Inside Ksrm Melting plant) isolator earth fault during maintenance time. | 0 | 0 | No interruption
KSRM 132/33kV Grid Sub-Station | Transformer-01 LT | 2023-10-28 22:58 | 2023-10-28 23:50 | 0:52 | T | over current fault | 0 | 0 | No interruption
KSRM 132/33kV Grid Sub-Station | Transformer-02 HT | 2023-10-05 10:22 | 2023-10-05 11:49 | 1:27 | T | 33kV load side (Inside Ksrm Melting plant) isolator earth fault during maintenance time. | 0 | 0 | No interruption
KSRM 132/33kV Grid Sub-Station | Transformer-02 HT | 2023-10-28 22:58 | 2023-10-28 23:52 | 0:54 | T |  | 0 | 0 | No interruption
KSRM 132/33kV Grid Sub-Station | Transformer-03 HT | 2023-10-05 10:22 | 2023-10-05 11:49 | 1:27 | T | 33kV load side (Inside Ksrm Melting plant) isolator earth fault during maintenance time. | 0 | 0 | No interruption
KSRM 132/33kV Grid Sub-Station | Transformer-03 HT | 2023-10-28 22:58 | 2023-10-28 23:52 | 0:54 | T |  | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | 405T (T1) HT | 2023-10-18 17:06 | 2023-10-22 12:30 | 91:24 | E/O | Fault at 33kv Bus | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | 415T (T2) HT | 2023-10-18 17:06 | 2023-10-18 17:42 | 0:36 | E/O | Fault at 33kv Bus | 80 | 48 | Power interruption
Madunaghat 132/33kV Grid Sub-Station | T-1 33kV BUS | 2023-10-28 16:32 | 2023-10-28 17:05 | 0:33 | T | Noapara 33kV Feeder Fault | 0 | 0 | No interruption
Madunaghat_I 400/230kV Grid Sub-Station | ATR-01 HT | 2023-10-18 13:22 | 2023-10-18 14:04 | 0:42 | T |  | 0 | 0 | No interruption
|  |  | Total : | 127:12 |  | Unserved Energy: |  | 63.3
Cumilla Grid Circle :
Chandpur 132/33kV Grid Sub-Station | 402T HT | 2023-10-05 10:42 | 2023-10-05 11:18 | 0:36 | T | Chandpur-2 feeder failt but Chandpur-2 feeder CB not open | 18 | 10.8 | Power interruption
Chandpur 132/33kV Grid Sub-Station | 402T LT | 2023-10-04 18:26 | 2023-10-04 18:55 | 0:29 | T | 33 kV Chandpur-2 Feeder O/C & E/F Signal, A-Phase trip, earth fault signal shown but Chandpur-2 Feeder CB Not Operat. Due to Chandpur-2 feeder fault current flow incomer-1 and incomer-1 CB Triped. | 20 | 9.6667 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-03 HT | 2023-10-19 15:10 | 2023-10-19 18:08 | 2:58 | T | Tripped showing Lookout relay. | 37 | 109.7667 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 LT | 2023-10-19 15:10 | 2023-10-19 15:45 | 0:35 | T | Tripped showing Over current relay. | 37 | 21.5833 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-02 HT | 2023-10-26 06:39 | 2023-10-26 12:56 | 6:17 | T | 33KV Tertiary Cable Blast(R phase) | 100 | 35 | Power interruption 06:39 to 07:00
Feni 132/33kV Grid Sub-Station | T-1(405T) LT | 2023-10-12 09:12 | 2023-10-12 11:32 | 2:20 | T | 33kV Chow-Ckt-1 Feeder Fault (loop B-Ph Mutilated) | 16 | 37.3333 | Power interruption
Feni 132/33kV Grid Sub-Station | T-2(415T) LT | 2023-10-12 09:12 | 2023-10-12 09:41 | 0:29 | T | 33 kV Cho-Ckt-1 Feeder Fault (Loop B-Ph Mutilated) | 16 | 7.7333 | Power interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-2 LT | 2023-10-12 09:36 | 2023-10-12 09:55 | 0:19 | E/O | TR-3 33 KV GCB gas Refill. | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-3 LT | 2023-10-12 09:36 | 2023-10-12 09:55 | 0:19 | E/O | TR-3 33 KV GCB gas Refill. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-10-01 15:20 | 2023-10-01 20:53 | 5:33 | T | Over load | 0 | 0 | No interruption
|  |  | Total : | 19:55 |  | Unserved Energy: |  | 231.8833
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Transformer-1 (403T) LT | 2023-10-21 07:51 | 2023-10-21 11:13 | 3:22 | E/O | Emergency Maintenance Works | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 2023-10-11 20:10 | 2023-10-11 20:20 | 0:10 | T | 33 kV kasipur feeder fault | 100 | 16.6667 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 2023-10-12 14:08 | 2023-10-12 14:13 | 0:05 | T | 33 kV nolcity feeder fault. | 58 | 4.8333 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 2023-10-28 08:34 | 2023-10-28 08:44 | 0:10 | T | Due to operate section bus isolator | 65 | 10.8333 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2023-10-11 20:10 | 2023-10-11 20:20 | 0:10 | T | 33 kv kasipur feeder fault. | 100 | 16.6667 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2023-10-12 14:08 | 2023-10-12 14:13 | 0:05 | T | 33 kV Nolcity Feeder fault. | 37 | 3.0833 | Power interruption
Gollamari 132/33kV Grid Sub-Station | Tr-2 HT | 2023-10-17 06:52 | 2023-10-17 09:44 | 2:52 | E/O | Ret Hot Maintenance in bus section 2 & 3 | 10 | 28.6667 | Power interruption
Gopalganj 132/33kV Grid Sub-Station | T1 HT | 2023-10-02 08:49 | 2023-10-05 00:37 | 63:48 | T | REB 6&7 Fault. | 32 | 2.6667 | Power interruption 08:49 to 08:54
Gopalganj 132/33kV Grid Sub-Station | T2 HT | 2023-10-02 08:49 | 2023-10-02 12:35 | 3:46 | T | REB 6&7 Fault | 32 | 120.5333 | Power interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T HT | 2023-10-16 09:20 | 2023-10-16 09:35 | 0:15 | T | 33 kv Feeder faulty | 0 | 0 | No interruption
Mongla 132/33kV Grid Sub-Station | T-1 LT | 2023-10-02 15:15 | 2023-10-02 18:55 | 3:40 | T | Seven circle feeder loop cut off. | 9 | 33 | Power interruption
Mongla 132/33kV Grid Sub-Station | T-1 LT | 2023-10-17 14:42 | 2023-10-17 16:20 | 1:38 | T | Unwanted flashing of 33kv bus section That's why T1-A tripped. | 28 | 45.7333 | Power interruption
Mongla 132/33kV Grid Sub-Station | T-2 LT | 2023-10-02 15:15 | 2023-10-02 15:57 | 0:42 | T | Seven circle feeder loop cut off & bus section out. | 9 | 6.3 | Power interruption
Mongla 132/33kV Grid Sub-Station | T-2 LT | 2023-10-04 16:57 | 2023-10-04 17:52 | 0:55 | T | 33 kv old port feeder fault. | 18 | 16.5 | Power interruption
Mongla 132/33kV Grid Sub-Station | T-2 LT | 2023-10-10 17:24 | 2023-10-10 17:53 | 0:29 | T | Bird fall in bus section | 14 | 6.7667 | Power interruption
Mongla 132/33kV Grid Sub-Station | T-2 LT | 2023-10-12 17:49 | 2023-10-12 18:19 | 0:30 | T | 33 kv bus section bird fall | 16 | 8 | Power interruption
Mongla 132/33kV Grid Sub-Station | T-2 LT | 2023-10-14 10:06 | 2023-10-14 10:24 | 0:18 | T | Under frequency | 23 | 6.9 | Power interruption
Patuakhali 132/33kV Grid Sub-Station | 425T (T-3) HT | 2023-10-07 17:27 | 2023-10-07 20:04 | 2:37 | E/O | T3 xformar abnormal sound, so emergency shut down work. | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-2 (T-2) LT | 2023-10-05 21:40 | 2023-10-05 22:41 | 1:01 | E/O | Due to emergency maint.work | 15 | 15.25 | Power interruption
|  |  | Total : | 86:33 |  | Unserved Energy: |  | 342.4
HVDC Grid Circle :
BIPTC | 20D09C 20MVA HT | 2023-10-19 11:02 | 2023-10-20 11:30 | 24:28 | E/O | 20MVA Auxiliary Transformer-1 tripped at 08:02 on 19.10.2023 | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | T-1 HT | 2023-10-17 13:25 | 2023-10-17 16:18 | 2:53 | E/O | Loop Maintenance for PDB 132 kv Side | 0 | 0 | No interruption
Bhangura 132/33kV Grid Sub-Station | Tr-1(403T) HT | 2023-10-29 09:31 | 2023-10-29 10:09 | 0:38 | E/O | Due to emergency maint.work | 12 | 7.6 | Power interruption
Bhangura 132/33kV Grid Sub-Station | Tr-1(403T) LT | 2023-10-27 06:36 | 2023-10-27 07:46 | 1:10 | T | 33 kv CT end bird flushing | 15 | 17.5 | Power interruption
Bhangura 132/33kV Grid Sub-Station | Tr-1(403T) LT | 2023-10-28 05:20 | 2023-10-28 06:02 | 0:42 | T | Bird in 33kv incommer. | 14 | 9.8 | Power interruption
Bhangura 132/33kV Grid Sub-Station | Tr-1(403T) LT | 2023-10-28 09:58 | 2023-10-28 11:37 | 1:39 | T | Bird in Incommer PT | 5 | 8.25 | Power interruption
Bhangura 132/33kV Grid Sub-Station | Tr-1(403T) LT | 2023-10-30 19:27 | 2023-10-30 20:42 | 1:15 | E/O | Due to emergency maint.work | 8 | 10 | Power interruption
Bhangura 132/33kV Grid Sub-Station | Tr-2(413T) HT | 2023-10-29 06:48 | 2023-10-29 10:07 | 3:19 | E/O | Due to emergency maint.work | 4 | 13.2667 | Power interruption
Bhangura 132/33kV Grid Sub-Station | Tr-2(413T) LT | 2023-10-27 06:36 | 2023-10-27 07:46 | 1:10 | T | Bird in 33 kv incommer | 16 | 18.6667 | Power interruption
Bhangura 132/33kV Grid Sub-Station | Tr-2(413T) LT | 2023-10-28 05:20 | 2023-10-28 06:02 | 0:42 | T | Bird in 33kv incommer | 14 | 9.8 | Power interruption
Bhangura 132/33kV Grid Sub-Station | Tr-2(413T) LT | 2023-10-28 09:58 | 2023-10-28 12:46 | 2:48 | T | Tripped showing 132/33 kv power transformer-2 relays. | 5 | 14 | Power interruption
Jashore 132/33kV Grid Sub-Station | T-1 LT | 2023-10-28 16:10 | 2023-10-28 16:30 | 0:20 | T | WZPADCO 33 KV BISIC Feeder CT Blast. | 39 | 13 | Power interruption
Jhenaidah 132/33kV Grid Sub-Station | Transformer T-1 LT | 2023-10-11 07:18 | 2023-10-11 08:28 | 1:10 | E/O | Red hot maintenance | 25 | 29.1667 | Power interruption
Jhenaidah 132/33kV Grid Sub-Station | Transformer T-2 HT | 2023-10-11 07:18 | 2023-10-11 08:28 | 1:10 | E/O | Red hot maintenance | 25 | 29.1667 | Power interruption
Kushtia 132/33kV Grid Sub-Station | 132 KV Bus-A | 2023-10-16 06:45 | 2023-10-16 08:15 | 1:30 | E/O | For 33KV B bus Shut down ( KPBS 33KV Feeder CB maintenance. ) | 30 | 45 | Power interruption
Kushtia 132/33kV Grid Sub-Station | 132 KV Bus-B | 2023-10-16 06:46 | 2023-10-16 08:14 | 1:28 | E/O | For 33 KV B bus Shut down ( KPBS 33KV Feeder CB maintenance. ) | 30 | 44 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T2 LT | 2023-10-01 10:13 | 2023-10-01 11:17 | 1:04 | E/O | 33 kv bus 33 kv outgoing feeder bus isolator Red hot maintenance | 30 | 32 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T2 LT | 2023-10-16 06:43 | 2023-10-16 08:18 | 1:35 | E/O | For 33 KV B bus Shut down ( KPBS 33KV Feeder CB maintenance. ) | 30 | 47.5 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-2 HT | 2023-10-27 07:08 | 2023-10-27 08:47 | 1:39 | E/O | For 33 KV B bus Shut down ( KPBS 33KV Feeder CB maintenance. ) | 20 | 33 | Power interruption
|  |  | Total : | 50:40 |  | Unserved Energy: |  | 381.7167
Bogura Grid Circle:
Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-3, 404T HT | 2023-10-11 21:17 | 2023-10-11 22:34 | 1:17 | E/O | Emergency red hot maintenance at Bus DS of 33KV Coal mine feeder-01. | 18 | 23.1 | Power interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-3, 404T LT | 2023-10-16 07:36 | 2023-10-16 09:26 | 1:50 | E/O | Emergency red hot maintenance at 33KV Bus. | 11 | 20.1667 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-3 HT | 2023-10-12 08:25 | 2023-10-12 13:46 | 5:21 | E/O | 132kV CT (B-Phase) Red-Hot Maintenance work. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-01 HT | 2023-10-05 03:50 | 2023-10-05 04:24 | 0:34 | T | Rain | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | 33 KV BUS | 2023-10-21 15:15 | 2023-10-21 15:50 | 0:35 | E/O | 33 Kv Bus-02 shutdown for Debigong-02 Red Hot. | 26 | 15.1667 | Power interruption
Joypurhat 132/33kV Grid Sub-Station | Transformer T-2 (417 T) HT | 2023-10-06 03:03 | 2023-10-06 10:17 | 7:14 | T | winding temperature. | 0 | 0 | No interruption
Mahasthangarh 132/33kV Grid Sub-Station | 416T MTR 2 LT | 2023-10-09 12:02 | 2023-10-09 13:08 | 1:06 | E/O | Maintenance of Pirob Feeder. | 20 | 22 | Power interruption
Mithapukur 132/33kV Grid Sub-Station | TR-1(404T) LT | 2023-10-01 09:10 | 2023-10-01 09:44 | 0:34 | T | tear off Sky ware | 20 | 11.3333 | Power interruption
Mithapukur 132/33kV Grid Sub-Station | TR-1(404T) LT | 2023-10-15 04:48 | 2023-10-15 05:12 | 0:24 | T | Tripped showing Non directional o/c operated. (R phase) relays | 12 | 4.8 | Power interruption
Mithapukur 132/33kV Grid Sub-Station | TR-2 (414T) LT | 2023-10-01 09:10 | 2023-10-01 09:44 | 0:34 | T | tear off Sky ware | 20 | 11.3333 | Power interruption
Mithapukur 132/33kV Grid Sub-Station | TR-2 (414T) LT | 2023-10-15 04:58 | 2023-10-15 05:12 | 0:14 | T | Tripped showing Non directional o/c operated. (R phase) relays | 12 | 2.8 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-3 LT | 2023-10-01 18:58 | 2023-10-01 19:25 | 0:27 | T | Trip | 44 | 19.8 | Power interruption
Natore 132/33kV Grid Sub-Station | TR-1 (405 T) LT | 2023-10-05 22:36 | 2023-10-05 23:59 | 1:23 | E/O | Due to emergency maint.work | 40 | 55.3333 | Power interruption
Palashbari 132/33kV Grid Sub-Station | TR2-404T HT | 2023-10-08 10:30 | 2023-10-08 11:05 | 0:35 | E/O | Red hot | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | T-1 Transformer (403T) HT | 2023-10-24 07:55 | 2023-10-24 08:20 | 0:25 | T | Balubari 33kv feeder fault | 5 | 2.0833 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | T-1 Transformer (403T) LT | 2023-10-04 06:23 | 2023-10-04 08:08 | 1:45 | E/O | 132kV BUS shutdown for Red hot maintenance at T4 BUS DS | 40 | 70 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | T-3 Transformer (423T) LT | 2023-10-04 06:23 | 2023-10-04 08:08 | 1:45 | E/O | 132kV BUS shutdown for Red hot maintenance at T4 BUS DS | 20 | 35 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | T-3 Transformer (423T) LT | 2023-10-24 07:55 | 2023-10-24 08:15 | 0:20 | T | Balubari 33kv feeder fault | 5 | 1.6667 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | T-4 Transformer HT | 2023-10-04 06:18 | 2023-10-04 08:09 | 1:51 | E/O | Red hot maintenance at T4 BUS DS | 25 | 46.25 | Power interruption
Rangpur 132/33kV Grid Sub-Station | T-1(414T) HT | 2023-10-16 13:06 | 2023-10-16 14:25 | 1:19 | T | 33kv all Feeder Trip | 110 | 144.8333 | Power interruption
Rangpur 132/33kV Grid Sub-Station | T-2 (404T) LT | 2023-10-16 13:06 | 2023-10-16 14:44 | 1:38 | T | 33kv All Feeder Trip | 110 | 179.6667 | Power interruption
Rangpur 132/33kV Grid Sub-Station | T-3 (424T) LT | 2023-10-16 13:53 | 2023-10-16 17:32 | 3:39 | T | DC Voltage is not available | 6 | 21.9 | Power interruption
Saidpur 132/33kV Grid Sub-Station | TR-4 (414T) LT | 2023-10-10 19:10 | 2023-10-10 20:22 | 1:12 | E/O | T4 transformar shut down due to red hot. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | T3-(435) LT | 2023-10-04 16:14 | 2023-10-04 16:28 | 0:14 | E/O | energy meter phase sequence change work. | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | Auxiliary Transformer-1 LT | 2023-10-05 12:41 | 2023-10-05 13:28 | 0:47 | E/O | DPS Feeder(NESCO) Y-Phase Bus DS Sparking | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) LT | 2023-10-05 12:41 | 2023-10-05 13:28 | 0:47 | E/O | DPS feeder (NESCO) Y Phase Bus DS Sparking | 0 | 0 | No interruption
|  |  | Total : | 37:50 |  | Unserved Energy: |  | 687.2333
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 595:59 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance | [10 empty] | 498.6333
Month: October 2023 | [10 empty] | 75.4667
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks |  | 574.1
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV Grid Sub-Station | Aminbazar Ckt-1 | 2023-10-06 00:45 | 2023-10-06 04:10 | 3:25 | T | Aminbazar & Agargaon ckt 1 fault. | 234 | 799.5 | Power interruption
Agargaon 230/132kV Grid Sub-Station | Aminbazar Ckt-2 | 2023-10-06 00:45 | 2023-10-06 04:47 | 4:02 | T | Aminbazar ckt -02 DEF Fault. | 234 | 943.8 | Power interruption
Agargaon 230/132kV Grid Sub-Station | Cantonment Ckt-1 | 2023-10-06 03:29 | 2023-10-06 04:19 | 0:50 | E/O | Aminbazar & Agargaon ckt 1 & 2 Triped. | 234 | 195 | Power interruption
Agargaon 230/132kV Grid Sub-Station | Cantonment Ckt-2 | 2023-10-06 03:30 | 2023-10-06 04:36 | 1:06 | E/O | Aminbazar & Agargaon ckt 1 & 2 Triped. | 234 | 257.4 | Power interruption
Agargaon 230/132kV Grid Sub-Station | Satmosjid Ckt-1 | 2023-10-06 03:29 | 2023-10-06 04:16 | 0:47 | E/O | Aminbazar & Agargaon ckt 1 & 2 Triped. | 234 | 183.3 | Power interruption
Aminbazar 400/230/132kV Grid Sub-Station | Mirpur-01 | 2023-10-14 19:14 | 2023-10-14 19:58 | 0:44 | T | Tripped showing Dist Trip R,S,T.Zone 3 relays. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Mirpur-02 | 2023-10-01 15:48 | 2023-10-01 17:52 | 2:04 | T | Tripped showing Distance relay relays. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Mirpur-02 | 2023-10-14 19:14 | 2023-10-14 19:39 | 0:25 | T | Tripped showing Dist Trip R,S,T.Zone 3 relays. | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-1 | 2023-10-19 10:29 | 2023-10-19 11:52 | 1:23 | T | Tripped showing no Relay relays. | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-2 | 2023-10-19 10:29 | 2023-10-19 12:07 | 1:38 | T | Tripped showing no Relay relays. | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Kishoreganj 132 kV Ckt-2 | 2023-10-17 08:56 | 2023-10-17 09:03 | 0:07 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Kishoreganj 132 kV Ckt-2 | 2023-10-19 10:29 | 2023-10-19 11:50 | 1:21 | T | Tripped showing no Relay relays. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Tongi-2 | 2023-10-09 09:04 | 2023-10-09 09:34 | 0:30 | E/O | Bird nest removing. | 40 | 20 | Power interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Aminbazar -1 | 2023-10-06 00:45 | 2023-10-06 04:44 | 3:59 | T | Tripped showing General Trip 21 O/C relays. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Tangail-1 | 2023-10-20 06:30 | 2023-10-20 06:42 | 0:12 | T | Dir O/C | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-2 | 2023-10-17 11:03 | 2023-10-17 12:09 | 1:06 | T | Tripped showing Dist. relay. | 40 | 44 | Power interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Old | 2023-10-14 19:18 | 2023-10-16 19:28 | 48:10 | E/O | 132 KV R-PH CVT Blast. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Old | 2023-10-17 09:50 | 2023-10-17 13:13 | 3:23 | T | When Uttara old ckt loaded then Uttara old & Bus coupler CB Triped . | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Sector-18 | 2023-10-14 11:25 | 2023-10-14 12:45 | 1:20 | E/O | Uttara 132KV line DS of R-phase male part & female part repairing works. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Sector-18 | 2023-10-14 19:18 | 2023-10-15 14:53 | 19:35 | E/O | Emmergency SD taken due to CVT Blast on 132 KV Mirpur-Uttata Ckt. | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Bhaluka Ckt-2 | 2023-10-06 04:35 | 2023-10-06 05:45 | 1:10 | T | Trip | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-2 | 2023-10-21 11:37 | 2023-10-21 12:12 | 0:35 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
|  |  | Total : | 97:52 |  | Unserved Energy: |  | 2443
Dhaka (South) Grid Circle :
Bhulta 132/33kV Grid Sub-Station | Narsingdi | 2023-10-14 07:48 | 2023-10-14 08:44 | 0:56 | T |  | 0 | 0 | No interruption |  |  | 120.3333 | 251.2167
Haripur 230/132kV Grid Sub-Station | Narsingdi | 2023-10-31 18:35 | 2023-10-31 18:45 | 0:10 | T |  | 135 | 22.5 | Power interruption |  |  | 14.7833
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2023-10-28 02:46 | 2023-10-28 03:01 | 0:15 | E/O | Dish line dropped on conductor. | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Hasnabad-Keraniganj Ckt-2 | 2023-10-03 11:49 | 2023-10-03 12:29 | 0:40 | T | Unknown | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aminbazar-1 | 2023-10-06 00:45 | 2023-10-06 04:03 | 3:18 | T | distance relay and Trip relay operated. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aminbazar-2 | 2023-10-06 00:45 | 2023-10-06 04:26 | 3:41 | T | Distance relay and Trip relay operated | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad | 2023-10-04 16:01 | 2023-10-04 16:32 | 0:31 | T | 132 kV Hasnabad CKT 01 tripped. | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Munshiganj 132 kv Ckt-1 | 2023-10-25 16:31 | 2023-10-25 17:57 | 1:26 | T | Munshiganj ckt-1 S/D from Munshiganj sub station for scada work than at this time trip from Madanganj substation. | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Shitalakhya 132 kv Ckt | 2023-10-23 01:52 | 2023-10-23 16:20 | 14:28 | E/O | 132 kv Fatullah ckt overloaded | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2023-10-10 10:41 | 2023-10-10 11:15 | 0:34 | E/O | Control Pannel work Fatulla Grid SS | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Kazla Ckt -1 | 2023-10-27 14:37 | 2023-10-27 14:37 | 0:00 | T | LA(B-ph) damaged. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Kazla Ckt -1 | 2023-10-27 18:23 | 2023-10-27 23:01 | 4:38 | E/O | Damage LA Replacement of Blue phase. | 0 | 0 | No interruption
Matuail 132/33kV Grid Sub-Station | 132 kV Maniknagar | 2023-10-02 13:38 | 2023-10-02 15:56 | 2:18 | E/O | For checking relay protection | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2023-10-05 21:59 | 2023-10-05 23:36 | 1:37 | T | Stormy weather | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2023-10-10 09:35 | 2023-10-10 11:00 | 1:25 | T | Triped | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2023-10-13 09:24 | 2023-10-13 09:54 | 0:30 | T | Triped | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Bhulta Ckt-01 | 2023-10-07 21:09 | 2023-10-08 11:56 | 14:47 | E/O | Redhot at T point upper loop | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Moghbazar-01 | 2023-10-18 18:17 | 2023-10-18 20:48 | 2:31 | E/O | Due to red hot at Moghbazar ss end. Order by NLDC. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Moghbazar-02 | 2023-10-02 20:00 | 2023-10-03 01:13 | 5:13 | T |  | 0 | 0 | No interruption
|  |  | Total : | 58:58 |  | Unserved Energy: |  | 22.5
Chattogram Grid Circle :
Baroaulia 132/33kV Grid Sub-Station | KSRM | 2023-10-05 10:20 | 2023-10-05 11:42 | 1:22 | T | Tripped showing K-34,K-35 relays | 15 | 20.5 | Power interruption
Baroaulia 132/33kV Grid Sub-Station | KSRM | 2023-10-28 22:58 | 2023-10-28 23:46 | 0:48 | T | Tripped showing O/C operted, K-34, K-35 relays. | 10 | 8 | Power interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona-Madunaghat Ckt-01 | 2023-10-08 10:24 | 2023-10-08 10:51 | 0:27 | T | Trip | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona-Madunaghat Ckt-02 | 2023-10-09 13:17 | 2023-10-09 17:23 | 4:06 | T | Tripped showing Rel-670 relays | 0 | 0 | No interruption
Coxsbazar 132/33kV Grid Sub-Station | Doh-Cox Ckt-2 | 2023-10-25 12:33 | 2023-10-25 15:30 | 2:57 | E/O | Tree cutting. | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-1 | 2023-10-24 21:33 | 2023-10-24 23:37 | 2:04 | T | Heavy Strom | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Madunaghat-02 | 2023-10-22 08:55 | 2023-10-22 09:28 | 0:33 | T | Earth fault | 0 | 0 | No interruption
Khagrachori 132/33kV Grid Sub-Station | RANGAMATI-1 | 2023-10-14 08:49 | 2023-10-14 09:04 | 0:15 | T | Tripped showing REL670 relays | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Madunaghat CKT-2 | 2023-10-08 10:24 | 2023-10-08 10:43 | 0:19 | T | E/F inst. operated | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Chandraghona-2 | 2023-10-05 16:13 | 2023-10-05 17:54 | 1:41 | T | Tripped showing REL-670 relays. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Kulshi-2 | 2023-10-02 08:30 | 2023-10-02 08:56 | 0:26 | T | General trip ,Zone-1 trip,y-ph fault,z-com trip | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Kulshi-2 | 2023-10-07 13:24 | 2023-10-07 13:40 | 0:16 | T | REL-670[ General trip,Zone-01,B-phase fault,ZCOM trip] | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Kulshi-2 | 2023-10-22 17:37 | 2023-10-22 18:45 | 1:08 | T | Tripped showing REC650 relays. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Sikalbaha ckt | 2023-10-22 14:54 | 2023-10-26 15:45 | 96:51 | T | Tripped showing REL670 relays. | 0 | 0 | No interruption
Rangamati 132/33kV Grid Sub-Station | Khagrachari Ckt-01 | 2023-10-04 18:34 | 2023-10-09 17:01 | 118:27 | E/O | Trip circuit unhealthy | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | Julda-1 | 2023-10-24 12:05 | 2023-10-24 12:51 | 0:46 | E/O | Filling SF6 gas in CB chamber of R phase | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Dohazari Ckt-2 | 2023-10-22 17:33 | 2023-10-22 18:13 | 0:40 | T | None | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Dohazari ckt-1 | 2023-10-07 11:15 | 2023-10-07 11:27 | 0:12 | T | Tripped showing main protection relay | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Interconnection-1 | 2023-10-22 13:15 | 2023-10-22 13:15 | 0:00 | E/O |  | 0 | 0 | No interruption
|  |  | Total : | 233:18 |  | Unserved Energy: |  | 28.5
Cumilla Grid Circle :
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Shahjibazar Circuit-2 | 2023-10-06 16:16 | 2023-10-06 16:29 | 0:13 | T | Started phase B N Zone-01 | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni line-01 | 2023-10-13 21:35 | 2023-10-14 05:01 | 7:26 | T | Tripped showing Distance Relay relays. | 70 | 520.3333 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni line-01 | 2023-10-17 06:36 | 2023-10-17 08:40 | 2:04 | E/O | Red hot maintenance work at feni end | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Shahajibazar Ckt-2 | 2023-10-15 11:55 | 2023-10-15 12:08 | 0:13 | T | Tripped showing Main-1: 21 trip Z com/EF | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Kulaura-1 | 2023-10-09 11:34 | 2023-10-09 12:45 | 1:11 | T | Bad weather. | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | Shahjibazar-B.Baria Ckt-02 | 2023-10-06 15:04 | 2023-10-06 15:31 | 0:27 | T | Bad weather | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Shahjibazar circuit-2 | 2023-10-06 15:19 | 2023-10-06 15:44 | 0:25 | T | Bad weather | 0 | 0 | No interruption
|  |  | Total : | 11:59 |  | Unserved Energy: |  | 520.3333
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Bagerhat-Mongla 2 | 2023-10-07 05:07 | 2023-10-07 05:30 | 0:23 | T | Unknown. (Assuming Thunderstorm) | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | Barishal ckt-02 | 2023-10-18 07:35 | 2023-10-18 15:17 | 7:42 | E/O | From barishal south | 0 | 0 | No interruption
Gollamari 132/33kV Grid Sub-Station | E01 Gollamari-Gopalgonj Line - 1 | 2023-10-02 08:49 | 2023-10-02 12:40 | 3:51 | T | Trip | 0 | 0 | No interruption
Gollamari 132/33kV Grid Sub-Station | E07 Gollamari-Gopalgonj Line - 2 | 2023-10-02 08:49 | 2023-10-02 12:41 | 3:52 | T | Trip | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Gopalganj North-1 | 2023-10-02 08:49 | 2023-10-02 12:27 | 3:38 | T | REB 6&7 FAULT | 52 | 188.9333 | Power interruption
Gopalganj 132/33kV Grid Sub-Station | Gopalganj North-2 | 2023-10-02 08:49 | 2023-10-02 12:18 | 3:29 | T | REB 6&7 FAULT | 52 | 181.1333 | Power interruption
|  |  | Total : | 22:55 |  | Unserved Energy: |  | 370.0667
HVDC Grid Circle :
BIPTC | Baharampur-4 | 2023-10-05 00:30 |  |  | T | None | 0 | 0 | No interruption
BIPTC | Baharampur-4 | 2023-10-05 09:46 | 2023-10-05 19:26 | 9:40 | E/O | Baharampur Ckt-04 is in shutdown taken from baharampur end due to tripped | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | NOA-1(L3) | 2023-10-05 23:38 | 2023-10-06 06:16 | 6:38 | T | Trip | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | NOA-2(L4) | 2023-10-05 23:38 | 2023-10-06 06:18 | 6:40 | T | Trip | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Jhenaidah-Jhenaidah New-1,132kV Circuit-1(L4) | 2023-10-17 12:19 | 2023-10-17 13:13 | 0:54 | E/O | Jhenaidah 230/132 kV Transformer Over Load | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Jhenaidah-Jhenaidah New-1,132kV Circuit-1(L4) | 2023-10-18 10:25 | 2023-10-18 11:58 | 1:33 | E/O | Jhenaidah 230/132 kV Transformer Over Load | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Jhenaidah-Jhenaidah New-2,132kV Circuit-2(L3) | 2023-10-17 12:20 | 2023-10-17 13:14 | 0:54 | E/O | Jhenaidah 230/132 kV Transformer Over Load | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Jhenaidah-Jhenaidah New-2,132kV Circuit-2(L3) | 2023-10-18 10:27 | 2023-10-18 11:58 | 1:31 | E/O | Jhenaidah 230/132 kV Transformer Over Load | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Jhenaidah-Jhenaidah New-3,132kV Circuit-3(L5) | 2023-10-17 12:23 | 2023-10-17 13:14 | 0:51 | E/O | Jhenaidah 230/132 kV Transformer Over Load | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Jhenaidah-Jhenaidah New-3,132kV Circuit-3(L5) | 2023-10-18 10:28 | 2023-10-18 11:59 | 1:31 | E/O | Jhenaidah 230/132 kV Transformer Over Load | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Jhenaidah-Kushtia 132kV Circuit-2(L2) | 2023-10-05 04:45 | 2023-10-05 05:00 | 0:15 | T | Inst. Over current | 0 | 0 | No interruption
Pabna 132/33kV Grid Sub-Station | Pabna-Shahjadpur Line | 2023-10-15 18:32 | 2023-10-25 07:10 | 228:38 | E/O | instruction by aldc bogra. | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | 132 KV Shahjadpur-Bghabari-1 | 2023-10-17 10:48 | 2023-10-17 13:25 | 2:37 | E/O | Maintenance work at Baghabari Power Station | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | 132 KV Shahjadpur-Pabna | 2023-10-28 09:50 | 2023-10-28 20:04 | 10:14 | E/O | Shahjadpur-Pabna 132kv Line CT Y-phase change. | 0 | 0 | No interruption
|  |  | Total : | 271:56 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Amnura 132/33kV Grid Sub-Station | Amnura - Rajshahi | 2023-10-26 05:09 | 2023-10-26 16:44 | 11:35 | T | PT Blust of Y-phase for Distance Trip, Zone-1 and Over Voltage. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Saidpur 132 KV Ckt1 | 2023-10-10 04:33 | 2023-10-10 04:45 | 0:12 | T | Heavy raining at Saidpur side | 100 | 20 | Power interruption
Naogaon 132/33kV Grid Sub-Station | Nao-SPPP Ckt-1 | 2023-10-17 17:35 | 2023-10-17 20:26 | 2:51 | E/O | measuring PT Check and Maintanance. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Ishurdi-1 | 2023-10-05 14:48 | 2023-10-05 16:18 | 1:30 | T | Tripped showing Z-1, General trip, AR block,Over vltage,C phase. relays. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Ishurdi-2 | 2023-10-05 14:48 | 2023-10-05 16:18 | 1:30 | T | Tripped showing Z-1, General trip, AR block,Over vltage,C phase. relays. | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Saidpur Line-1 | 2023-10-04 06:21 | 2023-10-04 08:07 | 1:46 | E/O | 132kV BUS shutdown for Red hot maintenance at T4 BUS DS | 90 | 159 | Power interruption | 1:46
Purbasadipur 132/33kV Grid Sub-Station | Saidpur Line-2 | 2023-10-04 06:21 | 2023-10-04 08:07 | 1:46 | E/O | 132kV BUS shutdown for Red hot maintenance at T4 BUS DS | 90 | 159 | Power interruption | 1:46
Purbasadipur 132/33kV Grid Sub-Station | Thakurgaon Line-1 | 2023-10-04 06:20 | 2023-10-04 08:14 | 1:54 | E/O | Red hot maintenance at T4 BUS DS | 40 | 76 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | Thakurgaon Line-2 | 2023-10-04 06:20 | 2023-10-04 08:18 | 1:58 | E/O | Red hot maintenance at T4 BUS DS | 40 | 78.6667 | Power interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Saidpur-1 | 2023-10-10 03:05 | 2023-10-10 03:25 | 0:20 | T | Distance relay operated | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Saidpur-2 | 2023-10-10 03:05 | 2023-10-10 03:25 | 0:20 | T | Distance relay operated | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Saidpur-2 | 2023-10-12 12:52 | 2023-10-12 13:08 | 0:16 | T | O/V | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Saidpur-2 | 2023-10-15 10:54 | 2023-10-15 11:25 | 0:31 | T | O/V | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Teesta Solar-2 | 2023-10-29 17:35 | 2023-10-29 17:55 | 0:20 | E/O | Maintenance work | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Baropukuria CKT-02 | 2023-10-10 04:33 | 2023-10-10 04:48 | 0:15 | T | Rainy weather and lightning | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Rangpur CKT-01 | 2023-10-04 10:13 | 2023-10-04 10:51 | 0:38 | E/O | Red hot | 0 | 0 | No interruption
|  |  | Total : | 27:42 |  | Unserved Energy: |  | 492.6667
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 724:40 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: October 2023
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) HT | 2023-10-03 08:14 | 2023-10-06 04:31 | 68:17 | S/O | Maintenance & Cleaning of Auxiliary Tr-2 | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 02 | 2023-10-15 06:49 | 2023-10-15 09:41 | 2:52 | S/O | HOTSPOT REMOVING | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 LT | 2023-10-15 05:39 | 2023-10-15 09:44 | 4:05 | S/O | hot spot removing | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | 132 kv Busbar-2 | 2023-10-14 06:35 | 2023-10-14 15:42 | 9:07 | S/O | OAT-12(132kv) Bay Upgradation | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | 132kv Busbar-1 | 2023-10-13 07:33 | 2023-10-13 17:07 | 9:34 | S/O | OAT-12 BAY UPGRADETION | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | 132kv Busbar-1 | 2023-10-15 06:59 | 2023-10-15 09:51 | 2:52 | S/O | OAT-12(132kv) Busbar-1 bay upgradation | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | 132kv Busbar-1 | 2023-10-22 06:56 | 2023-10-22 06:56 | 0:00 | S/O | kishorganj-1 bus isolator problem | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | 132kv Busbar-1 | 2023-10-22 06:58 | 2023-10-22 10:38 | 3:40 | S/O | Kishoreganj-1 bus-1 DS alignment problem | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | T-4 Kalabagan HT | 2023-10-22 06:54 | 2023-10-22 09:46 | 2:52 | S/O | 132kv bus-1 s/d | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | T-4 Kalabagan LT | 2023-10-13 07:08 | 2023-10-13 17:42 | 10:34 | S/O | 132 KV BUS-1 S/D | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | T-4 Kalabagan LT | 2023-10-15 06:53 | 2023-10-15 09:59 | 3:06 | S/O | OAT-12(132kv) Busbar-1 Bay Upgradation | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 LT | 2023-10-12 06:31 | 2023-10-16 13:32 | 103:01 | S/O | LT bushing and CT change | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-3 HT | 2023-10-06 11:04 | 2023-10-06 12:33 | 1:29 | S/O | 33 kv bus loop change | 12 | 17.8 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-3 HT | 2023-10-10 09:50 | 2023-10-10 11:10 | 1:20 | S/O | 33kv Energy meter replacement Work. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-3 HT | 2023-10-31 09:30 | 2023-10-31 17:45 | 8:15 | S/O | A/M | 0 | 0 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-4 HT | 2023-10-28 09:12 | 2023-10-28 16:25 | 7:13 | S/O | Annual Maintenance Work. | 0 | 0 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-4 HT | 2023-10-29 09:05 | 2023-10-29 17:09 | 8:04 | S/O | Annual maintenance work | 0 | 0 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | Main bus | 2023-10-02 06:08 | 2023-10-02 08:24 | 2:16 | S/O | High temperature maintenance work | 40 | 90.6667 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | Reserve bus | 2023-10-11 07:14 | 2023-10-11 09:16 | 2:02 | S/O | Red hot maintenance | 70 | 142.3333 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-1 (404T) HT | 2023-10-14 07:13 | 2023-10-14 11:35 | 4:22 | S/O | Nandail-1 bus ds and bus coupler ds between t1 & t3 Maintenance work by PBS | 12 | 52.4 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) HT | 2023-10-14 07:15 | 2023-10-14 11:37 | 4:22 | S/O | Nandail-1 bus ds and bus coupler ds between t1 & t3 Maintenance work by PBS | 28 | 122.2667 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) HT | 2023-10-30 09:50 | 2023-10-30 15:34 | 5:44 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) HT | 2023-10-31 12:59 | 2023-10-31 16:20 | 3:21 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Reserve Bus | 2023-10-15 12:24 | 2023-10-15 14:52 | 2:28 | S/O | 132 KV Reserve Bus with Uttara Sector 18 ckt bay Maintenance. | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Bus A | 2023-10-03 06:47 | 2023-10-03 08:55 | 2:08 | S/O | To perform high temperature mitigate works of A-Bus DS (221S) of 132kV Net-2. | 110 | 234.6667 | Power interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-2 (414T) LT | 2023-10-29 19:08 | 2023-10-29 21:35 | 2:27 | S/O | TR-3 X-F S/D due to 33KV Digharkanda(Bypass) Feeder R-Phase Bus -T Clamp Red hot Maintenance | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-3 (424T) HT | 2023-10-29 19:08 | 2023-10-29 21:34 | 2:26 | S/O | TR-3 X-F S/D due to 33KV Digharkanda(Bypass) Feeder R-Phase Bus -T Clamp Red hot Maintenance | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-A | 2023-10-25 10:26 | 2023-10-25 15:44 | 5:18 | S/O | red hot maintenance of 33kV feeders by DPBS-3. | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 02 LT | 2023-10-31 08:42 | 2023-10-31 16:10 | 7:28 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 04 HT | 2023-10-28 08:25 | 2023-10-30 16:02 | 55:37 | S/O | Annual Maintenance | 0 | 0 | No interruption
|  |  | Total : | 346:20 |  | Unserved Energy: |  | 660.1333
Dhaka (South) Grid Circle : | [12 empty] | 39.3333
Fatullah 132/33kV Grid Sub-Station | 132/33 kV GT-1 LT | 2023-10-09 13:44 | 2023-10-09 16:40 | 2:56 | D/W | SCADA Integration with NLDC | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | 132/33 kV GT-2 LT | 2023-10-10 13:01 | 2023-10-10 15:20 | 2:19 | D/W | Due to project work | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Auto TR-3 HT | 2023-10-15 05:55 | 2023-10-15 09:11 | 3:16 | S/O | Redhot Maintanance. | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 404 T-1 HT | 2023-10-25 10:27 | 2023-10-25 10:47 | 0:20 | S/O | Energy meter changing work by BPDB | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 424 T-5 HT | 2023-10-25 10:48 | 2023-10-25 11:20 | 0:32 | S/O | Energy meter replacemen work | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 HT | 2023-10-05 13:15 | 2023-10-05 14:59 | 1:44 | S/O | Busbar protection panel replacement work 132kv end. | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 HT | 2023-10-12 12:23 | 2023-10-12 15:04 | 2:41 | S/O | Bus protection work | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 HT | 2023-10-18 08:51 | 2023-10-19 12:57 | 28:06 | S/O | Oil Centrifuge | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 LT | 2023-10-30 08:18 | 2023-10-30 18:02 | 9:44 | S/O | Due to Tan Delta test and Others test. | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 HT | 2023-10-12 15:15 | 2023-10-12 16:29 | 1:14 | S/O | Maintenance work | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 HT | 2023-10-16 08:57 | 2023-10-17 15:44 | 30:47 | S/O | Oil centrifuge of yellow phase ATR-2 | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 HT | 2023-10-29 14:49 | 2023-10-29 17:38 | 2:49 | S/O | DS - 211 (132kV) maintenance | 0 | 0 | No interruption
Kazla 132/33kV Grid Sub-Station | GT-2 HT | 2023-10-15 10:12 | 2023-10-15 15:03 | 4:51 | D/W | NLDC communication and Maintenance purpose | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-1 LT | 2023-10-15 07:33 | 2023-10-15 10:15 | 2:42 | S/O | high temp.maintenance at 33kV side at several point. | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | GT-2 LT | 2023-10-16 10:18 | 2023-10-16 13:45 | 3:27 | S/O | 33 kv pbs breaker maintenance | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | T-3 HT | 2023-10-11 12:27 | 2023-10-11 13:16 | 0:49 | S/O | Tr-3, 132kV CT B- phase Hotspot maintenance work. | 30 | 24.5 | Power interruption
Rampura 230/132kV Grid Sub-Station | 132 kV Busbar-2 | 2023-10-30 15:16 | 2023-10-31 20:08 | 28:52 | D/W | 300/400 MVA new transformer commissioning and interin work | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 01 HT | 2023-10-20 06:09 | 2023-10-21 00:49 | 18:40 | S/O | Main tank oil centrifuge. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 HT | 2023-10-06 08:30 | 2023-10-06 12:50 | 4:20 | S/O | Transformer Oil and Winding Insulation Test(Megger), due to Trip by Diff. O/C & E/F Trip at 23:41(05.10.23) | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 HT | 2023-10-13 06:35 | 2023-10-14 00:16 | 17:41 | S/O | 230kV R Ph CT-2134 replacecing work (Beside of 815No CB) | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 LT | 2023-10-19 05:17 | 2023-10-19 07:34 | 2:17 | S/O | Red hot point maintenance | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Aux Transformer-02 HT | 2023-10-30 14:59 | 2023-10-30 14:59 | 0:00 | D/W | 300/400 MVA new transformer commissioning and interin work | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Aux Transformer-02 LT | 2023-10-30 14:59 | 2023-10-30 14:59 | 0:00 | D/W | 300/400 MVA new transformer commissioning and interin work | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | NLDC Trafo HT | 2023-10-06 08:30 | 2023-10-06 17:15 | 8:45 | S/O | Transformer Blasted R Phase LA & Surge Counter replace, Oil and Winding Insulation Test(Megger), due to Trip by Diff. O/C & E/F Trip at 23:41(05.10.23) | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | NLDC Trafo LT | 2023-10-15 19:20 | 2023-10-16 19:34 | 24:14 | S/O | Fuse replacing work in 11 kV Side | 0 | 0 | No interruption
Shitalakhya 132/33kV Grid Sub-Station | 132/33 kV GT-2 HT | 2023-10-27 09:20 | 2023-10-27 19:40 | 10:20 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2023-10-10 09:12 | 2023-10-10 10:45 | 1:33 | S/O | PBS Astafeed feeder Source side Bus to D/S jumper maintenance work. | 40 | 62 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 LT | 2023-10-05 09:20 | 2023-10-05 12:49 | 3:29 | S/O | PBS Langalband feeder to 33kv Bus connecting point cable maintenance under T-02 transformer. | 40 | 139.3333 | Power interruption
|  |  | Total : | 218:28 |  | Unserved Energy: |  | 225.8333
Chattogram Grid Circle :
Chandraghona 132/33kV Grid Sub-Station | TR-01(406T) HT | 2023-10-12 05:29 | 2023-10-22 13:10 | 247:41 | D/W |  | 23 | 203.55 | Power interruption 05:29 to 14:20 | 14:20
Chandraghona 132/33kV Grid Sub-Station | TR-02(416T) LT | 2023-10-01 08:34 | 2023-10-01 12:50 | 4:16 | S/O | High temperature maintenance and loop change. | 0 | 0 | No interruption
GPH 230/33kV Grid Sub-Station | Transformer -2 (D07) HT | 2023-10-12 10:08 | 2023-10-12 16:21 | 6:13 | S/O | for replacing the WTI meter | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | 403T(TR-1) LT | 2023-10-29 07:56 | 2023-10-29 14:50 | 6:54 | S/O | Due to annual grid maintenance. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | T-02 HT | 2023-10-04 07:04 | 2023-10-04 09:55 | 2:51 | S/O | OLTC oil change | 0 | 0 | Power interruption
KSRM 132/33kV Grid Sub-Station | Transformer-01 HT | 2023-10-18 09:32 | 2023-10-18 09:32 | 0:00 | S/O | Roster maintenance from KSRM Technical Team. | 0 | 0 | No interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-01(506T) HT | 2023-10-01 11:19 | 2023-10-01 13:28 | 2:09 | S/O | Relay setting change by spmd | 0 | 0 | Power interruption
Khagrachori 132/33kV Grid Sub-Station | TR-1 HT | 2023-10-29 08:53 | 2023-10-29 16:27 | 7:34 | S/O | Annual Maintenance | 0 | 0 | Power interruption
Mirsorai 230/33kV Grid Sub-Station | Bus-1 | 2023-10-17 10:16 | 2023-10-17 15:28 | 5:12 | S/O | Annual Maintenance | 0 | 0 | Power interruption
Mirsorai 230/33kV Grid Sub-Station | Bus-2 | 2023-10-18 10:50 | 2023-10-18 12:47 | 1:57 | S/O | Annual Maintenance | 0 | 0 | Power interruption
Rangamati 132/33kV Grid Sub-Station | Main Bus 01 | 2023-10-09 12:12 | 2023-10-09 15:12 | 3:00 | S/O | Annual maintenance | 0 | 0 | No interruption
Rangamati 132/33kV Grid Sub-Station | Main Bus 02 | 2023-10-09 10:10 | 2023-10-09 12:05 | 1:55 | S/O | Annual maintenance | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | 416T HT | 2023-10-06 12:15 | 2023-10-06 13:00 | 0:45 | S/O | To remove temporary "T" connection of Auxiliary Transformer -01(Teba,China) at 33kv sideTR-02 power Transformer | 0 | 0 | No interruption
Sholosohor 132/33kV Grid Sub-Station | TRAFO-01 HT | 2023-10-30 07:52 | 2023-10-30 14:28 | 6:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sholosohor 132/33kV Grid Sub-Station | TRAFO-02 HT | 2023-10-31 08:15 | 2023-10-31 13:40 | 5:25 | S/O | Annual maintanance, 2023 | 0 | 0 | No interruption
|  |  | Total : | 302:28 |  |  |  | 203.55
Cumilla Grid Circle :
Beanibazar 132/33kV Grid Sub-Station | 132 KV BUS-1 | 2023-10-10 09:15 | 2023-10-11 12:02 | 26:47 | D/W | Development work | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 422T HT | 2023-10-19 15:13 | 2023-10-19 15:38 | 0:25 | S/O | Shutdown for station supply T-2 fuse maintenance | 29 | 12.0833 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-03 LT | 2023-10-20 06:16 | 2023-10-20 14:57 | 8:41 | D/W | Due to project work | 0 | 0 | No interruption | Check
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-03 LT | 2023-10-21 11:03 | 2023-10-21 12:11 | 1:08 | S/O | Underground Cable reconnection. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 LT | 2023-10-02 12:29 | 2023-10-02 14:36 | 2:07 | S/O | 33KV Summit Gen BUS Side Red hot removed | 20 | 42.3333 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 LT | 2023-10-20 06:12 | 2023-10-20 09:10 | 2:58 | D/W | Due to maint.work | 31 | 91.9667 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-05 HT | 2023-10-20 06:10 | 2023-10-20 09:13 | 3:03 | D/W | Due to maint.work | 27 | 82.35 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-05 LT | 2023-10-08 13:58 | 2023-10-08 15:21 | 1:23 | S/O | 33KV BusSection Redhot Remove | 13 | 17.9833 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132kV MAIN BUSBAR | 2023-10-20 06:18 | 2023-10-20 09:07 | 2:49 | D/W | Development Work of Project for T-06 X-former. | 105 | 295.75 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-01 HT | 2023-10-20 06:13 | 2023-10-20 09:07 | 2:54 | D/W | Due to maint.work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-02 LT | 2023-10-20 06:18 | 2023-10-20 09:12 | 2:54 | D/W | Due to maint.work | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-1 HT | 2023-10-19 16:44 | 2023-10-19 17:02 | 0:18 | S/O | Tr-01 Transformer Shift from India Bus to Bangladesh Bus | 30 | 9 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-1 HT | 2023-10-23 10:35 | 2023-10-23 10:50 | 0:15 | S/O | Tr-01 transformer Shift from National Grid to India grid. Tripura L/C 160MW | 40 | 10 | Power interruption
Fenchuganj 230/132/33kV Grid Sub-Station | 132 KV Bus-2 | 2023-10-19 10:08 | 2023-10-19 13:45 | 3:37 | S/O | 132kV Bus-2 PT Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-02 HT | 2023-10-19 09:39 | 2023-10-19 14:18 | 4:39 | S/O | 132kV Bus-2 PT Maintenance | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) HT | 2023-10-02 14:24 | 2023-10-02 15:13 | 0:49 | S/O | 33kV (T-1) Feeder Bus DS Red Hot | 30 | 24.5 | Power interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) LT | 2023-10-12 10:02 | 2023-10-12 11:32 | 1:30 | S/O | 33kV Chow Ckt-1(Loop B-Ph Maintenance work) | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-2(415T) HT | 2023-10-11 06:30 | 2023-10-11 17:52 | 11:22 | S/O | 33kV Bus DS Red hot (Blue Ph.) | 35 | 262.5 | Power interruption 06:30to 09:30 | check | 9:30
Feni 132/33kV Grid Sub-Station | T-2(415T) HT | 2023-10-16 05:42 | 2023-10-16 11:00 | 5:18 | S/O | S/D Taken for Main bus-1(Bus lop-B Ph.) Red Hot Maintenance work | 0 | 0 | No interruption | no load sheed
Ramganj 132/33kV Grid Sub-Station | Transformer -02 LT | 2023-10-23 08:22 | 2023-10-23 09:57 | 1:35 | S/O | Red-hot maintenance work | 0 | 0 | No interruption
Ramganj 132/33kV Grid Sub-Station | Transformer-01 LT | 2023-10-23 09:59 | 2023-10-23 11:22 | 1:23 | S/O | Red-hot maintenance work. | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 HT | 2023-10-13 07:56 | 2023-10-13 21:23 | 13:27 | S/O | TR-02 Oil Centrifuging | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 HT | 2023-10-16 07:01 | 2023-10-16 08:53 | 1:52 | S/O | TR-04 33 side Breaker Bushing hot spot Maaintenance. Load flow by TR-02 | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Main Bus -1 | 2023-10-02 11:46 | 2023-10-02 14:20 | 2:34 | S/O | project work | 18 | 46.2 | Power interruption
|  |  | Total : | 103:48 |  | Unserved Energy: |  | 894.6667
Khulna Grid Circle : | [11 empty] | 251.2167
Bagerhat 132/33kV Grid Sub-Station | Transformer-1 (403T) LT | 2023-10-17 07:07 | 2023-10-17 14:37 | 7:30 | S/O | Yearly maintenance work. | 0 | 0 | No interruption |  |  | 113.55
Bagerhat 132/33kV Grid Sub-Station | Transformer-1 (403T) LT | 2023-10-18 07:05 | 2023-10-18 12:24 | 5:19 | S/O | Annual maintenance work | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-2 (413 T) LT | 2023-10-22 07:21 | 2023-10-22 14:17 | 6:56 | S/O | Annual maintenance. | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-3 ( 423 T) LT | 2023-10-30 07:11 | 2023-10-30 16:06 | 8:55 | S/O | Annual maintenance. | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2023-10-28 08:23 | 2023-10-28 10:12 | 1:49 | S/O | For work on 33 kv bus by WZPDCL | 0 | 0 | No interruption |  |  | 364.7667
Faridpur 132/33kV Grid Sub-Station | 33 KV Bus | 2023-10-19 07:18 | 2023-10-19 09:20 | 2:02 | S/O | Hot spot maintenance | 30 | 61 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-10-14 09:01 | 2023-10-14 12:21 | 3:20 | S/O | 132 kv bus protection | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-10-08 06:56 | 2023-10-08 08:21 | 1:25 | S/O | 33 kv Bus section-1 D/S red hot maintenance work. | 38 | 53.8333 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-10-14 12:40 | 2023-10-14 14:50 | 2:10 | D/W | 132 kv bus protecction | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-10-19 07:11 | 2023-10-19 09:25 | 2:14 | S/O | Hot spot maintenance work | 30 | 67 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-10-09 06:48 | 2023-10-09 10:50 | 4:02 | S/O | High Temperature maintenance. | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-3 HT | 2023-10-08 12:38 | 2023-10-08 14:08 | 1:30 | S/O |  | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-3 HT | 2023-10-15 09:58 | 2023-10-15 20:46 | 10:48 | S/O | Due to project work | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Bus 1 | 2023-10-30 08:59 | 2023-10-30 16:48 | 7:49 | S/O | Shutdown for Annual Maintenance works. | 0 | 0 | No interruption
Gollamari 132/33kV Grid Sub-Station | Tr-1 HT | 2023-10-28 08:16 | 2023-10-28 11:24 | 3:08 | S/O | 33 kv jumper change | 20 | 62.6667 | Power interruption
Gollamari 132/33kV Grid Sub-Station | Tr-2 LT | 2023-10-28 08:17 | 2023-10-28 11:26 | 3:09 | S/O | 33 kv jumper change | 20 | 63 | Power interruption
Gopalganj 132/33kV Grid Sub-Station | T1 LT | 2023-10-18 08:11 | 2023-10-18 16:12 | 8:01 | S/O | Annual maintenance of T-1 Transformer | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | T1 LT | 2023-10-19 08:20 | 2023-10-19 16:31 | 8:11 | S/O | Annual maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | T2 LT | 2023-10-21 08:30 | 2023-10-21 16:22 | 7:52 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | T2 LT | 2023-10-22 08:13 | 2023-10-22 15:38 | 7:25 | S/O | Yearly maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-03 LT | 2023-10-19 10:11 | 2023-10-19 22:05 | 11:54 | D/W | 132 kV SAS & DFDR Commissioning | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-03 LT | 2023-10-25 09:30 | 2023-10-25 21:42 | 12:12 | D/W |  | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | Bus Coupler | 2023-10-28 08:08 | 2023-10-28 14:05 | 5:57 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | Bus Coupler | 2023-10-29 08:06 | 2023-10-29 14:05 | 5:59 | S/O | Yearly Maintenance | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T LT | 2023-10-10 08:02 | 2023-10-10 15:03 | 7:01 | S/O | For Annual Maintenance. | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T LT | 2023-10-11 08:04 | 2023-10-11 15:44 | 7:40 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | Tr-2 415 T HT | 2023-10-15 08:01 | 2023-10-15 15:08 | 7:07 | S/O | For Annual Maintenance | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | Tr-2 415 T LT | 2023-10-14 07:46 | 2023-10-14 15:12 | 7:26 | S/O | Shutdown for annual maintenance | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | Tr-3 405T HT | 2023-10-18 08:10 | 2023-10-18 16:15 | 8:05 | S/O | Due to annual maintenance work | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | Tr-3 405T LT | 2023-10-17 09:54 | 2023-10-17 15:27 | 5:33 | S/O | Annual Maintanance | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | 230 KV Main Bus 2 | 2023-10-06 09:45 | 2023-10-09 15:40 | 77:55 | D/W | 800 MW NWPGCL Power Plant Project Work. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-1 LT | 2023-10-01 08:31 | 2023-10-01 17:30 | 8:59 | S/O | Annual maintenance work | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-1 LT | 2023-10-03 08:32 | 2023-10-03 16:38 | 8:06 | S/O | Annual maintenance work | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-1 LT | 2023-10-10 08:37 | 2023-10-10 15:55 | 7:18 | S/O | Annual maintenance work | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-2 HT | 2023-10-07 08:36 | 2023-10-07 16:00 | 7:24 | S/O | Annual Maintenance Work-2023 | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-2 HT | 2023-10-08 08:32 | 2023-10-08 18:12 | 9:40 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-2 LT | 2023-10-09 08:23 | 2023-10-09 17:21 | 8:58 | S/O | Yearly Maintenance Work. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-3 LT | 2023-10-14 09:34 | 2023-10-14 15:39 | 6:05 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-3 LT | 2023-10-15 08:30 | 2023-10-15 13:38 | 5:08 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T1-405T LT | 2023-10-29 08:14 | 2023-10-29 17:23 | 9:09 | S/O | Annual Maintenance | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T1-405T LT | 2023-10-30 08:22 | 2023-10-30 17:18 | 8:56 | S/O | Annual maintenance | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T2-415T HT | 2023-10-31 08:11 | 2023-10-31 16:09 | 7:58 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mongla 132/33kV Grid Sub-Station | T-1 LT | 2023-10-14 10:06 | 2023-10-14 16:11 | 6:05 | S/O | Annual maintenance | 0 | 0 | No interruption
Mongla 132/33kV Grid Sub-Station | T-2 LT | 2023-10-17 09:11 | 2023-10-17 16:21 | 7:10 | S/O | Annual maintenance | 5 | 0 | No interruption
Mongla 132/33kV Grid Sub-Station | Transfer Bus | 2023-10-21 09:54 | 2023-10-21 11:50 | 1:56 | S/O | Annual maintenance | 0 | 0 | No interruption
Narail 132/33kV Grid Sub-Station | TR1 (403-T) LT | 2023-10-18 11:29 | 2023-10-18 13:10 | 1:41 | S/O | Red hot maintenance work of 33 KV Incomer CT, R phase | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | BUS A | 2023-10-05 08:51 | 2023-10-18 16:12 | 319:21 | D/W | Conductor change bus-A | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | BUS-B | 2023-10-31 10:15 | 2023-10-31 10:15 | 0:00 | S/O | B-Bus Shutdown Due To Project Work . | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | T-1 LT | 2023-10-20 07:04 | 2023-10-20 09:04 | 2:00 | S/O | 33 kv bus shutdown | 20 | 40 | Power interruption
Noapara 132/33kV Grid Sub-Station | T-2 HT | 2023-10-20 07:07 | 2023-10-20 09:04 | 1:57 | S/O | 33 kv bus shutdown | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | 132/33 kV Transformer-03 LT | 2023-10-25 08:46 | 2023-10-25 20:08 | 11:22 | S/O | Annual maintenance | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | 132/33 kV Transformer-03 LT | 2023-10-26 07:25 | 2023-10-26 19:19 | 11:54 | S/O | Anual maintenance | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | 132/33 kV Transformer-04 LT | 2023-10-29 07:46 | 2023-10-29 20:44 | 12:58 | S/O | Anual maintenance | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | 132/33 kV Transformer-04 LT | 2023-10-30 09:54 | 2023-10-30 20:31 | 10:37 | S/O | anual maintenance | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | 132/33 kV Transformer-04 LT | 2023-10-31 07:10 | 2023-10-31 15:02 | 7:52 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-10-08 11:29 | 2023-10-08 13:21 | 1:52 | S/O |  | 18 | 33.6 | Power interruption
Rajbari 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-10-09 07:52 | 2023-10-09 17:05 | 9:13 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-10-14 11:52 | 2023-10-14 13:58 | 2:06 | S/O | Annual maintenance work | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-10-17 09:48 | 2023-10-17 11:48 | 2:00 | S/O | Annual maintenance work | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-10-12 08:24 | 2023-10-12 15:58 | 7:34 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | ICT-2 HT | 2023-10-30 11:18 | 2023-10-30 17:08 | 5:50 | D/W | Oil Leakage Maintenance | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-2 (T-2) HT | 2023-10-07 08:22 | 2023-10-07 18:38 | 10:16 | S/O | Annual maintenance | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-2 (T-2) HT | 2023-10-08 09:28 | 2023-10-08 13:52 | 4:24 | S/O | Annual maintenance work | 0 | 0 | No interruption
Shariatpur 132/33kV Grid Sub-Station | Auxiliary-01 (PGCB) HT | 2023-10-05 07:40 | 2023-10-05 16:42 | 9:02 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shariatpur 132/33kV Grid Sub-Station | Auxiliary-02 (PGCB) HT | 2023-10-03 07:20 | 2023-10-03 20:10 | 12:50 | S/O | annual maintenance | 0 | 0 | No interruption
Shariatpur 132/33kV Grid Sub-Station | Auxiliary-02 (PGCB) HT | 2023-10-04 07:22 | 2023-10-04 19:00 | 11:38 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Shariatpur 132/33kV Grid Sub-Station | Auxiliary-02 (PGCB) HT | 2023-10-08 08:40 | 2023-10-08 11:00 | 2:20 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Shariatpur 132/33kV Grid Sub-Station | Main Bus - 1 | 2023-10-07 08:22 | 2023-10-07 17:08 | 8:46 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Shariatpur 132/33kV Grid Sub-Station | Main Bus - 2 | 2023-10-08 11:23 | 2023-10-08 17:21 | 5:58 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Shariatpur 132/33kV Grid Sub-Station | T1-406T LT | 2023-10-01 08:29 | 2023-10-01 17:22 | 8:53 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shariatpur 132/33kV Grid Sub-Station | T1-406T LT | 2023-10-02 07:46 | 2023-10-02 18:35 | 10:49 | S/O | Annual Maintenance . | 0 | 0 | No interruption
Shariatpur 132/33kV Grid Sub-Station | T1-406T LT | 2023-10-21 08:05 | 2023-10-21 18:01 | 9:56 | S/O | For Annual Maintenance. | 0 | 0 | No interruption
Shariatpur 132/33kV Grid Sub-Station | T2-416T HT | 2023-10-03 07:23 | 2023-10-03 19:58 | 12:35 | S/O | annul maintenance | 0 | 0 | No interruption
Shariatpur 132/33kV Grid Sub-Station | T2-416T LT | 2023-10-04 07:26 | 2023-10-04 18:58 | 11:32 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Shariatpur 132/33kV Grid Sub-Station | T2-416T LT | 2023-10-22 08:12 | 2023-10-22 17:38 | 9:26 | S/O | Annual Maintenance. | 0 | 0 | No interruption
|  |  | Total : | 899:58 |  | Unserved Energy : |  | 381.1
HVDC Grid Circle
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 HT | 2023-10-10 09:06 | 2023-10-10 16:10 | 7:04 | S/O | Oil centrifuge of Oltc of 230/132 T01 | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | T-1 LT | 2023-10-06 07:23 | 2023-10-06 08:51 | 1:28 | D/W | Bus loop connection between 33 kv Narail feeder DS to T1A Bus | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 LT | 2023-10-17 09:31 | 2023-10-17 13:08 | 3:37 | D/W | Transformer colling fan maintenance | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 HT | 2023-10-18 10:30 | 2023-10-18 11:35 | 1:05 | D/W | Transformer 2 leakage problem observation | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | T-3 LT | 2023-10-15 13:52 | 2023-10-16 10:05 | 20:13 | S/O | Transformer-3 Testing | 0 | 0 | No interruption
|  |  | Total : | 33:27 |  | Unserved Energy : |  | 0
Bogura Grid Circle:
Amnura 132/33kV Grid Sub-Station | T-2 (416T) HT | 2023-10-06 11:50 | 2023-10-06 20:16 | 8:26 | S/O | For changing of OLTC's oil. | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | T-2 (416T) LT | 2023-10-09 12:05 | 2023-10-09 21:41 | 9:36 | S/O | Corrective Maintenance | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | 132KV Bus-B | 2023-10-07 07:55 | 2023-10-07 12:27 | 4:32 | S/O | 132 KV B-Bus DS Maintenance. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-10-07 08:00 | 2023-10-07 11:52 | 3:52 | S/O | Transformer-2 132 kv Bus DS Maintenance. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-10-08 14:33 | 2023-10-08 15:36 | 1:03 | S/O | Talora-33 KV feeder Red hot maintenance work (Talora 33KV bus Isolator.) | 15 | 15.75 | Power interruption
Chapai 132/33kV Grid Sub-Station | T-3 (425T) HT | 2023-10-06 06:03 | 2023-10-06 09:10 | 3:07 | S/O |  | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | 406T HT | 2023-10-02 08:16 | 2023-10-02 18:24 | 10:08 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | 406T LT | 2023-10-01 08:15 | 2023-10-01 17:07 | 8:52 | S/O | Annual Maintenance of 132/33kv T-1 | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | 416T LT | 2023-10-03 08:10 | 2023-10-03 17:55 | 9:45 | S/O | Annual Maintenance of Tr-02 | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | 416T LT | 2023-10-04 09:19 | 2023-10-04 17:53 | 8:34 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | Bus A | 2023-10-17 08:20 | 2023-10-17 16:44 | 8:24 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | Bus B | 2023-10-18 09:17 | 2023-10-18 15:53 | 6:36 | S/O | Annual Maitenance Work | 0 | 0 | No interruption
Mithapukur 132/33kV Grid Sub-Station | TR-1(404T) LT | 2023-10-05 10:10 | 2023-10-05 11:59 | 1:49 | S/O |  | 0 | 0 | No interruption
Mithapukur 132/33kV Grid Sub-Station | TR-2 (414T) LT | 2023-10-08 10:31 | 2023-10-08 16:45 | 6:14 | S/O | Annual Maintenance | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2023-10-30 10:39 | 2023-10-30 12:09 | 1:30 | S/O | T-1 132kv CT(YPH) HEAT SPOT MAINTENANCE. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | TR-3 (425 T) LT | 2023-10-19 07:12 | 2023-10-19 09:07 | 1:55 | S/O | Shutdown by NPBS 1. | 16 | 30.6667 | Power interruption
Palashbari 132/33kV Grid Sub-Station | BUS-A | 2023-10-12 09:16 | 2023-10-12 14:55 | 5:39 | S/O | Annual maintenance | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | BUS-B | 2023-10-14 08:46 | 2023-10-14 14:25 | 5:39 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | TR1-414T LT | 2023-10-16 08:29 | 2023-10-16 13:26 | 4:57 | S/O | Annual maintenance | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | TR1-414T LT | 2023-10-17 08:17 | 2023-10-17 14:59 | 6:42 | S/O | Annual maintenance | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | TR2-404T HT | 2023-10-19 08:30 | 2023-10-19 14:13 | 5:43 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | TR2-404T LT | 2023-10-18 08:20 | 2023-10-18 14:05 | 5:45 | S/O | Annual Maintenance 2023/2024 | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | TR3-424T HT | 2023-10-28 08:20 | 2023-10-28 15:25 | 7:05 | S/O | Annual maintenance | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | TR3-424T LT | 2023-10-26 08:15 | 2023-10-26 14:51 | 6:36 | S/O | Annual maintenance 2023/2024 | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | TR4-434T HT | 2023-10-29 08:30 | 2023-10-29 14:38 | 6:08 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | TR4-434T HT | 2023-10-30 08:30 | 2023-10-30 14:20 | 5:50 | S/O | Annual Maintenance | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-1(407T) HT | 2023-10-17 08:40 | 2023-10-17 16:33 | 7:53 | S/O | Annual Maintenance | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-1(407T) HT | 2023-10-18 08:34 | 2023-10-18 16:02 | 7:28 | S/O | Annual maintenance. | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-2(417T) HT | 2023-10-25 08:35 | 2023-10-25 16:06 | 7:31 | S/O | Anual maintance | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-2(417T) HT | 2023-10-26 08:32 | 2023-10-26 14:52 | 6:20 | S/O | Anual maintance | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) HT | 2023-10-28 08:32 | 2023-10-28 16:35 | 8:03 | S/O | Anual maintance | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) HT | 2023-10-29 08:22 | 2023-10-29 14:39 | 6:17 | S/O | Annual Maintenance | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | T-1 Transformer (403T) LT | 2023-10-03 07:45 | 2023-10-03 10:03 | 2:18 | S/O | 33kv LA Installation work by NESCO | 30 | 69 | Power interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132 kV Main BUS-01 | 2023-10-02 09:01 | 2023-10-02 14:16 | 5:15 | S/O | Isolator allignment work. | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132/33 kV T-01 (406T) HT | 2023-10-02 08:31 | 2023-10-02 16:11 | 7:40 | S/O | Isolator alignment work. | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132/33 kV T-02 (416T) HT | 2023-10-25 15:26 | 2023-10-25 16:30 | 1:04 | S/O | à¦¬à¦¸à¦¨à§à¦¤à¦ªà§à¦° à§©à§© à¦•à§‡à¦­à¦¿ à¦«à¦¿à¦¡à¦¾à¦°à§‡à¦° à¦¬à¦¾à¦¸ à¦¸à¦¾à¦‡à¦¡ à¦°à§‡à¦¡ à¦¹à¦Ÿ à¦¨à¦¿à¦°à¦¸à¦¨ à¦•à¦¾à¦œà§‡à¦° à¦œà¦¨à§à¦¯à¥¤ | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) LT | 2023-10-02 10:19 | 2023-10-02 14:24 | 4:05 | S/O | 132 kV Isolator Maintenance | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | T-1(414T) LT | 2023-10-25 09:14 | 2023-10-25 14:42 | 5:28 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | T-1(414T) LT | 2023-10-26 09:14 | 2023-10-26 12:59 | 3:45 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | T-2 (404T) LT | 2023-10-28 08:44 | 2023-10-28 15:45 | 7:01 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | T-2 (404T) LT | 2023-10-29 09:10 | 2023-10-29 14:41 | 5:31 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | T-3 (424T) HT | 2023-10-18 09:05 | 2023-10-18 14:54 | 5:49 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | T-3 (424T) HT | 2023-10-19 10:20 | 2023-10-19 14:45 | 4:25 | S/O | Annual Maintenance | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | BUS A | 2023-10-03 09:43 | 2023-10-03 11:04 | 1:21 | S/O | Annual Maintenance | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-01 LT | 2023-10-03 09:10 | 2023-10-03 11:30 | 2:20 | S/O | None | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-2 (404T) LT | 2023-10-15 08:15 | 2023-10-15 15:56 | 7:41 | S/O | QF-GMD-39 and the instructions of ALDC Bogura | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-2 (404T) LT | 2023-10-16 08:27 | 2023-10-16 15:56 | 7:29 | S/O | Annual maintanance | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-2 (404T) LT | 2023-10-28 10:21 | 2023-10-28 13:40 | 3:19 | S/O | 33Kv T-2 and T-4 Bus coupler DS Maintenance. | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-3 (424T) LT | 2023-10-17 08:20 | 2023-10-17 16:12 | 7:52 | S/O | For annual maintenance work. | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-3 (424T) LT | 2023-10-18 08:23 | 2023-10-18 12:32 | 4:09 | S/O | Annual maintanance | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-4 (414T) LT | 2023-10-26 08:15 | 2023-10-26 17:17 | 9:02 | S/O | Annual Maintenance | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-4 (414T) LT | 2023-10-28 08:20 | 2023-10-28 15:11 | 6:51 | S/O | Annual Maintenance | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-5 (434T) LT | 2023-10-29 08:26 | 2023-10-29 14:55 | 6:29 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-5 (434T) LT | 2023-10-30 08:28 | 2023-10-30 14:27 | 5:59 | S/O | Annual maintanance | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Main Bus | 2023-10-05 06:12 | 2023-10-05 07:55 | 1:43 | D/W | PGNS (G2G) project has taken shutdown for T4 132kV BUS Loop disconnection work. | 65 | 111.5833 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T2-(425) HT | 2023-10-05 06:03 | 2023-10-05 08:02 | 1:59 | D/W | PGNS (G2G) project has taken shutdown for T4 132kV BUS Loop disconnection work. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | T3-(435) HT | 2023-10-05 06:05 | 2023-10-05 09:17 | 3:12 | D/W | PGNS (G2G) project has taken shutdown for T4 132kV BUS Loop disconnection work. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | T3-(435) LT | 2023-10-02 08:00 | 2023-10-02 11:04 | 3:04 | D/W | Nut bolt tightening | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | T4-(445) HT | 2023-10-02 11:36 | 2023-10-02 11:36 | 0:00 | D/W | Bay equipment replacement under G to G project. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | T4-(445) LT | 2023-10-02 10:58 | 2023-10-02 10:58 | 0:00 | D/W | Bay equipment replacement under G to G project. | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) LT | 2023-10-07 09:14 | 2023-10-07 17:44 | 8:30 | S/O | Annual Maintenance | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) LT | 2023-10-08 08:30 | 2023-10-08 17:44 | 9:14 | S/O | Annual Maintenance | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-2(412T) LT | 2023-10-18 08:40 | 2023-10-19 16:31 | 31:51 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-3(432T) LT | 2023-10-22 08:42 | 2023-10-22 17:10 | 8:28 | S/O | Annual Maintenance | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-3(432T) LT | 2023-10-23 08:55 | 2023-10-23 17:22 | 8:27 | S/O | Annual Maintenance | 0 | 0 | No interruption
|  |  | Total : | 389:20 |  | Unserved Energy : |  | 227
Others :Nil
|  |  | Total : | 0:00 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 2293:49 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: October 2023
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir-01 | 2023-10-23 11:08 | 2023-10-23 16:11 | 5:03 | S/O | ERS Tower wire Relocation | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Mirpur-02 | 2023-10-11 06:24 | 2023-10-11 08:14 | 1:50 | S/O | LA Change | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Kishoreganj 132 kV Ckt-1 | 2023-10-13 11:35 | 2023-10-13 13:12 | 1:37 | S/O | Busbar-1 raiser clamp temperature high | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Kishoreganj 132 kV Ckt-1 | 2023-10-16 08:55 | 2023-10-16 15:33 | 6:38 | S/O | Annual maintenance of kishoreganj end. | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Kishoreganj 132 kV Ckt-1 | 2023-10-17 08:45 | 2023-10-17 15:45 | 7:00 | S/O | Annual maintenance of kishoreganj end. | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Kishoreganj 132 kV Ckt-2 | 2023-10-13 14:36 | 2023-10-13 16:45 | 2:09 | S/O | Busbar-1 raiser clamp temperature high | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Kishoreganj 132 kV Ckt-2 | 2023-10-26 09:08 | 2023-10-26 15:51 | 6:43 | S/O | Annual maintenance work | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Mymensingh- Bhaluka 132 kV Ckt- 01 | 2023-10-28 08:35 | 2023-10-28 17:16 | 8:41 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh Ckt-01 | 2023-10-14 08:47 | 2023-10-14 16:58 | 8:11 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh Ckt-01 | 2023-10-15 08:30 | 2023-10-15 17:37 | 9:07 | S/O | Annual maintenance | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh Ckt-01 | 2023-10-16 08:35 | 2023-10-16 16:34 | 7:59 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh Ckt-01 | 2023-10-17 09:07 | 2023-10-17 15:53 | 6:46 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh Ckt-01 | 2023-10-19 09:00 | 2023-10-19 16:37 | 7:37 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh Ckt-02 | 2023-10-21 08:40 | 2023-10-21 17:01 | 8:21 | S/O | Annual maintenance. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh Ckt-02 | 2023-10-22 09:08 | 2023-10-22 16:55 | 7:47 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh Ckt-02 | 2023-10-23 08:47 | 2023-10-23 15:45 | 6:58 | S/O | Annual maintenance. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh Ckt-02 | 2023-10-25 08:49 | 2023-10-25 16:24 | 7:35 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh Ckt-02 | 2023-10-26 09:17 | 2023-10-26 16:22 | 7:05 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Kodda ckt-1 | 2023-10-16 09:20 | 2023-10-16 16:53 | 7:33 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Kodda ckt-2 | 2023-10-17 09:43 | 2023-10-17 16:06 | 6:23 | S/O | Annual maintenance. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Manikganj-1 | 2023-10-02 06:45 | 2023-10-02 09:05 | 2:20 | S/O | High Temperature Maintenance Work. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Tongi-1 | 2023-10-09 07:36 | 2023-10-09 09:02 | 1:26 | S/O | Due to maint.work | 40 | 57.3333 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | Tongi-1 | 2023-10-11 07:30 | 2023-10-11 09:49 | 2:19 | S/O | Red hot maintenance | 70 | 162.1667 | Power interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Tangail-2 | 2023-10-20 06:19 | 2023-10-21 18:14 | 35:55 | D/W | work at mirzapur | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-1 | 2023-10-15 08:58 | 2023-10-15 16:03 | 7:05 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-1 | 2023-10-21 08:54 | 2023-10-22 14:49 | 29:55 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-1 | 2023-10-31 14:34 | 2023-10-31 16:39 | 2:05 | S/O | Annual maintenance work | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-2 | 2023-10-23 08:55 | 2023-10-23 15:15 | 6:20 | S/O |  | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-2 | 2023-10-25 09:01 | 2023-10-25 16:16 | 7:15 | S/O | For annual maintenance work | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Summit 149 MW PS | 2023-10-27 07:12 | 2023-10-27 21:42 | 14:30 | S/O | Work for 132 kv CT change | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2023-10-07 11:04 | 2023-10-07 13:30 | 2:26 | S/O | 132kv Main Bus-2 riser Red hot removed. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Aminbazar-2 | 2023-10-25 05:59 | 2023-10-26 16:27 | 34:28 | S/O | 132 KV Aminbazar CKT -2 Shifted on ERS tower at Tower no-02. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Old | 2023-10-18 10:24 | 2023-10-18 12:01 | 1:37 | S/O | Hot Spot Maintenance (CT Clamp, Y-Ph) on Mirpur SS end. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Sector-18 | 2023-10-14 07:16 | 2023-10-14 09:53 | 2:37 | S/O | Uttara 3rd phase ,CT (R-Phase) & others point hot spot repairing work. | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | 50 MW Solar Plant | 2023-10-03 06:12 | 2023-10-03 09:14 | 3:02 | S/O | A-Bus S/D | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | 50 MW Solar Plant | 2023-10-30 17:29 | 2023-10-30 18:09 | 0:40 | S/O | Multifunction meter replacement work | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Bhaluka Ckt-1 | 2023-10-29 08:40 | 2023-10-29 16:44 | 8:04 | S/O | S/D due to Annual maintenance | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Bhaluka Ckt-1 | 2023-10-30 08:36 | 2023-10-30 15:31 | 6:55 | S/O | Annual maintenance work | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Bhaluka Ckt-2 | 2023-10-31 08:42 | 2023-10-31 16:57 | 8:15 | S/O |  | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Netrakona Ckt-2 | 2023-10-03 05:56 | 2023-10-03 12:05 | 6:09 | S/O | High temperature | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Kaliakair-2 | 2023-10-20 06:19 | 2023-10-21 18:09 | 35:50 | S/O | To connect with Mirzapur SS | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-1 | 2023-10-15 09:18 | 2023-10-15 17:12 | 7:54 | S/O | Annual maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-1 | 2023-10-16 09:32 | 2023-10-16 17:16 | 7:44 | S/O | Annual maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-1 | 2023-10-17 09:23 | 2023-10-17 16:20 | 6:57 | S/O | Annual maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-1 | 2023-10-18 11:23 | 2023-10-18 17:21 | 5:58 | S/O | Annual maintenance works | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-1 | 2023-10-18 17:50 | 2023-10-18 21:26 | 3:36 | S/O | CT changing work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-2 | 2023-10-21 09:21 | 2023-10-21 16:54 | 7:33 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-2 | 2023-10-22 08:54 | 2023-10-22 16:56 | 8:02 | S/O | Annual maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-2 | 2023-10-25 08:29 | 2023-10-25 14:45 | 6:16 | S/O | Annual maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-1 | 2023-10-03 06:45 | 2023-10-03 08:16 | 1:31 | S/O | Rising temperature maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Uttara 3rd Phase Ckt | 2023-10-01 09:42 | 2023-10-01 16:14 | 6:32 | S/O | Annual maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Uttara 3rd Phase Ckt | 2023-10-02 09:30 | 2023-10-02 16:54 | 7:24 | S/O | Annual Maintenance Work. Deadline checking. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Uttara 3rd Phase Ckt | 2023-10-03 10:10 | 2023-10-03 16:42 | 6:32 | S/O | Annual maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Uttara 3rd Phase Ckt | 2023-10-04 09:10 | 2023-10-04 16:16 | 7:06 | S/O | Annual maintenance (DLC) | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Uttara 3rd Phase Ckt | 2023-10-05 10:27 | 2023-10-05 12:41 | 2:14 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Uttara Ckt | 2023-10-08 09:09 | 2023-10-08 17:11 | 8:02 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Uttara Ckt | 2023-10-10 09:01 | 2023-10-10 17:17 | 8:16 | S/O | Annual maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Uttara Ckt | 2023-10-11 09:05 | 2023-10-11 16:59 | 7:54 | S/O | Annual maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Uttara Ckt | 2023-10-12 09:13 | 2023-10-12 13:27 | 4:14 | S/O | Annual maintenance work | 0 | 0 | No interruption
|  |  | Total : | 464:01 |  | Unserved Energy: |  | 219.5
Dhaka (South) Grid Circle :
Fatullah 132/33kV Grid Sub-Station | 132 kV Madanganj | 2023-10-10 10:40 | 2023-10-10 11:12 | 0:32 | D/W | NLDC Integration | 0 | 0 | Power interruption
Fatullah 132/33kV Grid Sub-Station | 132 kV Shyampur-1 | 2023-10-09 12:15 | 2023-10-09 13:03 | 0:48 | D/W | Scada interegation with NLDC | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 230kV Siddhirganj-1 | 2023-10-11 08:43 | 2023-10-11 17:22 | 8:39 | S/O | Annual Maintenance, 2023-24 | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 230kV Siddhirganj-2 | 2023-10-28 08:46 | 2023-10-28 20:16 | 11:30 | S/O | From other end. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Meghnaghat-1 | 2023-10-09 07:38 | 2023-10-09 17:11 | 9:33 | S/O | For Loop and Clamp Change | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Siddhirganj-2 | 2023-10-30 09:31 | 2023-10-30 16:25 | 6:54 | S/O | Annual maintenance. | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | Fatulla (Pre-Brahmongaon) | 2023-10-10 11:25 | 2023-10-10 12:27 | 1:02 | S/O | Fatullah (before Aggreko Brahmongaon) line sutdown by NLDC | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Shyampur-Hasnabad Ckt-1 | 2023-10-05 09:22 | 2023-10-05 13:38 | 4:16 | S/O | TCS maintenance work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Bashundhara 132 kv Ckt | 2023-10-19 10:10 | 2023-10-19 16:43 | 6:33 | S/O | Corrective maintenance | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Summit 102 MW 132 kv Ckt | 2023-10-14 08:26 | 2023-10-14 11:00 | 2:34 | S/O | Red Hot maintenance | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Kazla Ckt -1 | 2023-10-08 14:30 | 2023-10-08 16:54 | 2:24 | S/O | SCADA work done by DPDC through CCCE. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Kazla Ckt -2 | 2023-10-15 12:30 | 2023-10-15 13:55 | 1:25 | S/O | Kazla-Matuail Maintenance work by DPDC. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Mero Rail - 2 | 2023-10-03 16:25 | 2023-10-27 11:47 | 571:22 | S/O | Metro rail ckt-2 cable terminat. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Motijheel Ckt-1 | 2023-10-17 15:53 | 2023-10-17 16:20 | 0:27 | S/O | Motijheel Ckt -1 SCADA work. (Motijheel end, shut down by DPDC) | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Motijheel Ckt-2 | 2023-10-17 16:25 | 2023-10-17 16:55 | 0:30 | S/O | Motijheel Ckt -2 SCADA work .(Motijheel end, Shut down by DPDC) | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | 230kV Siddhirganj-Maniknagar ckt-1 | 2023-10-01 06:46 | 2023-10-23 07:04 | 528:18 | S/O | Siddirganj-Maniknagar Line-1 Transmission Line Re-routing work. | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | 230kV Siddhirganj-Maniknagar ckt-2 | 2023-10-26 06:20 | 2023-10-26 06:20 | 0:00 | S/O | Re-Routing Of line section Work. | 0 | 0 | No interruption
Munshiganj 132/33kV Grid Sub-Station | Madanganj- Munshiganj- Ckt-2 | 2023-10-25 17:58 | 2023-10-25 18:55 | 0:57 | D/W | Total-Tel (Scada Communication) Work | 0 | 0 | No interruption
Munshiganj 132/33kV Grid Sub-Station | Sinha Peoples Energy Limited (SPEL) 52.5 MW IPP | 2023-10-26 12:55 | 2023-10-26 15:22 | 2:27 | D/W | Scada work By Communication(PGCB) and Totaltell. | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 132 kV Fatullah-2(E05) | 2023-10-10 12:35 | 2023-10-10 13:02 | 0:27 | S/O | Shut down by NLDC | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT2 | 2023-10-14 10:58 | 2023-10-14 15:39 | 4:41 | S/O | Schedule Maintenances Work | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Haripur 2 | 2023-10-30 09:32 | 2023-10-30 16:25 | 6:53 | S/O | Annual Maintenance in Haripur Sub-station. No load shed occurred . Load share by Haripur ckt-1 | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | 335MW EGCB 2 | 2023-10-30 07:38 | 2023-10-30 07:38 | 0:00 | S/O | annual maintenance | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | Haripur 1 | 2023-10-23 08:58 | 2023-10-23 21:07 | 12:09 | S/O | Annual maintenence | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | Maniknagar 2 | 2023-10-26 06:20 | 2023-10-26 06:20 | 0:00 | S/O | Order of NLDC | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | OPSL(IEL-2) | 2023-10-08 13:43 | 2023-10-08 14:46 | 1:03 | S/O | SCADA integration work at OPSL end. | 0 | 0 | No interruption
|  |  | Total : | 1185:24 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
BSRM 230/33kV Grid Sub-Station | Mirsarai Ckt-1 | 2023-10-15 09:05 | 2023-10-15 12:35 | 3:30 | S/O | Anual Maintenans | 0 | 0 | No interruption
Baroaulia 132/33kV Grid Sub-Station | Kulshi | 2023-10-31 07:32 | 2023-10-31 13:30 | 5:58 | S/O | Loop and T clamp hange | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | PHP | 2023-10-01 08:28 | 2023-10-01 15:25 | 6:57 | S/O | Annual Maintenance for dead line checking. | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona- Rangamati Ckt-02 | 2023-10-08 07:57 | 2023-10-08 16:24 | 8:27 | S/O | Annual maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona-Madunaghat Ckt-01 | 2023-10-12 09:01 | 2023-10-15 16:29 | 79:28 | D/W | Project Work | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona-Madunaghat Ckt-01 | 2023-10-16 08:26 | 2023-10-16 16:22 | 7:56 | S/O | Dead line check | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona-Madunaghat Ckt-01 | 2023-10-17 08:36 | 2023-10-17 17:35 | 8:59 | S/O | Annual maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona-Madunaghat Ckt-01 | 2023-10-18 08:51 | 2023-10-18 16:44 | 7:53 | S/O | Annual maintenance (Line) | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona-Madunaghat Ckt-02 | 2023-10-19 08:31 | 2023-10-19 16:41 | 8:10 | S/O | Anuual Maintenance | 0 | 0 | No interruption
Coxsbazar 132/33kV Grid Sub-Station | Doh-Cox Ckt-2 | 2023-10-17 12:46 | 2023-10-17 16:46 | 4:00 | S/O | Distance Relay installation | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Baroiarhat-01 | 2023-10-31 08:20 | 2023-10-31 16:57 | 8:37 | S/O | annual maintenance | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Raojan-01 | 2023-10-19 09:04 | 2023-10-19 17:04 | 8:00 | S/O | Annual maintenance (breaker & bay) | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Raojan-02 | 2023-10-21 09:02 | 2023-10-21 16:44 | 7:42 | S/O | Annual maintenance. | 0 | 0 | No interruption
Khagrachori 132/33kV Grid Sub-Station | RANGAMATI-1 | 2023-10-02 08:45 | 2023-10-02 17:19 | 8:34 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Khagrachori 132/33kV Grid Sub-Station | RANGAMATI-2 | 2023-10-03 08:32 | 2023-10-03 16:11 | 7:39 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Baraulia Circuit-2 | 2023-10-31 07:30 | 2023-10-31 13:30 | 6:00 | S/O | Red hot maintenance work. Baraulia End | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Halishahar CKT-2(Rampur) | 2023-10-18 09:11 | 2023-10-18 12:46 | 3:35 | S/O | Hot Spot Maintenance work at khulshi-Rampur Ckt-2 | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Sholoshahar CKT-1(Madunaghat) | 2023-10-05 14:24 | 2023-10-05 14:24 | 0:00 | D/W | due to project work(Filing work) of ESPNCA of 230/132/33 KV khulshi GIS Sub-Station in 132/33Kv Khulshi Grid sub-station. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Chandraghona-1 | 2023-10-15 08:51 | 2023-10-15 16:30 | 7:39 | S/O | For annual deadline checking and line maintenance | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Chandraghona-2 | 2023-10-10 12:49 | 2023-10-10 16:53 | 4:04 | D/W | For OPGW maintenance work by DCMPS project. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Chandraghona-2 | 2023-10-12 12:55 | 2023-10-12 14:07 | 1:12 | D/W | Shutdown for relay testing and project work by DCMPS project | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Chandraghona-2 | 2023-10-21 08:33 | 2023-10-21 16:36 | 8:03 | S/O | For Annual deadline checking and line maintenance | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Chandraghona-2 | 2023-10-22 09:44 | 2023-10-22 17:09 | 7:25 | S/O | For annual deadline checking and maintenance. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Chandraghona-2 | 2023-10-26 08:46 | 2023-10-26 17:22 | 8:36 | S/O | for corrective maintenance on Chandraghona Circuit 02 | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-T.K. chemical complex | 2023-10-30 08:39 | 2023-10-30 16:57 | 8:18 | S/O | For annual deadline checking. | 0 | 0 | No interruption
Mirsorai 230/33kV Grid Sub-Station | BSRM-2 | 2023-10-15 12:44 | 2023-10-15 15:32 | 2:48 | S/O | Annual maintenance | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Khulshi-2 | 2023-10-18 09:10 | 2023-10-18 12:47 | 3:37 | S/O | Maintenance at Khulshi side | 0 | 0 | No interruption
Rangamati 132/33kV Grid Sub-Station | Chandraghona Ckt-01 | 2023-10-07 08:19 | 2023-10-07 16:23 | 8:04 | S/O | Annual Bay maintenance | 0 | 0 | No interruption
Rangamati 132/33kV Grid Sub-Station | Khagrachari Ckt-01 | 2023-10-04 08:21 | 2023-10-04 16:54 | 8:33 | S/O | Annual maintenance | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Modunaghat Ckt-2(T.K Chemical) | 2023-10-31 09:44 | 2023-10-31 15:15 | 5:31 | S/O |  | 0 | 0 | No interruption
|  |  | Total : | 265:15 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Bibiana 400/230kV Sub-Station | Bibi-Shahzi Ckt-I | 2023-10-30 10:42 | 2023-10-30 16:27 | 5:45 | S/O | AM | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-2 | 2023-10-02 07:21 | 2023-10-02 17:49 | 10:28 | D/W | development work | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 115MW CPGL Power Plant Incomer (L5) | 2023-10-01 09:07 | 2023-10-01 14:34 | 5:27 | S/O | Shutdown taken by AE CPGL for D.S maintenance work | 0 | 0 | No interruption
Chauddagram 132/33kV Grid Sub-Station | Feni-1 | 2023-10-30 07:17 | 2023-10-30 15:45 | 8:28 | S/O | Yearly Maintenance | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Ramganj line-01 | 2023-10-27 06:27 | 2023-10-27 16:12 | 9:45 | D/W | Open Due to Scaffolding Remove work | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Ramganj line-02 | 2023-10-27 06:27 | 2023-10-27 16:13 | 9:46 | D/W | Open Due to Scaffolding Remove work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Cumilla(S) Ckt-3 | 2023-10-20 05:51 | 2023-10-20 09:16 | 3:25 | D/W | Due to maint.work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Kachua Ckt-1 | 2023-10-20 05:51 | 2023-10-20 09:17 | 3:26 | D/W | Due to maint.work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Shahajibazar Ckt-1 | 2023-10-30 10:40 | 2023-10-30 16:28 | 5:48 | S/O | Relay test | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Shahajibazar Ckt-2 | 2023-10-31 09:49 | 2023-10-31 20:09 | 10:20 | S/O | For relay test by SPMD,Cumilla. | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | 53.2MW Lakthanavi | 2023-10-16 08:40 | 2023-10-16 15:28 | 6:48 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Chowddagram-1 | 2023-10-25 09:27 | 2023-10-25 16:39 | 7:12 | S/O | Annual maintenance | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Chowddagram-1 | 2023-10-26 08:48 | 2023-10-26 15:24 | 6:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Cumilla North-1 | 2023-10-20 05:54 | 2023-10-20 09:22 | 3:28 | S/O | 132 KV Bus S/D from Cumilla (N) End | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Cumilla North-2 | 2023-10-20 05:54 | 2023-10-20 09:22 | 3:28 | S/O | 132 KV Bus S/D from Cumilla (N) End | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Cumilla North-3 | 2023-10-20 05:54 | 2023-10-20 09:22 | 3:28 | S/O | 132 KV Bus S/D from Cumilla (N) End | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Sonargaon-1 | 2023-10-30 10:02 | 2023-10-30 16:42 | 6:40 | S/O | SCADA maintenance work at Sonargaon substation | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sylhet-2 | 2023-10-31 10:50 | 2023-10-31 13:16 | 2:26 | S/O | Annual maintenance | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Chowddagram Ckt-1 | 2023-10-16 06:10 | 2023-10-16 11:27 | 5:17 | S/O | S/D Taken for Main bus-1(Bus lop-B Ph.) Red Hot Maintenance work | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Chowddagram Ckt-1 | 2023-10-31 07:22 | 2023-10-31 15:33 | 8:11 | S/O | AMS-2023-24 | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Chowddagram Ckt-2 | 2023-10-16 06:11 | 2023-10-16 11:28 | 5:17 | S/O | S/D Taken for Main bus-1(Bus lop-B Ph.) Red Hot Maintenance work | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Feni-Lanka HFO PS | 2023-10-16 06:25 | 2023-10-16 11:30 | 5:05 | S/O | S/D taken by Bus -1(Bus loop-B-Ph) Red hot Maintenance work | 0 | 0 | No interruption
|  |  | Total : | 136:34 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Barishal 132/33kV Grid Sub-Station | 132kv Bhandaria ckt | 2023-10-25 11:43 | 2023-10-25 12:40 | 0:57 | S/O | Shutdown by ALDC instructions | 27 | 25.65 | Power interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV 50MW Power Station ckt-1 | 2023-10-15 09:39 | 2023-10-15 15:41 | 6:02 | S/O | Due to project work. | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Gopalganj (400kv) ckt-1 | 2023-10-13 09:02 | 2023-10-13 13:34 | 4:32 | S/O | 132 kv bus protection | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Gopalganj (400kv) ckt-2 | 2023-10-13 13:35 | 2023-10-13 18:14 | 4:39 | S/O | 132 kv bus protection | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Rajbari ckt-1 | 2023-10-12 09:59 | 2023-10-12 15:52 | 5:53 | D/W | Due to project work. | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Rajbari ckt-2 | 2023-10-12 16:02 | 2023-10-12 20:31 | 4:29 | D/W | Due to project work. | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Faridpur Ckt-1 | 2023-10-08 08:23 | 2023-10-08 12:34 | 4:11 | S/O | To work in Faridpur end. | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-1 | 2023-10-18 10:41 | 2023-10-18 21:06 | 10:25 | S/O | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-1 | 2023-10-19 09:56 | 2023-10-19 21:50 | 11:54 | D/W | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-2 | 2023-10-25 09:11 | 2023-10-25 22:04 | 12:53 | D/W | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-2 | 2023-10-26 09:05 | 2023-10-26 19:05 | 10:00 | D/W | Madaripur ckt-02 SAS Commissioning | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | 132 kV Central- South -2 | 2023-10-16 08:17 | 2023-10-16 10:45 | 2:28 | S/O | Due to maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Rampal Ckt-2 | 2023-10-10 10:09 | 2023-10-10 10:09 | 0:00 | D/W | Rupsa 800MW project work | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | Jashore-1 | 2023-10-06 20:00 | 2023-10-06 21:33 | 1:33 | S/O | 513S DS High Temperature Point Maintenance. | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | khulna central - 2 | 2023-10-18 09:34 | 2023-10-18 16:40 | 7:06 | S/O | Project Work | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Faridpur - 2 | 2023-10-12 16:01 | 2023-10-12 20:31 | 4:30 | D/W | PW, S/D | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | Khulna Line-1 | 2023-10-10 10:10 | 2023-10-10 10:10 | 0:00 | D/W | khulna ALDC requirement. | 0 | 0 | No interruption
|  |  | Total : | 91:32 |  | Unserved Energy: |  | 25.65
HVDC Grid Circle :
BIPTC | Ishurdi-4 | 2023-10-29 14:49 | 2023-10-29 17:57 | 3:08 | D/W | could not shutdown properly due to problem in line isolator | 0 | 0 | No interruption
BIPTC | Rajshahi-1 | 2023-10-17 13:58 | 2023-10-17 17:48 | 3:50 | D/W | Ruppur power evacuation project. | 0 | 0 | No interruption
BIPTC | Rajshahi-2 | 2023-10-17 13:59 | 2023-10-17 17:49 | 3:50 | D/W | Ruppur power evacuation project. | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Pabna | 2023-10-25 08:09 | 2023-10-25 11:24 | 3:15 | S/O | Annual maintenance | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV HVDC 3 | 2023-10-29 14:54 | 2023-10-29 17:55 | 3:01 | D/W | Project work | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV HVDC 3 | 2023-10-30 10:33 | 2023-10-30 17:26 | 6:53 | D/W | Ruppur- Bogura project work | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV HVDC 4 | 2023-10-30 10:35 | 2023-10-30 17:39 | 7:04 | D/W | Ruppur- Bogura project work | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | NOA-1(L3) | 2023-10-09 06:33 | 2023-10-09 11:20 | 4:47 | S/O | Due to maintenance for Noapara Substation | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | NOA-2(L4) | 2023-10-10 06:18 | 2023-10-10 11:41 | 5:23 | S/O | Shut down from Noapara End. | 0 | 0 | No interruption
|  |  | Total : | 41:11 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Barapukuria 230/132/33kV Grid Sub-Station | Bogura 230 KV Ckt1 | 2023-10-15 08:12 | 2023-10-15 17:12 | 9:00 | D/W | Due to Project work | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Bogura 230 KV Ckt2 | 2023-10-14 09:12 | 2023-10-14 17:21 | 8:09 | D/W | None | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Bogura 230 KV Ckt2 | 2023-10-16 08:49 | 2023-10-16 12:33 | 3:44 | D/W | Due to Project work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-3 | 2023-10-14 08:27 | 2023-10-14 17:15 | 8:48 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-3 | 2023-10-16 08:19 | 2023-10-16 11:54 | 3:35 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-4 | 2023-10-15 07:37 | 2023-10-15 17:29 | 9:52 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai Rahanpur ckt 1 | 2023-10-08 10:21 | 2023-10-08 14:21 | 4:00 | S/O | Telicomimunication test | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai Rahanpur ckt 2 | 2023-10-08 14:24 | 2023-10-08 16:59 | 2:35 | D/W | Due to Project work | 0 | 0 | No interruption
Kurigram 132/33kV Grid Sub-Station | Rangpur-Kurigram Ckt-01 | 2023-10-13 06:03 | 2023-10-13 09:33 | 3:30 | D/W | 132KV Bus DS Installation | 38 | 133 | Power interruption
Rahanpur 400/132kV Grid Sub-Station | Rahanpur-Chapainawabganj 132 KV Line Ckt-02 | 2023-10-08 14:24 | 2023-10-08 16:58 | 2:34 | S/O | Due to maint.work | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Natore-1 | 2023-10-14 06:23 | 2023-10-14 08:08 | 1:45 | S/O | 132 KV Bus Shutdown (Red Hot Maintenance Work) | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Natore-2 | 2023-10-14 06:23 | 2023-10-14 08:10 | 1:47 | S/O | 132 KV Bus Shutdown (Red Hot Maintenance Work) | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV PPP 50 Mw | 2023-10-14 06:01 | 2023-10-14 08:30 | 2:29 | S/O | 132 KV Bus Shutdown (Red Hot Maintenance Work) | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV RPP 50 Mw | 2023-10-14 06:01 | 2023-10-14 08:36 | 2:35 | S/O | 132 KV Bus Shutdown (Red Hot Maintenance Work) | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Raj(new)-1 | 2023-10-14 06:38 | 2023-10-14 08:12 | 1:34 | S/O | Red Hot maintenance at Natore Ckt 1( R-Phase) of 132 kv main BUS. | 60 | 94 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Raj(new)-2 | 2023-10-14 06:38 | 2023-10-14 08:14 | 1:36 | S/O | Red Hot maintenance at Natore Ckt 1( R-Phase) of 132 kv main BUS. | 60 | 96 | Power interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132 kV Rajshahi ckt-02 | 2023-10-14 06:36 | 2023-10-14 08:14 | 1:38 | S/O | None | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 230 Kv BIPTC Ckt-01 | 2023-10-17 13:58 | 2023-10-17 17:48 | 3:50 | S/O | Due to maint.work | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 230 Kv BIPTC Ckt-02 | 2023-10-17 13:59 | 2023-10-17 17:49 | 3:50 | S/O | Due to maint.work | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Teesta Solar-2 | 2023-10-12 18:15 | 2023-10-12 19:13 | 0:58 | D/W | Axillary Contact Change | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | 132 kV BUS Coupler | 2023-10-02 08:30 | 2023-10-02 13:10 | 4:40 | S/O | Annual Maintenance | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | 132 kV BUS Coupler | 2023-10-03 09:40 | 2023-10-03 11:08 | 1:28 | S/O | Due to maint.work | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Baghabari Express | 2023-10-05 06:12 | 2023-10-05 07:59 | 1:47 | D/W | PGNS (G2G) project has taken shutdown for T4 132kV BUS Loop disconnection work. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Baghabari Express | 2023-10-21 08:14 | 2023-10-21 13:04 | 4:50 | D/W | Ullapara 132/33 kv Project work | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Shahjadpur | 2023-10-18 08:31 | 2023-10-18 16:53 | 8:22 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Shahjadpur | 2023-10-19 08:27 | 2023-10-19 16:00 | 7:33 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-1 | 2023-10-05 06:07 | 2023-10-05 08:04 | 1:57 | D/W | PGNS (G2G) project has taken shutdown for T4 132kV BUS Loop disconnection work. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 2023-10-05 06:12 | 2023-10-05 08:04 | 1:52 | D/W | PGNS (G2G) project has taken shutdown for T4 132kV BUS Loop disconnection work. | 0 | 0 | No interruption
|  |  | Total : | 110:18 |  | Unserved Energy: |  | 323
Others :NIL
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 2258:27 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:October 2023
| Area | Previous Month (September' 2023) |  |  |  | Current Month (October '2023)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 26 | 12 | 51 | 89 | 26 | 13 | 89 | 128
2 | Dhaka (South) Grid Circle. | 24 | 11 | 43 | 78 | 30 | 16 | 54 | 100
3 | Chattogram Grid Circle. | 20 | 12 | 32 | 64 | 25 | 8 | 45 | 78
4 | Cumilla Grid Circle. | 47 | 17 | 19 | 83 | 14 | 3 | 46 | 63
5 | Khulna Grid Circle. | 18 | 13 | 47 | 78 | 20 | 5 | 92 | 117
6 | HVDC Grid Circle | 7 | 10 | 13 | 30 | 11 | 19 | 14 | 44
7 | Bogura Grid Circle. | 20 | 46 | 53 | 119 | 21 | 21 | 93 | 135
8 | Others | 2 | 1 |  | 3 | 0 | 0 |  | 0
9 | Total | 164 | 122 | 258 | 544 | 147 | 85 | 433 | 665
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:October 2023
| Area | Previous Month (September' 2023) |  |  |  | Current Month (October '2023)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 1074.2 | 488.28 | 1338.58 | 2901.06 | 3057.88 | 905.37 | 879.63 | 4842.88
2 | Dhaka (South) Grid Circle. | 327.96 | 394.58 | 571.07 | 1293.61 | 626.53 | 124.75 | 225.83 | 977.11
3 | Chattogram Grid Circle. | 180.41 | 70.67 | 1106.27 | 1357.35 | 28.5 | 63.3 | 203.55 | 295.35
4 | Cumilla Grid Circle. | 264.07 | 207.65 | 135.93 | 607.65 | 752.21 | 0 | 894.67 | 1646.88
5 | Khulna Grid Circle. | 163.77 | 607.06 | 641.48 | 1412.31 | 668.55 | 43.92 | 406.75 | 1119.22
6 | HVDC Grid Circle | 71.5 | 76.42 | 75.83 | 223.75 | 98.62 | 283.1 | 0 | 381.72
7 | Bogura Grid Circle. | 135.13 | 1056.27 | 1260.2 | 2451.6 | 420.22 | 759.69 | 550 | 1729.91
8 | Others | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Total | 2217.04 | 2900.93 | 5129.36 | 10247.33 | 5652.51 | 2180.13 | 3160.43 | 10993.07
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:October 2023
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 12 | 6 | 18 | 2 | 3 | 7 | 2180.38
2 | Dhaka (South) | 5031.6 | 10 | 3 | 13 | 3 | 3 | 7 | 954.61
3 | Chattogram | 2042 | 2 | 1 | 3 |  | 2 | 1 | 266.85
4 | Khulna | 2434 | 16 | 7 | 23 | 9 | 2 | 12 | 723.5
5 | HVDC | 5954.3 | 17 |  | 17 | 1 | 3 | 13 | 381.72
6 | Bogura | 3145.6 | 18 | 4 | 22 | 5 | 3 | 14 | 914.23
7 | Cumilla | 2981 | 7 | 10 | 17 | 5 | 3 | 9 | 1126.55
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 6547.84
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.96%
2 | Dhaka (South) | 99.34%
3 | Chattogram | 99.26%
4 | Khulna | 99.95%
5 | HVDC | 99.7% | [6 empty] | Executive Engineer
6 | Bogura | 99.92% | [6 empty] | Information Management Division
7 | Cumilla | 99.88% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:October 2023
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 7 | 2 | 9 | 1 | 2 | 6 | 2662.5
2 | Dhaka (South) | 990.29 | - | 1 |  | 1 | 1 |  |  | 22.5
3 | Chattogram | 917 | - | 2 |  | 2 | 1 |  | 1 | 28.5
4 | Khulna | 1238.4 | - | 2 | 1 | 3 |  | 1 | 2 | 395.72
5 | HVDC | 1325 | - | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | 5 | 3 | 8 | 1 |  | 7 | 815.67
7 | Cumilla | 1648.16 | - | 1 |  | 1 |  |  | 1 | 520.33
8 | Others | - | - | - | - | - | - | - | - | -
| Total | 10176.6215 | [7 empty] | 4445.22
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.97%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.98%
4 | Khulna | 99.97%
5 | Bheramara (HVDC) | 100%
6 | Bogura | 99.98%
7 | Cumilla | 99.99%
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:October 2023
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2023-10-01 | 20 | - | 11 | 14hr26 min | 2 | 3hr32 min | - | - | 1 | 2:30 |  |  | Aminbazar zone blackout at 00:45 Due to 230kv bus coupler y phase CT fire hazard holl 230kv bus black out by 400kv ATR 2 and ATR 3 Trip at a time all 230 and 132 kv side power out
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:October 2023
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Agargaon 230/132kV Grid Sub-Station | 1 | 0:44 | 171.6
Aminbazar 400/230/132kV Grid Sub-Station | 1 | 2:30 | 990
Jamalpur 132/33kV Grid Sub-Station | 1 | 4:56 | 74
Kishoreganj 132/33kV Grid Sub-Station | 2 | 2:02 | 4.1
Manikganj 132/33kV Grid Sub-Station | 2 | 0:12 | 3.33
Sherpur 132/33kV Grid Sub-Station | 5 | 8:48 | 277.25
Agargaon 230/132kV Grid Sub-Station | 5 | 10:10 | 2379
Kabirpur 132/33kV Grid Sub-Station | 1 | 0:30 | 20
Kishoreganj 132/33kV Grid Sub-Station | 1 | 1:06 | 44
Mirpur 132/33kV Grid Sub-Station | 1 | 48:10 | 17.8
Tongi 230/132/33kV Grid Sub-Station | 1 | 0:35 | 90.6667
Jamalpur 132/33kV Grid Sub-Station | 3 | 11:04 | 317
Kabirpur 132/33kV Grid Sub-Station | 3 | 5:47 | 454.17
Fatullah 132/33kV Grid Sub-Station | 2 | 0:23 | 20.6
Maniknagar 132/33kV Grid Sub-Station | 3 | 6:38 | 563.63
Munshiganj 132/33kV Grid Sub-Station | 1 | 2:14 | 55.8333
Narshingdi 132/33kV Grid Sub-Station | 1 | 0:05 | 3.3333
Rampura 230/132kV Grid Sub-Station | 1 | 102:53 | 16.4613
Sonargaon 132/33kV Grid Sub-Station | 2 | 2:06 | 68.92
Haripur 230/132kV Grid Sub-Station | 1 | 0:10 | 22.5
Narshingdi 132/33kV Grid Sub-Station | 1 | 0:49 | 24.5
Sonargaon 132/33kV Grid Sub-Station | 2 | 5:02 | 201.33
Hathazari 230/132/33kV Grid Sub-Station | 1 | 0:51 | 15.3
Khulshi 132/33kV Grid Sub-Station | 1 | 0:36 | 48
Baroaulia 132/33kV Grid Sub-Station | 2 | 2:10 | 28.5
Chandraghona 132/33kV Grid Sub-Station | 1 | 8:52 | 203.55
Chandpur 132/33kV Grid Sub-Station | 2 | 1:05 | 20.47
Cumilla(N) 230/132/33kV Grid Sub-Station | 3 | 9:50 | 166.55
Feni 132/33kV Grid Sub-Station | 2 | 2:49 | 45.07
Chowmuhani 132/33kV Grid Sub-Station | 1 | 7:26 | 520.3333
Chandpur 132/33kV Grid Sub-Station | 1 | 0:25 | 12.0833
Cumilla(N) 230/132/33kV Grid Sub-Station | 8 | 18:26 | 539.38
Cumilla(S) 132/33kV Grid Sub-Station | 1 | 0:15 | 10
Feni 132/33kV Grid Sub-Station | 2 | 3:49 | 287
Sunamganj 132/33kV Grid Sub-Station | 1 | 2:34 | 46.2
Barishal 132/33kV Grid Sub-Station | 5 | 0:40 | 52.08
Gollamari 132/33kV Grid Sub-Station | 3 | 6:48 | 151.87
Mongla 132/33kV Grid Sub-Station | 7 | 8:12 | 123.2
Satkhira 132/33kV Grid Sub-Station |  | 1:01 | 15.25
Gopalganj 132/33kV Grid Sub-Station | 2 | 7:07 | 370.7
Faridpur 132/33kV Grid Sub-Station | 3 | 5:41 | 181.83
Gollamari 132/33kV Grid Sub-Station | 2 | 6:17 | 125.67
Noapara 132/33kV Grid Sub-Station | 1 | 2:00 | 40
Rajbari 132/33kV Grid Sub-Station | 1 | 1:52 | 33.6
Barishal 132/33kV Grid Sub-Station | 1 | 0:57 | 25.67
Bhangura 132/33kV Grid Sub-Station | 9 | 13:23 | 108.88
Jashore 132/33kV Grid Sub-Station | 1 | 0:20 | 13
Jhenaidah 132/33kV Grid Sub-Station | 2 | 2:20 | 58.33
Kushtia 132/33kV Grid Sub-Station | 4 | 5:37 | 168.5
Pabna 132/33kV Grid Sub-Station | 1 | 1:39 | 33
Barapukuria 230/132/33kV Grid Sub-Station | 2 | 3:07 | 43.27
Jaldhaka 132/33kV Grid Sub-Station | 1 | 0:35 | 15.1667
Mahasthangarh 132/33kV Grid Sub-Station | 1 | 1:06 | 22
Mithapukur 132/33kV Grid Sub-Station | 4 | 1:46 | 30.27
Naogaon 132/33kV Grid Sub-Station | 1 | 0:27 | 19.8
Natore 132/33kV Grid Sub-Station | 1 | 1:23 | 55.3333
Purbasadipur 132/33kV Grid Sub-Station | 5 | 6:06 | 155
Rangpur 132/33kV Grid Sub-Station | 3 | 6:36 | 346.4
Barapukuria 230/132/33kV Grid Sub-Station | 1 | 0:12 | 20
Purbasadipur 132/33kV Grid Sub-Station | 4 | 7:24 | 472.67
Bogura 132/33kV Grid Sub-Station | 1 | 1:03 | 15.75
Natore 132/33kV Grid Sub-Station | 1 | 1:55 | 30.6667
Purbasadipur 132/33kV Grid Sub-Station | 1 | 2:18 | 69
Sirajganj 132/33kV Grid Sub-Station | 1 | 1:43 | 111.5833
Kurigram 132/33kV Grid Sub-Station | 1 | 3:30 | 133
Rajshahi 132/33kV Grid Sub-Station | 2 | 3:10 | 190
Total Unserved energy : | 139 | 382:17 | 10993.9513
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:October 2023
Sl. No | Name | date_time | ss_MW
1 | Aftabnagar 132/33kV Grid Sub-Station | 2023-10-01 18:00 | 38
2 | Agargaon 230/132kV Grid Sub-Station | 2023-10-12 13:00 | 98
3 | Banani 132/33kV Grid Sub-Station | 2023-10-21 07:00 | 125.4
4 | Bangabhaban 132/33kV Grid Sub-Station | 2023-10-15 11:00 | 19
5 | Bashundhara 132/33kV Grid Sub-Station | 2023-10-01 18:30 | 202
6 | BashundharaCement 132/33kV Sub-Station | 2023-10-21 12:00 | 11
7 | Bhulta 132/33kV Grid Sub-Station | 2023-10-11 | 262
8 | Cantonment 132/33kV GIS Grid Sub-Station | 2023-10-01 18:00 | 176
9 | Charsaidpur 132/33kV Sub-Station | 2023-10-05 15:00 | 36
10 | Dhaka University 132/33kV Grid Sub-Station | 2023-10-22 13:00 | 48
11 | Dhamrai 132/33kV Grid Sub-Station | 2023-10-11 18:00 | 138
12 | Dhanmondi 132/33kV Grid Sub-Station | 2023-10-02 13:00 | 148
13 | Fatullah 132/33kV Grid Sub-Station | 2023-10-21 16:00 | 71
14 | Ghorashal 230/132/33kV Sub-Station | 2023-10-02 21:00 | 74
15 | Gulshan 132/33kV Grid Sub-Station | 2023-10-02 12:00 | 136
16 | HaripurSBU 132/33kV Sub-Station | 2023-10-10 15:00 | 173
17 | Hasnabad 132/33kV Grid Substation | 2023-10-15 19:00 | 115
18 | Joydebpur 132/33kV Grid Sub-Station | 2023-10-16 18:30 | 183
19 | Kabirpur 132/33kV Grid Sub-Station | 2023-10-16 12:00 | 301
20 | Kallyanpur 132/33kV Grid Sub-Station | 2023-10-12 | 129
21 | Kamrangirchar 132/33kV Grid Sub-Station | 2023-10-17 13:00 | 66
22 | Kazla 132/33kV Grid Sub-Station | 2023-10-09 13:00 | 107
23 | Keranigonj 230/132/33kV Grid Sub-Station | 2023-10-09 18:30 | 78
24 | Kodda 132/33kV Grid Sub-Station | 2023-10-19 18:00 | 319
25 | Lalbag 132/33kV Grid Sub-Station | 2023-10-14 13:00 | 94
26 | Madanganj 132/33kV Grid Sub-Station | 2023-10-02 21:00 | 42
27 | Madartek 132/33kV Grid Sub-Station | 2023-10-02 23:00 | 87.84
28 | Manikganj 132/33kV Grid Sub-Station | 2023-10-11 19:30 | 115
29 | Maniknagar 132/33kV Grid Sub-Station | 2023-10-12 13:00 | 106
30 | Matuail 132/33kV Grid Sub-Station | 2023-10-15 12:00 | 74
31 | Millgate Tongi 132/33kV Grid Sub-Station | 2023-10-03 12:00 | 112
32 | Mirpur 132/33kV Grid Sub-Station | 2023-10-11 18:00 | 138.5
33 | Mirzapur 132/33kV GIS Grid Sub-Station | 2023-10-29 10:00 | 0
34 | MI_Cement 132/33kV Grid Sub-Station | 2023-10-15 17:00 | 20.2
35 | Mogbazar 132/33kV Grid Sub-Station | 2023-10-01 12:00 | 146.4
36 | Motijheel 132/33kV Grid Sub-Station | 2023-10-02 13:00 | 49
37 | Munshiganj 132/33kV Grid Sub-Station | 2023-10-10 17:00 | 111
38 | Narinda 132/33kV Grid Sub-Station | 2023-10-21 13:00 | 84
39 | Narshingdi 132/33kV Grid Sub-Station | 2023-10-01 18:30 | 188
40 | Nawabganj 132/33kV Grid Sub-Station | 2023-10-01 22:00 | 54
41 | New Tongi 132/33kV Grid Sub-Station | 2023-10-02 12:00 | 81.4
42 | Postogola 132/33kV Grid Sub-Station | 2023-10-11 13:00 | 58
43 | Purbachal 132/33kV Grid Sub-Station | 2023-10-12 18:00 | 23
44 | Rahim Steel 132/33kV Sub-Station | 2023-10-25 13:00 | 54
45 | Rajendrapur 132/33kV Grid Sub-Station | 2023-10-12 19:00 | 100
46 | Satmasjid 132/33kV Grid Sub-Station | 2023-10-09 18:30 | 143
47 | Savar 132/33kV Grid Sub-Station | 2023-10-01 15:00 | 194
48 | SevenRings 132/11kV Sub-Station | 2023-10-24 17:00 | 12.55
49 | ShahCement 132/33kV Grid Sub-Station | 2023-10-19 | 37
50 | Shitalakhya 132/33kV Grid Sub-Station | 2023-10-02 12:00 | 107
51 | Shyampur 132/33kV Grid Sub-Station | 2023-10-25 13:00 | 170
52 | Siddhirganj 132/33kV Grid Sub-Station | 2023-10-08 12:00 | 124
53 | Sonargaon 132/33kV Grid Sub-Station | 2023-10-17 01:00 | 106
54 | Sreepur 230/132/33kV Grid Sub-Station | 2023-10-02 18:30 | 84
55 | Srinagar 132/33kV Grid Sub-Station | 2023-10-12 21:00 | 45.9
56 | Tongi 230/132/33kV Grid Sub-Station | 2023-10-01 08:00 | 139
57 | Ullon 132/33kV Grid Sub-Station | 2023-10-19 18:00 | 46
58 | Uttara 132/33kV Grid Sub-Station | 2023-10-03 11:00 | 86
59 | UttaraNew 132/33kV Grid Sub-Station | 2023-10-01 15:00 | 68
60 | Zigatola 132/33kV Grid Sub-Station | 2023-10-02 22:00 | 94
61 | Agrabad 132/33kV Grid Sub-Station | 2023-10-18 18:00 | 90
62 | AKS 132/33kV Grid Sub-Station | 2023-10-22 17:00 | 15
63 | AKSML 230/33kV Grid Sub-Station | 2023-10-23 15:00 | 121
64 | Bakulia 132/33kV Grid Sub-Station | 2023-10-19 18:00 | 109
65 | Baroaulia 132/33kV Grid Sub-Station | 2023-10-19 23:00 | 85
66 | Baroirhat 132/33kV Grid Sub-Station | 2023-10-18 18:00 | 66
67 | BSRM 230/33kV Grid Sub-Station | 2023-10-31 18:00 | 190
68 | Chandraghona 132/33kV Grid Sub-Station | 2023-10-02 18:00 | 31
69 | Coxsbazar 132/33kV Grid Sub-Station | 2023-10-01 19:30 | 131
70 | Dohazari 132/33kV Grid Sub-Station | 2023-10-01 20:00 | 90
71 | GPH 230/33kV Grid Sub-Station | 2023-10-25 19:30 | 99
72 | Halishahar 132/33kV Grid Sub-Station | 2023-10-22 11:00 | 120.5
73 | Hathazari 230/132/33kV Grid Sub-Station | 2023-10-24 04:00 | 136
74 | Juldah 132/33kV Grid Sub-Station | 2023-10-02 14:00 | 29
75 | Kalurghat 132/33kV Grid Sub-Station | 2023-10-31 12:00 | 38
76 | Khagrachori 132/33kV Grid Sub-Station | 2023-10-18 18:00 | 34
77 | Khulshi 132/33kV Grid Sub-Station | 2023-10-10 18:30 | 187
78 | KSRM 132/33kV Grid Sub-Station | 2023-10-05 13:00 | 52.5
79 | Madunaghat 132/33kV Grid Sub-Station | 2023-10-01 18:30 | 62
80 | Matarbari 132/33kV Sub-Station | 2023-10-16 19:00 | 46
81 | Mirsorai 230/33kV Grid Sub-Station | 2023-10-09 18:30 | 5
82 | Modern Steel 132/11kV Grid Sub-Station | 2023-10-07 18:30 | 0.26
83 | Rampur 230/132/33 kV GIS Grid Sub-Station | 2023-10-10 18:30 | 31
84 | Rangamati 132/33kV Grid Sub-Station | 2023-10-02 18:30 | 20
85 | Shahmirpur 132/33kV Grid Sub-Station | 2023-10-10 07:00 | 54
86 | Shikalbaha 132/33kV Sub-Station | 2023-10-29 | 32
87 | Sholosohor 132/33kV Grid Sub-Station | 2023-10-21 13:00 | 45
88 | SSM 132/33kV Grid Sub-Station | 2023-10-11 13:00 | 16
89 | TK chemical 132kV Grid Sub-Station | 2023-10-17 18:00 | 30.5
90 | Ashuganj 230/132/33kV Sub-Station | 2023-10-17 23:00 | 83
91 | Brahmanbaria 132/33kV Grid Sub-Station | 2023-10-17 20:00 | 175
92 | Chandpur 132/33kV Grid Sub-Station | 2023-10-01 21:00 | 76
93 | Chauddagram 132/33kV Grid Sub-Station | 2023-10-11 19:00 | 62
94 | Chowmuhani 132/33kV Grid Sub-Station | 2023-10-10 19:30 | 234
95 | Cumilla(N) 230/132/33kV Grid Sub-Station | 2023-10-18 20:00 | 198
96 | Cumilla(S) 132/33kV Grid Sub-Station | 2023-10-22 18:00 | 171
97 | Daudkandi 132/33kV Grid Sub-Station | 2023-10-11 20:00 | 148
98 | Feni 132/33kV Grid Sub-Station | 2023-10-11 18:00 | 125
99 | Kachua 132/33kV Grid Sub-Station | 2023-10-02 18:30 | 87
100 | PHP 132/33kV Sub-Station | 2023-10-13 18:00 | 10
101 | Ramganj 132/33kV Grid Sub-Station | 2023-10-12 18:00 | 120
102 | Bhaluka 132/33kV Grid Sub-Station | 2023-10-13 04:00 | 196
103 | Jamalpur 132/33kV Grid Sub-Station | 2023-10-02 19:00 | 174
104 | Kishoreganj 132/33kV Grid Sub-Station | 2023-10-02 18:30 | 160
105 | Mymensingh 132/33kV Grid Sub-Station | 2023-10-02 22:00 | 236
106 | Netrakona 132/33kV Grid Sub-Station | 2023-10-01 20:00 | 138
107 | Sherpur 132/33kV Grid Sub-Station | 2023-10-02 21:00 | 156
108 | Tangail 132/33kV Grid Sub-Station | 2023-10-12 19:00 | 232
109 | Beanibazar 132/33kV Grid Sub-Station | 2023-10-01 | 86
110 | Chhatak 132/33kV Grid Sub-Station | 2023-10-10 20:00 | 34
111 | Fenchuganj 230/132/33kV Grid Sub-Station | 2023-10-01 18:00 | 49
112 | Kulaura 132/33kV Grid Sub-Station | 2023-10-01 | 48
113 | Shahjibazar 132/33kV Grid Sub-Station | 2023-10-01 18:00 | 124
114 | Sreemongol 132/33kV Grid Sub-Station | 2023-10-02 18:30 | 70
115 | Sunamganj 132/33kV Grid Sub-Station | 2023-10-01 18:00 | 56
116 | Sylhet (South) 132/33kV GIS Grid Sub-Station | 2023-10-26 18:00 | 18
117 | Sylhet 132/33kV Grid Sub-Station | 2023-10-01 18:00 | 163
118 | Bagerhat 132/33kV Grid Sub-Station | 2023-10-01 18:30 | 95
119 | Benapole 132/33kV Grid Sub-Station | 2023-10-06 18:30 | 64
120 | Bheramara(GK) 132/33kV Grid Sub-Station | 2023-10-11 19:30 | 64
121 | Chuadanga 132/33kV Grid Sub-Station | 2023-10-11 19:00 | 111
122 | Faridpur 132/33kV Grid Sub-Station | 2023-10-09 21:00 | 168
123 | Goalpara 132/33kV Grid Sub-Station | 2023-10-11 19:00 | 42
124 | Gollamari 132/33kV Grid Sub-Station | 2023-10-11 13:00 | 77
125 | Gopalganj 132/33kV Grid Sub-Station | 2023-10-08 18:30 | 111
126 | Jashore 132/33kV Grid Sub-Station | 2023-10-11 19:00 | 147
127 | Jhenaidah 132/33kV Grid Sub-Station | 2023-10-11 19:00 | 134
128 | Khulna (C) 132/33kV Grid Sub-Station | 2023-10-07 18:30 | 100
129 | Kushtia 132/33kV Grid Sub-Station | 2023-10-09 18:30 | 142
130 | Madaripur 132/33kV Grid Sub-Station | 2023-10-12 21:00 | 108
131 | Magura 132/33kV Grid Sub-Station | 2023-10-14 18:30 | 70
132 | Mongla 132/33kV Grid Sub-Station | 2023-10-22 11:00 | 43
133 | Narail 132/33kV Grid Sub-Station | 2023-10-12 18:30 | 60
134 | Noapara 132/33kV Grid Sub-Station | 2023-10-12 18:30 | 53
135 | Rajbari 132/33kV Grid Sub-Station | 2023-10-11 19:00 | 74
136 | Satkhira 132/33kV Grid Sub-Station | 2023-10-09 21:00 | 129
137 | Shariatpur 132/33kV Grid Sub-Station | 2023-10-22 12:00 | 96
138 | Barguna 132/33kV Grid Sub-Station | 2023-10-09 22:00 | 22
139 | Barishal 132/33kV Grid Sub-Station | 2023-10-14 19:00 | 113
140 | Barishal 230/132kV Grid Sub-Station | 2023-10-12 19:30 | 104
141 | Bhandaria 132/33kV Grid Sub-Station | 2023-10-11 21:00 | 60
142 | Borhanuddin 230/33kV Grid Sub-Station | 2023-10-01 21:00 | 64
143 | Patuakhali 132/33kV Grid Sub-Station | 2023-10-10 22:00 | 111
144 | Payra 400/132/33kV Grid Sub-Station | 2023-10-16 20:00 | 30
145 | Amnura 132/33kV Grid Sub-Station | 2023-10-09 22:00 | 48
146 | Bhangura 132/33kV Grid Sub-Station | 2023-10-09 19:00 | 36
147 | Bog-Sherpur 132/33kV Grid Sub-Station | 2023-10-22 19:30 | 68
148 | Bogura 132/33kV Grid Sub-Station | 2023-10-01 19:00 | 167
149 | Chapai 132/33kV Grid Sub-Station | 2023-10-12 | 61
150 | Ishurdi 132/33kV Grid Sub-Station | 2023-10-09 18:30 | 79
151 | Joypurhat 132/33kV Grid Sub-Station | 2023-10-01 19:00 | 61
152 | Mahasthangarh 132/33kV Grid Sub-Station | 2023-10-01 20:00 | 80
153 | Naogaon 132/33kV Grid Sub-Station | 2023-10-11 21:00 | 130
154 | Natore 132/33kV Grid Sub-Station | 2023-10-11 21:00 | 146
155 | Niamatpur 132/33kV Grid Sub-Station | 2023-10-01 22:00 | 78
156 | Pabna 132/33kV Grid Sub-Station | 2023-10-11 19:30 | 127
157 | Rajshahi 132/33kV Grid Sub-Station | 2023-10-11 20:00 | 158
158 | Rajshahi 230/132/33kV Grid Sub-Station | 2023-10-31 20:00 | 37
159 | Ruppur 132/11kV Grid Sub-Station | 2023-10-01 11:00 | 6.4
160 | Shahjadpur 132/33kV Grid Sub-Station | 2023-10-11 19:00 | 112
161 | Sirajganj 132/33kV Grid Sub-Station | 2023-10-11 19:00 | 123
162 | Barapukuria 230/132/33kV Grid Sub-Station | 2023-10-15 18:30 | 63
163 | Jaldhaka 132/33kV Grid Sub-Station | 2023-10-02 19:00 | 80
164 | Kurigram 132/33kV Grid Sub-Station | 2023-10-12 18:00 | 93
165 | Lalmonirhat 132/33kV Grid Sub-Station | 2023-10-02 18:30 | 53
166 | Mithapukur 132/33kV Grid Sub-Station | 2023-10-17 18:00 | 66
167 | Palashbari 132/33kV Grid Sub-Station | 2023-10-01 22:00 | 124
168 | Panchagarh 132/33kV Grid Sub-Station | 2023-10-02 18:30 | 59
169 | Purbasadipur 132/33kV Grid Sub-Station | 2023-10-11 19:00 | 118
170 | Rangpur 132/33kV Grid Sub-Station | 2023-10-01 19:00 | 150
171 | Saidpur 132/33kV Grid Sub-Station | 2023-10-02 18:30 | 112
172 | Thakurgaon 132/33kV Grid Sub-Station | 2023-10-09 19:00 | 99
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:October 2023
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 5261.84 | 2023-10-02 | 12:00
Chattogram | 1388 | 2023-10-21 | 19:30
Cumilla | 1362 | 2023-10-11 | 21:00
Mymensingh | 1145 | 2023-10-08 | 19:30
Sylhet | 589 | 2023-10-01 | 18:00
Khulna | 1739.8 | 2023-10-11 | 19:00
Barishal | 466 | 2023-10-10 | 22:00
Rajshahi | 1447.2 | 2023-10-09 | 19:30
Rangpur | 951 | 2023-10-02 | 18:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month:October 2023
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar 400/230/132kV Grid Sub-Station | 400 | 401 | 2023-10-31 06:00 | 379 | 2023-10-01 22:00
2 | Bhulta 400/230kV Grid Sub-Station | 400 | 405 | 2023-10-20 18:00 | 381 | 2023-10-01 12:00
3 | Bibiana 400/230kV Sub-Station | 400 | 410 | 2023-10-18 19:00 | 379 | 2023-10-08 07:00
4 | BIPTC | 400 | 406 | 2023-10-25 04:00 | 391 | 2023-10-26 18:00
5 | Gopalganj 400/132kV Grid Sub-Station | 400 | 412 | 2023-10-06 01:00 | 390 | 2023-10-01 22:00
6 | Kaliakoir 400/230/132kV Grid Sub-Station | 400 | 411 | 2023-10-04 20:00 | 352 | 2023-10-23 18:00
7 | Payra 400kV Sub-Station | 400 | 416 | 2023-10-21 05:00 | 403 | 2023-10-01 21:00
8 | Rahanpur 400/132kV Grid Sub-Station | 400 | 415 | 2023-10-12 17:00 | 391 | 2023-10-02 02:00
9 | Rampal 400/230kV Grid Sub-Station | 400 | 410 | 2023-10-16 08:00 | 394 | 2023-10-01
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon 230/132kV Grid Sub-Station | 230 | 238 | 2023-10-06 05:00 | 218 | 2023-10-01 11:00
2 | AKSML 230/33kV Grid Sub-Station | 230 | 240 | 2023-10-22 18:00 | 221 | 2023-10-09 01:00
3 | Baghabari 230/132kV Grid Sub-Station | 230 | 234 | 2023-10-25 14:00 | 218 | 2023-10-01 22:00
4 | Barapukuria 230/132/33kV Grid Sub-Station | 230 | 236 | 2023-10-10 01:00 | 210 | 2023-10-03 18:30
5 | Barishal 230/132kV Grid Sub-Station | 230 | 240 | 2023-10-27 08:00 | 207 | 2023-10-09 19:30
6 | Bheramara 230/132kV Grid Sub-Station | 230 | 237 | 2023-10-08 06:00 | 221 | 2023-10-11 18:00
7 | Bogura 230/132kV Grid Sub-Station | 230 | 238 | 2023-10-10 17:00 | 218 | 2023-10-01 01:00
8 | BSRM 230/33kV Grid Sub-Station | 230 | 238 | 2023-10-07 19:30 | 222 | 2023-10-01 01:00
9 | Cumilla(N) 230/132/33kV Grid Sub-Station | 230 | 236 | 2023-10-18 19:00 | 222 | 2023-10-01 12:00
10 | Fenchuganj 230/132/33kV Grid Sub-Station | 230 | 240 | 2023-10-13 06:00 | 227 | 2023-10-01 11:00
11 | Ghorashal 230/132/33kV Sub-Station | 230 | 241 | 2023-10-22 05:00 | 230 | 2023-10-01
12 | GPH 230/33kV Grid Sub-Station | 230 | 240 | 2023-10-22 18:00 | 221 | 2023-10-12 03:00
13 | Haripur 230/132kV Grid Sub-Station | 230 | 236 | 2023-10-20 03:00 | 222 | 2023-10-01 11:00
14 | Hasnabad 230/132kV Grid Sub-Station | 230 | 238 | 2023-10-20 18:00 | 220 | 2023-10-01 11:00
15 | Hathazari 230/132/33kV Grid Sub-Station | 230 | 241 | 2023-10-22 18:00 | 222 | 2023-10-14 14:00
16 | Ishurdi 230/132kV Grid Sub-Station | 230 | 237 | 2023-10-05 06:00 | 220 | 2023-10-30 12:00
17 | Jhenaidah 230/132kV Grid Sub-Station | 230 | 231 | 2023-10-05 06:00 | 211 | 2023-10-11 18:30
18 | Keranigonj 230/132/33kV Grid Sub-Station | 230 | 236 | 2023-10-06 05:00 | 219 | 2023-10-01 11:00
19 | Khulna(S) 230/132kV Grid Sub-Station | 230 | 240 | 2023-10-16 08:00 | 219 | 2023-10-11 18:30
20 | Maniknagar 230/132kV Grid Sub-Station | 230 | 237 | 2023-10-20 18:00 | 220 | 2023-10-01 11:00
21 | Meghnaghat 230/132kV Grid Sub-Station | 230 | 243 | 2023-10-14 18:30 | 229 | 2023-10-01 10:00
22 | Mirsorai 230/33kV Grid Sub-Station | 230 | 240 | 2023-10-22 18:30 | 221 | 2023-10-07 11:00
23 | Rajshahi 230/132/33kV Grid Sub-Station | 230 | 236 | 2023-10-26 17:00 | 217 | 2023-10-01 23:00
24 | Rampura 230/132kV Grid Sub-Station | 230 | 238 | 2023-10-20 18:00 | 221 | 2023-10-01 11:00
25 | Shikalbaha 230/132kV Grid Sub-Station | 230 | 240 | 2023-10-22 19:00 | 221 | 2023-10-10 15:00
26 | Shyampur 230/132kV Grid Sub-Station | 230 | 244 | 2023-10-01 19:00 | 221 | 2023-10-01 11:00
27 | Siddhirganj 230/132kV Grid Sub-Station | 230 | 239 | 2023-10-13 16:00 | 223 | 2023-10-01 12:00
28 | Sirajgonj 230 kV Switching Station | 230 | 242 | 2023-10-16 06:00 | 230 | 2023-10-01 01:00
29 | Sreepur 230/132/33kV Grid Sub-Station | 230 | 237 | 2023-10-06 01:00 | 223 | 2023-10-01 12:00
30 | Tongi 230/132/33kV Grid Sub-Station | 230 | 257 | 2023-10-11 19:00 | 217 | 2023-10-01 10:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar 132/33kV Grid Sub-Station | 132 | 139 | 2023-10-13 06:00 | 126 | 2023-10-01 11:00
2 | Agrabad 132/33kV Grid Sub-Station | 132 | 137 | 2023-10-24 18:00 | 126 | 2023-10-09 15:00
3 | AKS 132/33kV Grid Sub-Station | 132 | 135 | 2023-10-24 18:00 | 125 | 2023-10-09 14:00
4 | Amnura 132/33kV Grid Sub-Station | 132 | 141 | 2023-10-07 19:00 | 122 | 2023-10-02 01:00
5 | Ashuganj 230/132/33kV Sub-Station | 132 | 141 | 2023-10-06 01:00 | 123 | 2023-10-19 11:00
6 | Bagerhat 132/33kV Grid Sub-Station | 132 | 137 | 2023-10-18 19:00 | 120 | 2023-10-11 18:00
7 | Bakulia 132/33kV Grid Sub-Station | 132 | 139 | 2023-10-24 19:00 | 126 | 2023-10-23 01:00
8 | Banani 132/33kV Grid Sub-Station | 132 | 143 | 2023-10-06 01:00 | 124 | 2023-10-01 11:00
9 | Bangabhaban 132/33kV Grid Sub-Station | 132 | 138 | 2023-10-28 06:00 | 126 | 2023-10-01 11:00
10 | Barguna 132/33kV Grid Sub-Station | 132 | 139 | 2023-10-07 16:00 | 127 | 2023-10-01 23:00
11 | Barishal 132/33kV Grid Sub-Station | 132 | 139 | 2023-10-05 06:00 | 120 | 2023-10-09 19:30
12 | Baroaulia 132/33kV Grid Sub-Station | 132 | 141 | 2023-10-22 18:00 | 126 | 2023-10-18 13:00
13 | Baroirhat 132/33kV Grid Sub-Station | 132 | 137 | 2023-10-20 08:00 | 119 | 2023-10-31 14:00
14 | Bashundhara 132/33kV Grid Sub-Station | 132 | 141 | 2023-10-27 18:00 | 123 | 2023-10-01 13:00
15 | BashundharaCement 132/33kV Sub-Station | 132 | 139 | 2023-10-06 18:30 | 123 | 2023-10-25 11:00
16 | Beanibazar 132/33kV Grid Sub-Station | 132 | 132 | 2023-10-22 07:00 | 117 | 2023-10-01
17 | Benapole 132/33kV Grid Sub-Station | 132 | 139 | 2023-10-16 06:00 | 122 | 2023-10-08 18:30
18 | Bhaluka 132/33kV Grid Sub-Station | 132 | 132 | 2023-10-06 01:00 | 117 | 2023-10-01 22:00
19 | Bhandaria 132/33kV Grid Sub-Station | 132 | 139 | 2023-10-12 | 120 | 2023-10-01 22:00
20 | Bhangura 132/33kV Grid Sub-Station | 132 | 142 | 2023-10-28 03:00 | 131 | 2023-10-01 21:00
21 | Bheramara(GK) 132/33kV Grid Sub-Station | 132 | 136 | 2023-10-05 06:00 | 126 | 2023-10-17 13:00
22 | Bhulta 132/33kV Grid Sub-Station | 132 | 130 | 2023-10-06 18:30 | 113 | 2023-10-25 10:00
23 | Bog-Sherpur 132/33kV Grid Sub-Station | 132 | 143 | 2023-10-06 01:00 | 127 | 2023-10-03 19:00
24 | Bogura 132/33kV Grid Sub-Station | 132 | 142 | 2023-10-05 18:00 | 113 | 2023-10-01 18:30
25 | Brahmanbaria 132/33kV Grid Sub-Station | 132 | 135 | 2023-10-13 06:00 | 116 | 2023-10-11 18:30
26 | Cantonment 132/33kV GIS Grid Sub-Station | 132 | 138 | 2023-10-06 05:00 | 123 | 2023-10-01 11:00
27 | Chandpur 132/33kV Grid Sub-Station | 132 | 141 | 2023-10-20 06:00 | 113 | 2023-10-10 01:00
28 | Chandraghona 132/33kV Grid Sub-Station | 132 | 140 | 2023-10-22 18:00 | 124 | 2023-10-06 22:00
29 | Chapai 132/33kV Grid Sub-Station | 132 | 138 | 2023-10-21 17:00 | 124 | 2023-10-03 21:00
30 | Charsaidpur 132/33kV Sub-Station | 132 | 141 | 2023-10-13 19:00 | 123 | 2023-10-25 12:00
31 | Chauddagram 132/33kV Grid Sub-Station | 132 | 139 | 2023-10-20 07:00 | 121 | 2023-10-14 14:00
32 | Chhatak 132/33kV Grid Sub-Station | 132 | 132 | 2023-10-22 08:00 | 120 | 2023-10-21 18:30
33 | Chowmuhani 132/33kV Grid Sub-Station | 132 | 136 | 2023-10-20 06:00 | 114 | 2023-10-04 01:00
34 | Chuadanga 132/33kV Grid Sub-Station | 132 | 138 | 2023-10-30 06:00 | 117 | 2023-10-11 18:30
35 | Coxsbazar 132/33kV Grid Sub-Station | 132 | 140 | 2023-10-24 22:00 | 113 | 2023-10-01 19:30
36 | Cumilla(S) 132/33kV Grid Sub-Station | 132 | 142 | 2023-10-20 08:00 | 124 | 2023-10-01 15:00
37 | Daudkandi 132/33kV Grid Sub-Station | 132 | 134 | 2023-10-12 19:00 | 116 | 2023-10-25 11:00
38 | Dhaka University 132/33kV Grid Sub-Station | 132 | 138 | 2023-10-13 04:00 | 126 | 2023-10-01 11:00
39 | Dhamrai 132/33kV Grid Sub-Station | 132 | 139 | 2023-10-05 18:30 | 124 | 2023-10-11 12:00
40 | Dhanmondi 132/33kV Grid Sub-Station | 132 | 138 | 2023-10-06 19:00 | 123 | 2023-10-04 19:00
41 | Dohazari 132/33kV Grid Sub-Station | 132 | 140 | 2023-10-24 22:00 | 121 | 2023-10-14 18:00
42 | Faridpur 132/33kV Grid Sub-Station | 132 | 133 | 2023-10-21 06:00 | 124 | 2023-10-01
43 | Fatullah 132/33kV Grid Sub-Station | 132 | 140 | 2023-10-06 19:00 | 128 | 2023-10-26 11:00
44 | Feni 132/33kV Grid Sub-Station | 132 | 136 | 2023-10-20 06:00 | 116 | 2023-10-16 10:00
45 | Goalpara 132/33kV Grid Sub-Station | 132 | 140 | 2023-10-18 17:00 | 126 | 2023-10-11 18:00
46 | Gollamari 132/33kV Grid Sub-Station | 132 | 138 | 2023-10-02 09:00 | 127 | 2023-10-11 18:30
47 | Gopalganj 132/33kV Grid Sub-Station | 132 | 136 | 2023-10-19 19:00 | 124 | 2023-10-13 18:00
48 | Gulshan 132/33kV Grid Sub-Station | 132 | 137 | 2023-10-13 03:00 | 125 | 2023-10-01 12:00
49 | Halishahar 132/33kV Grid Sub-Station | 132 | 140 | 2023-10-22 18:00 | 126 | 2023-10-09 15:00
50 | HaripurSBU 132/33kV Sub-Station | 132 | 143 | 2023-10-11 04:00 | 126 | 2023-10-25 11:00
51 | Hasnabad 132/33kV Grid Substation | 132 | 139 | 2023-10-06 19:30 | 128 | 2023-10-26 12:00
52 | Ishurdi 132/33kV Grid Sub-Station | 132 | 140 | 2023-10-31 04:00 | 129 | 2023-10-01 18:30
53 | Jaldhaka 132/33kV Grid Sub-Station | 132 | 138 | 2023-10-18 19:00 | 114 | 2023-10-10 04:00
54 | Jamalpur 132/33kV Grid Sub-Station | 132 | 140 | 2023-10-07 19:00 | 113 | 2023-10-01 18:00
55 | Jashore 132/33kV Grid Sub-Station | 132 | 139 | 2023-10-06 01:00 | 123 | 2023-10-08 18:30
56 | Jhenaidah 132/33kV Grid Sub-Station | 132 | 141 | 2023-10-16 06:00 | 118 | 2023-10-17 13:00
57 | Joydebpur 132/33kV Grid Sub-Station | 132 | 142 | 2023-10-20 18:30 | 125 | 2023-10-01 11:00
58 | Joypurhat 132/33kV Grid Sub-Station | 132 | 137 | 2023-10-06 01:00 | 119 | 2023-10-02 01:00
59 | Juldah 132/33kV Grid Sub-Station | 132 | 138 | 2023-10-22 18:30 | 126 | 2023-10-09 14:00
60 | Kabirpur 132/33kV Grid Sub-Station | 132 | 140 | 2023-10-05 18:30 | 121 | 2023-10-01 11:00
61 | Kachua 132/33kV Grid Sub-Station | 132 | 139 | 2023-10-20 06:00 | 117 | 2023-10-01 14:00
62 | Kallyanpur 132/33kV Grid Sub-Station | 132 | 142 | 2023-10-05 19:00 | 129 | 2023-10-01 11:00
63 | Kalurghat 132/33kV Grid Sub-Station | 132 | 139 | 2023-10-22 18:00 | 127 | 2023-10-09 16:00
64 | Kamrangirchar 132/33kV Grid Sub-Station | 132 | 141 | 2023-10-04 04:00 | 123 | 2023-10-01 15:00
65 | Kazla 132/33kV Grid Sub-Station | 132 | 139 | 2023-10-04 17:00 | 125 | 2023-10-01 12:00
66 | Khagrachori 132/33kV Grid Sub-Station | 132 | 139 | 2023-10-22 18:00 | 113 | 2023-10-17 17:00
67 | Khulna (C) 132/33kV Grid Sub-Station | 132 | 139 | 2023-10-18 17:00 | 126 | 2023-10-08 23:00
68 | Khulshi 132/33kV Grid Sub-Station | 132 | 140 | 2023-10-22 18:00 | 125 | 2023-10-09 16:00
69 | Kishoreganj 132/33kV Grid Sub-Station | 132 | 137 | 2023-10-06 05:00 | 121 | 2023-10-17 12:00
70 | Kodda 132/33kV Grid Sub-Station | 132 | 140 | 2023-10-20 18:00 | 119 | 2023-10-07 08:00
71 | KSRM 132/33kV Grid Sub-Station | 132 | 139 | 2023-10-25 18:30 | 127 | 2023-10-18 14:00
72 | Kulaura 132/33kV Grid Sub-Station | 132 | 135 | 2023-10-16 06:00 | 127 | 2023-10-01
73 | Kurigram 132/33kV Grid Sub-Station | 132 | 135 | 2023-10-18 19:00 | 115 | 2023-10-03 18:30
74 | Kushtia 132/33kV Grid Sub-Station | 132 | 137 | 2023-10-05 06:00 | 121 | 2023-10-17 13:00
75 | Lalbag 132/33kV Grid Sub-Station | 132 | 136 | 2023-10-21 05:00 | 122 | 2023-10-01 12:00
76 | Lalmonirhat 132/33kV Grid Sub-Station | 132 | 138 | 2023-10-19 20:00 | 118 | 2023-10-11 18:00
77 | Madanganj 132/33kV Grid Sub-Station | 132 | 139 | 2023-10-06 18:30 | 123 | 2023-10-25 11:00
78 | Madaripur 132/33kV Grid Sub-Station | 132 | 136 | 2023-10-15 16:00 | 125 | 2023-10-09 19:30
79 | Madartek 132/33kV Grid Sub-Station | 132 | 138 | 2023-10-13 06:00 | 126 | 2023-10-01 11:00
80 | Madunaghat 132/33kV Grid Sub-Station | 132 | 140 | 2023-10-22 18:00 | 128 | 2023-10-09 14:00
81 | Magura 132/33kV Grid Sub-Station | 132 | 141 | 2023-10-30 04:00 | 117 | 2023-10-17 13:00
82 | Mahasthangarh 132/33kV Grid Sub-Station | 132 | 141 | 2023-10-06 01:00 | 126 | 2023-10-02 01:00
83 | Manikganj 132/33kV Grid Sub-Station | 132 | 138 | 2023-10-05 18:30 | 120 | 2023-10-03 04:00
84 | Maniknagar 132/33kV Grid Sub-Station | 132 | 138 | 2023-10-20 18:30 | 126 | 2023-10-01 11:00
85 | Matarbari 132/33kV Sub-Station | 132 | 140 | 2023-10-24 22:00 | 113 | 2023-10-01 23:00
86 | Matuail 132/33kV Grid Sub-Station | 132 | 138 | 2023-10-06 19:00 | 125 | 2023-10-25 12:00
87 | Millgate Tongi 132/33kV Grid Sub-Station | 132 | 141 | 2023-10-06 07:00 | 124 | 2023-10-01 11:00
88 | Mirpur 132/33kV Grid Sub-Station | 132 | 142 | 2023-10-04 02:00 | 125 | 2023-10-11 16:00
89 | Mirzapur 132/33kV GIS Grid Sub-Station | 132 | 135 | 2023-10-30 18:00 | 124 | 2023-10-31 14:00
90 | Mithapukur 132/33kV Grid Sub-Station | 132 | 139 | 2023-10-06 01:00 | 122 | 2023-10-01 03:00
91 | MI_Cement 132/33kV Grid Sub-Station | 132 | 140 | 2023-10-06 19:00 | 126 | 2023-10-26 11:00
92 | Modern Steel 132/11kV Grid Sub-Station | 132 | 138 | 2023-10-25 18:30 | 126 | 2023-10-10 14:00
93 | Mogbazar 132/33kV Grid Sub-Station | 132 | 140 | 2023-10-20 18:00 | 127 | 2023-10-01 11:00
94 | Mongla 132/33kV Grid Sub-Station | 132 | 136 | 2023-10-02 16:00 | 120 | 2023-10-11 18:00
95 | Motijheel 132/33kV Grid Sub-Station | 132 | 138 | 2023-10-28 06:00 | 126 | 2023-10-01 11:00
96 | Munshiganj 132/33kV Grid Sub-Station | 132 | 140 | 2023-10-06 18:30 | 124 | 2023-10-25 11:00
97 | Mymensingh 132/33kV Grid Sub-Station | 132 | 139 | 2023-10-06 01:00 | 114 | 2023-10-01 18:30
98 | Naogaon 132/33kV Grid Sub-Station | 132 | 138 | 2023-10-06 01:00 | 122 | 2023-10-01 02:00
99 | Narail 132/33kV Grid Sub-Station | 132 | 140 | 2023-10-31 06:00 | 117 | 2023-10-17 13:00
100 | Narshingdi 132/33kV Grid Sub-Station | 132 | 137 | 2023-10-17 19:00 | 116 | 2023-10-25 15:00
101 | Natore 132/33kV Grid Sub-Station | 132 | 137 | 2023-10-31 04:00 | 117 | 2023-10-05 15:00
102 | Nawabganj 132/33kV Grid Sub-Station | 132 | 138 | 2023-10-08 15:00 | 123 | 2023-10-01 11:00
103 | Netrakona 132/33kV Grid Sub-Station | 132 | 140 | 2023-10-06 03:00 | 113 | 2023-10-01 18:30
104 | New Tongi 132/33kV Grid Sub-Station | 132 | 140 | 2023-10-06 02:00 | 125 | 2023-10-01 11:00
105 | Niamatpur 132/33kV Grid Sub-Station | 132 | 137 | 2023-10-06 01:00 | 117 | 2023-10-02 01:00
106 | Noapara 132/33kV Grid Sub-Station | 132 | 139 | 2023-10-18 19:00 | 125 | 2023-10-13 18:00
107 | Pabna 132/33kV Grid Sub-Station | 132 | 141 | 2023-10-20 03:00 | 127 | 2023-10-01 18:30
108 | Palashbari 132/33kV Grid Sub-Station | 132 | 139 | 2023-10-06 01:00 | 119 | 2023-10-11 18:30
109 | Panchagarh 132/33kV Grid Sub-Station | 132 | 144 | 2023-10-18 19:00 | 115 | 2023-10-11 18:30
110 | Patuakhali 132/33kV Grid Sub-Station | 132 | 140 | 2023-10-07 15:00 | 129 | 2023-10-01 22:00
111 | PHP 132/33kV Sub-Station | 132 | 137 | 2023-10-20 06:00 | 116 | 2023-10-27 11:00
112 | Postogola 132/33kV Grid Sub-Station | 132 | 139 | 2023-10-06 19:00 | 129 | 2023-10-01 10:00
113 | Purbachal 132/33kV Grid Sub-Station | 132 | 142 | 2023-10-27 17:00 | 124 | 2023-10-01 11:00
114 | Purbasadipur 132/33kV Grid Sub-Station | 132 | 137 | 2023-10-18 19:00 | 116 | 2023-10-03 18:30
115 | Rahim Steel 132/33kV Sub-Station | 132 | 138 | 2023-10-06 03:00 | 126 | 2023-10-25 11:00
116 | Rajbari 132/33kV Grid Sub-Station | 132 | 132 | 2023-10-06 01:00 | 122 | 2023-10-01 23:00
117 | Rajendrapur 132/33kV Grid Sub-Station | 132 | 138 | 2023-10-05 19:00 | 119 | 2023-10-11 13:00
118 | Rajshahi 132/33kV Grid Sub-Station | 132 | 137 | 2023-10-18 17:00 | 123 | 2023-10-01 23:00
119 | Ramganj 132/33kV Grid Sub-Station | 132 | 139 | 2023-10-20 08:00 | 113 | 2023-10-01 15:00
120 | Rangamati 132/33kV Grid Sub-Station | 132 | 139 | 2023-10-22 18:00 | 128 | 2023-10-08 12:00
121 | Rangpur 132/33kV Grid Sub-Station | 132 | 138 | 2023-10-09 23:00 | 119 | 2023-10-03 18:30
122 | Ruppur 132/11kV Grid Sub-Station | 132 | 139 | 2023-10-06 09:00 | 129 | 2023-10-01 21:00
123 | Saidpur 132/33kV Grid Sub-Station | 132 | 138 | 2023-10-18 19:00 | 118 | 2023-10-11 18:30
124 | Satkhira 132/33kV Grid Sub-Station | 132 | 137 | 2023-10-02 09:00 | 121 | 2023-10-08 18:30
125 | Satmasjid 132/33kV Grid Sub-Station | 132 | 138 | 2023-10-06 05:00 | 123 | 2023-10-01 11:00
126 | Savar 132/33kV Grid Sub-Station | 132 | 140 | 2023-10-04 01:00 | 127 | 2023-10-01 11:00
127 | SevenRings 132/11kV Sub-Station | 132 | 143 | 2023-10-20 18:00 | 134 | 2023-10-16 12:00
128 | ShahCement 132/33kV Grid Sub-Station | 132 | 141 | 2023-10-13 19:00 | 123 | 2023-10-25 12:00
129 | Shahjadpur 132/33kV Grid Sub-Station | 132 | 144 | 2023-10-17 02:00 | 135 | 2023-10-01 11:00
130 | Shahjibazar 132/33kV Grid Sub-Station | 132 | 136 | 2023-10-13 08:00 | 118 | 2023-10-02
131 | Shahmirpur 132/33kV Grid Sub-Station | 132 | 138 | 2023-10-25 19:30 | 126 | 2023-10-09 16:00
132 | Shariatpur 132/33kV Grid Sub-Station | 132 | 133 | 2023-10-21 06:00 | 123 | 2023-10-01 23:00
133 | Sherpur 132/33kV Grid Sub-Station | 132 | 140 | 2023-10-05 13:00 | 114 | 2023-10-01 01:00
134 | Shitalakhya 132/33kV Grid Sub-Station | 132 | 140 | 2023-10-06 19:00 | 126 | 2023-10-26 11:00
135 | Sholosohor 132/33kV Grid Sub-Station | 132 | 139 | 2023-10-22 18:00 | 120 | 2023-10-10 12:00
136 | Shyampur 132/33kV Grid Sub-Station | 132 | 139 | 2023-10-06 19:00 | 129 | 2023-10-26 11:00
137 | Siddhirganj 132/33kV Grid Sub-Station | 132 | 138 | 2023-10-06 19:00 | 125 | 2023-10-25 11:00
138 | Sirajganj 132/33kV Grid Sub-Station | 132 | 139 | 2023-10-20 04:00 | 126 | 2023-10-01 21:00
139 | Sonargaon 132/33kV Grid Sub-Station | 132 | 138 | 2023-10-06 19:00 | 123 | 2023-10-24 14:00
140 | Sreemongol 132/33kV Grid Sub-Station | 132 | 135 | 2023-10-13 08:00 | 121 | 2023-10-02
141 | Srinagar 132/33kV Grid Sub-Station | 132 | 137 | 2023-10-20 08:00 | 123 | 2023-10-01 12:00
142 | SSM 132/33kV Grid Sub-Station | 132 | 144 | 2023-10-22 18:00 | 129 | 2023-10-18 13:00
143 | Sunamganj 132/33kV Grid Sub-Station | 132 | 130 | 2023-10-06 08:00 | 117 | 2023-10-21 18:30
144 | Sylhet (South) 132/33kV GIS Grid Sub-Station | 132 | 132 | 2023-10-07 06:00 | 123 | 2023-10-31
145 | Sylhet 132/33kV Grid Sub-Station | 132 | 132 | 2023-10-16 07:00 | 123 | 2023-10-21 15:00
146 | Tangail 132/33kV Grid Sub-Station | 132 | 138 | 2023-10-06 01:00 | 124 | 2023-10-01 18:30
147 | Thakurgaon 132/33kV Grid Sub-Station | 132 | 140 | 2023-10-19 19:00 | 115 | 2023-10-01 03:00
148 | TK chemical 132kV Grid Sub-Station | 132 | 140 | 2023-10-22 18:00 | 126 | 2023-10-18 19:30
149 | Ullon 132/33kV Grid Sub-Station | 132 | 137 | 2023-10-04 05:00 | 125 | 2023-10-01 12:00
150 | Uttara 132/33kV Grid Sub-Station | 132 | 141 | 2023-10-05 19:00 | 126 | 2023-10-17 12:00
151 | UttaraNew 132/33kV Grid Sub-Station | 132 | 142 | 2023-10-05 03:00 | 127 | 2023-10-01 11:00
152 | Zigatola 132/33kV Grid Sub-Station | 132 | 136 | 2023-10-06 05:00 | 123 | 2023-10-01 13:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:October 2023
Substation | Transformer | voltage_level | mw | mva | date_time
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 | 400/230 | 459 | 483.5132 | 2023-10-02 15:00
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 | 400/230 | 500 | 522.5935 | 2023-10-23 09:00
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | -279 | 320.6322 | 2023-10-07 13:00
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | -279 | 320.6322 | 2023-10-07 13:00
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | -183 | 183.5347 | 2023-10-21 18:00
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | -179 | 179.4714 | 2023-10-21 18:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 248 | 263.1501 | 2023-10-05 21:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 258 | 272.5949 | 2023-10-05 21:00
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | -321.67 | 323.418 | 2023-10-09 20:00
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | -318.51 | 320.2994 | 2023-10-09 20:00
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 251 | 296.0574 | 2023-10-01
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | -196 | 196.023 | 2023-10-09 19:30
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | -196 | 196.023 | 2023-10-09 19:30
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | 11 | 315.192 | 2023-10-05 02:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 297 | 420.0214 | 2023-10-28 17:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 313 | 317.624 | 2023-10-17 07:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | -81 | 89.0505 | 2023-10-01 23:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | -81 | 89.0505 | 2023-10-01 23:00
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 408 | 416.5573 | 2023-10-21 14:00
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Substation | Transformer | voltage_level | mw | mva | date_time
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 185 | 201.1616 | 2023-10-01 18:00
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 185 | 201.1616 | 2023-10-01 18:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 188 | 198.5951 | 2023-10-12 11:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 188 | 198.5951 | 2023-10-12 11:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 193 | 209.3084 | 2023-10-10 13:00
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 105 | 138.2932 | 2023-10-26 10:00
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 200 | 206.1553 | 2023-10-23 22:00
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 185 | 200.0025 | 2023-10-07 21:00
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 146 | 168.9408 | 2023-10-17 16:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 173 | 180.9365 | 2023-10-11 18:30
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 170 | 184.2308 | 2023-10-11 18:30
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 221 | 230.9329 | 2023-10-11 18:30
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 166 | 167.2005 | 2023-10-24 13:00
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 152 | 335.4177 | 2023-10-30 18:00
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | -156 | 163.817 | 2023-10-30 11:00
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | -156 | 163.817 | 2023-10-30 11:00
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 190 | 194.805 | 2023-10-30 12:00
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 182 | 190.7171 | 2023-10-03 22:00
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 250 | 255.9785 | 2023-10-03 19:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-01 | 230/132 | 165 | 219.6588 | 2023-10-24 19:30
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-02 | 230/132 | 189 | 204.4627 | 2023-10-13 13:00
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 264 | 284.1144 | 2023-10-20 18:30
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 110 | 110 | 2023-10-12 21:00
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 110 | 110 | 2023-10-12 21:00
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 149 | 199.7248 | 2023-10-15 09:00
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 130 | 178.2807 | 2023-10-16 06:00
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 154 | 199.6121 | 2023-10-18 10:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 78 | 116.1034 | 2023-10-17 03:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 70 | 109.3435 | 2023-10-18 15:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 78 | 116.1034 | 2023-10-17 03:00
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 124 | 127.122 | 2023-10-16 19:30
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 124 | 127.122 | 2023-10-16 19:30
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 124 | 127.122 | 2023-10-16 19:30
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 124 | 127.122 | 2023-10-16 19:30
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 120 | 147.6347 | 2023-10-01 18:30
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 125 | 161.3351 | 2023-10-10 13:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 125 | 161.3351 | 2023-10-10 13:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | -214 | 248.3385 | 2023-10-17 12:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | -214 | 248.3385 | 2023-10-17 12:00
Kaliakoir 400/230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 224 | 229.9565 | 2023-10-03 15:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 133 | 186.6815 | 2023-10-14 01:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 33 | 33 | 2023-10-14 01:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 226 | 242.1673 | 2023-10-13 08:00
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | -161 | 169.8146 | 2023-10-15 13:00
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | -161 | 169.8146 | 2023-10-15 13:00
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | -197 | 200.085 | 2023-10-03 12:00
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 169 | 184.4912 | 2023-10-09 13:00
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 200 | 214.6718 | 2023-10-01 07:00
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | -110 | 117.3925 | 2023-10-05 15:00
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | -126 | 136.6931 | 2023-10-02 13:00
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 12 | 12.0416 | 2023-10-17
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 1 | 1.4142 | 2023-10-22 03:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 01 | 230/132 | 216 | 216.2314 | 2023-10-06 12:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 | 230/132 | 216 | 216.2314 | 2023-10-06 12:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 | 230/132 | 160 | 207.4223 | 2023-10-22 14:00
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 248 | 272.5307 | 2023-10-21 18:30
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 248 | 272.5307 | 2023-10-21 18:30
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 149 | 173.0462 | 2023-10-26 11:00
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 149 | 173.0462 | 2023-10-26 11:00
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 194 | 217.8004 | 2023-10-25 11:00
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 194 | 217.8004 | 2023-10-25 11:00
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 170 | 178.3704 | 2023-10-02 18:00
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 159 | 179.8249 | 2023-10-03 07:00
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 222 | 223.5173 | 2023-10-07 11:00
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 222 | 223.5173 | 2023-10-07 11:00
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 222 | 223.5173 | 2023-10-07 11:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-37
|  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
|  |  |  | Report on load shedding | [14 empty] | Report on load shedding
Month: October 2023 |  |  |  | (For Evening Peak) | [10 empty] | Month: October 2023 |  |  |  | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) |  | Areawise load shed (MW) | [8 empty] | Remarks |  | Peak Hour |  | Total load shed (SS end) |  | Areawise load shed (MW) | [8 empty] | Remarks
Date | Generation (Gen End) | Demand (Gen End) | [12 empty] | Date | Generation | Demand (Gen End)
| (MW) | (MW) | MW | Time | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2023-10-01 | 13998 | 14200 | 193 | 19:00 | 0 | 0 | 0 | 0 | 0 | 80 | 113 | 0 | 0 | - | 2023-10-01 | 12530 | 12530 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-10-02 | 14022 | 14200 | 170 | 19:00 | 0 | 0 | 0 | 0 | 20 | 45 | 105 | 0 | 0 | - | 2023-10-02 | 12293 | 12293 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-10-03 | 13294 | 13360 | 63 | 19:00 | 0 | 0 | 0 | 0 | 25 | 20 | 18 | 0 | 0 | - | 2023-10-03 | 12053 | 12115 | 59 | 12:00 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | -
2023-10-04 | 12561 | 12582 | 20 | 19:00 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | - | 2023-10-04 | 11245 | 11311 | 63 | 12:00 | 33 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | -
2023-10-05 | 11300 | 11300 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-10-05 | 10985 | 10985 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-10-06 | 11396 | 11396 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-10-06 | 9326 | 9326 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-10-07 | 13458 | 13458 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-10-07 | 11030 | 11030 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-10-08 | 14021 | 14060 | 37 | 19:00 | 0 | 0 | 0 | 0 | 10 | 27 | 0 | 0 | 0 | - | 2023-10-08 | 11991 | 11991 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-10-09 | 14220 | 14220 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-10-09 | 11911 | 11911 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-10-10 | 14017 | 14085 | 65 | 19:00 | 0 | 0 | 0 | 0 | 25 | 0 | 40 | 0 | 0 | - | 2023-10-10 | 12224 | 12224 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-10-11 | 14356 | 14470 | 109 | 20:00 | 0 | 0 | 0 | 0 | 18 | 21 | 70 | 0 | 0 | - | 2023-10-11 | 12238 | 12290 | 50 | 12:00 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-10-12 | 13944 | 14200 | 244 | 19:00 | 55 | 0 | 0 | 0 | 90 | 64 | 35 | 0 | 0 | - | 2023-10-12 | 11976 | 12130 | 147 | 12:00 | 75 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | -
2023-10-13 | 12852 | 12852 | 0 | 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-10-13 | 10593 | 10593 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-10-14 | 13639 | 13720 | 77 | 19:00 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 0 | 0 | - | 2023-10-14 | 11230 | 11230 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-10-15 | 13826 | 13852 | 25 | 19:30 | 15 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | - | 2023-10-15 | 11898 | 11995 | 74 | 12:00 | 50 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | -
2023-10-16 | 13742 | 13742 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-10-16 | 11862 | 11862 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-10-17 | 13832 | 13832 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-10-17 | 11754 | 11754 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-10-18 | 13313 | 13313 | 0 | 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-10-18 | 11833 | 11833 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-10-19 | 13351 | 13370 | 18 | 19:30 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | - | 2023-10-19 | 11503 | 11503 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-10-20 | 13204 | 11780 | 143 | 19:00 | 0 | 0 | 0 | 0 | 40 | 30 | 73 | 0 | 0 | - | 2023-10-20 | 10165 | 10165 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-10-21 | 13108 | 13180 | 69 | 19:00 | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 0 | 0 | - | 2023-10-21 | 11390 | 11390 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-10-22 | 12918 | 12948 | 29 | 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | - | 2023-10-22 | 11420 | 11800 | 363 | 12:00 | 20 | 65 | 0 | 90 | 0 | 130 | 8 | 0 | 50 | -
2023-10-23 | 12144 | 12144 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-10-23 | 11359 | 11850 | 469 | 12:00 | 144 | 90 | 0 | 0 | 105 | 130 | 0 | 0 | 0 | -
2023-10-24 | 11269 | 11269 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-10-24 | 10238 | 10238 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-10-25 | 12390 | 12425 | 33 | 19:00 | 18 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | - | 2023-10-25 | 10768 | 10768 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-10-26 | 12688 | 12730 | 40 | 19:00 | 0 | 0 | 0 | 0 | 0 | 25 | 15 | 0 | 0 | - | 2023-10-26 | 11245 | 11289 | 42 | 12:00 | 15 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | -
2023-10-27 | 10943 | 10967 | 23 | 19:00 | 0 | 0 | 0 | 0 | 15 | 0 | 8 | 0 | 0 | - | 2023-10-27 | 9860 | 9860 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-10-28 | 11798 | 11798 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-10-28 | 10299 | 10299 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-10-29 | 11825 | 11825 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2023-10-29 | 10675 | 10675 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023-10-30 | 11977 | 11977 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2023-10-30 | 10823 | 10823 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023-10-31 | 12466 | 12466 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2023-10-31 | 11078 | 11078 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Max. L/S | - | 1537 | - | [10 empty] | Max. L/S | - |  | 1638
| Min. L/S | - | 54 | - | [10 empty] | Min. L/S | - |  | 0
| No. of Days | - | 31 | - | [10 empty] | No. of Days | - | 31
| Average L/S |  | 21566 | [11 empty] | Average L/S |  | 19669
|  | - | - | - | [11 empty] | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:October 2023
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 14356 | 2023-10-11 | 20:00
2 | Maximum Day Peak Genaration | MW | 12530 | 2023-10-01 | 12:00
3 | Maximum Evening Peak Demand | MW | 14470 | 2023-10-30 | 18:00
4 | Minimum Generation | MW | 8008 | 2023-10-06 | 6:00
5 | Average of the daily evening peak Genaration | MW | 12963.6129 | - | -
6 | Average of the daily day peak Genaration | MW | 11283.7097 | - | -
7 | Maximum load shed | MW | 244 | 2023-10-12 | 19:00
8 | Minimum load shed | MW | 0 | 2023-10-13 | 20:00
9 | Total nos. of load shed days | Day | 17 | - | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 45.2667 | - | -
11 | Total Generation | MkWh | 8422.148 | - | -
12 | Total Generation by BPDB | MkWh | 2096.5113 | % of total Gen. | 24.89%
13 | Total Generation by IPP | MkWh | 2322.8657 | '' | 27.58%
14 | A) Total Generation by Generation Companies | MkWh | 2356.1995 | '' | 27.98%
| B) Total Generation by REB | MkWh | 117.5706 | " | 1.396%
| C) Total Generation by RENTAL | MkWh | 198.4182 | " | 2.356%
| D) Total Imported from India (BIPTC) | MkWh | 652.0974 | " | 7.743%
| E) Total Imported from Tripura, India (A.C) | MkWh | 678.4853 | " | 8.056%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4134.9757 | % of total Gen. | 49.22%
| B) Oil | MkWh | 957.94 | '' | 11.4%
| C) Hydro | MkWh | 134.4035 | '' | 1.6%
| D) Solar | MkWh | 70.3503 | '' | 0.8374%
| E) Coal | MkWh | 2377.7026 | '' | 28.3%
| F) BIPTC (Import from India) | MkWh | 630.8356 | '' | 7.509%
| G) A.C (Import from Tripura, India) | MkWh | 92.6171 | '' | 1.102%
| H) Wind | MkWh | 2.0664 | '' | 0.0246%
16 | Maximun of the daily total Generation . | MkWh | 355.3806 | 2023-10-19
17 | Monthly Load factor | % | 78.905 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 34210.3044 | - | -
| A) Gas | M.Taka | 4436.4127 | - | -
| B) Liquid fuel | M.Taka | 11414.7613 | - | -
| C) Coal | M.Taka | 14815.6767 | - | -
| D) BIPTC (Import from India) | M.Taka | 2876.6104 | - | -
| E) Tripura(Import from India) | M.Taka | 666.8433 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1280.4344 | 2023-10-12
| A) Gas | M.Taka | 227.2507 | 2023-10-12
| B) Liquid fuel | M.Taka | 607.9497 | 2023-10-01
| C) Coal | M.Taka | 699.6856 | 2023-10-19
| D) BIPTC (Import from India) | M.Taka | 101.0894 | 2023-10-20
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 4.0619
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 4.1642
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 108.7 | 31/10/2023 | 06:00
b) | Actual | FT (MSL) | 102.39 | 31/10/2023 | 6:00
22 | Peak Genaration of October 2022 | MW | 12901 | 2022-10-10 | 20:00
23 | Peak Demand of October 2022 | MW | 14300 | 2022-10-31 | 20:00
24 | Maximum peak Generation recorded upto 31/10/2023 | MW | 15648 | 19/04/2023 | 21:00
25 | Maximum peak Demand recorded upto 31/10/2023 | MW | 16096 | 19/04/2023 | 21:00
26 | Maximum load shed recorded upto 30/09/2023 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## FGMO
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month:October 2023
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
1 | Bibiyana-III 400 MW CCPP | BPDB | 400 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | [13 empty] | √ | √
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220
6 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
7 | Meghnaghat CCPP(Summit) | IPP | 335 | √ | √ | √ | √ | [6 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √
8 | Ashuganj 225 MW CCPP | APSCL | 221 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
9 | Ashuganj 450 MW CCPP(North) | APSCL | 361 | √ | √ | √ | √ | √ |  |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
10 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
11 | Ashuganj 420 MW CCPP(East) | APSCL | 400
12 | Ashuganj 55 MW PP (Precision) | QRPP | 55
13 | Bheramara 410 MW CCPP | NWPGCL | 410
14 | Haripur 412 MW CCPP | EGCB | 412
15 | Fenchugonj CCPP Phase-1 | BPDB | 97
16 | Fenchugonj CCPP Phase-2 | BPDB | 104
17 | Siddhirganj 2x120 MW GTPP | EGCB | 210
18 | Shikalbaha 225 MW CCPP | BPDB | 225
19 | Shikalbaha Peaking GT | BPDB | 150
20 | Shahjibazar 330 MW CCPP | BPDB | 330
21 | Chandpur 150 MW CCPP | BPDB | 163
22 | Bhola 225 MW CCPP | BPDB | 194
23 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
24 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
25 | Siddhirganj 335 MW CCPP | EGCB | 335
26 | Bibiyana-III 400 MW CCPP | BPDB | 400
27 | Sylhet 225 MW CCPP | BPDB | 231
28 | RPCL 210 MW CCPP | IPP | 210
29 | Khulna 225 MW CCPP | NWPGCL | 230
30 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
31 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
32 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
33 | Bibiyana South 400 MW CCPP | BPDB | 383
34 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
35 | Shajibazar 100 MW PP | BPDB | 100
36 | Payra 1320 MW Unit-1 | BCPCL | 622
37 | Kushiara 163 MW CCPP (KP) | IPP | 163
38 | Haripur 360MW CCPP(HPL) | IPP | 360
39 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450
due to gas shortage

## FGMO Weekly
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status |  |  |  |  | SR at 50 Hz (MW)
SL | Plant Name | Owner | Installed capacity | Capability Status of Last Week | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
(MW)
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | Capable | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70 | Capable
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | Capable
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220 | Capable
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220 | Capable
6 | Meghnaghat CCPP(Summit) | IPP | 335 | Capable |  | 10 | 20 | 20 | 20 | 20 | 20 | 20
7 | Ashuganj 450 MW CCPP(North) | APSCL | 360 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
8 | Ashuganj 225 MW CCPP | APSCL | 221 | Capable |  | 20 | 20 | 20 | 20 | 20 | 20
9 | Bheramara 410 MW CCPP | NWPGCL | 410 | Capable
10 | Haripur 412 MW CCPP | EGCB | 412 | Capable
11 | Fenchugonj CCPP Phase-1 | BPDB | 97 | Capable |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
12 | Chandpur 150 MW CCPP | BPDB | 163 | Capable
13 | Siddhirganj 2x120 MW GTPP | EGCB | 210 | Capable
14 | Shikalbaha 225 MW CCPP | BPDB | 225 | Capable
15 | Shikalbaha Peaking GT | BPDB | 150 | Capable
16 | Shahjibazar 330 MW CCPP | BPDB | 330 | Capable
17 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | Capable |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
18 | Fenchugonj CCPP Phase-2 | BPDB | 104 | Capable | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
19 | Bhola 225 MW CCPP | BPDB | 194 | Capable
20 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365 | Capable
21 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 | Capable
22 | Siddhirganj 335 MW CCPP | EGCB | 335 | Capable but not tested recently
23 | Bibiyana-III 400 MW CCPP | BPDB | 400 | Capable | 30 | 30 |  |  |  |  | 30 | 30 | 30
24 | Sylhet 225 MW CCPP | BPDB | 231 | Capable
25 | RPCL 210 MW CCPP | IPP | 210 | Capable but not tested recently
26 | Khulna 225 MW CCPP | NWPGCL | 230 | Capable but not tested recently
27 | a) Baghabari 71 MW GTPP | BPDB | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | 100 | Not Capable but feasible
28 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50 | Not Capable but feasible
29 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410 | Not Capable but feasible
30 | Bibiyana South 400 MW CCPP | BPDB | 383 | Capable
31 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274 | Not Capable but feasible
32 | Shajibazar 100 MW PP | BPDB | 100 | Not Capable but feasible
33 | Payra 1320 MW Unit-1 | BCPCL | 622 | Capable
34 | Kushiara 163 MW CCPP (KP) | IPP | 163 | Not Capable but feasible
35 | Bhola Nutan Bidyut | IPP | 220 | Capable
36 | Haripur 360MW CCPP(HPL) | IPP | 360 | Not Capable but feasible
37 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450 | Not Capable but feasible
Total Installed capacity |  |  |  |  | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity |  |  |  |  | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve |  |  |  |  | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO |  |  |  |  | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list |  |  |  |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list |  |  |  |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable |  |  |  |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently |  |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible |  |  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD