## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-11-29 | Wednesday
|  | Date (day): | 2023-11-29 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12235.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14048 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-11-28 | 2023-11-29 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 76 | 74 | 70 | 76 | 32 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 394 | 354 | 412 | 412
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 213 | 162 | 200 | 200 | 160 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | GT-1 under S/D due to Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 12 | 90 | 90 |  | 10 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 17 | 17 | 85 | 85 |  | 17 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 20 | 15 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 30 | 40 | 35 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 13 | 14 | 15 | 15 |  | 7 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 16 | 90 | 90 |  | 10 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 240 | 227 | 250 | 250 | 85 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 32 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 0 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 48 | 16 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 0 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 0 | 35 | 20 |  | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 38 | 38 | 38 | 38 |  | 42 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 31 | 3 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 13 | 8 | 25 | 27 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 125 | 80 | 130 | 170 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 24 | 51 | 18 | 100 | 49 |  | Fuel shortage
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 105 | 30 | 105
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 55 | 26 | 72 | 32 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 55 | 17 | 55 | 107 |  | Fuel shortage
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 29 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 5763 | 5422 | 1663 | 1963 | 2113 | 2680 | 1720 | 1026
38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
39 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 1 | 17 | 8 | 17 | 8 |  | Fuel shortage
40 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 18 | 0 | 20 | 0
41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 20 | 6 | 19 | 31 |  | Fuel shortage
42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 86 | 86 | 86 | 86 | 144 |  | Low water lavel
43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 142 | 141 | 212 | 215
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 17 | 17 | 88 |  | Fuel shortage
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 2 | 18 | 40 | 64 | 34 |  | Fuel shortage
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 3 | 13 | 0 | 0 | 102 |  | Fuel shortage
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 12 | 0 | 12 | 12 | 10 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 2 | 10 | 20
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 20 | 120 | 260 | 260 | 40 |  | Fuel shortage+Engine problem
54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 10 | 36 | 17 | 17 | 37 |  | Fuel shortage
55 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 17 | 17 | 93 |  | Fuel shortage
56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 12 | 12 | 88 |  | Fuel shortage
57 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 17 | 99 |  | Fuel shortage
58 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 31 | 0 | 0 | 0 | 163 |  | Fuel shortage
59 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 500 | 480 | 500 | 500
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 4 | 1 | 10 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 565 | 273 | 270 | 270 |  |  | On test.
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 3829 | 3769 | 1479 | 1282 | 1543 | 1577 | 1401 | 330
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 0 | 0 |  | 221 | Under maint.
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 310 | 320 | 320 | 40 |  | Gas shortage
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
63 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 225 | 390 | 300 | 380 | 20
64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 44 | 43 | 47 | 47
65 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 0 | 44 | 42 | 40 | 46
66 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 102 | 130 | 55 | 130 | 65 |  | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
68 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 41 | 150 | 150
69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 20
70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
71 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 67 | 140 | 17 | 17 | 183 |  | Fuel shortage
72 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 10 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 114 | 126 | 128 | 140
74 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 8 | 6 | 10 | 10 |  | 15 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 34 | 48 | 28 | 55 | 58 |  | Fuel shortage
79 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
80 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 18 | 36 | 36 | 53 | 62 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2896 | 1085 | 1441 | 1427 | 1664 | 428 | 800
81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 34 | 47 | 80 | 80 | 122 |  | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Contract Expired
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 56 | 104 | 84 | 100 | 100 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 10 | 75 | 56 | 85 | 30 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 47 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 149 | 232 | 277.6 | 271 | 122 | 22
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 22 | 30 | 28 | 28 |  | 62 | Engine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 44 | 47
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 3 | 8 | 8 |  | 3 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 |  | 66 | Under maint.
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 83 | 60 | 80
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 199 | 193 | 200 | 200 |  | 31 | Machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 17 | 17
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 8 | 16 | 16 | 9 |  | Gas shortage
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 285 | 270 | 280 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 397 | 402 | 400 | 400
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 398 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1474 | 1459 | 1506 | 1549 | 223 | 619
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 440 | 757 | 928 | 928
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 32 | 32 | 48 | 67 |  | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 50
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 70 | 39 |  | Fuel shortage
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 16 | 24 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 90 | 90 |  | 15 | Engine problem
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 71 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 446 | 460 | 500 | 620
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 957 | 1266 | 1650 | 1822 | 891 | 15
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 16 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 12 | 18 | 21 | 25 |  | 15 | Engine problem
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 130 | 130 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 930 | 1080 | 1000 | 1220
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 144 | 110 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 55 | 0 | 150
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 200 | 200 | 200 | 200 | 107 |  | Coal shortage
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1416 | 1593 | 1587 | 2055 | 107 | 79
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 30 | 22 |  | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 20 |  | 51 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 28 | 28
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 34 | 42 |  | 8 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 40 |  | 10 | Engine problem
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 221 | 187 | 190 | 214 |  |  | DCT
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 91 | 300 | 414
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 38 | 12 |  | Fuel shortage
136 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 40 | 85 |  | 19 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 45 | 35 | 50 | 63 |  | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 90 | 35 | 113
143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 816 | 873 | 850 | 900
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 1053 | 1297 | 1611 | 2037 | 908 | 88
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 98 | 113 | 113
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 46 | 70 | 110
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 27 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 175 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 375 | 314 | 521 | 393 | 125 | 189
| Total |  |  |  |  | 25951 | 25211 | 9651 | 10847 | 12235.6 | 14048 | 5925 | 3168
A. |  | 2023-11-28 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 10847 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 7508 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10847 | MW
3 | Day peak Generation : |  |  | 9651 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10744.97 | MW
4 | Evening peak Generation : |  |  | 10847 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 220.2229 | MKWHr | By Solar | 2.3459 | MKWHr
| By Gas : | 106.625 | MKWHr |  | By Oil: | 11.4024 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 81.7176 | MKWHr |  | By Hydro: | 2.0767 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.0408 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5925 | MW | Dhaka | 4342.97 | 4342.97 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3168 | MW | Chittagong | 1089.2 | 1089.2 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 9093 | MW | Khulna | 1181.8 | 1181.8 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 823.27 | MMCFD |  |  | Rajshahi | 1002 | 1002 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 109101488.994 | ii) Oil : | Taka | 150057349.6 | Comilla | 918 | 918 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 556624780.1 | Total | Taka | 815783618.694 | Mymensingh | 813 | 813 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 385 | 385 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 260 | MW (W to E) at | 18:00 | hrs | Barisal | 286 | 286 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 194 | MW at | 8:00 | hrs | Rangpur | 727 | 727 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 32.5°C |  |  | Total | 10744.97 | 10744.97 |  | 0
B. |  | 2023-11-29 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 32.5°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14048 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9400 | MW
4 | Reserve(Generation end) |  |  |  | 3048 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 223.3292 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7400 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 13.5011 | MKWHr. | ii) HVDC Flow at Peak Time |  | 757 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.5133 | MKWHr. | iii) Maximum HVDC Flow : |  | 910 | MW at | 24:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 98.34 |  | (b) Today: | 98.22 |  | (c) Rule Curve: |  | 106.2
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-11-28 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 77 | 0 | 362 | 203 |  | 0 | 225 | 0 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 19 | 25 | 31 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 17 | 0 | 0 | 0 | 280 | 0 | 0 | 102 | 0 | 47 | 46 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 8 | 100 | 85 | 0 | 0 | 0 | 43 | 28 | 0 | 47 | 0 | 0 | 0 | 40 | 0 | 199 | 18 | 0 | 10 | 280 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 467 | 0 | 217 | 0 | 0 |  | 440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1020 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 443 | 0 | 140 | 825 | 0 | 0 |  | 4880 | 3547 | 8427 | 3035 | 440 | 1433 | 0 | 51 | 3282 | 86 | 0 | 0 | 100 | 0 | 0 | 0 | 98.36
2:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 362 | 202 |  | 0 | 170 | 0 | 0 | 0 | 0 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 19 | 25 | 31 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 23 | 0 | 0 | 0 | 280 | 0 | 0 | 102 | 0 | 45 | 46 | 0 | 5 | 0 | 0 | 0 | 18 | 10 | 8 | 8 | 98 | 85 | 0 | 0 | 0 | 43 | 28 | 0 | 5 | 0 | 0 | 0 | 5 | 0 | 199 | 18 | 0 | 10 | 270 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 460 | 1 | 213 | 0 | 0 |  | 440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 960 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 457 | 0 | 140 | 826 | 0 | 0 |  | 4539 | 3481 | 8020 | 3037 | 440 | 1132 | 0 | 0 | 3226 | 86 | 0 | 0 | 98 | 0 | 1 | 0 | 98.36
3:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 363 | 201 |  | 0 | 170 | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 19 | 25 | 31 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 8 | 0 | 45 | 46 | 0 | 5 | 0 | 0 | 0 | 18 | 10 | 8 | 8 | 96 | 89 | 0 | 0 | 0 | 43 | 28 | 0 | 5 | 0 | 0 | 0 | 5 | 0 | 199 | 18 | 0 | 10 | 295 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 433 | 1 | 214 | 0 | 0 |  | 440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 860 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 140 | 819 | 0 | 0 |  | 4460 | 3238 | 7698 | 3151 | 440 | 895 | 0 | 0 | 3029 | 86 | 0 | 0 | 96 | 0 | 1 | 0 | 98.35
4:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 363 | 201 |  | 0 | 170 | 0 | 0 | 0 | 0 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 19 | 25 | 31 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 0 | 280 | 0 | 0 | 8 | 0 | 45 | 46 | 0 | 5 | 0 | 0 | 0 | 18 | 10 | 8 | 8 | 92 | 103 | 0 | 0 | 0 | 43 | 28 | 0 | 5 | 0 | 0 | 0 | 5 | 0 | 199 | 18 | 0 | 10 | 290 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 400 | 0 | 213 | 0 | 0 |  | 439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 740 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 140 | 814 | 0 | 0 |  | 4424 | 3146 | 7570 | 3161 | 439 | 912 | 0 | 0 | 2880 | 86 | 0 | 0 | 92 | 0 | 0 | 0 | 98.35
5:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 363 | 211 |  | 0 | 170 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 19 | 25 | 31 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 32 | 0 | 0 | 0 | 280 | 0 | 0 | 8 | 0 | 45 | 46 | 0 | 5 | 0 | 0 | 0 | 18 | 10 | 8 | 8 | 90 | 100 | 0 | 0 | 0 | 43 | 28 | 0 | 5 | 0 | 0 | 0 | 5 | 0 | 199 | 18 | 0 | 10 | 275 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 365 | 0 | 213 | 0 | 0 |  | 440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 740 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 140 | 815 | 0 | 0 |  | 4392 | 3116 | 7508 | 3171 | 440 | 917 | 0 | 0 | 2804 | 86 | 0 | 0 | 90 | 0 | 0 | 0 | 98.34
6:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 363 | 211 |  | 0 | 170 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 19 | 25 | 33 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 32 | 0 | 0 | 0 | 280 | 0 | 0 | 8 | 0 | 42 | 46 | 0 | 8 | 0 | 0 | 0 | 18 | 10 | 19 | 8 | 90 | 100 | 0 | 0 | 0 | 43 | 28 | 0 | 30 | 0 | 0 | 0 | 25 | 0 | 199 | 18 | 0 | 10 | 290 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 401 | 2 | 211 | 0 | 0 |  | 440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 740 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 140 | 823 | 0 | 0 |  | 4564 | 3128 | 7692 | 3246 | 440 | 980 | 0 | 0 | 2848 | 86 | 0 | 0 | 90 | 0 | 2 | 0 | 98.34
7:00 | 0 | 0 | 0 | 180 | 0 | 40 | 0 | 371 | 232 |  | 0 | 225 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 19 | 25 | 33 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 28 | 0 | 0 | 0 | 280 | 0 | 0 | 50 | 0 | 45 | 45 | 0 | 38 | 0 | 0 | 0 | 18 | 10 | 33 | 8 | 88 | 74 | 0 | 0 | 0 | 43 | 28 | 0 | 47 | 0 | 0 | 0 | 40 | 0 | 198 | 17 | 0 | 10 | 305 | 8 | 8 | 0 | 0 | 0 | 0 | 5 | 0 | 1 | 3 | 0 | 0 | 0 | 400 | 3 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 250 | 0 | 0 | 453 | 7 | 215 | 0 | 0 |  | 440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 123 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 419 | 1 | 176 | 838 | 6 | 0 |  | 4951 | 3275 | 8226 | 3299 | 440 | 1198 | 0 | 34 | 3041 | 86 | 0 | 16 | 88 | 17 | 7 | 30 | 98.33
8:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 400 | 211 |  | 0 | 225 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 19 | 25 | 33 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 2 | 0 | 0 | 0 | 290 | 0 | 0 | 55 | 0 | 45 | 46 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 8 | 92 | 71 | 0 | 0 | 1 | 43 | 26 | 0 | 47 | 0 | 0 | 0 | 40 | 0 | 199 | 17 | 0 | 10 | 280 | 8 | 8 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 10 | 0 | 0 | 0 | 401 | 16 | 17 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 20 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 330 | 0 | 0 | 495 | 5 | 213 | 0 | 0 |  | 440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 890 | 123 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 424 | 6 | 200 | 822 | 69 | 0 |  | 5152 | 3489 | 8641 | 3404 | 440 | 1177 | 0 | 75 | 3214 | 86 | 0 | 16 | 92 | 132 | 5 | 104 | 98.33
9:00 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 389 | 222 |  | 0 | 175 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 19 | 25 | 32 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 55 | 0 | 44 | 46 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 8 | 98 | 35 | 0 | 0 | 2 | 43 | 28 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 200 | 17 | 0 | 10 | 285 | 8 | 5 | 0 | 0 | 0 | 0 | 56 | 0 | 17 | 14 | 0 | 3 | 0 | 365 | 16 | 35 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 40 | 0 | 5 | 0 | 17 | 18 | 2 | 0 | 320 | 0 | 0 | 450 | 1 | 213 | 0 | 0 |  | 439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 850 | 122 | 0 | 0 | 3 | 42 | 0 | 0 | 0 | 398 | 19 | 200 | 812 | 77 | 0 |  | 5059 | 3514 | 8573 | 3353 | 439 | 1108 | 0 | 159 | 3093 | 86 | 0 | 16 | 98 | 220 | 1 | 102 | 98.32
10:00 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 384 | 220 |  | 0 | 200 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 18 | 25 | 32 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 310 | 0 | 0 | 102 | 0 | 44 | 46 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 8 | 94 | 35 | 0 | 0 | 2 | 43 | 28 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 200 | 17 | 0 | 10 | 290 | 8 | 5 | 0 | 0 | 0 | 0 | 32 | 0 | 17 | 18 | 12 | 17 | 0 | 353 | 8 | 35 | 0 | 4 | 0 | 0 | 14 | 0 | 10 | 0 | 370 | 0 | 43 | 0 | 17 | 0 | 17 | 25 | 18 | 0 | 230 | 0 | 0 | 450 | 0 | 356 | 0 | 0 |  | 440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 164 | 0 | 0 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 860 | 124 | 0 | 0 | 4 | 62 | 0 | 0 | 0 | 402 | 27 | 172 | 816 | 74 | 0 |  | 5288 | 3476 | 8764 | 3192 | 440 | 1215 | 0 | 223 | 3220 | 86 | 0 | 32 | 94 | 262 | 0 | 73 | 98.32
11:00 | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 361 | 222 |  | 0 | 170 | 0 | 0 | 2 | 0 | 270 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 18 | 33 | 32 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 0 | 0 | 3 | 12 | 0 | 6 | 10 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 102 | 0 | 37 | 45 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 8 | 102 | 34 | 0 | 0 | 2 | 43 | 22 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 199 | 17 | 0 | 10 | 285 | 8 | 5 | 0 | 0 | 0 | 0 | 32 | 0 | 20 | 20 | 12 | 25 | 0 | 353 | 8 | 52 | 5 | 4 | 0 | 8 | 17 | 0 | 18 | 0 | 370 | 0 | 45 | 0 | 17 | 0 | 17 | 29 | 18 | 4 | 225 | 0 | 14 | 450 | 2 | 564 | 0 | 0 |  | 440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 870 | 144 | 0 | 0 | 4 | 70 | 0 | 0 | 0 | 398 | 33 | 170 | 819 | 151 | 0 |  | 5510 | 3596 | 9106 | 3143 | 440 | 1199 | 0 | 281 | 3441 | 86 | 0 | 51 | 102 | 361 | 2 | 0 | 98.31
12:00 | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 394 | 213 |  | 0 | 225 | 0 | 0 | 17 | 0 | 240 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 18 | 33 | 31 | 8 | 0 | 46 | 40 | 0 | 0 | 1 | 142 | 0 | 0 | 0 |  | 0 | 2 | 3 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 102 | 0 | 44 | 44 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 8 | 114 | 34 | 0 | 0 | 2 | 43 | 22 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 199 | 17 | 0 | 10 | 285 | 16 | 5 | 0 | 0 | 0 | 0 | 56 | 0 | 24 | 18 | 12 | 67 | 0 | 397 | 10 | 52 | 17 | 4 | 20 | 10 | 17 | 0 | 34 | 0 | 398 | 0 | 47 | 17 | 17 | 0 | 17 | 29 | 18 | 17 | 225 | 0 | 31 | 500 | 4 | 565 | 0 | 0 |  | 440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 930 | 144 | 0 | 0 | 5 | 71 | 0 | 0 | 0 | 446 | 27 | 200 | 816 | 175 | 0 |  | 5850 | 3801 | 9651 | 3245 | 440 | 1244 | 0 | 457 | 3627 | 86 | 0 | 53 | 114 | 381 | 4 | 0 | 98.31
13:00 | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 396 | 186 |  | 0 | 225 | 0 | 0 | 34 | 0 | 226 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 17 | 33 | 31 | 8 | 0 | 46 | 40 | 0 | 0 | 8 | 140 | 0 | 0 | 0 |  | 0 | 56 | 6 | 12 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 158 | 0 | 44 | 44 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 8 | 110 | 34 | 0 | 0 | 2 | 43 | 22 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 199 | 17 | 0 | 10 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 56 | 0 | 24 | 18 | 12 | 100 | 0 | 403 | 56 | 52 | 17 | 4 | 100 | 17 | 17 | 0 | 38 | 0 | 398 | 0 | 44 | 17 | 17 | 0 | 17 | 28 | 17 | 17 | 225 | 0 | 17 | 500 | 4 | 390 | 0 | 0 |  | 440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 40 | 0 | 4 | 30 | 1020 | 144 | 0 | 0 | 4 | 68 | 17 | 0 | 0 | 473 | 31 | 230 | 811 | 167 | 0 |  | 5925 | 4054 | 9979 | 3198 | 440 | 1288 | 0 | 779 | 3594 | 86 | 0 | 110 | 110 | 370 | 4 | 34.38 | 98.3
14:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 385 | 187 |  | 0 | 190 | 0 | 0 | 34 | 0 | 225 | 0 | 0 | 0 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 20 | 17 | 33 | 31 | 8 | 0 | 46 | 40 | 0 | 0 | 8 | 141 | 0 | 0 | 0 |  | 0 | 48 | 6 | 12 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 102 | 0 | 43 | 42 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 8 | 120 | 34 | 0 | 0 | 2 | 43 | 22 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 196 | 17 | 0 | 10 | 270 | 8 | 5 | 0 | 43 | 0 | 0 | 58 | 0 | 39 | 15 | 12 | 110 | 6 | 354 | 56 | 52 | 17 | 3 | 100 | 17 | 17 | 0 | 38 | 0 | 370 | 0 | 36 | 17 | 17 | 0 | 17 | 23 | 18 | 17 | 255 | 0 | 17 | 460 | 2 | 393 | 0 | 0 |  | 440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 50 | 0 | 40 | 0 | 4 | 54 | 950 | 144 | 0 | 0 | 4 | 55 | 35 | 0 | 0 | 403 | 23 | 194 | 819 | 139 | 0 |  | 5741 | 3873 | 9614 | 3000 | 440 | 1257 | 0 | 914 | 3389 | 86 | 0 | 102 | 120 | 304 | 2 | 0 | 98.31
15:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 373 | 186 |  | 0 | 190 | 0 | 0 | 34 | 0 | 230 | 0 | 0 | 0 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 20 | 17 | 25 | 31 | 8 | 0 | 46 | 40 | 0 | 0 | 8 | 141 | 0 | 0 | 0 |  | 0 | 8 | 9 | 12 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 102 | 0 | 43 | 42 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 8 | 114 | 33 | 0 | 0 | 1 | 41 | 22 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 197 | 17 | 0 | 9 | 290 | 8 | 3 | 0 | 65 | 0 | 0 | 58 | 0 | 31 | 11 | 12 | 120 | 20 | 354 | 56 | 52 | 17 | 2 | 65 | 17 | 17 | 0 | 9 | 0 | 370 | 0 | 25 | 17 | 17 | 0 | 17 | 16 | 17 | 17 | 330 | 0 | 0 | 450 | 0 | 399 | 0 | 0 |  | 436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 50 | 0 | 37 | 0 | 3 | 35 | 940 | 170 | 0 | 0 | 2 | 37 | 36 | 0 | 0 | 402 | 17 | 150 | 815 | 84 | 0 |  | 5708 | 3732 | 9440 | 3037 | 436 | 1312 | 0 | 866 | 3326 | 86 | 0 | 65 | 114 | 198 | 0 | 20.055 | 98.29
16:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 363 | 176 |  | 0 | 190 | 0 | 0 | 25 | 0 | 225 | 0 | 0 | 1 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 14 | 20 | 17 | 33 | 31 | 8 | 0 | 46 | 40 | 0 | 0 | 8 | 142 | 0 | 0 | 0 |  | 4 | 8 | 10 | 12 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 102 | 0 | 43 | 41 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 8 | 114 | 32 | 0 | 0 | 0 | 40 | 22 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 197 | 17 | 0 | 10 | 285 | 8 | 3 | 0 | 95 | 0 | 0 | 58 | 0 | 27 | 6 | 12 | 85 | 20 | 356 | 56 | 52 | 17 | 1 | 65 | 17 | 17 | 0 | 9 | 0 | 380 | 7 | 9 | 17 | 17 | 0 | 17 | 7 | 18 | 17 | 350 | 0 | 0 | 450 | 1 | 360 | 0 | 0 |  | 437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 3 | 0 | 35 | 0 | 35 | 0 | 1 | 35 | 940 | 170 | 0 | 2 | 0 | 16 | 36 | 0 | 0 | 404 | 8 | 150 | 827 | 31 | 0 |  | 5667 | 3632 | 9299 | 3051 | 437 | 1281 | 0 | 883 | 3301 | 86 | 0 | 66 | 114 | 79 | 1 | 20.055 | 98.29
17:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 358 | 167 |  | 0 | 225 | 0 | 5 | 17 | 1 | 227 | 0 | 0 | 9 | 16 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 14 | 20 | 19 | 33 | 31 | 8 | 0 | 46 | 40 | 0 | 0 | 8 | 141 | 0 | 0 | 0 |  | 6 | 8 | 4 | 12 | 0 | 19 | 0 | 2 | 0 | 0 | 0 | 280 | 0 | 0 | 102 | 0 | 43 | 41 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 8 | 116 | 46 | 0 | 0 | 0 | 43 | 26 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 197 | 17 | 0 | 10 | 290 | 8 | 3 | 0 | 100 | 0 | 0 | 58 | 0 | 26 | 0 | 12 | 95 | 20 | 354 | 56 | 105 | 17 | 0 | 70 | 36 | 17 | 0 | 27 | 0 | 380 | 17 | 0 | 55 | 17 | 0 | 17 | 0 | 26 | 17 | 360 | 0 | 0 | 452 | 2 | 270 | 0 | 0 |  | 700 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 17 | 0 | 35 | 0 | 42 | 0 | 0 | 35 | 970 | 142 | 0 | 35 | 0 | 1 | 36 | 0 | 0 | 404 | 0 | 150 | 824 | 2 | 0 |  | 5856 | 3911 | 9767 | 3081 | 700 | 1287 | 0 | 1192 | 3240 | 86 | 0 | 60 | 116 | 3 | 2 | 20 | 98.28
18:00 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 354 | 162 |  | 0 | 225 | 0 | 12 | 17 | 20 | 227 | 0 | 0 | 16 | 32 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 14 | 20 | 18 | 33 | 3 | 13 | 0 | 46 | 40 | 0 | 0 | 17 | 141 | 0 | 0 | 0 |  | 6 | 18 | 13 | 12 | 0 | 20 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 0 | 130 | 0 | 43 | 42 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 6 | 126 | 47 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 193 | 17 | 0 | 10 | 270 | 8 | 3 | 0 | 125 | 0 | 0 | 104 | 0 | 51 | 0 | 12 | 140 | 41 | 402 | 75 | 105 | 17 | 0 | 120 | 36 | 17 | 0 | 48 | 0 | 400 | 55 | 0 | 55 | 17 | 0 | 17 | 0 | 36 | 17 | 390 | 0 | 0 | 480 | 1 | 273 | 0 | 0 |  | 757 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 17 | 0 | 45 | 0 | 98 | 0 | 0 | 90 | 1080 | 110 | 0 | 55 | 0 | 0 | 46 | 0 | 0 | 460 | 0 | 200 | 873 | 0 | 0 |  | 6377 | 4470 | 10847 | 3271 | 757 | 1268 | 0 | 1723 | 3536 | 86 | 0 | 79 | 126 | 0 | 1 | 0 | 98.28
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 353 | 161 |  | 0 | 225 | 0 | 29 | 34 | 15 | 227 | 0 | 0 | 34 | 32 | 16 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 14 | 20 | 19 | 25 | 31 | 25 | 0 | 46 | 40 | 0 | 0 | 8 | 140 | 0 | 0 | 0 |  | 6 | 25 | 14 | 12 | 0 | 20 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 0 | 130 | 0 | 44 | 43 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 6 | 120 | 47 | 0 | 0 | 0 | 43 | 28 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 195 | 17 | 0 | 10 | 270 | 8 | 3 | 0 | 30 | 0 | 0 | 107 | 0 | 60 | 0 | 12 | 155 | 70 | 402 | 24 | 52 | 17 | 0 | 100 | 17 | 17 | 0 | 49 | 0 | 400 | 30 | 0 | 55 | 17 | 0 | 17 | 0 | 48 | 17 | 393 | 0 | 0 | 480 | 0 | 275 | 0 | 0 |  | 626 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 17 | 0 | 50 | 0 | 70 | 0 | 0 | 50 | 1150 | 110 | 0 | 17 | 0 | 0 | 36 | 0 | 0 | 613 | 0 | 200 | 854 | 0 | 0 |  | 6247 | 4468 | 10715 | 3321 | 626 | 1271 | 0 | 1494 | 3742 | 86 | 0 | 55 | 120 | 0 | 0 | 0 | 98.26
19:30 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 355 | 161 |  | 0 | 225 | 0 | 0 | 17 | 0 | 227 | 0 | 0 | 8 | 32 | 16 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 14 | 20 | 19 | 25 | 31 | 8 | 0 | 46 | 40 | 0 | 0 | 8 | 141 | 0 | 0 | 0 |  | 6 | 25 | 14 | 12 | 0 | 20 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 0 | 130 | 0 | 44 | 43 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 6 | 118 | 54 | 0 | 0 | 0 | 43 | 28 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 195 | 18 | 0 | 10 | 275 | 8 | 7 | 0 | 0 | 0 | 0 | 108 | 0 | 17 | 0 | 12 | 155 | 70 | 402 | 24 | 52 | 17 | 0 | 100 | 17 | 17 | 0 | 26 | 0 | 400 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 35 | 17 | 395 | 0 | 0 | 480 | 0 | 274 | 0 | 0 |  | 767 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 17 | 0 | 50 | 0 | 34 | 0 | 0 | 35 | 1160 | 110 | 0 | 17 | 0 | 0 | 36 | 0 | 0 | 627 | 0 | 200 | 870 | 0 | 0 |  | 6003 | 4583 | 10586 | 3330 | 767 | 1277 | 0 | 1172 | 3781 | 86 | 0 | 55 | 118 | 0 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 356 | 161 |  | 0 | 225 | 0 | 0 | 15 | 0 | 227 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 15 | 20 | 20 | 25 | 31 | 8 | 0 | 46 | 40 | 0 | 0 | 8 | 141 | 0 | 0 | 0 |  | 6 | 0 | 4 | 12 | 0 | 20 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 0 | 130 | 0 | 44 | 44 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 6 | 112 | 77 | 0 | 0 | 0 | 43 | 28 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 195 | 18 | 0 | 10 | 280 | 16 | 7 | 0 | 0 | 0 | 0 | 108 | 0 | 23 | 0 | 12 | 155 | 20 | 402 | 8 | 52 | 17 | 0 | 50 | 17 | 17 | 0 | 9 | 0 | 400 | 0 | 0 | 17 | 17 | 0 | 17 | 0 | 30 | 17 | 393 | 0 | 0 | 480 | 0 | 273 | 0 | 0 |  | 767 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 1150 | 121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 632 | 0 | 200 | 871 | 0 | 0 |  | 5772 | 4526 | 10298 | 3370 | 767 | 1307 | 0 | 876 | 3776 | 86 | 0 | 4 | 112 | 0 | 0 | 0 | 98.27
21:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 360 | 162 |  | 0 | 225 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 20 | 20 | 25 | 30 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 141 | 0 | 0 | 0 |  | 0 | 0 | 17 | 12 | 0 | 20 | 0 | 2 | 0 | 0 | 0 | 315 | 0 | 0 | 45 | 0 | 44 | 44 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 6 | 112 | 95 | 0 | 0 | 0 | 43 | 28 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 195 | 18 | 0 | 10 | 290 | 8 | 7 | 0 | 0 | 0 | 0 | 85 | 0 | 20 | 0 | 12 | 85 | 0 | 401 | 8 | 35 | 17 | 0 | 50 | 17 | 17 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 17 | 17 | 393 | 0 | 0 | 480 | 0 | 272 | 0 | 0 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619 | 0 | 200 | 870 | 0 | 0 |  | 5459 | 4550 | 10009 | 3380 | 908 | 1274 | 0 | 471 | 3761 | 86 | 0 | 17 | 112 | 0 | 0 | 0 | 98.26
22:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 364 | 161 |  | 0 | 225 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 20 | 20 | 25 | 16 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 141 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 20 | 0 | 6 | 0 | 0 | 0 | 310 | 0 | 0 | 45 | 0 | 44 | 44 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 6 | 112 | 95 | 0 | 0 | 0 | 43 | 28 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 197 | 18 | 0 | 10 | 260 | 8 | 7 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 12 | 68 | 0 | 401 | 8 | 35 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 350 | 0 | 0 | 480 | 0 | 274 | 0 | 0 |  | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 505 | 0 | 160 | 841 | 0 | 0 |  | 5171 | 4480 | 9651 | 3240 | 909 | 1513 | 0 | 264 | 3510 | 86 | 0 | 17 | 112 | 0 | 0 | 0 | 98.26
23:00 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 362 | 171 |  | 0 | 225 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 20 | 20 | 25 | 30 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 141 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 10 | 9 | 0 | 0 | 0 | 280 | 0 | 0 | 45 | 0 | 44 | 43 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 8 | 108 | 95 | 0 | 0 | 0 | 43 | 28 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 199 | 18 | 0 | 10 | 270 | 8 | 7 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 34 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 350 | 0 | 0 | 478 | 0 | 274 | 0 | 0 |  | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 880 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 423 | 0 | 150 | 839 | 0 | 0 |  | 4997 | 4280 | 9277 | 3200 | 909 | 1620 | 0 | 123 | 3214 | 86 | 0 | 17 | 108 | 0 | 0 | 0 | 98.25
24:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 343 | 181 |  | 0 | 225 | 0 | 0 | 0 | 0 | 236 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 20 | 20 | 25 | 30 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 141 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 280 | 0 | 0 | 45 | 0 | 44 | 45 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 8 | 104 | 94 | 0 | 0 | 0 | 43 | 28 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 199 | 18 | 0 | 10 | 280 | 8 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 350 | 0 | 0 | 452 | 0 | 272 | 0 | 0 |  | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 150 | 820 | 0 | 0 |  | 4864 | 4056 | 8920 | 3182 | 910 | 1615 | 0 | 59 | 2947 | 86 | 0 | 17 | 104 | 0 | 0 | 0 | 98.25
KWH | 0 | 0 | 0 | 4347000 | 0 | 1421818 | 0 | 8945670 | 4650000 |  | 0 | 4682800 | 0 | 48960 | 187729 | 58770 | 5960557 | 0 | 0 | 54077 | 207072 | 500160 | 0 | 0 | 0 | 0 | 124560 | 133513 | 137956 | 306900 | 480000 | 427320 | 667800 | 719600 | 144960 | 0 | 1108740 | 968000 | 0 | 0 | 83644 | 4128611 | 0 | 0 | 0 |  | 40320 | 144000 | 120219 | 130560 | 0 | 160800 | 156816 | 202000 | 0 | 0 | 0 | 7512100 | 0 | 0 | 1856727 | 0 | 1041120 | 1059840 | 0 | 1034616 | 0 | 0 | 0 | 433800 | 217440 | 688100 | 190000 | 2513280 | 1527360 | 0 | 0 | 11750 | 1006000 | 673560 | 0 | 202176 | 0 | 0 | 0 | 1428480 | 0 | 3992320 | 415000 | 0 | 252360 | 6942500 | 229536 | 145152 | 0 | 536945 | 0 | 0 | 1010400 | 0 | 413856 | 131220 | 161280 | 140544 | 281018 | 8898000 | 525600 | 807360 | 204072 | 26043 | 875673 | 252678 | 285200 | 0 | 331800 | 0 | 9183700 | 114240 | 296630 | 272160 | 284782 | 0 | 308160 | 186558 | 319680 | 200520 | 7248000 | 0 | 85309 | 10979999 | 40800 | 7192727 | 0 | 0 |  | 13501090 | 0 | 0 | 0 | 120000 | 0 | 0 | 0 | 0 | 0 | 0 | 2390000 | 361900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10632 | 0 | 0 | 0 | 236592 | 0 | 0 | 4155600 | 0 | 0 | 4749764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2217200 | 63840 | 0 | 411168 | 0 | 396364 | 0 | 24817 | 386880 | 24558400 | 3309491 | 0 | 123600 | 29220 | 445680 | 286656 | 0 | 0 | 10727270 | 190361 | 4080000 | 20023636 | 1003590 | 0 |  | 126419103 | 93803751 | 220222854 | 77003127 | 13501090 | 29621908 | 0 | 10638029 | 81717632 | 2076740 | 0 | 764379 | 2513280 | 2345869 | 40800 | 0
Fuel Cost | 0 | 0 | 0 | 6477030 | 0 | 1891017.94 | 0 | 9392953.5 | 5022000 |  | 0 | 5104252 | 0 | 547372.8 | 2487409.25 | 778702.5 | 6675823.84 | 0 | 0 | 790605.74 | 2913503.04 | 8107593.6 | 0 | 0 | 0 | 0 | 1584403.2 | 1802425.5 | 1849989.96 | 230175 | 360000 | 0 | 0 | 0 | 2465769.6 | 0 | 299359.8 | 261360 | 0 | 0 | 1367579.4 | 4293755.44 | 0 | 0 | 0 |  | 526176 | 2401920 | 2046127.38 | 1763865.6 | 0 | 1860456 | 199156.32 | 672660 | 0 | 0 | 0 | 8338431 | 0 | 0 | 2395177.83 | 0 | 1176465.6 | 1579161.6 | 0 | 1727808.72 | 0 | 0 | 0 | 594306 | 163080 | 1204175 | 142500 | 18045350.4 | 1664822.4 | 0 | 0 | 187295 | 1378220 | 889099.2 | 0 | 349764.48 | 0 | 0 | 0 | 3256934.4 | 0 | 4032243.2 | 892250 | 0 | 499672.8 | 6942500 | 172152 | 110315.52 | 0 | 7329299.25 | 0 | 0 | 13620192 | 0 | 5731905.6 | 1533961.8 | 1664409.6 | 1919831.04 | 3729108.86 | 8186160 | 6391296 | 11674425.6 | 2581510.8 | 405229.08 | 10280401.02 | 2751663.42 | 3031676 | 0 | 4276902 | 0 | 8449004 | 1479408 | 4286303.5 | 3453710.4 | 3240819.16 | 0 | 4024569.6 | 2229368.1 | 4785609.6 | 2640848.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 40503270 | 0 | 0 | 0 | 1249200 | 0 | 0 | 0 | 0 | 0 | 0 | 2676800 | 702086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144914.16 | 0 | 0 | 0 | 179100.144 | 0 | 0 | 35239488 | 0 | 0 | 5509726.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2195028 | 858009.6 | 0 | 4864117.44 | 0 | 5033822.8 | 0 | 274227.85 | 4696723.2 | 203834720 | 3375680.82 | 0 | 914640 | 330478.2 | 5227826.4 | 4394436.48 | 0 | 0 | 97510884.3 | 0 | 48837600 | 171202087.8 | 0 | 0 |  | 249612781.39 | 639754867.434 | 889367648.824 | 73387744.404 | 40503270 | 35713744.59 | 0 | 137501708.62 | 556624780.1 | 560719.8 | 0 | 12555640.98 | 18045350.4 | 14474689.93 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 394 | 213 |  | 0 | 225 | 0 | 0 | 17 | 0 | 240 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 18 | 33 | 31 | 8 | 0 | 46 | 40 | 0 | 0 | 1 | 142 | 0 | 0 | 0 |  | 0 | 2 | 3 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 102 | 0 | 44 | 44 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 25 | 8 | 114 | 34 | 0 | 0 | 2 | 43 | 22 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 199 | 17 | 0 | 10 | 285 | 16 | 5 | 0 | 0 | 0 | 0 | 56 | 0 | 24 | 18 | 12 | 67 | 0 | 397 | 10 | 52 | 17 | 4 | 20 | 10 | 17 | 0 | 34 | 0 | 398 | 0 | 47 | 17 | 17 | 0 | 17 | 29 | 18 | 17 | 225 | 0 | 31 | 500 | 4 | 565 | 0 | 0 |  | 440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 930 | 144 | 0 | 0 | 5 | 71 | 0 | 0 | 0 | 446 | 27 | 200 | 816 | 175 | 0 |  | 9651 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 354 | 162 |  | 0 | 225 | 0 | 12 | 17 | 20 | 227 | 0 | 0 | 16 | 32 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 14 | 20 | 18 | 33 | 3 | 13 | 0 | 46 | 40 | 0 | 0 | 17 | 141 | 0 | 0 | 0 | 0 | 6 | 18 | 13 | 12 | 0 | 20 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 0 | 130 | 0 | 43 | 42 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 6 | 126 | 47 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 193 | 17 | 0 | 10 | 270 | 8 | 3 | 0 | 125 | 0 | 0 | 104 | 0 | 51 | 0 | 12 | 140 | 41 | 402 | 75 | 105 | 17 | 0 | 120 | 36 | 17 | 0 | 48 | 0 | 400 | 55 | 0 | 55 | 17 | 0 | 17 | 0 | 36 | 17 | 390 | 0 | 0 | 480 | 1 | 273 | 0 | 0 |  | 757 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 17 | 0 | 45 | 0 | 98 | 0 | 0 | 90 | 1080 | 110 | 0 | 55 | 0 | 0 | 46 | 0 | 0 | 460 | 0 | 200 | 873 | 0 | 0 |  | 10847 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 412 | 200 |  | 0 | 225 | 0 | 90 | 85 | 55 | 250 | 0 | 0 | 90 | 100 | 149 | 40 | 0 | 0 | 0 | 35 | 35 | 35 | 15 | 20 | 18 | 33 | 33 | 25 | 0 | 46 | 40 | 0 | 0 | 17 | 215 | 0 | 0 | 0 |  | 6 | 64 | 0 | 12 | 0 | 19 | 12 | 20 | 0 | 0 | 0 | 320 | 0 | 0 | 130 | 0 | 47 | 46 | 0 | 51 | 0 | 20 | 52 | 18 | 11 | 33 | 10 | 140 | 80 | 0 | 0 | 0 | 43 | 28 | 0 | 47 | 0 | 0 | 0 | 80 | 0 | 200 | 17 | 0 | 10 | 300 | 16 | 8 | 0 | 130 | 0 | 0 | 100 | 0 | 100 | 0 | 12 | 17 | 150 | 400 | 85 | 105 | 17 | 0 | 260 | 17 | 17 | 114 | 55 | 12 | 400 | 72 | 0 | 55 | 17 | 0 | 17 | 0 | 53 | 17 | 380 | 0 | 0 | 500 | 10 | 270 | 0 | 0 |  | 928 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 50 | 70 | 16 | 130 | 25 | 110 | 0 | 0 | 0 | 30 | 20 | 85 | 28 | 42 | 40 | 52 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 90 | 0 | 50 | 0 | 113 | 0 | 0 | 113 | 1220 | 220 | 0 | 150 | 0 | 0 | 110 | 0 | 0 | 620 | 0 | 200 | 900 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 412 | 200 | 0 | 0 | 225 | 0 | 90 | 85 | 15 | 250 | 0 | 0 | 90 | 100 | 16 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 20 | 18 | 33 | 33 | 8 | 0 | 46 | 40 | 0 | 0 | 8 | 212 |  | 0 | 0 | 0 | 6 | 40 | 0 | 12 | 0 | 6 | 12 | 10 | 0 | 0 | 0 | 320 | 0 | 0 | 55 | 0 | 47 | 40 | 0 | 51 | 0 | 0 | 52 | 18 | 11 | 33 | 10 | 128 | 80 | 0 | 0 | 1.6 | 43 | 28 | 0 | 44 | 0 | 0 | 0 | 60 | 0 | 200 | 17 | 0 | 10 | 280 | 16 | 8 | 0 | 80 | 0 | 0 | 84 | 0 | 18 | 20 | 12 | 17 | 150 | 400 | 56 | 30 | 17 | 5 | 260 | 17 | 17 | 114 | 28 | 12 | 400 | 26 | 50 | 17 | 17 | 0 | 17 | 35 | 36 | 17 | 300 | 0 |  | 500 | 10 | 270 | 0 | 0 |  | 928 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 28 | 34 | 30 | 52 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 90 | 0 | 35 | 0 | 113 | 0 | 8 | 35 | 1000 | 220 |  | 0 | 6 | 100 | 70 | 0 |  | 500 | 30 | 200 | 850 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 160 | 0 | 74 | 0 | 303 | 189 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 238 | 0 | 0 | 0 | 103 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 20 | 19 | 25 | 33 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 0 | 0 | 0 | 330 | 0 | 0 | 45 | 0 | 44 | 46 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 8 | 86 | 74 | 0 | 0 | 1 | 43 | 28 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 201 | 17 | 0 | 10 | 305 | 8 | 7 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 6 | 0 | 0 | 0 | 350 | 0 | 52 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 15 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 395 | 0 | 0 | 360 | 3 | 273 | 0 | 0 | 0 | 764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 600 | 220 | 0 | 0 | 1 | 7 | 0 | 0 | 0 | 355 | 6 | 150 | 819 | 34 | 0 | 0 |  |  |  | 106625035 | 13501090 | 0 | 81717632 | 11402408 | 2513280 | 2345869 | 40800 | 2076740
[8 empty] | 299430 | [13 empty] | 299565 | [26 empty] | 399366 | 399587 | [8 empty] | 299280 | [26 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 |  | 399747 |  |  |  | 399575 |  | 399337 | 399589 | 299230 | [7 empty] | 399245 |  | 299282 | 399274 |  | 399223 |  | 399630 | [12 empty] | 599468 | [32 empty] | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 | [8 empty] | 599726 | [9 empty] | 106.625 | 13.5011 | 0 | 81.7176 | 11.4024 | 2.5133 | 2.3459 | 0.0408 | 2.0767
| Minimum Generation |  | 7508 | 5:00
| Highest Generation |  | 10847 | 18:00 | [200 empty] | 220.2229
| Day Peak Generation |  | 9651 | 12:00
| Evening Peak Generation |  | 10847 | 18:00 | [200 empty] | 202699852
| HVDC Max Flow |  | 910 | 24:00 | [200 empty] | 202.6999
| HVDC EvPeak Flow |  | 757 | 18:00
| Load factor L.F |  | 84.59% | [166 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-11-29
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-11-28 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9651 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 7400
Evening Peak Generation : |  |  | 10847 | MW Hour : | 18:00 | Available Max Generation : |  | 14048
E.P. Demand (at gen end) : |  |  | 10847 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 11000
Maximum Generation : |  |  | 10847 | MW Hour : | 18:00 | Reserve(Generation end) |  | 3048
Total Gen. (MKWH) : |  |  | 220.2229 | System Load Factor : | 84.59% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 194 | MW at | 8:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-11-29
Actual : |  | 98.22 | Ft.(MSL) , | Rule curve : | 106.2 | Ft.( MSL )
Gas Consumed : |  | Total = | 823.27 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 109101488.994
: |  |  | Coal : | 556624780.1 | Oil : | 150057349.6 | Total : | 815783618.694
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3693.7597 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1009.6328 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1412.702 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1226.4236 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1009.8797 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 750.3172 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 421.4087 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 350.4332 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 685.4034 |  |  | 0 | 0%
Total |  | 0 |  | 10559.9605 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:05 | 16:53 | Patuakhali 132/33kV S/S 415T (T-2) LT Scheduled S/D Due to Annual Maintenance-2023
08:05 | 16:52 | Patuakhali 132/33kV S/S 415T (T-2) HT Scheduled S/D Due to Annual Maintenance-2023
Annual maintenance-2023
08:13 | 16:24 | Cumilla(N)-Daudkandi 132 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to Annual maintenance and
from Daudkandi 132/33kV end Due to for Annual Maintenance Work at Daudkandi substation end
08:15 | 16:23 | Bogura(New)-Naogaon 132 kV Ckt-2 Scheduled S/D from Naogaon 132/33kV end Due to Annual Maintenance and from Bogura
230/132kV end Due to Annual Maintenance Work.
08:16 | 16:01 | Gopalganj 132/33kV S/S Gallamari-2 Scheduled S/D Due to Annual maintenance
08:22 | 16:44 | Barishal 230/132kV S/S 230kV BUS Scheduled S/D Due to Annual maintenance
08:27 | 13:06 | Shahjibazar 132/33kV S/S TR-06 HT Scheduled S/D Due to Annual Maintenance. Load flow by TR-04
08:28 | 16:34 | Rajshahi 230/132/33kV S/S 230/132 kV ATR-02 (714T) HT Scheduled S/D
08:28 | 16:34 | Rajshahi 230/132/33kV S/S 230/132 kV ATR-02 (714T) LT Scheduled S/D
08:30 |  | Chandpur 200MW (Desh energy) Syncronized
08:31 |  | Anlima Energy Ltd. Syncronized
08:36 |  | Fenchuganj 44MW (Energyprima) Shutdown
08:37 | 16:01 | Chandraghona-Rangamati 132 kV Ckt-2 Scheduled S/D from Rangamati 132/33kV end Due to Rangamati-Chandraghona Ckt-02
taken shutdown due to annual deadline Checking.
08:38 | 14:37 | Gopalganj 400/132kV S/S ATR-02 LT Scheduled S/D Due to Annual maintenance
08:41 | 17:02 | Fenchuganj-Kulaura 132 kV Ckt-1 Scheduled S/D from Kulaura 132/33kV end Due to Annual maintenance. and from Fenchuganj
230/132/33kV end Due to Annual Maintenance by Kulaura Substation.
08:44 | 14:36 | Gopalganj 400/132kV S/S ATR-02 HT Scheduled S/D Due to Annual maintenance
08:44 |  | Chandpur 115(Doreen) Syncronized
08:45 | 17:36 | Rampur 230/132/33 S/S Halishahar-1 Scheduled S/D Due to Annual maintenance
08:48 | 15:48 | Barapukuria-Rangpur 132 kV Ckt-2 Scheduled S/D from Saidpur 132/33kV end Due to Annual maintenance
08:49 | 15:50 | Barapukuria-Saidpur 132 kV Ckt-1 Scheduled S/D from Barapukuria 230/132/33kV end Due to Annual Maintenance
| 08:59 | Palashbari 132/33kV S/S TR1-414T HT is restored.
| 08:59 | Palashbari 132/33kV S/S TR2-404T HT is restored.
08:59 | 13:35 | Brahmanbaria 132/33kV S/S 403T LT Scheduled S/D Due to Annual maintenance
08:59 | 13:35 | Brahmanbaria 132/33kV S/S 403T HT Scheduled S/D Due to Annual maintenance
09:01 |  | Karnaphuli Power Ltd. Syncronized
09:02 |  | Patenga 50MW PP (Baraka) Syncronized
09:05 | 09:29 | Aminbazar 400/230/132kV S/S Bus-2 (400kV) Scheduled S/D
09:05 |  | Aminbazar 400/230/132kV S/S 230 kv Bus 02 Scheduled S/D Due to Bus conductor change
09:08 |  | Khulna (C) S/S Tr-3 405T LT Scheduled S/D Due to Due to oil Centrifuging
09:09 |  | Khulna (C) S/S Tr-3 405T HT Scheduled S/D Due to Oil Centrifuging
09:18 |  | Chowmuhani 113 MW Syncronized
09:26 | 17:01 | Fenchuganj-Sreemangal 132kV Ckt-1 Scheduled S/D from Sreemongol 132/33kV end Due to Annual Maintenance. and from
Fenchuganj 230/132/33kV end Due to Annual Maintenance by Sremongal Substation.
09:32 |  | Juldah 100 MW PP Unit-3 (Acorn) Syncronized
09:38 |  | Juldah 100 MW Unit-1 (Acorn) Syncronized
09:39 | 17:33 | Rampur 230/132/33 S/S Khulshi-1 Scheduled S/D Due to Replacing jumper over monopole.
09:48 | 16:52 | Mirpur 132/33kV S/S Reserve Bus Scheduled S/D Due to Annual maintenance work .
10:22 |  | Jodiac Power Syncronized
10:31 |  | Sikalbaha 105 MW PP (Baraka Sikalbaha) Syncronized
10:32 |  | Mirsharai 150 MW Syncronized
10:40 |  | Kanchan Purbachal Power Generation Ltd. Syncronized
10:42 |  | Dohazari -Kalaish 100 MW Peaking Syncronized
10:50 |  | Madanganj 102 PP(Summit) Syncronized
10:52 | 11:15 | Jamalpur 132/33kV S/S Bus-B Project Work S/D
11:01 |  | Gagnagar 102 MW PP (Digital Power) Syncronized
11:04 |  | Sikalbaha 225MW CCPP Tripped with remarks:- ST
11:05 |  | Sikalbaha 225MW CCPP Syncronized with remarks:- GT
11:20 | 12:50 | Jamalpur 132/33kV S/S Bus-A Project Work S/D Due to 132 KV T-4 transformer bay G2G project work
11:22 |  | Kabirpur -Tongi 132kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Annual maintenance work
11:22 |  | Kabirpur -Tongi 132kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Annual maintenance work
11:30 |  | Manikgonj 162MW PP(MPGL) Syncronized
11:30 |  | Anwara 300 MW PP (United) Syncronized
11:35 | 13:53 | Patuakhali 132/33kV S/S 405T (T-1) HT Scheduled S/D Due to TAN-DELTA test
11:35 | 13:54 | Patuakhali 132/33kV S/S 405T (T-1) LT Scheduled S/D Due to TAN-DELTA test
11:56 |  | Raozan 25 MW PP Syncronized
11:57 |  | Hathazari 100 MW peaking PP Syncronized
12:00 |  | Day peak generation is 9651MW
12:01 |  | Bagura 113 MW PP (Confidence)-2 Syncronized
12:09 |  | Rangpur 113 MW PP (Confidence) Syncronized
12:19 | 13:29 | Hathazari-Kaptai 132kV Ckt-1 Forced S/D from Hathazari 230/132/33kV end Due to Bamboo trimming near to line.
12:25 |  | Confidence Power Bogura Unit-1 113 MW Syncronized
12:38 |  | Barabkunda 22 MW PP (Regent) Tripped with remarks:- grid failure
12:41 |  | Energypac Power Venture Thakurgaon Ltd. Syncronized
12:55 | 21:29 | Madanganj 132/33kV S/S Madanganj -Shitalakhya 132 kv Ckt Tripped showing TCS-1, TCS-2 relays Due to Hydraulic
pressure pipe leakage
13:01 |  | Kodda 300 MW PP Unit-2 (Summit) Syncronized
13:09 | 21:31 | Madanganj-Shitalakhya 132kV ckt-1 Forced S/D from Shitalakhya 132/33kV end Due to By NLDC
13:10 |  | Ashuganj 150MW PP (Midland) Syncronized
13:32 | 16:23 | Kaliakoir 400/230/132kV S/S Bibiyana1 Scheduled S/D Due to Relay Testing by SPMD
13:34 |  | Sirajgonj 400 MW CCPP Unit-4 Syncronized with remarks:- GT
13:35 |  | Sirajgonj Unit-4 GT was sync.
14:44 |  | Mirsharai 150 MW Shutdown
15:01 |  | Tangail Palli Power Gen 22 MW Syncronized
| 15:02 | Aminbazar 400/230/132kV S/S 132 kv Bus 01 is restored.
| 15:02 | Aminbazar 400/230/132kV S/S 132 kv Bus 01 is restored.
15:37 |  | Nababganj 55 MW PP (Southern power ) Syncronized
15:48 |  | Meghnaghat 104 MW PP (OPCL) Syncronized
15:49 |  | United Payra Power Ltd. Syncronized
15:51 |  | Siddhirganj 100 PP(Dutch Bangla) Syncronized
15:56 |  | Rupsha 105 MW PP (Orion rupsha) Syncronized
15:58 |  | Manikganj 55 MW PP (Northern) Syncronized
16:07 |  | Khulna 115 PP MW (KPCL-2) Syncronized
| 16:10 | Shahjibazar 132/33kV S/S TR-06 LT is restored.
16:10 |  | Kamalaghat 54 MW PP(Banco Energy) Syncronized
16:21 |  | Meghnaghat 100 MW(IEL) Syncronized
| 16:23 | Mirpur 132/33kV S/S T1 HT is restored.
16:30 | 17:25 | Bibiyana-Kaliakoir 400 kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to Relay Test.
16:32 |  | Kaptai 7 MW Solar PP Shutdown
16:45 |  | Madanganj-55 MW PP(Summit) Syncronized
| 16:58 | Kabirpur -Kodda 132kV Ckt-1 is restored.
| 16:58 | Kabirpur -Kodda 132kV Ckt-2 is restored.
| 17:00 | Baghabari-Sirajganj 132 kV Ckt-1 is restored.
| 17:01 | Sirajganj 132/33kV S/S Sherpur-2 is restored.
| 17:01 | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-2 is restored.
| 17:03 | Kabirpur - Manikganj 132kV Ckt-1 is restored.
| 17:03 | Dohazari 132/33kV S/S Power Transformer -T-2 LT is restored.
| 17:03 | Dohazari 132/33kV S/S Power Transformer -T-2 HT is restored.
| 17:04 | Aminbazar 400/230/132kV S/S 230/132kv Tr-02 HT is restored.
| 17:05 | Aminbazar 400/230/132kV S/S 230/132kv Tr-02 LT is restored.
17:13 |  | Sirajgonj 6.55 MW Solar Shutdown
17:13 |  | Teesta Solar Limited Shutdown
17:14 |  | Sarishabari 3 MW Solar Plant Shutdown
17:14 |  | Teknaf 20MW PP (Solartech) Shutdown
17:15 |  | Sympa Solar Power 8 MW Shutdown
17:20 |  | Spectra Solar Plant Ltd. Shutdown
17:21 |  | Mongla Orion 100 MW Solar PP Shutdown
17:25 |  | Sutiakhali 50 MW Solar PP Shutdown
17:26 |  | Intraco Solar 30 MW Shutdown
18:00 |  | Evening peak generation 10847 MW.
18:01 |  | Summit Power Madhabdi Control Room Shutdown
18:07 |  | Natore 52 MW PP (Rajlanka) Syncronized
| 18:08 | Ghorasal- Ishwardi 230 kV Ckt-2 is restored.
18:13 |  | Summit Power Madhabdi Control Room Syncronized
19:24 |  | Kodda 300 MW PP Unit-2 (Summit) Shutdown
19:28 |  | Madanganj-55 MW PP(Summit) Shutdown
19:29 |  | Natore 52 MW PP (Rajlanka) Shutdown
19:30 |  | Meghnaghat 100 MW(IEL) Shutdown
19:31 |  | Siddhirganj 100 PP(Dutch Bangla) Shutdown
19:38 |  | Hathazari 100 MW peaking PP Shutdown
19:38 |  | Hathazari 100 MW peaking PP Syncronized
19:45 |  | Meghnaghat 104 MW PP (OPCL) Shutdown
19:47 |  | Kodda 150 MW PP B-R Shutdown
19:49 |  | Energypac Power Venture Thakurgaon Ltd. Shutdown
19:57 |  | United Payra Power Ltd. Shutdown
| 19:57 | Hasnabad 230/132kV S/S AUTO TR-1 HT is restored.
| 19:57 | Hasnabad 230/132kV S/S AUTO TR-1 LT is restored.
19:59 |  | Rupsha 105 MW PP (Orion rupsha) Shutdown
20:03 |  | Madanganj 102 PP(Summit) Shutdown
20:07 |  | Gazipur 52 MW PP Shutdown
20:08 |  | Confidence Power Bogura Unit-1 113 MW Shutdown
20:17 |  | Tangail Palli Power Gen 22 MW Shutdown
20:29 |  | Bagura 113 MW PP (Confidence)-2 Shutdown
20:39 |  | Nababganj 55 MW PP (Southern power ) Shutdown
20:39 |  | Sirajgonj 400 MW CCPP Unit-4 Syncronized with remarks:- ST
20:40 |  | Manikganj 55 MW PP (Northern) Shutdown
20:40 |  | Rangpur 113 MW PP (Confidence) Shutdown
20:42 |  | Ashuganj 150MW PP (Midland) Shutdown
20:44 |  | Manikgonj 162MW PP(MPGL) Shutdown
20:49 |  | Khulna 115 PP MW (KPCL-2) Shutdown
20:51 |  | Chowmuhani 113 MW Shutdown
20:52 |  | Raozan 25 MW PP Shutdown

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-11-28 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 74 | 1421818 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 354 | 8945670 | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 162 | 4650000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4682800 | GT-1 under S/D due to gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 12 | 48960 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | GT-1 under S/D due to gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 17 | 187729 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 20 | 58770 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 14 | 306900 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 16 | 54077 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 227 | 5960557 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 32 | 207072 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 124560 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 48 | 500160 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 133513 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 137956 | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 38 | 907320 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 667800
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 3 | 719600 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 13 | 144960 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 125 | 536945 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 51 | 413856 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 807360
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 55 | 114240 | Low demand
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 55 | 272160 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 186558
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 200520 | Fuel shortage
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5422 | 1963 | 36738861
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 83644 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 131220
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 20 | 160800 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 86 | 2076740 | Unit-2 under maint.
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 141 | 4128611 | Machine problem
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 204072 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 18 | 144000 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 13 | 120219 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 12 | 130560 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 161280 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 156816 | Fuel shortage
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 2 | 202000
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26043
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 120 | 875673 | Low demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 252678 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 285200 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 284782 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 0 | 0 | Fuel shortage
| SS Power I |  | SS Power | 2*612 | 1224 | 480 | 10979999
| Cox's Bazar Wind |  | IPP | 66 | 0 | 1 | 40800 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 273 | 7192727 | On test.
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 85309
| Chattogram area Total |  |  |  | 3769 | 1282 | 27723173
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 0 | Under maint.
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7512100 | Under maint.
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 390 | 7248000
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 43 | 1041120
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 0 | 42 | 1059840 | Engine problem
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 130 | 1856727
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1034616
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 41 | 281018 | Low demand
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 140 | 140544 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 433800 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 217440
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 126 | 2513280
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 688100
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 6 | 190000 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 48 | 331800 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 308160 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 36 | 319680 | Fuel shortage
| Cumilla Area Total |  |  |  | 2896 | 1441 | 25176225
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 47 | 1527360 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Contract Expired
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11750
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 104 | 1010400 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 75 | 525600 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 296630
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 40320 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 232 | 3412060
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1006000
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 673560 | Engine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 202176 | Gas shortage
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 3 | 145152 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under maint.
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1428480
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 193 | 3992320 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 415000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 229536 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 6942500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 402 | 8898000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 252360
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9183700
| Sylhet Area Total |  |  |  | 2427 | 1459 | 33368784
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 757 | 13501090
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 32 | 120000 | Low demand
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Reserve
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 63840 | Low demand
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Reserve
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 445680
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | Fuel shortage
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 460 | 10727270
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 1266 | 24857880
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 18 | 361900 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 130 | 2390000
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1080 | 24558400
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 110 | 3309491 | Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 55 | 123600 | Low demand
| Barisal 307 MW |  | IPP | 307*1 | 307 | 200 | 4080000 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1593 | 34823391
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 187 | 4749764 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 91 | 2217200 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 236592
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 10632 | Reserve
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Low demand
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Reserve
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 45 | 411168 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 90 | 386880 | Low demand
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 29220
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 873 | 20023636
| Rajshahi Area Total |  |  |  | 3631 | 1297 | 28065092
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4155600 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 98 | 396364 | Low demand
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 24817
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 46 | 286656 | Low demand
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 190361
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1003590
| Rangpur Area Total |  |  |  | 950 | 314 | 6057388
| Total |  |  |  | 25211 | 10847 | 220222854
| Eastern Grid Total |  |  |  | 15128 | 6377 | 126419103
| Western Grid Total |  |  |  | 10083 | 4470 | 93803751
| National Grid Total |  |  |  | 25211 | 10847 | 220222854
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-11-28
| (a) ENTIRE EASTERN GRID : |  | 7548.17 | MW | (b) ENTIRE WESTERN GRID : |  | 3196.8 | MW
| i) Dhaka area |  | 4342.97 | MW | i) Khulna area |  | 1181.8 | MW
| ii) Chittagong area |  | 1089.2 | MW | ii) Rajshahi area |  | 1002 | MW
| iii) Comilla area |  | 918 | MW | iii) Barisal area |  | 286 | MW
| iv) Mymensingh area |  | 813 | MW | iv) Rangpur area |  | 727 | MW
| v) Sylhet area |  | 385 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10744.97 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 18 | 14:00 | Kamrangirchar | 48 | 18:00 | Narinda | 32 | 13:00 | Sherpur | 100 | 18:00
2 | AKSML | 105 | 15:00 | Chowmuhani | 143 | 18:00 | Kaptai | N/A | N/A | Narshingdi | 144 | 18:30 | Shikalbaha | 32 | 11:00
3 | Aftabnagar | 30 | 18:00 | Chuadanga | 68 | 18:00 | Kazla | 81 | 15:00 | Natore | 112 | 18:00 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 81 | 13:00 | Coxsbazar | 97 | 18:30 | Keranigonj | 58 | 18:30 | Nawabganj | 33.8 | 21:00 | Shitalakhya | 92.4 | 12:00
5 | Agrabad | 56 | 15:00 | Cumilla(N) | 92 | 18:00 | Khagrachori | 24 | 18:00 | Netrakona | 90 | 18:00 | Sholosohor | 38 | 12:00
6 | Amnura | 32 | 18:00 | Cumilla(S) | 124 | 18:00 | Khulna | 76 | 18:00 | New | 62 | 12:00 | Shyampur | 140 | 02:00
7 | Ashuganj | 58 | 00:00 | Daudkandi | 120 | 18:00 | Khulshi | 142 | 14:00 | Niamatpur | 49 | 18:00 | Siddhirganj | 104 | 16:00
8 | BIPTC | N/A | N/A | Dhaka | 34 | 12:00 | Kishoreganj | 98 | 18:00 | Noapara | 33 | 18:30 | Sirajganj | 83 | 19:00
9 | BSRM | 141 | 17:00 | Dhamrai | 108 | 18:30 | Kodda | 263 | 18:30 | PHP | 10 | 19:00 | Sonargaon | 106 | 00:00
10 | Bagerhat | 64 | 18:00 | Dhanmondi | 103 | 13:00 | Kulaura | 32 | 18:00 | Pabna | 80 | 18:00 | Sreemongol | 46 | 18:00
11 | Bakulia | 89 | 17:00 | Dohazari | 58 | 18:00 | Kurigram | 52 | 18:00 | Palashbari | 82 | 18:00 | Sreepur | 61 | 18:00
12 | Banani | 0 | 00:00 | Faridpur | 111 | 18:00 | Kushtia | 102 | 18:00 | Panchagarh | 44 | 18:00 | Srinagar | 29.2 | 20:00
13 | Bangabhaban | 13 | 10:00 | Fatullah | 62 | 16:00 | Lalbag | 95 | 13:00 | Patuakhali | 59 | 21:00 | Sunamganj | 34 | 18:30
14 | Barapukuria | 47 | 18:00 | Fenchuganj | 25 | 18:30 | Lalmonirhat | 34 | 18:00 | Payra | 20 | 21:00 | Sylhet | 14 | 18:00
15 | Barguna | 12 | 18:30 | Feni | 86 | 18:00 | MI_Cement | 19.7 | 13:00 | Postogola | 47 | 13:00 | Sylhet-132 | 95 | 18:00
16 | Barishal | 86 | 12:00 | GPH | 76 | 12:00 | Madanganj | 34 | 11:00 | Purbachal | 17 | 18:00 | TK | 20.5 | 18:00
17 | Barishal-230 | 60 | 18:00 | Ghorashal | 63 | 18:00 | Madaripur | 64 | 20:00 | Purbasadipur | 101 | 18:00 | Tangail | 146 | 18:00
18 | Baroaulia | 72 | 09:00 | Goalpara | 28 | 13:00 | Madartek | 61.61 | 18:30 | Rahim | 54 | 12:00 | Thakurgaon | 71 | 18:00
19 | Baroirhat | 36 | 17:00 | Gollamari | 34 | 13:00 | Madunaghat | 38 | 18:00 | Rajbari | 48 | 18:00 | Tongi | 100 | 15:00
20 | Bashundhara | 140 | 13:00 | Gopalganj | 71.8 | 18:00 | Magura | 45 | 18:00 | Rajendrapur | 76 | 18:00 | Ullon | 44 | 18:00
21 | BashundharaCement | 5 | 11:00 | Gulshan | 98 | 13:00 | Mahasthangarh | 48 | 18:00 | Rajshahi | 98 | 13:00 | Uttara | 55 | 12:00
22 | Beanibazar | 40 | 18:00 | Halishahar | 98.5 | 12:00 | Manikganj | 84 | 18:00 | Rajshahi-230 | 22 | 13:00 | UttaraNew | 44 | 13:00
23 | Benapole | 40 | 18:00 | HaripurSBU | 136 | 17:00 | Maniknagar | 66 | 13:00 | Ramganj | 72 | 22:00 | Zigatola | 80 | 19:00
24 | Bhaluka | 118 | 18:30 | Hasnabad | 74 | 18:30 | Matarbari | 29 | 18:00 | Rampur | 28 | 19:30
25 | Bhandaria | 33 | 18:30 | Hathazari | 47 | 19:00 | Matuail | 66 | 12:00 | Rangamati | 13 | 18:00
26 | Bhangura | 22 | 18:00 | Ishurdi | 60 | 18:00 | Millgate | 92 | 15:00 | Rangpur | 117 | 18:00
27 | Bheramara(GK) | 38 | 18:00 | Jaldhaka | 55 | 18:00 | Mirpur | 110 | 18:00 | Ruppur | 5 | 15:00
28 | Bhulta | 227 | 12:00 | Jamalpur | 114 | 18:00 | Mirsorai | 4 | 11:00 | SSM | 13 | 00:00
29 | Bog-Sherpur | 52 | 18:00 | Jashore | 99 | 18:00 | Mirzapur | 15 | 18:00 | Saidpur | 86 | 18:00
30 | Bogura | 107 | 18:30 | Jhenaidah | 87 | 18:00 | Mithapukur | 38 | 18:00 | Satkhira | 81 | 18:00
31 | Borhanuddin | 36 | 21:00 | Joydebpur | 147 | 18:30 | Modern | 0 | 00:00 | Satmasjid | 76 | 13:00
32 | Brahmanbaria | 108 | 18:00 | Joypurhat | 42 | 18:30 | Mogbazar | 84.1 | 13:00 | Savar | 158 | 16:00
33 | Cantonment | 128 | 13:00 | Juldah | 22 | 22:00 | Mongla | 28 | 11:00 | SevenRings | 9.95 | 04:00
34 | Chandpur | 47 | 19:30 | KSRM | 30 | 09:00 | Motijheel | 33 | 18:00 | ShahCement | 19 | 00:00
35 | Chandraghona | 21 | 18:00 | Kabirpur | 274 | 15:00 | Munshiganj | 82 | 15:00 | Shahjadpur | 67 | 18:00
36 | Chapai | 46 | 13:00 | Kachua | 48 | 18:00 | Mymensingh | 157 | 18:00 | Shahjibazar | 87 | 21:00
37 | Charsaidpur | 22 | 11:00 | Kallyanpur | 74 | 18:00 | Naogaon | 90 | 18:00 | Shahmirpur | 43 | 01:00
38 | Chauddagram | 42 | 18:00 | Kalurghat | 35 | 12:00 | Narail | 39 | 18:00 | Shariatpur | 48 | 18:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-11-28 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 399 | 05:00 | 380 | 13:00 | Gopalganj | 408 | 05:00 | 392 | 12:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 391 | 05:00 | 376 | 14:00
| Bhulta | 411 | 01:00 | 394 | 12:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 408 | 18:00 | 397 | 11:00 | Payra | 415 | 03:00 | 407 | 13:00
| BIPTC | 407 | 00:00 | 395 | 18:00 | Rahanpur | 412 | 14:00 | 400 | 08:00
| Bogura | N/A | N/A | N/A | N/A | Rampal | 413 | 05:00 | 395 | 21:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 234 | 04:00 | 221 | 12:00 | Hasnabad | 233 | 07:00 | 221 | 12:00
| AKSML | 227 | 18:00 | 220 | 02:00 | Hathazari | 227 | 16:00 | 220 | 05:00
| Aminbazar | 235 | 02:00 | 225 | 11:00 | Ishurdi | 237 | 02:00 | 223 | 08:00
| Ashuganj | 233 | 18:30 | 226 | 12:00 | Jhenaidah | 236 | 02:00 | 222 | 08:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 235 | 04:00 | 223 | 14:00
| Baghabari | 229 | 01:00 | 222 | 09:00 | Keranigonj | 234 | 05:00 | 221 | 12:00
| Barapukuria | 227 | 14:00 | 216 | 08:00 | Khulna(S) | 241 | 02:00 | 229 | 12:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 244 | 04:00 | 237 | 19:30 | Maniknagar | 235 | 04:00 | 226 | 12:00
| Bheramara | 236 | 01:00 | 222 | 11:00 | Meghnaghat | 240 | 03:00 | 231 | 12:00
| Bhulta | 237 | 01:00 | 226 | 12:00 | Mirsorai | 229 | 14:00 | 220 | 23:00
| Bibiana | 233 | 18:00 | 226 | 11:00 | Rajshahi | 236 | 02:00 | 221 | 08:00
| BIPTC | 236 | 01:00 | 221 | 08:00 | Rampal | 239 | 01:00 | 227 | 21:00
| Bogura | 235 | 04:00 | 223 | 08:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 244 | 07:00 | 240 | 02:00 | Rampura | 234 | 05:00 | 223 | 12:00
| BSRM | 227 | 18:00 | 220 | 08:00 | Shikalbaha | 225 | 18:30 | 218 | 00:00
| Cumilla(N) | 231 | 05:00 | 224 | 11:00 | Shyampur | 236 | 06:00 | 224 | 12:00
| Fenchuganj | 235 | 18:00 | 231 | 00:00 | Siddhirganj | 234 | 00:00 | 227 | 12:00
| Ghorashal | 235 | 00:00 | 230 | 10:00 | Sirajgonj | 239 | 03:00 | 232 | 21:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 233 | 01:00 | 224 | 21:00
| GPH | 229 | 03:00 | 221 | 15:00 | Tongi | 230 | 04:00 | 220 | 11:00
| Haripur | 235 | 06:00 | 226 | 12:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 132 | 02:00 | 124 | 12:00 | Lalbag | 134 | 04:00 | 126 | 13:00
| Agargaon | 137 | 04:00 | 129 | 11:00 | Lalmonirhat | 132 | 15:00 | 121 | 07:00
| Agrabad | 132 | 17:00 | 128 | 11:00 | Madanganj | 133 | 18:00 | 125 | 11:00
| AKS | 131 | 17:00 | 126 | 23:00 | Madaripur | 133 | 17:00 | 130 | 00:00
| Aminbazar | 137 | 17:00 | 128 | 11:00 | Madartek | 132 | 04:00 | 125 | 11:00
| Amnura | 136 | 00:00 | 129 | 08:00 | Madunaghat | 133 | 13:00 | 129 | 11:00
| Ashuganj | 138 | 00:00 | 135 | 11:00 | Magura | 139 | 02:00 | 131 | 08:00
| Bagerhat | 133 | 01:00 | 125 | 07:00 | Mahasthangarh | 137 | 05:00 | 127 | 08:00
| Bakulia | 135 | 18:30 | 130 | 03:00 | Manikganj | 131 | 10:00 | 124 | 16:00
| Banani | 136 | 01:00 | 124 | 12:00 | Maniknagar | 135 | 04:00 | 128 | 11:00
| Bangabhaban | 135 | 04:00 | 128 | 12:00 | Matarbari | 130 | 14:00 | 125 | 00:00
| Barapukuria | 137 | 14:00 | 127 | 08:00 | Matuail | 133.8 | 04:00 | 127 | 12:00
| Barguna | 135 | 03:00 | 131 | 12:00 | Millgate | 136 | 01:00 | 125 | 15:00
| Barishal | 136 | 03:00 | 128 | 20:00 | Mirpur | 136 | 18:30 | 127 | 16:00
| Barishal-230 | 137 | 04:00 | 132 | 11:00 | Mirzapur | 133 | 04:00 | 126 | 17:00
| Baroaulia | 134 | 18:30 | 129 | 09:00 | Mithapukur | 136 | 18:30 | 123 | 07:00
| Baroirhat | 132 | 19:00 | 126 | 21:00 | MI_Cement | 133.6 | 06:00 | 126.5 | 12:00
| Bashundhara | 136 | 02:00 | 125 | 15:00 | Modern | 134 | 18:00 | 128 | 11:00
| BashundharaCement | 136 | 20:00 | 125 | 11:00 | Mogbazar | 133 | 02:00 | 125 | 12:00
| Beanibazar | 130 | 00:00 | 128 | 09:00 | Mongla | 130 | 00:00 | 124 | 12:00
| Benapole | 137 | 06:00 | 128 | 12:00 | Motijheel | 135 | 04:00 | 128 | 12:00
| Bhaluka | 133 | 02:00 | 126 | 12:00 | Munshiganj | 134 | 18:30 | 126 | 12:00
| Bhandaria | 134 | 07:00 | 130 | 12:00 | Mymensingh | 136 | 13:00 | 125 | 21:00
| Bhangura | 142 | 02:00 | 130 | 19:00 | Naogaon | 135 | 18:30 | 122 | 12:00
| Bheramara | 137 | 01:00 | 129 | 11:00 | Narail | 138 | 01:00 | 130 | 11:00
| Bheramara(GK) | 137 | 02:00 | 130 | 09:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 125 | 17:00 | 120 | 11:00 | Narshingdi | 129 | 06:00 | 121 | 12:00
| Bog-Sherpur | 138 | 02:00 | 129 | 08:00 | Natore | 137 | 01:00 | 129 | 08:00
| Bogura | 138 | 18:30 | 130 | 08:00 | Nawabganj | 134 | 06:00 | 126 | 12:00
| Bogura-230 | 138 | 04:00 | 129 | 08:00 | Netrakona | 134 | 13:00 | 127 | 06:00
| Brahmanbaria | 130 | 17:00 | 127 | 00:00 | New | 136 | 04:00 | 125 | 14:00
| Cantonment | 137 | 04:00 | 128 | 12:00 | Niamatpur | 134 | 03:00 | 119 | 12:00
| Chandpur | 140 | 18:00 | 124 | 23:00 | Noapara | 136 | 04:00 | 128 | 12:00
| Chandraghona | 133 | 05:00 | 130 | 22:00 | Pabna | 139 | 02:00 | 131 | 08:00
| Chapai | 134 | 06:00 | 131 | 00:00 | Palashbari | 133 | 14:00 | 125 | 08:00
| Charsaidpur | 134 | 04:00 | 127 | 11:00 | Panchagarh | 133 | 18:30 | 115 | 08:00
| Chauddagram | 133 | 18:30 | 125 | 23:00 | Patuakhali | 135 | 17:00 | 131 | 12:00
| Chhatak | 131 | 03:00 | 128 | 17:00 | Payra | 135 | 01:00 | 133 | 00:00
| Chowmuhani | 132 | 17:00 | 121 | 00:00 | PHP | 133 | 18:30 | 125 | 23:00
| Chuadanga | 137 | 01:00 | 128 | 11:00 | Postogola | 136 | 05:00 | 128 | 11:00
| Coxsbazar | 126 | 08:00 | 119 | 18:30 | Purbachal | 136 | 01:00 | 124 | 15:00
| Cumilla(N) | 135 | 18:00 | 130 | 23:00 | Purbasadipur | 132 | 15:00 | 116 | 08:00
| Cumilla(S) | 137 | 18:30 | 128 | 12:00 | Rahanpur | 136 | 14:00 | 132 | 00:00
| Daudkandi | 132 | 18:00 | 124 | 11:00 | Rahim | 134 | 05:00 | 127 | 12:00
| Dhaka | 133 | 03:00 | 125 | 12:00 | Rajbari | 134 | 01:00 | 127 | 21:00
| Dhamrai | 132 | 02:00 | 123 | 15:00 | Rajendrapur | 134 | 08:00 | 122 | 21:00
| Dhanmondi | 134 | 04:00 | 127 | 11:00 | Rajshahi | 137 | 04:00 | 129 | 08:00
| Dohazari | 132 | 05:00 | 128 | 14:00 | Rajshahi-230 | 138 | 02:00 | 128 | 08:00
| Faridpur | 133 | 04:00 | 128 | 11:00 | Ramganj | 135 | 18:30 | 122 | 23:00
| Fatullah | 135 | 06:00 | 127 | 12:00 | Rampur | 133 | 18:00 | 128 | 12:00
| Fenchuganj | 134 | 06:00 | 131 | 14:00 | Rampura | 133 | 01:00 | 125 | 12:00
| Feni | 132 | 00:00 | 125 | 23:00 | Rangamati | 134 | 18:30 | 129 | 11:00
| Ghorashal | 138 | 00:00 | 134 | 12:00 | Rangpur | 134 | 18:30 | 121 | 07:00
| Goalpara | 137 | 02:00 | 128 | 07:00 | Ruppur | 138 | 00:00 | 131 | 12:00
| Gollamari | 135 | 01:00 | 128 | 12:00 | Saidpur | 132 | 03:00 | 120 | 08:00
| Gopalganj | 134 | 02:00 | 127 | 21:00 | Satkhira | 134 | 04:00 | 125 | 21:00
| Gopalganj-400 | 134 | 05:00 | 129 | 11:00 | Satmasjid | 137 | 05:00 | 128 | 12:00
| Gulshan | 133 | 03:00 | 126 | 12:00 | Savar | 136 | 18:00 | 123 | 11:00
| Halishahar | 133 | 18:30 | 128 | 11:00 | SevenRings | 140 | 02:00 | 134 | 12:00
| Haripur | 134 | 04:00 | 127 | 12:00 | ShahCement | 134 | 04:00 | 127 | 11:00
| HaripurSBU | 134 | 05:00 | 127 | 12:00 | Shahjadpur | 143 | 05:00 | 136 | 07:00
| Hasnabad | 135 | 01:00 | 128 | 11:00 | Shahjibazar | 131 | 11:00 | 127 | 00:00
| Hathazari | 135 | 13:00 | 130 | 03:00 | Shahmirpur | 133 | 17:00 | 129 | 22:00
| Ishurdi | 140 | 01:00 | 131 | 08:00 | Shariatpur | 135 | 05:00 | 129 | 12:00
| Jaldhaka | 133 | 16:00 | 119 | 09:00 | Sherpur | 137 | 18:30 | 120 | 23:00
| Jamalpur | 138 | 18:30 | 124 | 05:00 | Shikalbaha | 123 | 05:00 | 119 | 00:00
| Jashore | 137 | 01:00 | 128 | 12:00 | Shikalbaha-230 | 134 | 14:00 | 131 | 00:00
| Jhenaidah | 139 | 01:00 | 131 | 10:00 | Shitalakhya | 133.6 | 06:00 | 126.5 | 12:00
| Jhenaidah-230 | 140 | 02:00 | 130 | 12:00 | Sholosohor | 133 | 18:30 | 129 | 08:00
| Joydebpur | 137 | 06:00 | 129 | 12:00 | Shyampur | 135 | 05:00 | 127 | 11:00
| Joypurhat | 135 | 04:00 | 121 | 12:00 | Shyampur-230 | 135 | 05:00 | 128 | 12:00
| Juldah | 133 | 13:00 | 130 | 00:00 | Siddhirganj | 134 | 18:30 | 127 | 12:00
| Kabirpur | 133 | 09:00 | 122 | 15:00 | Sirajganj | 138 | 00:00 | 129 | 11:00
| Kachua | 138 | 18:00 | 124 | 22:00 | Sonargaon | 134 | 18:30 | 125 | 11:00
| Kaliakoir | 135 | 18:00 | 128 | 15:00 | Sreemongol | 131 | 17:00 | 128 | 13:00
| Kallyanpur | 135 | 01:00 | 126 | 12:00 | Sreepur | 133 | 01:00 | 128 | 21:00
| Kalurghat | 133 | 18:00 | 128 | 00:00 | Srinagar | 136 | 04:00 | 126 | 13:00
| Kamrangirchar | 135 | 01:00 | 130 | 04:00 | SSM | 140 | 18:30 | 130 | 00:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 129 | 00:00 | 127 | 12:00
| Kazla | 135 | 05:00 | 128 | 11:00 | Sylhet | 131 | 00:00 | 129 | 10:00
| Keranigonj | 135 | 05:00 | 126 | 12:00 | Sylhet-132 | 131 | 01:00 | 129 | 11:00
| Khagrachori | 133 | 06:00 | 129 | 09:00 | Tangail | 132 | 09:00 | 126 | 21:00
| Khulna | 135 | 04:00 | 127 | 12:00 | Thakurgaon | 134 | 18:30 | 115 | 08:00
| Khulna(S) | 135 | 01:00 | 128 | 12:00 | TK | 134 | 19:00 | 130 | 08:00
| Khulshi | 132 | 18:30 | 127 | 09:00 | Tongi | 136 | 04:00 | 127 | 11:00
| Kishoreganj | 135 | 04:00 | 130 | 11:00 | Ullon | 131 | 01:00 | 125 | 11:00
| Kodda | 136 | 18:00 | 122 | 21:00 | Uttara | 135 | 02:00 | 130 | 22:00
| KSRM | 133 | 13:00 | 128 | 23:00 | UttaraNew | 135 | 04:00 | 124 | 12:00
| Kulaura | 132 | 00:00 | 129 | 15:00 | Zigatola | 134 | 04:00 | 125 | 13:00
| Kurigram | 132 | 18:30 | 124 | 21:00
| Kushtia | 137 | 04:00 | 130 | 11:00

## L-Curve
Date | 2023-11-28
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 980 | 4864 | 4056 | 8920 |  |  |  | QF-LDC-11
0:30 | 675 | 4872 | 3801.5 | 8673.5 | Date: | 2023-11-28
1:00 | 370 | 4880 | 3547 | 8427
1:30 | 380 | 4709.5 | 3514 | 8223.5
2:00 | 390 | 4539 | 3481 | 8020
2:30 | 385 | 4499.5 | 3359.5 | 7859 | [5 empty] | Gen. at Eve. Peak | 10847 | 10847 MW (18:00 )
3:00 | 380 | 4460 | 3238 | 7698 | [6 empty] | 18:00
3:30 | 360 | 4442 | 3192 | 7634 | [5 empty] | Gen. at Day Peak | 9651 | 9651 MW (12:00 )
4:00 | 340 | 4424 | 3146 | 7570 | [6 empty] | 12:00
4:30 | 343 | 4408 | 3131 | 7539 | [5 empty] | Highest Generation | 10847
5:00 | 346 | 4392 | 3116 | 7508 | [6 empty] | 18:00
5:30 | 318 | 4478 | 3122 | 7600
6:00 | 290 | 4564 | 3128 | 7692
6:30 | 250 | 4757.5 | 3201.5 | 7959
7:00 | 210 | 4951 | 3275 | 8226
7:30 | 202 | 5051.5 | 3382 | 8433.5
8:00 | 194 | 5152 | 3489 | 8641
8:30 | 282 | 5105.5 | 3501.5 | 8607
9:00 | 370 | 5059 | 3514 | 8573
9:30 | 365 | 5173.5 | 3495 | 8668.5
10:00 | 360 | 5288 | 3476 | 8764
10:30 | 390 | 5399 | 3536 | 8935
11:00 | 420 | 5510 | 3596 | 9106
11:30 | 380 | 5680 | 3698.5 | 9378.5
12:00 | 340 | 5850 | 3801 | 9651
12:30 | 375 | 5887.5 | 3927.5 | 9815
13:00 | 410 | 5925 | 4054 | 9979
13:30 | 460 | 5833 | 3963.5 | 9796.5
14:00 | 510 | 5741 | 3873 | 9614
14:30 | 500 | 5724.5 | 3802.5 | 9527
15:00 | 490 | 5708 | 3732 | 9440
15:30 | 470 | 5687.5 | 3682 | 9369.5
16:00 | 450 | 5667 | 3632 | 9299
16:30 | 435 | 5761.5 | 3771.5 | 9533
17:00 | 420 | 5856 | 3911 | 9767
17:30 | 340 | 6116.5 | 4190.5 | 10307
18:00 | 260 | 6377 | 4470 | 10847
18:30 | 280 | 6312 | 4469 | 10781
19:00 | 300 | 6247 | 4468 | 10715
19:30 | 390 | 6003 | 4583 | 10586
20:00 | 440 | 5772 | 4526 | 10298 |  |  |  | Executive Engineer
20:30 | 575 | 5615.5 | 4538 | 10153.5 |  |  |  | Network Operation Division
21:00 | 710 | 5459 | 4550 | 10009
21:30 | 775 | 5315 | 4515 | 9830
22:00 | 840 | 5171 | 4480 | 9651 |  |  |  |  | Page 6 of 7
22:30 | 895 | 5084 | 4380 | 9464
23:00 | 950 | 4997 | 4280 | 9277
23:30 | 965 | 4930.5 | 4168 | 9098.5
24:00 | 980 | 4864 | 4056 | 8920
10847 MW (18:00 )
9651 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-11-28 |  | Energy |  | 220222854
[15 empty] | 43796 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3182 | 910 | 1615 | 0 | 59 | 2947 | 86 | 0 | 17 | 104 | 0 | 0 | 0
0:30 | 3108.5 | 675 | 1524 | 0 | 55 | 3114.5 | 86 | 0 | 8.5 | 102 | 0 | 0 | 0 |  |  | Date: | 43796
1:00 | 3035 | 440 | 1433 | 0 | 51 | 3282 | 86 | 0 | 0 | 100 | 0 | 0 | 0
1:30 | 3036 | 440 | 1282.5 | 0 | 25.5 | 3254 | 86 | 0 | 0 | 99 | 0 | 0.5 | 0 | [9 empty] | Total Energy | 220.2229 | 220.2229 | Total Energy Gen 220.223 MKWHr Energy Not Served 0.354 MKWHr Energy Requirement 220.577 MKWHr
2:00 | 3037 | 440 | 1132 | 0 | 0 | 3226 | 86 | 0 | 0 | 98 | 0 | 1 | 0 | [9 empty] | Energy not Served | 0.35435 | 0.35435
2:30 | 3094 | 440 | 1013.5 | 0 | 0 | 3127.5 | 86 | 0 | 0 | 97 | 0 | 1 | 0 | [9 empty] | Energy Requirement | 220.5772 | 220.5772
3:00 | 3151 | 440 | 895 | 0 | 0 | 3029 | 86 | 0 | 0 | 96 | 0 | 1 | 0
3:30 | 3156 | 439.5 | 903.5 | 0 | 0 | 2954.5 | 86 | 0 | 0 | 94 | 0 | 0.5 | 0 | [8 empty] | Shortage
4:00 | 3161 | 439 | 912 | 0 | 0 | 2880 | 86 | 0 | 0 | 92 | 0 | 0 | 0
4:30 | 3166 | 439.5 | 914.5 | 0 | 0 | 2842 | 86 | 0 | 0 | 91 | 0 | 0 | 0
5:00 | 3171 | 440 | 917 | 0 | 0 | 2804 | 86 | 0 | 0 | 90 | 0 | 0 | 0
5:30 | 3208.5 | 440 | 948.5 | 0 | 0 | 2826 | 86 | 0 | 0 | 90 | 0 | 1 | 0
6:00 | 3246 | 440 | 980 | 0 | 0 | 2848 | 86 | 0 | 0 | 90 | 0 | 2 | 0
6:30 | 3272.5 | 440 | 1089 | 0 | 17 | 2944.5 | 86 | 0 | 8 | 89 | 8.5 | 4.5 | 15 | [7 empty] | Coal
7:00 | 3299 | 440 | 1198 | 0 | 34 | 3041 | 86 | 0 | 16 | 88 | 17 | 7 | 30
7:30 | 3351.5 | 440 | 1187.5 | 0 | 54.5 | 3127.5 | 86 | 0 | 16 | 90 | 74.5 | 6 | 67 | [6 empty] | Oil
8:00 | 3404 | 440 | 1177 | 0 | 75 | 3214 | 86 | 0 | 16 | 92 | 132 | 5 | 104
8:30 | 3378.5 | 439.5 | 1142.5 | 0 | 117 | 3153.5 | 86 | 0 | 16 | 95 | 176 | 3 | 103
9:00 | 3353 | 439 | 1108 | 0 | 159 | 3093 | 86 | 0 | 16 | 98 | 220 | 1 | 102
9:30 | 3272.5 | 439.5 | 1161.5 | 0 | 191 | 3156.5 | 86 | 0 | 24 | 96 | 241 | 0.5 | 87.5
10:00 | 3192 | 440 | 1215 | 0 | 223 | 3220 | 86 | 0 | 32 | 94 | 262 | 0 | 73
10:30 | 3167.5 | 440 | 1207 | 0 | 252 | 3330.5 | 86 | 0 | 41.5 | 98 | 311.5 | 1 | 36.5
11:00 | 3143 | 440 | 1199 | 0 | 281 | 3441 | 86 | 0 | 51 | 102 | 361 | 2 | 0
11:30 | 3194 | 440 | 1221.5 | 0 | 369 | 3534 | 86 | 0 | 52 | 108 | 371 | 3 | 0
12:00 | 3245 | 440 | 1244 | 0 | 457 | 3627 | 86 | 0 | 53 | 114 | 381 | 4 | 0
12:30 | 3221.5 | 440 | 1266 | 0 | 618 | 3610.5 | 86 | 0 | 81.5 | 112 | 375.5 | 4 | 0
13:00 | 3198 | 440 | 1288 | 0 | 779 | 3594 | 86 | 0 | 110 | 110 | 370 | 4 | 0
13:30 | 3198 | 440 | 1288 | 0 | 779 | 3594 | 86 | 0 | 110 | 110 | 370 | 4 | 0
14:00 | 3198 | 440 | 1288 | 0 | 779 | 3594 | 86 | 0 | 110 | 110 | 370 | 4 | 0
14:30 | 3117.5 | 438 | 1300 | 0 | 822.5 | 3460 | 86 | 0 | 87.5 | 112 | 284 | 2 | 10.0275
15:00 | 3037 | 436 | 1312 | 0 | 866 | 3326 | 86 | 0 | 65 | 114 | 198 | 0 | 20.055
15:30 | 3044 | 436.5 | 1296.5 | 0 | 874.5 | 3313.5 | 86 | 0 | 65.5 | 114 | 138.5 | 0.5 | 20.055
16:00 | 3051 | 437 | 1281 | 0 | 883 | 3301 | 86 | 0 | 66 | 114 | 79 | 1 | 20.055
16:30 | 3066 | 568.5 | 1284 | 0 | 1037.5 | 3270.5 | 86 | 0 | 63 | 115 | 41 | 1.5 | 20.0275
17:00 | 3081 | 700 | 1287 | 0 | 1192 | 3240 | 86 | 0 | 60 | 116 | 3 | 2 | 20
17:30 | 3176 | 728.5 | 1277.5 | 0 | 1457.5 | 3388 | 86 | 0 | 69.5 | 121 | 1.5 | 1.5 | 10
18:00 | 3271 | 757 | 1268 | 0 | 1723 | 3536 | 86 | 0 | 79 | 126 | 0 | 1 | 0
18:30 | 3296 | 691.5 | 1269.5 | 0 | 1608.5 | 3639 | 86 | 0 | 67 | 123 | 0 | 0.5 | 0
19:00 | 3321 | 626 | 1271 | 0 | 1494 | 3742 | 86 | 0 | 55 | 120 | 0 | 0 | 0
19:30 | 3330 | 767 | 1277 | 0 | 1172 | 3781 | 86 | 0 | 55 | 118 | 0 | 0 | 0
20:00 | 3370 | 767 | 1307 | 0 | 876 | 3776 | 86 | 0 | 4 | 112 | 0 | 0 | 0
20:30 | 3375 | 837.5 | 1290.5 | 0 | 673.5 | 3768.5 | 86 | 0 | 10.5 | 112 | 0 | 0 | 0
21:00 | 3380 | 908 | 1274 | 0 | 471 | 3761 | 86 | 0 | 17 | 112 | 0 | 0 | 0
21:30 | 3310 | 908.5 | 1393.5 | 0 | 367.5 | 3635.5 | 86 | 0 | 17 | 112 | 0 | 0 | 0
22:00 | 3240 | 909 | 1513 | 0 | 264 | 3510 | 86 | 0 | 17 | 112 | 0 | 0 | 0
22:30 | 3220 | 909 | 1566.5 | 0 | 193.5 | 3362 | 86 | 0 | 17 | 110 | 0 | 0 | 0
23:00 | 3200 | 909 | 1620 | 0 | 123 | 3214 | 86 | 0 | 17 | 108 | 0 | 0 | 0
23:30 | 3191 | 909.5 | 1617.5 | 0 | 91 | 3080.5 | 86 | 0 | 17 | 106 | 0 | 0 | 0 |  |  | Max Temp. in Dhaka |  | 32.5°C
24:00 | 3182 | 910 | 1615 | 0 | 59 | 2947 | 86 | 0 | 17 | 104 | 0 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 220.223 MKWHr Energy Not Served 0.354 MKWHr Energy Requirement 220.577 MKWHr
Note on W13: Author:

## Generation
g | 2023-11-28
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1108740
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 968000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [11 empty] | 1 | 8 | 8 | 8 | 8 | 8 | 17 |  | 8 | 8 | 8 | 0 |  |  | 0 | 83644
| Teknaf 20MW PP (Solartech) | [6 empty] | 3 | 10 | 14 | 18 | 20 | 18 | 18 | 15 | 11 | 6 | 0 | [9 empty] | 131220
6 | Sikalbaha 225MW CCPP (Gas) | 213 | 213 | 214 | 214 | 214 | 214 | 215 | 213 | 215 | 215 | 214 | 142 | 140 | 141 | 141 | 142 | 141 | 141 |  | 140 | 141 | 141 | 141 | 141 | 141 | 141 | 4128611
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [10 empty] | 3 | 3 | 6 | 6 | 9 | 10 | 4 | 13 |  | 14 | 14 | 4 | 17 | 17 | 17 | 17 | 120219
12 | Hathazari 100 MW peaking PP | [11 empty] | 2 | 56 | 48 | 8 | 8 | 8 | 18 |  | 25 | 25 | [5 empty] | 144000
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 0 | [9 empty] | 5 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 204072
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 252 | 258 | 265 | 267 | 270 | 276 | 278 | 270 | 275 | 270 | 270 | 240 | 226 | 225 | 230 | 225 | 227 | 227 |  | 227 | 227 | 227 | 228 | 228 | 232 | 236 | 5960557
18 | Kodda 300 MW PP Unit-2 (Summit) | [13 empty] | 43 | 65 | 95 | 100 | 125 |  | 30 | 0 |  |  |  |  | 0 | 536945
19 | Ashuganj 195 MW PP (APSCL-United) | 102 | 102 | 8 | 8 | 8 | 8 | 50 | 55 | 55 | 102 | 102 | 102 | 158 | 102 | 102 | 102 | 102 | 130 |  | 130 | 130 | 130 | 45 | 45 | 45 | 45 | 1856727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 467 | 460 | 433 | 400 | 365 | 401 | 453 | 495 | 450 | 450 | 450 | 500 | 500 | 460 | 450 | 450 | 452 | 480 |  | 480 | 480 | 480 | 480 | 480 | 478 | 452 | 10979999
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 47 | 45 | 45 | 45 | 45 | 42 | 45 | 45 | 44 | 44 | 37 | 44 | 44 | 43 | 43 | 43 | 43 | 43 |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 1041120
33 | Ashuganj 225 MW CCPP
34 | Ashuganj 450 MW CCPP(South) | [25 empty] | 0 | 0
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 310 | 280 | 280 | 280 | 280 | 290 | 305 | 310 | 285 | 310 | 310 | 280 | 290 | 280 | 280 | 310 |  | 310 | 310 | 310 | 315 | 310 | 280 | 280 | 7512100
| Ashuganj 420 MW CCPP(East) | 230 | 230 | 230 | 230 | 230 | 230 | 250 | 330 | 320 | 230 | 225 | 225 | 225 | 255 | 330 | 350 | 360 | 390 |  | 393 | 395 | 393 | 393 | 350 | 350 | 350 | 7248000
35 | Ashuganj 55 MW PP (Precision) | 46 | 46 | 46 | 46 | 46 | 46 | 45 | 46 | 46 | 46 | 45 | 44 | 44 | 42 | 42 | 41 | 41 | 42 |  | 43 | 43 | 44 | 44 | 44 | 43 | 45 | 1059840
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 362 | 362 | 363 | 363 | 363 | 363 | 371 | 400 | 389 | 384 | 361 | 394 | 396 | 385 | 373 | 363 | 358 | 354 |  | 353 | 355 | 356 | 360 | 364 | 362 | 343 | 8945670
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 170 | 170 | 170 | 170 | 170 | 225 | 225 | 175 | 200 | 170 | 225 | 225 | 190 | 190 | 190 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4682800
41 | Haripur 360 MW CCPP(HPL) | 203 | 202 | 201 | 201 | 211 | 211 | 232 | 211 | 222 | 220 | 222 | 213 | 186 | 187 | 186 | 176 | 167 | 162 |  | 161 | 161 | 161 | 162 | 161 | 171 | 181 | 4650000
42 | RPCL 210MW CCPP | 85 | 85 | 89 | 103 | 100 | 100 | 74 | 71 | 35 | 35 | 34 | 34 | 34 | 34 | 33 | 32 | 46 | 47 |  | 47 | 54 | 77 | 95 | 95 | 95 | 94 | 1527360
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 3 | 20 | 40 | 43 | 45 | 47 | 44 | 36 | 25 | 9 | 0 | [9 empty] | 296630
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 41 | 40 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1006000
45 | Fenchugonj CCPP Phase-2 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 26 | 28 | 28 | 22 | 22 | 22 | 22 | 22 | 22 | 26 | 30 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 673560
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86 MW PP (Shahjibazar) | 40 | 5 | 5 | 5 | 5 | 25 | 40 | 40 | 55 | 83 | 83 | 82 | 81 | 82 | 82 | 82 | 83 | 83 |  | 84 | 84 | 84 | 84 | 84 | 84 | 40 | 1428480
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 199 | 199 | 199 | 199 | 199 | 199 | 198 | 199 | 200 | 200 | 199 | 199 | 199 | 196 | 197 | 197 | 197 | 193 |  | 195 | 195 | 195 | 195 | 197 | 199 | 199 | 3992320
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 415000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 252360
54 | Hobiganj 11 MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 3 | 3 | 3 | 3 |  | 3 | 7 | 7 | 7 | 7 | 7 | 7 | 145152
55 | Fenchugonj 51 MW PP (Barakatullah) | [25 empty] | 0 | 0
56 | Shahjahanulla 25 MW PP | 16 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 16 | 8 | 8 | 8 | 8 | 229536
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 270 | 295 | 290 | 275 | 290 | 305 | 280 | 285 | 290 | 285 | 285 | 300 | 270 | 290 | 285 | 290 | 270 |  | 270 | 275 | 280 | 290 | 260 | 270 | 280 | 6942500
| Bibiyana South 400 MW | 370 | 370 | 370 | 370 | 370 | 370 | 400 | 400 | 370 | 370 | 370 | 398 | 398 | 370 | 370 | 380 | 380 | 400 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 9183700
58 | Nababganj 55 MW PP (Southern power ) | [15 empty] | 17 | 35 | 35 |  | 35 | 35 | 17 |  |  |  | 0 | 137956
59 | Tangail Palli Power Gen 22 MW | [15 empty] | 4 | 6 | 6 |  | 6 | 6 | 6 |  |  |  | 0 | 40320
60 | Barabkunda 22 MW PP (Regent) | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 10 | 10 | 12 | [8 empty] | 0 | 0 | 0 |  | 10 | 10 | 156816
61 | Narshingdi 22 MW PP (Doreen) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 15 | 15 | 15 | 15 | 15 | 306900
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 100 | 98 | 96 | 92 | 90 | 90 | 88 | 92 | 98 | 94 | 102 | 114 | 110 | 120 | 114 | 114 | 116 | 126 |  | 120 | 118 | 112 | 112 | 112 | 108 | 104 | 2513280
64 | Malancha, Ctg. EPZ (United) | 17 | 23 | 0 | 22 | 32 | 32 | 28 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 2 | 2 | 2 | 2 | 6 | 9 | 10 | 202000
65 | Feni 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 433800
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 217440
67 | Jangalia 33 MW PP (Summit) | 33 | 8 | 8 | 8 | 8 | 19 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 688100
68 | Cumilla 25 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 6 |  | 6 | 6 | 6 | 6 | 6 | 8 | 8 | 190000
69 | Summit Ashulia | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 480000
70 | Summit Madhabdi | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 19 | 18 |  | 19 | 19 | 20 | 20 | 20 | 20 | 20 | 427320
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 33 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 667800
72 | Rupganj 33 MW PP(Summit) | 31 | 31 | 31 | 31 | 31 | 33 | 33 | 33 | 32 | 32 | 32 | 31 | 31 | 31 | 31 | 31 | 31 | 3 |  | 31 | 31 | 31 | 30 | 16 | 30 | 30 | 719600
73 | Ghorashal 108 MW PP (Regent) | 77 | 12 | 12 | 12 | 12 | 12 | 40 | 72 | 74 | 74 | 76 | 76 | 76 | 73 | 73 | 73 | 73 | 74 |  | 75 | 75 | 75 | 75 | 75 | 74 | 75 | 1421818
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | [9 empty] | 10 | 18 | 34 | 38 | 38 | 9 | 9 | 27 | 48 |  | 49 | 26 | 9 |  |  |  |  | 331800
| Manikgonj 162MW PP(MPGL) | [11 empty] | 17 | 17 | 17 | 17 | 17 | 55 | 55 |  | 55 | 17 | 17 |  |  |  | 0 | 272160
77 | Siddhirganj 100 PP(Dutch Bangla) | [15 empty] | 1 | 9 | 16 |  | 34 | 8 |  |  |  |  | 0 | 54077
78 | Gazipur 52 MW PP | [6 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 13 |  | 25 | 8 | 8 |  |  |  | 0 | 144960
79 | Kodda 150 MW PP | [6 empty] | 16 | 16 | 16 | 32 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 |  | 16 | 16 |  |  |  |  | 0 | 500160
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [26 empty] | 0
| Gazipur 100 MW PP | [6 empty] | 17 | 17 | 35 | 35 | 52 | 52 | 52 | 52 | 52 | 52 | 105 | 105 |  | 52 | 52 | 52 | 35 | 35 |  | 0 | 807360
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 26043
| Jodiac Power | [10 empty] | 8 | 10 | 17 | 17 | 17 | 17 | 36 | 36 |  | 17 | 17 | 17 | 17 |  |  | 0 | 252678
| Karnaphuli Power Ltd. | 17 | 0 | [7 empty] | 14 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 285200
82 | Madanganj 102 PP(Summit) | [10 empty] | 2 | 17 | 34 | 34 | 34 | 25 | 17 | 17 |  | 34 | 17 | 15 |  |  |  | 0 | 187729
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | [16 empty] | 5 | 12 |  | 29 | 0 |  |  |  |  | 0 | 48960
| Meghnaghat 104 MW PP (OPCL) | [15 empty] | 7 | 17 | 55 |  | 30 | 17 |  |  |  |  | 0 | 114240
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [9 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 |  |  | 0 | 130560
92 | Fenchuganj 44 MW (Energyprima) | 47 | 5 | 5 | 5 | 5 | 30 | 47 | 47 | 0 | [16 empty] | 0 | 202176
93 | Ashuganj 51 MW PP (Midland) | 51 | 5 | 5 | 5 | 5 | 8 | 38 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1034616
94 | Gagnagar 102 MW PP (Digital Power) | 0 | [10 empty] | 8 | 8 | 16 | 16 | 16 | 16 | 32 |  | 32 | 32 | 16 | 8 | 8 | 8 | 8 | 207072
95 | Patenga 50MW PP (Baraka) | [9 empty] | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 19 | 20 |  | 20 | 20 | 20 | 20 | 20 |  | 0 | 160800
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [16 empty] | 1 | 20 |  | 15 | 0 |  |  |  |  | 0 | 58770
100 | Manikganj 55 MW PP (Northern) | [15 empty] | 17 | 35 | 35 |  | 35 | 35 | 17 |  |  |  | 0 | 133513
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [9 empty] | 11750
103 | Kamalaghat 54 MW PP(Banco Energy) | [16 empty] | 17 | 17 |  | 35 | 35 | 35 | 17 |  |  | 0 | 124560
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 0 | [5 empty] | 5 | 16 | 56 | 32 | 32 | 56 | 56 | 58 | 58 | 58 | 58 | 104 |  | 107 | 108 | 108 | 85 | 45 | 30 |  | 1010400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [6 empty] | 1 | 8 | 17 | 17 | 20 | 24 | 24 | 39 | 31 | 27 | 26 | 51 |  | 60 | 17 | 23 | 20 |  |  | 0 | 413856
115 | Juldah 100 MW PP Unit-3 (Acorn) | [9 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 |  | 0 | 161280
116 | Chandpur 200 MW (Desh energy) | 17 | 0 | [6 empty] | 3 | 17 | 25 | 67 | 100 | 110 | 120 | 85 | 95 | 140 |  | 155 | 155 | 155 | 85 | 68 | 34 | 17 | 140544
117 | Ashuganj 150 MW PP (Midland) | [13 empty] | 6 | 20 | 20 | 20 | 41 |  | 70 | 70 | 20 |  |  |  |  | 281018
118 | Bibiyana-III 400 MW CCPP | 341 | 341 | 340 | 340 | 340 | 397 | 400 | 401 | 365 | 353 | 353 | 397 | 403 | 354 | 354 | 356 | 354 | 402 |  | 402 | 402 | 402 | 401 | 401 | 353 | 352 | 8898000
| Jamalpur 115 MW PP (United) | 0 | [5 empty] | 3 | 16 | 16 | 8 | 8 | 10 | 56 | 56 | 56 | 56 | 56 | 75 |  | 24 | 24 | 8 | 8 | 8 |  | 0 | 525600
| Anwara 300 MW PP (United) | [11 empty] | 20 | 100 | 100 | 65 | 65 | 70 | 120 |  | 100 | 100 | 50 | 50 |  |  | 0 | 875673
| Juldah unit-2 (Acorn) | [25 empty] | 0 | 0
| Anlima Energy Ltd. | 17 | 0 | [6 empty] | 5 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 284782
| Bhairob 54.5 MW | 0 | [6 empty] | 10 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 308160
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 10 | 18 | 25 | 29 | 29 | 28 | 23 | 16 | 7 | 0 | [9 empty] | 186558
| Chandpur 115(Doreen) | 0 | [7 empty] | 2 | 18 | 18 | 18 | 17 | 18 | 17 | 18 | 26 | 36 |  | 48 | 35 | 30 | 17 |  |  | 0 | 319680
| Kanchan Purbachal Power Generation Ltd. | [10 empty] | 4 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 |  |  | 0 | 200520
Mirsharai 150 MW (Oil)
| Mirsharai 150 MW (Gas) | [10 empty] | 14 | 31 | 17 | 17 | [6 empty] | 0 |  |  |  |  | 0 | 85309
| Cox's Bazar Wind | 0 | 1 | 1 | 0 | 0 | 2 | 7 | 5 | 1 | 0 | 2 | 4 | 4 | 2 | 0 | 1 | 2 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40800
| Matarbari 2*600 MW (CPGCL) | 217 | 213 | 214 | 213 | 213 | 211 | 215 | 213 | 213 | 356 | 564 | 565 | 390 | 393 | 399 | 360 | 270 | 273 |  | 275 | 274 | 273 | 272 | 274 | 274 | 272 | 7192727
120 | Eastern Zone Total | 4880 | 4539 | 4460 | 4424 | 4392 | 4564 | 4951 | 5152 | 5059 | 5288 | 5510 | 5850 | 5925 | 5741 | 5708 | 5667 | 5856 | 6377 |  | 6247 | 6003 | 5772 | 5459 | 5171 | 4997 | 4864 | 126419103
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [16 empty] | 16 | 32 |  | 32 | 32 | 32 |  |  |  | 0 | 120000
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [15 empty] | 3 | 17 | 17 |  | 17 | 17 |  |  |  |  | 0 | 63840
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 3 | 14 | 42 | 62 | 70 | 71 | 68 | 55 | 37 | 16 | 1 | [9 empty] | 445680
131 | Rampal 1320 MW (BIFPCL) | 443 | 457 | 393 | 403 | 361 | 363 | 419 | 424 | 398 | 402 | 398 | 446 | 473 | 403 | 402 | 404 | 404 | 460 |  | 613 | 627 | 632 | 619 | 505 | 423 | 363 | 10727270
132 | United Payra Power Ltd. | [15 empty] | 2 | 35 | 55 |  | 17 | 17 |  |  |  |  | 0 | 123600
133 | Bhola Nutan Biddut BD LTD (GAS) | 122 | 123 | 122 | 123 | 123 | 123 | 123 | 123 | 122 | 124 | 144 | 144 | 144 | 144 | 170 | 170 | 142 | 110 |  | 110 | 110 | 121 | 131 | 135 | 204 | 220 | 3309491
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [25 empty] | 0 | 0
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 140 | 140 | 140 | 140 | 140 | 140 | 176 | 200 | 200 | 172 | 170 | 200 | 230 | 194 | 150 | 150 | 150 | 200 |  | 200 | 200 | 200 | 200 | 160 | 150 | 150 | 4080000
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 130 | 80 | 80 | 130 | 122 | 72 | 80 | 80 | 80 | 130 |  | 130 | 122 | 130 | 122 | 122 | 130 | 130 | 2390000
140 | Bhola 33 MW PP (Venture) | 17 | 17 | 16 | 15 | 15 | 15 | 15 | 15 | 13 | 13 | 11 | 12 | 13 | 13 | 11 | 11 | 11 | 18 |  | 19 | 20 | 19 | 20 | 20 | 20 | 19 | 361900
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 440 | 440 | 440 | 439 | 440 | 440 | 440 | 440 | 439 | 440 | 440 | 440 | 440 | 440 | 436 | 437 | 700 | 757 |  | 626 | 767 | 767 | 908 | 909 | 909 | 910 | 13501090
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 1020 | 960 | 860 | 740 | 740 | 740 | 770 | 890 | 850 | 860 | 870 | 930 | 1020 | 950 | 940 | 940 | 970 | 1080 |  | 1150 | 1160 | 1150 | 1150 | 1080 | 880 | 720 | 24558400
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 164 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4155600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 3 | 4 | 4 | 5 | 4 | 4 | 2 | 0 | 0 | [9 empty] | 29220
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 86 | 118 | 190 | 214 | 224 | 226 | 226 | 227 | 226 | 224 | 222 | 221 | 217 | 160 | 140 | 140 | 140 | 187 |  | 214 | 214 | 214 | 214 | 130 | 130 | 132 | 4749764
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 196 | 142 | 0 | [10 empty] | 93 | 106 | 90 | 90 | 91 |  | 91 | 91 | 105 | 135 | 397 | 414 | 414 | 2217200
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 236592
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [26 empty] | 0
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 8 | 0 |  |  |  |  | 0 | 10632
170 | Chapainawabganj 100 MW Peaking PP | [26 empty] | 0
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [12 empty] | 42 | 50 | 50 | 35 | 35 | 45 |  | 50 | 50 | 35 |  |  |  | 0 | 411168
172 | Confidence Power Bogura Unit-1 113 MW | [12 empty] | 30 | 54 | 35 | 35 | 35 | 90 |  | 50 | 35 | 35 |  |  |  | 0 | 386880
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [12 empty] | 40 | 40 | 37 | 35 | 42 | 98 |  | 70 | 34 | 34 |  |  |  | 0 | 396364
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 3 | 3 | 3 | 4 | 4 | 3 | 1 | 0 | [9 empty] | 24817
178 | Energypac Power Venture Thakurgaon Ltd. | [12 empty] | 17 | 35 | 36 | 36 | 36 | 46 |  | 36 | 36 |  |  |  |  | 0 | 286656
| Intraco Solar 30 MW | [6 empty] | 1 | 6 | 19 | 27 | 33 | 27 | 31 | 23 | 17 | 8 | 0 | [9 empty] | 190361
| Adani Power Jharkhanda Ltd | 825 | 826 | 819 | 814 | 815 | 823 | 838 | 822 | 812 | 816 | 819 | 816 | 811 | 819 | 815 | 827 | 824 | 873 |  | 854 | 870 | 871 | 870 | 841 | 839 | 820 | 20023636
178 | Teesta Solar Limited | [6 empty] | 6 | 69 | 77 | 74 | 151 | 175 | 167 | 139 | 84 | 31 | 2 | [9 empty] | 1003590