## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-12-03 | Sunday
|  | Date (day): | 2023-12-03 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11874.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13550 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-12-02 | 2023-12-03 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 73 | 72 | 70 | 72 | 36 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 404 | 357 | 350 | 360 | 52 |  | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 390 | 390 | 400 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 90 | 90 |  | 10 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 20 | 0 | 85 | 85 |  | 17 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 13 | 25 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 30 | 40 | 35 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 13 | 15 | 15 |  | 7 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 90 | 90 |  | 10 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 271 | 277 | 275 | 280 | 55
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 17 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 48 | 48 | 48
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 9 | 17 | 0 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 0 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 35 | 30 | 38 | 38 |  | 42 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 17 | 8 | 16 | 36 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 16 | 55 | 80 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 35 | 46 | 36 | 80 | 69 |  | Fuel shortage
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 105 | 30 | 105
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 4 | 27 | 26 | 52 | 52 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 54 | 35 | 54 | 108 |  | Fuel shortage
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 27 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 35 | 20 |  | Fuel shortage
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 5763 | 5422 | 1601 | 1782 | 2176 | 2736 | 1203 | 1026
38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
39 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 0 | 8 | 17 | 8 |  | Fuel shortage
40 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 11 | 0 | 20 | 0
41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 17 | 6 | 19 | 31 |  | Fuel shortage
42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 86 | 86 | 86 | 86 | 144 |  | Low water lavel
43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 193 | 192 | 200 | 200
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 2 | 17 | 17 | 17 | 88 |  | Fuel shortage
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 80 | 80 | 18 |  | Fuel shortage
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 0 | 17 | 85 |  | Fuel shortage
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 12 | 0 | 12 | 12 | 88 |  | Fuel shortage
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 12 | 12 | 88 |  | Fuel shortage
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 13 | 13 | 12 | 12 | 10 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 0 | 10 | 20
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 30 | 115 | 200 | 260 | 40 |  | Fuel shortage
54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 8 | 36 | 17 | 36 | 18 |  | Fuel shortage
55 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 17 | 17 | 93 |  | Fuel shortage
56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 12 | 12 | 88 |  | Fuel shortage
57 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 17 | 99 |  | Fuel shortage
58 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 6 | 0 | 0 | 0 | 163 |  | Fuel shortage
59 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 492 | 491 | 500 | 500
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 0 | 4 | 10 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 133 | 505 | 500 | 420 |  |  | On test.
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 17 | 0 | 0
| Chattogram area Total |  |  |  |  | 3829 | 3769 | 1024 | 1544 | 1741 | 1764 | 1349 | 330
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 0 | 0 |  | 221 | Under maint.
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 330 | 310 | 320 | 320 | 40 |  | Gas shortage
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
63 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 393 | 393 | 400 | 400
64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 41 | 41 | 47 | 47
65 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 0 | 39 | 25 | 20 | 25 | 30 |  | Gas shortage
66 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 83 | 170 | 100 | 100 | 95 |  | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
68 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 26 | 92 | 150 | 150
69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 20
70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
71 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 11 | 100 | 150 | 50 |  | Fuel shortage
72 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 98 | 118 | 128 | 140
74 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 14 | 52 | 52
76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 10 | 10 | 10 | 10 |  | 15 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 17 | 114 | 114
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 27 | 42 | 28 | 60 | 53 |  | Fuel shortage
79 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
80 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 18 | 51 | 17 | 54 | 61 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2896 | 1190 | 1421 | 1616 | 1772 | 329 | 800
81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 69 | 68 | 60 | 70 | 132 |  | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Contract Expired
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 18 | 93 | 84 | 100 | 100 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 94 | 85 | 56 | 85 | 30 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 47 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 230 | 252 | 257.6 | 261 | 132 | 22
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 22 | 28 | 28 | 28 |  | 62 | Engine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 25 | 0 | 25 | 26 |  | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 25 | 0 | 25 | 25 |  | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 3 | 3 | 8 | 8 |  | 3 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 |  | 66 | Under maint.
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 40 | 40 | 60 | 60 | 26 |  | Gas shortage
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 127 | 126 | 128 | 128 |  | 103 | Machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 17 | 17
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 16 | 16 | 16 | 9 |  | Gas shortage
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 290 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 400 | 368 | 400 | 400
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 392 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1352 | 1374 | 1410 | 1460 | 249 | 691
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 437 | 443 | 449 | 449
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 32 | 48 | 67 |  | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 50
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 70 | 39 |  | Fuel shortage
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 8 | 32 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 90 | 90 |  | 15 | Engine problem
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 54 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 456 | 623 | 620 | 620
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 947 | 1066 | 1291 | 1335 | 899 | 15
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 16 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 11 | 16 | 21 | 25 |  | 15 | Engine problem
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 64 | 64 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1080 | 1210 | 1000 | 1220
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 150
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 150 | 286 | 200 | 300
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1525 | 1796 | 1587 | 2155 | 0 | 79
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 30 | 22 |  | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 20 |  | 51 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 28 | 28
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 34 | 42 |  | 8 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 40 |  | 10 | Engine problem
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 306 | 414 | 414
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 38 | 12 |  | Fuel shortage
136 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 40 | 86 |  | 18 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 20 | 50 | 63 |  | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 35 | 113 | 113
143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 0 | 739 | 600 | 750
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 542 | 1126 | 1348 | 1674 | 1118 | 87
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 49 | 70 | 40 | 113
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 35 | 70 | 110
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 43 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 119 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 422 | 275 | 448 | 393 | 125 | 189
| Total |  |  |  |  | 25951 | 25211 | 8833 | 10636 | 11874.6 | 13550 | 5404 | 3239
A. |  | 2023-12-02 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 10636 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 6874 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10636 | MW
3 | Day peak Generation : |  |  | 8833 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10117.33 | MW
4 | Evening peak Generation : |  |  | 10636 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 202.2471 | MKWHr | By Solar | 2.1557 | MKWHr
| By Gas : | 109.2265 | MKWHr |  | By Oil: | 10.9307 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 62.9836 | MKWHr |  | By Hydro: | 2.064 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.04656 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5404 | MW | Dhaka | 3797.13 | 3797.13 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3239 | MW | Chittagong | 1151.2 | 1151.2 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 8643 | MW | Khulna | 1173.4 | 1173.4 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 806.73 | MMCFD |  |  | Rajshahi | 970.3 | 970.3 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 109741374.992 | ii) Oil : | Taka | 145485954.3 | Comilla | 894 | 894 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 455660839.25 | Total | Taka | 710888168.542 | Mymensingh | 799 | 799 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.396 | MKWHr. | Sylhet | 375 | 375 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 156 | MW (W to E) at | 18:00 | hrs | Barisal | 277.3 | 277.3 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 75 | MW at | 11:00 | hrs | Rangpur | 680 | 680 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.3°C |  |  | Total | 10117.33 | 10117.33 |  | 0
B. |  | 2023-12-03 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 30.3°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13550 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9500 | MW
4 | Reserve(Generation end) |  |  |  | 2650 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 207.2672 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7314 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 12.3978 | MKWHr. | ii) HVDC Flow at Peak Time |  | 443 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.4422 | MKWHr. | iii) Maximum HVDC Flow : |  | 920 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 97.83 |  | (b) Today: | 97.67 |  | (c) Rule Curve: |  | 105.91
.

## YesterdayGen
2023-12-02 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 402 | 0 |  | 0 | 380 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 15 | 25 | 31 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 30 | 0 | 0 | 0 | 280 | 0 | 0 | 65 | 0 | 44 | 47 | 0 | 5 | 0 | 0 | 0 | 18 | 11 | 33 | 10 | 100 | 93 | 0 | 0 | 0 | 43 | 28 | 5 | 5 | 0 | 0 | 0 | 5 | 0 | 128 | 0 | 0 | 0 | 270 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 405 | 2 | 0 | 0 | 0 |  | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 860 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 150 | 0 | 0 | 0 |  | 4492 | 3197 | 7689 | 3087 | 920 | 1502 | 0 | 0 | 1992 | 86 | 0 | 0 | 100 | 0 | 2 | 0 | 97.88
2:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 398 | 0 |  | 0 | 380 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 15 | 25 | 31 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 30 | 0 | 0 | 0 | 280 | 0 | 0 | 65 | 0 | 44 | 47 | 0 | 5 | 0 | 0 | 0 | 18 | 11 | 33 | 10 | 90 | 109 | 0 | 0 | 0 | 43 | 28 | 5 | 5 | 0 | 0 | 0 | 5 | 0 | 128 | 0 | 0 | 0 | 275 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 380 | 0 | 0 | 0 | 0 |  | 730 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 820 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 150 | 0 | 0 | 0 |  | 4455 | 2922 | 7377 | 3082 | 730 | 1507 | 0 | 0 | 1882 | 86 | 0 | 0 | 90 | 0 | 0 | 0 | 97.87
3:00 | 0 | 0 | 0 | 180 | 0 | 23 | 0 | 398 | 0 |  | 0 | 340 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 15 | 25 | 31 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 30 | 0 | 0 | 0 | 280 | 0 | 0 | 36 | 0 | 44 | 25 | 0 | 5 | 0 | 0 | 0 | 18 | 11 | 33 | 10 | 88 | 110 | 0 | 0 | 0 | 43 | 28 | 5 | 5 | 0 | 0 | 0 | 5 | 0 | 128 | 0 | 0 | 0 | 285 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 350 | 2 | 0 | 0 | 0 |  | 682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 820 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 150 | 0 | 0 | 0 |  | 4223 | 2838 | 7061 | 3011 | 682 | 1345 | 0 | 0 | 1847 | 86 | 0 | 0 | 88 | 0 | 2 | 0 | 97.86
4:00 | 0 | 0 | 0 | 180 | 0 | 23 | 0 | 388 | 0 |  | 0 | 340 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 15 | 25 | 31 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 193 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 30 | 0 | 0 | 0 | 280 | 0 | 0 | 36 | 0 | 44 | 10 | 0 | 5 | 0 | 0 | 0 | 18 | 11 | 33 | 10 | 88 | 109 | 0 | 0 | 0 | 43 | 28 | 5 | 5 | 0 | 0 | 0 | 5 | 0 | 128 | 0 | 0 | 0 | 285 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 350 | 8 | 0 | 0 | 0 |  | 682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 150 | 0 | 0 | 0 |  | 4152 | 2751 | 6903 | 2949 | 682 | 1300 | 0 | 0 | 1790 | 86 | 0 | 0 | 88 | 0 | 8 | 0 | 97.85
5:00 | 0 | 0 | 0 | 180 | 0 | 30 | 0 | 350 | 0 |  | 0 | 340 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 15 | 25 | 31 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 193 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 31 | 0 | 0 | 0 | 280 | 0 | 0 | 36 | 0 | 44 | 10 | 0 | 5 | 0 | 0 | 0 | 18 | 11 | 33 | 10 | 92 | 110 | 0 | 0 | 0 | 43 | 28 | 5 | 5 | 0 | 0 | 0 | 5 | 0 | 128 | 0 | 0 | 0 | 280 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 350 | 4 | 0 | 0 | 0 |  | 682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 150 | 0 | 0 | 0 |  | 4119 | 2755 | 6874 | 2913 | 682 | 1303 | 0 | 0 | 1794 | 86 | 0 | 0 | 92 | 0 | 4 | 0 | 97.84
6:00 | 0 | 0 | 0 | 180 | 0 | 53 | 0 | 351 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 15 | 25 | 31 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 193 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 30 | 0 | 0 | 0 | 325 | 0 | 0 | 45 | 0 | 44 | 11 | 0 | 5 | 0 | 0 | 0 | 18 | 11 | 33 | 10 | 88 | 110 | 0 | 0 | 0 | 43 | 28 | 5 | 5 | 0 | 0 | 0 | 5 | 0 | 128 | 0 | 0 | 0 | 310 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 350 | 4 | 0 | 0 | 0 |  | 602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 760 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 150 | 0 | 0 | 0 |  | 4333 | 2759 | 7092 | 3009 | 602 | 1474 | 0 | 35 | 1794 | 86 | 0 | 0 | 88 | 0 | 4 | 0 | 97.83
7:00 | 0 | 0 | 0 | 180 | 0 | 53 | 0 | 382 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 15 | 25 | 31 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 13 | 0 | 0 | 0 | 340 | 0 | 0 | 73 | 0 | 44 | 24 | 0 | 30 | 0 | 0 | 0 | 18 | 11 | 30 | 10 | 78 | 93 | 0 | 0 | 0 | 43 | 28 | 25 | 22 | 0 | 0 | 0 | 40 | 0 | 128 | 0 | 0 | 10 | 295 | 5 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 27 | 1 | 0 | 0 | 0 | 342 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 355 | 0 | 0 | 400 | 2 | 0 | 0 | 0 |  | 440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 820 | 220 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 405 | 2 | 150 | 0 | 9 | 0 |  | 4685 | 2832 | 7517 | 3097 | 440 | 1653 | 0 | 165 | 1945 | 86 | 0 | 32 | 78 | 19 | 2 | 0 | 97.82
8:00 | 0 | 0 | 0 | 180 | 0 | 65 | 0 | 401 | 0 |  | 0 | 390 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 0 | 25 | 16 | 5 | 0 | 46 | 40 | 0 | 0 | 0 | 193 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 8 | 0 | 0 | 0 | 315 | 0 | 0 | 130 | 0 | 44 | 27 | 0 | 43 | 0 | 0 | 0 | 18 | 11 | 33 | 10 | 92 | 75 | 0 | 0 | 1 | 43 | 28 | 5 | 5 | 0 | 0 | 0 | 40 | 0 | 128 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 3 | 0 | 0 | 0 | 368 | 16 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 14 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 340 | 0 | 0 | 450 | 0 | 0 | 0 | 0 |  | 439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 113 | 940 | 220 | 0 | 0 | 1 | 25 | 0 | 0 | 0 | 455 | 3 | 200 | 0 | 67 | 0 |  | 4817 | 3093 | 7910 | 3067 | 439 | 1616 | 0 | 221 | 2215 | 86 | 0 | 48 | 92 | 126 | 0 | 20.055 | 97.81
9:00 | 0 | 0 | 0 | 180 | 0 | 66 | 0 | 397 | 0 |  | 0 | 390 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 193 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 0 | 0 | 0 | 280 | 0 | 0 | 83 | 0 | 44 | 27 | 0 | 43 | 0 | 0 | 0 | 18 | 5 | 33 | 10 | 102 | 75 | 0 | 0 | 1 | 43 | 22 | 5 | 0 | 0 | 0 | 0 | 40 | 0 | 130 | 0 | 0 | 10 | 290 | 0 | 8 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 5 | 0 | 0 | 0 | 368 | 24 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 29 | 0 | 0 | 0 | 16 | 20 | 0 | 1 | 300 | 0 | 0 | 450 | 0 | 0 | 0 | 0 |  | 438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 113 | 900 | 180 | 0 | 0 | 3 | 47 | 0 | 0 | 0 | 430 | 9 | 177 | 0 | 113 | 0 |  | 4668 | 3041 | 7709 | 2890 | 438 | 1523 | 0 | 266 | 2127 | 86 | 0 | 48 | 102 | 229 | 0 | 58.255 | 97.8
10:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 384 | 0 |  | 0 | 390 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 193 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 0 | 0 | 0 | 280 | 0 | 0 | 83 | 0 | 42 | 27 | 0 | 43 | 0 | 0 | 0 | 18 | 5 | 0 | 10 | 96 | 72 | 0 | 0 | 2 | 43 | 22 | 5 | 0 | 0 | 0 | 0 | 40 | 0 | 130 | 0 | 0 | 10 | 300 | 0 | 3 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 6 | 6 | 0 | 0 | 370 | 24 | 34 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 37 | 0 | 1 | 0 | 17 | 26 | 0 | 17 | 350 | 0 | 0 | 470 | 0 | 0 | 0 | 0 |  | 438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 20 | 0 | 3 | 113 | 880 | 220 | 0 | 0 | 4 | 66 | 35 | 0 | 0 | 409 | 20 | 150 | 0 | 84 | 0 |  | 4729 | 3114 | 7843 | 2880 | 438 | 1621 | 0 | 345 | 2079 | 86 | 0 | 48 | 96 | 250 | 0 | 29.605 | 97.79
11:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 406 | 0 |  | 0 | 390 | 0 | 0 | 2 | 0 | 272 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 6 | 0 | 0 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 193 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 0 | 0 | 13 | 2 | 0 | 0 | 0 | 330 | 0 | 0 | 83 | 0 | 42 | 30 | 0 | 43 | 0 | 0 | 0 | 18 | 5 | 25 | 10 | 84 | 70 | 0 | 0 | 2 | 43 | 22 | 5 | 0 | 0 | 0 | 0 | 40 | 0 | 129 | 0 | 0 | 10 | 295 | 0 | 3 | 0 | 1 | 0 | 0 | 18 | 0 | 35 | 7 | 0 | 10 | 3 | 368 | 24 | 34 | 0 | 3 | 5 | 0 | 7 | 0 | 9 | 0 | 392 | 0 | 22 | 0 | 17 | 0 | 17 | 30 | 5 | 17 | 393 | 0 | 0 | 491 | 0 | 0 | 0 | 0 |  | 438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 34 | 0 | 5 | 113 | 970 | 220 | 0 | 0 | 5 | 76 | 35 | 0 | 0 | 409 | 21 | 150 | 0 | 135 | 0 |  | 4908 | 3243 | 8151 | 3016 | 438 | 1577 | 0 | 406 | 2190 | 86 | 0 | 48 | 84 | 306 | 0 | 29.605 | 97.78
12:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 404 | 0 |  | 0 | 390 | 0 | 0 | 20 | 13 | 271 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 20 | 15 | 0 | 0 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 193 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 0 | 0 | 13 | 2 | 0 | 0 | 0 | 330 | 0 | 0 | 83 | 0 | 41 | 39 | 0 | 43 | 0 | 0 | 0 | 18 | 5 | 25 | 10 | 98 | 69 | 0 | 0 | 2 | 43 | 22 | 5 | 0 | 0 | 0 | 0 | 40 | 0 | 127 | 0 | 0 | 10 | 310 | 0 | 3 | 0 | 16 | 0 | 0 | 18 | 0 | 35 | 11 | 0 | 17 | 26 | 400 | 94 | 34 | 2 | 2 | 30 | 8 | 17 | 0 | 27 | 0 | 392 | 4 | 47 | 17 | 17 | 0 | 17 | 27 | 18 | 17 | 393 | 0 | 6 | 492 | 0 | 133 | 0 | 0 |  | 437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 49 | 0 | 6 | 113 | 1080 | 220 | 0 | 0 | 4 | 54 | 35 | 0 | 0 | 456 | 43 | 150 | 0 | 119 | 0 |  | 5397 | 3436 | 8833 | 3055 | 437 | 1640 | 0 | 673 | 2481 | 86 | 0 | 48 | 98 | 315 | 0 | 30 | 98.77
13:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 406 | 0 |  | 0 | 380 | 0 | 1 | 34 | 15 | 270 | 0 | 0 | 5 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 15 | 0 | 0 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 193 | 0 | 0 | 0 |  | 3 | 0 | 0 | 12 | 0 | 0 | 13 | 2 | 0 | 0 | 0 | 310 | 0 | 0 | 83 | 0 | 41 | 45 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 25 | 10 | 104 | 61 | 0 | 0 | 2 | 43 | 22 | 5 | 0 | 0 | 0 | 0 | 60 | 0 | 128 | 0 | 0 | 10 | 300 | 0 | 3 | 0 | 42 | 0 | 0 | 19 | 0 | 35 | 7 | 0 | 17 | 50 | 368 | 94 | 34 | 17 | 3 | 32 | 17 | 17 | 0 | 28 | 0 | 400 | 17 | 43 | 17 | 17 | 0 | 17 | 29 | 18 | 17 | 390 | 0 | 14 | 492 | 0 | 152 | 0 | 0 |  | 444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 391 | 0 | 0 | 0 | 0 | 65 | 0 | 6 | 113 | 1100 | 220 | 0 | 0 | 2 | 62 | 36 | 0 | 0 | 490 | 33 | 180 | 75 | 155 | 0 |  | 5508 | 3629 | 9137 | 3010 | 444 | 1630 | 0 | 814 | 2659 | 86 | 0 | 48 | 104 | 342 | 0 | 26.74 | 98.76
14:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 362 | 0 |  | 0 | 340 | 0 | 8 | 34 | 15 | 270 | 0 | 0 | 8 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 15 | 0 | 0 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 193 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 6 | 13 | 2 | 0 | 0 | 0 | 280 | 0 | 0 | 83 | 0 | 43 | 44 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 10 | 104 | 63 | 0 | 0 | 1 | 43 | 22 | 5 | 0 | 0 | 0 | 0 | 60 | 0 | 126 | 0 | 0 | 10 | 290 | 0 | 3 | 0 | 60 | 0 | 0 | 19 | 0 | 17 | 4 | 0 | 0 | 50 | 318 | 94 | 34 | 17 | 3 | 45 | 17 | 17 | 0 | 29 | 0 | 360 | 17 | 36 | 35 | 17 | 0 | 17 | 24 | 18 | 17 | 390 | 0 | 0 | 491 | 0 | 269 | 0 | 0 |  | 444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 70 | 0 | 6 | 113 | 1070 | 220 | 0 | 0 | 2 | 71 | 36 | 0 | 0 | 405 | 30 | 150 | 149 | 143 | 0 |  | 5423 | 3522 | 8945 | 2842 | 444 | 1544 | 0 | 853 | 2704 | 86 | 0 | 48 | 104 | 320 | 0 | 52.525 | 97.78
15:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 351 | 0 |  | 0 | 340 | 0 | 0 | 26 | 15 | 284 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 15 | 0 | 0 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 193 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 6 | 11 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 83 | 0 | 40 | 42 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 10 | 110 | 62 | 0 | 0 | 1 | 43 | 22 | 5 | 0 | 0 | 0 | 0 | 60 | 0 | 126 | 0 | 0 | 10 | 290 | 0 | 3 | 0 | 0 | 0 | 0 | 18 | 0 | 17 | 1 | 0 | 0 | 18 | 343 | 8 | 34 | 17 | 2 | 45 | 17 | 17 | 0 | 9 | 0 | 393 | 0 | 19 | 0 | 17 | 0 | 17 | 16 | 17 | 17 | 388 | 0 | 0 | 491 | 0 | 563 | 0 | 0 |  | 443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 7 | 0 | 3 | 0 | 940 | 220 | 0 | 0 | 2 | 40 | 0 | 0 | 0 | 407 | 17 | 150 | 325 | 88 | 0 |  | 5480 | 3231 | 8711 | 2920 | 443 | 1516 | 0 | 353 | 3046 | 86 | 0 | 48 | 110 | 189 | 0 | 51.57 | 98.74
16:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 355 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 287 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 15 | 0 | 0 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 193 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 6 | 13 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 83 | 0 | 34 | 24 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 10 | 120 | 65 | 0 | 0 | 0 | 43 | 22 | 5 | 0 | 0 | 0 | 0 | 60 | 0 | 126 | 0 | 0 | 10 | 310 | 0 | 3 | 0 | 0 | 0 | 0 | 18 | 0 | 17 | 1 | 0 | 0 | 6 | 372 | 8 | 34 | 17 | 0 | 15 | 17 | 17 | 0 | 0 | 0 | 395 | 0 | 9 | 0 | 17 | 0 | 17 | 7 | 17 | 12 | 385 | 0 | 0 | 492 | 0 | 563 | 0 | 0 |  | 444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 900 | 220 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 403 | 7 | 150 | 433 | 33 | 0 |  | 5471 | 3174 | 8645 | 2957 | 444 | 1555 | 0 | 249 | 3111 | 86 | 0 | 48 | 120 | 75 | 0 | 52.525 | 98.74
17:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 393 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 5 | 13 | 20 | 15 | 0 | 0 | 17 | 0 | 46 | 40 | 0 | 0 | 0 | 191 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 8 | 13 | 2 | 0 | 0 | 0 | 280 | 0 | 0 | 167 | 0 | 32 | 24 | 0 | 51 | 0 | 0 | 0 | 18 | 8 | 33 | 10 | 126 | 68 | 0 | 0 | 0 | 43 | 28 | 25 | 15 | 0 | 0 | 0 | 40 | 0 | 126 | 0 | 0 | 10 | 315 | 0 | 3 | 0 | 0 | 0 | 0 | 24 | 0 | 17 | 0 | 0 | 0 | 28 | 330 | 19 | 105 | 17 | 0 | 45 | 23 | 17 | 1 | 9 | 0 | 370 | 2 | 0 | 54 | 17 | 0 | 17 | 0 | 11 | 17 | 340 | 0 | 13 | 491 | 0 | 505 | 0 | 0 |  | 443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 25 | 1010 | 220 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 501 | 0 | 182 | 598 | 2 | 0 |  | 5666 | 3559 | 9225 | 2872 | 443 | 1664 | 0 | 526 | 3457 | 86 | 0 | 48 | 126 | 3 | 0 | 0 | 98.73
18:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 357 | 0 |  | 0 | 390 | 0 | 0 | 0 | 25 | 277 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 13 | 20 | 10 | 0 | 0 | 17 | 0 | 46 | 40 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 6 | 0 | 17 | 0 | 0 | 17 | 13 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 170 | 0 | 41 | 25 | 0 | 51 | 0 | 0 | 14 | 18 | 8 | 33 | 10 | 118 | 68 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 0 | 40 | 0 | 126 | 0 | 0 | 10 | 290 | 16 | 3 | 0 | 55 | 0 | 0 | 93 | 0 | 46 | 0 | 0 | 11 | 92 | 368 | 85 | 105 | 17 | 0 | 115 | 36 | 17 | 17 | 42 | 0 | 400 | 27 | 0 | 54 | 17 | 0 | 17 | 0 | 51 | 17 | 393 | 0 | 17 | 491 | 4 | 505 | 0 | 0 |  | 443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 35 | 1210 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 623 | 0 | 286 | 739 | 0 | 0 |  | 6373 | 4263 | 10636 | 3019 | 443 | 1640 | 0 | 1237 | 4024 | 86 | 0 | 65 | 118 | 0 | 4 | 0 | 98.73
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 400 | 0 |  | 0 | 380 | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 13 | 20 | 15 | 25 | 0 | 17 | 0 | 46 | 40 | 0 | 0 | 0 | 193 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 20 | 13 | 3 | 0 | 0 | 0 | 305 | 0 | 0 | 102 | 0 | 45 | 24 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 10 | 112 | 68 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 0 | 40 | 0 | 128 | 0 | 0 | 10 | 280 | 16 | 3 | 0 | 0 | 0 | 0 | 93 | 0 | 64 | 0 | 0 | 69 | 150 | 367 | 85 | 88 | 17 | 0 | 150 | 36 | 17 | 0 | 48 | 0 | 400 | 0 | 0 | 54 | 17 | 0 | 17 | 0 | 34 | 17 | 384 | 0 | 0 | 491 | 0 | 507 | 0 | 0 |  | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 35 | 1244 | 220 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 626 | 0 | 307 | 753 | 0 | 0 |  | 6319 | 4089 | 10408 | 3058 | 208 | 1562 | 0 | 1219 | 4098 | 86 | 0 | 65 | 112 | 0 | 0 | 0 | 97.71
19:30 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 401 | 0 |  | 0 | 380 | 0 | 0 | 0 | 0 | 261 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 13 | 20 | 15 | 25 | 8 | 17 | 0 | 46 | 40 | 0 | 0 | 0 | 193 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 20 | 13 | 7 | 0 | 0 | 0 | 305 | 0 | 0 | 102 | 0 | 45 | 24 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 10 | 120 | 73 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 0 | 40 | 0 | 128 | 0 | 0 | 10 | 285 | 16 | 5 | 0 | 0 | 0 | 0 | 93 | 0 | 80 | 0 | 0 | 51 | 70 | 367 | 0 | 88 | 17 | 0 | 150 | 36 | 17 | 0 | 9 | 0 | 400 | 0 | 0 | 54 | 17 | 0 | 0 | 0 | 17 | 12 | 372 | 0 | 0 | 491 | 1 | 503 | 0 | 0 |  | 444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 626 | 0 | 307 | 757 | 0 | 0 |  | 6053 | 4145 | 10198 | 3058 | 444 | 1588 | 0 | 782 | 4054 | 86 | 0 | 65 | 120 | 0 | 1 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 400 | 0 |  | 0 | 370 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 13 | 20 | 15 | 25 | 18 | 17 | 0 | 46 | 40 | 0 | 0 | 0 | 193 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 20 | 13 | 8 | 0 | 0 | 0 | 310 | 0 | 0 | 158 | 0 | 46 | 26 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 10 | 120 | 73 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 0 | 40 | 0 | 128 | 0 | 0 | 10 | 295 | 16 | 5 | 0 | 0 | 0 | 0 | 93 | 0 | 80 | 0 | 0 | 51 | 70 | 366 | 0 | 88 | 17 | 0 | 150 | 36 | 17 | 0 | 9 | 0 | 400 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 17 | 12 | 357 | 0 | 0 | 491 | 3 | 505 | 0 | 0 |  | 444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 624 | 0 | 307 | 695 | 0 | 0 |  | 6043 | 4094 | 10137 | 3057 | 444 | 1659 | 0 | 711 | 3992 | 86 | 0 | 65 | 120 | 0 | 3 | 0 | 97.72
21:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 371 | 0 |  | 0 | 370 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 13 | 20 | 15 | 25 | 20 | 17 | 0 | 46 | 40 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 20 | 13 | 12 | 0 | 0 | 0 | 280 | 0 | 0 | 158 | 0 | 45 | 26 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 10 | 116 | 73 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 0 | 40 | 0 | 128 | 0 | 0 | 10 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 65 | 0 | 80 | 0 | 0 | 83 | 0 | 321 | 0 | 88 | 17 | 0 | 80 | 36 | 17 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 17 | 17 | 318 | 0 | 0 | 491 | 6 | 505 | 0 | 0 |  | 443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1244 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 625 | 0 | 307 | 750 | 0 | 0 |  | 5728 | 4217 | 9945 | 2949 | 443 | 1617 | 0 | 571 | 4092 | 86 | 0 | 65 | 116 | 0 | 6 | 0 | 97.71
22:00 | 0 | 0 | 0 | 180 | 0 | 68 | 0 | 354 | 0 |  | 0 | 380 | 0 | 0 | 0 | 0 | 262 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 15 | 17 | 25 | 17 | 0 | 46 | 40 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 20 | 13 | 22 | 0 | 0 | 0 | 280 | 0 | 0 | 102 | 0 | 47 | 26 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 10 | 111 | 73 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 0 | 40 | 0 | 130 | 0 | 0 | 10 | 285 | 16 | 5 | 0 | 0 | 0 | 0 | 24 | 0 | 80 | 0 | 0 | 28 | 0 | 321 | 0 | 70 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 17 | 17 | 325 | 0 | 0 | 492 | 3 | 508 | 0 | 0 |  | 444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1140 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582 | 0 | 294 | 754 | 0 | 0 |  | 5408 | 4062 | 9470 | 2942 | 444 | 1571 | 0 | 324 | 3940 | 86 | 0 | 49 | 111 | 0 | 3 | 0 | 97.71
23:00 | 0 | 0 | 0 | 180 | 0 | 68 | 0 | 354 | 0 |  | 0 | 380 | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 15 | 17 | 25 | 17 | 0 | 46 | 40 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 20 | 13 | 25 | 0 | 0 | 0 | 280 | 0 | 0 | 102 | 0 | 47 | 26 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 10 | 108 | 73 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 0 | 40 | 0 | 130 | 0 | 0 | 10 | 265 | 16 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 69 | 0 | 0 | 17 | 0 | 321 | 0 | 35 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 17 | 0 | 370 | 0 | 0 | 490 | 5 | 506 | 0 | 0 |  | 443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 505 | 0 | 211 | 758 | 0 | 0 |  | 5327 | 3763 | 9090 | 2990 | 443 | 1552 | 0 | 234 | 3640 | 86 | 0 | 32 | 108 | 0 | 5 | 0 | 97.7
24:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 354 | 0 |  | 0 | 380 | 0 | 0 | 0 | 0 | 267 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 15 | 17 | 28 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 26 | 0 | 0 | 0 | 280 | 0 | 0 | 102 | 0 | 47 | 27 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 10 | 100 | 74 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 0 | 40 | 0 | 130 | 0 | 0 | 10 | 270 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 17 | 0 | 321 | 0 | 35 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 490 | 10 | 509 | 0 | 0 |  | 444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 471 | 0 | 183 | 691 | 0 | 0 |  | 5179 | 3531 | 8710 | 3016 | 444 | 1490 | 0 | 118 | 3414 | 86 | 0 | 32 | 100 | 0 | 10 | 0 | 97.7
KWH | 0 | 0 | 0 | 4328100 | 0 | 1476181 | 0 | 9189370 | 0 |  | 0 | 8293500 | 0 | 12480 | 102102 | 120591 | 6700530 | 0 | 0 | 14486 | 0 | 832800 | 0 | 0 | 0 | 0 | 94500 | 132449 | 88401 | 200664 | 480000 | 299520 | 301000 | 338100 | 200069 | 0 | 1104000 | 960000 | 0 | 0 | 0 | 4638323 | 0 | 0 | 0 |  | 39840 | 0 | 80710 | 40560 | 0 | 150240 | 278832 | 336000 | 0 | 0 | 0 | 7482200 | 0 | 0 | 2258182 | 0 | 1015344 | 688800 | 0 | 942668 | 0 | 0 | 20362 | 428940 | 201960 | 762300 | 237230 | 2442240 | 1850880 | 0 | 0 | 12600 | 1016000 | 652440 | 320400 | 271080 | 0 | 0 | 0 | 860160 | 0 | 3086870 | 0 | 0 | 194580 | 7063000 | 155000 | 127210 | 0 | 243382 | 0 | 0 | 664800 | 0 | 767808 | 49680 | 7680 | 304320 | 543636 | 8350000 | 608400 | 917760 | 195709 | 19297 | 790364 | 285634 | 237526 | 20520 | 246120 | 0 | 9402900 | 104640 | 270340 | 241920 | 242127 | 0 | 207720 | 188894 | 272640 | 237240 | 8700500 | 0 | 46836 | 10925453 | 46560 | 550545 | 0 | 0 |  | 12397818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1780000 | 333200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237366 | 0 | 0 | 4136500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8556000 | 0 | 0 | 122880 | 0 | 413097 | 0 | 31908 | 1047168 | 25430700 | 5344364 | 0 | 0 | 29340 | 462240 | 278016 | 0 | 0 | 11156360 | 177213 | 4647300 | 6136727 | 914190 | 0 |  | 118614745 | 83632387 | 202247132 | 72288415 | 12397818 | 36938115 | 0 | 10017187 | 62983585 | 2064000 | 0 | 913510 | 2442240 | 2155702 | 46560 | 0
Fuel Cost | 0 | 0 | 0 | 6448869 | 0 | 1963320.73 | 0 | 9648838.5 | 0 |  | 0 | 9039915 | 0 | 139526.4 | 1352851.5 | 1597830.75 | 7504593.6 | 0 | 0 | 211785.32 | 0 | 13499688 | 0 | 0 | 0 | 0 | 1202040 | 1788061.5 | 1185457.41 | 150498 | 360000 | 0 | 0 | 0 | 3403173.69 | 0 | 298080 | 259200 | 0 | 0 | 0 | 4823855.92 | 0 | 0 | 0 |  | 519912 | 0 | 1373684.2 | 547965.6 | 0 | 1738276.8 | 354116.64 | 1118880 | 0 | 0 | 0 | 8305242 | 0 | 0 | 2913054.78 | 0 | 1147338.72 | 1026312 | 0 | 1574255.56 | 0 | 0 | 273868.9 | 587647.8 | 151470 | 1334025 | 177922.5 | 17535283.2 | 2017459.2 | 0 | 0 | 200844 | 1391920 | 861220.8 | 557496 | 468968.4 | 0 | 0 | 0 | 1961164.8 | 0 | 3117738.7 | 0 | 0 | 385268.4 | 7063000 | 116250 | 96679.6 | 0 | 3322164.3 | 0 | 0 | 8961504 | 0 | 10634140.8 | 580759.2 | 79257.6 | 4157011.2 | 7214049.72 | 7682000 | 7398144 | 13270809.6 | 2475718.85 | 300261.32 | 9278873.36 | 3110554.26 | 2524901.38 | 278456.4 | 3172486.8 | 0 | 8650668 | 1355088 | 3906413 | 3069964.8 | 2755405.26 | 0 | 2712823.2 | 2257283.3 | 4081420.8 | 3124450.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 37193454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1993600 | 646408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179686.062 | 0 | 0 | 35077520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8470440 | 0 | 0 | 1453670.4 | 0 | 5246331.9 | 0 | 352583.4 | 12712619.52 | 211074810 | 5451251.28 | 0 | 0 | 331835.4 | 5422075.2 | 4261985.28 | 0 | 0 | 101411312.4 | 0 | 55628181 | 52469015.85 | 0 | 0 |  | 240149460.87 | 539376779.692 | 779526240.562 | 67101640.042 | 37193454 | 42639734.95 | 0 | 130612582.1 | 455660839.25 | 557280 | 0 | 14873372.2 | 17535283.2 | 13352054.82 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 404 | 0 |  | 0 | 390 | 0 | 0 | 20 | 13 | 271 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 20 | 15 | 0 | 0 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 193 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 0 | 0 | 13 | 2 | 0 | 0 | 0 | 330 | 0 | 0 | 83 | 0 | 41 | 39 | 0 | 43 | 0 | 0 | 0 | 18 | 5 | 25 | 10 | 98 | 69 | 0 | 0 | 2 | 43 | 22 | 5 | 0 | 0 | 0 | 0 | 40 | 0 | 127 | 0 | 0 | 10 | 310 | 0 | 3 | 0 | 16 | 0 | 0 | 18 | 0 | 35 | 11 | 0 | 17 | 26 | 400 | 94 | 34 | 2 | 2 | 30 | 8 | 17 | 0 | 27 | 0 | 392 | 4 | 47 | 17 | 17 | 0 | 17 | 27 | 18 | 17 | 393 | 0 | 6 | 492 | 0 | 133 | 0 | 0 |  | 437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 49 | 0 | 6 | 113 | 1080 | 220 | 0 | 0 | 4 | 54 | 35 | 0 | 0 | 456 | 43 | 150 | 0 | 119 | 0 |  | 8833 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 357 | 0 |  | 0 | 390 | 0 | 0 | 0 | 25 | 277 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 13 | 20 | 10 | 0 | 0 | 17 | 0 | 46 | 40 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 6 | 0 | 17 | 0 | 0 | 17 | 13 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 170 | 0 | 41 | 25 | 0 | 51 | 0 | 0 | 14 | 18 | 8 | 33 | 10 | 118 | 68 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 0 | 40 | 0 | 126 | 0 | 0 | 10 | 290 | 16 | 3 | 0 | 55 | 0 | 0 | 93 | 0 | 46 | 0 | 0 | 11 | 92 | 368 | 85 | 105 | 17 | 0 | 115 | 36 | 17 | 17 | 42 | 0 | 400 | 27 | 0 | 54 | 17 | 0 | 17 | 0 | 51 | 17 | 393 | 0 | 17 | 491 | 4 | 505 | 0 | 0 |  | 443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 35 | 1210 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 623 | 0 | 286 | 739 | 0 | 0 |  | 10636 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 360 | 0 |  | 0 | 450 | 0 | 90 | 85 | 55 | 280 | 0 | 0 | 90 | 100 | 48 | 40 | 0 | 0 | 0 | 35 | 35 | 55 | 15 | 20 | 18 | 33 | 33 | 16 | 0 | 46 | 40 | 0 | 0 | 17 | 200 | 0 | 0 | 0 |  | 6 | 80 | 17 | 12 | 0 | 19 | 12 | 20 | 0 | 0 | 0 | 320 | 0 | 0 | 100 | 0 | 47 | 25 | 0 | 51 | 0 | 20 | 52 | 18 | 11 | 33 | 10 | 140 | 70 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 0 | 60 | 0 | 128 | 17 | 0 | 10 | 300 | 16 | 8 | 0 | 300 | 0 | 0 | 100 | 0 | 80 | 0 | 12 | 150 | 150 | 400 | 85 | 105 | 17 | 0 | 260 | 36 | 17 | 114 | 60 | 12 | 400 | 52 | 0 | 54 | 17 | 0 | 17 | 0 | 54 | 35 | 400 | 0 | 0 | 500 | 10 | 420 | 0 | 0 |  | 449 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 50 | 70 | 8 | 130 | 25 | 110 | 0 | 0 | 0 | 30 | 20 | 86 | 28 | 42 | 40 | 52 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 90 | 0 | 50 | 0 | 113 | 0 | 0 | 113 | 1220 | 220 | 0 | 150 | 0 | 0 | 110 | 0 | 0 | 620 | 0 | 300 | 750 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 350 | 0 | 0 | 0 | 400 | 0 | 90 | 85 | 55 | 275 | 0 | 0 | 90 | 100 | 48 | 30 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 20 | 18 | 33 | 33 | 8 | 0 | 46 | 40 | 0 | 0 | 8 | 200 |  | 0 | 0 | 0 | 6 | 80 | 0 | 12 | 0 | 6 | 12 | 10 | 0 | 0 | 0 | 320 | 0 | 0 | 100 | 0 | 47 | 20 | 0 | 51 | 0 | 0 | 52 | 18 | 11 | 33 | 10 | 128 | 60 | 0 | 0 | 1.6 | 43 | 28 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 128 | 17 | 0 | 10 | 300 | 16 | 8 | 0 | 80 | 0 | 0 | 84 | 0 | 36 | 20 | 12 | 100 | 150 | 400 | 56 | 30 | 17 | 5 | 200 | 17 | 17 | 114 | 28 | 12 | 400 | 26 | 50 | 35 | 17 | 0 | 17 | 35 | 17 | 17 | 400 | 0 |  | 500 | 10 | 500 | 0 | 0 |  | 449 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 28 | 34 | 30 | 52 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 90 | 0 | 20 | 0 | 40 | 0 | 8 | 113 | 1000 | 220 |  | 0 | 6 | 100 | 70 | 0 |  | 620 | 30 | 200 | 600 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 40 | 0 | 395 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 20 | 15 | 17 | 29 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5 | 0 | 0 | 0 | 340 | 0 | 0 | 65 | 0 | 48 | 27 | 0 | 38 | 0 | 0 | 0 | 18 | 8 | 25 | 10 | 86 | 67 | 0 | 0 | 1 | 43 | 28 | 25 | 25 | 0 | 0 | 0 | 40 | 0 | 130 | 0 | 0 | 10 | 320 | 8 | 5 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 3 | 0 | 0 | 0 | 402 | 10 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 17 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 393 | 0 | 0 | 420 | 0 | 507 | 0 | 0 | 0 | 444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 650 | 220 | 0 | 0 | 2 | 22 | 0 | 0 | 0 | 419 | 9 | 140 | 573 | 22 | 0 | 0 |  |  |  | 109226530 | 12397818 | 0 | 62983585 | 10930697 | 2442240 | 2155702 | 46560 | 2064000
[8 empty] | 299430 | [13 empty] | 299565 | [26 empty] | 399366 | 399587 | [8 empty] | 299280 | [26 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 |  | 399747 |  |  |  | 399575 |  | 399337 | 399589 | 299230 | [7 empty] | 399245 |  | 299282 | 399274 |  | 399223 |  | 399630 | [12 empty] | 599468 | [32 empty] | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 | [8 empty] | 599726 | [9 empty] | 109.2265 | 12.3978 | 0 | 62.9836 | 10.9307 | 2.4422 | 2.1557 | 0.04656 | 2.064
| Minimum Generation |  | 6874 | 5:00
| Highest Generation |  | 10636 | 18:00 | [200 empty] | 202.2471
| Day Peak Generation |  | 8833 | 12:00
| Evening Peak Generation |  | 10636 | 18:00 | [200 empty] | 202699852
| HVDC Max Flow |  | 920 | 1:00 | [200 empty] | 202.6999
| HVDC EvPeak Flow |  | 443 | 18:00
| Load factor L.F |  | 79.23% | [166 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-12-03
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-12-02 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 8833 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 7314
Evening Peak Generation : |  |  | 10636 | MW Hour : | 18:00 | Available Max Generation : |  | 13550
E.P. Demand (at gen end) : |  |  | 10636 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 10900
Maximum Generation : |  |  | 10636 | MW Hour : | 18:00 | Reserve(Generation end) |  | 2650
Total Gen. (MKWH) : |  |  | 202.2471 | System Load Factor : | 79.23% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 75 | MW at | 11:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-12-03
Actual : |  | 97.67 | Ft.(MSL) , | Rule curve : | 105.91 | Ft.( MSL )
Gas Consumed : |  | Total = | 806.73 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 109741374.992
: |  |  | Coal : | 455660839.25 | Oil : | 145485954.3 | Total : | 710888168.542
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3726.0878 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1018.712 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1425.4791 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1237.5835 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1019.0346 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 757.155 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 425.2106 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 353.6298 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 691.6548 |  |  | 0 | 0%
Total |  | 0 |  | 10654.5473 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:01 |  | Bhairob 54.5 MW Syncronized
08:08 | 17:10 | Narail 132/33kV S/S TR1 (403-T) LT Scheduled S/D Due to Annual maintenance work of
Tr-01 and associated equipments.
08:09 | 15:08 | Bakulia 132/33kV S/S T-3 (422T) LT Scheduled S/D Due to Annual Maintenance.
08:09 | 15:04 | Bakulia 132/33kV S/S T-3 (422T) HT Scheduled S/D Due to Annual Maintenance.
08:09 | 17:09 | Narail 132/33kV S/S TR1 (403-T) HT Scheduled S/D Due to Annual maintenance work of
Tr-01 and associated equipments.
08:14 | 17:16 | Mahasthangarh 132/33kV S/S 406T MTR1 LT Scheduled S/D Due to Annual Maintenance
08:15 | 17:15 | Mahasthangarh 132/33kV S/S 406T MTR1 HT Scheduled S/D Due to Annual Maintenance
08:15 |  | Narshingdi 22 MW PP (Doreen) Shutdown
08:18 | 17:27 | Rajshahi 230/132/33kV S/S 132/33 kV T-02 (416T) LT Scheduled S/D Due to Annual Maintenance
08:18 | 17:26 | Rajshahi 230/132/33kV S/S 132/33 kV T-02 (416T) HT Scheduled S/D Due to Annual Maintenance
08:25 |  | BIPTC S/S 22T01 HT Scheduled S/D Due to For maintenance purpose
08:27 |  | Cumilla(N)-Daudkandi 132 kV Ckt-2 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
Annual maintenance works( Dead Line Cheek)
08:28 |  | Fenchuganj 44MW (Energyprima) Shutdown
08:30 |  | Maona 33 MW PP(Summit) Forced Shutdown
08:32 | 16:11 | Barapukuria-Saidpur 132 kV Ckt-2 Scheduled S/D from Saidpur 132/33kV end Due to As the instructions of
ALDC, Bogura and QF-GMD-39 and from Barapukuria 230/132/33kV end Due to Annual Maintenance
08:35 | 15:27 | Goalpara 132/33kV S/S Bus 2 Scheduled S/D Due to annual maintenance
08:38 | 15:28 | Faridpur-Gopalganj(N) 132 kV Ckt-1 Scheduled S/D from Gopalganj 400/132kV end.
08:38 | 15:57 | Aminbazar 400/230/132kV S/S 230/132kv Tr-01 LT Scheduled S/D Due to Annual Maintenance
08:39 | 16:05 | Jamalpur United (20MW)- Sherpur 132kV Ckt-2 Scheduled S/D from Sherpur 132/33kV end.
08:40 | 15:56 | Aminbazar 400/230/132kV S/S 230/132kv Tr-01 HT Scheduled S/D Due to Annual Maintenance
08:41 |  | Rupganj 33 MW PP(Summit) Shutdown
08:43 | 08:59 | Matuail-Siddhirganj 132kV Ckt-1 Tripped from Siddhirganj 132/33kV end showing lockout
relays Due to General trip,Distance Zone 02,B-phase
08:45 | 15:58 | Fenchuganj-Kulaura 132 kV Ckt-2 Scheduled S/D from Kulaura 132/33kV end Due to Annual
maintenance. and from Fenchuganj 230/132/33kV end Due to Annual Maintenance of Kulaura
08:46 |  | Shahjahanulla 25 MW PP Shutdown
08:52 | 15:28 | Faridpur-Gopalganj(N) 132 kV Ckt-1 Scheduled S/D from Faridpur 132/33kV end Due to
Annual maintenance
08:53 | 16:22 | Fenchuganj-Sreemangal 132kV Ckt-2 Scheduled S/D from Sreemongol 132/33kV end Due to Annual
maintance works and from Fenchuganj 230/132/33kV end Due to Annual Maintenance of Sreemongal
08:54 |  | Kanchan Purbachal Power Generation Ltd. Syncronized
08:56 |  | BIPTC S/S 22T01 LT Scheduled S/D Due to For Annual maintenance
| 08:56 | Naogaon 132/33kV S/S Main Bus is restored.
08:58 | 17:03 | Ashuganj-Sreepur 230 kV Ckt-2 Scheduled S/D from Sirajgonj 230 end Due to Annual maintenance.
09:00 | 17:05 | Sreepur 230/132/33kV S/S Sreepur-Sirajganj Ckt-2 Scheduled S/D Due to Line annual maintenance
09:00 |  | Kaptai 7 MW Solar PP Shutdown
| 09:21 | Barishal 230/132kV S/S T-5 HT is restored.
09:21 |  | Netrakona 132/33kV S/S Transformer-1 (415T) HT Scheduled S/D Due to Annual Maintenance
09:22 | 16:26 | Mymensingh RPCL -Mymensingh 132kV Ckt-2 Scheduled S/D from Mymensingh 132/33kV end Due to
Annual maintenance works
| 09:22 | Barishal 230/132kV S/S T-5 LT is restored.
09:24 |  | Energypac Power Venture Thakurgaon Ltd. Syncronized
09:28 |  | Rangpur 113 MW PP (Confidence) Syncronized
09:30 | 18:54 | HVDC Bheramera- Ishwardi 230kV Ckt-3 Scheduled S/D from Ishurdi 230/132kV end Due to A/M
09:32 | 16:34 | Jamalpur United (20MW)-Jamalpur 132kV Ckt-2 Scheduled S/D from Jamalpur 132/33kV end
Due to Annual Maintenance.
09:34 |  | Jangalia 33MW PP (Summit) Shutdown
09:34 | 16:07 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT Scheduled S/D Due to
Annual Maintenance work.
09:35 | 16:04 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT Scheduled S/D Due to
Annual Maintenance work.
09:35 | 16:02 | Kabirpur - Manikganj 132kV Ckt-1 Scheduled S/D from Manikganj 132/33kV end Due to
Annual Maintenance work.
09:36 |  | Juldah 100 MW PP Unit-3 (Acorn) Syncronized
09:39 | 16:51 | Baroirhat 132/33kV S/S TR-1, 406T LT Scheduled S/D Due to Annual maintenance work
09:50 | 15:36 | Jhenaidah-Magura 132 kV Ckt-1 Scheduled S/D from Magura 132/33kV end Due to Annual Maintenance
and from Jhenaidah 132/33kV end Due to Annual maintenance
09:51 | 16:48 | Barapukuria-Bogura 230 kV Ckt-1 Scheduled S/D from Barapukuria 230/132/33kV end Due to Annual Maintenance
09:53 |  | Anlima Energy Ltd. Syncronized
09:55 | 16:51 | Baroirhat 132/33kV S/S TR-1, 406T HT Scheduled S/D Due to Annual maintenance work
09:55 |  | Kaptai 7 MW Solar PP Syncronized
09:59 | 16:57 | Savar 132/33kV S/S T-1 LT Scheduled S/D Due to annual maintenance of T-1 Transformer
09:59 | 16:57 | Savar 132/33kV S/S T-1 HT Scheduled S/D Due to annual maintenance of T-1 Transformer
10:00 |  | Jangalia 33MW PP (Summit) Syncronized
10:03 | 11:55 | Brahmanbaria 132/33kV S/S 403T HT Forced S/D Due to maintenance work by PDB in TR-3 33 kv bus |  |  |  |  | 10.0MW load interruption.
10:03 | 11:55 | Brahmanbaria 132/33kV S/S 403T LT Forced S/D Due to maintenance work by PDB in TR-3 33 kv bus
10:05 |  | Chandpur 200MW (Desh energy) Syncronized
10:07 | 14:51 | Madanganj 132/33kV S/S Madanganj -Haripur 132 kv Ckt-2 Scheduled S/D
10:09 | 14:51 | Haripur 230/132kV S/S Madanganj-2 Scheduled S/D Due to For Annual maintanance Work.
10:10 |  | Ashuganj 150MW PP (Midland) Syncronized
10:10 | 16:40 | Tongi 230/132/33kV S/S 230 kV Bus-1 Scheduled S/D Due to Annual maintenance
10:11 | 18:55 | HVDC Bheramera- Ishwardi 230kV Ckt-3 Scheduled S/D from BIPTC end Due to Shutdown is taken
from Ishurdi end for Annual maintenance
10:15 |  | Karnaphuli Power Ltd. Syncronized
10:18 |  | Juldah 100 MW PP Unit-3 (Acorn) Shutdown
10:20 |  | Juldah 100 MW Unit-1 (Acorn) Syncronized
10:24 |  | Anwara 300 MW PP (United) Syncronized
10:26 |  | Chowmuhani 113 MW Syncronized
10:30 |  | Cox'sbazar-Dohazari 132 kV Ckt-1 Scheduled S/D from Coxsbazar 132/33kV end Due to Annual maintenance
10:32 |  | Chandpur 115(Doreen) Syncronized
10:37 | 14:49 | Maniknagar-Siddhirganj 230kV Ckt-1 Scheduled S/D from Siddhirganj 230/132kV end Due to Due to
annual maintenance
10:42 |  | Kodda 300 MW PP Unit-2 (Summit) Syncronized
10:49 | 15:10 | Kabirpur 132/33kV S/S Reserve bus Scheduled S/D Due to Annual maintenance
10:50 |  | Summit Power Madhabdi Control Room Syncronized
10:52 |  | Madanganj 102 PP(Summit) Syncronized
11:01 |  | Manikgonj 162MW PP(MPGL) Syncronized
11:01 |  | Madanganj-55 MW PP(Summit) Syncronized
11:08 |  | Matarbari 2*600 MW (CPGCL) Syncronized
11:21 |  | Jodiac Power Syncronized
11:32 |  | Meghnaghat 104 MW PP (OPCL) Syncronized
11:39 |  | Mirsharai 150 MW Syncronized
11:47 |  | Sikalbaha 105 MW PP (Baraka Sikalbaha) Syncronized
11:50 |  | Manikganj 55 MW PP (Northern) Syncronized
12:00 |  | Day peak generation: 8833 MW.
12:04 |  | Tangail Palli Power Gen 22 MW Syncronized
12:06 |  | Adani Power Jharkhanda Ltd Syncronized with remarks:- unit-1
12:10 | 16:40 | Bhaluka 132/33kV S/S Bus B Scheduled S/D Due to Annual maintenance
12:12 | 15:55 | Bhaluka-Mymensingh 132 kV Ckt-1 Scheduled S/D from Bhaluka 132/33kV end Due to Annual maintenance
12:17 | 16:20 | Bhaluka 132/33kV S/S Transformer- 01 HT Scheduled S/D Due to Annual maintenance
12:17 | 16:20 | Bhaluka 132/33kV S/S Transformer- 01 LT Scheduled S/D Due to Annual maintenance
12:22 |  | Siddhirganj 100 PP(Dutch Bangla) Syncronized
12:51 |  | Meghnaghat 100 MW(IEL) Syncronized
13:04 |  | Chandpur 200MW (Desh energy) Shutdown
13:05 |  | Patenga 50MW PP (Baraka) Syncronized
13:38 |  | Mirsharai 150 MW Shutdown
14:08 |  | Teknaf 20MW PP (Solartech) Shutdown
14:14 |  | Teknaf 20MW PP (Solartech) Syncronized
14:18 |  | Siddhirganj 100 PP(Dutch Bangla) Shutdown
14:22 |  | Juldah 100 MW Unit-1 (Acorn) Shutdown
| 14:24 | Chattak-Sylhet 132 kV Ckt-2 is restored.
| 14:26 | Jhenaidah 132/33kV S/S Transformer T-1 LT is restored.
| 14:26 | Jhenaidah 132/33kV S/S Transformer T-1 HT is restored.
| 14:27 | Jhenaidah 132/33kV S/S Transformer T-2 HT is restored.
| 14:27 | Jhenaidah 132/33kV S/S Transformer T-2 LT is restored.
14:28 |  | Confidence Power Bogura Unit-1 113 MW Shutdown
14:33 |  | Energypac Power Venture Thakurgaon Ltd. Shutdown
14:33 |  | Meghnaghat 100 MW(IEL) Shutdown
14:48 |  | Kodda 300 MW PP Unit-2 (Summit) Shutdown
14:54 |  | Meghnaghat 104 MW PP (OPCL) Shutdown
14:58 |  | Manikgonj 162MW PP(MPGL) Shutdown
15:01 |  | Madanganj 102 PP(Summit) Shutdown
15:03 |  | Madanganj-55 MW PP(Summit) Shutdown
15:07 |  | Chowmuhani 113 MW Shutdown
15:37 |  | Kanchan Purbachal Power Generation Ltd. Tripped
15:41 | 16:50 | Madaripur 132/33kV S/S T3-426T LT Forced S/D Due to Unexpected sound
15:42 | 16:46 | Madaripur 132/33kV S/S T3-426T HT Forced S/D Due to Unexpected sound
| 15:44 | Patuakhali 132/33kV S/S 425T (T-3) HT is restored.
15:45 |  | Rangpur 113 MW PP (Confidence) Shutdown
| 15:47 | Patuakhali 132/33kV S/S 425T (T-3) LT is restored.
15:50 |  | Kanchan Purbachal Power Generation Ltd. Syncronized
16:02 | 16:14 | Candpur (Desh)- Chandpur 132kV Ckt-2 Scheduled S/D from Chandpur 132/33kV end Due to
Black start operation
16:02 | 16:14 | Chandpur 132/33kV S/S 100MW(GT) Power Plant Incomer (T4) Scheduled S/D Due to Black Start operation
16:02 |  | Narshingdi 22 MW PP (Doreen) Syncronized
| 16:05 | Ishwardi-Natore 132kV Ckt-1 is restored.
| 16:05 | Agargaon 230/132kV S/S 132kV Transformer-1 (405T1) LT is restored.
| 16:08 | Baghabari-Sirajganj 132 kV Ckt-1 is restored.
16:33 |  | Kaptai 7 MW Solar PP Shutdown
16:34 |  | Chowmuhani 113 MW Syncronized
16:36 |  | Manikgonj 162MW PP(MPGL) Syncronized
16:38 |  | Kamalaghat 54 MW PP(Banco Energy) Syncronized
16:39 |  | Bagura 113 MW PP (Confidence)-2 Syncronized
16:44 |  | Nababganj 55 MW PP (Southern power ) Syncronized
16:49 |  | Mirsharai 150 MW Syncronized
| 16:50 | Madaripur 132/33kV S/S T3-426T LT is restored.
16:50 |  | Fenchuganj 44MW (Energyprima) Syncronized
16:50 |  | Meghnaghat 104 MW PP (OPCL) Syncronized
16:55 |  | Rangpur 113 MW PP (Confidence) Syncronized
16:55 |  | Teknaf 20MW PP (Solartech) Shutdown
16:55 |  | Confidence Power Bogura Unit-1 113 MW Syncronized
16:57 |  | Jangalia 52 MW PP (Lakdanavi) Syncronized
16:58 |  | Feni Lanka Power Syncronized
16:59 |  | Energypac Power Venture Thakurgaon Ltd. Syncronized
16:59 |  | Energypac Power Venture Thakurgaon Ltd. Shutdown
17:01 |  | Madanganj-55 MW PP(Summit) Syncronized
17:01 |  | Kodda 300 MW PP Unit-2 (Summit) Syncronized
17:02 |  | Teknaf 20MW PP (Solartech) Syncronized
17:08 |  | Teknaf 20MW PP (Solartech) Shutdown
17:10 |  | Chandpur 200MW (Desh energy) Syncronized
17:10 |  | Sirajgonj 6.55 MW Solar Shutdown
17:14 |  | Teesta Solar Limited Shutdown
17:14 |  | Mongla Orion 100 MW Solar PP Shutdown
17:15 |  | Sympa Solar Power 8 MW Shutdown
17:15 |  | Spectra Solar Plant Ltd. Shutdown
17:24 |  | Shahjahanulla 25 MW PP Syncronized
17:27 |  | Sutiakhali 50 MW Solar PP Shutdown
17:38 |  | Intraco Solar 30 MW Shutdown
17:39 |  | Dohazari -Kalaish 100 MW Peaking Syncronized
17:45 |  | Sonargaon 132/33kV S/S Tr-2 LT Forced S/D Due to Corrective Maintenance of 33 KV CT at B Phase |  |  |  |  | 30.0MW load interruption.
(Transformer-2) for Oil Leakage
17:46 |  | Sonargaon 132/33kV S/S Tr-2 HT Forced S/D Due to Corrective Maintenance of 33 KV CT at B Phase
(Transformer-2) for Oil Leakage
17:58 |  | Sarishabari 3 MW Solar Plant Shutdown
18:00 |  | Evening Peak Gen. 10636 MW
18:17 |  | Kodda 300 MW PP Unit-2 (Summit) Shutdown
18:19 |  | Feni Lanka Power Shutdown
18:22 |  | Jangalia 52 MW PP (Lakdanavi) Shutdown
18:30 |  | Maona 33 MW PP(Summit) Syncronized
18:37 |  | Mirsharai 150 MW Shutdown
18:52 |  | Meghnaghat 104 MW PP (OPCL) Shutdown
18:54 |  | Madanganj-55 MW PP(Summit) Shutdown
18:58 |  | Tangail Palli Power Gen 22 MW Shutdown
19:03 |  | Energypac Power Venture Thakurgaon Ltd. Shutdown
19:08 |  | Confidence Power Bogura Unit-1 113 MW Shutdown
19:08 |  | Bhairob 54.5 MW Shutdown
19:09 |  | Kanchan Purbachal Power Generation Ltd. Shutdown
19:10 |  | Rupganj 33 MW PP(Summit) Syncronized
19:14 |  | Bagura 113 MW PP (Confidence)-2 Shutdown
19:21 |  | Kanchan Purbachal Power Generation Ltd. Syncronized
19:29 |  | Rangpur 113 MW PP (Confidence) Shutdown
19:29 |  | Jamalpur 115 MW PP (United) Shutdown
19:30 |  | Nababganj 55 MW PP (Southern power ) Shutdown
19:37 |  | Manikganj 55 MW PP (Northern) Shutdown
19:46 |  | Manikgonj 162MW PP(MPGL) Shutdown
20:20 |  | Chowmuhani 113 MW Shutdown
20:28 |  | Bhola 225 MW CCPP Syncronized with remarks:- GT-1
20:48 |  | Ashuganj 150MW PP (Midland) Shutdown
21:55 |  | Anwara 300 MW PP (United) Shutdown
21:56 |  | Kamalaghat 54 MW PP(Banco Energy) Shutdown
22:06 |  | Jodiac Power Shutdown
| 22:08 | Gulsan-Rampura 132kV Ckt-1 is restored.
| 22:08 | Gulsan-Rampura 132kV Ckt-1 is restored.
| 22:11 | Rampura 230/132kV S/S Aux Transformer-03 LT is restored.
| 22:11 | Rampura 230/132kV S/S Aux Transformer-03 HT is restored.
22:37 |  | Dohazari -Kalaish 100 MW Peaking Shutdown
22:48 |  | Kanchan Purbachal Power Generation Ltd. Shutdown
23:05 |  | Chandpur 115(Doreen) Shutdown
23:07 |  | Sikalbaha 105 MW PP (Baraka Sikalbaha) Shutdown
23:40 |  | Ghorashal 108 MW PP (Regent) Shutdown
23:47 |  | Mymensingh 200 MW PP (United) Shutdown
23:58 |  | Patenga 50MW PP (Baraka) Shutdown
00:13 |  | Chandpur 200MW (Desh energy) Shutdown
00:21 |  | Anlima Energy Ltd. Shutdown
00:22 |  | Karnaphuli Power Ltd. Shutdown
03:54 |  | Feni 11 MW PP (Doreen) Shutdown
04:30 |  | Feni 11 MW PP (Doreen) Syncronized
05:00 |  | Minimum generation: 7314 MW.
05:58 |  | Ghorashal 108 MW PP (Regent) Syncronized
06:15 |  | Teknaf 20MW PP (Solartech) Syncronized
06:16 |  | Kaptai 7 MW Solar PP Syncronized
06:17 |  | Sutiakhali 50 MW Solar PP Syncronized
06:19 |  | Rangamati 132/33kV S/S Power Transformer TR1 (405T) HT Forced S/D Due to T1(404T) X-former
secondary breaker(407B) is off due to R-phase current not show.
06:23 |  | Mongla Orion 100 MW Solar PP Syncronized
06:25 |  | Spectra Solar Plant Ltd. Syncronized
06:30 |  | Sympa Solar Power 8 MW Syncronized
06:31 |  | Sarishabari 3 MW Solar Plant Syncronized
06:32 |  | Intraco Solar 30 MW Syncronized
06:34 |  | Sirajgonj 6.55 MW Solar Syncronized
06:41 |  | Teesta Solar Limited Syncronized
07:14 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) LT Scheduled S/D Due to Annual Maintenance
07:15 |  | Kabirpur - Manikganj 132kV Ckt-2 Scheduled S/D from Manikganj 132/33kV end Due to Annual Maintenance
07:15 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) HT Scheduled S/D Due to Annual Maintenance
07:20 |  | Hasnabad 230/132kV S/S AUTO TR-2 LT Scheduled S/D Due to Annual maintenance
07:20 |  | Hasnabad 230/132kV S/S AUTO TR-2 HT Scheduled S/D Due to Annual maintenance
07:25 |  | Mymensingh 200 MW PP (United) Syncronized
07:42 |  | Jamalpur 115 MW PP (United) Syncronized
07:45 |  | Kabirpur-Kaliakoir 132kV Ckt-2 Scheduled S/D from Kabirpur 132/33kV end Due to Annual maintenance
07:47 |  | Jhenaidah-Magura 132 kV Ckt-1 Scheduled S/D from Magura 132/33kV end Due to Annual
Maintenance of Jhe. Mag. Ckt.-1

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-12-02 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4328100
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 72 | 1476181 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 357 | 9189370 | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 390 | 8293500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 0 | 12480 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 102102 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 25 | 120591 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 13 | 200664 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 0 | 14486 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 277 | 6700530 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 94500 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 48 | 832800 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 132449 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 88401 | Low demand
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 30 | 779520 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 0 | 301000 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 0 | 338100 | 33 kV feeder problem.
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 17 | 200069 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 55 | 243382 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 46 | 767808 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 917760
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 27 | 104640 | Low demand
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 241920 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 188894
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 237240 | Low demand
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5422 | 1782 | 35906487
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 0 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 49680
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 17 | 150240 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 86 | 2064000 | Unit-2 under maint.
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 192 | 4638323 | Machine problem
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 195709 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 80710 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 40560 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 7680 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 13 | 278832 | Fuel shortage
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 0 | 336000
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 19297
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 115 | 790364 | Low demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 285634 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 237526 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Low demand
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 242127 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 0 | 0 | Fuel shortage
| SS Power I |  | SS Power | 2*612 | 1224 | 491 | 10925453
| Cox's Bazar Wind |  | IPP | 66 | 0 | 4 | 46560 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 505 | 550545 | On test.
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 17 | 46836
| Chattogram area Total |  |  |  | 3769 | 1544 | 20986076
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 0 | Under maint.
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7482200 | Under maint.
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 393 | 8700500
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 41 | 1015344
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 0 | 25 | 688800
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 170 | 2258182 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 942668
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 92 | 543636 | Low demand
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 11 | 304320 | Low demand
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 428940 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 201960
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 118 | 2442240
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 762300 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 14 | 20362 | Low demand
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 10 | 237230 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 20520 | Low demand
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 42 | 246120 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 207720 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 51 | 272640 | Fuel shortage
| Cumilla Area Total |  |  |  | 2896 | 1421 | 26775682
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 68 | 1850880 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Contract Expired
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12600
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 93 | 664800 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 85 | 608400 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 270340
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 39840 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 252 | 3446860
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1016000
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 28 | 652440 | Engine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 25 | 320400 | Gas shortage
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 25 | 271080 | Gas shortage
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 3 | 127210 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under maint.
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 40 | 860160 | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 126 | 3086870 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 155000 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7063000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 368 | 8350000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 194580
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9402900
| Sylhet Area Total |  |  |  | 2427 | 1374 | 31499640
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 443 | 12397818
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 0 | Reserve
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Reserve
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 462240
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | Fuel shortage
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 623 | 11156360
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 1066 | 24016418
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 16 | 333200 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 64 | 1780000
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1210 | 25430700
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5344364
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve
| Barisal 307 MW |  | IPP | 307*1 | 307 | 286 | 4647300 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1796 | 37535564
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 306 | 8556000
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 237366
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 122880 | Low demand
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 1047168 | Low demand
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 29340
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 739 | 6136727
| Rajshahi Area Total |  |  |  | 3631 | 1126 | 16129481
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4136500 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 413097 | Low demand
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 31908
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 35 | 278016 | Low demand
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 177213
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 914190
| Rangpur Area Total |  |  |  | 950 | 275 | 5950924
| Total |  |  |  | 25211 | 10636 | 202247132
| Eastern Grid Total |  |  |  | 15128 | 6373 | 118614745
| Western Grid Total |  |  |  | 10083 | 4263 | 83632387
| National Grid Total |  |  |  | 25211 | 10636 | 202247132
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-12-02
| (a) ENTIRE EASTERN GRID : |  | 7016.33 | MW | (b) ENTIRE WESTERN GRID : |  | 3101 | MW
| i) Dhaka area |  | 3797.13 | MW | i) Khulna area |  | 1173.4 | MW
| ii) Chittagong area |  | 1151.2 | MW | ii) Rajshahi area |  | 970.3 | MW
| iii) Comilla area |  | 894 | MW | iii) Barisal area |  | 277.3 | MW
| iv) Mymensingh area |  | 799 | MW | iv) Rangpur area |  | 680 | MW
| v) Sylhet area |  | 375 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10117.33 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 21 | 19:30 | Kamrangirchar | 39 | 13:00 | Narinda | 48 | 17:00 | Sherpur | 104 | 18:00
2 | AKSML | 15 | 20:00 | Chowmuhani | 142 | 20:00 | Kaptai | N/A | N/A | Narshingdi | 144 | 18:30 | Shikalbaha | 22 | 17:00
3 | Aftabnagar | 28 | 13:00 | Chuadanga | 66 | 18:30 | Kazla | 80 | 13:00 | Natore | 94 | 18:00 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 69 | 13:00 | Coxsbazar | 111 | 18:00 | Keranigonj | 54 | 13:00 | Nawabganj | 34.2 | 21:00 | Shitalakhya | 88.7 | 12:00
5 | Agrabad | 54 | 18:00 | Cumilla(N) | 102 | 14:00 | Khagrachori | 22 | 18:00 | Netrakona | 90 | 18:00 | Sholosohor | 37 | 17:00
6 | Amnura | 33 | 18:30 | Cumilla(S) | 126 | 17:00 | Khulna | 56 | 13:00 | New | 56.6 | 12:00 | Shyampur | 148 | 11:00
7 | Ashuganj | 51 | 18:00 | Daudkandi | 112 | 18:00 | Khulshi | 151 | 15:00 | Niamatpur | 49 | 18:00 | Siddhirganj | 100 | 12:00
8 | BIPTC | N/A | N/A | Dhaka | 20 | 12:00 | Kishoreganj | 100 | 21:00 | Noapara | 37 | 18:00 | Sirajganj | 74 | 18:00
9 | BSRM | 114 | 18:30 | Dhamrai | 112 | 17:00 | Kodda | 256 | 18:00 | PHP | 5 | 05:00 | Sonargaon | 85 | 12:00
10 | Bagerhat | 65 | 18:00 | Dhanmondi | 105 | 13:00 | Kulaura | 28 | 18:00 | Pabna | 77 | 18:00 | Sreemongol | 47 | 18:00
11 | Bakulia | 79 | 19:00 | Dohazari | 53 | 18:30 | Kurigram | 49 | 18:00 | Palashbari | 76 | 18:00 | Sreepur | 59 | 17:00
12 | Banani | 21 | 14:00 | Faridpur | 106 | 21:00 | Kushtia | 105 | 18:00 | Panchagarh | 43 | 18:00 | Srinagar | 28.6 | 20:00
13 | Bangabhaban | 6 | 11:00 | Fatullah | 58 | 12:00 | Lalbag | 70 | 12:00 | Patuakhali | 55.8 | 20:00 | Sunamganj | 35 | 18:30
14 | Barapukuria | 47 | 18:00 | Fenchuganj | 25 | 17:00 | Lalmonirhat | 37 | 18:00 | Payra | 20 | 18:30 | Sylhet | 10 | 00:00
15 | Barguna | 12 | 18:30 | Feni | 89 | 18:00 | MI_Cement | 18 | 21:00 | Postogola | 45 | 12:00 | Sylhet-132 | 99 | 18:30
16 | Barishal | 74 | 18:00 | GPH | 96 | 19:00 | Madanganj | 23 | 00:00 | Purbachal | 14 | 13:00 | TK | 22 | 18:00
17 | Barishal-230 | 60 | 19:30 | Ghorashal | 48 | 18:00 | Madaripur | 53 | 19:30 | Purbasadipur | 96 | 18:00 | Tangail | 144 | 18:00
18 | Baroaulia | 53 | 11:00 | Goalpara | 26 | 19:00 | Madartek | 59.05 | 19:30 | Rahim | 48 | 13:00 | Thakurgaon | 73 | 18:00
19 | Baroirhat | 36 | 17:00 | Gollamari | 49 | 12:00 | Madunaghat | 36 | 18:00 | Rajbari | 46 | 18:30 | Tongi | 86 | 11:00
20 | Bashundhara | 118 | 13:00 | Gopalganj | 65.4 | 18:00 | Magura | 45 | 18:00 | Rajendrapur | 76 | 18:00 | Ullon | 42 | 13:00
21 | BashundharaCement | 6 | 12:00 | Gulshan | 74 | 13:00 | Mahasthangarh | 56 | 18:00 | Rajshahi | 103 | 18:00 | Uttara | 53 | 18:00
22 | Beanibazar | 42 | 18:00 | Halishahar | 94 | 15:00 | Manikganj | 73 | 18:30 | Rajshahi-230 | 18 | 00:00 | UttaraNew | 43 | 14:00
23 | Benapole | 42 | 18:00 | HaripurSBU | 162 | 13:00 | Maniknagar | 56 | 13:00 | Ramganj | 70 | 17:00 | Zigatola | 82 | 18:00
24 | Bhaluka | 116 | 18:30 | Hasnabad | 66 | 18:00 | Matarbari | 38 | 23:00 | Rampur | 32 | 11:00
25 | Bhandaria | 34 | 21:00 | Hathazari | 53 | 13:00 | Matuail | 58 | 17:00 | Rangamati | 13 | 18:00
26 | Bhangura | 20 | 18:00 | Ishurdi | 55 | 18:00 | Millgate | 95 | 12:00 | Rangpur | 103 | 18:00
27 | Bheramara(GK) | 39 | 18:00 | Jaldhaka | 52 | 18:30 | Mirpur | 105 | 18:00 | Ruppur | 3.2 | 15:00
28 | Bhulta | 206 | 21:00 | Jamalpur | 108 | 18:00 | Mirsorai | 3 | 18:00 | SSM | 11 | 22:00
29 | Bog-Sherpur | 50 | 18:00 | Jashore | 94 | 18:00 | Mirzapur | 14.64 | 18:00 | Saidpur | 86 | 18:00
30 | Bogura | 104 | 18:00 | Jhenaidah | 102 | 18:00 | Mithapukur | 32 | 18:30 | Satkhira | 83 | 18:00
31 | Borhanuddin | 39 | 20:00 | Joydebpur | 123 | 21:00 | Modern | 0 | 00:00 | Satmasjid | 80 | 13:00
32 | Brahmanbaria | 112 | 18:00 | Joypurhat | 42 | 07:00 | Mogbazar | 76.3 | 13:00 | Savar | 134 | 18:00
33 | Cantonment | 104 | 13:00 | Juldah | 18 | 00:00 | Mongla | 27 | 12:00 | SevenRings | 11.12 | 11:00
34 | Chandpur | 45 | 18:00 | KSRM | 33 | 19:00 | Motijheel | 32 | 13:00 | ShahCement | 35 | 00:00
35 | Chandraghona | 26 | 17:00 | Kabirpur | 234 | 12:00 | Munshiganj | 70 | 14:00 | Shahjadpur | 64 | 18:00
36 | Chapai | 47 | 18:30 | Kachua | 44 | 18:00 | Mymensingh | 161 | 18:00 | Shahjibazar | 81 | 20:00
37 | Charsaidpur | 20 | 00:00 | Kallyanpur | 68 | 18:00 | Naogaon | 96 | 18:00 | Shahmirpur | 43.2 | 18:00
38 | Chauddagram | 38 | 18:00 | Kalurghat | 46 | 12:00 | Narail | 38 | 18:00 | Shariatpur | 56 | 20:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-12-02 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 403 | 03:00 | 385 | 16:00 | Gopalganj | 411 | 05:00 | 393 | 18:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 393 | 04:00 | 238 | 05:00
| Bhulta | 414 | 05:00 | 399 | 16:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 409 | 13:00 | 401 | 16:00 | Payra | 417 | 05:00 | 407 | 17:00
| BIPTC | 408 | 04:00 | 394 | 18:00 | Rahanpur | 417 | 01:00 | 394 | 05:00
| Bogura | N/A | N/A | N/A | N/A | Rampal | 410 | 02:00 | 397 | 18:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 237 | 03:00 | 225 | 16:00 | Hasnabad | 237 | 05:00 | 227 | 16:00
| AKSML | 226 | 06:00 | 220 | 15:00 | Hathazari | 226 | 06:00 | 217 | 16:00
| Aminbazar | 241 | 04:00 | 229 | 15:00 | Ishurdi | 235 | 05:00 | 223 | 16:00
| Ashuganj | 234 | 05:00 | 226 | 16:00 | Jhenaidah | 236 | 05:00 | 222 | 16:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 238 | 04:00 | 227 | 16:00
| Baghabari | 229 | 06:00 | 220 | 16:00 | Keranigonj | 237 | 05:00 | 225 | 16:00
| Barapukuria | 226 | 02:00 | 216 | 19:30 | Khulna(S) | 242 | 02:00 | 228 | 18:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 242 | 03:00 | 238 | 11:00 | Maniknagar | 240 | 04:00 | 227 | 16:00
| Bheramara | 234 | 05:00 | 223 | 16:00 | Meghnaghat | 243 | 05:00 | 235 | 13:00
| Bhulta | 240 | 04:00 | 229 | 16:00 | Mirsorai | 229 | 05:00 | 219 | 16:00
| Bibiana | 235 | 02:00 | 228 | 16:00 | Rajshahi | 235 | 02:00 | 222 | 16:00
| BIPTC | 236 | 05:00 | 222 | 16:00 | Rampal | 238 | 02:00 | 225 | 18:00
| Bogura | 233 | 06:00 | 224 | 20:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 244 | 04:00 | 240 | 00:00 | Rampura | 238 | 05:00 | 227 | 16:00
| BSRM | 230 | 03:00 | 221 | 15:00 | Shikalbaha | 222 | 03:00 | 216 | 16:00
| Cumilla(N) | 234 | 05:00 | 220 | 17:00 | Shyampur | 238 | 05:00 | 226 | 16:00
| Fenchuganj | 234 | 00:00 | 231 | 15:00 | Siddhirganj | 241 | 04:00 | 230 | 16:00
| Ghorashal | 235 | 00:00 | 235 | 00:00 | Sirajgonj | 238 | 04:00 | 226 | 16:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 233 | 02:00 | 225 | 16:00
| GPH | 226 | 03:00 | 218 | 15:00 | Tongi | 237 | 04:00 | 222 | 15:00
| Haripur | 236 | 00:00 | 228 | 16:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 134 | 05:00 | 126 | 16:00 | Lalbag | 137 | 03:00 | 128 | 16:00
| Agargaon | 139 | 02:00 | 131 | 16:00 | Lalmonirhat | 131 | 13:00 | 121 | 19:30
| Agrabad | 132 | 03:00 | 127 | 14:00 | Madanganj | 134 | 01:00 | 128 | 15:00
| AKS | 130 | 00:00 | 126 | 14:00 | Madaripur | 134 | 00:00 | 131 | 16:00
| Aminbazar | 140 | 03:00 | 132 | 15:00 | Madartek | 134 | 05:00 | 126 | 17:00
| Amnura | 140 | 01:00 | 132 | 14:00 | Madunaghat | 132 | 00:00 | 128 | 14:00
| Ashuganj | 139 | 01:00 | 135 | 16:00 | Magura | 138 | 02:00 | 128 | 16:00
| Bagerhat | 132 | 01:00 | 120 | 18:00 | Mahasthangarh | 135 | 06:00 | 128 | 16:00
| Bakulia | 133 | 04:00 | 127 | 16:00 | Manikganj | 133 | 08:00 | 128 | 00:00
| Banani | 138 | 02:00 | 128 | 16:00 | Maniknagar | 137 | 04:00 | 128 | 11:00
| Bangabhaban | 136 | 03:00 | 129 | 16:00 | Matarbari | 128 | 12:00 | 122 | 22:00
| Barapukuria | 136 | 02:00 | 127 | 19:30 | Matuail | 135.5 | 06:00 | 128.4 | 16:00
| Barguna | 136 | 04:00 | 132 | 18:00 | Millgate | 138 | 01:00 | 128 | 16:00
| Barishal | 140 | 05:00 | 129 | 18:00 | Mirpur | 139 | 01:00 | 131 | 15:00
| Barishal-230 | 139 | 03:00 | 135 | 12:00 | Mirzapur | 134 | 04:00 | 128 | 15:00
| Baroaulia | 133 | 02:00 | 128 | 15:00 | Mithapukur | 135 | 18:30 | 124 | 18:00
| Baroirhat | 132 | 09:00 | 124 | 16:00 | MI_Cement | 136.1 | 06:00 | 129 | 16:00
| Bashundhara | 139 | 03:00 | 127 | 16:00 | Modern | 132 | 03:00 | 127 | 16:00
| BashundharaCement | 134 | 01:00 | 130 | 11:00 | Mogbazar | 135 | 05:00 | 127 | 16:00
| Beanibazar | 132 | 04:00 | 128 | 13:00 | Mongla | 132 | 03:00 | 121 | 18:00
| Benapole | 135 | 04:00 | 124 | 18:00 | Motijheel | 136 | 03:00 | 129 | 16:00
| Bhaluka | 132 | 00:00 | 128 | 16:00 | Munshiganj | 135 | 05:00 | 129 | 15:00
| Bhandaria | 136 | 09:00 | 128 | 19:30 | Mymensingh | 137 | 17:00 | 124 | 16:00
| Bhangura | 140 | 05:00 | 134 | 16:00 | Naogaon | 133 | 05:00 | 126 | 19:30
| Bheramara | 136 | 02:00 | 129 | 16:00 | Narail | 138 | 02:00 | 128 | 16:00
| Bheramara(GK) | 136 | 05:00 | 129 | 16:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 127 | 06:00 | 120 | 15:00 | Narshingdi | 129 | 00:00 | 120 | 13:00
| Bog-Sherpur | 136 | 02:00 | 130 | 16:00 | Natore | 136 | 02:00 | 129 | 16:00
| Bogura | 136 | 06:00 | 130 | 00:00 | Nawabganj | 137 | 03:00 | 129 | 15:00
| Bogura-230 | 138 | 05:00 | 130 | 16:00 | Netrakona | 134 | 12:00 | 125 | 01:00
| Brahmanbaria | 132 | 09:00 | 127 | 13:00 | New | 138 | 04:00 | 130 | 16:00
| Cantonment | 139 | 02:00 | 131 | 16:00 | Niamatpur | 132 | 01:00 | 126 | 16:00
| Chandpur | 132 | 12:00 | 122 | 16:00 | Noapara | 136 | 03:00 | 125 | 18:00
| Chandraghona | 135 | 12:00 | 128 | 16:00 | Pabna | 138 | 02:00 | 131 | 17:00
| Chapai | 140 | 00:00 | 131 | 10:00 | Palashbari | 135 | 02:00 | 124 | 18:00
| Charsaidpur | 136 | 04:00 | 129 | 15:00 | Panchagarh | 130 | 03:00 | 118 | 19:30
| Chauddagram | 134 | 09:00 | 125 | 16:00 | Patuakhali | 136 | 02:00 | 131 | 21:00
| Chhatak | 131 | 00:00 | 127 | 15:00 | Payra | 137 | 02:00 | 134 | 17:00
| Chowmuhani | 130 | 07:00 | 121 | 16:00 | PHP | 131 | 09:00 | 123 | 16:00
| Chuadanga | 137 | 03:00 | 127 | 16:00 | Postogola | 138 | 05:00 | 130 | 16:00
| Coxsbazar | 127 | 09:00 | 115 | 18:00 | Purbachal | 138 | 01:00 | 127 | 15:00
| Cumilla(N) | 136 | 07:00 | 128 | 16:00 | Purbasadipur | 131 | 03:00 | 120 | 09:00
| Cumilla(S) | 135 | 06:00 | 127 | 16:00 | Rahanpur | 142 | 02:00 | 131 | 12:00
| Daudkandi | 133 | 03:00 | 124 | 16:00 | Rahim | 135 | 01:00 | 132 | 10:00
| Dhaka | 134 | 04:00 | 126 | 16:00 | Rajbari | 135 | 03:00 | 127 | 16:00
| Dhamrai | 134 | 02:00 | 125 | 16:00 | Rajendrapur | 138 | 23:00 | 129 | 00:00
| Dhanmondi | 136 | 03:00 | 129.5 | 16:00 | Rajshahi | 137 | 03:00 | 129 | 16:00
| Dohazari | 131 | 08:00 | 127 | 15:00 | Rajshahi-230 | 138 | 02:00 | 130 | 12:00
| Faridpur | 134 | 03:00 | 128 | 13:00 | Ramganj | 131 | 19:00 | 118 | 16:00
| Fatullah | 137 | 03:00 | 130 | 15:00 | Rampur | 132 | 03:00 | 126 | 15:00
| Fenchuganj | 134 | 00:00 | 132 | 15:00 | Rampura | 135 | 05:00 | 127 | 15:00
| Feni | 130 | 07:00 | 125 | 16:00 | Rangamati | 133 | 03:00 | 128 | 15:00
| Ghorashal | 141 | 07:00 | 135 | 15:00 | Rangpur | 132 | 03:00 | 121 | 19:30
| Goalpara | 136 | 05:00 | 128 | 17:00 | Ruppur | 138 | 00:00 | 132 | 16:00
| Gollamari | 135 | 05:00 | 127 | 18:00 | Saidpur | 131 | 06:00 | 119 | 19:30
| Gopalganj | 134 | 02:00 | 128 | 16:00 | Satkhira | 134 | 04:00 | 123 | 18:00
| Gopalganj-400 | 135 | 05:00 | 129 | 16:00 | Satmasjid | 138 | 03:00 | 131 | 16:00
| Gulshan | 134 | 01:00 | 126 | 16:00 | Savar | 137 | 01:00 | 130 | 15:00
| Halishahar | 132 | 05:00 | 126 | 15:00 | SevenRings | 142 | 03:00 | 135 | 16:00
| Haripur | 135 | 01:00 | 129 | 16:00 | ShahCement | 136 | 04:00 | 129 | 15:00
| HaripurSBU | 135 | 01:00 | 132 | 10:00 | Shahjadpur | 144 | 03:00 | 140 | 00:00
| Hasnabad | 136 | 01:00 | 131 | 16:00 | Shahjibazar | 131 | 00:00 | 128 | 11:00
| Hathazari | 135 | 06:00 | 130 | 16:00 | Shahmirpur | 133 | 07:00 | 126 | 16:00
| Ishurdi | 139 | 02:00 | 132 | 16:00 | Shariatpur | 135 | 04:00 | 130 | 12:00
| Jaldhaka | 130 | 06:00 | 118 | 19:30 | Sherpur | 137 | 18:00 | 118 | 07:00
| Jamalpur | 138 | 14:00 | 118 | 07:00 | Shikalbaha | 122 | 05:00 | 117 | 15:00
| Jashore | 135 | 04:00 | 125 | 18:00 | Shikalbaha-230 | 134 | 03:00 | 129 | 16:00
| Jhenaidah | 139 | 04:00 | 130 | 16:00 | Shitalakhya | 136.3 | 06:00 | 129 | 16:00
| Jhenaidah-230 | 139 | 02:00 | 129 | 18:00 | Sholosohor | 133 | 03:00 | 127 | 16:00
| Joydebpur | 139 | 04:00 | 132 | 16:00 | Shyampur | 135 | 00:00 | 131 | 16:00
| Joypurhat | 133 | 06:00 | 125 | 18:00 | Shyampur-230 | 137 | 03:00 | 130 | 16:00
| Juldah | 134 | 07:00 | 127 | 16:00 | Siddhirganj | 134 | 01:00 | 129 | 16:00
| Kabirpur | 136 | 06:00 | 127 | 16:00 | Sirajganj | 138 | 04:00 | 129 | 16:00
| Kachua | 132 | 08:00 | 122 | 16:00 | Sonargaon | 135 | 06:00 | 129 | 11:00
| Kaliakoir | 141 | 05:00 | 131 | 15:00 | Sreemongol | 131 | 04:00 | 128 | 12:00
| Kallyanpur | 137 | 02:00 | 131 | 18:00 | Sreepur | 134 | 02:00 | 129 | 15:00
| Kalurghat | 132 | 03:00 | 127 | 15:00 | Srinagar | 137 | 04:00 | 129 | 15:00
| Kamrangirchar | 136 | 02:00 | 129 | 19:30 | SSM | 138 | 07:00 | 132 | 10:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 130 | 00:00 | 126 | 13:00
| Kazla | 137 | 05:00 | 128 | 16:00 | Sylhet | 132 | 00:00 | 129 | 10:00
| Keranigonj | 137 | 03:00 | 129 | 16:00 | Sylhet-132 | 131 | 00:00 | 129 | 15:00
| Khagrachori | 133 | 03:00 | 128 | 15:00 | Tangail | 134 | 14:00 | 127 | 16:00
| Khulna | 132 | 00:00 | 125 | 18:00 | Thakurgaon | 130 | 04:00 | 117 | 19:30
| Khulna(S) | 135 | 03:00 | 126 | 18:00 | TK | 133 | 02:00 | 130 | 16:00
| Khulshi | 131 | 09:00 | 125 | 16:00 | Tongi | 137 | 04:00 | 132 | 15:00
| Kishoreganj | 134 | 02:00 | 129 | 16:00 | Ullon | 134 | 06:00 | 126 | 16:00
| Kodda | 139 | 22:00 | 129 | 00:00 | Uttara | 139 | 02:00 | 131 | 15:00
| KSRM | 132 | 03:00 | 126 | 16:00 | UttaraNew | 137 | 01:00 | 127 | 16:00
| Kulaura | 134 | 01:00 | 130 | 15:00 | Zigatola | 136 | 04:00 | 129 | 16:00
| Kurigram | 133 | 04:00 | 120 | 19:30
| Kushtia | 137 | 02:00 | 130 | 16:00

## L-Curve
Date | 2023-12-02
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 270 | 5179 | 3531 | 8710 |  |  |  | QF-LDC-11
0:30 | 265 | 4835.5 | 3364 | 8199.5 | Date: | 2023-12-02
1:00 | 260 | 4492 | 3197 | 7689
1:30 | 288 | 4473.5 | 3059.5 | 7533
2:00 | 316 | 4455 | 2922 | 7377
2:30 | 310 | 4339 | 2880 | 7219 | [5 empty] | Gen. at Eve. Peak | 10636 | 10636 MW (18:00 )
3:00 | 304 | 4223 | 2838 | 7061 | [6 empty] | 18:00
3:30 | 287 | 4187.5 | 2794.5 | 6982 | [5 empty] | Gen. at Day Peak | 8833 | 8833 MW (12:00 )
4:00 | 270 | 4152 | 2751 | 6903 | [6 empty] | 12:00
4:30 | 267 | 4135.5 | 2753 | 6888.5 | [5 empty] | Highest Generation | 10636
5:00 | 264 | 4119 | 2755 | 6874 | [6 empty] | 18:00
5:30 | 242 | 4226 | 2757 | 6983
6:00 | 220 | 4333 | 2759 | 7092
6:30 | 165 | 4509 | 2795.5 | 7304.5
7:00 | 110 | 4685 | 2832 | 7517
7:30 | 122 | 4751 | 2962.5 | 7713.5
8:00 | 134 | 4817 | 3093 | 7910
8:30 | 122 | 4742.5 | 3067 | 7809.5
9:00 | 110 | 4668 | 3041 | 7709
9:30 | 98 | 4698.5 | 3077.5 | 7776
10:00 | 86 | 4729 | 3114 | 7843
10:30 | 80.5 | 4818.5 | 3178.5 | 7997
11:00 | 75 | 4908 | 3243 | 8151
11:30 | 88.5 | 5152.5 | 3339.5 | 8492
12:00 | 102 | 5397 | 3436 | 8833
12:30 | 106 | 5452.5 | 3532.5 | 8985
13:00 | 110 | 5508 | 3629 | 9137
13:30 | 142.5 | 5465.5 | 3575.5 | 9041
14:00 | 175 | 5423 | 3522 | 8945
14:30 | 188.5 | 5451.5 | 3376.5 | 8828
15:00 | 202 | 5480 | 3231 | 8711
15:30 | 180 | 5475.5 | 3202.5 | 8678
16:00 | 158 | 5471 | 3174 | 8645
16:30 | 152 | 5568.5 | 3366.5 | 8935
17:00 | 146 | 5666 | 3559 | 9225
17:30 | 151 | 6019.5 | 3911 | 9930.5
18:00 | 156 | 6373 | 4263 | 10636
18:30 | 202 | 6346 | 4176 | 10522
19:00 | 248 | 6319 | 4089 | 10408
19:30 | 250 | 6053 | 4145 | 10198
20:00 | 150 | 6043 | 4094 | 10137 |  |  |  | Executive Engineer
20:30 | 130 | 5885.5 | 4155.5 | 10041 |  |  |  | Network Operation Division
21:00 | 110 | 5728 | 4217 | 9945
21:30 | 145 | 5568 | 4139.5 | 9707.5
22:00 | 180 | 5408 | 4062 | 9470 |  |  |  |  | Page 6 of 7
22:30 | 220 | 5367.5 | 3912.5 | 9280
23:00 | 260 | 5327 | 3763 | 9090
23:30 | 265 | 5253 | 3647 | 8900
24:00 | 270 | 5179 | 3531 | 8710
10636 MW (18:00 )
8833 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-12-02 |  | Energy |  | 202247132
QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3016 | 444 | 1490 | 0 | 118 | 3414 | 86 | 0 | 32 | 100 | 0 | 10 | 0
0:30 | 3051.5 | 682 | 1496 | 0 | 59 | 2703 | 86 | 0 | 16 | 100 | 0 | 6 | 0 |  | Date: | 43800
1:00 | 3087 | 920 | 1502 | 0 | 0 | 1992 | 86 | 0 | 0 | 100 | 0 | 2 | 0
1:30 | 3084.5 | 825 | 1504.5 | 0 | 0 | 1937 | 86 | 0 | 0 | 95 | 0 | 1 | 0 | [8 empty] | Total Energy | 202.2471 | 202.2471 | Total Energy Gen 202.247 MKWHr Energy Not Served 0.362 MKWHr Energy Requirement 202.609 MKWHr
2:00 | 3082 | 730 | 1507 | 0 | 0 | 1882 | 86 | 0 | 0 | 90 | 0 | 0 | 0 | [8 empty] | Energy not Served | 0.3616 | 0.3616
2:30 | 3046.5 | 706 | 1426 | 0 | 0 | 1864.5 | 86 | 0 | 0 | 89 | 0 | 1 | 0 | [8 empty] | Energy Requirement | 202.6087 | 202.6087
3:00 | 3011 | 682 | 1345 | 0 | 0 | 1847 | 86 | 0 | 0 | 88 | 0 | 2 | 0
3:30 | 2980 | 682 | 1322.5 | 0 | 0 | 1818.5 | 86 | 0 | 0 | 88 | 0 | 5 | 0 | [7 empty] | Shortage
4:00 | 2949 | 682 | 1300 | 0 | 0 | 1790 | 86 | 0 | 0 | 88 | 0 | 8 | 0
4:30 | 2931 | 682 | 1301.5 | 0 | 0 | 1792 | 86 | 0 | 0 | 90 | 0 | 6 | 0
5:00 | 2913 | 682 | 1303 | 0 | 0 | 1794 | 86 | 0 | 0 | 92 | 0 | 4 | 0
5:30 | 2961 | 642 | 1388.5 | 0 | 17.5 | 1794 | 86 | 0 | 0 | 90 | 0 | 4 | 0
6:00 | 3009 | 602 | 1474 | 0 | 35 | 1794 | 86 | 0 | 0 | 88 | 0 | 4 | 0
6:30 | 3053 | 521 | 1563.5 | 0 | 100 | 1869.5 | 86 | 0 | 16 | 83 | 9.5 | 3 | 0 | [6 empty] | Coal
7:00 | 3097 | 440 | 1653 | 0 | 165 | 1945 | 86 | 0 | 32 | 78 | 19 | 2 | 0
7:30 | 3082 | 439.5 | 1634.5 | 0 | 193 | 2080 | 86 | 0 | 40 | 85 | 72.5 | 1 | 10.0275 | [5 empty] | Oil
8:00 | 3067 | 439 | 1616 | 0 | 221 | 2215 | 86 | 0 | 48 | 92 | 126 | 0 | 20.055
8:30 | 2978.5 | 438.5 | 1569.5 | 0 | 243.5 | 2171 | 86 | 0 | 48 | 97 | 177.5 | 0 | 39.155
9:00 | 2890 | 438 | 1523 | 0 | 266 | 2127 | 86 | 0 | 48 | 102 | 229 | 0 | 58.255
9:30 | 2885 | 438 | 1572 | 0 | 305.5 | 2103 | 86 | 0 | 48 | 99 | 239.5 | 0 | 43.93
10:00 | 2880 | 438 | 1621 | 0 | 345 | 2079 | 86 | 0 | 48 | 96 | 250 | 0 | 29.605
10:30 | 2948 | 438 | 1599 | 0 | 375.5 | 2134.5 | 86 | 0 | 48 | 90 | 278 | 0 | 29.605
11:00 | 3016 | 438 | 1577 | 0 | 406 | 2190 | 86 | 0 | 48 | 84 | 306 | 0 | 29.605
11:30 | 3035.5 | 437.5 | 1608.5 | 0 | 539.5 | 2335.5 | 86 | 0 | 48 | 91 | 310.5 | 0 | 29.8025
12:00 | 3055 | 437 | 1640 | 0 | 673 | 2481 | 86 | 0 | 48 | 98 | 315 | 0 | 30
12:30 | 3032.5 | 440.5 | 1635 | 0 | 743.5 | 2570 | 86 | 0 | 48 | 101 | 328.5 | 0 | 41.2625
13:00 | 3010 | 444 | 1630 | 0 | 814 | 2659 | 86 | 0 | 48 | 104 | 342 | 0 | 52.525
13:30 | 3010 | 444 | 1630 | 0 | 814 | 2659 | 86 | 0 | 48 | 104 | 342 | 0 | 52.525
14:00 | 3010 | 444 | 1630 | 0 | 814 | 2659 | 86 | 0 | 48 | 104 | 342 | 0 | 52.525
14:30 | 2965 | 443.5 | 1573 | 0 | 583.5 | 2852.5 | 86 | 0 | 48 | 107 | 265.5 | 0 | 52.0475
15:00 | 2920 | 443 | 1516 | 0 | 353 | 3046 | 86 | 0 | 48 | 110 | 189 | 0 | 51.57
15:30 | 2938.5 | 443.5 | 1535.5 | 0 | 301 | 3078.5 | 86 | 0 | 48 | 115 | 132 | 0 | 52.0475
16:00 | 2957 | 444 | 1555 | 0 | 249 | 3111 | 86 | 0 | 48 | 120 | 75 | 0 | 52.525
16:30 | 2914.5 | 443.5 | 1609.5 | 0 | 387.5 | 3284 | 86 | 0 | 48 | 123 | 39 | 0 | 26.2625
17:00 | 2872 | 443 | 1664 | 0 | 526 | 3457 | 86 | 0 | 48 | 126 | 3 | 0 | 0
17:30 | 2945.5 | 443 | 1652 | 0 | 881.5 | 3740.5 | 86 | 0 | 56.5 | 122 | 1.5 | 2 | 0
18:00 | 3019 | 443 | 1640 | 0 | 1237 | 4024 | 86 | 0 | 65 | 118 | 0 | 4 | 0
18:30 | 3038.5 | 325.5 | 1601 | 0 | 1228 | 4061 | 86 | 0 | 65 | 115 | 0 | 2 | 0
19:00 | 3058 | 208 | 1562 | 0 | 1219 | 4098 | 86 | 0 | 65 | 112 | 0 | 0 | 0
19:30 | 3058 | 444 | 1588 | 0 | 782 | 4054 | 86 | 0 | 65 | 120 | 0 | 1 | 0
20:00 | 3057 | 444 | 1659 | 0 | 711 | 3992 | 86 | 0 | 65 | 120 | 0 | 3 | 0
20:30 | 3003 | 443.5 | 1638 | 0 | 641 | 4042 | 86 | 0 | 65 | 118 | 0 | 4.5 | 0
21:00 | 2949 | 443 | 1617 | 0 | 571 | 4092 | 86 | 0 | 65 | 116 | 0 | 6 | 0
21:30 | 2945.5 | 443.5 | 1594 | 0 | 447.5 | 4016 | 86 | 0 | 57 | 113.5 | 0 | 4.5 | 0
22:00 | 2942 | 444 | 1571 | 0 | 324 | 3940 | 86 | 0 | 49 | 111 | 0 | 3 | 0
22:30 | 2966 | 443.5 | 1561.5 | 0 | 279 | 3790 | 86 | 0 | 40.5 | 109.5 | 0 | 4 | 0
23:00 | 2990 | 443 | 1552 | 0 | 234 | 3640 | 86 | 0 | 32 | 108 | 0 | 5 | 0
23:30 | 3003 | 443.5 | 1521 | 0 | 176 | 3527 | 86 | 0 | 32 | 104 | 0 | 7.5 | 0 |  | Max Temp. in Dhaka |  | 30.3°C
24:00 | 3016 | 444 | 1490 | 0 | 118 | 3414 | 86 | 0 | 32 | 100 | 0 | 10 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 202.247 MKWHr Energy Not Served 0.362 MKWHr Energy Requirement 202.609 MKWHr
Note on W13: Author:

## Generation
g | 2023-12-02
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1104000
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 3 | 5 | 6 | 7 | 11 | 7 | 4 | 1 | 1 | [10 empty] | 49680
6 | Sikalbaha 225MW CCPP (Gas) | 192 | 192 | 192 | 193 | 193 | 193 | 192 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 191 | 192 |  | 193 | 193 | 193 | 192 | 192 | 192 | 192 | 4638323
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 17 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 80710
12 | Hathazari 100 MW peaking PP | [26 empty] | 0
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [11 empty] | 2 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 195709
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 301 | 300 | 270 | 270 | 270 | 270 | 300 | 295 | 278 | 272 | 272 | 271 | 270 | 270 | 284 | 287 | 270 | 277 |  | 265 | 261 | 260 | 260 | 262 | 265 | 267 | 6700530
18 | Kodda 300 MW PP Unit-2 (Summit) | [10 empty] | 1 | 16 | 42 | 60 |  |  |  | 55 | [7 empty] | 0 | 243382
19 | Ashuganj 195 MW PP (APSCL-United) | 65 | 65 | 36 | 36 | 36 | 45 | 73 | 130 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 167 | 170 |  | 102 | 102 | 158 | 158 | 102 | 102 | 102 | 2258182
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4328100
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 405 | 380 | 350 | 350 | 350 | 350 | 400 | 450 | 450 | 470 | 491 | 492 | 492 | 491 | 491 | 492 | 491 | 491 |  | 491 | 491 | 491 | 491 | 492 | 490 | 490 | 10925453
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 42 | 42 | 41 | 41 | 43 | 40 | 34 | 32 | 41 |  | 45 | 45 | 46 | 45 | 47 | 47 | 47 | 1015344
33 | Ashuganj 225 MW CCPP
34 | Ashuganj 450 MW CCPP(South) | [26 empty] | 0
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 325 | 340 | 315 | 280 | 280 | 330 | 330 | 310 | 280 | 305 | 305 | 280 | 310 |  | 305 | 305 | 310 | 280 | 280 | 280 | 280 | 7482200
| Ashuganj 420 MW CCPP(East) | 393 | 393 | 350 | 300 | 300 | 350 | 355 | 340 | 300 | 350 | 393 | 393 | 390 | 390 | 388 | 385 | 340 | 393 |  | 384 | 372 | 357 | 318 | 325 | 370 | 393 | 8700500
35 | Ashuganj 55 MW PP (Precision) | 47 | 47 | 25 | 10 | 10 | 11 | 24 | 27 | 27 | 27 | 30 | 39 | 45 | 44 | 42 | 24 | 24 | 25 |  | 24 | 24 | 26 | 26 | 26 | 26 | 27 | 688800
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 402 | 398 | 398 | 388 | 350 | 351 | 382 | 401 | 397 | 384 | 406 | 404 | 406 | 362 | 351 | 355 | 393 | 357 |  | 400 | 401 | 400 | 371 | 354 | 354 | 354 | 9189370
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 380 | 380 | 340 | 340 | 340 | 400 | 420 | 390 | 390 | 390 | 390 | 390 | 380 | 340 | 340 | 400 | 400 | 390 |  | 380 | 380 | 370 | 370 | 380 | 380 | 380 | 8293500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 93 | 109 | 110 | 109 | 110 | 110 | 93 | 75 | 75 | 72 | 70 | 69 | 61 | 63 | 62 | 65 | 68 | 68 |  | 68 | 73 | 73 | 73 | 73 | 73 | 74 | 1850880
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 4 | 14 | 29 | 37 | 22 | 47 | 43 | 36 | 19 | 9 | 0 | [9 empty] | 270340
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1016000
45 | Fenchugonj CCPP Phase-2 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 652440
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86 MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 40 | 40 | 40 | 40 | 40 | 40 | 60 | 60 | 60 | 60 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 860160
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 130 | 130 | 129 | 127 | 128 | 126 | 126 | 126 | 126 | 126 |  | 128 | 128 | 128 | 128 | 130 | 130 | 130 | 3086870
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [6 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 194580
54 | Hobiganj 11 MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 5 | 5 | 5 | 5 | 5 | 5 | 127210
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 320400
56 | Shahjahanulla 25 MW PP | 16 | 0 |  |  |  |  | 5 | 16 | [9 empty] | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 155000
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 275 | 285 | 285 | 280 | 310 | 295 | 290 | 290 | 300 | 295 | 310 | 300 | 290 | 290 | 310 | 315 | 290 |  | 280 | 285 | 295 | 290 | 285 | 265 | 270 | 7063000
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 392 | 392 | 400 | 360 | 393 | 395 | 370 | 400 |  | 400 | 400 | 400 | 370 | 370 | 370 | 370 | 9402900
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 5 | 35 |  | 35 | [5 empty] | 0 | 88401
59 | Tangail Palli Power Gen 22 MW | [12 empty] | 3 | 6 | 6 | 6 | 6 | 6 | [7 empty] | 0 | 39840
60 | Barabkunda 22 MW PP (Regent) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 10 | 10 | 13 | 13 | 13 | 13 | 11 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 278832
61 | Narshingdi 22 MW PP (Doreen) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | [8 empty] | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 200664
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 100 | 90 | 88 | 88 | 92 | 88 | 78 | 92 | 102 | 96 | 84 | 98 | 104 | 104 | 110 | 120 | 126 | 118 |  | 112 | 120 | 120 | 116 | 111 | 108 | 100 | 2442240
64 | Malancha, Ctg. EPZ (United) | 30 | 30 | 30 | 30 | 31 | 30 | 13 | 8 | 6 | 6 | 2 | 2 | 2 | 2 | 0 | 0 | 2 | 0 |  | 3 | 7 | 8 | 12 | 22 | 25 | 26 | 336000
65 | Feni 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 428940
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 201960
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 33 | 33 |  | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 762300
68 | Cumilla 25 MW PP (Summit) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 237230
69 | Summit Ashulia | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 480000
70 | Summit Madhabdi | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 0 | 0 | 6 | 15 | 15 | 15 | 15 | 15 | 15 | 10 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 299520
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | [8 empty] | 0 | 0 |  | 25 | 25 | 25 | 25 | 17 | 17 | 17 | 301000
72 | Rupganj 33 MW PP(Summit) | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 16 | 0 | [11 empty] | 8 | 18 | 20 | 25 | 25 | 28 | 338100
73 | Ghorashal 108 MW PP (Regent) | 73 | 73 | 23 | 23 | 30 | 53 | 53 | 65 | 66 | 71 | 73 | 73 | 71 | 71 | 71 | 71 | 71 | 72 |  | 73 | 73 | 73 | 73 | 68 | 68 |  | 1476181
| Feni Lanka Power | [16 empty] | 1 | 17 | [7 empty] | 0 | 20520
| Chowmuhani 113 MW | [10 empty] | 9 | 27 | 28 | 29 | 9 |  | 9 | 42 |  | 48 | 9 | 9 |  |  |  |  | 246120
| Manikgonj 162MW PP(MPGL) | [11 empty] | 17 | 17 | 35 |  |  | 54 | 54 |  | 54 | 54 |  |  |  |  | 0 | 241920
77 | Siddhirganj 100 PP(Dutch Bangla) | [12 empty] | 5 | 8 | [11 empty] | 0 | 14486
78 | Gazipur 52 MW PP | [7 empty] | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 8 | 200069
79 | Kodda 150 MW PP | [6 empty] | 32 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 |  | 48 | 48 | 48 | 48 | 32 | 32 | 32 | 832800
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [17 empty] | 14 | [8 empty] | 20362
| Gazipur 100 MW PP | [6 empty] | 17 | 17 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 105 | 105 |  | 88 | 88 | 88 | 88 | 70 | 35 | 35 | 917760
| Kaptai 7 MW Solar PP | [9 empty] | 2 | 3 | 2 | 3 | 3 | 2 | 0 | [10 empty] | 19297
| Jodiac Power | [11 empty] | 8 | 17 | 17 | 17 | 17 | 23 | 36 |  | 36 | 36 | 36 | 36 |  |  | 0 | 285634
| Karnaphuli Power Ltd. | [10 empty] | 7 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 237526
82 | Madanganj 102 PP(Summit) | [10 empty] | 2 | 20 | 34 | 34 | 26 | [10 empty] | 0 | 102102
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | [12 empty] | 1 | 8 | [11 empty] | 0 | 12480
| Meghnaghat 104 MW PP (OPCL) | [11 empty] | 4 | 17 | 17 |  |  | 2 | 27 | [7 empty] | 0 | 104640
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [10 empty] | 12 | 12 | 12 | 12 | [11 empty] | 0 | 40560
92 | Fenchuganj 44 MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 22 | 5 | [8 empty] | 15 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 271080
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 30 | 43 | 43 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 942668
94 | Gagnagar 102 MW PP (Digital Power) | [25 empty] | 0 | 0
95 | Patenga 50MW PP (Baraka) | [13 empty] | 6 | 6 | 6 | 8 | 17 |  | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 150240
96 | Chattogram 108 MW PP (ECPV) | [20 empty] | 0 |  |  |  |  | 0 | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [11 empty] | 13 | 15 | 15 | 15 |  |  | 25 | [7 empty] | 0 | 120591
100 | Manikganj 55 MW PP (Northern) | [11 empty] | 9 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 |  |  |  |  | 0 | 132449
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [10 empty] | 12600
103 | Kamalaghat 54 MW PP(Banco Energy) | [16 empty] | 17 | 17 |  | 17 | 17 | 17 | 17 |  |  | 0 | 94500
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [6 empty] | 8 | 35 | 35 | 35 | 18 | 18 | 19 | 19 | 18 | 18 | 24 | 93 |  | 93 | 93 | 93 | 65 | 24 | 8 | 0 | 664800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [6 empty] | 27 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 46 |  | 64 | 80 | 80 | 80 | 80 | 69 | 24 | 767808
115 | Juldah 100 MW PP Unit-3 (Acorn) | [9 empty] | 6 | 0 | [14 empty] | 0 | 7680
116 | Chandpur 200 MW (Desh energy) | [10 empty] | 10 | 17 | 17 |  |  |  |  | 11 |  | 69 | 51 | 51 | 83 | 28 | 17 | 17 | 304320
117 | Ashuganj 150 MW PP (Midland) | [10 empty] | 3 | 26 | 50 | 50 | 18 | 6 | 28 | 92 |  | 150 | 70 | 70 |  |  |  | 0 | 543636
118 | Bibiyana-III 400 MW CCPP | 319 | 319 | 320 | 318 | 319 | 319 | 342 | 368 | 368 | 370 | 368 | 400 | 368 | 318 | 343 | 372 | 330 | 368 |  | 367 | 367 | 366 | 321 | 321 | 321 | 321 | 8350000
| Jamalpur 115 MW PP (United) | [7 empty] | 16 | 24 | 24 | 24 | 94 | 94 | 94 | 8 | 8 | 19 | 85 |  | 85 | [5 empty] | 0 | 608400
| Anwara 300 MW PP (United) | [10 empty] | 5 | 30 | 32 | 45 | 45 | 15 | 45 | 115 |  | 150 | 150 | 150 | 80 |  |  | 0 | 790364
| Juldah unit-2 (Acorn) | [25 empty] | 0 | 0
| Anlima Energy Ltd. | [9 empty] | 1 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 242127
| Bhairob 54.5 MW | [8 empty] | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | [5 empty] | 0 | 207720
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 11 | 20 | 26 | 30 | 27 | 29 | 24 | 16 | 7 | 0 | [9 empty] | 188894
| Chandpur 115(Doreen) | [10 empty] | 5 | 18 | 18 | 18 | 17 | 17 | 11 | 51 |  | 34 | 17 | 17 | 17 | 17 | 17 | 0 | 272640
| Kanchan Purbachal Power Generation Ltd. | [8 empty] | 1 | 17 | 17 | 17 | 17 | 17 | 17 | 12 | 17 | 17 |  | 17 | 12 | 12 | 17 | 17 |  | 0 | 237240
Mirsharai 150 MW (Oil)
| Mirsharai 150 MW (Gas) | [11 empty] | 6 | 14 |  |  |  | 13 | 17 | [7 empty] | 0 | 46836
| Cox's Bazar Wind | 2 | 0 | 2 | 8 | 4 | 4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 |  | 0 | 1 | 3 | 6 | 3 | 5 | 10 | 46560
| Matarbari 2*600 MW (CPGCL) | [10 empty] | 0 | 133 | 152 | 269 | 563 | 563 | 505 | 505 |  | 507 | 503 | 505 | 505 | 508 | 506 | 509 | 550545
120 | Eastern Zone Total | 4492 | 4455 | 4223 | 4152 | 4119 | 4333 | 4685 | 4817 | 4668 | 4729 | 4908 | 5397 | 5508 | 5423 | 5480 | 5471 | 5666 | 6373 |  | 6319 | 6053 | 6043 | 5728 | 5408 | 5327 | 5179 | 118614745
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [25 empty] | 0 | 0
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [25 empty] | 0 | 0
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 2 | 25 | 47 | 66 | 76 | 54 | 62 | 71 | 40 | 17 | 1 | [9 empty] | 462240
131 | Rampal 1320 MW (BIFPCL) | 407 | 362 | 357 | 360 | 364 | 364 | 405 | 455 | 430 | 409 | 409 | 456 | 490 | 405 | 407 | 403 | 501 | 623 |  | 626 | 626 | 624 | 625 | 582 | 505 | 471 | 11156360
132 | United Payra Power Ltd. | [25 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5344364
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [25 empty] | 0 | 0
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 200 | 177 | 150 | 150 | 150 | 180 | 150 | 150 | 150 | 182 | 286 |  | 307 | 307 | 307 | 307 | 294 | 211 | 183 | 4647300
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 64 | 64 | 64 | 64 | 64 | 64 | 64 |  | 64 | 64 | 65 | 130 | 130 | 130 | 130 | 1780000
140 | Bhola 33 MW PP (Venture) | 17 | 17 | 16 | 16 | 16 | 15 | 14 | 13 | 13 | 12 | 6 | 11 | 12 | 14 | 12 | 11 | 12 | 16 |  | 16 | 16 | 17 | 17 | 17 | 15 | 14 | 333200
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 920 | 730 | 682 | 682 | 682 | 602 | 440 | 439 | 438 | 438 | 438 | 437 | 444 | 444 | 443 | 444 | 443 | 443 |  | 208 | 444 | 444 | 443 | 444 | 443 | 444 | 12397818
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 860 | 820 | 820 | 760 | 760 | 760 | 820 | 940 | 900 | 880 | 970 | 1080 | 1100 | 1070 | 940 | 900 | 1010 | 1210 |  | 1244 | 1200 | 1200 | 1244 | 1140 | 1000 | 900 | 25430700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4136500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 3 | 4 | 5 | 4 | 2 | 2 | 2 | 0 | 0 | [9 empty] | 29340
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 380 | 380 | 350 | 320 | 320 | 370 | 414 | 370 | 370 | 414 | 380 | 414 | 391 | 354 | 332 | 310 | 312 | 306 |  | 313 | 330 | 341 | 300 | 300 | 300 | 300 | 8556000
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 237366
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [26 empty] | 0
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [25 empty] | 0 | 0
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [16 empty] | 3 | 35 |  | 35 | [5 empty] | 0 | 122880
172 | Confidence Power Bogura Unit-1 113 MW |  |  |  |  | 0 | 35 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  |  | 25 | 35 |  | 35 | [6 empty] | 1047168
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [9 empty] | 20 | 34 | 49 | 65 | 70 | 7 |  | 5 | 70 |  | 70 | [5 empty] | 0 | 413097
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 3 | 5 | 6 | 6 | 6 | 3 | 1 | 0 | [9 empty] | 31908
178 | Energypac Power Venture Thakurgaon Ltd. | [9 empty] | 35 | 35 | 35 | 36 | 36 |  |  |  | 35 |  | 17 | [5 empty] | 0 | 278016
| Intraco Solar 30 MW | [6 empty] | 2 | 3 | 9 | 20 | 21 | 43 | 33 | 30 | 17 | 7 | 0 | [9 empty] | 177213
| Adani Power Jharkhanda Ltd | [12 empty] | 75 | 149 | 325 | 433 | 598 | 739 |  | 753 | 757 | 695 | 750 | 754 | 758 | 691 | 6136727
178 | Teesta Solar Limited | [6 empty] | 9 | 67 | 113 | 84 | 135 | 119 | 155 | 143 | 88 | 33 | 2 | [9 empty] | 914190