## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-12-06 | Wednesday
|  | Date (day): | 2023-12-06 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11562.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12216 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-12-05 | 2023-12-06 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 70 | 73 | 74 | 74 | 34 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 371 | 339 | 330 | 375 | 37 |  | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 40 | 92 | 92
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 4 | 68 | 85 | 85 |  | 17 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 18 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 36 | 36 | 39 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 10 | 15 | 15 |  | 7 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 4 | 80 | 90 | 90 |  | 10 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 310 | 288 | 300 | 300 | 35
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 63 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 6 | 118 | 100 | 149 | 0 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 0 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 0 | 35 | 20 |  | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 35 | 34 | 38 | 38 |  | 42 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 26 | 26 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 17 | 8 | 16 | 36 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 10 | 280 | 300 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 35 | 67 | 35 | 60 | 89 |  | Fuel shortage
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 105 | 52 | 105
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 72 | 90 | 90 | 14 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 17 | 18 | 54 | 108 |  | Fuel shortage
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 11 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 17 | 35 | 20 |  | Fuel shortage
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 5763 | 5422 | 1703 | 2529 | 2583 | 2852 | 1190 | 1016
38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
39 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 16 | 8 | 17 | 8 |  | Fuel shortage
40 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 11 | 0 | 20 | 0
41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 19 | 6 | 18 | 32 |  | Fuel shortage
42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 86 | 86 | 86 | 86 | 144 |  | Low water lavel
43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 179 | 194 | 190 | 190 | 35 |  | Gas shortage
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 17 | 17 | 88 |  | Fuel shortage
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 40 | 50 | 65 | 33 |  | Fuel shortage
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 0 | 17 | 85 |  | Fuel shortage
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 12 | 13 | 12 | 12 | 10 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 2 | 10 | 20
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 20 | 106 | 100 | 100 | 200 |  | Fuel shortage
54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 36 | 17 | 36 | 18 |  | Fuel shortage
55 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 17 | 17 | 93 |  | Fuel shortage
56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
57 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 17 | 99 |  | Fuel shortage
58 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 33 | 150 | 150 | 13
59 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 490 | 490 | 500 | 500
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 1 | 11 | 10 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 35 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 3829 | 3769 | 905 | 1109 | 1227 | 1284 | 1434 | 330
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 0 | 0 |  | 221 | Under maint.
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 300 | 320 | 320 | 40 |  | Gas shortage
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 265 | 295 | 300 | 300 |  | 360
63 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 320 | 230 | 390 | 390
64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 34 | 47 | 47 | 47
65 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 0 | 23 | 24 | 25 | 25 | 30 |  | Gas shortage
66 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 8 | 8 | 8 | 187 |  | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
68 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 14 | 55 | 150 | 150
69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 20
70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
71 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 100 | 20 | 200 | 200
72 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 110 | 102 | 128 | 140
74 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 36 | 52 | 52
76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 10 | 8 | 10 | 10 |  | 15 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 76 | 114 | 114
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 27 | 47 | 28 | 55 |  | 58 | Engine problem
79 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 13 | 17 | 17 |  | 37 | Engine problem
80 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 18 | 40 | 17 | 53 | 62 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2896 | 1298 | 1414 | 1919 | 2014 | 319 | 858
81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 34 | 35 | 75 | 50 | 152 |  | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Contract Expired
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 77 | 56 | 65 | 135 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 28 | 8 | 25 | 90 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 14 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 116 | 146 | 196.6 | 146 | 152 | 22
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 27 | 28 | 28 | 28 |  | 62 | Engine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 25 | 25 | 25 | 25 | 26 |  | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 25 | 25 | 25 | 25 | 25 |  | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 8 | 8 |  | 3 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 19 | 59 | 60 | 60 |  | 6
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 0 | 0 | 0 | 86 |  | Gas shortage
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 158 | 164 | 163 | 163 |  | 68 | Machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 16 | 16 | 16 | 9 |  | Gas shortage
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 290 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 365 | 384 | 400 | 400 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 310 | 400 | 400 | 400 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1310 | 1452 | 1478 | 1478 | 309 | 596
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 438 | 428 | 449 | 449
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 18 | 49 | 32 | 48 | 67 |  | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 45
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 | 109 |  | under maint.
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 0 | 16 | 24 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 90 | 90 |  | 15 | Engine problem
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 23 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 380 | 375 | 370 | 370 |  |  | Coal Shortage.
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 859 | 860 | 1041 | 1018 | 1297 | 15
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 15 | 19 | 21 | 25 |  | 15 | Engine problem
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 60 | 130 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1000 | 1244 | 622 | 622 |  |  | #01 under maint.
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 222 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 7 | 17 | 0 | 150
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 140 | 140 | 140 | 140 |  |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1442 | 1772 | 1243 | 1397 | 0 | 79
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 30 | 22 |  | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 20 |  | 51 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 28 | 28
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 42 | 34 | 42 |  | 8 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 40 |  | 10 | Engine problem
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 256 | 246 | 414 | 414
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 38 | 12 |  | Fuel shortage
136 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 52 | 52
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 40 | 86 |  | 18 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 50 | 35 | 55 | 58 |  | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 55 | 35 | 70 | 43 |  | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 1 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 758 | 760 | 748 | 748
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 1096 | 1172 | 1433 | 1634 | 1156 | 87
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 33 | 100 | 34 | 113
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 114 | 70 | 110
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 18 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 86 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 310 | 384 | 442 | 393 | 125 | 189
| Total |  |  |  |  | 25951 | 25211 | 9039 | 10838 | 11562.6 | 12216 | 5982 | 3192
A. |  | 2023-12-05 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 10838 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 7347 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10838 | MW
3 | Day peak Generation : |  |  | 9039 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10404.38 | MW
4 | Evening peak Generation : |  |  | 10838 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 216.9973 | MKWHr | By Solar | 0.96169 | MKWHr
| By Gas : | 108.3101 | MKWHr |  | By Oil: | 17.4334 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 75.0694 | MKWHr |  | By Hydro: | 2.0699 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.13488 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5982 | MW | Dhaka | 4121.78 | 4121.78 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3192 | MW | Chittagong | 1144 | 1144 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 9174 | MW | Khulna | 1130.3 | 1130.3 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 814 | MMCFD |  |  | Rajshahi | 967.8 | 967.8 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 110479281.144 | ii) Oil : | Taka | 224925961.82 | Comilla | 891 | 891 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 505055704.87 | Total | Taka | 840460947.834 | Mymensingh | 782 | 782 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.198 | MKWHr. | Sylhet | 374 | 374 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 290 | MW (W to E) at | 18:00 | hrs | Barisal | 278.5 | 278.5 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 140 | MW at | 8:00 | hrs | Rangpur | 715 | 715 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 27.1°C |  |  | Total | 10404.38 | 10404.38 |  | 0
B. |  | 2023-12-06 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 30.3°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12216 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9200 | MW
4 | Reserve(Generation end) |  |  |  | 1216 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 220.2409 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7309 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 10.6007 | MKWHr. | ii) HVDC Flow at Peak Time |  | 428 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.4173 | MKWHr. | iii) Maximum HVDC Flow : |  | 443 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 97.36 |  | (b) Today: | 97.22 |  | (c) Rule Curve: |  | 105.55
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-12-05 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 330 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 15 | 25 | 24 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 21 | 0 | 0 | 0 | 280 | 135 | 0 | 0 | 0 | 46 | 6 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 33 | 10 | 100 | 85 | 0 | 0 | 0 | 43 | 28 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 111 | 0 | 0 | 0 | 275 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 490 | 0 | 565 | 0 | 0 |  | 442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 850 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 140 | 763 | 0 | 0 |  | 5014 | 3331 | 8345 | 3049 | 442 | 1217 | 0 | 95 | 3356 | 86 | 0 | 0 | 100 | 0 | 0 | 0 | 97.4
2:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 330 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 15 | 25 | 28 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | 0 | 0 | 0 | 280 | 100 | 0 | 0 | 0 | 5 | 3 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 8 | 10 | 104 | 85 | 0 | 0 | 0 | 43 | 28 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 113 | 0 | 0 | 0 | 280 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 460 | 0 | 565 | 0 | 0 |  | 443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 790 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 140 | 701 | 0 | 0 |  | 4819 | 3220 | 8039 | 2970 | 443 | 1231 | 0 | 0 | 3205 | 86 | 0 | 0 | 104 | 0 | 0 | 0 | 97.4
3:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 325 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 15 | 25 | 28 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 30 | 0 | 0 | 0 | 280 | 125 | 0 | 0 | 0 | 5 | 3 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 8 | 10 | 104 | 85 | 0 | 0 | 0 | 43 | 28 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 122 | 0 | 0 | 0 | 280 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 395 | 5 | 566 | 0 | 0 |  | 442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 140 | 550 | 0 | 0 |  | 4765 | 3065 | 7830 | 2969 | 442 | 1242 | 0 | 0 | 2982 | 86 | 0 | 0 | 104 | 0 | 5 | 0 | 97.39
4:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 320 | 0 |  | 0 | 340 | 0 | 0 | 0 | 0 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 15 | 25 | 28 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 32 | 0 | 0 | 0 | 280 | 140 | 0 | 0 | 0 | 5 | 3 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 8 | 10 | 96 | 85 | 0 | 0 | 0 | 43 | 28 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 136 | 0 | 0 | 0 | 275 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 335 | 5 | 566 | 0 | 0 |  | 443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 680 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 140 | 535 | 0 | 0 |  | 4561 | 2884 | 7445 | 2896 | 443 | 1116 | 0 | 0 | 2803 | 86 | 0 | 0 | 96 | 0 | 5 | 0 | 97.38
5:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 310 | 0 |  | 0 | 340 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 15 | 25 | 28 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 33 | 0 | 0 | 0 | 280 | 165 | 0 | 0 | 0 | 5 | 3 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 8 | 10 | 92 | 85 | 0 | 0 | 0 | 43 | 28 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 137 | 0 | 0 | 0 | 290 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 320 | 3 | 565 | 0 | 0 |  | 443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 640 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 140 | 522 | 0 | 0 |  | 4515 | 2832 | 7347 | 2856 | 443 | 1132 | 0 | 0 | 2735 | 86 | 0 | 0 | 92 | 0 | 3 | 0 | 97.37
6:00 | 0 | 0 | 0 | 180 | 0 | 32 | 0 | 311 | 0 |  | 0 | 340 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 15 | 25 | 29 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 33 | 0 | 0 | 0 | 280 | 210 | 0 | 0 | 0 | 37 | 3 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 33 | 10 | 98 | 85 | 0 | 0 | 0 | 43 | 28 | 4 | 5 | 0 | 0 | 40 | 0 | 0 | 138 | 0 | 0 | 10 | 310 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 350 | 0 | 0 | 320 | 3 | 565 | 0 | 0 |  | 443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 140 | 522 | 0 | 0 |  | 4822 | 2853 | 7675 | 3083 | 443 | 1263 | 0 | 3 | 2696 | 86 | 0 | 0 | 98 | 0 | 3 | 0 | 97.36
7:00 | 0 | 0 | 0 | 180 | 0 | 33 | 0 | 311 | 0 |  | 0 | 340 | 0 | 0 | 0 | 0 | 277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 15 | 25 | 29 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 193 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 30 | 0 | 0 | 0 | 330 | 330 | 0 | 0 | 0 | 47 | 3 | 0 | 30 | 0 | 0 | 0 | 5 | 0 | 33 | 10 | 100 | 69 | 0 | 0 | 0 | 43 | 28 | 10 | 5 | 0 | 0 | 53 | 0 | 0 | 137 | 0 | 0 | 10 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 54 | 0 | 319 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 0 | 0 | 325 | 5 | 567 | 0 | 0 |  | 443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 180 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 378 | 1 | 140 | 552 | 6 | 0 |  | 5087 | 2885 | 7972 | 3250 | 443 | 1272 | 0 | 73 | 2732 | 86 | 0 | 0 | 100 | 11 | 5 | 0 | 97.35
8:00 | 0 | 0 | 0 | 180 | 0 | 52 | 0 | 306 | 0 |  | 0 | 340 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 15 | 25 | 29 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 280 | 365 | 0 | 0 | 0 | 47 | 16 | 0 | 43 | 0 | 0 | 0 | 13 | 8 | 33 | 10 | 100 | 70 | 0 | 0 | 0 | 43 | 28 | 25 | 21 | 0 | 0 | 63 | 0 | 0 | 138 | 0 | 0 | 10 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 56 | 0 | 1 | 8 | 0 | 68 | 0 | 327 | 8 | 17 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 7 | 0 | 0 | 0 | 0 | 4 | 18 | 0 | 270 | 0 | 0 | 430 | 6 | 565 | 0 | 0 |  | 443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 700 | 220 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 377 | 5 | 140 | 645 | 24 | 0 |  | 5385 | 3146 | 8531 | 3267 | 443 | 1361 | 0 | 179 | 3027 | 86 | 0 | 0 | 100 | 62 | 6 | 0 | 97.34
9:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 302 | 0 |  | 0 | 340 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 15 | 25 | 29 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 280 | 365 | 0 | 0 | 0 | 47 | 23 | 0 | 43 | 0 | 0 | 0 | 16 | 8 | 33 | 10 | 96 | 34 | 0 | 0 | 1 | 43 | 28 | 25 | 25 | 0 | 0 | 62 | 0 | 0 | 138 | 0 | 0 | 10 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 56 | 0 | 17 | 0 | 0 | 68 | 1 | 317 | 8 | 35 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 18 | 0 | 4 | 0 | 0 | 3 | 18 | 0 | 270 | 0 | 0 | 492 | 0 | 271 | 0 | 0 |  | 443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 900 | 220 | 0 | 0 | 1 | 18 | 0 | 0 | 0 | 377 | 6 | 140 | 751 | 46 | 0 |  | 5175 | 3483 | 8658 | 3220 | 443 | 1401 | 0 | 215 | 3101 | 86 | 0 | 0 | 96 | 96 | 0 | 0 | 97.33
10:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 302 | 0 |  | 0 | 340 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 15 | 25 | 28 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 190 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 5 | 12 | 0 | 0 | 0 | 0 | 330 | 335 | 0 | 0 | 0 | 44 | 24 | 0 | 43 | 0 | 0 | 0 | 16 | 8 | 17 | 10 | 106 | 35 | 0 | 0 | 1 | 43 | 28 | 25 | 25 | 0 | 0 | 61 | 0 | 0 | 138 | 0 | 0 | 10 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 46 | 0 | 23 | 8 | 0 | 68 | 8 | 371 | 9 | 35 | 0 | 2 | 0 | 0 | 3 | 0 | 0 | 0 | 340 | 0 | 18 | 0 | 17 | 0 | 0 | 7 | 18 | 0 | 270 | 35 | 0 | 491 | 0 | 153 | 0 | 0 |  | 443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 980 | 220 | 0 | 0 | 1 | 24 | 0 | 0 | 0 | 374 | 26 | 140 | 765 | 49 | 0 |  | 5133 | 3575 | 8708 | 3219 | 443 | 1367 | 0 | 240 | 3073 | 86 | 0 | 35 | 106 | 139 | 0 | 0 | 97.32
11:00 | 0 | 0 | 0 | 180 | 0 | 69 | 0 | 332 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 15 | 25 | 28 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 340 | 335 | 0 | 0 | 0 | 38 | 23 | 0 | 43 | 0 | 0 | 0 | 18 | 8 | 25 | 10 | 108 | 35 | 0 | 0 | 1 | 43 | 27 | 25 | 25 | 0 | 0 | 46 | 0 | 0 | 158 | 0 | 0 | 10 | 325 | 16 | 5 | 0 | 0 | 0 | 0 | 58 | 0 | 35 | 19 | 0 | 70 | 12 | 422 | 9 | 35 | 0 | 2 | 5 | 0 | 17 | 0 | 0 | 0 | 365 | 0 | 15 | 17 | 17 | 0 | 0 | 9 | 18 | 10 | 300 | 35 | 0 | 490 | 0 | 0 | 0 | 0 |  | 443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268 | 0 | 0 | 5 | 0 | 0 | 0 | 5 | 35 | 1000 | 220 | 0 | 0 | 1 | 37 | 0 | 0 | 0 | 376 | 10 | 140 | 757 | 46 | 0 |  | 5373 | 3597 | 8970 | 3375 | 443 | 1471 | 0 | 374 | 2933 | 86 | 0 | 35 | 108 | 145 | 0 | 0 | 97.31
12:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 371 | 0 |  | 0 | 450 | 0 | 0 | 4 | 18 | 310 | 0 | 0 | 4 | 0 | 6 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 15 | 25 | 26 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 179 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 280 | 265 | 0 | 0 | 0 | 34 | 23 | 0 | 43 | 0 | 0 | 0 | 18 | 11 | 25 | 10 | 110 | 34 | 0 | 0 | 1 | 43 | 27 | 25 | 25 | 0 | 0 | 19 | 0 | 0 | 158 | 0 | 0 | 10 | 315 | 8 | 5 | 0 | 10 | 0 | 0 | 58 | 0 | 35 | 11 | 0 | 100 | 14 | 365 | 9 | 35 | 17 | 2 | 20 | 0 | 17 | 0 | 27 | 0 | 310 | 17 | 14 | 54 | 17 | 0 | 0 | 11 | 18 | 17 | 320 | 35 | 0 | 490 | 1 | 0 | 0 | 0 |  | 438 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 0 | 0 | 35 | 0 | 33 | 0 | 3 | 35 | 1000 | 220 | 0 | 7 | 1 | 23 | 0 | 0 | 0 | 380 | 18 | 140 | 758 | 86 | 0 |  | 5332 | 3707 | 9039 | 3141 | 438 | 1452 | 0 | 662 | 2938 | 86 | 0 | 41 | 110 | 170 | 1 | 0 | 97.31
13:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 365 | 0 |  | 0 | 450 | 0 | 5 | 25 | 40 | 300 | 0 | 0 | 34 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 15 | 25 | 26 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 188 | 0 | 0 | 0 |  | 5 | 0 | 0 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 280 | 275 | 0 | 0 | 0 | 41 | 23 | 0 | 43 | 0 | 0 | 0 | 18 | 11 | 33 | 10 | 110 | 34 | 0 | 0 | 1 | 43 | 27 | 25 | 25 | 0 | 0 | 59 | 0 | 0 | 164 | 0 | 0 | 10 | 310 | 16 | 5 | 0 | 88 | 0 | 0 | 58 | 0 | 35 | 11 | 0 | 120 | 14 | 367 | 9 | 35 | 17 | 1 | 65 | 0 | 17 | 0 | 27 | 0 | 400 | 52 | 18 | 162 | 17 | 0 | 0 | 6 | 18 | 17 | 240 | 27 | 0 | 490 | 4 | 0 | 0 | 0 |  | 438 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 267 | 0 | 0 | 35 | 0 | 33 | 0 | 3 | 35 | 1020 | 220 | 0 | 17 | 1 | 19 | 50 | 0 | 0 | 374 | 15 | 140 | 766 | 66 | 0 |  | 5767 | 3791 | 9558 | 3225 | 438 | 1460 | 0 | 1091 | 2960 | 86 | 0 | 43 | 110 | 141 | 4 | 0 | 97.3
14:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 344 | 0 |  | 0 | 340 | 0 | 26 | 39 | 55 | 250 | 0 | 0 | 36 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 15 | 25 | 26 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 193 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 280 | 280 | 0 | 8 | 0 | 47 | 23 | 0 | 43 | 0 | 0 | 0 | 18 | 11 | 33 | 10 | 120 | 34 | 0 | 0 | 1 | 43 | 27 | 25 | 25 | 0 | 0 | 60 | 0 | 0 | 164 | 0 | 0 | 10 | 260 | 16 | 5 | 0 | 95 | 0 | 0 | 58 | 0 | 35 | 0 | 0 | 120 | 13 | 368 | 9 | 35 | 17 | 1 | 65 | 8 | 17 | 0 | 29 | 0 | 340 | 35 | 13 | 108 | 17 | 0 | 0 | 4 | 18 | 17 | 240 | 27 | 0 | 491 | 15 | 0 | 0 | 0 |  | 438 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 264 | 0 | 0 | 35 | 0 | 33 | 0 | 3 | 35 | 1060 | 180 | 0 | 17 | 1 | 13 | 52 | 0 | 0 | 376 | 16 | 140 | 759 | 52 | 0 |  | 5505 | 3747 | 9252 | 3117 | 438 | 1261 | 0 | 1072 | 2996 | 86 | 0 | 43 | 120 | 104 | 15 | 0 | 97.31
15:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 343 | 0 |  | 0 | 340 | 0 | 0 | 17 | 15 | 250 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 15 | 25 | 26 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 194 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 6 | 10 | 0 | 0 | 0 | 0 | 280 | 280 | 0 | 8 | 0 | 47 | 23 | 0 | 43 | 0 | 0 | 0 | 18 | 8 | 33 | 10 | 106 | 35 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 56 | 0 | 0 | 164 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 45 | 0 | 0 | 58 | 0 | 35 | 3 | 0 | 120 | 15 | 366 | 9 | 35 | 17 | 1 | 69 | 36 | 17 | 0 | 29 | 0 | 340 | 17 | 7 | 35 | 17 | 0 | 1 | 4 | 18 | 17 | 240 | 17 | 0 | 490 | 18 | 0 | 0 | 0 |  | 443 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253 | 0 | 0 | 35 | 0 | 34 | 0 | 2 | 35 | 1050 | 180 | 0 | 17 | 0 | 8 | 54 | 0 | 0 | 377 | 6 | 140 | 760 | 38 | 0 |  | 5284 | 3706 | 8990 | 3111 | 443 | 1292 | 0 | 845 | 2987 | 86 | 0 | 33 | 106 | 69 | 18 | 0 | 97.29
16:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 327 | 0 |  | 0 | 340 | 0 | 5 | 4 | 15 | 250 | 0 | 0 | 3 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 15 | 25 | 26 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 6 | 10 | 0 | 0 | 0 | 0 | 305 | 305 | 0 | 8 | 0 | 47 | 23 | 0 | 43 | 0 | 0 | 0 | 18 | 11 | 25 | 10 | 94 | 35 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 56 | 0 | 0 | 164 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 45 | 0 | 0 | 58 | 0 | 35 | 1 | 0 | 123 | 13 | 344 | 9 | 35 | 17 | 0 | 69 | 36 | 17 | 0 | 29 | 0 | 350 | 17 | 3 | 17 | 17 | 0 | 0 | 2 | 18 | 17 | 240 | 15 | 0 | 490 | 12 | 0 | 0 | 0 |  | 443 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244 | 0 | 0 | 40 | 0 | 34 | 0 | 1 | 35 | 1000 | 180 | 0 | 17 | 0 | 10 | 53 | 0 | 0 | 369 | 3 | 140 | 756 | 15 | 0 |  | 5302 | 3581 | 8883 | 3091 | 443 | 1275 | 0 | 843 | 2925 | 86 | 0 | 79 | 94 | 35 | 12 | 0 | 97.29
17:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 301 | 0 |  | 0 | 340 | 0 | 23 | 45 | 24 | 250 | 0 | 0 | 24 | 24 | 64 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 0 | 20 | 15 | 25 | 26 | 17 | 0 | 46 | 40 | 0 | 0 | 7 | 193 | 0 | 0 | 0 |  | 6 | 1 | 0 | 12 | 0 | 19 | 12 | 0 | 0 | 0 | 0 | 280 | 280 | 0 | 8 | 0 | 47 | 23 | 0 | 43 | 0 | 0 | 8 | 18 | 11 | 33 | 10 | 90 | 36 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 60 | 0 | 0 | 164 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 85 | 0 | 0 | 58 | 0 | 36 | 0 | 0 | 122 | 30 | 318 | 9 | 90 | 17 | 0 | 102 | 36 | 17 | 34 | 29 | 0 | 390 | 68 | 0 | 17 | 17 | 0 | 0 | 0 | 19 | 30 | 240 | 17 | 0 | 490 | 11 | 0 | 0 | 0 |  | 443 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 8 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247 | 2 | 0 | 50 | 0 | 87 | 0 | 0 | 55 | 980 | 180 | 0 | 17 | 0 | 0 | 70 | 0 | 0 | 378 | 0 | 140 | 758 | 1 | 0 |  | 5704 | 3748 | 9452 | 3095 | 443 | 1289 | 0 | 1439 | 2916 | 86 | 0 | 82 | 90 | 1 | 11 | 0 | 97.28
18:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 339 | 0 |  | 0 | 450 | 0 | 40 | 68 | 55 | 288 | 0 | 0 | 80 | 63 | 118 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 10 | 20 | 14 | 25 | 26 | 17 | 0 | 46 | 40 | 0 | 0 | 16 | 194 | 0 | 0 | 0 |  | 6 | 40 | 0 | 12 | 0 | 19 | 13 | 2 | 0 | 0 | 0 | 300 | 295 | 0 | 8 | 0 | 47 | 24 | 0 | 51 | 0 | 0 | 36 | 18 | 11 | 33 | 8 | 102 | 35 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 59 | 0 | 0 | 164 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 280 | 0 | 0 | 77 | 0 | 67 | 0 | 0 | 20 | 55 | 384 | 28 | 105 | 17 | 0 | 106 | 36 | 17 | 76 | 47 | 0 | 400 | 72 | 0 | 17 | 17 | 0 | 13 | 0 | 40 | 35 | 230 | 33 | 0 | 490 | 11 | 0 | 0 | 0 |  | 428 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 8 | 130 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246 | 0 | 0 | 50 | 0 | 100 | 0 | 0 | 55 | 1244 | 222 | 0 | 17 | 0 | 0 | 114 | 0 | 0 | 375 | 0 | 140 | 760 | 0 | 0 |  | 6650 | 4188 | 10838 | 3329 | 428 | 1445 | 0 | 2067 | 3179 | 86 | 0 | 191 | 102 | 0 | 11 | 0 | 97.28
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 364 | 0 |  | 0 | 320 | 0 | 57 | 75 | 15 | 230 | 0 | 0 | 84 | 40 | 98 | 19 | 0 | 0 | 0 | 17 | 35 | 35 | 10 | 20 | 14 | 25 | 26 | 17 | 0 | 46 | 40 | 0 | 0 | 17 | 193 | 0 | 0 | 0 |  | 6 | 84 | 17 | 12 | 0 | 20 | 12 | 0 | 0 | 0 | 0 | 335 | 330 | 0 | 8 | 0 | 47 | 23 | 0 | 51 | 0 | 0 | 8 | 18 | 11 | 33 | 4 | 106 | 35 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 59 | 0 | 0 | 164 | 0 | 0 | 10 | 285 | 16 | 8 | 0 | 145 | 0 | 0 | 78 | 0 | 72 | 0 | 0 | 17 | 57 | 368 | 28 | 105 | 17 | 0 | 106 | 36 | 17 | 22 | 47 | 0 | 396 | 53 | 0 | 17 | 17 | 0 | 17 | 0 | 58 | 35 | 230 | 114 | 0 | 440 | 9 | 122 | 0 | 0 |  | 209 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 3 | 0 | 50 | 0 | 102 | 0 | 0 | 55 | 1160 | 224 | 0 | 35 | 0 | 0 | 54 | 0 | 0 | 376 | 0 | 140 | 725 | 0 | 0 |  | 6496 | 3747 | 10243 | 3329 | 209 | 1301 | 0 | 1724 | 3133 | 86 | 0 | 346 | 106 | 0 | 9 | 0 | 97.26
19:30 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 362 | 0 |  | 0 | 360 | 0 | 17 | 17 | 15 | 287 | 0 | 0 | 30 | 16 | 98 | 24 | 0 | 0 | 0 | 17 | 35 | 35 | 10 | 20 | 15 | 25 | 26 | 17 | 0 | 46 | 40 | 0 | 0 | 17 | 193 | 0 | 0 | 0 |  | 6 | 83 | 17 | 12 | 0 | 20 | 12 | 0 | 0 | 0 | 0 | 280 | 270 | 0 | 8 | 0 | 47 | 23 | 0 | 51 | 0 | 0 | 8 | 18 | 11 | 33 | 4 | 110 | 48 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 62 | 0 | 0 | 164 | 0 | 0 | 10 | 285 | 16 | 8 | 0 | 145 | 0 | 0 | 78 | 0 | 72 | 0 | 0 | 17 | 62 | 319 | 28 | 105 | 17 | 0 | 106 | 36 | 17 | 17 | 47 | 0 | 400 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 36 | 35 | 215 | 127 | 0 | 440 | 12 | 158 | 0 | 0 |  | 443 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245 | 10 | 0 | 50 | 0 | 107 | 0 | 0 | 55 | 1120 | 224 | 0 | 35 | 0 | 0 | 35 | 0 | 0 | 376 | 0 | 140 | 767 | 0 | 0 |  | 6259 | 3986 | 10245 | 3226 | 443 | 1347 | 0 | 1488 | 3171 | 86 | 0 | 362 | 110 | 0 | 12 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 360 | 0 |  | 0 | 360 | 0 | 23 | 17 | 15 | 278 | 0 | 0 | 20 | 0 | 64 | 31 | 0 | 0 | 0 | 17 | 35 | 17 | 10 | 20 | 15 | 25 | 26 | 17 | 0 | 86 | 0 | 0 | 0 | 17 | 195 | 0 | 0 | 0 |  | 6 | 83 | 17 | 12 | 0 | 20 | 12 | 3 | 0 | 0 | 0 | 280 | 250 | 0 | 8 | 0 | 47 | 26 | 0 | 51 | 0 | 0 | 8 | 18 | 11 | 33 | 4 | 106 | 84 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 62 | 0 | 0 | 164 | 0 | 0 | 10 | 295 | 16 | 8 | 0 | 145 | 0 | 0 | 78 | 0 | 72 | 0 | 0 | 17 | 60 | 319 | 28 | 105 | 17 | 0 | 105 | 36 | 17 | 17 | 48 | 0 | 400 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 40 | 35 | 220 | 67 | 0 | 440 | 11 | 234 | 0 | 0 |  | 443 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245 | 17 | 0 | 50 | 0 | 107 | 0 | 0 | 55 | 1120 | 224 | 0 | 35 | 0 | 0 | 35 | 0 | 0 | 378 | 0 | 140 | 739 | 0 | 0 |  | 6235 | 3974 | 10209 | 3238 | 443 | 1366 | 0 | 1466 | 3221 | 86 | 0 | 272 | 106 | 0 | 11 | 0 | 97.27
21:00 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 361 | 0 |  | 0 | 360 | 0 | 0 | 17 | 15 | 280 | 0 | 0 | 17 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 10 | 20 | 15 | 25 | 26 | 17 | 0 | 86 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 |  | 6 | 0 | 17 | 0 | 0 | 20 | 12 | 2 | 0 | 0 | 0 | 300 | 250 | 0 | 8 | 0 | 47 | 34 | 0 | 51 | 0 | 0 | 8 | 18 | 11 | 33 | 4 | 96 | 83 | 0 | 0 | 0 | 43 | 28 | 26 | 25 | 0 | 0 | 62 | 0 | 0 | 164 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 45 | 0 | 0 | 78 | 0 | 72 | 0 | 0 | 17 | 57 | 344 | 28 | 70 | 17 | 0 | 106 | 36 | 17 | 17 | 48 | 0 | 400 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 21 | 35 | 230 | 0 | 0 | 440 | 9 | 268 | 0 | 0 |  | 443 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 35 | 0 | 50 | 0 | 50 | 0 | 0 | 55 | 1100 | 224 | 0 | 35 | 0 | 0 | 35 | 0 | 0 | 378 | 0 | 140 | 760 | 0 | 0 |  | 5807 | 3953 | 9760 | 3293 | 443 | 1387 | 0 | 1116 | 3256 | 86 | 0 | 74 | 96 | 0 | 9 | 0 | 97.26
22:00 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 362 | 0 |  | 0 | 360 | 0 | 0 | 17 | 0 | 280 | 0 | 0 | 17 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 10 | 20 | 0 | 25 | 26 | 17 | 0 | 86 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 6 | 0 | 17 | 0 | 0 | 20 | 12 | 8 | 0 | 0 | 0 | 280 | 250 | 0 | 8 | 0 | 47 | 34 | 0 | 51 | 0 | 0 | 8 | 18 | 11 | 33 | 4 | 94 | 83 | 0 | 0 | 0 | 43 | 28 | 26 | 25 | 0 | 0 | 61 | 0 | 0 | 164 | 0 | 0 | 10 | 285 | 16 | 8 | 0 | 45 | 0 | 0 | 58 | 0 | 72 | 0 | 0 | 17 | 55 | 320 | 9 | 70 | 17 | 0 | 105 | 21 | 17 | 17 | 48 | 0 | 370 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 18 | 35 | 230 | 0 | 0 | 440 | 6 | 271 | 0 | 0 |  | 443 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 35 | 0 | 50 | 0 | 34 | 0 | 0 | 55 | 1080 | 220 | 0 | 35 | 0 | 0 | 35 | 0 | 0 | 378 | 0 | 140 | 761 | 0 | 0 |  | 5641 | 3891 | 9532 | 3203 | 443 | 1402 | 0 | 1025 | 3240 | 86 | 0 | 33 | 94 | 0 | 6 | 0 | 97.26
23:00 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 357 | 0 |  | 0 | 360 | 0 | 0 | 3 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 15 | 25 | 26 | 17 | 0 | 86 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 20 | 12 | 12 | 0 | 0 | 0 | 280 | 250 | 0 | 8 | 0 | 46 | 37 | 0 | 51 | 0 | 0 | 8 | 18 | 11 | 33 | 10 | 98 | 84 | 0 | 0 | 0 | 43 | 28 | 26 | 25 | 0 | 0 | 61 | 0 | 0 | 163 | 0 | 0 | 10 | 270 | 16 | 8 | 0 | 15 | 0 | 0 | 58 | 0 | 37 | 0 | 0 | 17 | 35 | 320 | 9 | 17 | 17 | 0 | 50 | 17 | 17 | 0 | 48 | 0 | 360 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 17 | 35 | 230 | 0 | 0 | 440 | 4 | 270 | 0 | 0 |  | 443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 282 | 0 | 0 | 50 | 0 | 6 | 0 | 0 | 0 | 980 | 220 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 377 | 0 | 140 | 745 | 0 | 0 |  | 5326 | 3622 | 8948 | 3208 | 443 | 1394 | 0 | 593 | 3122 | 86 | 0 | 0 | 98 | 0 | 4 | 0 | 97.25
24:00 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 352 | 0 |  | 0 | 360 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 15 | 25 | 26 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 12 | 16 | 0 | 0 | 0 | 280 | 250 | 0 | 8 | 0 | 46 | 36 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 10 | 100 | 84 | 0 | 0 | 0 | 43 | 28 | 26 | 25 | 0 | 0 | 60 | 0 | 0 | 163 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 58 | 0 | 14 | 0 | 0 | 17 | 8 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 27 | 0 | 360 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 18 | 17 | 230 | 0 | 0 | 440 | 4 | 270 | 0 | 0 |  | 443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 980 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 140 | 759 | 0 | 0 |  | 5083 | 3533 | 8616 | 3201 | 443 | 1430 | 0 | 216 | 3136 | 86 | 0 | 0 | 100 | 0 | 4 | 0 | 97.25
KWH | 0 | 0 | 0 | 4378500 | 0 | 1245136 | 0 | 8153090 | 0 |  | 0 | 8483300 | 0 | 186240 | 269634 | 323274 | 6754685 | 0 | 0 | 309226 | 133056 | 524160 | 54365 | 0 | 0 | 0 | 129960 | 134296 | 134785 | 142632 | 48000 | 340200 | 629800 | 636400 | 194880 | 0 | 1273860 | 796000 | 0 | 0 | 62209 | 4479138 | 0 | 0 | 0 |  | 78240 | 199440 | 65258 | 90840 | 0 | 181440 | 278256 | 274560 | 0 | 0 | 0 | 7470900 | 6273000 | 0 | 83636 | 0 | 886176 | 459840 | 0 | 850588 | 0 | 0 | 122842 | 414252 | 208980 | 633700 | 193180 | 2417280 | 1397760 | 0 | 0 | 5300 | 1015000 | 694920 | 458400 | 455760 | 0 | 0 | 1274784 | 0 | 0 | 3691600 | 0 | 0 | 194040 | 7154000 | 279168 | 158100 | 0 | 1337345 | 0 | 0 | 1046400 | 0 | 711792 | 58725 | 0 | 1284960 | 444945 | 8458000 | 237600 | 858269 | 214945 | 11160 | 1031236 | 324789 | 265130 | 193800 | 458640 | 0 | 9025300 | 395520 | 113970 | 427680 | 267218 | 0 | 140760 | 54488 | 416640 | 368280 | 6358800 | 419855 | 0 | 10701817 | 134880 | 6494545 | 0 | 0 |  | 10600727 | 0 | 0 | 0 | 269760 | 0 | 0 | 0 | 0 | 0 | 14625 | 1951000 | 378700 | 0 | 0 | 0 | 0 | 0 | 0 | 109848 | 0 | 28284 | 0 | 62875 | 0 | 0 | 0 | 145332 | 0 | 0 | 4152300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6883272 | 85490 | 0 | 641568 | 0 | 652857 | 0 | 22247 | 581760 | 24308000 | 5018182 | 0 | 292800 | 10680 | 182880 | 653568 | 0 | 0 | 9061818 | 88925 | 3425500 | 16925455 | 413310 | 0 |  | 130035555 | 86961763 | 216997318 | 76370653 | 10600727 | 31939414 | 0 | 16114823 | 75069435 | 2069860 | 0 | 1318561 | 2417280 | 961685 | 134880 | 0
Fuel Cost | 0 | 0 | 0 | 6523965 | 0 | 1656030.88 | 0 | 8560744.5 | 0 |  | 0 | 9246797 | 0 | 2082163.2 | 3572650.5 | 4283380.5 | 7565247.2 | 0 | 0 | 4520884.12 | 1872097.92 | 8496633.6 | 501245.3 | 0 | 0 | 0 | 1653091.2 | 1812996 | 1807466.85 | 106974 | 36000 | 0 | 0 | 0 | 3314908.8 | 0 | 343942.2 | 214920 | 0 | 0 | 1017117.15 | 4658303.52 | 0 | 0 | 0 |  | 1021032 | 3326659.2 | 1110691.16 | 1227248.4 | 0 | 2099260.8 | 353385.12 | 914284.8 | 0 | 0 | 0 | 8292699 | 6837570 | 0 | 107890.44 | 0 | 1001378.88 | 685161.6 | 0 | 1420481.96 | 0 | 0 | 1652224.9 | 567525.24 | 156735 | 1108975 | 144885 | 17356070.4 | 1523558.4 | 0 | 0 | 84482 | 1390550 | 917294.4 | 797616 | 788464.8 | 0 | 0 | 2473080.96 | 0 | 0 | 3728516 | 0 | 0 | 384199.2 | 7154000 | 209376 | 120156 | 0 | 18254759.25 | 0 | 0 | 14105472 | 0 | 9858319.2 | 686495.25 | 0 | 17552553.6 | 5904420.15 | 7781360 | 2889216 | 12410569.74 | 2719054.25 | 173649.6 | 12106710.64 | 3536952.21 | 2818331.9 | 2629866 | 5911869.6 | 0 | 8303276 | 5121984 | 1646866.5 | 5427259.2 | 3040940.84 | 0 | 1838325.6 | 651131.6 | 6237100.8 | 4850247.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 31802181 | 0 | 0 | 0 | 2808201.6 | 0 | 0 | 0 | 0 | 0 | 210161.25 | 2185120 | 734678 | 0 | 0 | 0 | 0 | 0 | 0 | 1718022.72 | 0 | 468383.04 | 0 | 856986.25 | 0 | 0 | 0 | 110016.324 | 0 | 0 | 35211504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6814439.28 | 1148985.6 | 0 | 7589749.44 | 0 | 8291283.9 | 0 | 245829.35 | 7062566.4 | 201756400 | 5118545.64 | 0 | 2166720 | 120790.8 | 2145182.4 | 10019197.44 | 0 | 0 | 82371925.62 | 0 | 41003235 | 144712640.25 | 0 | 0 |  | 299259743.63 | 596672745.304 | 895932488.934 | 74656691.544 | 31802181 | 35822589.6 | 0 | 210273955.14 | 505055704.87 | 558862.2 | 0 | 14652006.68 | 17356070.4 | 5754427.5 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 371 | 0 |  | 0 | 450 | 0 | 0 | 4 | 18 | 310 | 0 | 0 | 4 | 0 | 6 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 15 | 25 | 26 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 179 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 280 | 265 | 0 | 0 | 0 | 34 | 23 | 0 | 43 | 0 | 0 | 0 | 18 | 11 | 25 | 10 | 110 | 34 | 0 | 0 | 1 | 43 | 27 | 25 | 25 | 0 | 0 | 19 | 0 | 0 | 158 | 0 | 0 | 10 | 315 | 8 | 5 | 0 | 10 | 0 | 0 | 58 | 0 | 35 | 11 | 0 | 100 | 14 | 365 | 9 | 35 | 17 | 2 | 20 | 0 | 17 | 0 | 27 | 0 | 310 | 17 | 14 | 54 | 17 | 0 | 0 | 11 | 18 | 17 | 320 | 35 | 0 | 490 | 1 | 0 | 0 | 0 |  | 438 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 0 | 0 | 35 | 0 | 33 | 0 | 3 | 35 | 1000 | 220 | 0 | 7 | 1 | 23 | 0 | 0 | 0 | 380 | 18 | 140 | 758 | 86 | 0 |  | 9039 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 339 | 0 |  | 0 | 450 | 0 | 40 | 68 | 55 | 288 | 0 | 0 | 80 | 63 | 118 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 10 | 20 | 14 | 25 | 26 | 17 | 0 | 46 | 40 | 0 | 0 | 16 | 194 | 0 | 0 | 0 | 0 | 6 | 40 | 0 | 12 | 0 | 19 | 13 | 2 | 0 | 0 | 0 | 300 | 295 | 0 | 8 | 0 | 47 | 24 | 0 | 51 | 0 | 0 | 36 | 18 | 11 | 33 | 8 | 102 | 35 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 59 | 0 | 0 | 164 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 280 | 0 | 0 | 77 | 0 | 67 | 0 | 0 | 20 | 55 | 384 | 28 | 105 | 17 | 0 | 106 | 36 | 17 | 76 | 47 | 0 | 400 | 72 | 0 | 17 | 17 | 0 | 13 | 0 | 40 | 35 | 230 | 33 | 0 | 490 | 11 | 0 | 0 | 0 |  | 428 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 8 | 130 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246 | 0 | 0 | 50 | 0 | 100 | 0 | 0 | 55 | 1244 | 222 | 0 | 17 | 0 | 0 | 114 | 0 | 0 | 375 | 0 | 140 | 760 | 0 | 0 |  | 10838 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 375 | 0 |  | 0 | 450 | 0 | 92 | 85 | 55 | 300 | 0 | 0 | 90 | 100 | 149 | 36 | 0 | 0 | 0 | 17 | 35 | 35 | 15 | 20 | 18 | 33 | 33 | 16 | 0 | 46 | 40 | 0 | 0 | 17 | 190 | 0 | 0 | 0 |  | 6 | 65 | 17 | 12 | 0 | 18 | 12 | 20 | 0 | 0 | 0 | 320 | 300 | 0 | 8 | 0 | 47 | 25 | 0 | 51 | 0 | 20 | 52 | 18 | 11 | 33 | 10 | 140 | 50 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 60 | 0 | 0 | 163 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 300 | 0 | 0 | 65 | 0 | 60 | 0 | 0 | 200 | 150 | 400 | 25 | 105 | 17 | 0 | 100 | 36 | 17 | 114 | 55 | 0 | 400 | 90 | 0 | 54 | 17 | 0 | 17 | 0 | 53 | 35 | 390 | 150 | 0 | 500 | 10 | 0 | 0 | 0 |  | 449 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 45 | 0 | 16 | 130 | 25 | 110 | 0 | 0 | 0 | 30 | 20 | 86 | 28 | 42 | 40 | 52 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 90 | 0 | 55 | 0 | 113 | 0 | 0 | 70 | 622 | 220 | 0 | 150 | 0 | 0 | 110 | 0 | 0 | 370 | 0 | 140 | 748 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 330 | 0 | 0 | 0 | 450 | 0 | 92 | 85 | 55 | 300 | 0 | 0 | 90 | 100 | 100 | 36 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 20 | 18 | 33 | 33 | 8 | 0 | 46 | 40 | 0 | 0 | 8 | 190 |  | 0 | 0 | 0 | 6 | 50 | 0 | 12 | 0 | 6 | 12 | 10 | 0 | 0 | 0 | 320 | 300 | 0 | 8 | 0 | 47 | 25 | 0 | 51 | 0 | 0 | 52 | 18 | 11 | 33 | 10 | 128 | 75 | 0 | 0 | 1.6 | 43 | 28 | 25 | 25 | 0 | 0 | 60 | 0 | 0 | 163 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 300 | 0 | 0 | 56 | 0 | 35 | 20 | 0 | 200 | 150 | 400 | 8 | 52 | 17 | 5 | 100 | 17 | 17 | 114 | 28 | 0 | 400 | 90 | 50 | 18 | 17 | 0 | 17 | 35 | 17 | 17 | 390 | 150 |  | 500 | 10 | 0 | 0 | 0 |  | 449 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 21 | 110 | 0 | 0 | 0 | 0 | 0 | 40 | 28 | 34 | 30 | 52 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 90 | 0 | 35 | 0 | 34 | 0 | 8 | 35 | 622 | 220 |  | 0 | 6 | 100 | 70 | 0 |  | 370 | 30 | 140 | 748 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 64 | 0 | 325 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 15 | 17 | 27 | 8 | 0 | 76 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 10 | 4 | 0 | 0 | 0 | 290 | 300 | 0 | 8 | 0 | 42 | 10 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 10 | 86 | 73 | 0 | 0 | 0 | 43 | 28 | 25 | 20 | 0 | 0 | 63 | 0 | 0 | 163 | 0 | 0 | 10 | 310 | 8 | 5 | 0 | 0 | 0 | 0 | 24 | 0 | 17 | 6 | 0 | 17 | 1 | 370 | 9 | 17 | 2 | 1 | 10 | 0 | 3 | 0 | 9 | 0 | 400 | 0 | 4 | 0 | 7 | 0 | 0 | 3 | 17 | 7 | 393 | 0 | 0 | 397 | 0 | 272 | 0 | 0 | 0 | 443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 740 | 220 | 0 | 0 | 0 | 10 | 16 | 0 | 0 | 379 | 5 | 140 | 611 | 14 | 0 | 0 |  |  |  | 108310067 | 10600727 | 0 | 75069435 | 17433384 | 2417280 | 961685 | 134880 | 2069860
[8 empty] | 299430 | [13 empty] | 299565 | [26 empty] | 399366 | 399587 | [8 empty] | 299280 | [26 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 |  | 399747 |  |  |  | 399575 | 399337 | 399467 | 399589 | 299230 | [7 empty] | 399245 |  | 299282 | 399274 |  | 399223 |  | 399630 | [12 empty] | 599468 | [32 empty] | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 | [8 empty] | 599726 | [9 empty] | 108.3101 | 10.6007 | 0 | 75.0694 | 17.4334 | 2.4173 | 0.96169 | 0.13488 | 2.0699
| Minimum Generation |  | 7347 | 5:00
| Highest Generation |  | 10838 | 18:00 | [200 empty] | 216.9973
| Day Peak Generation |  | 9039 | 12:00
| Evening Peak Generation |  | 10838 | 18:00 | [200 empty] | 202699852
| HVDC Max Flow |  | 443 | 2:00 | [200 empty] | 202.6999
| HVDC EvPeak Flow |  | 428 | 18:00
| Load factor L.F |  | 83.42% | [166 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-12-06
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-12-05 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9039 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 7309
Evening Peak Generation : |  |  | 10838 | MW Hour : | 18:00 | Available Max Generation : |  | 12216
E.P. Demand (at gen end) : |  |  | 10838 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 11000
Maximum Generation : |  |  | 10838 | MW Hour : | 18:00 | Reserve(Generation end) |  | 1216
Total Gen. (MKWH) : |  |  | 216.9973 | System Load Factor : | 83.42% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 140 | MW at | 8:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-12-06
Actual : |  | 97.22 | Ft.(MSL) , | Rule curve : | 105.55 | Ft.( MSL )
Gas Consumed : |  | Total = | 814 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 110479281.144
: |  |  | Coal : | 505055704.87 | Oil : | 224925961.82 | Total : | 840460947.834
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3661.4317 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1000.5536 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1399.9249 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1215.2638 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1000.7249 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 743.4794 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 417.6068 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 347.2366 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 679.152 |  |  | 0 | 0%
Total |  | 0 |  | 10465.3737 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:08 | 16:11 | Jhenaidah-Magura 132 kV Ckt-2 Scheduled S/D from Jhenaidahend Due to Annual Maintenance .
08:11 | 16:17 | Narail 132/33kV S/S TR2 (413-T) LT Scheduled S/D Due to Annual maintenance works of Tr-02
08:17 | 16:11 | Ishwardi-Natore 132kV Ckt-2 Scheduled S/D from Natore end Due to Annual maintanance .
08:17 | 16:06 | Mahasthangarh 132/33kV S/S 416T MTR 2 HT Scheduled S/D Due to Annual Maintenance
08:22 | 16:05 | Halishahar 132/33kV S/S Halishahar-Khulshi-Ckt.-3 Scheduled S/D Due to Due to annual maintenance.
08:23 | 16:08 | Khulshi 132/33kV S/S Khulshi-Halishahar CKT-3 Scheduled S/D Due to Annual Maintenance
08:26 | 16:31 | Bhandaria 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Yearly Maintenance.
08:30 | 16:11 | Jamalpur United (20MW)- Sherpur 132kV Ckt-2 Scheduled S/D from Sherpur 132/33kV end Due to Annual Maintenance.
08:39 | 16:30 | Barapukuria-Bogura 230 kV Ckt-2 Scheduled S/D from Barapukuria 230/132/33kV end Due to Annual Maintenance
08:40 | 16:14 | Daudkandi-Sonargaon 132 kV Ckt-1 Scheduled S/D from Daudkandi 132/33kV end Due to Annual Maintenance
08:45 | 16:34 | Rangpur-Rangpur Confidence(100MW) 132kV Ckt-2 Scheduled S/D from Rangpur 132/33kV end Due to Annual maintenance
08:49 | 19:56 | Mirpur 132/33kV S/S T1 LT Scheduled S/D Due to Annual Maintenance
08:52 | 15:16 | Kurigram 132/33kV S/S Transformer T-1 (Tr-403T) HT S/D Due to Annual Maintenance.
08:54 | 13:21 | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 HT Scheduled S/D Due to Annual Maintenance.
08:59 | 16:32 | Tangail 132/33kV S/S RPCL-1 Scheduled S/D Due to Due to Dead line checking
09:00 | 16:00 | Gopalganj 400/132kV S/S 400kV Bus-01 Scheduled S/D Due to Annual maintenance
09:06 | 16:32 | Shahjibazar-Sreemangal 132kV Ckt-1 Scheduled S/D from Shahjibazar 132/33kV end Due to Annual Maintenance.
09:10 | 19:02 | HVDC Bheramera-Ishwardi 230kV Ckt-4 S/D from Ishurdi 230/132kV end Due to A/M and from BIPTC end Due to A/M.
09:13 | 20:24 | Rampur 230/132/33 S/S ATR-02 (716T) HT Scheduled S/D
09:17 | 13:32 | Chattak-Sylhet 132 kV Ckt-2 Scheduled S/D from Sylhet 132/33kV end Due to work of chhatak end
09:24 | 15:08 | Naogaon 132/33kV S/S T-3 HT Scheduled S/D Due to annual maintenance
09:24 | 15:10 | Ashuganj-Ghorasal 132kV Ckt-1 Scheduled S/D from Ashuganj 230/132/33kV end Due to Annual maintenance work
09:49 | 14:51 | Cumilla(N)-Meghnaghat 230 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to Relay test (SPMD)
09:53 | 11:49 | Aminbazar-Kaliakoir 230kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to relay test by SPMD
09:56 | 16:47 | Cumilla(S) 132/33kV S/S TR-1 LT Scheduled S/D
10:06 | 16:27 | Jashore 132/33kV S/S JH-2(L1) Scheduled S/D Due to Requested By Jhenaidah 230/132KV S/S
10:07 | 16:26 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-2 Project Work S/D Due to Circuit breaker punch point problem clear
10:18 | 19:09 | BIPTC S/S 20DF41 Scheduled S/D Due to Annual Maintenance.
10:50 | 14:18 | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) LT Project Work S/D Due to SCADA Integration with NLDC.
10:53 |  | Matarbari 2*600 MW (CPGCL) Shutdown with remarks:- manual update
11:30 | 19:07 | BIPTC S/S 230kV Bus-2 Scheduled S/D Due to Annual Maintenance
11:55 | 11:57 | Dhamrai-Kaliakoir 132 kV Ckt-2 Project Work S/D from Dhamrai 132/33kV end Due to Work at Kaliakoir end. |  |  |  |  | 100 MW power interrupt.
11:55 | 11:57 | Dhamrai-Kaliakoir 132 kV Ckt-1 Scheduled S/D from Dhamrai 132/33kV end Due to Work on kaliakoir end.
13:13 | 16:26 | Kabirpur-Kaliakoir 132kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to Relay Test by SPMD.
15:14 | 17:22 | Cumilla(N)-Meghnaghat 230 kV Ckt-2 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to Relay testing
| 15:44 | Khulna (C) S/S Tr-3 405T HT is restored.
| 15:54 | Sirajganj-Sreepur 230 kV Ckt-1 is restored.
| 15:58 | Sreepur 230/132/33kV S/S Sreepur-Sirajganj Ckt-1 is restored.
| 16:18 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50MVA) HT is restored.
| 16:39 | Kachua 132/33kV S/S Main Bus-1 is restored.
| 16:39 | Kachua 132/33kV S/S Main Bus-2 is restored.
| 16:40 | Cumilla(S)-Kachua 132 kV Ckt-1 is restored.
16:42 |  | Bhola CCPP GT1 was sync.
16:42 |  | Bhola 225 MW CCPP Syncronized with remarks:- GT1
| 16:46 | Kachua 132/33kV S/S TR-1 HT is restored.
| 16:51 | Kabirpur 132/33kV S/S XFR, T-3 HT is restored.
| 17:01 | Kachua 132/33kV S/S TR-2 HT is restored.
| 17:05 | Candpur- Kachua 132kV Ckt-1 is restored.
| 17:05 | Candpur- Kachua 132kV Ckt-2 is restored.
| 17:42 | Cumilla(N)-Kachua 132 kV Ckt-2 is restored.
18:24 |  | Matarbari 2*600 MW (CPGCL) Syncronized
18:24 |  | Matarbari Unit-1 was sync.
| 19:55 | Hasnabad 230/132kV S/S AUTO TR-2 HT is restored.
06:18 |  | Cumilla(N)-Kachua 132 kV Ckt-2 Project Work S/D from Kachua 132/33kV end Due to None |  |  |  |  | 09 MW power interrupt.
06:18 |  | Cumilla(S)-Kachua 132 kV Ckt-1 Project Work S/D from Kachua end and Cumilla(S) 132/33kV end Due to Annual maintenance.
06:20 | 06:52 | Siddhirganj 132/33kV S/S T-1 HT Tripped showing O/C (50)relays Due to DPDC ends 33kv Bus Problem |  |  |  |  | 34 MW power interrupt.
06:20 |  | Siddhirganj 132/33kV S/S T-2 LT Tripped showing O/C relays Due to DPDC ends 33kv Bus Problem
06:20 | 07:00 | Siddhirganj 132/33kV S/S T-1 LT Tripped showing O/C, ABC-ph, E/F relays Due to DPDC ends 33kv Bus Problem
06:26 |  | Kachua 132/33kV S/S Main Bus-1 Project Work S/D
06:27 |  | Kachua 132/33kV S/S Main Bus-2 Project Work S/D
06:27 |  | Kachua 132/33kV S/S TR-2 HT Project Work S/D Due to None
06:29 |  | Candpur- Kachua 132kV Ckt-1 Project Work S/D from Kachua end and Chandpur 132/33kV end Due to project work
06:33 |  | Candpur- Kachua 132kV Ckt-2 Project Work S/D from Kachua end Due to None and from Chandpur 132/33kV end Due to project work
06:58 |  | Kabirpur -Kodda 132kV Ckt-1 Scheduled S/D from Kabirpur 132/33kV end Due to OPGW change work.
06:58 |  | Kabirpur -Kodda 132kV Ckt-2 Scheduled S/D from Kabirpur end Due to OPGW change work
07:42 |  | Narail 132/33kV S/S TR2 (413-T) LT Scheduled S/D Due to Annual Maintenance.
07:59 |  | Chapai 132/33kV S/S T-1 (405T) HT Scheduled S/D Due to Annual maintenance
| Sub Divisional Engineer |  |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-12-05 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4378500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 73 | 1245136 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 339 | 8153090 | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8483300 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 40 | 186240 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 68 | 269634 | Machine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 323274
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 54365 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 10 | 142632 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 80 | 309226 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 288 | 6754685 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 63 | 133056 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 129960 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 118 | 524160 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 134296 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 134785 | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 34 | 388200 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 629800 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 26 | 636400
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 17 | 194880 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 280 | 1337345 | Engine problem
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 67 | 711792 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 858269
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 72 | 395520 | Low demand
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 427680 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 54488
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 368280 | Fuel shortage
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5422 | 2529 | 37358993
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 16 | 62209 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 58725
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 181440 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 86 | 2069860 | Unit-2 under maint.
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 194 | 4479138 | Machine problem
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 214945 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 40 | 199440 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 65258 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 12 | 90840 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 13 | 278256 | Fuel shortage
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 2 | 274560
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 11160
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 106 | 1031236 | Low demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 324789 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 265130 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 267218 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 33 | 419855 | Fuel shortage
| SS Power I |  | SS Power | 2*612 | 1224 | 490 | 10701817
| Cox's Bazar Wind |  | IPP | 66 | 0 | 11 | 134880 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 0 | 6494545 | On test.
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0
| Chattogram area Total |  |  |  | 3769 | 1109 | 27625301
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 0 | Under maint.
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 300 | 7470900 | Under maint.
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 295 | 6273000
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 230 | 6358800 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 47 | 886176
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 0 | 24 | 459840
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 83636 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 850588 | Engine problem
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 55 | 444945 | High voltage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 20 | 1284960 | Machine problem
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 414252 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 208980
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 102 | 2417280
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 633700
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 36 | 122842 | Low demand
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 8 | 193180 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 76 | 193800 | Low demand
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 47 | 458640 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 13 | 140760 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 40 | 416640 | Fuel shortage
| Cumilla Area Total |  |  |  | 2896 | 1414 | 29312919
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 35 | 1397760 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Contract Expired
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 5300
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 77 | 1046400 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 28 | 237600 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 113970
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 78240 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 146 | 2879270
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1015000
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 28 | 694920 | Engine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 25 | 458400 | Gas shortage
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 25 | 455760 | Gas shortage
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 158100 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 59 | 1274784
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 0 | 0 | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 164 | 3691600
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 279168 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7154000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 384 | 8458000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 194040
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9025300
| Sylhet Area Total |  |  |  | 2427 | 1452 | 32859072
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 428 | 10600727 | Pole-2 shut down
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 49 | 269760 | Low demand
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 14625 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 85490 | Reserve
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 182880
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | Fuel shortage
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 375 | 9061818 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 860 | 20215300
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 19 | 378700 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 130 | 1951000
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 24308000
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 222 | 5018182
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 292800 | Low demand
| Barisal 307 MW |  | IPP | 307*1 | 307 | 140 | 3425500 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1772 | 35374182
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 28284
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 246 | 6883272 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 145332
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 62875 | Low demand
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 109848 | Reserve
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 641568 | Machine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 55 | 581760 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 10680
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 760 | 16925455
| Rajshahi Area Total |  |  |  | 3631 | 1172 | 25389074
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4152300 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 100 | 652857 | Machine problem
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 22247
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 114 | 653568
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 88925
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 413310
| Rangpur Area Total |  |  |  | 950 | 384 | 5983207
| Total |  |  |  | 25211 | 10838 | 216997318
| Eastern Grid Total |  |  |  | 15128 | 6650 | 130035555
| Western Grid Total |  |  |  | 10083 | 4188 | 86961763
| National Grid Total |  |  |  | 25211 | 10838 | 216997318
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-12-05
| (a) ENTIRE EASTERN GRID : |  | 7312.78 | MW | (b) ENTIRE WESTERN GRID : |  | 3091.6 | MW
| i) Dhaka area |  | 4121.78 | MW | i) Khulna area |  | 1130.3 | MW
| ii) Chittagong area |  | 1144 | MW | ii) Rajshahi area |  | 967.8 | MW
| iii) Comilla area |  | 891 | MW | iii) Barisal area |  | 278.5 | MW
| iv) Mymensingh area |  | 782 | MW | iv) Rangpur area |  | 715 | MW
| v) Sylhet area |  | 374 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10404.38 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 18 | 17:00 | Kamrangirchar | 54 | 21:00 | Narinda | 54 | 12:00 | Sherpur | 96 | 18:00
2 | AKSML | 13 | 19:00 | Chowmuhani | 138 | 18:00 | Kaptai | N/A | N/A | Narshingdi | 142 | 19:00 | Shikalbaha | 26 | 11:00
3 | Aftabnagar | 28 | 13:00 | Chuadanga | 67 | 18:00 | Kazla | 82 | 13:00 | Natore | 93 | 18:30 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 72 | 13:00 | Coxsbazar | 105 | 19:00 | Keranigonj | 66 | 18:00 | Nawabganj | 34 | 20:00 | Shitalakhya | 90.5 | 12:00
5 | Agrabad | 52 | 11:00 | Cumilla(N) | 115 | 18:30 | Khagrachori | 22 | 18:00 | Netrakona | 90 | 18:00 | Sholosohor | 36 | 12:00
6 | Amnura | 26 | 08:00 | Cumilla(S) | 120 | 14:00 | Khulna | 74 | 13:00 | New | 60 | 11:00 | Shyampur | 144 | 11:00
7 | Ashuganj | 54 | 00:00 | Daudkandi | 128 | 18:00 | Khulshi | 159 | 17:00 | Niamatpur | 48 | 13:00 | Siddhirganj | 100 | 11:00
8 | BIPTC | N/A | N/A | Dhaka | 22 | 11:00 | Kishoreganj | 100 | 18:30 | Noapara | 37 | 18:00 | Sirajganj | 97 | 18:30
9 | BSRM | 112 | 03:00 | Dhamrai | 120 | 11:00 | Kodda | 249 | 18:30 | PHP | 7 | 10:00 | Sonargaon | 78 | 12:00
10 | Bagerhat | 62 | 18:30 | Dhanmondi | 99 | 13:00 | Kulaura | 30 | 18:00 | Pabna | 81 | 18:00 | Sreemongol | 43 | 18:00
11 | Bakulia | 74 | 13:00 | Dohazari | 54 | 18:30 | Kurigram | 46 | 07:00 | Palashbari | 82 | 18:00 | Sreepur | 62 | 18:30
12 | Banani | 22 | 13:00 | Faridpur | 106 | 20:00 | Kushtia | 98 | 18:00 | Panchagarh | 45 | 18:00 | Srinagar | 30.1 | 20:00
13 | Bangabhaban | 14 | 10:00 | Fatullah | 57 | 11:00 | Lalbag | 74 | 13:00 | Patuakhali | 60 | 20:00 | Sunamganj | 34 | 19:30
14 | Barapukuria | 52 | 18:00 | Fenchuganj | 24 | 18:00 | Lalmonirhat | 36 | 18:00 | Payra | 20 | 19:00 | Sylhet | 10 | 10:00
15 | Barguna | 14 | 21:00 | Feni | 73 | 18:00 | MI_Cement | 18.7 | 04:00 | Postogola | 45 | 13:00 | Sylhet-132 | 94 | 18:00
16 | Barishal | 74 | 12:00 | GPH | 94 | 15:00 | Madanganj | 21 | 19:30 | Purbachal | 13 | 13:00 | TK | 20.5 | 17:00
17 | Barishal-230 | 62 | 18:00 | Ghorashal | 48 | 12:00 | Madaripur | 59 | 21:00 | Purbasadipur | 99 | 18:00 | Tangail | 138 | 18:00
18 | Baroaulia | 68 | 01:00 | Goalpara | 18 | 12:00 | Madartek | 58.77 | 18:00 | Rahim | 49 | 14:00 | Thakurgaon | 75 | 18:00
19 | Baroirhat | 40 | 18:00 | Gollamari | 38 | 13:00 | Madunaghat | 36 | 18:00 | Rajbari | 46 | 18:00 | Tongi | 97 | 17:00
20 | Bashundhara | 120 | 13:00 | Gopalganj | 65.3 | 18:00 | Magura | 40 | 18:00 | Rajendrapur | 74 | 18:00 | Ullon | 43 | 13:00
21 | BashundharaCement | 6 | 12:00 | Gulshan | 88 | 13:00 | Mahasthangarh | 50 | 08:00 | Rajshahi | 99 | 18:00 | Uttara | 55 | 13:00
22 | Beanibazar | 42 | 18:00 | Halishahar | 95.5 | 15:00 | Manikganj | 84 | 18:00 | Rajshahi-230 | 23 | 13:00 | UttaraNew | 44 | 13:00
23 | Benapole | 38 | 08:00 | HaripurSBU | 167 | 10:00 | Maniknagar | 60 | 13:00 | Ramganj | 72 | 18:30 | Zigatola | 76 | 18:00
24 | Bhaluka | 114 | 19:00 | Hasnabad | 59 | 20:00 | Matarbari | 28 | 18:00 | Rampur | 27 | 00:00
25 | Bhandaria | 34 | 20:00 | Hathazari | 52 | 18:00 | Matuail | 62 | 12:00 | Rangamati | 14 | 18:00
26 | Bhangura | 20 | 18:00 | Ishurdi | 57 | 18:00 | Millgate | 90 | 12:00 | Rangpur | 106 | 18:00
27 | Bheramara(GK) | 38 | 18:00 | Jaldhaka | 52 | 18:00 | Mirpur | 111 | 13:00 | Ruppur | 4.6 | 11:00
28 | Bhulta | 234 | 12:00 | Jamalpur | 109 | 18:00 | Mirsorai | 6 | 10:00 | SSM | 15 | 00:00
29 | Bog-Sherpur | 46 | 18:00 | Jashore | 91 | 12:00 | Mirzapur | 20 | 18:00 | Saidpur | 88 | 18:00
30 | Bogura | 112 | 18:00 | Jhenaidah | 89 | 18:00 | Mithapukur | 34 | 08:00 | Satkhira | 80 | 18:00
31 | Borhanuddin | 36 | 22:00 | Joydebpur | 145 | 20:00 | Modern | 0 | 00:00 | Satmasjid | 68 | 13:00
32 | Brahmanbaria | 108 | 21:00 | Joypurhat | 41 | 18:00 | Mogbazar | 74.6 | 12:00 | Savar | 140 | 16:00
33 | Cantonment | 104 | 13:00 | Juldah | 22 | 07:00 | Mongla | 28 | 09:00 | SevenRings | 2.51 | 00:00
34 | Chandpur | 54 | 19:30 | KSRM | 29 | 06:00 | Motijheel | 34 | 12:00 | ShahCement | 24 | 12:00
35 | Chandraghona | 21 | 17:00 | Kabirpur | 259 | 18:00 | Munshiganj | 68 | 13:00 | Shahjadpur | 57 | 18:00
36 | Chapai | 48 | 09:00 | Kachua | 35 | 00:00 | Mymensingh | 153 | 18:00 | Shahjibazar | 85 | 18:30
37 | Charsaidpur | 26 | 15:00 | Kallyanpur | 75 | 04:00 | Naogaon | 87 | 08:00 | Shahmirpur | 50 | 00:00
38 | Chauddagram | 42 | 18:00 | Kalurghat | 34 | 12:00 | Narail | 37 | 18:00 | Shariatpur | 50 | 20:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-12-05 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 402 | 18:30 | 386 | 11:00 | Aminbazar | 408 | 04:00 | 368 | 11:00
| Ashuganj | N/A | N/A | N/A | N/A | Ashuganj | 399 | 18:30 | 381 | 15:00
| Bhulta | 415 | 18:30 | 401 | 10:00 | Bhulta | N/A | N/A | N/A | N/A
| Bibiana | 411 | 17:00 | 401 | 03:00 | Bibiana | 416 | 04:00 | 410 | 11:00
| BIPTC | 411 | 00:00 | 400 | 18:00 | BIPTC | 414 | 05:00 | 400 | 08:00
| Bogura | N/A | N/A | N/A | N/A | Bogura | 410 | 04:00 | 400 | 11:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 238 | 18:30 | 225 | 11:00 | Hasnabad | 237 | 20:00 | 228 | 11:00
| AKSML | 230 | 17:00 | 219 | 01:00 | Hathazari | 231 | 18:30 | 221 | 08:00
| Aminbazar | 238 | 17:00 | 228 | 11:00 | Ishurdi | 235 | 05:00 | 223 | 10:00
| Ashuganj | 238 | 18:30 | 220 | 05:00 | Jhenaidah | 237 | 06:00 | 223 | 10:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 242 | 18:30 | 229 | 10:00
| Baghabari | 229 | 05:00 | 220 | 12:00 | Keranigonj | 238 | 18:30 | 225 | 11:00
| Barapukuria | 227 | 17:00 | 215 | 08:00 | Khulna(S) | 240 | 04:00 | 231 | 11:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 242 | 02:00 | 238 | 11:00 | Maniknagar | 239 | 18:30 | 228 | 11:00
| Bheramara | 236 | 18:30 | 222 | 10:00 | Meghnaghat | 242 | 04:00 | 237 | 09:00
| Bhulta | 240 | 18:30 | 230 | 10:00 | Mirsorai | 236 | 18:30 | 221 | 03:00
| Bibiana | 236 | 18:30 | 228 | 11:00 | Rajshahi | 234 | 04:00 | 220 | 10:00
| BIPTC | 235 | 05:00 | 224 | 10:00 | Rampal | 238 | 04:00 | 229 | 11:00
| Bogura | 232 | 18:30 | 222 | 08:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 244 | 06:00 | 240 | 02:00 | Rampura | 237 | 18:30 | 228 | 10:00
| BSRM | 235 | 19:30 | 224 | 01:00 | Shikalbaha | 227 | 18:30 | 217 | 11:00
| Cumilla(N) | 238 | 18:30 | 226 | 10:00 | Shyampur | 239 | 18:30 | 221 | 12:00
| Fenchuganj | 237 | 18:30 | 231 | 13:00 | Siddhirganj | 241 | 18:30 | 231 | 11:00
| Ghorashal | 240 | 18:00 | 235 | 14:00 | Sirajgonj | 238 | 06:00 | 227 | 11:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 234 | 22:00 | 225 | 10:00
| GPH | 232 | 18:30 | 221 | 01:00 | Tongi | 237 | 19:30 | 225 | 15:00
| Haripur | 239 | 18:30 | 229 | 10:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 134 | 22:00 | 127 | 10:00 | Lalbag | 136 | 18:30 | 128 | 11:00
| Agargaon | 138 | 05:00 | 132 | 10:00 | Lalmonirhat | 132 | 17:00 | 120 | 08:00
| Agrabad | 135 | 18:30 | 127 | 10:00 | Madanganj | 138 | 18:00 | 129 | 10:00
| AKS | 134 | 19:30 | 125 | 11:00 | Madaripur | 136 | 06:00 | 132 | 10:00
| Aminbazar | 139 | 17:00 | 131 | 10:00 | Madartek | 133 | 20:00 | 127 | 10:00
| Amnura | 136 | 03:00 | 130 | 09:00 | Madunaghat | 136 | 19:30 | 129 | 10:00
| Ashuganj | 140 | 17:00 | 136 | 10:00 | Magura | 137 | 06:00 | 130 | 09:00
| Bagerhat | 133 | 05:00 | 125 | 08:00 | Mahasthangarh | 136 | 18:30 | 126 | 08:00
| Bakulia | 136 | 18:30 | 129 | 10:00 | Manikganj | 136 | 18:30 | 124 | 12:00
| Banani | 136 | 18:30 | 128 | 11:00 | Maniknagar | 136 | 18:30 | 125 | 16:00
| Bangabhaban | 136 | 18:30 | 130 | 10:00 | Matarbari | 126 | 09:00 | 121 | 00:00
| Barapukuria | 138 | 17:00 | 127 | 08:00 | Matuail | 137 | 18:30 | 129 | 10:00
| Barguna | 136 | 06:00 | 134 | 00:00 | Millgate | 139 | 18:30 | 131 | 09:00
| Barishal | 139 | 05:00 | 131 | 10:00 | Mirpur | 139 | 13:00 | 129 | 11:00
| Barishal-230 | 139 | 05:00 | 135 | 10:00 | Mirzapur | 133 | 18:00 | 128 | 00:00
| Baroaulia | 137 | 18:30 | 129 | 00:00 | Mithapukur | 137 | 18:30 | 123 | 08:00
| Baroirhat | 134 | 18:30 | 127 | 11:00 | MI_Cement | 139 | 18:30 | 129 | 11:00
| Bashundhara | 135 | 04:00 | 128 | 11:00 | Modern | 135 | 18:30 | 129 | 11:00
| BashundharaCement | 138 | 18:00 | 129 | 10:00 | Mogbazar | 134 | 04:00 | 123 | 19:00
| Beanibazar | 131 | 02:00 | 128 | 10:00 | Mongla | 132 | 04:00 | 125 | 10:00
| Benapole | 135 | 04:00 | 126 | 11:00 | Motijheel | 136 | 18:30 | 130 | 10:00
| Bhaluka | 132 | 04:00 | 128 | 10:00 | Munshiganj | 139 | 18:30 | 132 | 03:00
| Bhandaria | 135 | 01:00 | 132 | 00:00 | Mymensingh | 135 | 09:00 | 126 | 10:00
| Bhangura | 141 | 05:00 | 133 | 10:00 | Naogaon | 134 | 17:00 | 124 | 08:00
| Bheramara | 136 | 03:00 | 129 | 10:00 | Narail | 138 | 06:00 | 129 | 08:00
| Bheramara(GK) | 136 | 03:00 | 129 | 10:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 126 | 18:30 | 118 | 10:00 | Narshingdi | 132 | 18:30 | 121 | 10:00
| Bog-Sherpur | 137 | 05:00 | 128 | 08:00 | Natore | 136 | 02:00 | 128 | 10:00
| Bogura | 137 | 17:00 | 130 | 08:00 | Nawabganj | 137 | 18:30 | 129 | 10:00
| Bogura-230 | 137 | 18:30 | 129 | 08:00 | Netrakona | 134 | 08:00 | 125 | 17:00
| Brahmanbaria | 129 | 06:00 | 126 | 12:00 | New | 140 | 20:00 | 132 | 09:00
| Cantonment | 138 | 05:00 | 131 | 11:00 | Niamatpur | 133 | 17:00 | 123 | 08:00
| Chandpur | 144 | 12:00 | 129 | 21:00 | Noapara | 135 | 05:00 | 127 | 11:00
| Chandraghona | 137 | 18:30 | 129 | 10:00 | Pabna | 138 | 03:00 | 131 | 10:00
| Chapai | 136 | 03:00 | 130 | 10:00 | Palashbari | 135 | 18:30 | 122 | 08:00
| Charsaidpur | 139 | 18:30 | 129 | 10:00 | Panchagarh | 137 | 17:00 | 115 | 08:00
| Chauddagram | 138 | 18:30 | 123 | 00:00 | Patuakhali | 137 | 22:00 | 133 | 00:00
| Chhatak | 131 | 03:00 | 128 | 10:00 | Payra | 137 | 02:00 | 135 | 09:00
| Chowmuhani | 137 | 18:30 | 120 | 00:00 | PHP | 138 | 18:30 | 127 | 01:00
| Chuadanga | 136 | 06:00 | 127 | 08:00 | Postogola | 139 | 18:30 | 131 | 10:00
| Coxsbazar | 125 | 08:00 | 120 | 00:00 | Purbachal | 137 | 00:00 | 128 | 11:00
| Cumilla(N) | 140 | 18:30 | 132 | 10:00 | Purbasadipur | 136 | 16:00 | 115 | 08:00
| Cumilla(S) | 141 | 18:30 | 129 | 10:00 | Rahanpur | 138 | 03:00 | 132 | 08:00
| Daudkandi | 136 | 18:30 | 128 | 10:00 | Rahim | 138 | 18:30 | 130 | 10:00
| Dhaka | 134 | 22:00 | 127 | 10:00 | Rajbari | 134 | 04:00 | 129 | 11:00
| Dhamrai | 135 | 18:30 | 125 | 11:00 | Rajendrapur | 137 | 19:00 | 123 | 02:00
| Dhanmondi | 138 | 18:30 | 129 | 11:00 | Rajshahi | 136 | 04:00 | 129 | 10:00
| Dohazari | 132 | 18:00 | 126 | 01:00 | Rajshahi-230 | 136 | 04:00 | 129 | 08:00
| Faridpur | 134 | 06:00 | 129 | 13:00 | Ramganj | 136 | 18:30 | 126 | 17:00
| Fatullah | 137 | 17:00 | 130 | 10:00 | Rampur | 134 | 07:00 | 128 | 09:00
| Fenchuganj | 135 | 18:30 | 131 | 01:00 | Rampura | 135 | 05:00 | 128 | 12:00
| Feni | 136 | 18:30 | 130 | 05:00 | Rangamati | 136 | 18:30 | 130 | 01:00
| Ghorashal | 142 | 18:00 | 137 | 13:00 | Rangpur | 134 | 17:00 | 120 | 08:00
| Goalpara | 136 | 22:00 | 128 | 11:00 | Ruppur | 140 | 06:00 | 132 | 08:00
| Gollamari | 134 | 03:00 | 128 | 12:00 | Saidpur | 135 | 17:00 | 120 | 08:00
| Gopalganj | 134 | 06:00 | 129 | 10:00 | Satkhira | 134 | 04:00 | 126 | 08:00
| Gopalganj-400 | 134 | 04:00 | 130 | 10:00 | Satmasjid | 139 | 18:30 | 131 | 11:00
| Gulshan | 135 | 22:00 | 128 | 10:00 | Savar | 139 | 13:00 | 129 | 10:00
| Halishahar | 136 | 20:00 | 128 | 10:00 | SevenRings | 142 | 18:30 | 136 | 11:00
| Haripur | 138 | 18:30 | 130 | 10:00 | ShahCement | 139 | 18:30 | 129 | 10:00
| HaripurSBU | 130 | 12:00 | 123 | 21:00 | Shahjadpur | 142 | 01:00 | 138 | 09:00
| Hasnabad | 138 | 17:00 | 130 | 11:00 | Shahjibazar | 129 | 03:00 | 126 | 12:00
| Hathazari | 136 | 18:30 | 130 | 08:00 | Shahmirpur | 135 | 19:30 | 129 | 10:00
| Ishurdi | 139 | 03:00 | 132 | 10:00 | Shariatpur | 135 | 06:00 | 131 | 10:00
| Jaldhaka | 135 | 17:00 | 118 | 08:00 | Sherpur | 132 | 20:00 | 120 | 07:00
| Jamalpur | 136 | 12:00 | 125 | 01:00 | Shikalbaha | 125 | 18:30 | 118 | 03:00
| Jashore | 134 | 05:00 | 126 | 10:00 | Shikalbaha-230 | 137 | 19:30 | 130 | 11:00
| Jhenaidah | 138 | 04:00 | 131 | 10:00 | Shitalakhya | 140 | 18:30 | 129 | 11:00
| Jhenaidah-230 | 139 | 05:00 | 131 | 10:00 | Sholosohor | 135 | 20:00 | 128 | 10:00
| Joydebpur | 140 | 17:00 | 133 | 10:00 | Shyampur | 137 | 18:30 | 130 | 10:00
| Joypurhat | 134 | 05:00 | 124 | 08:00 | Shyampur-230 | 138 | 18:30 | 130 | 10:00
| Juldah | 136 | 18:00 | 130 | 00:00 | Siddhirganj | 137 | 18:30 | 129 | 10:00
| Kabirpur | 136 | 18:30 | 122 | 10:00 | Sirajganj | 137 | 01:00 | 128 | 08:00
| Kachua | 138 | 18:30 | 127 | 01:00 | Sonargaon | 139 | 18:00 | 129 | 11:00
| Kaliakoir | 138 | 18:30 | 128 | 10:00 | Sreemongol | 131 | 08:00 | 129 | 10:00
| Kallyanpur | 136 | 18:30 | 132 | 09:00 | Sreepur | 134 | 22:00 | 125 | 10:00
| Kalurghat | 136 | 20:00 | 130 | 00:00 | Srinagar | 136 | 18:30 | 129 | 11:00
| Kamrangirchar | 136 | 19:30 | 129 | 11:00 | SSM | 140 | 18:30 | 131 | 09:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 129 | 03:00 | 127 | 11:00
| Kazla | 135 | 06:00 | 128 | 11:00 | Sylhet | 131 | 06:00 | 129 | 01:00
| Keranigonj | 137 | 18:30 | 129 | 11:00 | Sylhet-132 | 131 | 06:00 | 129 | 01:00
| Khagrachori | 135 | 18:30 | 129 | 10:00 | Tangail | 134 | 12:00 | 127 | 07:00
| Khulna | 134 | 06:00 | 127 | 11:00 | Thakurgaon | 139 | 18:30 | 113 | 08:00
| Khulna(S) | 134 | 02:00 | 128 | 11:00 | TK | 136 | 19:00 | 130 | 01:00
| Khulshi | 134 | 18:30 | 127 | 10:00 | Tongi | 141 | 18:00 | 132 | 11:00
| Kishoreganj | 135 | 05:00 | 130 | 10:00 | Ullon | 133 | 05:00 | 127 | 10:00
| Kodda | 140 | 20:00 | 125 | 15:00 | Uttara | 139 | 14:00 | 130 | 10:00
| KSRM | 136 | 18:30 | 128 | 11:00 | UttaraNew | 139 | 20:00 | 129 | 11:00
| Kulaura | 132 | 00:00 | 131 | 11:00 | Zigatola | 137 | 18:30 | 129 | 11:00
| Kurigram | 133 | 17:00 | 117 | 07:00
| Kushtia | 137 | 04:00 | 130 | 08:00

## L-Curve
Date | 2023-12-05
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 288 | 5083 | 3533 | 8616 |  |  |  | QF-LDC-11
0:30 | 334 | 5048.5 | 3432 | 8480.5 | Date: | 2023-12-05
1:00 | 380 | 5014 | 3331 | 8345
1:30 | 370 | 4916.5 | 3275.5 | 8192
2:00 | 360 | 4819 | 3220 | 8039
2:30 | 355 | 4792 | 3142.5 | 7934.5 | [5 empty] | Gen. at Eve. Peak | 10838 | 10838 MW (18:00 )
3:00 | 350 | 4765 | 3065 | 7830 | [6 empty] | 18:00
3:30 | 315 | 4663 | 2974.5 | 7637.5 | [5 empty] | Gen. at Day Peak | 9039 | 9039 MW (12:00 )
4:00 | 280 | 4561 | 2884 | 7445 | [6 empty] | 12:00
4:30 | 290 | 4538 | 2858 | 7396 | [5 empty] | Highest Generation | 10838
5:00 | 300 | 4515 | 2832 | 7347 | [6 empty] | 18:00
5:30 | 305 | 4668.5 | 2842.5 | 7511
6:00 | 310 | 4822 | 2853 | 7675
6:30 | 240 | 4954.5 | 2869 | 7823.5
7:00 | 170 | 5087 | 2885 | 7972
7:30 | 155 | 5236 | 3015.5 | 8251.5
8:00 | 140 | 5385 | 3146 | 8531
8:30 | 255.5 | 5280 | 3314.5 | 8594.5
9:00 | 371 | 5175 | 3483 | 8658
9:30 | 453 | 5154 | 3529 | 8683
10:00 | 535 | 5133 | 3575 | 8708
10:30 | 556 | 5253 | 3586 | 8839
11:00 | 577 | 5373 | 3597 | 8970
11:30 | 545 | 5352.5 | 3652 | 9004.5
12:00 | 513 | 5332 | 3707 | 9039
12:30 | 443.5 | 5549.5 | 3749 | 9298.5
13:00 | 374 | 5767 | 3791 | 9558
13:30 | 409 | 5636 | 3769 | 9405
14:00 | 444 | 5505 | 3747 | 9252
14:30 | 458 | 5394.5 | 3726.5 | 9121
15:00 | 472 | 5284 | 3706 | 8990
15:30 | 466 | 5293 | 3643.5 | 8936.5
16:00 | 460 | 5302 | 3581 | 8883
16:30 | 411 | 5503 | 3664.5 | 9167.5
17:00 | 362 | 5704 | 3748 | 9452
17:30 | 326 | 6177 | 3968 | 10145
18:00 | 290 | 6650 | 4188 | 10838
18:30 | 250 | 6573 | 3967.5 | 10540.5
19:00 | 210 | 6496 | 3747 | 10243
19:30 | 200 | 6259 | 3986 | 10245
20:00 | 170 | 6235 | 3974 | 10209 |  |  |  | Executive Engineer
20:30 | 182 | 6021 | 3963.5 | 9984.5 |  |  |  | Network Operation Division
21:00 | 194 | 5807 | 3953 | 9760
21:30 | 202 | 5724 | 3922 | 9646
22:00 | 210 | 5641 | 3891 | 9532 |  |  |  |  | Page 6 of 7
22:30 | 220 | 5483.5 | 3756.5 | 9240
23:00 | 230 | 5326 | 3622 | 8948
23:30 | 259 | 5204.5 | 3577.5 | 8782
24:00 | 288 | 5083 | 3533 | 8616
10838 MW (18:00 )
9039 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-12-05 |  | Energy |  | 216997318
[14 empty] | 2023-12-06 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3201 | 443 | 1430 | 0 | 216 | 3136 | 86 | 0 | 0 | 100 | 0 | 4 | 0
0:30 | 3125 | 442.5 | 1323.5 | 0 | 155.5 | 3246 | 86 | 0 | 0 | 100 | 0 | 2 | 0 |  | Date: | 43803
1:00 | 3049 | 442 | 1217 | 0 | 95 | 3356 | 86 | 0 | 0 | 100 | 0 | 0 | 0
1:30 | 3009.5 | 442.5 | 1224 | 0 | 47.5 | 3280.5 | 86 | 0 | 0 | 102 | 0 | 0 | 0 | [8 empty] | Total Energy | 216.9973 | 216.9973 | Total Energy Gen 216.997 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 216.997 MKWHr
2:00 | 2970 | 443 | 1231 | 0 | 0 | 3205 | 86 | 0 | 0 | 104 | 0 | 0 | 0 | [8 empty] | Energy not Served | 0 | 0
2:30 | 2969.5 | 442.5 | 1236.5 | 0 | 0 | 3093.5 | 86 | 0 | 0 | 104 | 0 | 2.5 | 0 | [8 empty] | Energy Requirement | 216.9973 | 216.9973
3:00 | 2969 | 442 | 1242 | 0 | 0 | 2982 | 86 | 0 | 0 | 104 | 0 | 5 | 0
3:30 | 2932.5 | 442.5 | 1179 | 0 | 0 | 2892.5 | 86 | 0 | 0 | 100 | 0 | 5 | 0 | [7 empty] | Shortage
4:00 | 2896 | 443 | 1116 | 0 | 0 | 2803 | 86 | 0 | 0 | 96 | 0 | 5 | 0
4:30 | 2876 | 443 | 1124 | 0 | 0 | 2769 | 86 | 0 | 0 | 94 | 0 | 4 | 0
5:00 | 2856 | 443 | 1132 | 0 | 0 | 2735 | 86 | 0 | 0 | 92 | 0 | 3 | 0
5:30 | 2969.5 | 443 | 1197.5 | 0 | 1.5 | 2715.5 | 86 | 0 | 0 | 95 | 0 | 3 | 0
6:00 | 3083 | 443 | 1263 | 0 | 3 | 2696 | 86 | 0 | 0 | 98 | 0 | 3 | 0
6:30 | 3166.5 | 443 | 1267.5 | 0 | 38 | 2714 | 86 | 0 | 0 | 99 | 5.5 | 4 | 0 | [6 empty] | Coal
7:00 | 3250 | 443 | 1272 | 0 | 73 | 2732 | 86 | 0 | 0 | 100 | 11 | 5 | 0
7:30 | 3258.5 | 443 | 1316.5 | 0 | 126 | 2879.5 | 86 | 0 | 0 | 100 | 36.5 | 5.5 | 0 | [5 empty] | Oil
8:00 | 3267 | 443 | 1361 | 0 | 179 | 3027 | 86 | 0 | 0 | 100 | 62 | 6 | 0
8:30 | 3243.5 | 443 | 1381 | 0 | 197 | 3064 | 86 | 0 | 0 | 98 | 79 | 3 | 0
9:00 | 3220 | 443 | 1401 | 0 | 215 | 3101 | 86 | 0 | 0 | 96 | 96 | 0 | 0
9:30 | 3219.5 | 443 | 1384 | 0 | 227.5 | 3087 | 86 | 0 | 17.5 | 101 | 117.5 | 0 | 0
10:00 | 3219 | 443 | 1367 | 0 | 240 | 3073 | 86 | 0 | 35 | 106 | 139 | 0 | 0
10:30 | 3297 | 443 | 1419 | 0 | 307 | 3003 | 86 | 0 | 35 | 107 | 142 | 0 | 0
11:00 | 3375 | 443 | 1471 | 0 | 374 | 2933 | 86 | 0 | 35 | 108 | 145 | 0 | 0
11:30 | 3258 | 440.5 | 1461.5 | 0 | 518 | 2935.5 | 86 | 0 | 38 | 109 | 157.5 | 0.5 | 0
12:00 | 3141 | 438 | 1452 | 0 | 662 | 2938 | 86 | 0 | 41 | 110 | 170 | 1 | 0
12:30 | 3183 | 438 | 1456 | 0 | 876.5 | 2949 | 86 | 0 | 42 | 110 | 155.5 | 2.5 | 0
13:00 | 3225 | 438 | 1460 | 0 | 1091 | 2960 | 86 | 0 | 43 | 110 | 141 | 4 | 0
13:30 | 3225 | 438 | 1460 | 0 | 1091 | 2960 | 86 | 0 | 43 | 110 | 141 | 4 | 0
14:00 | 3225 | 438 | 1460 | 0 | 1091 | 2960 | 86 | 0 | 43 | 110 | 141 | 4 | 0
14:30 | 3168 | 440.5 | 1376 | 0 | 968 | 2973.5 | 86 | 0 | 38 | 108 | 105 | 11 | 0
15:00 | 3111 | 443 | 1292 | 0 | 845 | 2987 | 86 | 0 | 33 | 106 | 69 | 18 | 0
15:30 | 3101 | 443 | 1283.5 | 0 | 844 | 2956 | 86 | 0 | 56 | 100 | 52 | 15 | 0
16:00 | 3091 | 443 | 1275 | 0 | 843 | 2925 | 86 | 0 | 79 | 94 | 35 | 12 | 0
16:30 | 3093 | 443 | 1282 | 0 | 1141 | 2920.5 | 86 | 0 | 80.5 | 92 | 18 | 11.5 | 0
17:00 | 3095 | 443 | 1289 | 0 | 1439 | 2916 | 86 | 0 | 82 | 90 | 1 | 11 | 0
17:30 | 3212 | 435.5 | 1367 | 0 | 1753 | 3047.5 | 86 | 0 | 136.5 | 96 | 0.5 | 11 | 0
18:00 | 3329 | 428 | 1445 | 0 | 2067 | 3179 | 86 | 0 | 191 | 102 | 0 | 11 | 0
18:30 | 3329 | 318.5 | 1373 | 0 | 1895.5 | 3156 | 86 | 0 | 268.5 | 104 | 0 | 10 | 0
19:00 | 3329 | 209 | 1301 | 0 | 1724 | 3133 | 86 | 0 | 346 | 106 | 0 | 9 | 0
19:30 | 3226 | 443 | 1347 | 0 | 1488 | 3171 | 86 | 0 | 362 | 110 | 0 | 12 | 0
20:00 | 3238 | 443 | 1366 | 0 | 1466 | 3221 | 86 | 0 | 272 | 106 | 0 | 11 | 0
20:30 | 3265.5 | 443 | 1376.5 | 0 | 1291 | 3238.5 | 86 | 0 | 173 | 101 | 0 | 10 | 0
21:00 | 3293 | 443 | 1387 | 0 | 1116 | 3256 | 86 | 0 | 74 | 96 | 0 | 9 | 0
21:30 | 3248 | 443 | 1394.5 | 0 | 1070.5 | 3248 | 86 | 0 | 53.5 | 95 | 0 | 7.5 | 0
22:00 | 3203 | 443 | 1402 | 0 | 1025 | 3240 | 86 | 0 | 33 | 94 | 0 | 6 | 0
22:30 | 3205.5 | 443 | 1398 | 0 | 809 | 3181 | 86 | 0 | 16.5 | 96 | 0 | 5 | 0
23:00 | 3208 | 443 | 1394 | 0 | 593 | 3122 | 86 | 0 | 0 | 98 | 0 | 4 | 0
23:30 | 3204.5 | 443 | 1412 | 0 | 404.5 | 3129 | 86 | 0 | 0 | 99 | 0 | 4 | 0 |  | Max Temp. in Dhaka |  | 27.1°C
24:00 | 3201 | 443 | 1430 | 0 | 216 | 3136 | 86 | 0 | 0 | 100 | 0 | 4 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 216.997 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 216.997 MKWHr
Note on W13: Author:

## Generation
g | 2023-12-05
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 86 | 86 | 86 | 86 | 86 | 1273860
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 0 |  |  |  |  | 796000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [15 empty] | 0 | 7 | 16 |  | 17 | 17 | 17 |  |  |  |  | 62209
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 8 |  | 8 | 19 | 11 | 11 |  | 3 | 1 | [10 empty] | 58725
6 | Sikalbaha 225MW CCPP (Gas) | 192 | 192 | 192 | 192 | 192 | 192 | 193 | 192 | 192 | 190 | 192 | 179 | 188 | 193 | 194 | 192 | 193 | 194 |  | 193 | 193 | 195 | 193 | 192 | 192 | 191 | 4479138
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 17 | 17 | 17 | 17 | 17 |  |  | 65258
12 | Hathazari 100 MW peaking PP | [16 empty] | 1 | 40 |  | 84 | 83 | 83 |  |  |  |  | 199440
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [11 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 214945
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 289 | 295 | 305 | 266 | 240 | 240 | 277 | 307 | 308 | 309 | 309 | 310 | 300 | 250 | 250 | 250 | 250 | 288 |  | 230 | 287 | 278 | 280 | 280 | 280 | 280 | 6754685
18 | Kodda 300 MW PP Unit-2 (Summit) | [11 empty] | 10 | 88 | 95 | 45 | 45 | 85 | 280 |  | 145 | 145 | 145 | 45 | 45 | 15 | 0 | 1337345
19 | Ashuganj 195 MW PP (APSCL-United) | [13 empty] | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 83636
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4378500
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 490 | 460 | 395 | 335 | 320 | 320 | 325 | 430 | 492 | 491 | 490 | 490 | 490 | 491 | 490 | 490 | 490 | 490 |  | 440 | 440 | 440 | 440 | 440 | 440 | 440 | 10701817
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 46 | 5 | 5 | 5 | 5 | 37 | 47 | 47 | 47 | 44 | 38 | 34 | 41 | 47 | 47 | 47 | 47 | 47 |  | 47 | 47 | 47 | 47 | 47 | 46 | 46 | 886176
33 | Ashuganj 225 MW CCPP
34 | Ashuganj 450 MW CCPP(South) | 135 | 100 | 125 | 140 | 165 | 210 | 330 | 365 | 365 | 335 | 335 | 265 | 275 | 280 | 280 | 305 | 280 | 295 |  | 330 | 270 | 250 | 250 | 250 | 250 | 250 | 6273000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 330 | 280 | 280 | 330 | 340 | 280 | 280 | 280 | 280 | 305 | 280 | 300 |  | 335 | 280 | 280 | 300 | 280 | 280 | 280 | 7470900
| Ashuganj 420 MW CCPP(East) | 270 | 280 | 240 | 240 | 240 | 350 | 300 | 270 | 270 | 270 | 300 | 320 | 240 | 240 | 240 | 240 | 240 | 230 |  | 230 | 215 | 220 | 230 | 230 | 230 | 230 | 6358800
35 | Ashuganj 55 MW PP (Precision) | 6 | 3 | 3 | 3 | 3 | 3 | 3 | 16 | 23 | 24 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 24 |  | 23 | 23 | 26 | 34 | 34 | 37 | 36 | 459840
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 330 | 330 | 325 | 320 | 310 | 311 | 311 | 306 | 302 | 302 | 332 | 371 | 365 | 344 | 343 | 327 | 301 | 339 |  | 364 | 362 | 360 | 361 | 362 | 357 | 352 | 8153090
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 400 | 400 | 400 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 450 | 450 | 450 | 340 | 340 | 340 | 340 | 450 |  | 320 | 360 | 360 | 360 | 360 | 360 | 360 | 8483300
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 85 | 85 | 85 | 85 | 85 | 85 | 69 | 70 | 34 | 35 | 35 | 34 | 34 | 34 | 35 | 35 | 36 | 35 |  | 35 | 48 | 84 | 83 | 83 | 84 | 84 | 1397760
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 2 | 7 | 18 | 18 | 15 | 14 | 18 | 13 | 7 | 3 | 0 | [9 empty] | 113970
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1015000
45 | Fenchugonj CCPP Phase-2 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 27 | 27 | 27 | 27 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 694920
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 53 | 63 | 62 | 61 | 46 | 19 | 59 | 60 | 56 | 56 | 60 | 59 |  | 59 | 62 | 62 | 62 | 61 | 61 | 60 | 1274784
48 | Shahjibazar 86 MW PP (Shahjibazar) | [26 empty] | 0
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 111 | 113 | 122 | 136 | 137 | 138 | 137 | 138 | 138 | 138 | 158 | 158 | 164 | 164 | 164 | 164 | 164 | 164 |  | 164 | 164 | 164 | 164 | 164 | 163 | 163 | 3691600
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) |  |  |  |  | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 194040
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 158100
55 | Fenchugonj 51 MW PP (Barakatullah) |  |  |  |  | 0 | 4 | 10 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 458400
56 | Shahjahanulla 25 MW PP |  |  |  |  | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 279168
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 280 | 280 | 275 | 290 | 310 | 290 | 290 | 300 | 300 | 325 | 315 | 310 | 260 | 300 | 290 | 300 | 290 |  | 285 | 285 | 295 | 290 | 285 | 270 | 290 | 7154000
| Bibiyana South 400 MW | 400 | 400 | 400 | 380 | 360 | 360 | 380 | 400 | 400 | 340 | 365 | 310 | 400 | 340 | 340 | 350 | 390 | 400 |  | 396 | 400 | 400 | 400 | 370 | 360 | 360 | 9025300
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 35 | 35 |  | 35 | 35 | 17 |  |  |  |  | 134785
59 | Tangail Palli Power Gen 22 MW | [7 empty] | 3 |  |  |  |  | 5 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 |  | 78240
60 | Barabkunda 22 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 10 | 10 | 12 | 13 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 278256
61 | Narshingdi 22 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [10 empty] | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 142632
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 100 | 104 | 104 | 96 | 92 | 98 | 100 | 100 | 96 | 106 | 108 | 110 | 110 | 120 | 106 | 94 | 90 | 102 |  | 106 | 110 | 106 | 96 | 94 | 98 | 100 | 2417280
64 | Malancha, Ctg. EPZ (United) | 21 | 24 | 30 | 32 | 33 | 33 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 0 | 0 | 3 | 2 | 8 | 12 | 16 | 274560
65 | Feni 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 5 | 13 | 16 | 16 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 414252
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 8 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 208980
67 | Jangalia 33 MW PP (Summit) | 33 | 8 | 8 | 8 | 8 | 33 | 33 | 33 | 33 | 17 | 25 | 25 | 33 | 33 | 33 | 25 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 633700
68 | Cumilla 25 MW PP (Summit) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 |  | 4 | 4 | 4 | 4 | 4 | 10 | 10 | 193180
69 | Summit Ashulia | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 48000
70 | Summit Madhabdi | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 14 |  | 14 | 15 | 15 | 15 |  | 15 | 15 | 340200
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 629800
72 | Rupganj 33 MW PP(Summit) | 24 | 28 | 28 | 28 | 28 | 29 | 29 | 29 | 29 | 28 | 28 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 636400
73 | Ghorashal 108 MW PP (Regent) |  |  |  |  | 0 | 32 | 33 | 52 | 71 | 71 | 69 | 70 | 71 | 72 | 73 | 73 | 73 | 73 |  | 73 | 73 | 73 | 74 | 74 | 74 | 74 | 1245136
| Feni Lanka Power | [16 empty] | 34 | 76 |  | 22 | 17 | 17 | 17 | 17 |  |  | 193800
| Chowmuhani 113 MW | [11 empty] | 27 | 27 | 29 | 29 | 29 | 29 | 47 |  | 47 | 47 | 48 | 48 | 48 | 48 | 27 | 458640
| Manikgonj 162MW PP(MPGL) | [10 empty] | 17 | 54 | 162 | 108 | 35 | 17 | 17 | 17 |  | 17 | 17 | 17 |  |  |  |  | 427680
77 | Siddhirganj 100 PP(Dutch Bangla) | [11 empty] | 4 | 34 | 36 |  | 3 | 24 | 80 |  | 84 | 30 | 20 | 17 | 17 |  |  | 309226
78 | Gazipur 52 MW PP | [7 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 |  | 194880
79 | Kodda 150 MW PP | [11 empty] | 6 | 16 | 16 | 16 | 64 | 64 | 118 |  | 98 | 98 | 64 | 16 | 16 |  |  | 524160
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 8 | 36 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 122842
| Gazipur 100 MW PP | [7 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 90 | 105 |  | 105 | 105 | 105 | 70 | 70 | 17 |  | 858269
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 1 | 0 | [10 empty] | 11160
| Jodiac Power | [13 empty] | 8 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 21 | 17 |  | 324789
| Karnaphuli Power Ltd. | [9 empty] | 3 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 265130
82 | Madanganj 102 PP(Summit) | [11 empty] | 4 | 25 | 39 | 17 | 4 | 45 | 68 |  | 75 | 17 | 17 | 17 | 17 | 3 |  | 269634
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 19 | 24 | 31 |  |  |  |  | 54365
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | [12 empty] | 5 | 26 |  | 5 | 23 | 40 |  | 57 | 17 | 23 |  |  |  |  | 186240
| Meghnaghat 104 MW PP (OPCL) | [11 empty] | 17 | 52 | 35 | 17 | 17 | 68 | 72 |  | 53 | 17 | 17 | 17 | 17 |  |  | 395520
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [11 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 |  |  |  |  | 90840
92 | Fenchuganj 44 MW (Energyprima) | 0 |  |  |  | 0 | 5 | 5 | 21 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 455760
93 | Ashuganj 51 MW PP (Midland) | [5 empty] | 0 | 30 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 850588
94 | Gagnagar 102 MW PP (Digital Power) | [16 empty] | 24 | 63 |  | 40 | 16 | [5 empty] | 133056
95 | Patenga 50MW PP (Baraka) | [9 empty] | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 19 | 19 |  | 20 | 20 | 20 | 20 | 20 | 20 | 6 | 181440
96 | Chattogram 108 MW PP (ECPV) | [26 empty] | 0
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [11 empty] | 18 | 40 | 55 | 15 | 15 | 24 | 55 |  | 15 | 15 | 15 | 15 |  |  |  | 323274
100 | Manikganj 55 MW PP (Northern) | [15 empty] | 17 | 17 | 35 |  | 35 | 35 | 35 |  |  |  |  | 134296
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | [10 empty] | 5300
103 | Kamalaghat 54 MW PP(Banco Energy) | [10 empty] | 17 | 17 |  |  |  |  | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  |  | 129960
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [7 empty] | 56 | 56 | 46 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 77 |  | 78 | 78 | 78 | 78 | 58 | 58 | 58 | 1046400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 1 | 17 | 23 | 35 | 35 | 35 | 35 | 35 | 35 | 36 | 67 |  | 72 | 72 | 72 | 72 | 72 | 37 | 14 | 711792
115 | Juldah 100 MW PP Unit-3 (Acorn) | [26 empty] | 0
116 | Chandpur 200 MW (Desh energy) | 95 | 0 |  |  | 0 | 1 | 54 | 68 | 68 | 68 | 70 | 100 | 120 | 120 | 120 | 123 | 122 | 20 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 1284960
117 | Ashuganj 150 MW PP (Midland) | [8 empty] | 1 | 8 | 12 | 14 | 14 | 13 | 15 | 13 | 30 | 55 |  | 57 | 62 | 60 | 57 | 55 | 35 | 8 | 444945
118 | Bibiyana-III 400 MW CCPP | 367 | 367 | 367 | 329 | 319 | 315 | 319 | 327 | 317 | 371 | 422 | 365 | 367 | 368 | 366 | 344 | 318 | 384 |  | 368 | 319 | 319 | 344 | 320 | 320 | 320 | 8458000
| Jamalpur 115 MW PP (United) | [6 empty] | 2 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 28 |  | 28 | 28 | 28 | 28 | 9 | 9 |  | 237600
| Anwara 300 MW PP (United) | [10 empty] | 5 | 20 | 65 | 65 | 69 | 69 | 102 | 106 |  | 106 | 106 | 105 | 106 | 105 | 50 |  | 1031236
| Juldah unit-2 (Acorn) | [26 empty] | 0
| Anlima Energy Ltd. | [8 empty] | 4 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 267218
| Bhairob 54.5 MW | [14 empty] | 1 |  |  | 13 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 140760
| Spectra Solar Plant Ltd. | [6 empty] | 0 | 4 | 3 | 7 | 9 | 11 | 6 | 4 | 4 | 2 | 0 | [9 empty] | 54488
| Chandpur 115(Doreen) |  |  |  |  | 0 | 2 | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 40 |  | 58 | 36 | 40 | 21 | 18 | 17 | 18 | 416640
| Kanchan Purbachal Power Generation Ltd. | [10 empty] | 10 | 17 | 17 | 17 | 17 | 17 | 30 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 368280
| Mirsharai 150 MW (Oil) | [9 empty] | 35 | 35 | 35 | 27 | 27 | 17 | 15 | 17 | 33 |  | 114 | 127 | 67 |  |  |  |  | 419855
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 0 | 5 | 5 | 3 | 3 | 5 | 6 | 0 | 0 | 0 | 1 | 4 | 15 | 18 | 12 | 11 | 11 |  | 9 | 12 | 11 | 9 | 6 | 4 | 4 | 134880
| Matarbari 2*600 MW (CPGCL) | 565 | 565 | 566 | 566 | 565 | 565 | 567 | 565 | 271 | 153 | 0 | [8 empty] | 122 | 158 | 234 | 268 | 271 | 270 | 270 | 6494545
120 | Eastern Zone Total | 5014 | 4819 | 4765 | 4561 | 4515 | 4822 | 5087 | 5385 | 5175 | 5133 | 5373 | 5332 | 5767 | 5505 | 5284 | 5302 | 5704 | 6650 |  | 6496 | 6259 | 6235 | 5807 | 5641 | 5326 | 5083 | 130035555
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [11 empty] | 18 | 35 | 16 | 16 | 16 | 48 | 49 |  | 16 | 16 | 16 | 16 | 16 |  |  | 269760
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [16 empty] | 2 | 0 |  | 3 | 10 | 17 | 35 | 35 |  |  | 85490
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 1 | 12 | 18 | 24 | 37 | 23 | 19 | 13 | 8 | 10 | 0 | [9 empty] | 182880
131 | Rampal 1320 MW (BIFPCL) | 378 | 379 | 381 | 377 | 378 | 379 | 378 | 377 | 377 | 374 | 376 | 380 | 374 | 376 | 377 | 369 | 378 | 375 |  | 376 | 376 | 378 | 378 | 378 | 377 | 377 | 9061818
132 | United Payra Power Ltd. | [11 empty] | 7 | 17 | 17 | 17 | 17 | 17 | 17 |  | 35 | 35 | 35 | 35 | 35 | 17 |  | 292800
133 | Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 180 | 180 | 222 |  | 224 | 224 | 224 | 224 | 220 | 220 | 220 | 5018182
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [26 empty] | 0
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3425500
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 60 | 60 | 60 | 60 | 65 | 65 | 30 | 80 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 1951000
140 | Bhola 33 MW PP (Venture) | 18 | 17 | 16 | 16 | 16 | 16 | 11 | 14 | 14 | 13 | 13 | 15 | 16 | 11 | 12 | 14 | 15 | 19 |  | 17 | 18 | 21 | 20 | 20 | 19 | 18 | 378700
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [16 empty] | 8 | 8 | [8 empty] | 14625
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 442 | 443 | 442 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 438 | 438 | 438 | 443 | 443 | 443 | 428 |  | 209 | 443 | 443 | 443 | 443 | 443 | 443 | 10600727
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 850 | 790 | 780 | 680 | 640 | 600 | 600 | 700 | 900 | 980 | 1000 | 1000 | 1020 | 1060 | 1050 | 1000 | 980 | 1244 |  | 1160 | 1120 | 1120 | 1100 | 1080 | 980 | 980 | 24308000
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4152300
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | [9 empty] | 10680
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 317 | 327 | 333 | 270 | 270 | 330 | 330 | 330 | 330 | 296 | 268 | 256 | 267 | 264 | 253 | 244 | 247 | 246 |  | 240 | 245 | 245 | 263 | 281 | 282 | 296 | 6883272
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | [8 empty] | 145332
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 42 | [8 empty] | 28284
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [26 empty] | 0
169 | Natore 52 MW PP (Rajlanka) | [16 empty] | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 62875
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 33 | 37 | 41 | 41 |  |  |  | 109848
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [10 empty] | 5 | 35 | 35 | 35 | 35 | 40 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 |  | 641568
172 | Confidence Power Bogura Unit-1 113 MW | [10 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 |  |  | 581760
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [11 empty] | 33 | 33 | 33 | 34 | 34 | 87 | 100 |  | 102 | 107 | 107 | 50 | 34 | 6 | 0 | 652857
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 3 | 5 | 3 | 3 | 3 | 2 | 1 | [10 empty] | 22247
178 | Energypac Power Venture Thakurgaon Ltd. | [12 empty] | 50 | 52 | 54 | 53 | 70 | 114 |  | 54 | 35 | 35 | 35 | 35 | 35 |  | 653568
| Intraco Solar 30 MW | [6 empty] | 1 | 5 | 6 | 26 | 10 | 18 | 15 | 16 | 6 | 3 | 0 | [9 empty] | 88925
| Adani Power Jharkhanda Ltd | 763 | 701 | 550 | 535 | 522 | 522 | 552 | 645 | 751 | 765 | 757 | 758 | 766 | 759 | 760 | 756 | 758 | 760 |  | 725 | 767 | 739 | 760 | 761 | 745 | 759 | 16925455
178 | Teesta Solar Limited | [6 empty] | 6 | 24 | 46 | 49 | 46 | 86 | 66 | 52 | 38 | 15 | 1 | [9 empty] | 413310