## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-12-08 | Friday
|  | Date (day): | 2023-12-08 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11594.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12664 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-12-07 | 2023-12-08 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 67 | 73 | 74 | 74 | 34 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 355 | 311 | 350 | 360 | 52 |  | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 18 | 80 | 90 |  | 10 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 17 | 85 | 85 |  | 17 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 40 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 36 | 36 | 39 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 10 | 10 | 15 | 15 |  | 7 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 200 | 210
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 25 | 90 | 90 |  | 10 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 296 | 240 | 0 | 0 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 90 | 90 |  | 12 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 17 | 17 | 37 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 149 | 98 | 149 | 149 |  |  | DTC
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 0 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 0 | 55 |  |  | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 34 | 33 | 38 | 38 |  | 42 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 22 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 17 | 8 | 16 | 36 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 40 | 80 | 130
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 70 | 35 | 70 | 79 |  | Fuel shortage
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 1 | 70 | 52 | 105
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 36 | 70 | 70 | 34 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 54 | 17 | 72 | 90 |  | Fuel shortage
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 7 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 35 | 20 |  | Fuel shortage
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 5763 | 5422 | 1644 | 1915 | 2289 | 2593 | 1267 | 1038
38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
39 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 8 | 8 | 17 | 8 |  | Fuel shortage
40 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 17 | 0 | 20 | 0
41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 20 | 6 | 20 | 30 |  | Fuel shortage
42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 86 | 86 | 86 | 86 | 144 |  | Low water lavel
43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 194 | 192 | 190 | 192 | 33 |  | Gas shortage
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 14 | 17 | 17 | 17 | 88 |  | Fuel shortage
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 50 | 65 | 33 |  | Fuel shortage
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 0 | 17 | 85 |  | Fuel shortage
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 12 | 0 | 0 | 12 | 88 |  | Fuel shortage
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 12 | 12 | 12 | 12 | 10 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 2 | 15 | 30
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 64 | 100 | 100 | 100 | 200 |  | Fuel shortage
54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 17 | 17 | 17 | 37 |  | Fuel shortage
55 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 17 | 17 | 93 |  | Fuel shortage
56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
57 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 17 | 99 |  | Fuel shortage
58 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 0 | 150 | 150 | 13
59 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 490 | 485 | 500 | 500
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 0 | 1 | 10 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 0 | 563 | 400 | 550 |  |  | On test.
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 35 | 17 | 0 | 0
| Chattogram area Total |  |  |  |  | 3829 | 3769 | 966 | 1554 | 1620 | 1829 | 1449 | 330
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 0 | 0 |  | 221 | Under maint.
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 280 | 320 | 320 | 40 |  | FGMO
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 270 | 300 | 300 |  |  | FGMO
63 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 350 | 230 | 320 | 350
64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 40 | 48 | 45 | 48
65 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 0 | 41 | 47 | 10 | 47
66 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 0 | 0 | 0 | 195 |  | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 28 | 51 | 51
68 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 1 | 26 | 12 | 50 | 100 |  | Fuel shortage
69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 20
70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
71 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 17 | 17 | 17 | 183 |  | Fuel shortage
72 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 18 | 18 | 18 |  | 4 | Engine problem
73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 94 | 100 | 128 | 140
74 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 16 | 52 | 52
76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 8 | 8 | 10 | 10 |  | 15 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 17 | 60 | 100 |  | 14 | Engine problem
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 28 | 47 | 28 | 55 | 58 |  | Engine problem
79 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 0 | 17 | 17 |  | 37 | Engine problem
80 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 18 | 53 | 17 | 17 | 98 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2896 | 1367 | 1249 | 1449 | 1656 | 674 | 454
81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 33 | 35 | 70 | 70 | 132 |  | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Contract Expired
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 76 | 56 | 75 | 125 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 28 | 8 | 25 | 90 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 6 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 106 | 139 | 191.6 | 176 | 132 | 22
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 28 | 28 | 28 | 28 |  | 62 | Engine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 25 | 25 | 25 | 25 | 26 |  | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 25 | 25 | 25 | 25 | 25 |  | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 |  | 6 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 63 | 60 | 60 |  | 6
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 0 | 0 | 0 | 86 |  | Gas shortage
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 163 | 163 | 163 | 163 |  | 68 | Machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 23 | 16 | 16 | 9 |  | Gas shortage
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 260 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 367 | 320 | 400 | 400 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 360 | 400 | 400 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1439 | 1325 | 1475 | 1475 | 309 | 599
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 918 | 617 | 935 | 935
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 32 | 32 | 83 |  | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 45
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 | 109 |  | under maint.
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 16 | 24 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 70 | 90 |  | 15 | Engine problem
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 25 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 375 | 633 | 400 | 617
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 1318 | 1250 | 1537 | 1735 | 1313 | 15
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 15 | 18 | 20 | 20 |  | 20 | Engine problem
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 125 | 130 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 610 | 600 | 622 | 622 |  | 622 | #01 under maint.
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 2 | 0 | 0 | 35
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 140 | 140 | 140 | 140 | 167 |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1112 | 1108 | 1242 | 1277 | 167 | 706
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 30 | 22 |  | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 20 |  | 51 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 28 | 28
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 34 | 42 |  | 8 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 40 |  | 10 | Engine problem
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 275 | 227 | 330 | 330 | 84 |  | Gas shortage
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 38 | 12 |  | Fuel shortage
136 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 0 | 11 | 11
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 40 | 86 |  | 18 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 3 | 45 | 35 | 50 | 63 |  | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 20 | 55 | 35 | 55 | 58 |  | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 0 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 759 | 717 | 748 | 748
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 1068 | 1044 | 1349 | 1530 | 1260 | 87
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 50 | 34 | 113
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 35 | 70 | 110
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 3 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 19 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 194 | 255 | 442 | 393 | 125 | 189
| Total |  |  |  |  | 25951 | 25211 | 9214 | 9839 | 11594.6 | 12664 | 6696 | 3440
A. |  | 2023-12-07 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 9839 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 6835 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9839 | MW
3 | Day peak Generation : |  |  | 9214 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9528.44 | MW
4 | Evening peak Generation : |  |  | 9839 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 208.0705 | MKWHr | By Solar | 0.53221 | MKWHr
| By Gas : | 108.702 | MKWHr |  | By Oil: | 10.0119 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 65.1223 | MKWHr |  | By Hydro: | 2.0633 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.0408 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6696 | MW | Dhaka | 3720.84 | 3720.84 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3440 | MW | Chittagong | 1156.2 | 1156.2 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 10136 | MW | Khulna | 1065 | 1065 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 792.32 | MMCFD |  |  | Rajshahi | 846.4 | 846.4 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 111106296.356 | ii) Oil : | Taka | 136128175.34 | Comilla | 805 | 805 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 408875803.2 | Total | Taka | 656110274.896 | Mymensingh | 669 | 669 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.0165 | MKWHr. | Sylhet | 344 | 344 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 170 | MW (W to E) at | 18:00 | hrs | Barisal | 266 | 266 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 170 | MW at | 7:00 | hrs | Rangpur | 656 | 656 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 21°C |  |  | Total | 9528.44 | 9528.44 |  | 0
B. |  | 2023-12-08 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 21°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12664 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7700 | MW
4 | Reserve(Generation end) |  |  |  | 2664 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 211.4752 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6539 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.4793 | MKWHr. | ii) HVDC Flow at Peak Time |  | 617 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.1187 | MKWHr. | iii) Maximum HVDC Flow : |  | 918 | MW at | 12:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 97.1 |  | (b) Today: | 96.98 |  | (c) Rule Curve: |  | 105.37
.

## YesterdayGen
2023-12-07 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 356 | 0 |  | 0 | 390 | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 14 | 16 | 24 | 8 | 0 | 86 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 2 | 10 | 17 | 0 | 0 | 0 | 280 | 250 | 0 | 8 | 0 | 45 | 31 | 0 | 43 | 0 | 0 | 0 | 18 | 11 | 33 | 8 | 82 | 95 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 63 | 0 | 0 | 164 | 0 | 0 | 10 | 275 | 23 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 319 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 445 | 0 | 0 | 0 | 0 |  | 823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 140 | 670 | 0 | 0 |  | 4781 | 3414 | 8195 | 3226 | 823 | 1410 | 0 | 88 | 2382 | 86 | 0 | 98 | 82 | 0 | 0 | 0 | 97.12
2:00 | 0 | 0 | 0 | 180 | 0 | 40 | 0 | 356 | 0 |  | 0 | 390 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 16 | 24 | 8 | 0 | 86 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 22 | 0 | 0 | 0 | 280 | 250 | 0 | 8 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 8 | 76 | 99 | 0 | 0 | 0 | 43 | 28 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 164 | 0 | 0 | 0 | 260 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 320 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 240 | 0 | 0 | 350 | 0 | 0 | 0 | 0 |  | 746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 140 | 618 | 0 | 0 |  | 4392 | 3222 | 7614 | 3154 | 746 | 1249 | 0 | 49 | 2156 | 86 | 0 | 98 | 76 | 0 | 0 | 0 | 97.12
3:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 352 | 0 |  | 0 | 390 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 14 | 16 | 24 | 8 | 0 | 86 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 27 | 0 | 0 | 0 | 280 | 250 | 0 | 8 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 72 | 107 | 0 | 0 | 0 | 43 | 28 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 163 | 0 | 0 | 0 | 270 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 320 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 300 | 1 | 0 | 0 | 0 |  | 633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 140 | 607 | 0 | 0 |  | 4275 | 3058 | 7333 | 3105 | 633 | 1234 | 0 | 59 | 2045 | 86 | 0 | 98 | 72 | 0 | 1 | 0 | 97.11
4:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 323 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 277 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 16 | 16 | 8 | 0 | 86 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 27 | 0 | 0 | 0 | 280 | 250 | 0 | 8 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 80 | 109 | 0 | 0 | 0 | 43 | 28 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 164 | 0 | 0 | 0 | 275 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 321 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 300 | 0 | 0 | 0 | 0 |  | 633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 140 | 520 | 0 | 0 |  | 4211 | 2890 | 7101 | 3038 | 633 | 1265 | 0 | 42 | 1859 | 86 | 0 | 98 | 80 | 0 | 0 | 0 | 97.11
5:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 307 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 267 | 0 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 16 | 24 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 41 | 0 | 0 | 0 | 280 | 240 | 0 | 8 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 74 | 109 | 0 | 0 | 0 | 43 | 28 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 163 | 0 | 0 | 0 | 275 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 319 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 300 | 0 | 0 | 0 | 0 |  | 633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 140 | 525 | 0 | 0 |  | 4112 | 2723 | 6835 | 2927 | 633 | 1159 | 0 | 34 | 1814 | 86 | 0 | 108 | 74 | 0 | 0 | 0 | 97.1
6:00 | 0 | 0 | 0 | 180 | 0 | 14 | 0 | 306 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 267 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 16 | 28 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 41 | 0 | 0 | 0 | 305 | 240 | 0 | 8 | 0 | 28 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 72 | 109 | 0 | 0 | 0 | 43 | 28 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 163 | 0 | 0 | 0 | 295 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 305 | 0 | 0 | 0 | 0 |  | 633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 140 | 468 | 0 | 0 |  | 4203 | 2693 | 6896 | 3003 | 633 | 1192 | 0 | 0 | 1761 | 86 | 0 | 149 | 72 | 0 | 0 | 0 | 97.1
7:00 | 0 | 0 | 0 | 180 | 0 | 60 | 0 | 303 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 263 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 7 | 16 | 28 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 33 | 0 | 0 | 0 | 320 | 360 | 0 | 8 | 0 | 42 | 10 | 0 | 14 | 0 | 0 | 0 | 3 | 0 | 33 | 8 | 82 | 94 | 0 | 0 | 0 | 43 | 28 | 26 | 25 | 0 | 0 | 40 | 0 | 0 | 163 | 0 | 0 | 10 | 310 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 230 | 0 | 0 | 330 | 0 | 0 | 0 | 0 |  | 623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 220 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 379 | 0 | 140 | 471 | 2 | 0 |  | 4604 | 2713 | 7317 | 3195 | 623 | 1330 | 0 | 36 | 1810 | 86 | 0 | 149 | 82 | 6 | 0 | 0 | 97.09
8:00 | 0 | 0 | 0 | 180 | 0 | 66 | 0 | 307 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 7 | 16 | 28 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 315 | 240 | 0 | 8 | 0 | 45 | 10 | 0 | 14 | 0 | 0 | 27 | 15 | 11 | 33 | 8 | 82 | 70 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 62 | 0 | 0 | 163 | 0 | 0 | 10 | 310 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 17 | 0 | 426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 7 | 0 | 400 | 0 | 5 | 0 | 0 | 0 | 0 | 2 | 18 | 0 | 355 | 0 | 0 | 400 | 0 | 0 | 0 | 0 |  | 790 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 400 | 220 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 377 | 2 | 140 | 515 | 15 | 0 |  | 5010 | 3115 | 8125 | 3341 | 790 | 1522 | 0 | 113 | 2002 | 86 | 0 | 149 | 82 | 40 | 0 | 0 | 97.09
9:00 | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 310 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 262 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 7 | 16 | 28 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 280 | 270 | 0 | 8 | 0 | 45 | 32 | 0 | 14 | 0 | 0 | 52 | 15 | 11 | 33 | 8 | 88 | 70 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 62 | 0 | 0 | 163 | 0 | 0 | 10 | 300 | 8 | 8 | 0 | 0 | 0 | 0 | 12 | 0 | 1 | 8 | 0 | 17 | 0 | 367 | 9 | 17 | 0 | 2 | 0 | 0 | 0 | 44 | 9 | 0 | 400 | 0 | 6 | 0 | 0 | 0 | 2 | 2 | 18 | 0 | 350 | 0 | 0 | 465 | 0 | 0 | 0 | 0 |  | 847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 500 | 223 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 379 | 7 | 140 | 626 | 23 | 0 |  | 5107 | 3419 | 8526 | 3330 | 847 | 1504 | 0 | 181 | 2280 | 86 | 0 | 149 | 88 | 61 | 0 | 0 | 97.08
10:00 | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 319 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 0 | 16 | 28 | 8 | 0 | 86 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 280 | 270 | 0 | 8 | 0 | 42 | 36 | 0 | 14 | 0 | 0 | 52 | 15 | 11 | 33 | 8 | 90 | 70 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 63 | 0 | 0 | 163 | 0 | 0 | 10 | 285 | 16 | 8 | 0 | 0 | 0 | 0 | 56 | 0 | 15 | 8 | 0 | 17 | 0 | 368 | 9 | 17 | 0 | 3 | 0 | 0 | 3 | 44 | 9 | 0 | 400 | 0 | 10 | 0 | 0 | 0 | 17 | 5 | 18 | 0 | 300 | 35 | 0 | 478 | 0 | 0 | 0 | 0 |  | 828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 520 | 222 | 0 | 0 | 1 | 13 | 0 | 0 | 0 | 376 | 7 | 140 | 621 | 24 | 0 |  | 5218 | 3339 | 8557 | 3260 | 828 | 1465 | 0 | 265 | 2305 | 86 | 0 | 184 | 90 | 74 | 0 | 0 | 97.08
11:00 | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 353 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 283 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 7 | 25 | 28 | 8 | 0 | 86 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 2 | 10 | 0 | 0 | 0 | 0 | 300 | 280 | 0 | 8 | 0 | 42 | 42 | 0 | 28 | 0 | 0 | 43 | 15 | 11 | 25 | 8 | 98 | 33 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 63 | 0 | 0 | 164 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 56 | 0 | 17 | 18 | 0 | 17 | 0 | 320 | 9 | 0 | 0 | 4 | 0 | 0 | 17 | 17 | 28 | 0 | 400 | 0 | 15 | 0 | 15 | 0 | 17 | 4 | 18 | 2 | 300 | 35 | 0 | 487 | 0 | 0 | 0 | 0 |  | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 540 | 180 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 376 | 6 | 140 | 739 | 22 | 0 |  | 5247 | 3515 | 8762 | 3261 | 917 | 1401 | 0 | 266 | 2452 | 86 | 0 | 184 | 98 | 97 | 0 | 0 | 97.07
12:00 | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 355 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 14 | 25 | 28 | 8 | 0 | 86 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 26 | 0 | 40 | 41 | 0 | 51 | 0 | 0 | 8 | 15 | 11 | 25 | 8 | 94 | 33 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 62 | 0 | 0 | 163 | 0 | 0 | 10 | 295 | 16 | 5 | 0 | 0 | 0 | 0 | 58 | 0 | 17 | 17 | 0 | 17 | 1 | 367 | 9 | 1 | 14 | 2 | 64 | 0 | 17 | 17 | 28 | 0 | 400 | 0 | 6 | 0 | 17 | 0 | 17 | 7 | 18 | 17 | 350 | 35 | 0 | 490 | 0 | 0 | 0 | 0 |  | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 3 | 0 | 0 | 0 | 2 | 20 | 610 | 220 | 0 | 2 | 0 | 25 | 0 | 0 | 0 | 375 | 3 | 140 | 759 | 19 | 0 |  | 5522 | 3692 | 9214 | 3436 | 918 | 1500 | 0 | 371 | 2544 | 86 | 0 | 184 | 94 | 81 | 0 | 0 | 97.07
13:00 | 0 | 0 | 0 | 180 | 0 | 69 | 0 | 356 | 0 |  | 0 | 450 | 0 | 0 | 10 | 0 | 294 | 0 | 0 | 2 | 0 | 149 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 10 | 20 | 14 | 25 | 28 | 8 | 0 | 86 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 8 | 0 | 44 | 41 | 0 | 51 | 0 | 0 | 8 | 18 | 11 | 25 | 8 | 90 | 33 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 62 | 0 | 0 | 165 | 0 | 0 | 10 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 58 | 0 | 28 | 13 | 0 | 17 | 3 | 367 | 9 | 17 | 17 | 1 | 49 | 0 | 36 | 17 | 28 | 0 | 400 | 1 | 4 | 17 | 17 | 0 | 17 | 5 | 18 | 17 | 315 | 27 | 0 | 490 | 0 | 0 | 0 | 0 |  | 918 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 35 | 0 | 30 | 0 | 1 | 35 | 622 | 220 | 0 | 17 | 0 | 13 | 4 | 0 | 0 | 372 | 7 | 140 | 764 | 28 | 0 |  | 5545 | 3813 | 9358 | 3408 | 918 | 1477 | 0 | 573 | 2558 | 86 | 0 | 176 | 90 | 72 | 0 | 0 | 97.06
14:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 332 | 0 |  | 0 | 320 | 0 | 3 | 49 | 40 | 250 | 0 | 0 | 39 | 0 | 149 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 10 | 20 | 14 | 25 | 28 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 |  | 0 | 8 | 0 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 280 | 270 | 0 | 0 | 0 | 40 | 36 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 25 | 2 | 90 | 33 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 40 | 0 | 0 | 163 | 0 | 0 | 10 | 270 | 16 | 5 | 0 | 20 | 0 | 0 | 58 | 0 | 0 | 12 | 0 | 22 | 13 | 320 | 9 | 0 | 17 | 0 | 48 | 2 | 51 | 17 | 29 | 0 | 340 | 14 | 5 | 17 | 17 | 0 | 0 | 3 | 18 | 17 | 250 | 27 | 0 | 477 | 1 | 0 | 0 | 0 |  | 917 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242 | 7 | 0 | 35 | 0 | 34 | 0 | 2 | 35 | 520 | 220 | 0 | 17 | 0 | 6 | 55 | 0 | 0 | 372 | 1 | 140 | 720 | 15 | 0 |  | 5148 | 3673 | 8821 | 3039 | 917 | 1286 | 0 | 750 | 2399 | 86 | 0 | 209 | 90 | 44 | 1 | 0 | 97.07
15:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 307 | 0 |  | 0 | 320 | 0 | 9 | 36 | 15 | 240 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 14 | 25 | 24 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 8 | 0 | 0 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 280 | 270 | 0 | 0 | 0 | 35 | 30 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 25 | 8 | 100 | 35 | 0 | 0 | 0 | 43 | 27 | 25 | 25 | 0 | 0 | 40 | 0 | 0 | 165 | 0 | 0 | 10 | 290 | 24 | 5 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 7 | 0 | 29 | 13 | 364 | 9 | 25 | 17 | 1 | 48 | 17 | 51 | 0 | 29 | 0 | 345 | 17 | 3 | 17 | 17 | 0 | 0 | 1 | 18 | 17 | 300 | 17 | 0 | 450 | 3 | 140 | 0 | 0 |  | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 22 | 0 | 1 | 0 | 480 | 180 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 435 | 2 | 140 | 663 | 6 | 0 |  | 5202 | 3354 | 8556 | 3110 | 918 | 1243 | 0 | 470 | 2478 | 86 | 0 | 123 | 100 | 25 | 3 | 0 | 97.05
16:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 307 | 0 |  | 0 | 340 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 14 | 25 | 24 | 8 | 0 | 86 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 10 | 0 | 0 | 0 | 0 | 300 | 280 | 0 | 0 | 0 | 44 | 46 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 25 | 8 | 106 | 35 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 40 | 0 | 0 | 165 | 0 | 0 | 10 | 300 | 20 | 5 | 0 | 0 | 0 | 0 | 45 | 0 | 8 | 1 | 0 | 20 | 0 | 401 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 370 | 0 | 1 | 0 | 17 | 0 | 0 | 1 | 0 | 17 | 270 | 17 | 0 | 450 | 3 | 315 | 0 | 0 |  | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 400 | 180 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 582 | 2 | 140 | 669 | 5 | 0 |  | 5151 | 3403 | 8554 | 3176 | 918 | 1287 | 0 | 155 | 2726 | 86 | 0 | 85 | 106 | 12 | 3 | 0 | 97.05
17:00 | 0 | 0 | 0 | 180 | 0 | 13 | 0 | 314 | 0 |  | 0 | 340 | 0 | 2 | 2 | 4 | 240 | 0 | 0 | 4 | 0 | 64 | 0 | 0 | 0 | 0 | 17 | 17 | 5 | 10 | 20 | 13 | 25 | 21 | 17 | 0 | 86 | 0 | 0 | 0 | 1 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 12 | 4 | 0 | 0 | 0 | 280 | 270 | 0 | 0 | 0 | 44 | 46 | 0 | 10 | 0 | 0 | 1 | 18 | 11 | 33 | 8 | 100 | 35 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 40 | 0 | 0 | 163 | 0 | 0 | 10 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 66 | 0 | 27 | 0 | 0 | 17 | 2 | 319 | 6 | 40 | 6 | 0 | 48 | 6 | 17 | 17 | 14 | 0 | 370 | 8 | 0 | 35 | 17 | 0 | 0 | 0 | 11 | 17 | 230 | 0 | 17 | 450 | 4 | 550 | 0 | 0 |  | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 10 | 0 | 28 | 0 | 0 | 45 | 370 | 180 | 0 | 0 | 0 | 1 | 17 | 0 | 0 | 631 | 0 | 140 | 694 | 0 | 0 |  | 5416 | 3510 | 8926 | 3048 | 918 | 1158 | 0 | 542 | 3005 | 86 | 0 | 64 | 100 | 1 | 4 | 0 | 97.04
18:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 311 | 0 |  | 0 | 450 | 0 | 18 | 17 | 40 | 240 | 0 | 0 | 25 | 0 | 98 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 10 | 20 | 13 | 25 | 22 | 17 | 0 | 86 | 0 | 0 | 0 | 8 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 20 | 12 | 2 | 0 | 0 | 0 | 280 | 270 | 0 | 0 | 0 | 48 | 47 | 0 | 28 | 0 | 0 | 16 | 18 | 11 | 33 | 8 | 100 | 35 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 63 | 0 | 0 | 163 | 0 | 0 | 10 | 260 | 23 | 5 | 0 | 40 | 0 | 0 | 76 | 0 | 70 | 0 | 0 | 17 | 26 | 320 | 28 | 70 | 17 | 0 | 100 | 17 | 17 | 17 | 47 | 0 | 360 | 36 | 0 | 54 | 17 | 0 | 0 | 0 | 53 | 17 | 230 | 0 | 17 | 485 | 1 | 563 | 0 | 0 |  | 617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 45 | 0 | 50 | 0 | 0 | 55 | 600 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 633 | 0 | 140 | 717 | 0 | 0 |  | 6182 | 3657 | 9839 | 3110 | 617 | 1385 | 0 | 1134 | 3308 | 86 | 0 | 98 | 100 | 0 | 1 | 0 | 97.04
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 314 | 0 |  | 0 | 400 | 0 | 0 | 6 | 0 | 242 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 10 | 20 | 13 | 25 | 22 | 17 | 0 | 86 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 20 | 12 | 2 | 0 | 0 | 0 | 280 | 270 | 0 | 0 | 0 | 48 | 47 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 8 | 102 | 35 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 63 | 0 | 0 | 163 | 0 | 0 | 9 | 265 | 24 | 5 | 0 | 0 | 0 | 0 | 78 | 0 | 59 | 0 | 0 | 19 | 30 | 330 | 8 | 35 | 17 | 0 | 65 | 17 | 17 | 0 | 47 | 0 | 360 | 47 | 0 | 35 | 17 | 0 | 0 | 0 | 17 | 17 | 230 | 0 | 17 | 490 | 2 | 564 | 0 | 0 |  | 630 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 50 | 0 | 45 | 0 | 0 | 55 | 610 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 633 | 0 | 140 | 753 | 0 | 0 |  | 5807 | 3694 | 9501 | 3137 | 630 | 1365 | 0 | 787 | 3360 | 86 | 0 | 32 | 102 | 0 | 2 | 0 | 97.02
19:30 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 312 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 242 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 10 | 20 | 13 | 25 | 22 | 17 | 0 | 86 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 20 | 12 | 2 | 0 | 0 | 0 | 280 | 280 | 0 | 0 | 0 | 48 | 47 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 8 | 102 | 35 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 63 | 0 | 0 | 164 | 0 | 0 | 9 | 305 | 24 | 5 | 0 | 0 | 0 | 0 | 78 | 0 | 35 | 0 | 0 | 17 | 6 | 334 | 0 | 17 | 17 | 0 | 30 | 17 | 17 | 0 | 11 | 0 | 360 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 17 | 17 | 240 | 0 | 17 | 490 | 16 | 565 | 0 | 0 |  | 678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 50 | 0 | 10 | 0 | 0 | 0 | 622 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 628 | 0 | 140 | 753 | 0 | 0 |  | 5649 | 3659 | 9308 | 3160 | 678 | 1405 | 0 | 461 | 3368 | 86 | 0 | 32 | 102 | 0 | 16 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 307 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 242 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 13 | 25 | 22 | 17 | 0 | 86 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 20 | 12 | 9 | 0 | 0 | 0 | 280 | 270 | 0 | 0 | 0 | 48 | 47 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 10 | 92 | 40 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 63 | 0 | 0 | 163 | 0 | 0 | 9 | 270 | 24 | 5 | 0 | 0 | 0 | 0 | 45 | 0 | 35 | 0 | 0 | 17 | 0 | 330 | 0 | 2 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 17 | 17 | 240 | 0 | 17 | 490 | 10 | 566 | 0 | 0 |  | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 631 | 0 | 140 | 753 | 0 | 0 |  | 5396 | 3764 | 9160 | 3144 | 915 | 1377 | 0 | 204 | 3300 | 86 | 0 | 32 | 92 | 0 | 10 | 0 | 97.03
21:00 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 298 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 242 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 13 | 25 | 24 | 17 | 0 | 86 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 20 | 12 | 8 | 0 | 0 | 0 | 280 | 270 | 0 | 0 | 0 | 48 | 47 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 10 | 96 | 78 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 63 | 0 | 0 | 164 | 0 | 0 | 9 | 275 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 0 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 17 | 17 | 240 | 0 | 0 | 470 | 2 | 565 | 0 | 0 |  | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 643 | 0 | 140 | 764 | 0 | 0 |  | 5330 | 3634 | 8964 | 3146 | 912 | 1381 | 0 | 157 | 3152 | 86 | 0 | 32 | 96 | 0 | 2 | 0 | 97.02
22:00 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 316 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 13 | 20 | 24 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 0 | 0 | 0 | 280 | 270 | 0 | 0 | 0 | 48 | 47 | 0 | 51 | 0 | 0 | 0 | 18 | 11 | 33 | 10 | 92 | 78 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 63 | 0 | 0 | 163 | 0 | 0 | 9 | 265 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 400 | 3 | 564 | 0 | 0 |  | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 521 | 0 | 140 | 718 | 0 | 0 |  | 5097 | 3406 | 8503 | 3146 | 911 | 1334 | 0 | 52 | 2863 | 86 | 0 | 16 | 92 | 0 | 3 | 0 | 97.02
23:00 | 0 | 0 | 0 | 180 | 0 | 22 | 0 | 323 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 7 | 16 | 26 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 18 | 0 | 0 | 0 | 280 | 270 | 0 | 0 | 0 | 48 | 46 | 0 | 5 | 0 | 0 | 0 | 18 | 11 | 33 | 10 | 88 | 76 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 40 | 0 | 0 | 163 | 0 | 0 | 9 | 270 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 350 | 1 | 564 | 0 | 0 |  | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 140 | 669 | 0 | 0 |  | 4906 | 3233 | 8139 | 3107 | 911 | 1237 | 0 | 52 | 2641 | 86 | 0 | 16 | 88 | 0 | 1 | 0 | 97.01
24:00 | 0 | 0 | 0 | 180 | 0 | 22 | 0 | 292 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 7 | 16 | 26 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 18 | 0 | 0 | 0 | 280 | 270 | 0 | 0 | 0 | 20 | 0 | 0 | 5 | 0 | 0 | 0 | 18 | 0 | 33 | 10 | 78 | 76 | 0 | 0 | 0 | 43 | 28 | 5 | 5 | 0 | 0 | 40 | 0 | 0 | 163 | 0 | 0 | 0 | 270 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 350 | 3 | 564 | 0 | 0 |  | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 140 | 576 | 0 | 0 |  | 4692 | 3025 | 7717 | 2973 | 911 | 1112 | 0 | 35 | 2503 | 86 | 0 | 16 | 78 | 0 | 3 | 0 | 97
KWH | 0 | 0 | 0 | 4378500 | 0 | 1232590 | 0 | 7825410 | 0 |  | 0 | 8905300 | 0 | 41280 | 93731 | 156934 | 6164421 | 0 | 0 | 84480 | 0 | 2447040 | 0 | 0 | 0 | 0 | 87840 | 81643 | 50269 | 143820 | 48000 | 254520 | 496440 | 565600 | 169440 | 0 | 2063280 | 0 | 0 | 0 | 15132 | 4558156 | 0 | 0 | 0 |  | 0 | 12000 | 0 | 37320 | 0 | 141120 | 245904 | 303360 | 0 | 0 | 0 | 7318900 | 6588000 | 0 | 133818 | 0 | 925704 | 696960 | 0 | 774516 | 0 | 0 | 225778 | 308232 | 181620 | 624800 | 196240 | 2118720 | 1549440 | 0 | 0 | 1200 | 1013000 | 697920 | 481200 | 502704 | 0 | 0 | 1219200 | 0 | 0 | 4402390 | 0 | 0 | 184320 | 6948000 | 308184 | 163824 | 0 | 102873 | 0 | 0 | 710400 | 0 | 547056 | 90180 | 0 | 336000 | 127127 | 8106000 | 122400 | 347203 | 133818 | 13082 | 451636 | 81399 | 335380 | 248520 | 323400 | 0 | 9022500 | 136320 | 56910 | 181440 | 220800 | 0 | 98640 | 28830 | 336960 | 245520 | 6533000 | 198091 | 47800 | 10112726 | 40800 | 8858181 | 0 | 0 |  | 19479272 | 0 | 0 | 0 | 62400 | 0 | 0 | 0 | 0 | 0 | 0 | 2523000 | 385000 | 0 | 0 | 0 | 0 | 0 | 0 | 34400 | 0 | 0 | 4065 | 0 | 0 | 0 | 0 | 184968 | 0 | 0 | 4134400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6400690 | 46560 | 0 | 261312 | 0 | 205852 | 0 | 13819 | 249888 | 12109700 | 5158064 | 0 | 50400 | 5160 | 117360 | 168000 | 0 | 0 | 10756360 | 38034 | 3447300 | 15703636 | 167630 | 0 |  | 126363192 | 81707270 | 208070462 | 76595493 | 19479272 | 32106522 | 0 | 7316271 | 65122303 | 2063280 | 0 | 2695596 | 2118720 | 532205 | 40800 | 0
Fuel Cost | 0 | 0 | 0 | 6523965 | 0 | 1639344.7 | 0 | 8216680.5 | 0 |  | 0 | 9706777 | 0 | 461510.4 | 1241935.75 | 2079375.5 | 6904151.52 | 0 | 0 | 1235097.6 | 0 | 39666518.4 | 0 | 0 | 0 | 0 | 1117324.8 | 1102180.5 | 674107.29 | 107865 | 36000 | 0 | 0 | 0 | 2882174.4 | 0 | 557085.6 | 0 | 0 | 0 | 247408.2 | 4740482.24 | 0 | 0 | 0 |  | 0 | 200160 | 0 | 504193.2 | 0 | 1632758.4 | 312298.08 | 1010188.8 | 0 | 0 | 0 | 8123979 | 7180920 | 0 | 172625.22 | 0 | 1046045.52 | 1038470.4 | 0 | 1293441.72 | 0 | 0 | 3036714.1 | 422277.84 | 136215 | 1093400 | 147180 | 15212409.6 | 1688889.6 | 0 | 0 | 19128 | 1387810 | 921254.4 | 837288 | 869677.92 | 0 | 0 | 2365248 | 0 | 0 | 4446413.9 | 0 | 0 | 364953.6 | 6948000 | 231138 | 124506.24 | 0 | 1404216.45 | 0 | 0 | 9576192 | 0 | 7576725.6 | 1054204.2 | 0 | 4589760 | 1686975.29 | 7457520 | 1488384 | 5020555.38 | 1692797.7 | 203555.92 | 5302206.64 | 886435.11 | 3565089.4 | 3372416.4 | 4168626 | 0 | 8300700 | 1765344 | 822349.5 | 2302473.6 | 2512704 | 0 | 1288238.4 | 344518.5 | 5044291.2 | 3233498.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 58437816 | 0 | 0 | 0 | 649584 | 0 | 0 | 0 | 0 | 0 | 0 | 2825760 | 746900 | 0 | 0 | 0 | 0 | 0 | 0 | 538016 | 0 | 0 | 68739.15 | 0 | 0 | 0 | 0 | 140020.776 | 0 | 0 | 35059712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6336683.1 | 625766.4 | 0 | 3091320.96 | 0 | 2614320.4 | 0 | 152699.95 | 3033640.32 | 100510510 | 5261225.28 | 0 | 372960 | 58359.6 | 1376632.8 | 2575440 | 0 | 0 | 97775312.4 | 0 | 41264181 | 134266087.8 | 0 | 0 |  | 236567346.63 | 497781687.936 | 734349034.566 | 74880720.616 | 58437816 | 36225575.74 | 0 | 95654741.79 | 408875803.2 | 557085.6 | 0 | 40473433.55 | 15212409.6 | 4031448.47 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 355 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 14 | 25 | 28 | 8 | 0 | 86 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 26 | 0 | 40 | 41 | 0 | 51 | 0 | 0 | 8 | 15 | 11 | 25 | 8 | 94 | 33 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 62 | 0 | 0 | 163 | 0 | 0 | 10 | 295 | 16 | 5 | 0 | 0 | 0 | 0 | 58 | 0 | 17 | 17 | 0 | 17 | 1 | 367 | 9 | 1 | 14 | 2 | 64 | 0 | 17 | 17 | 28 | 0 | 400 | 0 | 6 | 0 | 17 | 0 | 17 | 7 | 18 | 17 | 350 | 35 | 0 | 490 | 0 | 0 | 0 | 0 |  | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 3 | 0 | 0 | 0 | 2 | 20 | 610 | 220 | 0 | 2 | 0 | 25 | 0 | 0 | 0 | 375 | 3 | 140 | 759 | 19 | 0 |  | 9214 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 311 | 0 |  | 0 | 450 | 0 | 18 | 17 | 40 | 240 | 0 | 0 | 25 | 0 | 98 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 10 | 20 | 13 | 25 | 22 | 17 | 0 | 86 | 0 | 0 | 0 | 8 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 12 | 2 | 0 | 0 | 0 | 280 | 270 | 0 | 0 | 0 | 48 | 47 | 0 | 28 | 0 | 0 | 16 | 18 | 11 | 33 | 8 | 100 | 35 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 63 | 0 | 0 | 163 | 0 | 0 | 10 | 260 | 23 | 5 | 0 | 40 | 0 | 0 | 76 | 0 | 70 | 0 | 0 | 17 | 26 | 320 | 28 | 70 | 17 | 0 | 100 | 17 | 17 | 17 | 47 | 0 | 360 | 36 | 0 | 54 | 17 | 0 | 0 | 0 | 53 | 17 | 230 | 0 | 17 | 485 | 1 | 563 | 0 | 0 |  | 617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 45 | 0 | 50 | 0 | 0 | 55 | 600 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 633 | 0 | 140 | 717 | 0 | 0 |  | 9839 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 360 | 0 |  | 0 | 450 | 0 | 90 | 85 | 55 | 0 | 0 | 210 | 90 | 90 | 149 | 36 | 0 | 0 | 0 | 17 | 35 | 55 | 15 | 20 | 18 | 33 | 33 | 16 | 0 | 86 | 0 | 0 | 0 | 17 | 192 | 0 | 0 | 0 |  | 6 | 65 | 17 | 12 | 0 | 20 | 12 | 30 | 0 | 0 | 0 | 320 | 300 | 0 | 0 | 0 | 48 | 47 | 0 | 51 | 0 | 20 | 52 | 18 | 11 | 33 | 10 | 140 | 70 | 0 | 0 | 0 | 43 | 28 | 25 | 25 | 0 | 0 | 60 | 0 | 0 | 163 | 0 | 0 | 10 | 300 | 16 | 5 | 0 | 130 | 0 | 0 | 75 | 0 | 70 | 0 | 0 | 17 | 50 | 400 | 25 | 105 | 17 | 0 | 100 | 17 | 17 | 100 | 55 | 0 | 400 | 70 | 0 | 72 | 17 | 0 | 17 | 0 | 17 | 35 | 350 | 150 | 0 | 500 | 10 | 550 | 0 | 0 |  | 935 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 45 | 0 | 16 | 130 | 20 | 110 | 0 | 0 | 0 | 30 | 20 | 86 | 28 | 42 | 40 | 52 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 90 | 0 | 50 | 0 | 113 | 0 | 0 | 55 | 622 | 220 | 0 | 35 | 0 | 0 | 110 | 0 | 0 | 617 | 0 | 140 | 748 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 350 | 0 | 0 | 0 | 450 | 0 | 80 | 85 | 55 | 0 | 0 | 200 | 90 | 90 | 149 | 36 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 20 | 18 | 33 | 33 | 8 | 0 | 86 | 0 | 0 | 0 | 8 | 190 |  | 0 | 0 | 0 | 6 | 50 | 0 | 0 | 0 | 6 | 12 | 15 | 0 | 0 | 0 | 320 | 300 | 0 | 0 | 0 | 45 | 10 | 0 | 51 | 0 | 0 | 52 | 18 | 11 | 33 | 10 | 128 | 70 | 0 | 0 | 1.6 | 43 | 28 | 25 | 25 | 0 | 0 | 60 | 0 | 0 | 163 | 0 | 0 | 10 | 300 | 16 | 5 | 0 | 80 | 0 | 0 | 56 | 0 | 35 | 20 | 0 | 17 | 12 | 400 | 8 | 52 | 17 | 5 | 100 | 17 | 17 | 60 | 28 | 0 | 400 | 70 | 50 | 17 | 17 | 0 | 17 | 35 | 17 | 17 | 320 | 150 |  | 500 | 10 | 400 | 0 | 0 |  | 935 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 20 | 110 | 0 | 0 | 0 | 0 | 0 | 40 | 28 | 34 | 30 | 52 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 70 | 0 | 35 | 0 | 34 | 0 | 8 | 35 | 622 | 220 |  | 0 | 6 | 100 | 70 | 0 |  | 400 | 30 | 140 | 748 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 14 | 16 | 28 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 26 | 0 | 0 | 0 | 360 | 310 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 10 | 70 | 72 | 0 | 0 | 0 | 43 | 28 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 163 | 0 | 0 | 0 | 300 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 5 | 0 | 0 | 0 | 17 | 7 | 0 | 0 | 350 | 0 | 0 | 350 | 6 | 360 | 0 | 0 | 0 | 576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 290 | 224 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 361 | 8 | 140 | 423 | 25 | 0 | 0 |  |  |  | 108702015 | 19479272 | 0 | 65122303 | 10011867 | 2118720 | 532205 | 40800 | 2063280
[8 empty] | 299430 | [13 empty] | 299565 | [26 empty] | 399366 | 399587 | [8 empty] | 299280 | [26 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 |  | 399747 |  |  |  | 399575 | 399337 | 399467 | 399589 | 299230 | [7 empty] | 399245 |  | 299282 | 399274 |  | 399223 |  | 399630 | [12 empty] | 599468 | [32 empty] | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 | [8 empty] | 599726 | [9 empty] | 108.702 | 19.4793 | 0 | 65.1223 | 10.0119 | 2.1187 | 0.53221 | 0.0408 | 2.0633
| Minimum Generation |  | 6835 | 5:00
| Highest Generation |  | 9839 | 18:00 | [200 empty] | 208.0705
| Day Peak Generation |  | 9214 | 12:00
| Evening Peak Generation |  | 9839 | 18:00 | [200 empty] | 202699852
| HVDC Max Flow |  | 918 | 12:00 | [200 empty] | 202.6999
| HVDC EvPeak Flow |  | 617 | 18:00
| Load factor L.F |  | 88.11% | [166 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-12-08
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-12-07 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9214 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6539
Evening Peak Generation : |  |  | 9839 | MW Hour : | 18:00 | Available Max Generation : |  | 12664
E.P. Demand (at gen end) : |  |  | 9839 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 10000
Maximum Generation : |  |  | 9839 | MW Hour : | 18:00 | Reserve(Generation end) |  | 2664
Total Gen. (MKWH) : |  |  | 208.0705 | System Load Factor : | 88.11% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 170 | MW at | 7:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-12-08
Actual : |  | 96.98 | Ft.(MSL) , | Rule curve : | 105.37 | Ft.( MSL )
Gas Consumed : |  | Total = | 792.32 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 111106296.356
: |  |  | Coal : | 408875803.2 | Oil : | 136128175.34 | Total : | 656110274.896
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3629.1036 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 991.4744 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1387.1478 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1204.1039 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 991.57 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 736.6417 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 413.8049 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 344.0399 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 672.9006 |  |  | 0 | 0%
Total |  | 0 |  | 10370.7869 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:03 |  | Shahjahanulla 25 MW PP Syncronized
| 08:05 | Natore 132/33kV S/S TR-1 (405 T) LT is restored.
| 08:08 | Natore 132/33kV S/S TR-2 (415 T) LT is restored.
08:11 | 15:52 | Bhandaria 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Annual Maintenance
08:11 | 15:51 | Bhandaria 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Annual Maintenance
08:23 | 17:25 | Cox'sbazar-Dohazari 132 kV Ckt-2 Scheduled S/D from Coxsbazar 132/33kV end Due to Annual maintenance ( Dohazari
side) and from Dohazari 132/33kV end Due to Annual Maintenance
08:25 |  | Gazipur 100 MW PP Syncronized
08:30 |  | Jamalpur 115 MW PP (United) Syncronized
08:30 |  | Mymensingh 200 MW PP (United) Syncronized
08:35 | 12:20 | Mithapukur 132/33kV S/S TR-1(404T) LT Forced S/D Due to Changing Of 33 kv Bus DS
08:35 | 12:20 | Mithapukur 132/33kV S/S TR-2 (414T) LT Forced S/D Due to Changing Of 33 kv Bus DS
08:36 |  | Kodda 149 MW PP Unit-1 (Summit) Syncronized
08:40 |  | Bhairob 54.5 MW Syncronized
08:47 | 09:12 | Pabna 132/33kV S/S T-1 LT Scheduled S/D Due to Power shifting from main bus to transfer bus using bus coupler BKR (903B) |  |  |  |  | 20.0MW load interruption.
08:47 | 12:11 | Brahmanbaria-Shahjibazar 132 kV Ckt-1 Scheduled S/D from Brahmanbaria 132/33kV end Due to Relay testing by SPMD and
from Shahjibazar 132/33kV end Due to S/D taken By B.baria grid
08:47 |  | Pabna 132/33kV S/S T-1 HT Scheduled S/D Due to Power shifting from main bus to transfer bus using bus coupler BKR (903B)
08:48 | 14:47 | Khulshi 132/33kV S/S Khulshi-Baraulia Circuit-2 Scheduled S/D Due to Annual Maintenance .
08:50 |  | Sarishabari 3 MW Solar Plant Tripped
09:01 |  | Gazipur 52 MW PP Syncronized
09:02 | 15:49 | Tangail 132/33kV S/S RPCL-1 Scheduled S/D Due to Dead Line Checking
09:05 |  | Narshingdi 22 MW PP (Doreen) Syncronized
09:11 | 14:35 | Barapukuria-Bogura 230 kV Ckt-2 Scheduled S/D from Barapukuria 230/132/33kV end Due to Annual maintenance work.
09:18 | 16:16 | Chapai 132/33kV S/S T-1 (405T) HT Scheduled S/D Due to Annual Maintenance
09:18 | 16:17 | Chapai 132/33kV S/S T-1 (405T) LT Scheduled S/D Due to Annual Maintenance
09:31 |  | Mirsharai 150 MW Syncronized
09:33 |  | Sarishabari 3 MW Solar Plant Syncronized
09:40 |  | Karnaphuli Power Ltd. Syncronized
09:44 | 13:42 | UttaraNew 132/33kV S/S GT-01 HT Scheduled S/D Due to Annual maintenance
09:56 | 12:06 | Kaliakoir 400/230/132kV S/S 400/132kV TR1 HT Scheduled S/D Due to Annual Maintenance
09:56 | 12:06 | Kaliakoir 400/230/132kV S/S 400/132kV TR1 LT Scheduled S/D Due to Annual Maintenance
09:59 |  | Anlima Energy Ltd. Syncronized
10:00 |  | Anlima Energy Ltd. Syncronized
10:01 |  | Anlima Energy Ltd. Syncronized
| 10:02 | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT is restored.
| 10:04 | Rajshahi 132/33kV S/S Transformer T-3 (425T) LT is restored.
10:11 | 11:40 | Tangail 132/33kV S/S Tr-2 HT Forced S/D Due to 33kV BUS
Section DS burn. Working on PDB's own responsibility for
this reason no loadshed.
10:11 | 11:40 | Tangail 132/33kV S/S Tr-2 LT Forced S/D Due to 33kV BUS Section DS burn. Working on PDB's own responsibility for
this reason no loadshed.
10:13 | 12:34 | Rajshahi 132/33kV S/S Transformer T-2(415T) LT Scheduled S/D Due to Maintenance Work of T-33KV Bus. |  |  |  |  | 4.0MW load interruption.
10:14 | 12:33 | Rajshahi 132/33kV S/S Transformer T-2(415T) HT Scheduled S/D Due to Maintenance Work of T-33KV Bus.
10:17 |  | Gazipur 100 MW PP Shutdown
10:35 |  | Patenga 50MW PP (Baraka) Syncronized
10:46 |  | Kanchan Purbachal Power Generation Ltd. Syncronized
10:50 |  | Spectra Solar Plant Ltd. Tripped
10:59 |  | Spectra Solar Plant Ltd. Syncronized
11:01 |  | Anwara 300 MW PP (United) Syncronized
11:03 |  | Sikalbaha 105 MW PP (Baraka Sikalbaha) Syncronized
11:21 |  | Sarishabari 3 MW Solar Plant Tripped
11:23 |  | Juldah 100 MW Unit-1 (Acorn) Syncronized
11:28 | 12:02 | Kushtia 132/33kV S/S T2 LT Tripped showing Trip O/C IDMT 1 relays Due to Trip 50/51 O/C IDMT-1 |  |  |  |  | 36.0MW load interruption.
11:46 |  | Bagura 113 MW PP (Confidence)-2 Syncronized
11:47 |  | Ashuganj 150MW PP (Midland) Syncronized
11:51 |  | United Payra Power Ltd. Syncronized
11:52 |  | Confidence Power Bogura Unit-1 113 MW Syncronized
11:57 |  | Gazipur 100 MW PP Syncronized
12:00 |  | Day peak generation: 9214 MW.
12:03 |  | Rangpur 113 MW PP (Confidence) Syncronized
12:09 |  | Manikgonj 162MW PP(MPGL) Syncronized
12:10 |  | Khulna 115 PP MW (KPCL-2) Syncronized
12:13 |  | Kamalaghat 54 MW PP(Banco Energy) Syncronized
12:30 |  | Madanganj 102 PP(Summit) Syncronized
12:30 | 14:04 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Scheduled S/D from Brahmanbaria 132/33kV end Due to Relay test by SPMD,
Cumilla. and from Shahjibazar 132/33kV end Due to S/D taken by B.baria grid for Relay Testing
12:41 |  | Siddhirganj 100 PP(Dutch Bangla) Syncronized
12:46 |  | Meghnaghat 104 MW PP (OPCL) Syncronized
12:47 |  | Energypac Power Venture Thakurgaon Ltd. Syncronized
12:49 | 14:44 | Rajshahi 132/33kV S/S Transformer T-1(405T) LT Scheduled S/D Due to Maintenance Work of T-1 33KV Bus. |  |  |  |  | 9.0MW load interruption.
12:50 | 14:43 | Rajshahi 132/33kV S/S Transformer T-1(405T) HT Scheduled S/D Due to Maintenance Work of T-33KV Bus.
13:01 |  | Chapainawabganj 100 MW Peaking PP Syncronized
13:01 |  | Madanganj-55 MW PP(Summit) Syncronized
13:01 |  | Kodda 300 MW PP Unit-2 (Summit) Syncronized
13:07 |  | Ashuganj 195 MW PP (APSCL-United) Shutdown
13:11 |  | Gazipur 100 MW PP Shutdown
13:14 |  | Gazipur 52 MW PP Shutdown
13:16 |  | Hathazari 100 MW peaking PP Syncronized
13:16 |  | Raozan 25 MW PP Syncronized
| 13:24 | Hasnabad-Keraniganj 230kV Ckt-2 is restored.
13:25 |  | Rupsha 105 MW PP (Orion rupsha) Syncronized
13:30 |  | Meghnaghat 100 MW(IEL) Syncronized
13:36 |  | Kodda 149 MW PP Unit-1 (Summit) Shutdown
13:41 |  | Jangalia 52 MW PP (Lakdanavi) Shutdown
13:43 |  | Jodiac Power Syncronized
| 13:47 | Cumilla(N)-Kachua 132 kV Ckt-2 is restored.
| 13:55 | Kachua 132/33kV S/S TR-1 HT is restored.
| 13:56 | Kachua 132/33kV S/S TR-1 LT is restored.
13:56 |  | Raozan 25 MW PP Shutdown
13:56 |  | Bhairob 54.5 MW Shutdown
14:00 |  | Matarbari 2*600 MW (CPGCL) Syncronized
14:11 |  | Kamalaghat 54 MW PP(Banco Energy) Shutdown
| 14:17 | Cumilla(S)-Kachua 132 kV Ckt-1 is restored.
| 14:19 | Kachua 132/33kV S/S TR-2 HT is restored.
| 14:20 | Kachua 132/33kV S/S TR-2 LT is restored.
| 14:25 | Shahjadpur 132/33kV S/S T-4(435T) HT is restored.
14:28 |  | Gazipur 100 MW PP Syncronized
| 14:29 | Shahjadpur 132/33kV S/S T-4(435T) LT is restored.
14:32 |  | Kodda 300 MW PP Unit-2 (Summit) Shutdown
14:34 |  | Bagura 113 MW PP (Confidence)-2 Shutdown
14:35 |  | Energypac Power Venture Thakurgaon Ltd. Shutdown
14:36 |  | Sarishabari 3 MW Solar Plant Syncronized
14:39 |  | Confidence Power Bogura Unit-1 113 MW Shutdown
14:42 |  | Chapainawabganj 100 MW Peaking PP Shutdown
14:45 |  | Khulna 115 PP MW (KPCL-2) Shutdown
14:46 |  | United Payra Power Ltd. Shutdown
| 14:47 | Candpur- Kachua 132kV Ckt-1 is restored.
| 14:47 | Candpur- Kachua 132kV Ckt-2 is restored.
14:53 |  | Siddhirganj 100 PP(Dutch Bangla) Shutdown
14:58 |  | Juldah 100 MW Unit-1 (Acorn) Shutdown
14:59 |  | Rupsha 105 MW PP (Orion rupsha) Shutdown
15:00 |  | Feni Lanka Power Shutdown
15:02 |  | Gazipur 52 MW PP Syncronized
15:02 | 15:09 | Niamatpur 132/33kV S/S 426T LT Tripped showing DID. O/C & E/F Realy relays Due to 33 kV porsa feeder (PBS) O/C & E/F. |  |  |  |  | 10.0MW load interruption.
15:05 |  | Jamalpur 115 MW PP (United) Shutdown
15:05 |  | Madanganj-55 MW PP(Summit) Shutdown
15:07 |  | Meghnaghat 100 MW(IEL) Shutdown
15:09 |  | Jodiac Power Shutdown
15:10 |  | Hathazari 100 MW peaking PP Shutdown
15:10 |  | Rangpur 113 MW PP (Confidence) Shutdown
15:14 |  | Meghnaghat 104 MW PP (OPCL) Shutdown
15:15 |  | Katakhali 50 MW Peaking PP Syncronized
15:20 |  | Sikalbaha 105 MW PP (Baraka Sikalbaha) Shutdown
15:21 |  | Kodda 149 MW PP Unit-1 (Summit) Syncronized
15:22 |  | Manikgonj 162MW PP(MPGL) Shutdown
15:25 |  | Chowmuhani 113 MW Shutdown
15:29 |  | Ashuganj 150MW PP (Midland) Shutdown
15:29 |  | Bogra (West) 400/230 KV S/S-230 KV bus A1 & bus A2 S/D. L/S free.
15:29 |  | Chandpur 115(Doreen) Shutdown
15:33 |  | Anwara 300 MW PP (United) Shutdown
15:48 | 16:05 | Kushtia 132/33kV S/S T2 LT Tripped showing K31 relays Due to poradaha(PBS) 33 kv feeder fault (R & Y phase) |  |  |  |  | 32.0MW load interruption.
16:02 |  | Madanganj 102 PP(Summit) Shutdown
16:03 |  | Kaptai 7 MW Solar PP Shutdown
16:22 |  | Chandpur 115(Doreen) Syncronized
16:24 |  | Bagura 113 MW PP (Confidence)-2 Syncronized
16:26 |  | Chowmuhani 113 MW Syncronized
16:27 |  | Sikalbaha 105 MW PP (Baraka Sikalbaha) Syncronized
16:28 |  | Rangpur 113 MW PP (Confidence) Syncronized
16:30 |  | Jodiac Power Syncronized
16:31 |  | Energypac Power Venture Thakurgaon Ltd. Syncronized
16:31 |  | Katakhali 50 MW Peaking PP Shutdown
16:32 |  | Meghnaghat 104 MW PP (OPCL) Syncronized
16:33 |  | Manikgonj 162MW PP(MPGL) Syncronized
16:35 |  | Anwara 300 MW PP (United) Syncronized
16:37 |  | Jamalpur 115 MW PP (United) Syncronized
16:38 |  | Confidence Power Bogura Unit-1 113 MW Syncronized
16:39 |  | Mirsharai 150 MW Shutdown
16:40 |  | Madanganj-55 MW PP(Summit) Syncronized
16:40 |  | Kamalaghat 54 MW PP(Banco Energy) Syncronized
16:40 |  | Siddhirganj 100 PP(Dutch Bangla) Syncronized
16:40 |  | Meghnaghat 100 MW(IEL) Syncronized
16:42 |  | Manikganj 55 MW PP (Northern) Syncronized
16:42 |  | Mirsharai 150 MW Syncronized
16:44 |  | Spectra Solar Plant Ltd. Shutdown
16:45 |  | Raozan 25 MW PP Syncronized
16:46 |  | Ashuganj 150MW PP (Midland) Syncronized
16:51 |  | Jangalia 52 MW PP (Lakdanavi) Syncronized
16:51 |  | Feni Lanka Power Syncronized
16:52 |  | Sarishabari 3 MW Solar Plant Shutdown
16:53 |  | Nababganj 55 MW PP (Southern power ) Syncronized
16:55 |  | Sympa Solar Power 8 MW Shutdown
16:56 |  | Sirajgonj 6.55 MW Solar Shutdown
16:57 |  | Madanganj 102 PP(Summit) Syncronized
16:58 |  | Teknaf 20MW PP (Solartech) Shutdown
17:01 |  | Kodda 300 MW PP Unit-2 (Summit) Syncronized
17:03 | 18:04 | Sirajganj 132/33kV S/S T1-(415) HT Forced S/D Due to Sirajgonj PBS-01 has been taken shut down for emergency
tamai 33kV feeder maintenance.(tami bus ds red hot)
17:03 | 18:04 | Sirajganj 132/33kV S/S T1-(415) LT Forced S/D Due to Sirajgonj PBS-01 has been taken shut down for emergency
tamai 33kV feeder maintenance.(tami bus ds red hot)load shed will be 10MW at pbs
17:05 |  | Teesta Solar Limited Shutdown
17:05 |  | Mongla Orion 100 MW Solar PP Shutdown
17:14 |  | Sutiakhali 50 MW Solar PP Shutdown
17:20 |  | Intraco Solar 30 MW Shutdown
17:23 |  | Ullapara 11 MW PP (Summit) Tripped
17:54 | 19:57 | Rajshahi-Rajshahi(New) 132kV Ckt-2 Forced S/D from Rajshahi 132/33kV end Due to Red hot maintenance
18:00 |  | Evening Peak Gen. 9839 MW
18:11 |  | Jangalia 52 MW PP (Lakdanavi) Shutdown
18:13 |  | Feni Lanka Power Shutdown
18:17 |  | Siddhirganj 100 PP(Dutch Bangla) Shutdown
18:24 |  | Kodda 300 MW PP Unit-2 (Summit) Shutdown
18:25 |  | Raozan 25 MW PP Shutdown
18:31 |  | Energypac Power Venture Thakurgaon Ltd. Shutdown
18:33 |  | Madanganj-55 MW PP(Summit) Shutdown
18:34 |  | Meghnaghat 100 MW(IEL) Shutdown
18:45 |  | Ullapara 11 MW PP (Summit) Syncronized
19:01 |  | Madanganj 102 PP(Summit) Shutdown
19:18 |  | Meghnaghat 104 MW PP (OPCL) Shutdown
19:21 |  | Jamalpur 115 MW PP (United) Shutdown
19:24 |  | Confidence Power Bogura Unit-1 113 MW Shutdown
19:34 |  | Ashuganj 150MW PP (Midland) Shutdown
19:36 |  | Bagura 113 MW PP (Confidence)-2 Shutdown
19:39 |  | Anwara 300 MW PP (United) Shutdown
19:40 |  | Rangpur 113 MW PP (Confidence) Shutdown
19:41 |  | Manikgonj 162MW PP(MPGL) Shutdown
19:43 |  | Kamalaghat 54 MW PP(Banco Energy) Shutdown
19:46 |  | Jodiac Power Shutdown
19:46 |  | Nababganj 55 MW PP (Southern power ) Shutdown
19:50 |  | Manikganj 55 MW PP (Northern) Shutdown
19:53 |  | Sikalbaha 105 MW PP (Baraka Sikalbaha) Shutdown
19:53 |  | Chowmuhani 113 MW Shutdown
20:01 |  | Gazipur 100 MW PP Shutdown
20:15 |  | Mirsharai 150 MW Shutdown
| 20:38 | Feni 132/33kV S/S T-1(405T) HT is restored.
20:46 |  | Mymensingh 200 MW PP (United) Shutdown
21:18 |  | Gazipur 52 MW PP Shutdown
21:30 | 22:18 | Siddhirganj 132/33kV S/S 120MW EGCB GT2 Forced S/D Due to Transformer Oil leakage maintenance work by EGCB.
21:38 |  | Chandpur 115(Doreen) Shutdown
21:40 |  | Anlima Energy Ltd. Shutdown
21:43 |  | Kanchan Purbachal Power Generation Ltd. Shutdown
21:44 |  | Karnaphuli Power Ltd. Shutdown
21:49 |  | Patenga 50MW PP (Baraka) Shutdown
23:03 |  | Chandpur 200MW (Desh energy) Shutdown
23:18 |  | Shahjahanulla 25 MW PP Shutdown
23:25 |  | Ashuganj 55 MW PP (Precision) Shutdown
23:47 |  | Ghorashal 108 MW PP (Regent) Shutdown
23:49 |  | Narshingdi 22 MW PP (Doreen) Shutdown
23:50 |  | Sylhet 10MW PP (Desh) Shutdown with remarks:- NLDC no demand.
23:55 |  | Feni 11 MW PP (Doreen) Shutdown
00:10 |  | Ghorashal 108 MW PP (Regent) Shutdown
00:10 |  | Ghorashal 108 MW PP (Regent) Shutdown
00:26 |  | Kodda 150 MW PP B-R Shutdown
01:03 |  | Ashuganj 50 MW PP Shutdown
01:05 |  | Fenchugonj 51 MW PP (Barakatullah) Shutdown
01:08 |  | Fenchuganj 44MW (Energyprima) Shutdown
01:13 |  | Jangalia 33MW PP (Summit) Shutdown
01:29 |  | Feni 22MW PP (Doreen) Forced Shutdown with remarks:- NLDC DEMAND ZERO
01:49 |  | Ashuganj 51 MW PP (Midland) Shutdown
05:00 |  | Minimum Generation 6539 MW.
05:03 |  | Bhairob 54.5 MW Syncronized
05:51 |  | Ashuganj 50 MW PP Syncronized
06:13 |  | Ishwardi-Natore 132kV Ckt-2 Scheduled S/D from Natore 132/33kV end Due to bus maintenance.
06:14 |  | Natore-Rajshahi 132kV Ckt-1 Scheduled S/D from Natore 132/33kV end Due to bus maintenance
06:14 |  | Natore-Rajshahi 132kV Ckt-2 Scheduled S/D from Natore 132/33kV end Due to bus maintenance
06:15 |  | Bogura-Natore 132 kV Ckt-1 Scheduled S/D from Natore 132/33kV end Due to bus maintenance
06:15 |  | Bogura-Natore 132 kV Ckt-2 Scheduled S/D from Natore 132/33kV end Due to bus maintenance.
06:15 |  | Natore 132/33kV S/S Rajlanka Scheduled S/D Due to bus maintenance
06:16 |  | Natore 132/33kV S/S TR-2 (415 T) LT Scheduled S/D Due to bus maintenance.
06:16 |  | Natore 132/33kV S/S TR-1 (405 T) LT Scheduled S/D Due to bus maintenance.
06:17 |  | Natore 132/33kV S/S TR-4 (435 T) LT Scheduled S/D Due to bus maintenance.
06:17 |  | Natore 132/33kV S/S TR-3 (425 T) LT Scheduled S/D Due to bus maintenance.
06:19 |  | Natore 132/33kV S/S TR-1 (405 T) HT Scheduled S/D Due to bus maintenance.
06:19 |  | Natore 132/33kV S/S TR-2 (415 T) HT Scheduled S/D Due to bus maintenance.
06:19 |  | Natore 132/33kV S/S TR-3 (425 T) HT Scheduled S/D Due to bus maintenance.
06:19 |  | Natore 132/33kV S/S TR-4 (435 T) HT Scheduled S/D Due to bus maintenance.
06:20 |  | Ishwardi-Natore 132kV Ckt-1 Scheduled S/D from Natore 132/33kV end Due to bus maintenance
06:20 |  | Natore 132/33kV S/S 132 KV MAIN BUS Scheduled S/D Due to annual maintenance |  |  |  |  | 51.0MW load interruption.
06:23 |  | Kaptai 7 MW Solar PP Syncronized
06:26 |  | Siddhirganj 335 MW CCPP Shutdown with remarks:- GT
06:35 |  | Feni 22MW PP (Doreen) Syncronized
06:35 |  | Sympa Solar Power 8 MW Syncronized
06:36 |  | Teknaf 20MW PP (Solartech) Syncronized
06:36 |  | Sutiakhali 50 MW Solar PP Syncronized
06:37 |  | Intraco Solar 30 MW Syncronized
06:40 |  | Spectra Solar Plant Ltd. Syncronized
06:41 |  | Teesta Solar Limited Syncronized
06:50 |  | Sarishabari 3 MW Solar Plant Syncronized
06:51 |  | Ashuganj 50 MW PP Syncronized
06:54 |  | Sirajgonj 6.55 MW Solar Syncronized
07:16 |  | Siddhirgonj 2*120 MW GTPP Syncronized with remarks:- GT-1
07:21 |  | Kodda 150 MW PP B-R Syncronized
07:25 |  | Bogura-Natore 132 kV Ckt-1 Scheduled S/D from Bogura 132/33kV end Due to S/d.
07:25 |  | Bogura-Natore 132 kV Ckt-2 Scheduled S/D from Bogura 132/33kV end Due to S/D.
07:34 |  | Munshiganj 132/33kV S/S Transformer-1 LT Scheduled S/D Due to PBS Annual Maintenance |  |  |  |  | 46.0MW load interruption.
07:34 |  | Munshiganj 132/33kV S/S Transformer-2 LT Scheduled S/D Due to PBS Annual Maintenance
07:34 |  | Munshiganj 132/33kV S/S Transformer-1 HT Scheduled S/D Due to PBS Annual Maintenance
07:34 |  | Munshiganj 132/33kV S/S Transformer-2 HT Scheduled S/D Due to PBS Annual Maintenance
07:39 |  | Aminbazar-Mirpur 132kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to PT change

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-12-07 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4378500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 73 | 1232590 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 311 | 7825410 | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8905300 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 18 | 41280 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 17 | 93731 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 40 | 156934 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 10 | 143820 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 25 | 84480 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 240 | 6164421 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 87840 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 98 | 2447040 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 81643 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 50269 | Low demand
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 33 | 302520 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 496440 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 22 | 565600 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 17 | 169440 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 40 | 102873 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 70 | 547056 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 347203 | Low demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 36 | 136320 | Low demand
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 181440
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 28830
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 245520 | Fuel shortage
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5422 | 1915 | 34816500
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 8 | 15132 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 90180
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 20 | 141120 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 86 | 2063280 | Unit-2 under maint.
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 192 | 4558156 | Machine problem
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 133818 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 12000 | Low demand
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 37320 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 12 | 245904 | Fuel shortage
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 2 | 303360
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 13082
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 100 | 451636 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 81399 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 335380 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 220800 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 0 | 198091 | Reserve
| SS Power I |  | SS Power | 2*612 | 1224 | 485 | 10112726
| Cox's Bazar Wind |  | IPP | 66 | 0 | 1 | 40800 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 563 | 8858181 | On test.
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 17 | 47800
| Chattogram area Total |  |  |  | 3769 | 1554 | 27960165
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 0 | Under maint.
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7318900 | Under maint.
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 6588000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 230 | 6533000 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 48 | 925704
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 0 | 47 | 696960
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 133818 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 28 | 774516 | load increase.
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 26 | 127127 | Low demand
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 336000 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 308232 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 181620
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 100 | 2118720
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 624800
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 16 | 225778 | Low demand
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 8 | 196240 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 248520 | Low demand
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 47 | 323400 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 98640 | Low demand
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 53 | 336960 | Fuel shortage
| Cumilla Area Total |  |  |  | 2896 | 1249 | 28096935
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 35 | 1549440 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Contract Expired
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 1200
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 76 | 710400 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 28 | 122400 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 56910
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 139 | 2440350
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1013000
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 28 | 697920 | Engine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 25 | 481200 | Gas shortage
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 25 | 502704 | Gas shortage
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 163824 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1219200
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 0 | 0 | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 163 | 4402390 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 23 | 308184 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 260 | 6948000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 320 | 8106000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 184320
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 360 | 9022500
| Sylhet Area Total |  |  |  | 2427 | 1325 | 33049242
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 617 | 19479272
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 62400 | Reserve
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 46560 | Reserve
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 117360
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | Fuel shortage
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 633 | 10756360
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 1250 | 30461952
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 18 | 385000 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 130 | 2523000
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 600 | 12109700 | Unit-2 under maint.
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5158064
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 50400 | Reserve
| Barisal 307 MW |  | IPP | 307*1 | 307 | 140 | 3447300 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1108 | 23673464
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 4065 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 227 | 6400690 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 0 | 184968
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 34400 | Reserve
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 45 | 261312 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 55 | 249888 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 5160
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 717 | 15703636
| Rajshahi Area Total |  |  |  | 3631 | 1044 | 22844119
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4134400 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 50 | 205852 | Low demand
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 13819
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 35 | 168000 | Low demand
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 38034
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 167630
| Rangpur Area Total |  |  |  | 950 | 255 | 4727735
| Total |  |  |  | 25211 | 9839 | 208070462
| Eastern Grid Total |  |  |  | 15128 | 6182 | 126363192
| Western Grid Total |  |  |  | 10083 | 3657 | 81707270
| National Grid Total |  |  |  | 25211 | 9839 | 208070462
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-12-07
| (a) ENTIRE EASTERN GRID : |  | 6695.04 | MW | (b) ENTIRE WESTERN GRID : |  | 2833.4 | MW
| i) Dhaka area |  | 3720.84 | MW | i) Khulna area |  | 1065 | MW
| ii) Chittagong area |  | 1156.2 | MW | ii) Rajshahi area |  | 846.4 | MW
| iii) Comilla area |  | 805 | MW | iii) Barisal area |  | 266 | MW
| iv) Mymensingh area |  | 669 | MW | iv) Rangpur area |  | 656 | MW
| v) Sylhet area |  | 344 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 9528.44 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 16 | 17:00 | Kamrangirchar | 46.8 | 13:00 | Narinda | 50 | 13:00 | Sherpur | 90 | 18:00
2 | AKSML | 14 | 01:00 | Chowmuhani | 134 | 19:00 | Kaptai | N/A | N/A | Narshingdi | 135 | 19:00 | Shikalbaha | 24 | 11:00
3 | Aftabnagar | 24 | 11:00 | Chuadanga | 65 | 18:00 | Kazla | 76 | 15:00 | Natore | 88 | 18:00 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 68 | 13:00 | Coxsbazar | 108 | 18:00 | Keranigonj | 64 | 13:00 | Nawabganj | 29 | 13:00 | Shitalakhya | 84 | 12:00
5 | Agrabad | 54 | 17:00 | Cumilla(N) | 114 | 02:00 | Khagrachori | 20 | 17:00 | Netrakona | 83 | 18:00 | Sholosohor | 37 | 18:00
6 | Amnura | 27 | 18:00 | Cumilla(S) | 105 | 16:00 | Khulna | 78 | 18:30 | New | 56.4 | 12:00 | Shyampur | 158 | 10:00
7 | Ashuganj | 56 | 00:00 | Daudkandi | 100 | 18:00 | Khulshi | 158 | 18:00 | Niamatpur | 39 | 18:00 | Siddhirganj | 76 | 00:00
8 | BIPTC | N/A | N/A | Dhaka | 18 | 11:00 | Kishoreganj | 82 | 00:00 | Noapara | 36 | 18:00 | Sirajganj | 79 | 12:00
9 | BSRM | 140 | 04:00 | Dhamrai | 94 | 11:00 | Kodda | 238 | 09:00 | PHP | 7 | 14:00 | Sonargaon | 87 | 01:00
10 | Bagerhat | 65 | 18:00 | Dhanmondi | 85.2 | 13:00 | Kulaura | 30 | 18:00 | Pabna | 77 | 18:00 | Sreemongol | 43 | 18:00
11 | Bakulia | 77 | 18:00 | Dohazari | 58 | 18:00 | Kurigram | 48 | 18:00 | Palashbari | 64 | 18:00 | Sreepur | 62 | 10:00
12 | Banani | 19.2 | 13:00 | Faridpur | 98 | 19:00 | Kushtia | 90 | 13:00 | Panchagarh | 38 | 18:00 | Srinagar | 25.22 | 19:00
13 | Bangabhaban | 11 | 10:00 | Fatullah | 58 | 12:00 | Lalbag | 86 | 13:00 | Patuakhali | 60 | 21:00 | Sunamganj | 30 | 18:00
14 | Barapukuria | 47 | 19:00 | Fenchuganj | 23 | 20:00 | Lalmonirhat | 30 | 18:30 | Payra | 20 | 18:30 | Sylhet | 10 | 13:00
15 | Barguna | 12 | 00:00 | Feni | 71 | 18:00 | MI_Cement | 18.9 | 11:00 | Postogola | 41 | 13:00 | Sylhet-132 | 88 | 18:30
16 | Barishal | 76 | 13:00 | GPH | 85 | 06:00 | Madanganj | 21 | 12:00 | Purbachal | 12 | 12:00 | TK | 22 | 18:00
17 | Barishal-230 | 62 | 20:00 | Ghorashal | 60 | 18:30 | Madaripur | 55 | 19:30 | Purbasadipur | 97 | 18:00 | Tangail | 112 | 13:00
18 | Baroaulia | 64 | 10:00 | Goalpara | 18 | 13:00 | Madartek | 57.66 | 13:00 | Rahim | 43 | 00:00 | Thakurgaon | 73 | 18:00
19 | Baroirhat | 38 | 18:30 | Gollamari | 43 | 13:00 | Madunaghat | 36 | 13:00 | Rajbari | 40 | 18:00 | Tongi | 94 | 11:00
20 | Bashundhara | 119 | 18:00 | Gopalganj | 64 | 18:00 | Magura | 40 | 18:00 | Rajendrapur | 84 | 11:00 | Ullon | 39 | 18:00
21 | BashundharaCement | 0 | 00:00 | Gulshan | 74 | 12:00 | Mahasthangarh | 44 | 17:00 | Rajshahi | 88 | 12:00 | Uttara | 57 | 18:00
22 | Beanibazar | 40 | 18:30 | Halishahar | 95 | 15:00 | Manikganj | 79 | 10:00 | Rajshahi-230 | 28 | 18:00 | UttaraNew | 39 | 03:00
23 | Benapole | 34 | 18:00 | HaripurSBU | 137 | 17:00 | Maniknagar | 48 | 13:00 | Ramganj | 66 | 20:00 | Zigatola | 73 | 13:00
24 | Bhaluka | 106 | 19:00 | Hasnabad | 60 | 12:00 | Matarbari | 32 | 18:00 | Rampur | 27 | 17:00
25 | Bhandaria | 34 | 19:30 | Hathazari | 52 | 18:00 | Matuail | 54 | 00:00 | Rangamati | 13 | 18:00
26 | Bhangura | 17 | 18:00 | Ishurdi | 49 | 18:00 | Millgate | 85 | 12:00 | Rangpur | 101 | 09:00
27 | Bheramara(GK) | 38 | 18:00 | Jaldhaka | 45 | 18:00 | Mirpur | 86 | 18:00 | Ruppur | 4.2 | 10:00
28 | Bhulta | 219 | 00:00 | Jamalpur | 103 | 18:00 | Mirsorai | 3 | 09:00 | SSM | 1 | 21:00
29 | Bog-Sherpur | 38 | 00:00 | Jashore | 85 | 18:00 | Mirzapur | 22.7 | 19:00 | Saidpur | 85 | 09:00
30 | Bogura | 99 | 18:30 | Jhenaidah | 79 | 18:00 | Mithapukur | 35 | 18:00 | Satkhira | 82 | 18:00
31 | Borhanuddin | 36 | 21:00 | Joydebpur | 123 | 12:00 | Modern | 0 | 00:00 | Satmasjid | 59 | 18:00
32 | Brahmanbaria | 95 | 00:00 | Joypurhat | 36 | 18:00 | Mogbazar | 72.4 | 13:00 | Savar | 136 | 10:00
33 | Cantonment | 134 | 11:00 | Juldah | 19 | 07:00 | Mongla | 25 | 10:00 | SevenRings | 9.12 | 19:30
34 | Chandpur | 51 | 18:00 | KSRM | 24 | 00:00 | Motijheel | 28 | 13:00 | ShahCement | 23 | 00:00
35 | Chandraghona | 22 | 18:00 | Kabirpur | 248 | 09:00 | Munshiganj | 62 | 01:00 | Shahjadpur | 65 | 18:00
36 | Chapai | 44 | 12:00 | Kachua | 24 | 18:30 | Mymensingh | 133 | 00:00 | Shahjibazar | 78 | 19:00
37 | Charsaidpur | 11 | 00:00 | Kallyanpur | 68 | 12:00 | Naogaon | 83 | 18:00 | Shahmirpur | 48.8 | 16:00
38 | Chauddagram | 38 | 20:00 | Kalurghat | 36 | 15:00 | Narail | 32 | 18:30 | Shariatpur | 46 | 20:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-12-07 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 408 | 05:00 | 389 | 16:00 | Aminbazar | 413 | 05:00 | 399 | 12:00
| Ashuganj | N/A | N/A | N/A | N/A | Ashuganj | 402 | 04:00 | 390 | 08:00
| Bhulta | 415 | 06:00 | 404 | 12:00 | Bhulta | N/A | N/A | N/A | N/A
| Bibiana | 409 | 14:00 | 402 | 12:00 | Bibiana | 418 | 04:00 | 410 | 12:00
| BIPTC | 412 | 02:00 | 400 | 09:00 | BIPTC | 417 | 05:00 | 404 | 12:00
| Bogura | N/A | N/A | N/A | N/A | Bogura | 415 | 04:00 | 400 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 240 | 05:00 | 229 | 12:00 | Hasnabad | 240 | 05:00 | 230 | 15:00
| AKSML | 228 | 18:00 | 219 | 02:00 | Hathazari | 226 | 16:00 | 219 | 20:00
| Aminbazar | 240 | 01:00 | 232 | 16:00 | Ishurdi | 237 | 05:00 | 226 | 12:00
| Ashuganj | 237 | 06:00 | 231 | 16:00 | Jhenaidah | 237 | 05:00 | 225 | 12:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 241 | 04:00 | 236 | 08:00
| Baghabari | 233 | 01:00 | 225 | 12:00 | Keranigonj | 240 | 05:00 | 228 | 12:00
| Barapukuria | 225 | 17:00 | 218 | 11:00 | Khulna(S) | 243 | 05:00 | 232 | 12:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 243 | 05:00 | 238 | 20:00 | Maniknagar | 239 | 04:00 | 232 | 12:00
| Bheramara | 236 | 05:00 | 223 | 12:00 | Meghnaghat | 243 | 03:00 | 239 | 11:00
| Bhulta | 241 | 04:00 | 232 | 12:00 | Mirsorai | 231 | 18:00 | 221 | 16:00
| Bibiana | 234 | 10:00 | 229 | 13:00 | Rajshahi | 235 | 02:00 | 223 | 12:00
| BIPTC | 237 | 01:00 | 223 | 03:00 | Rampal | 242 | 05:00 | 228 | 12:00
| Bogura | 234 | 04:00 | 220 | 05:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 245 | 10:00 | 242 | 01:00 | Rampura | 239 | 05:00 | 231 | 12:00
| BSRM | 230 | 18:00 | 221 | 02:00 | Shikalbaha | 223 | 18:30 | 217 | 09:00
| Cumilla(N) | 235 | 18:00 | 229 | 16:00 | Shyampur | 240 | 05:00 | 230 | 12:00
| Fenchuganj | 239 | 18:00 | 233 | 12:00 | Siddhirganj | 240 | 05:00 | 233 | 11:00
| Ghorashal | 240 | 00:00 | 235 | 01:00 | Sirajgonj | 240 | 04:00 | 233 | 12:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 236 | 05:00 | 229 | 12:00
| GPH | 230 | 19:00 | 218 | 22:00 | Tongi | 236 | 04:00 | 230 | 07:00
| Haripur | 238 | 05:00 | 232 | 12:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 135 | 04:00 | 130 | 12:00 | Lalbag | 138 | 04:00 | 129 | 00:00
| Agargaon | 141 | 04:00 | 134 | 12:00 | Lalmonirhat | 131 | 01:00 | 123 | 08:00
| Agrabad | 132 | 18:00 | 127 | 16:00 | Madanganj | 136 | 05:00 | 130 | 12:00
| AKS | 130 | 18:00 | 126 | 10:00 | Madaripur | 136 | 04:00 | 132 | 12:00
| Aminbazar | 140 | 01:00 | 134 | 11:00 | Madartek | 135 | 05:00 | 129 | 12:00
| Amnura | 137 | 02:00 | 131 | 12:00 | Madunaghat | 132 | 05:00 | 128 | 16:00
| Ashuganj | 140 | 00:00 | 139 | 13:00 | Magura | 139 | 01:00 | 131 | 12:00
| Bagerhat | 133 | 03:00 | 126 | 12:00 | Mahasthangarh | 136 | 03:00 | 130 | 12:00
| Bakulia | 132 | 02:00 | 128 | 11:00 | Manikganj | 134 | 17:00 | 126 | 08:00
| Banani | 137 | 04:00 | 131 | 12:00 | Maniknagar | 137 | 04:00 | 132 | 12:00
| Bangabhaban | 137 | 04:00 | 132 | 12:00 | Matarbari | 124 | 05:00 | 115 | 16:00
| Barapukuria | 135 | 14:00 | 129 | 08:00 | Matuail | 136 | 18:00 | 130 | 12:00
| Barguna | 137 | 04:00 | 133 | 19:30 | Millgate | 140 | 04:00 | 131 | 12:00
| Barishal | 139 | 04:00 | 130 | 19:30 | Mirpur | 139 | 05:00 | 133 | 12:00
| Barishal-230 | 138 | 05:00 | 136 | 19:30 | Mirzapur | 136 | 05:00 | 127 | 08:00
| Baroaulia | 133 | 18:30 | 128 | 01:00 | Mithapukur | 135 | 05:00 | 127 | 08:00
| Baroirhat | 132 | 14:00 | 126 | 16:00 | MI_Cement | 137 | 04:00 | 130 | 12:00
| Bashundhara | 137 | 01:00 | 131 | 12:00 | Modern | 131 | 01:00 | 129 | 10:00
| BashundharaCement | 136 | 05:00 | 130 | 12:00 | Mogbazar | 137 | 05:00 | 130.5 | 12:00
| Beanibazar | 131 | 01:00 | 129 | 12:00 | Mongla | 133 | 04:00 | 126 | 12:00
| Benapole | 138 | 04:00 | 129 | 12:00 | Motijheel | 137 | 04:00 | 132 | 12:00
| Bhaluka | 134 | 18:00 | 129 | 12:00 | Munshiganj | 136 | 18:00 | 131 | 12:00
| Bhandaria | 136 | 09:00 | 130 | 19:30 | Mymensingh | 139 | 10:00 | 121 | 08:00
| Bhangura | 142 | 05:00 | 134 | 11:00 | Naogaon | 134 | 05:00 | 128 | 11:00
| Bheramara | 138 | 05:00 | 130 | 12:00 | Narail | 138 | 01:00 | 132 | 11:00
| Bheramara(GK) | 137 | 01:00 | 131 | 11:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 129 | 18:00 | 120 | 12:00 | Narshingdi | 132 | 18:00 | 125 | 12:00
| Bog-Sherpur | 138 | 04:00 | 132 | 12:00 | Natore | 137 | 01:00 | 131 | 12:00
| Bogura | 138 | 14:00 | 132 | 11:00 | Nawabganj | 137 | 06:00 | 130 | 12:00
| Bogura-230 | 139 | 04:00 | 131 | 12:00 | Netrakona | 135 | 17:00 | 120 | 08:00
| Brahmanbaria | 130 | 17:00 | 127 | 00:00 | New | 139 | 00:00 | 132 | 12:00
| Cantonment | 141 | 04:00 | 133 | 12:00 | Niamatpur | 135 | 04:00 | 128 | 11:00
| Chandpur | 136 | 17:00 | 124 | 07:00 | Noapara | 136 | 02:00 | 129 | 12:00
| Chandraghona | 133 | 18:00 | 129 | 19:30 | Pabna | 140 | 05:00 | 133 | 12:00
| Chapai | 137 | 00:00 | 132 | 12:00 | Palashbari | 134 | 00:00 | 126 | 19:30
| Charsaidpur | 136 | 06:00 | 131 | 12:00 | Panchagarh | 132 | 14:00 | 118 | 08:00
| Chauddagram | 135 | 08:00 | 128 | 06:00 | Patuakhali | 136 | 04:00 | 133 | 18:30
| Chhatak | 131 | 04:00 | 129 | 00:00 | Payra | 138 | 05:00 | 135 | 18:30
| Chowmuhani | 133 | 18:00 | 124 | 22:00 | PHP | 133 | 18:00 | 125 | 22:00
| Chuadanga | 140 | 03:00 | 130 | 12:00 | Postogola | 138 | 05:00 | 132 | 12:00
| Coxsbazar | 122 | 18:00 | 112 | 17:00 | Purbachal | 138 | 04:00 | 130 | 12:00
| Cumilla(N) | 138 | 18:00 | 132 | 16:00 | Purbasadipur | 131 | 14:00 | 120 | 08:00
| Cumilla(S) | 138 | 18:00 | 116 | 17:00 | Rahanpur | 138 | 02:00 | 134 | 08:00
| Daudkandi | 135 | 18:00 | 130 | 11:00 | Rahim | 137 | 18:00 | 131 | 12:00
| Dhaka | 135 | 05:00 | 130 | 12:00 | Rajbari | 135 | 03:00 | 130 | 12:00
| Dhamrai | 137 | 01:00 | 128 | 12:00 | Rajendrapur | 139 | 04:00 | 127 | 16:00
| Dhanmondi | 138 | 05:00 | 131.6 | 12:00 | Rajshahi | 137 | 03:00 | 131 | 12:00
| Dohazari | 129 | 13:00 | 127 | 00:00 | Rajshahi-230 | 137 | 02:00 | 130 | 12:00
| Faridpur | 135 | 03:00 | 130 | 12:00 | Ramganj | 135 | 18:00 | 124 | 21:00
| Fatullah | 139 | 05:00 | 132 | 12:00 | Rampur | 132 | 18:00 | 128 | 10:00
| Fenchuganj | 136 | 18:00 | 133 | 00:00 | Rampura | 136 | 04:00 | 131 | 12:00
| Feni | 132 | 18:00 | 126 | 16:00 | Rangamati | 132 | 18:00 | 128 | 16:00
| Ghorashal | 142 | 00:00 | 137 | 16:00 | Rangpur | 132 | 02:00 | 123 | 09:00
| Goalpara | 137 | 05:00 | 130 | 12:00 | Ruppur | 139 | 02:00 | 132 | 12:00
| Gollamari | 135 | 04:00 | 129 | 12:00 | Saidpur | 132 | 03:00 | 124 | 12:00
| Gopalganj | 135 | 04:00 | 129 | 12:00 | Satkhira | 134 | 04:00 | 127 | 11:00
| Gopalganj-400 | 135 | 05:00 | 130 | 12:00 | Satmasjid | 141 | 05:00 | 133 | 12:00
| Gulshan | 136 | 05:00 | 131 | 12:00 | Savar | 139 | 02:00 | 131 | 12:00
| Halishahar | 132 | 18:00 | 127 | 11:00 | SevenRings | 143 | 05:00 | 137 | 12:00
| Haripur | 137 | 18:00 | 131 | 12:00 | ShahCement | 136 | 06:00 | 131 | 12:00
| HaripurSBU | 137 | 18:00 | 131 | 12:00 | Shahjadpur | 143 | 03:00 | 137 | 12:00
| Hasnabad | 138 | 03:00 | 132 | 11:00 | Shahjibazar | 130 | 02:00 | 128 | 00:00
| Hathazari | 134 | 14:00 | 130 | 11:00 | Shahmirpur | 132 | 18:00 | 126 | 16:00
| Ishurdi | 140 | 01:00 | 133 | 12:00 | Shariatpur | 136 | 05:00 | 131 | 12:00
| Jaldhaka | 132 | 05:00 | 121 | 07:00 | Sherpur | 135 | 10:00 | 115 | 08:00
| Jamalpur | 139 | 10:00 | 118 | 08:00 | Shikalbaha | 122 | 07:00 | 118 | 01:00
| Jashore | 136 | 04:00 | 128 | 12:00 | Shikalbaha-230 | 133 | 05:00 | 129 | 16:00
| Jhenaidah | 138 | 04:00 | 133 | 12:00 | Shitalakhya | 137 | 04:00 | 130 | 12:00
| Jhenaidah-230 | 140 | 04:00 | 133 | 12:00 | Sholosohor | 132 | 18:00 | 126 | 16:00
| Joydebpur | 140 | 02:00 | 132 | 12:00 | Shyampur | 137 | 02:00 | 131 | 12:00
| Joypurhat | 134 | 00:00 | 128 | 12:00 | Shyampur-230 | 138 | 04:00 | 132 | 12:00
| Juldah | 132 | 18:00 | 129 | 20:00 | Siddhirganj | 136 | 06:00 | 131 | 12:00
| Kabirpur | 136 | 18:00 | 128 | 12:00 | Sirajganj | 140 | 03:00 | 130 | 12:00
| Kachua | 138 | 18:00 | 127 | 21:00 | Sonargaon | 137 | 18:00 | 130 | 12:00
| Kaliakoir | 138 | 04:00 | 133 | 08:00 | Sreemongol | 131 | 01:00 | 129 | 12:00
| Kallyanpur | 138 | 01:00 | 132 | 12:00 | Sreepur | 135 | 04:00 | 131 | 12:00
| Kalurghat | 132 | 00:00 | 128 | 16:00 | Srinagar | 139 | 05:00 | 130 | 12:00
| Kamrangirchar | 137 | 03:00 | 130 | 12:00 | SSM | 138 | 18:30 | 131 | 11:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 130 | 05:00 | 128 | 12:00
| Kazla | 137 | 06:00 | 131 | 13:00 | Sylhet | 132 | 01:00 | 130 | 13:00
| Keranigonj | 138 | 04:00 | 130 | 12:00 | Sylhet-132 | 131 | 00:00 | 130 | 02:00
| Khagrachori | 131 | 00:00 | 127 | 16:00 | Tangail | 134 | 02:00 | 126 | 08:00
| Khulna | 135 | 03:00 | 129 | 12:00 | Thakurgaon | 133 | 14:00 | 118 | 08:00
| Khulna(S) | 136 | 04:00 | 129 | 12:00 | TK | 133 | 01:00 | 128 | 11:00
| Khulshi | 131 | 18:00 | 126 | 16:00 | Tongi | 140 | 00:00 | 134 | 16:00
| Kishoreganj | 136 | 10:00 | 132 | 12:00 | Ullon | 135 | 05:00 | 129 | 12:00
| Kodda | 139 | 13:00 | 126 | 15:00 | Uttara | 141 | 05:00 | 133 | 12:00
| KSRM | 132 | 03:00 | 128 | 10:00 | UttaraNew | 140 | 02:00 | 132 | 12:00
| Kulaura | 133 | 04:00 | 131 | 12:00 | Zigatola | 138 | 04:00 | 130 | 04:00
| Kurigram | 132 | 03:00 | 124 | 09:00
| Kushtia | 138 | 03:00 | 132 | 12:00

## L-Curve
Date | 2023-12-07
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 560 | 4692 | 3025 | 7717 |  |  |  | QF-LDC-11
0:30 | 525 | 4736.5 | 3219.5 | 7956 | Date: | 2023-12-07
1:00 | 490 | 4781 | 3414 | 8195
1:30 | 460 | 4586.5 | 3318 | 7904.5
2:00 | 430 | 4392 | 3222 | 7614
2:30 | 420 | 4333.5 | 3140 | 7473.5 | [5 empty] | Gen. at Eve. Peak | 9839 | 9839 MW (18:00 )
3:00 | 410 | 4275 | 3058 | 7333 | [6 empty] | 18:00
3:30 | 391 | 4243 | 2974 | 7217 | [5 empty] | Gen. at Day Peak | 9214 | 9214 MW (12:00 )
4:00 | 372 | 4211 | 2890 | 7101 | [6 empty] | 12:00
4:30 | 357 | 4161.5 | 2806.5 | 6968 | [5 empty] | Highest Generation | 9839
5:00 | 342 | 4112 | 2723 | 6835 | [6 empty] | 18:00
5:30 | 321 | 4157.5 | 2708 | 6865.5
6:00 | 300 | 4203 | 2693 | 6896
6:30 | 235 | 4403.5 | 2703 | 7106.5
7:00 | 170 | 4604 | 2713 | 7317
7:30 | 250 | 4807 | 2914 | 7721
8:00 | 330 | 5010 | 3115 | 8125
8:30 | 358 | 5058.5 | 3267 | 8325.5
9:00 | 386 | 5107 | 3419 | 8526
9:30 | 389 | 5162.5 | 3379 | 8541.5
10:00 | 392 | 5218 | 3339 | 8557
10:30 | 486 | 5232.5 | 3427 | 8659.5
11:00 | 580 | 5247 | 3515 | 8762
11:30 | 560 | 5384.5 | 3603.5 | 8988
12:00 | 540 | 5522 | 3692 | 9214
12:30 | 585 | 5533.5 | 3752.5 | 9286
13:00 | 630 | 5545 | 3813 | 9358
13:30 | 667 | 5346.5 | 3743 | 9089.5
14:00 | 704 | 5148 | 3673 | 8821
14:30 | 674 | 5175 | 3513.5 | 8688.5
15:00 | 644 | 5202 | 3354 | 8556
15:30 | 628 | 5176.5 | 3378.5 | 8555
16:00 | 612 | 5151 | 3403 | 8554
16:30 | 572 | 5283.5 | 3456.5 | 8740
17:00 | 532 | 5416 | 3510 | 8926
17:30 | 351 | 5799 | 3583.5 | 9382.5
18:00 | 170 | 6182 | 3657 | 9839
18:30 | 180 | 5994.5 | 3675.5 | 9670
19:00 | 190 | 5807 | 3694 | 9501
19:30 | 280 | 5649 | 3659 | 9308
20:00 | 330 | 5396 | 3764 | 9160 |  |  |  | Executive Engineer
20:30 | 385 | 5363 | 3699 | 9062 |  |  |  | Network Operation Division
21:00 | 440 | 5330 | 3634 | 8964
21:30 | 460 | 5213.5 | 3520 | 8733.5
22:00 | 480 | 5097 | 3406 | 8503 |  |  |  |  | Page 6 of 7
22:30 | 515 | 5001.5 | 3319.5 | 8321
23:00 | 550 | 4906 | 3233 | 8139
23:30 | 555 | 4799 | 3129 | 7928
24:00 | 560 | 4692 | 3025 | 7717
9839 MW (18:00 )
9214 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-12-07 |  | Energy |  | 208070462
QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 2973 | 911 | 1112 | 0 | 35 | 2503 | 86 | 0 | 16 | 78 | 0 | 3 | 0
0:30 | 3099.5 | 867 | 1261 | 0 | 61.5 | 2442.5 | 86 | 0 | 57 | 80 | 0 | 1.5 | 0 |  | Date: | 43805
1:00 | 3226 | 823 | 1410 | 0 | 88 | 2382 | 86 | 0 | 98 | 82 | 0 | 0 | 0
1:30 | 3190 | 784.5 | 1329.5 | 0 | 68.5 | 2269 | 86 | 0 | 98 | 79 | 0 | 0 | 0 | [8 empty] | Total Energy | 208.0705 | 208.0705 | Total Energy Gen 208.070 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 208.070 MKWHr
2:00 | 3154 | 746 | 1249 | 0 | 49 | 2156 | 86 | 0 | 98 | 76 | 0 | 0 | 0 | [8 empty] | Energy not Served | 0 | 0
2:30 | 3129.5 | 689.5 | 1241.5 | 0 | 54 | 2100.5 | 86 | 0 | 98 | 74 | 0 | 0.5 | 0 | [8 empty] | Energy Requirement | 208.0705 | 208.0705
3:00 | 3105 | 633 | 1234 | 0 | 59 | 2045 | 86 | 0 | 98 | 72 | 0 | 1 | 0
3:30 | 3071.5 | 633 | 1249.5 | 0 | 50.5 | 1952 | 86 | 0 | 98 | 76 | 0 | 0.5 | 0 | [7 empty] | Shortage
4:00 | 3038 | 633 | 1265 | 0 | 42 | 1859 | 86 | 0 | 98 | 80 | 0 | 0 | 0
4:30 | 2982.5 | 633 | 1212 | 0 | 38 | 1836.5 | 86 | 0 | 103 | 77 | 0 | 0 | 0
5:00 | 2927 | 633 | 1159 | 0 | 34 | 1814 | 86 | 0 | 108 | 74 | 0 | 0 | 0
5:30 | 2965 | 633 | 1175.5 | 0 | 17 | 1787.5 | 86 | 0 | 128.5 | 73 | 0 | 0 | 0
6:00 | 3003 | 633 | 1192 | 0 | 0 | 1761 | 86 | 0 | 149 | 72 | 0 | 0 | 0
6:30 | 3099 | 628 | 1261 | 0 | 18 | 1785.5 | 86 | 0 | 149 | 77 | 3 | 0 | 0 | [6 empty] | Coal
7:00 | 3195 | 623 | 1330 | 0 | 36 | 1810 | 86 | 0 | 149 | 82 | 6 | 0 | 0
7:30 | 3268 | 706.5 | 1426 | 0 | 74.5 | 1906 | 86 | 0 | 149 | 82 | 23 | 0 | 0 | [5 empty] | Oil
8:00 | 3341 | 790 | 1522 | 0 | 113 | 2002 | 86 | 0 | 149 | 82 | 40 | 0 | 0
8:30 | 3335.5 | 818.5 | 1513 | 0 | 147 | 2141 | 86 | 0 | 149 | 85 | 50.5 | 0 | 0
9:00 | 3330 | 847 | 1504 | 0 | 181 | 2280 | 86 | 0 | 149 | 88 | 61 | 0 | 0
9:30 | 3295 | 837.5 | 1484.5 | 0 | 223 | 2292.5 | 86 | 0 | 166.5 | 89 | 67.5 | 0 | 0
10:00 | 3260 | 828 | 1465 | 0 | 265 | 2305 | 86 | 0 | 184 | 90 | 74 | 0 | 0
10:30 | 3260.5 | 872.5 | 1433 | 0 | 265.5 | 2378.5 | 86 | 0 | 184 | 94 | 85.5 | 0 | 0
11:00 | 3261 | 917 | 1401 | 0 | 266 | 2452 | 86 | 0 | 184 | 98 | 97 | 0 | 0
11:30 | 3348.5 | 917.5 | 1450.5 | 0 | 318.5 | 2498 | 86 | 0 | 184 | 96 | 89 | 0 | 0
12:00 | 3436 | 918 | 1500 | 0 | 371 | 2544 | 86 | 0 | 184 | 94 | 81 | 0 | 0
12:30 | 3422 | 918 | 1488.5 | 0 | 472 | 2551 | 86 | 0 | 180 | 92 | 76.5 | 0 | 0
13:00 | 3408 | 918 | 1477 | 0 | 573 | 2558 | 86 | 0 | 176 | 90 | 72 | 0 | 0
13:30 | 3408 | 918 | 1477 | 0 | 573 | 2558 | 86 | 0 | 176 | 90 | 72 | 0 | 0
14:00 | 3408 | 918 | 1477 | 0 | 573 | 2558 | 86 | 0 | 176 | 90 | 72 | 0 | 0
14:30 | 3259 | 918 | 1360 | 0 | 521.5 | 2518 | 86 | 0 | 149.5 | 95 | 48.5 | 1.5 | 0
15:00 | 3110 | 918 | 1243 | 0 | 470 | 2478 | 86 | 0 | 123 | 100 | 25 | 3 | 0
15:30 | 3143 | 918 | 1265 | 0 | 312.5 | 2602 | 86 | 0 | 104 | 103 | 18.5 | 3 | 0
16:00 | 3176 | 918 | 1287 | 0 | 155 | 2726 | 86 | 0 | 85 | 106 | 12 | 3 | 0
16:30 | 3112 | 918 | 1222.5 | 0 | 348.5 | 2865.5 | 86 | 0 | 74.5 | 103 | 6.5 | 3.5 | 0
17:00 | 3048 | 918 | 1158 | 0 | 542 | 3005 | 86 | 0 | 64 | 100 | 1 | 4 | 0
17:30 | 3079 | 767.5 | 1271.5 | 0 | 838 | 3156.5 | 86 | 0 | 81 | 100 | 0.5 | 2.5 | 0
18:00 | 3110 | 617 | 1385 | 0 | 1134 | 3308 | 86 | 0 | 98 | 100 | 0 | 1 | 0
18:30 | 3123.5 | 623.5 | 1375 | 0 | 960.5 | 3334 | 86 | 0 | 65 | 101 | 0 | 1.5 | 0
19:00 | 3137 | 630 | 1365 | 0 | 787 | 3360 | 86 | 0 | 32 | 102 | 0 | 2 | 0
19:30 | 3160 | 678 | 1405 | 0 | 461 | 3368 | 86 | 0 | 32 | 102 | 0 | 16 | 0
20:00 | 3144 | 915 | 1377 | 0 | 204 | 3300 | 86 | 0 | 32 | 92 | 0 | 10 | 0
20:30 | 3145 | 913.5 | 1379 | 0 | 180.5 | 3226 | 86 | 0 | 32 | 94 | 0 | 6 | 0
21:00 | 3146 | 912 | 1381 | 0 | 157 | 3152 | 86 | 0 | 32 | 96 | 0 | 2 | 0
21:30 | 3146 | 911.5 | 1357.5 | 0 | 104.5 | 3007.5 | 86 | 0 | 24 | 94 | 0 | 2.5 | 0
22:00 | 3146 | 911 | 1334 | 0 | 52 | 2863 | 86 | 0 | 16 | 92 | 0 | 3 | 0
22:30 | 3126.5 | 911 | 1285.5 | 0 | 52 | 2752 | 86 | 0 | 16 | 90 | 0 | 2 | 0
23:00 | 3107 | 911 | 1237 | 0 | 52 | 2641 | 86 | 0 | 16 | 88 | 0 | 1 | 0
23:30 | 3040 | 911 | 1174.5 | 0 | 43.5 | 2572 | 86 | 0 | 16 | 83 | 0 | 2 | 0 |  | Max Temp. in Dhaka |  | 21°C
24:00 | 2973 | 911 | 1112 | 0 | 35 | 2503 | 86 | 0 | 16 | 78 | 0 | 3 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 208.070 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 208.070 MKWHr
Note on W13: Author:

## Generation
g | 2023-12-07
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 2063280
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [16 empty] | 1 | 8 | [8 empty] | 15132
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 5 | 8 | 8 | 18 | 17 | 13 | 12 | 7 | 1 | [10 empty] | 90180
6 | Sikalbaha 225MW CCPP (Gas) | 192 | 192 | 192 | 193 | 192 | 194 | 195 | 195 | 195 | 193 | 198 | 194 | 193 | 193 | 192 | 192 | 192 | 192 |  | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 4558156
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [26 empty] | 0
12 | Hathazari 100 MW peaking PP | [13 empty] | 8 | 8 | [11 empty] | 12000
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [11 empty] | 14 | 17 | 17 | 17 |  | 6 | 17 |  | 17 | 17 | [5 empty] | 133818
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 265 | 276 | 275 | 277 | 267 | 267 | 263 | 265 | 262 | 275 | 283 | 296 | 294 | 250 | 240 | 240 | 240 | 240 |  | 242 | 242 | 242 | 242 | 232 | 221 | 221 | 6164421
18 | Kodda 300 MW PP Unit-2 (Summit) | [13 empty] | 20 |  |  |  | 40 | [8 empty] | 102873
19 | Ashuganj 195 MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 26 | 8 | [13 empty] | 133818
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4378500
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 445 | 350 | 300 | 300 | 300 | 305 | 330 | 400 | 465 | 478 | 487 | 490 | 490 | 477 | 450 | 450 | 450 | 485 |  | 490 | 490 | 490 | 470 | 400 | 350 | 350 | 10112726
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 45 | 45 | 5 | 5 | 5 | 28 | 42 | 45 | 45 | 42 | 42 | 40 | 44 | 40 | 35 | 44 | 44 | 48 |  | 48 | 48 | 48 | 48 | 48 | 48 | 20 | 925704
33 | Ashuganj 225 MW CCPP
34 | Ashuganj 450 MW CCPP(South) | 250 | 250 | 250 | 250 | 240 | 240 | 360 | 240 | 270 | 270 | 280 | 300 | 300 | 270 | 270 | 280 | 270 | 270 |  | 270 | 280 | 270 | 270 | 270 | 270 | 270 | 6588000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 305 | 320 | 315 | 280 | 280 | 300 | 300 | 300 | 280 | 280 | 300 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 7318900
| Ashuganj 420 MW CCPP(East) | 240 | 240 | 240 | 240 | 230 | 230 | 230 | 355 | 350 | 300 | 300 | 350 | 315 | 250 | 300 | 270 | 230 | 230 |  | 230 | 240 | 240 | 240 | 240 | 240 | 240 | 6533000
35 | Ashuganj 55 MW PP (Precision) | 31 |  |  |  |  | 1 | 10 | 10 | 32 | 36 | 42 | 41 | 41 | 36 | 30 | 46 | 46 | 47 |  | 47 | 47 | 47 | 47 | 47 | 46 |  | 696960
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 356 | 356 | 352 | 323 | 307 | 306 | 303 | 307 | 310 | 319 | 353 | 355 | 356 | 332 | 307 | 307 | 314 | 311 |  | 314 | 312 | 307 | 298 | 316 | 323 | 292 | 7825410
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 390 | 390 | 390 | 400 | 350 | 320 | 320 | 450 | 450 | 450 | 420 | 450 | 450 | 320 | 320 | 340 | 340 | 450 |  | 400 | 400 | 400 | 400 | 350 | 350 | 350 | 8905300
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 95 | 99 | 107 | 109 | 109 | 109 | 94 | 70 | 70 | 70 | 33 | 33 | 33 | 33 | 35 | 35 | 35 | 35 |  | 35 | 35 | 40 | 78 | 78 | 76 | 76 | 1549440
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 0 | 5 | 6 | 10 | 15 | 6 | 4 | 5 | 3 | 1 | 0 | [9 empty] | 56910
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1013000
45 | Fenchugonj CCPP Phase-2 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 27 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 697920
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 63 | 40 | 40 | 40 | 40 | 40 | 40 | 62 | 62 | 63 | 63 | 62 | 62 | 40 | 40 | 40 | 40 | 63 |  | 63 | 63 | 63 | 63 | 63 | 40 | 40 | 1219200
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 164 | 164 | 163 | 164 | 163 | 163 | 163 | 163 | 163 | 163 | 164 | 163 | 165 | 163 | 165 | 165 | 163 | 163 |  | 163 | 164 | 163 | 164 | 163 | 163 | 163 | 4402390
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | [5 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 9 | 9 | 9 | 9 | 9 | 9 |  | 184320
54 | Hobiganj 11 MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 163824
55 | Fenchugonj 51 MW PP (Barakatullah) | 25 | [5 empty] | 26 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 5 | 481200
56 | Shahjahanulla 25 MW PP | 23 | [7 empty] | 8 | 16 | 16 | 16 | 16 | 16 | 24 | 20 | 16 | 23 |  | 24 | 24 | 24 | 24 | 24 | 24 |  | 308184
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 260 | 270 | 275 | 275 | 295 | 310 | 310 | 300 | 285 | 290 | 295 | 300 | 270 | 290 | 300 | 290 | 260 |  | 265 | 305 | 270 | 275 | 265 | 270 | 270 | 6948000
| Bibiyana South 400 MW | 380 | 400 | 400 | 370 | 360 | 360 | 360 | 400 | 400 | 400 | 400 | 400 | 400 | 340 | 345 | 370 | 370 | 360 |  | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 9022500
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 5 | 17 |  | 17 | 17 | [5 empty] | 50269
59 | Tangail Palli Power Gen 22 MW | [26 empty] | 0
60 | Barabkunda 22 MW PP (Regent) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 12 | 12 | 12 | 12 | 10 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 245904
61 | Narshingdi 22 MW PP (Doreen) | [9 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 |  | 143820
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 82 | 76 | 72 | 80 | 74 | 72 | 82 | 82 | 88 | 90 | 98 | 94 | 90 | 90 | 100 | 106 | 100 | 100 |  | 102 | 102 | 92 | 96 | 92 | 88 | 78 | 2118720
64 | Malancha, Ctg. EPZ (United) | 17 | 22 | 27 | 27 | 41 | 41 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 2 |  | 2 | 2 | 9 | 8 | 15 | 18 | 18 | 303360
65 | Feni 22 MW PP (Doreen) | 18 | [5 empty] | 3 | 15 | 15 | 15 | 15 | 15 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 308232
66 | Feni 11 MW PP (Doreen) | 11 | [6 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 181620
67 | Jangalia 33 MW PP (Summit) | 33 | 25 |  |  |  |  | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 624800
68 | Cumilla 25 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 2 | 8 | 8 | 8 | 8 |  | 8 | 8 | 10 | 10 | 10 | 10 | 10 | 196240
69 | Summit Ashulia | 20 | 9 | 9 | 0 | 0 | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 48000
70 | Summit Madhabdi | 14 | 0 | 14 | 14 | 7 | 7 | 7 | 7 | 7 | 0 | 7 | 14 | 14 | 14 | 14 | 14 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 7 | 7 | 254520
71 | Maona 33 MW PP(Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 20 | 16 | 16 | 496440
72 | Rupganj 33 MW PP(Summit) | 24 | 24 | 24 | 16 | 24 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 24 | 24 | 21 | 22 |  | 22 | 22 | 22 | 24 | 24 | 26 | 26 | 565600
73 | Ghorashal 108 MW PP (Regent) | 73 | 40 |  |  |  | 14 | 60 | 66 | 67 | 67 | 67 | 67 | 69 | 70 | 70 | 70 | 13 | 73 |  | 74 | 74 | 74 | 74 | 74 | 22 | 22 | 1232590
| Feni Lanka Power | [6 empty] | 24 | 44 | 44 | 44 | 17 | 17 | 17 | 17 |  |  | 17 | 17 | [8 empty] | 248520
| Chowmuhani 113 MW | [7 empty] | 7 | 9 | 9 | 28 | 28 | 28 | 29 | 29 |  | 14 | 47 |  | 47 | 11 | [5 empty] | 323400
| Manikgonj 162MW PP(MPGL) | [12 empty] | 17 | 17 | 17 |  | 35 | 54 |  | 35 | 17 | [5 empty] | 181440
77 | Siddhirganj 100 PP(Dutch Bangla) | [12 empty] | 2 | 39 |  |  | 4 | 25 | [8 empty] | 84480
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | [5 empty] | 8 | 8 | 8 | 8 |  |  | 8 | 17 | 17 |  | 17 | 17 | 17 | 17 |  |  |  | 169440
79 | Kodda 150 MW PP | 98 | 98 | 98 | 98 | 108 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 98 | 64 | 64 | 98 |  | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 2447040
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [7 empty] | 27 | 52 | 52 | 43 | 8 | 8 |  |  |  | 1 | 16 | [8 empty] | 225778
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 |  |  |  | 17 | 17 |  | 1 | 17 |  | 25 | 17 | 40 | 70 |  | 35 | 17 | 2 |  |  |  |  | 347203
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 0 | 2 | 3 | 4 | 2 | 1 | 0 | 1 | 0 | [10 empty] | 13082
| Jodiac Power | [13 empty] | 2 | 17 |  | 6 | 17 |  | 17 | 17 | [5 empty] | 81399
| Karnaphuli Power Ltd. | [9 empty] | 3 | 17 | 17 | 36 | 51 | 51 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 |  |  |  | 335380
82 | Madanganj 102 PP(Summit) | [12 empty] | 10 | 49 | 36 |  | 2 | 17 |  | 6 | [6 empty] | 93731
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | [13 empty] | 3 | 9 |  | 2 | 18 | [8 empty] | 41280
| Meghnaghat 104 MW PP (OPCL) | [12 empty] | 1 | 14 | 17 |  | 8 | 36 |  | 47 | [6 empty] | 136320
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [11 empty] | 12 | 12 | 12 | [12 empty] | 37320
92 | Fenchuganj 44 MW (Energyprima) | 25 | 0 |  |  |  |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 5 | 502704
93 | Ashuganj 51 MW PP (Midland) | 43 | [5 empty] | 14 | 14 | 14 | 14 | 28 | 51 | 51 | 51 | 51 | 51 | 10 | 28 |  | 51 | 51 | 51 | 51 | 51 | 5 | 5 | 774516
94 | Gagnagar 102 MW PP (Digital Power) | [26 empty] | 0
95 | Patenga 50MW PP (Baraka) | 2 | [9 empty] | 2 | 6 | 6 | 6 | 6 | 6 | 18 | 20 |  | 20 | 20 | 20 | 20 |  |  |  | 141120
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 | [9 empty] | 0
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [13 empty] | 40 | 15 |  | 4 | 40 | [8 empty] | 156934
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 17 | 35 |  | 35 | 17 | [5 empty] | 81643
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 |  | 0 | 0 |  |  |  | 0 | 0 | [10 empty] | 1200
103 | Kamalaghat 54 MW PP(Banco Energy) | [12 empty] | 17 | 17 |  |  | 17 | 17 |  | 17 | 17 | [5 empty] | 87840
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [8 empty] | 12 | 56 | 56 | 58 | 58 | 58 | 58 | 45 | 66 | 76 |  | 78 | 78 | 45 |  |  |  |  | 710400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | 17 | 17 | 17 |  |  |  | 1 | 15 | 17 | 17 | 28 |  |  | 8 | 27 | 70 |  | 59 | 35 | 35 | 35 | 35 | 35 | 35 | 547056
115 | Juldah 100 MW PP Unit-3 (Acorn) | [26 empty] | 0
116 | Chandpur 200 MW (Desh energy) | 17 | [5 empty] | 7 | 17 | 17 | 17 | 17 | 17 | 17 | 22 | 29 | 20 | 17 | 17 |  | 19 | 17 | 17 | 17 | 17 | 17 |  | 336000
117 | Ashuganj 150 MW PP (Midland) | [11 empty] | 1 | 3 | 13 | 13 |  | 2 | 26 |  | 30 | 6 | [5 empty] | 127127
118 | Bibiyana-III 400 MW CCPP | 319 | 320 | 320 | 321 | 319 | 342 | 350 | 426 | 367 | 368 | 320 | 367 | 367 | 320 | 364 | 401 | 319 | 320 |  | 330 | 334 | 330 | 317 | 330 | 320 | 330 | 8106000
| Jamalpur 115 MW PP (United) | [8 empty] | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 6 | 28 |  | 8 | [6 empty] | 122400
| Anwara 300 MW PP (United) | [11 empty] | 64 | 49 | 48 | 48 |  | 48 | 100 |  | 65 | 30 | [5 empty] | 451636
| Juldah unit-2 (Acorn) | [26 empty] | 0
| Anlima Energy Ltd. | 10 | [9 empty] | 15 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 |  |  |  | 220800
| Bhairob 54.5 MW | [8 empty] | 2 | 17 | 17 | 17 | 17 | [13 empty] | 98640
| Spectra Solar Plant Ltd. | [6 empty] | 0 | 2 | 2 | 5 | 4 | 7 | 5 | 3 | 1 | 1 | [10 empty] | 28830
| Chandpur 115(Doreen) | [6 empty] | 5 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 11 | 53 |  | 17 | 17 | 17 | 17 |  |  |  | 336960
| Kanchan Purbachal Power Generation Ltd. | 17 | 7 | 17 | [7 empty] | 2 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 |  |  |  | 245520
| Mirsharai 150 MW (Oil) | [9 empty] | 35 | 35 | 35 | 27 | 27 | 17 | 17 | [10 empty] | 198091
| Mirsharai 150 MW (Gas) | [16 empty] | 17 | 17 |  | 17 | 17 | 17 |  |  |  |  | 47800
| Cox's Bazar Wind | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 3 | 4 | 1 |  | 2 | 16 | 10 | 2 | 3 | 1 | 3 | 40800
| Matarbari 2*600 MW (CPGCL) | [14 empty] | 140 | 315 | 550 | 563 |  | 564 | 565 | 566 | 565 | 564 | 564 | 564 | 8858181
120 | Eastern Zone Total | 4781 | 4392 | 4275 | 4211 | 4112 | 4203 | 4604 | 5010 | 5107 | 5218 | 5247 | 5522 | 5545 | 5148 | 5202 | 5151 | 5416 | 6182 |  | 5807 | 5649 | 5396 | 5330 | 5097 | 4906 | 4692 | 126363192
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [12 empty] | 23 | 32 | [12 empty] | 62400
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [13 empty] | 7 | [12 empty] | 46560
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 3 | 10 | 11 | 13 | 26 | 25 | 13 | 6 | 4 | 1 | 1 | [9 empty] | 117360
131 | Rampal 1320 MW (BIFPCL) | 377 | 378 | 378 | 379 | 379 | 378 | 379 | 377 | 379 | 376 | 376 | 375 | 372 | 372 | 435 | 582 | 631 | 633 |  | 633 | 628 | 631 | 643 | 521 | 408 | 363 | 10756360
132 | United Payra Power Ltd. | [11 empty] | 2 | 17 | 17 | [12 empty] | 50400
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 223 | 222 | 180 | 220 | 220 | 220 | 180 | 180 | 180 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 5158064
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [26 empty] | 0
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3447300
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 130 | 130 | 130 | 132 | 80 | 80 | 80 | 80 | 130 | 80 | 80 | 125 | 125 | 80 | 80 | 80 | 80 | 130 |  | 130 | 130 | 130 | 130 | 115 | 120 | 80 | 2523000
140 | Bhola 33 MW PP (Venture) | 17 | 16 | 16 | 15 | 15 | 13 | 14 | 14 | 14 | 13 | 13 | 15 | 18 | 17 | 14 | 15 | 15 | 18 |  | 19 | 19 | 20 | 20 | 19 | 19 | 18 | 385000
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 823 | 746 | 633 | 633 | 633 | 633 | 623 | 790 | 847 | 828 | 917 | 918 | 918 | 917 | 918 | 918 | 918 | 617 |  | 630 | 678 | 915 | 912 | 911 | 911 | 911 | 19479272
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 580 | 500 | 450 | 350 | 300 | 300 | 320 | 400 | 500 | 520 | 540 | 610 | 622 | 520 | 480 | 400 | 370 | 600 |  | 610 | 622 | 550 | 400 | 350 | 340 | 340 | 12109700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4134400
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 5160
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 276 | 293 | 303 | 320 | 250 | 280 | 280 | 370 | 336 | 310 | 293 | 275 | 260 | 242 | 228 | 225 | 200 | 227 |  | 228 | 228 | 227 | 227 | 234 | 228 | 239 | 6400690
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  |  | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 184968
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP | [15 empty] | 4 | [10 empty] | 4065
168 | Santahar 50 MW Peaking PP | [26 empty] | 0
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | [13 empty] | 25 | [12 empty] | 34400
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [11 empty] | 3 | 35 | 35 |  |  | 10 | 45 |  | 50 | 50 | [5 empty] | 261312
172 | Confidence Power Bogura Unit-1 113 MW | [11 empty] | 20 | 35 | 35 |  |  | 45 | 55 |  | 55 | [6 empty] | 249888
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [12 empty] | 30 | 34 | 22 |  | 28 | 50 |  | 45 | 10 | [5 empty] | 205852
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 3 | 2 | 2 | 1 | 2 | 1 | 1 | [10 empty] | 13819
178 | Energypac Power Venture Thakurgaon Ltd. | [12 empty] | 4 | 55 |  |  | 17 | 35 | [8 empty] | 168000
| Intraco Solar 30 MW | [6 empty] | 0 | 2 | 7 | 7 | 6 | 3 | 7 | 1 | 2 | 2 | 0 | [9 empty] | 38034
| Adani Power Jharkhanda Ltd | 670 | 618 | 607 | 520 | 525 | 468 | 471 | 515 | 626 | 621 | 739 | 759 | 764 | 720 | 663 | 669 | 694 | 717 |  | 753 | 753 | 753 | 764 | 718 | 669 | 576 | 15703636
178 | Teesta Solar Limited | [6 empty] | 2 | 15 | 23 | 24 | 22 | 19 | 28 | 15 | 6 | 5 | 0 | [9 empty] | 167630