## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-12-18 | Monday
|  | Date (day): | 2023-12-18 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10489.6 | MW |  |  | (b) At Evening Peak Hour : |  | 11734 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-12-17 | 2023-12-18 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 72 | 72 | 71 | 71 | 37 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 386 | 402 | 412 | 412 | 0 |  | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 420 | 450 | 450 | 0
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 90 | 100 |  | 0
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 17 | 85 | 85 |  | 17 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 55 | 15 | 55 |  |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 48 | 48 | 27 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 15 | 15 | 15 | 15 |  | 7 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 97 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 90 | 90 |  | 10 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 90 | 90 |  | 12 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 10 | 35 | 17 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 8 | 48 | 48 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 0 | 0 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 5 | 17 | 0 | 35 | 20 |  | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 44 | 31 | 34 | 34 |  | 46 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 17 | 25 |  |  | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 27 | 27 | 26 | 26 |  |  | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 16 | 8 | 17 | 35 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 12 | 45 | 82 | 130 | 170 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 12 | 44 | 36 | 50 | 99 |  | Fuel shortage
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 50 | 17 | 105
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 51 | 72 | 72
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 54 | 17 | 54 | 108 |  | Fuel shortage
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 29 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 5763 | 5422 | 1287 | 1718 | 1972 | 2380 | 1609 | 1032
38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 80 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
39 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 17 | 8 | 17 | 8 |  | Fuel shortage
40 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 19 | 6 | 20 | 30 |  | Fuel shortage
42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 92 | 92 | 92 | 138 |  | Low water lavel
43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 228 | 218 | 225 | 225
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 17 | 17 | 88 |  | Fuel shortage
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 70 | 70 | 28 |  | Fuel shortage
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 0 | 34 | 68 |  | Fuel shortage
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 5 | 0 | 12 | 12 | 88 |  | Fuel shortage
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 13 | 13 | 12 | 12 | 10 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 13 | 24 | 10 | 25
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 100 | 65 | 100 | 200 |  | Fuel shortage
54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 17 | 17 | 17 | 37 |  | Fuel shortage
55 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 4 | 17 | 17 | 17 | 93 |  | Fuel shortage
56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
57 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 17 | 99 |  | Fuel shortage
58 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 0 | 0 | 0 | 163
59 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 350 | 400 | 400 | 620
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 0 | 5 | 10 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 36 | 36 | 36 | 36 |  |  | On test.
| Chattogram area Total |  |  |  |  | 3829 | 3769 | 878 | 1116 | 1163 | 1465 | 1414 | 330
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 0 | 0 |  | 221 | Under maint.
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 295 | 360 | 360 | 0 |  | FGMO
63 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 375 | 393 | 393 | 393 | 7
64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 49 | 48 | 48 | 48 |  |  | Gas shortage
65 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 0 | 25 | 25 | 30 | 25 |  |  | Gas shortage
66 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 73 | 73 | 73 | 73 | 122 |  | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
68 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 6 | 142 | 12 | 150
69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 30
70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
71 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 17 | 17 | 17 | 183 |  | Fuel shortage
72 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 94 | 92 | 128 | 140
74 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 52
76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 5 | 11 | 10 | 10 |  | 15 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 100 | 100 | 14 |  | Fuel shortage
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 2 | 47 | 9 | 47 | 66 |  | Engine problem
79 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 17 | 17 | 17 |  | 37 | Engine problem
80 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 18 | 34 | 18 | 18 | 97 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2896 | 1088 | 1306 | 1327 | 1592 | 489 | 800
81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 190 | 112 | 70 | 100 | 102 |  | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 56 | 75 | 56 | 75 | 125 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 28 | 9 | 28 | 87 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 43 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 4 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 300 | 219 | 192.6 | 209 | 102 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 120 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 51 | 53 | 52 | 52
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 46 | 39 | 46 | 46
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 5 | 5 | 5 |  | 6 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 63 | 63 | 63
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 30 | 30 | 80 | 80
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 130 | 128 | 130 | 130 |  | 101
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 16 | 16 | 16 | 9 |  | Gas shortage
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  |  | Under maint.
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 394 | 332 | 400 | 400 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1301 | 1282 | 1408 | 1408 | 9 | 654
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 863 | 816 | 881 | 930
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 32 | 32 | 83 |  | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 45
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 |  | 109 | under maint.
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 16 | 24 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 75 | 95 |  | 10 | Engine problem
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 68 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 510 | 628 | 510 | 510
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 1441 | 1444 | 1598 | 1628 | 1204 | 119
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 15 | 18 | 20 | 20 |  | 20 | Engine problem
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 120 | 120 | 120 | 120 |  | 74 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 550 | 622 | 622 | 622 |  | 622 | #01 under maint.
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 222 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 75 | 17 | 75
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 140 | 140 | 140 | 140 | 167 |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1045 | 1197 | 1249 | 1307 | 167 | 716
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 30 | 22 |  | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 20 |  | 51 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 28 | 28
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 34 | 42 |  | 8 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 45 |  | 5 | Engine problem
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 341 | 414 | 414 | 0
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 0 | 38 | 12 |  | Fuel shortage
136 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 11 | 11
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 17 | 8 | 8
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 50 | 82 |  | 22 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 35 | 35 | 78 |  | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 55 | 0 | 55 | 58 |  | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 416 | 581 | 550 | 550
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 848 | 1072 | 1166 | 1358 | 1191 | 86
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 89 | 6 | 107 | 6 |  | Fuel shortage
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 35 | 70 | 110
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 174 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 379 | 294 | 414 | 387 | 131 | 189
| Total |  |  |  |  | 25951 | 25211 | 8567 | 9648 | 10489.6 | 11734 | 6316 | 3926
A. |  | 2023-12-17 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 9648 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5635 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9648 | MW
3 | Day peak Generation : |  |  | 8567 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9162.56 | MW
4 | Evening peak Generation : |  |  | 9648 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 189.3112 | MKWHr | By Solar | 2.2907 | MKWHr
| By Gas : | 103.322 | MKWHr |  | By Oil: | 10.1598 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 51.0515 | MKWHr |  | By Hydro: | 1.607 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.10704 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6316 | MW | Dhaka | 3428.86 | 3428.86 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3926 | MW | Chittagong | 862.7 | 862.7 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 10242 | MW | Khulna | 1080.5 | 1080.5 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 812.65 | MMCFD |  |  | Rajshahi | 930 | 930 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 107149335.154 | ii) Oil : | Taka | 133406951.11 | Comilla | 837 | 837 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 378998989.2 | Total | Taka | 619555275.464 | Mymensingh | 753 | 753 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.0165 | MKWHr. | Sylhet | 353 | 353 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 180 | MW (W to E) at | 19:00 | hrs | Barisal | 275.5 | 275.5 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 128 | MW at | 7:00 | hrs | Rangpur | 642 | 642 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 26.7°C |  |  | Total | 9162.56 | 9162.56 |  | 0
B. |  | 2023-12-18 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 22.6°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 11734 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8700 | MW
4 | Reserve(Generation end) |  |  |  | 1934 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 192.2937 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6274 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 18.8349 | MKWHr. | ii) HVDC Flow at Peak Time |  | 816 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9382 | MKWHr. | iii) Maximum HVDC Flow : |  | 911 | MW at | 19:30 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 95.92 |  | (b) Today: | 95.81 |  | (c) Rule Curve: |  | 104.4
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-12-17 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 342 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 11 | 22 | 17 | 27 | 0 | 0 | 92 | 0 | 80 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 42 | 0 | 0 | 0 | 0 | 280 | 0 | 16 | 0 | 48 | 6 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 70 | 218 | 0 | 0 | 0 | 42 | 0 | 5 | 0 | 130 | 0 | 40 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 337 | 6 | 0 | 0 | 0 |  | 592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 140 | 428 | 0 | 0 |  | 3736 | 2716 | 6452 | 2812 | 592 | 1081 | 0 | 0 | 1799 | 92 | 0 | 0 | 70 | 0 | 6 | 0 | 95.97
2:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 334 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 11 | 22 | 17 | 27 | 0 | 0 | 92 | 0 | 80 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 42 | 0 | 0 | 0 | 0 | 280 | 0 | 8 | 0 | 25 | 6 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 68 | 218 | 0 | 0 | 0 | 42 | 0 | 5 | 0 | 130 | 0 | 40 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 320 | 7 | 0 | 0 | 0 |  | 584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 140 | 426 | 0 | 0 |  | 3617 | 2552 | 6169 | 2719 | 584 | 1012 | 0 | 0 | 1687 | 92 | 0 | 0 | 68 | 0 | 7 | 0 | 95.96
3:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 304 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 11 | 22 | 17 | 27 | 0 | 0 | 92 | 0 | 80 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 42 | 0 | 0 | 0 | 0 | 280 | 0 | 8 | 0 | 25 | 6 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 148 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 315 | 7 | 0 | 0 | 0 |  | 584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 140 | 427 | 0 | 0 |  | 3431 | 2490 | 5921 | 2557 | 584 | 955 | 0 | 0 | 1662 | 92 | 0 | 0 | 64 | 0 | 7 | 0 | 95.95
4:00 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 304 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11 | 22 | 17 | 27 | 0 | 0 | 46 | 0 | 80 | 0 | 0 | 194 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 42 | 0 | 0 | 0 | 0 | 250 | 0 | 8 | 0 | 25 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 147 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 300 | 10 | 0 | 0 | 0 |  | 584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 140 | 428 | 0 | 0 |  | 3239 | 2454 | 5693 | 2433 | 584 | 909 | 0 | 0 | 1651 | 46 | 0 | 0 | 60 | 0 | 10 | 0 | 95.94
5:00 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 304 | 0 |  | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11 | 22 | 17 | 27 | 0 | 0 | 46 | 0 | 80 | 0 | 0 | 194 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 42 | 0 | 0 | 0 | 0 | 250 | 0 | 8 | 0 | 25 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 147 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 305 | 9 | 0 | 0 | 0 |  | 584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 140 | 426 | 0 | 0 |  | 3203 | 2432 | 5635 | 2433 | 584 | 849 | 0 | 0 | 1654 | 46 | 0 | 0 | 60 | 0 | 9 | 0 | 95.93
6:00 | 0 | 0 | 0 | 160 | 0 | 20 | 0 | 332 | 0 |  | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12 | 22 | 17 | 27 | 0 | 0 | 46 | 0 | 80 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 42 | 0 | 0 | 0 | 0 | 280 | 0 | 8 | 0 | 48 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 7 | 5 | 62 | 219 | 0 | 0 | 0 | 43 | 0 | 10 | 10 | 120 | 0 | 64 | 0 | 0 | 130 | 0 | 0 | 10 | 0 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 305 | 14 | 0 | 0 | 0 |  | 583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 140 | 427 | 0 | 0 |  | 3618 | 2493 | 6111 | 2725 | 583 | 1027 | 0 | 0 | 1654 | 46 | 0 | 0 | 62 | 0 | 14 | 0 | 95.92
7:00 | 0 | 0 | 0 | 180 | 0 | 32 | 0 | 352 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12 | 22 | 17 | 27 | 0 | 0 | 46 | 0 | 80 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 34 | 0 | 0 | 0 | 0 | 375 | 0 | 16 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 0 | 15 | 10 | 33 | 5 | 62 | 218 | 0 | 0 | 0 | 43 | 0 | 44 | 23 | 120 | 0 | 63 | 0 | 0 | 130 | 0 | 0 | 10 | 0 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 300 | 0 | 0 | 320 | 10 | 0 | 0 | 0 |  | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 222 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 407 | 0 | 140 | 427 | 3 | 0 |  | 3991 | 2647 | 6638 | 3024 | 490 | 1233 | 0 | 0 | 1764 | 46 | 0 | 0 | 62 | 9 | 10 | 0 | 95.91
8:00 | 0 | 0 | 0 | 180 | 0 | 53 | 0 | 374 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12 | 22 | 17 | 27 | 0 | 0 | 46 | 0 | 80 | 0 | 0 | 225 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19 | 0 | 0 | 0 | 0 | 340 | 0 | 45 | 0 | 49 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 5 | 74 | 218 | 0 | 0 | 1 | 43 | 0 | 49 | 46 | 140 | 0 | 63 | 20 | 0 | 130 | 0 | 0 | 10 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 8 | 0 | 0 | 0 | 346 | 8 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 5 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 350 | 0 | 0 | 352 | 6 | 0 | 0 | 0 |  | 706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 470 | 222 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 460 | 5 | 140 | 426 | 41 | 0 |  | 4343 | 3213 | 7556 | 3111 | 706 | 1484 | 0 | 24 | 2018 | 46 | 0 | 0 | 74 | 87 | 6 | 0 | 95.9
9:00 | 0 | 0 | 0 | 180 | 0 | 56 | 0 | 404 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12 | 22 | 17 | 27 | 0 | 0 | 46 | 0 | 80 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 2 | 10 | 12 | 0 | 0 | 0 | 0 | 310 | 0 | 45 | 0 | 49 | 10 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 5 | 82 | 217 | 0 | 0 | 1 | 43 | 0 | 51 | 46 | 140 | 0 | 62 | 20 | 0 | 130 | 0 | 0 | 10 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 15 | 0 | 6 | 0 | 330 | 38 | 17 | 0 | 3 | 0 | 0 | 7 | 0 | 0 | 12 | 400 | 0 | 11 | 0 | 9 | 0 | 0 | 16 | 0 | 0 | 320 | 0 | 10 | 350 | 1 | 0 | 0 | 0 |  | 864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 520 | 180 | 0 | 0 | 2 | 38 | 0 | 0 | 0 | 510 | 15 | 140 | 426 | 96 | 0 |  | 4430 | 3447 | 7877 | 3074 | 864 | 1380 | 0 | 115 | 2116 | 46 | 0 | 0 | 82 | 199 | 1 | 0 | 95.89
10:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 400 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 22 | 25 | 27 | 3 | 0 | 46 | 0 | 80 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 13 | 12 | 0 | 0 | 0 | 0 | 275 | 0 | 45 | 0 | 49 | 25 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 5 | 84 | 217 | 0 | 0 | 2 | 43 | 0 | 51 | 46 | 140 | 0 | 62 | 30 | 0 | 130 | 0 | 0 | 9 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 18 | 0 | 17 | 0 | 322 | 47 | 17 | 0 | 4 | 0 | 0 | 17 | 0 | 0 | 12 | 400 | 0 | 27 | 0 | 17 | 0 | 0 | 23 | 0 | 0 | 305 | 0 | 36 | 350 | 0 | 0 | 0 | 0 |  | 864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 550 | 180 | 0 | 0 | 3 | 55 | 0 | 0 | 0 | 506 | 22 | 140 | 423 | 142 | 0 |  | 4507 | 3462 | 7969 | 2999 | 864 | 1377 | 0 | 160 | 2139 | 46 | 0 | 0 | 84 | 300 | 0 | 0 | 95.88
11:00 | 0 | 0 | 0 | 180 | 0 | 68 | 0 | 384 | 0 |  | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 12 | 15 | 25 | 27 | 8 | 0 | 46 | 0 | 80 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 13 | 11 | 0 | 0 | 0 | 0 | 275 | 0 | 45 | 0 | 49 | 25 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 5 | 94 | 212 | 0 | 0 | 2 | 43 | 0 | 51 | 46 | 120 | 0 | 62 | 30 | 0 | 130 | 0 | 0 | 9 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 20 | 2 | 17 | 5 | 400 | 37 | 17 | 0 | 4 | 0 | 0 | 15 | 0 | 0 | 12 | 400 | 0 | 41 | 0 | 17 | 0 | 0 | 27 | 13 | 0 | 340 | 0 | 36 | 349 | 0 | 0 | 0 | 0 |  | 865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 550 | 180 | 0 | 0 | 4 | 65 | 0 | 0 | 0 | 457 | 27 | 140 | 415 | 166 | 0 |  | 4603 | 3497 | 8100 | 3100 | 865 | 1374 | 0 | 179 | 2081 | 46 | 0 | 0 | 94 | 361 | 0 | 0 | 95.88
12:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 386 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 10 | 17 | 5 | 15 | 22 | 22 | 25 | 27 | 8 | 0 | 46 | 0 | 80 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 0 | 5 | 0 | 6 | 13 | 13 | 0 | 0 | 0 | 0 | 345 | 0 | 73 | 0 | 49 | 25 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 0 | 5 | 94 | 190 | 0 | 0 | 2 | 43 | 0 | 51 | 46 | 120 | 0 | 61 | 30 | 0 | 130 | 0 | 0 | 10 | 0 | 8 | 8 | 0 | 12 | 0 | 0 | 56 | 0 | 12 | 20 | 12 | 17 | 6 | 394 | 9 | 17 | 17 | 4 | 15 | 0 | 4 | 0 | 2 | 12 | 400 | 0 | 43 | 0 | 17 | 0 | 0 | 29 | 18 | 0 | 375 | 0 | 36 | 350 | 0 | 0 | 0 | 0 |  | 863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 550 | 220 | 0 | 0 | 5 | 68 | 0 | 0 | 0 | 510 | 30 | 140 | 416 | 174 | 0 |  | 4854 | 3713 | 8567 | 3195 | 863 | 1560 | 0 | 285 | 2136 | 46 | 0 | 8 | 94 | 380 | 0 | 0 | 95.87
13:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 400 | 0 |  | 0 | 420 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 15 | 22 | 22 | 25 | 27 | 8 | 0 | 46 | 0 | 80 | 0 | 7 | 228 | 0 | 0 | 0 |  | 3 | 0 | 0 | 12 | 0 | 6 | 13 | 17 | 0 | 0 | 0 | 0 | 320 | 0 | 73 | 0 | 49 | 25 | 0 | 51 | 0 | 0 | 4 | 18 | 10 | 0 | 5 | 94 | 147 | 0 | 0 | 2 | 43 | 0 | 53 | 46 | 163 | 0 | 61 | 30 | 0 | 128 | 0 | 0 | 10 | 0 | 8 | 8 | 0 | 43 | 0 | 0 | 56 | 0 | 17 | 19 | 12 | 17 | 20 | 348 | 9 | 17 | 17 | 4 | 16 | 0 | 17 | 34 | 9 | 12 | 400 | 1 | 41 | 17 | 17 | 0 | 13 | 28 | 18 | 0 | 380 | 0 | 0 | 349 | 0 | 0 | 0 | 0 |  | 863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 36 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 1 | 0 | 25 | 0 | 0 | 0 | 5 | 0 | 590 | 220 | 0 | 0 | 5 | 57 | 0 | 0 | 0 | 575 | 26 | 140 | 422 | 160 | 0 |  | 4979 | 3791 | 8770 | 3022 | 863 | 1574 | 0 | 510 | 2246 | 46 | 0 | 68 | 94 | 347 | 0 | 0 | 95.87
14:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 393 | 0 |  | 0 | 370 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 15 | 22 | 22 | 25 | 27 | 8 | 0 | 46 | 0 | 80 | 0 | 8 | 229 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 6 | 13 | 13 | 0 | 0 | 0 | 0 | 275 | 0 | 73 | 0 | 49 | 25 | 0 | 51 | 0 | 0 | 25 | 18 | 10 | 0 | 5 | 96 | 148 | 0 | 0 | 2 | 43 | 0 | 53 | 46 | 120 | 0 | 40 | 30 | 0 | 128 | 0 | 0 | 10 | 0 | 8 | 8 | 0 | 45 | 0 | 0 | 57 | 0 | 17 | 16 | 12 | 17 | 50 | 330 | 9 | 17 | 17 | 3 | 32 | 17 | 17 | 24 | 9 | 12 | 360 | 12 | 32 | 17 | 17 | 0 | 17 | 27 | 18 | 0 | 320 | 0 | 36 | 349 | 0 | 0 | 0 | 0 |  | 863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 13 | 0 | 35 | 0 | 0 | 0 | 4 | 35 | 560 | 180 | 0 | 0 | 3 | 52 | 0 | 0 | 0 | 554 | 21 | 140 | 421 | 140 | 0 |  | 4853 | 3646 | 8499 | 2869 | 863 | 1356 | 0 | 693 | 2194 | 46 | 0 | 82 | 96 | 300 | 0 | 0 | 95.88
15:00 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 375 | 0 |  | 0 | 370 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 15 | 22 | 22 | 21 | 27 | 0 | 0 | 86 | 0 | 80 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 6 | 13 | 12 | 0 | 0 | 0 | 0 | 325 | 0 | 73 | 0 | 45 | 25 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 21 | 11 | 82 | 111 | 0 | 0 | 1 | 43 | 0 | 53 | 46 | 120 | 0 | 40 | 30 | 0 | 128 | 0 | 0 | 10 | 0 | 8 | 8 | 0 | 15 | 0 | 0 | 24 | 0 | 17 | 12 | 0 | 17 | 50 | 365 | 0 | 0 | 17 | 2 | 30 | 0 | 17 | 0 | 0 | 12 | 350 | 0 | 22 | 35 | 17 | 0 | 17 | 16 | 18 | 0 | 320 | 0 | 36 | 349 | 0 | 0 | 0 | 0 |  | 863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 17 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 500 | 180 | 0 | 0 | 2 | 35 | 0 | 0 | 0 | 463 | 15 | 140 | 428 | 93 | 0 |  | 4597 | 3406 | 8003 | 2900 | 863 | 1406 | 0 | 365 | 2050 | 86 | 0 | 50 | 82 | 201 | 0 | 0 | 95.86
16:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 381 | 0 |  | 0 | 400 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 15 | 22 | 14 | 21 | 27 | 0 | 0 | 86 | 0 | 80 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 6 | 13 | 12 | 0 | 0 | 0 | 0 | 320 | 0 | 73 | 0 | 41 | 25 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 11 | 82 | 112 | 0 | 0 | 0 | 43 | 0 | 53 | 46 | 163 | 0 | 40 | 30 | 0 | 128 | 0 | 0 | 10 | 0 | 16 | 8 | 0 | 15 | 0 | 0 | 24 | 0 | 17 | 7 | 0 | 17 | 6 | 371 | 0 | 0 | 17 | 1 | 15 | 0 | 17 | 0 | 0 | 12 | 370 | 0 | 9 | 35 | 17 | 0 | 17 | 7 | 18 | 0 | 320 | 0 | 13 | 350 | 2 | 0 | 0 | 0 |  | 863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 15 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 490 | 180 | 0 | 2 | 0 | 16 | 0 | 0 | 0 | 453 | 6 | 140 | 434 | 38 | 0 |  | 4599 | 3309 | 7908 | 2913 | 863 | 1486 | 0 | 306 | 2037 | 86 | 0 | 48 | 82 | 85 | 2 | 0 | 95.86
17:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 395 | 0 |  | 0 | 320 | 0 | 3 | 8 | 15 | 0 | 0 | 0 | 8 | 16 | 55 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 15 | 21 | 14 | 25 | 18 | 16 | 0 | 86 | 0 | 80 | 0 | 2 | 218 | 0 | 0 | 0 |  | 6 | 37 | 0 | 12 | 0 | 10 | 13 | 15 | 0 | 0 | 0 | 0 | 280 | 0 | 73 | 0 | 41 | 25 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 11 | 90 | 111 | 0 | 0 | 0 | 43 | 0 | 53 | 46 | 120 | 0 | 40 | 30 | 0 | 128 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 15 | 0 | 0 | 54 | 0 | 17 | 0 | 12 | 19 | 23 | 332 | 19 | 40 | 17 | 0 | 96 | 3 | 17 | 17 | 16 | 12 | 340 | 15 | 1 | 35 | 17 | 0 | 17 | 0 | 18 | 15 | 280 | 0 | 0 | 349 | 2 | 0 | 0 | 0 |  | 862 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 8 | 80 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 48 | 17 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 17 | 0 | 12 | 0 | 40 | 0 | 0 | 35 | 490 | 180 | 0 | 35 | 0 | 2 | 35 | 0 | 0 | 456 | 0 | 140 | 525 | 3 | 0 |  | 4756 | 3482 | 8238 | 2747 | 862 | 1279 | 0 | 896 | 2130 | 86 | 0 | 140 | 90 | 6 | 2 | 0 | 95.85
18:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 313 | 0 |  | 0 | 350 | 0 | 24 | 24 | 46 | 0 | 0 | 0 | 40 | 24 | 98 | 16 | 0 | 0 | 0 | 35 | 0 | 17 | 15 | 20 | 14 | 25 | 27 | 16 | 0 | 86 | 0 | 90 | 0 | 15 | 218 | 0 | 0 | 0 |  | 4 | 41 | 0 | 12 | 0 | 19 | 13 | 20 | 0 | 0 | 0 | 0 | 290 | 0 | 73 | 0 | 47 | 25 | 0 | 51 | 0 | 0 | 25 | 18 | 10 | 33 | 11 | 88 | 112 | 0 | 0 | 0 | 43 | 0 | 53 | 43 | 163 | 0 | 62 | 30 | 0 | 128 | 0 | 0 | 10 | 0 | 16 | 3 | 0 | 117 | 0 | 0 | 75 | 0 | 28 | 0 | 12 | 24 | 112 | 338 | 28 | 50 | 17 | 0 | 100 | 17 | 17 | 34 | 47 | 12 | 375 | 46 | 0 | 54 | 17 | 0 | 17 | 0 | 19 | 35 | 330 | 0 | 10 | 400 | 4 | 0 | 0 | 0 |  | 816 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 20 | 0 | 8 | 120 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 34 | 48 | 17 | 38 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 17 | 0 | 35 | 0 | 70 | 0 | 0 | 55 | 560 | 220 | 0 | 45 | 0 | 0 | 72 | 0 | 0 | 610 | 0 | 140 | 598 | 0 | 0 |  | 5543 | 4095 | 9638 | 2866 | 816 | 1470 | 0 | 1564 | 2478 | 86 | 0 | 266 | 88 | 0 | 4 | 0 | 95.85
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 402 | 0 |  | 0 | 420 | 0 | 0 | 17 | 55 | 0 | 0 | 97 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 15 | 17 | 14 | 25 | 27 | 16 | 0 | 92 | 0 | 100 | 0 | 17 | 218 | 0 | 0 | 0 |  | 4 | 0 | 0 | 0 | 0 | 19 | 13 | 24 | 0 | 0 | 0 | 0 | 295 | 0 | 73 | 0 | 48 | 25 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 11 | 92 | 112 | 0 | 0 | 0 | 43 | 0 | 53 | 39 | 163 | 0 | 63 | 30 | 0 | 128 | 0 | 0 | 10 | 0 | 16 | 5 | 0 | 45 | 0 | 0 | 75 | 0 | 44 | 0 | 12 | 17 | 142 | 332 | 28 | 50 | 17 | 0 | 100 | 17 | 17 | 0 | 47 | 12 | 400 | 51 | 0 | 54 | 17 | 0 | 17 | 0 | 34 | 17 | 393 | 0 | 36 | 400 | 5 | 0 | 0 | 0 |  | 816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 38 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 35 | 0 | 89 | 0 | 0 | 55 | 622 | 222 | 0 | 75 | 0 | 0 | 35 | 0 | 0 | 628 | 0 | 140 | 581 | 0 | 0 |  | 5641 | 4007 | 9648 | 3176 | 816 | 1541 | 0 | 1299 | 2541 | 92 | 0 | 86 | 92 | 0 | 5 | 0 | 95.84
19:30 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 399 | 0 |  | 0 | 420 | 0 | 0 | 0 | 55 | 0 | 0 | 186 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 10 | 17 | 14 | 25 | 27 | 16 | 0 | 92 | 0 | 100 | 0 | 17 | 218 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 19 | 13 | 17 | 0 | 0 | 0 | 0 | 280 | 0 | 73 | 0 | 48 | 25 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 11 | 92 | 112 | 0 | 0 | 0 | 43 | 0 | 53 | 39 | 163 | 0 | 63 | 30 | 0 | 128 | 0 | 0 | 10 | 0 | 16 | 5 | 0 | 15 | 0 | 0 | 75 | 0 | 45 | 0 | 12 | 17 | 50 | 332 | 28 | 50 | 17 | 0 | 100 | 17 | 17 | 0 | 47 | 12 | 400 | 35 | 0 | 54 | 17 | 0 | 17 | 0 | 36 | 17 | 393 | 0 | 36 | 400 | 5 | 0 | 0 | 0 |  | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 38 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 35 | 0 | 49 | 0 | 0 | 55 | 622 | 222 | 0 | 82 | 0 | 0 | 35 | 0 | 0 | 627 | 0 | 140 | 605 | 0 | 0 |  | 5521 | 4059 | 9580 | 3242 | 911 | 1501 | 0 | 1098 | 2564 | 92 | 0 | 75 | 92 | 0 | 5 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 401 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 0 | 0 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 10 | 15 | 14 | 25 | 27 | 8 | 0 | 92 | 0 | 102 | 0 | 0 | 218 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 19 | 13 | 25 | 0 | 0 | 0 | 0 | 290 | 0 | 73 | 0 | 48 | 25 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 11 | 90 | 112 | 0 | 0 | 0 | 43 | 0 | 53 | 43 | 163 | 0 | 63 | 30 | 0 | 128 | 0 | 0 | 10 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 75 | 0 | 45 | 0 | 12 | 17 | 50 | 372 | 8 | 17 | 17 | 0 | 50 | 17 | 17 | 0 | 48 | 12 | 400 | 33 | 0 | 54 | 17 | 0 | 17 | 0 | 36 | 17 | 385 | 0 | 36 | 404 | 3 | 0 | 0 | 0 |  | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 35 | 0 | 36 | 0 | 0 | 55 | 622 | 222 | 0 | 35 | 0 | 0 | 35 | 0 | 0 | 627 | 0 | 140 | 597 | 0 | 0 |  | 5319 | 4046 | 9365 | 3210 | 910 | 1640 | 0 | 860 | 2560 | 92 | 0 | 0 | 90 | 0 | 3 | 0 | 95.84
21:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 400 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 10 | 15 | 14 | 25 | 27 | 8 | 0 | 92 | 0 | 100 | 0 | 0 | 224 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 13 | 29 | 0 | 0 | 0 | 0 | 310 | 0 | 73 | 0 | 48 | 25 | 0 | 43 | 0 | 0 | 0 | 18 | 10 | 33 | 11 | 96 | 112 | 0 | 0 | 0 | 43 | 0 | 53 | 43 | 163 | 0 | 62 | 30 | 0 | 130 | 0 | 0 | 10 | 0 | 16 | 5 | 0 | 0 | 0 | 0 | 75 | 0 | 44 | 0 | 12 | 17 | 50 | 360 | 0 | 17 | 17 | 0 | 15 | 17 | 17 | 0 | 49 | 12 | 380 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 22 | 17 | 390 | 0 | 0 | 400 | 1 | 0 | 0 | 0 |  | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 55 | 622 | 223 | 0 | 35 | 0 | 0 | 35 | 0 | 0 | 630 | 0 | 140 | 602 | 0 | 0 |  | 5114 | 4002 | 9116 | 3172 | 910 | 1585 | 0 | 696 | 2564 | 92 | 0 | 0 | 96 | 0 | 1 | 0 | 95.84
22:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 399 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15 | 14 | 25 | 27 | 0 | 0 | 92 | 0 | 100 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 13 | 31 | 0 | 0 | 0 | 0 | 280 | 0 | 73 | 0 | 48 | 25 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 25 | 11 | 90 | 113 | 0 | 0 | 0 | 43 | 0 | 53 | 43 | 120 | 0 | 63 | 30 | 0 | 130 | 0 | 0 | 10 | 0 | 16 | 5 | 0 | 0 | 0 | 0 | 56 | 0 | 17 | 0 | 12 | 17 | 0 | 332 | 0 | 17 | 17 | 0 | 0 | 17 | 17 | 0 | 49 | 12 | 400 | 0 | 0 | 17 | 17 | 0 | 17 | 0 | 18 | 17 | 385 | 0 | 0 | 350 | 6 | 0 | 0 | 0 |  | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 622 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 627 | 0 | 140 | 599 | 0 | 0 |  | 4779 | 3957 | 8736 | 3078 | 911 | 1603 | 0 | 448 | 2508 | 92 | 0 | 0 | 90 | 0 | 6 | 0 | 95.84
23:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 352 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15 | 22 | 25 | 27 | 0 | 0 | 92 | 0 | 90 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 2 | 13 | 34 | 0 | 0 | 0 | 0 | 305 | 0 | 73 | 0 | 48 | 25 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 12 | 90 | 112 | 0 | 0 | 0 | 43 | 0 | 53 | 43 | 120 | 0 | 66 | 30 | 0 | 130 | 0 | 0 | 10 | 0 | 16 | 5 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 17 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 9 | 12 | 400 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 350 | 3 | 0 | 0 | 0 |  | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 505 | 0 | 140 | 504 | 0 | 0 |  | 4632 | 3558 | 8190 | 3163 | 911 | 1614 | 0 | 98 | 2219 | 92 | 0 | 0 | 90 | 0 | 3 | 0 | 95.83
24:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 352 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 22 | 25 | 27 | 0 | 0 | 92 | 0 | 93 | 0 | 0 | 225 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 25 | 0 | 0 | 0 | 0 | 270 | 0 | 73 | 0 | 48 | 25 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 11 | 82 | 73 | 0 | 0 | 0 | 42 | 0 | 53 | 43 | 120 | 0 | 67 | 30 | 0 | 130 | 0 | 0 | 10 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 350 | 5 | 0 | 0 | 0 |  | 725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 514 | 0 | 140 | 475 | 0 | 0 |  | 4422 | 3261 | 7683 | 3066 | 725 | 1574 | 0 | 0 | 2139 | 92 | 0 | 0 | 82 | 0 | 5 | 0 | 95.83
KWH | 0 | 0 | 0 | 4347000 | 0 | 1155227 | 0 | 8881200 | 0 |  | 0 | 9204600 | 0 | 41280 | 42746 | 309732 | 0 | 0 | 649000 | 64320 | 30384 | 275040 | 19667 | 0 | 0 | 0 | 129600 | 143846 | 137101 | 268812 | 48000 | 465480 | 527500 | 716100 | 113280 | 0 | 1607040 | 0 | 1900000 | 0 | 71029 | 5185865 | 0 | 0 | 0 |  | 49440 | 71712 | 0 | 49560 | 0 | 172320 | 271632 | 652320 | 0 | 0 | 0 | 0 | 7137000 | 0 | 1221090 | 0 | 1046808 | 408960 | 0 | 1060362 | 0 | 0 | 98126 | 318922 | 184320 | 484400 | 191930 | 1938240 | 3733440 | 0 | 0 | 11500 | 1006000 | 0 | 933000 | 786240 | 3456900 | 0 | 1304352 | 517440 | 0 | 3108030 | 0 | 0 | 183960 | 0 | 248640 | 159310 | 0 | 451636 | 0 | 0 | 782400 | 0 | 291168 | 136350 | 126720 | 277920 | 572072 | 8117000 | 250800 | 342019 | 198218 | 25918 | 526909 | 138886 | 247562 | 103740 | 325080 | 191040 | 9036500 | 193920 | 233590 | 361440 | 258436 | 0 | 189720 | 179682 | 268800 | 134640 | 8002600 | 0 | 301091 | 8410908 | 107040 | 0 | 0 | 0 |  | 18834909 | 0 | 0 | 0 | 30720 | 0 | 0 | 0 | 24480 | 0 | 14625 | 2289000 | 376728 | 0 | 0 | 0 | 0 | 0 | 0 | 25712 | 0 | 46817 | 268858 | 100546 | 85678 | 0 | 0 | 143892 | 0 | 0 | 4130500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8377900 | 91680 | 0 | 332352 | 0 | 313372 | 0 | 30659 | 340128 | 12428600 | 4913427 | 0 | 242400 | 30180 | 415440 | 190080 | 0 | 0 | 11578180 | 168601 | 3381800 | 11121540 | 1058810 | 0 |  | 107923608 | 81387614 | 189311222 | 70073824 | 18834909 | 33248154 | 0 | 9408277 | 51051528 | 1607040 | 0 | 751480 | 1938240 | 2290730 | 107040 | 0
Fuel Cost | 0 | 0 | 0 | 6477030 | 0 | 1536451.91 | 0 | 9325260 | 0 |  | 0 | 10033014 | 0 | 461510.4 | 566384.5 | 4103949 | 0 | 0 | 1135750 | 940358.4 | 427502.88 | 4458398.4 | 181329.74 | 0 | 0 | 0 | 1648512 | 1941921 | 1838524.41 | 201609 | 36000 | 0 | 0 | 0 | 1926892.8 | 0 | 433900.8 | 0 | 3591000 | 0 | 1161324.15 | 5393299.6 | 0 | 0 | 0 |  | 645192 | 1196156.16 | 0 | 669555.6 | 0 | 1993742.4 | 344972.64 | 2172225.6 | 0 | 0 | 0 | 0 | 7779330 | 0 | 1575206.1 | 0 | 1182893.04 | 609350.4 | 0 | 1770804.54 | 0 | 0 | 1319794.7 | 436923.14 | 138240 | 847700 | 143947.5 | 13916563.2 | 4069449.6 | 0 | 0 | 183310 | 1378220 | 0 | 1623420 | 1360195.2 | 3975435 | 0 | 2530442.88 | 1179763.2 | 0 | 3139110.3 | 0 | 0 | 364240.8 | 0 | 186480 | 121075.6 | 0 | 6164831.4 | 0 | 0 | 10546752 | 0 | 4032676.8 | 1593931.5 | 1307750.4 | 3796387.2 | 7591395.44 | 7467640 | 3049728 | 4945594.74 | 2507457.7 | 403284.08 | 6185911.66 | 1512468.54 | 2631584.06 | 1407751.8 | 4190281.2 | 2250451.2 | 8313580 | 2511264 | 3375375.5 | 4586673.6 | 2941001.68 | 0 | 2477743.2 | 2147199.9 | 4023936 | 1773208.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 56504727 | 0 | 0 | 0 | 319795.2 | 0 | 0 | 0 | 440884.8 | 0 | 210161.25 | 2563680 | 730852.32 | 0 | 0 | 0 | 0 | 0 | 0 | 402135.68 | 0 | 775289.52 | 4546388.78 | 1370441.98 | 1445387.86 | 0 | 0 | 108926.244 | 0 | 0 | 35026640 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8294121 | 1232179.2 | 0 | 3931724.16 | 0 | 3979824.4 | 0 | 338781.95 | 4129153.92 | 103157380 | 5011695.54 | 0 | 1793760 | 341335.8 | 4873111.2 | 2913926.4 | 0 | 0 | 105245656.2 | 0 | 40480146 | 95089167 | 0 | 0 |  | 218409522.99 | 485257273.404 | 703666796.394 | 66912559.544 | 56504727 | 40236775.61 | 0 | 120917599.43 | 378998989.2 | 433900.8 | 0 | 12489351.68 | 13916563.2 | 13256329.93 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 386 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 10 | 17 | 5 | 15 | 22 | 22 | 25 | 27 | 8 | 0 | 46 | 0 | 80 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 0 | 5 | 0 | 6 | 13 | 13 | 0 | 0 | 0 | 0 | 345 | 0 | 73 | 0 | 49 | 25 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 0 | 5 | 94 | 190 | 0 | 0 | 2 | 43 | 0 | 51 | 46 | 120 | 0 | 61 | 30 | 0 | 130 | 0 | 0 | 10 | 0 | 8 | 8 | 0 | 12 | 0 | 0 | 56 | 0 | 12 | 20 | 12 | 17 | 6 | 394 | 9 | 17 | 17 | 4 | 15 | 0 | 4 | 0 | 2 | 12 | 400 | 0 | 43 | 0 | 17 | 0 | 0 | 29 | 18 | 0 | 375 | 0 | 36 | 350 | 0 | 0 | 0 | 0 |  | 863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 550 | 220 | 0 | 0 | 5 | 68 | 0 | 0 | 0 | 510 | 30 | 140 | 416 | 174 | 0 |  | 8567 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 402 | 0 |  | 0 | 420 | 0 | 0 | 17 | 55 | 0 | 0 | 97 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 15 | 17 | 14 | 25 | 27 | 16 | 0 | 92 | 0 | 100 | 0 | 17 | 218 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 19 | 13 | 24 | 0 | 0 | 0 | 0 | 295 | 0 | 73 | 0 | 48 | 25 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 11 | 92 | 112 | 0 | 0 | 0 | 43 | 0 | 53 | 39 | 163 | 0 | 63 | 30 | 0 | 128 | 0 | 0 | 10 | 0 | 16 | 5 | 0 | 45 | 0 | 0 | 75 | 0 | 44 | 0 | 12 | 17 | 142 | 332 | 28 | 50 | 17 | 0 | 100 | 17 | 17 | 0 | 47 | 12 | 400 | 51 | 0 | 54 | 17 | 0 | 17 | 0 | 34 | 17 | 393 | 0 | 36 | 400 | 5 | 0 | 0 | 0 |  | 816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 38 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 35 | 0 | 89 | 0 | 0 | 55 | 622 | 222 | 0 | 75 | 0 | 0 | 35 | 0 | 0 | 628 | 0 | 140 | 581 | 0 | 0 |  | 9648 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 412 | 0 |  | 0 | 450 | 0 | 100 | 85 | 55 | 0 | 0 | 0 | 90 | 90 | 149 | 48 | 0 | 0 | 0 | 35 | 35 | 35 | 15 | 12 | 22 | 25 | 26 | 17 | 0 | 92 | 0 | 100 | 0 | 17 | 225 | 0 | 0 | 0 |  | 6 | 70 | 34 | 12 | 0 | 20 | 12 | 25 | 0 | 0 | 0 | 0 | 360 | 0 | 73 | 0 | 48 | 25 | 0 | 51 | 0 | 30 | 52 | 18 | 10 | 33 | 10 | 140 | 100 | 0 | 0 | 0 | 43 | 0 | 52 | 46 | 163 | 0 | 63 | 80 | 0 | 130 | 0 | 0 | 10 | 0 | 16 | 5 | 0 | 130 | 0 | 0 | 75 | 0 | 50 | 0 | 12 | 17 | 150 | 400 | 28 | 105 | 17 | 0 | 100 | 17 | 17 | 100 | 47 | 12 | 400 | 72 | 0 | 54 | 17 | 0 | 17 | 0 | 18 | 17 | 393 | 0 | 36 | 620 | 10 | 0 | 0 | 0 |  | 930 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 45 | 0 | 16 | 120 | 20 | 110 | 0 | 0 | 0 | 30 | 20 | 82 | 28 | 42 | 45 | 8 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 95 | 0 | 35 | 0 | 107 | 0 | 0 | 55 | 622 | 220 | 0 | 75 | 0 | 0 | 110 | 0 | 0 | 510 | 0 | 140 | 550 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 412 | 0 | 0 | 0 | 450 | 0 | 90 | 85 | 15 | 0 | 0 | 0 | 90 | 90 | 48 | 48 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 12 | 22 | 17 | 26 | 8 | 0 | 92 | 0 | 100 | 0 | 8 | 225 |  | 0 | 0 | 0 | 6 | 70 | 0 | 12 | 0 | 6 | 12 | 10 | 0 | 0 | 0 | 0 | 360 | 0 | 73 | 0 | 48 | 30 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 10 | 128 | 70 | 0 | 0 | 1.6 | 43 | 0 | 52 | 46 | 163 | 0 | 63 | 80 | 0 | 130 | 0 | 0 | 10 | 0 | 16 | 5 | 0 | 82 | 0 | 0 | 56 | 0 | 36 | 20 | 12 | 17 | 12 | 400 | 9 | 17 | 17 | 5 | 65 | 17 | 17 | 100 | 9 | 12 | 400 | 72 | 50 | 17 | 17 | 0 | 17 | 35 | 18 | 17 | 393 | 0 | 36 | 400 | 10 | 0 | 0 | 0 |  | 881 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 20 | 110 | 0 | 0 | 0 | 0 | 0 | 50 | 28 | 34 | 30 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 75 | 0 | 35 | 0 | 6 | 0 | 8 | 0 | 622 | 220 |  | 17 | 6 | 100 | 70 | 0 |  | 510 | 30 | 140 | 550 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 60 | 0 | 393 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 22 | 10 | 27 | 0 | 0 | 92 | 0 | 95 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 18 | 0 | 0 | 0 | 0 | 360 | 0 | 73 | 0 | 48 | 31 | 0 | 43 | 0 | 0 | 0 | 18 | 9 | 33 | 0 | 80 | 68 | 0 | 0 | 0 | 43 | 0 | 51 | 40 | 163 | 0 | 66 | 30 | 0 | 25 | 0 | 0 | 10 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 7 | 0 | 0 | 0 | 340 | 8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 12 | 400 | 0 | 4 | 0 | 1 | 0 | 0 | 7 | 0 | 0 | 393 | 0 | 0 | 621 | 1 | 0 | 0 | 0 | 0 | 769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 490 | 220 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 478 | 6 | 140 | 431 | 38 | 0 | 0 |  |  |  | 103321978 | 18834909 | 0 | 51051528 | 10159757 | 1938240 | 2290730 | 107040 | 1607040
[8 empty] | 299430 | [13 empty] | 299565 | [26 empty] | 399366 | 399587 | [8 empty] | 299280 | [15 empty] | 299772 | [10 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 |  | 399747 |  |  |  | 399575 | 399337 | 399467 | 399589 | 299230 | 765 | [6 empty] | 399245 |  | 299282 | 399274 |  | 399223 |  | 399630 | [12 empty] | 599468 | [32 empty] | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 | [8 empty] | 599726 | [9 empty] | 103.322 | 18.8349 | 0 | 51.0515 | 10.1598 | 1.9382 | 2.2907 | 0.10704 | 1.607
| Minimum Generation |  | 5635 | 5:00
| Highest Generation |  | 9648 | 19:00 | [200 empty] | 189.3112
| Day Peak Generation |  | 8567 | 12:00
| Evening Peak Generation |  | 9648 | 19:00 | [200 empty] | 202699852
| HVDC Max Flow |  | 911 | 19:30 | [200 empty] | 202.6999
| HVDC EvPeak Flow |  | 816 | 19:00
| Load factor L.F |  | 81.76% | [166 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-12-18
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-12-17 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 8567 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6274
Evening Peak Generation : |  |  | 9648 | MW Hour : | 19:00 | Available Max Generation : |  | 11734
E.P. Demand (at gen end) : |  |  | 9648 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9800
Maximum Generation : |  |  | 9648 | MW Hour : | 19:00 | Reserve(Generation end) |  | 1934
Total Gen. (MKWH) : |  |  | 189.3112 | System Load Factor : | 81.76% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 128 | MW at | 7:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-12-18
Actual : |  | 95.81 | Ft.(MSL) , | Rule curve : | 104.4 | Ft.( MSL )
Gas Consumed : |  | Total = | 812.65 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 107149335.154
: |  |  | Coal : | 378998989.2 | Oil : | 133406951.11 | Total : | 619555275.464
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3338.151 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 909.7616 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1272.1541 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1103.6653 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 909.1763 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 675.1017 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 379.5877 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 315.2702 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 616.6379 |  |  | 0 | 0%
Total |  | 0 |  | 9519.5058 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:02 | 14:43 | Chowmuhani 132/33kV S/S TR2 Scheduled S/D Due to Due to yearly maintenance
08:08 |  | Ashuganj 55 MW PP (Precision) Syncronized
08:19 | 15:29 | Baroaulia-Hathazari 132 kV Ckt-2 Scheduled S/D from Baroaulia 132/33kV end Due to Annual Maintenance
08:23 | 19:36 | Kachua 132/33kV S/S TR-2 LT Scheduled S/D Due to Annual maintenance
08:24 | 17:34 | Kaliakoir 400/230/132kV S/S Bibiyana1 Scheduled S/D Due to Annual Maintenance and Dead Line Checking.
08:27 |  | Bibiyana-Kaliakoir 400 kV Ckt-1 Scheduled S/D from Bibiana 400/230kV end Due to For dead line checking.
08:27 | 10:55 | Amnura-Rajshahi 132kV Ckt-1 Scheduled S/D from Rajshahi 230/132/33kV end Due to A/M
08:28 | 16:32 | Sirajganj 132/33kV S/S T1-(415) LT Scheduled S/D Due to annual maintenance
08:29 | 12:20 | Bogura 230/132kV S/S T-03 LT Scheduled S/D Due to annual maintenance(tan delta test)
08:30 | 14:29 | Bogura 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Annual Maintenance.
08:32 | 15:06 | Purbasadipur-Saidpur 132kV Ckt-2 Scheduled S/D from Saidpur 132/33kV end Due to Annual maintenance work.
08:34 | 14:54 | Bheramara P/S-Kustia 132 kV Ckt-1 Scheduled S/D from Kushtia 132/33kV end. and from Bheramara 230/132kVend.
08:37 | 16:34 | Barishal(N)-Madaripur 132 kV Ckt-1 Scheduled S/D from Barishal 230/132kV end Due to Annual maintenance work
08:38 | 17:06 | Madartek-Rampura 132kV Ckt-2 Scheduled S/D from Rampura 230/132kV end Due to Annual maintenance.
08:48 | 16:58 | Aminbazar-Kallyanpur 132kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to Annual maintenace
09:02 | 16:47 | Brahmanbaria-Narsinghdi 132 kV Ckt-2 Scheduled S/D from Brahmanbaria 132/33kV end Due to Annual Maintenance .
09:06 | 14:42 | Ashuganj-Brahmanbaria 132kV Ckt-2 Project Work S/D from Brahmanbaria 132/33kV end Due to LA replacement work
09:11 | 17:33 | Cox'sbazar-Dohazari 132 kV Ckt-2 Scheduled S/D from Dohazari 132/33kV end Due to Annual Maintenance(Line)
09:18 | 16:30 | Khulna (S)-Satkhira 132kV Ckt-2 Scheduled S/D from Satkhira 132/33kV end Due to Yearly maintenance.
09:19 | 14:31 | UttaraNew 132/33kV S/S GT-02 HT Scheduled S/D Due to Due to Annual maintenance of GT-2 X/Former
09:26 | 15:22 | Kodda 132/33kV S/S Tr-4 (436T) LT Scheduled S/D Due to Annual maintenance
09:26 |  | Siddhirganj 230/132kV S/S 230kV BUS A Scheduled S/D Due to Annual maintence
09:35 | 16:56 | Mymensingh 132/33kV S/S Transformer-1 (404T) LT Scheduled S/D Due to Annual maintenance works
09:37 | 12:27 | Chandpur 132/33kV S/S 422T HT Scheduled S/D Due to Relay Testing by SPMD, Cumilla.
09:37 | 12:27 | Chandpur 132/33kV S/S 422T LT Scheduled S/D Due to Do
09:51 | 10:15 | BIPTC S/S 10CF16 Forced S/D Due to Rectification work due to trip
09:55 | 15:22 | Ashuganj 230/132/33kV S/S SHUNT REACTOR-2 Scheduled S/D Due to Maintenance work by apscl sub-station.
10:11 | 15:32 | Haripur-Haripur (360MW) 230kV Ckt-2 Scheduled S/D from Haripur 230/132kV end Due to S/D taken by HPL.
10:36 |  | Sympa Solar Power 8 MW Tripped with remarks:- Panchagarh to Tetulia 33 KV grid line tripped.
10:40 | 12:11 | Aminbazar 400/230/132kV S/S 230/132kv Tr-01 LT Scheduled S/D Due to DS Red Hot maint.
11:10 | 11:21 | Benapole 132/33kV S/S Transformer-2(416T) LT Forced S/D Due to 33KV Bus connector Disconnect |  |  |  |  | 12.0MW load interrup.
11:16 | 13:22 | Aminbazar-Keraniganj 230kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to work by TRTU depertment.
11:52 | 16:45 | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-1 Scheduled S/D Due to Annual Maintenance work
12:12 | 15:53 | Kalurghat 132/33kV S/S TRFO-02(516T) HT Project Work S/D Due to For Oil leakage removed.
12:27 | 16:20 | Bogura 230/132kV S/S T-02 HT Scheduled S/D Due to Annual maintenance(Tan dalta test)
12:28 |  | Amnura 132/33kV S/S T-1 (406T) LT Scheduled S/D Due to 132 KV CT change. Clearance from NLDC.
12:35 | 20:16 | Chandpur 132/33kV S/S 402T LT Scheduled S/D Due to Do
13:23 | 14:39 | Aminbazar-Keraniganj 230kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to Teleprotection Test
15:19 |  | Ashuganj 230/132/33kV S/S SHUNT REACTOR-3 Forced S/D
| 15:40 | Natore 132/33kV S/S TR-1 (405 T) HT is restored.
16:40 | 17:01 | Daudkandi-Sonargaon 132 kV Ckt-1 Tripped from Daudkandi 132/33kV end showing Dist Trip , C-Phase , Zone-1. relays.
| 18:00 | Shyampur 230/132kV S/S 230 kV APR (D04) is restored.
| 18:03 | APR-Hasnabad 230kV Ckt-2 is restored.
18:36 |  | Siddhirgonj 2*120 MW GTPP Syncronized with remarks:- GT-2
19:21 |  | Siddhirgonj 2*120 MW GTPP Syncronized with remarks:- GT-1
| 19:42 | Agargaon 230/132kV S/S 230kV Transformer-1 ( 705T1) HT is restored.
06:48 | 07:14 | Coxsbazar 132/33kV S/S 415T-T2 HT Forced S/D Due to High Temperature Maintenance. |  |  |  |  | 15 MW load interrup.
06:54 |  | Shahjadpur-Sirajganj 132kV Ckt-1 Project Work S/D from Sirajganj 132/33kV end.
07:26 |  | Agargaon 230/132kV S/S Auxiliary Tr-1 LT Scheduled S/D Due to Anual maintenance
07:35 |  | Hasnabad-Keraniganj 230kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to Annual maintenance work.
07:38 |  | Bogura 230/132kV S/S T-01 LT Scheduled S/D Due to annual maintenance
| Sub Divisional Engineer |  |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-12-17 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 72 | 1155227 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 402 | 8881200
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9204600
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 0 | 41280 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 17 | 42746 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 309732
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 19667 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 15 | 268812 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 97 | 649000 | GT-2 Sync. at 18:36.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 0 | 64320 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 30384 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 129600 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 48 | 275040 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 143846 | Reserve
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 137101 | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 31 | 513480 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 527500 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 27 | 716100 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 16 | 113280 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 45 | 451636 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 44 | 291168 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 50 | 342019 | Low demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 51 | 193920 | Low demand
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 361440 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 179682
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 134640 | Fuel shortage
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5422 | 1718 | 29524420
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 1900000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 71029 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 136350
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 172320 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 92 | 1607040 | Unit-3 under maint.
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 218 | 5185865
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 198218 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 71712 | Reserve
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 49560 | Reserve
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 126720 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 13 | 271632 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 24 | 652320
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25918
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 100 | 526909 | Low demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 138886 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 247562 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 191040 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 258436 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 0 | 0 | Gas Commissioning
| SS Power I |  | SS Power | 2*612 | 1224 | 400 | 8410908 | Coal shortage
| Cox's Bazar Wind |  | IPP | 66 | 0 | 5 | 107040 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 0 | 0 | On test.
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 36 | 301091 | Gas Commissioning
| Chattogram area Total |  |  |  | 3769 | 1116 | 20650556
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 0 | Under maint.
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 295 | 7137000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 393 | 8002600 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 48 | 1046808
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 0 | 25 | 408960 | Gas shortage
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 73 | 1221090 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1060362
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 142 | 572072 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 277920 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 318922 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 184320 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 92 | 1938240
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 484400
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 98126 | Reserve
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 11 | 191930 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 103740 | Reserve
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 47 | 325080 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 189720 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 34 | 268800 | Fuel shortage
| Cumilla Area Total |  |  |  | 2896 | 1306 | 23830090
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 112 | 3733440 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Contract Expired
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11500
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 75 | 782400 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 28 | 250800 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 233590
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 4 | 49440 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 219 | 5061170
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1006000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3456900
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 933000
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 39 | 786240
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 159310 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1304352
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 30 | 517440 | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 128 | 3108030 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 248640
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Under maint.
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 332 | 8117000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 183960
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9036500
| Sylhet Area Total |  |  |  | 2427 | 1282 | 28857372
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 816 | 18834909
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 30720 | Reserve
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 24480 | Reserve
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Machine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 14625 | Reserve
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 91680 | Reserve
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 415440
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | Fuel shortage
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 628 | 11578180
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 1444 | 30990034
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 18 | 376728 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 120 | 2289000 | ST Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 622 | 12428600 | Unit-2 under maint.
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 222 | 4913427
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 75 | 242400 | Fuel shortage
| Barisal 307 MW |  | IPP | 307*1 | 307 | 140 | 3381800 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1197 | 23631955
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 46817 | Reserve
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 268858 | Reserve
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 341 | 8377900 | FGMO
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 85678 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 143892
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 17 | 100546 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 25712 | Reserve
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 332352 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 55 | 340128 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 30180
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 581 | 11121540
| Rajshahi Area Total |  |  |  | 3631 | 1072 | 20873603
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4130500 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 89 | 313372 | Low demand
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 30659
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 35 | 190080 | Low demand
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 168601
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1058810
| Rangpur Area Total |  |  |  | 950 | 294 | 5892022
| Total |  |  |  | 25211 | 9648 | 189311222
| Eastern Grid Total |  |  |  | 15128 | 5641 | 107923608
| Western Grid Total |  |  |  | 10083 | 4007 | 81387614
| National Grid Total |  |  |  | 25211 | 9648 | 189311222
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-12-17
| (a) ENTIRE EASTERN GRID : |  | 6234.56 | MW | (b) ENTIRE WESTERN GRID : |  | 2928 | MW
| i) Dhaka area |  | 3428.86 | MW | i) Khulna area |  | 1080.5 | MW
| ii) Chittagong area |  | 862.7 | MW | ii) Rajshahi area |  | 930 | MW
| iii) Comilla area |  | 837 | MW | iii) Barisal area |  | 275.5 | MW
| iv) Mymensingh area |  | 753 | MW | iv) Rangpur area |  | 642 | MW
| v) Sylhet area |  | 353 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 9162.56 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 18 | 18:30 | Kamrangirchar | 40.5 | 13:00 | Narinda | 44 | 13:00 | Sherpur | 98 | 18:00
2 | AKSML | 14 | 17:00 | Chowmuhani | 130 | 20:00 | Kaptai | N/A | N/A | Narshingdi | 143 | 18:30 | Shikalbaha | 21 | 13:00
3 | Aftabnagar | 24 | 12:00 | Chuadanga | 69 | 18:00 | Kazla | 59 | 04:00 | Natore | 87 | 18:00 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 52 | 14:00 | Coxsbazar | 86 | 16:00 | Keranigonj | 50 | 13:00 | Nawabganj | 32.4 | 21:00 | Shitalakhya | 73.2 | 12:00
5 | Agrabad | 42 | 18:00 | Cumilla(N) | 116 | 19:00 | Khagrachori | 20 | 18:00 | Netrakona | 91 | 18:00 | Sholosohor | 34 | 21:00
6 | Amnura | 30 | 08:00 | Cumilla(S) | 96 | 14:00 | Khulna | 66 | 13:00 | New | 37 | 11:00 | Shyampur | 128 | 10:00
7 | Ashuganj | 54 | 21:00 | Daudkandi | 100 | 19:00 | Khulshi | 138 | 18:30 | Niamatpur | 47 | 18:30 | Siddhirganj | 92 | 13:00
8 | BIPTC | N/A | N/A | Dhaka | 16 | 13:00 | Kishoreganj | 100 | 18:30 | Noapara | 34.5 | 19:00 | Sirajganj | 82 | 18:30
9 | BSRM | 63 | 19:30 | Dhamrai | 96 | 18:00 | Kodda | 214 | 11:00 | PHP | 10 | 14:00 | Sonargaon | 74 | 11:00
10 | Bagerhat | 67 | 18:00 | Dhanmondi | 78.6 | 13:00 | Kulaura | 28 | 18:00 | Pabna | 78 | 18:00 | Sreemongol | 40 | 18:00
11 | Bakulia | 62 | 18:00 | Dohazari | 52 | 20:00 | Kurigram | 52 | 18:00 | Palashbari | 80 | 18:00 | Sreepur | 56 | 12:00
12 | Banani | 18 | 12:00 | Faridpur | 106 | 19:30 | Kushtia | 96 | 18:30 | Panchagarh | 44 | 18:00 | Srinagar | 27.7 | 20:00
13 | Bangabhaban | 8 | 10:00 | Fatullah | 43 | 12:00 | Lalbag | 75 | 13:00 | Patuakhali | 59.3 | 21:00 | Sunamganj | 40 | 18:00
14 | Barapukuria | 49 | 18:30 | Fenchuganj | 24 | 18:00 | Lalmonirhat | 32 | 19:00 | Payra | 20 | 18:00 | Sylhet | 14 | 18:00
15 | Barguna | 14 | 20:00 | Feni | 75 | 18:00 | MI_Cement | 16.1 | 16:00 | Postogola | 32 | 13:00 | Sylhet-132 | 92 | 13:00
16 | Barishal | 74 | 12:00 | GPH | 20 | 23:00 | Madanganj | 23 | 19:00 | Purbachal | 9 | 12:00 | TK | 20 | 18:30
17 | Barishal-230 | 62 | 19:30 | Ghorashal | 49 | 18:00 | Madaripur | 61 | 19:30 | Purbasadipur | 103 | 18:00 | Tangail | 134 | 18:00
18 | Baroaulia | 47 | 21:00 | Goalpara | 24 | 13:00 | Madartek | 50.25 | 13:00 | Rahim | 40 | 07:00 | Thakurgaon | 72 | 18:00
19 | Baroirhat | 32 | 18:00 | Gollamari | 34 | 13:00 | Madunaghat | 31 | 12:00 | Rajbari | 46 | 18:00 | Tongi | 80 | 11:00
20 | Bashundhara | 109 | 18:00 | Gopalganj | 68.3 | 18:00 | Magura | 42 | 18:00 | Rajendrapur | 66 | 19:30 | Ullon | 31 | 18:00
21 | BashundharaCement | 0 | 00:00 | Gulshan | 68 | 13:00 | Mahasthangarh | 50 | 18:30 | Rajshahi | 100 | 19:30 | Uttara | 55 | 13:00
22 | Beanibazar | 42 | 18:00 | Halishahar | 54.5 | 15:00 | Manikganj | 83 | 18:00 | Rajshahi-230 | 21 | 18:00 | UttaraNew | 26 | 13:00
23 | Benapole | 39 | 18:00 | HaripurSBU | 128 | 16:00 | Maniknagar | 54 | 13:00 | Ramganj | 72 | 19:30 | Zigatola | 68 | 14:00
24 | Bhaluka | 96 | 18:00 | Hasnabad | 66 | 13:00 | Matarbari | 27 | 18:00 | Rampur | 22 | 13:00
25 | Bhandaria | 34 | 21:00 | Hathazari | 47 | 19:00 | Matuail | 56 | 10:00 | Rangamati | 14 | 18:00
26 | Bhangura | 20 | 18:00 | Ishurdi | 52 | 18:30 | Millgate | 79 | 12:00 | Rangpur | 94 | 18:30
27 | Bheramara(GK) | 38 | 18:00 | Jaldhaka | 53 | 18:00 | Mirpur | 70 | 18:00 | Ruppur | 4.2 | 16:00
28 | Bhulta | 197 | 12:00 | Jamalpur | 108 | 19:00 | Mirsorai | 3 | 18:00 | SSM | 1 | 21:00
29 | Bog-Sherpur | 46 | 08:00 | Jashore | 90 | 13:00 | Mirzapur | 28.74 | 18:30 | Saidpur | 82 | 18:00
30 | Bogura | 99 | 18:30 | Jhenaidah | 87 | 18:00 | Mithapukur | 46 | 18:00 | Satkhira | 79 | 18:00
31 | Borhanuddin | 35 | 22:00 | Joydebpur | 127 | 12:00 | Modern | 0 | 00:00 | Satmasjid | 61 | 14:00
32 | Brahmanbaria | 99 | 18:00 | Joypurhat | 39 | 18:00 | Mogbazar | 65.9 | 13:00 | Savar | 120 | 09:00
33 | Cantonment | 106 | 13:00 | Juldah | 18 | 12:00 | Mongla | 24 | 12:00 | SevenRings | 3.68 | 20:00
34 | Chandpur | 40 | 18:00 | KSRM | 25 | 23:00 | Motijheel | 26 | 13:00 | ShahCement | 32 | 16:00
35 | Chandraghona | 22 | 19:00 | Kabirpur | 173 | 18:30 | Munshiganj | 64 | 21:00 | Shahjadpur | 69 | 18:00
36 | Chapai | 45 | 19:00 | Kachua | 46 | 20:00 | Mymensingh | 155 | 18:00 | Shahjibazar | 82 | 21:00
37 | Charsaidpur | 20 | 15:00 | Kallyanpur | 72 | 13:00 | Naogaon | 93 | 18:00 | Shahmirpur | 36 | 16:00
38 | Chauddagram | 38 | 18:00 | Kalurghat | 26 | 12:00 | Narail | 37 | 18:00 | Shariatpur | 48 | 19:30
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-12-17 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 410 | 03:00 | 386 | 12:00 | Gopalganj | 415 | 03:00 | 394 | 12:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 421 | 02:00 | 381 | 12:00
| Bhulta | 414 | 03:00 | 401 | 12:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 422 | 04:00 | 405 | 11:00 | Payra | 420 | 03:00 | 408 | 12:00
| BIPTC | 407 | 00:00 | 397 | 09:00 | Rahanpur | 413 | 03:00 | 404 | 08:00
| Bogura | N/A | N/A | N/A | N/A | Rampal | 416 | 03:00 | 396 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 243 | 04:00 | 224 | 12:00 | Hasnabad | 243 | 01:00 | 226 | 12:00
| AKSML | 232 | 00:00 | 224 | 11:00 | Hathazari | 231 | 17:00 | 223 | 12:00
| Aminbazar | 242 | 00:00 | 226 | 11:00 | Ishurdi | 240 | 03:00 | 224 | 12:00
| Ashuganj | 240 | 05:00 | 232 | 12:00 | Jhenaidah | 239 | 03:00 | 222 | 12:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 240 | 02:00 | 218 | 12:00
| Baghabari | 237 | 02:00 | 224 | 11:00 | Keranigonj | 242 | 03:00 | 225 | 12:00
| Barapukuria | 224 | 04:00 | 216 | 08:00 | Khulna(S) | 244 | 02:00 | 228 | 12:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 244 | 02:00 | 238 | 13:00 | Maniknagar | 242 | 00:00 | 231 | 12:00
| Bheramara | 238 | 03:00 | 221 | 12:00 | Meghnaghat | 248 | 15:00 | 238 | 12:00
| Bhulta | 246 | 04:00 | 233 | 12:00 | Mirsorai | 235 | 05:00 | 228 | 10:00
| Bibiana | 240 | 00:00 | 232 | 11:00 | Rajshahi | 237 | 05:00 | 221 | 12:00
| BIPTC | 239 | 03:00 | 222 | 12:00 | Rampal | 241 | 03:00 | 226 | 12:00
| Bogura | 235 | 03:00 | 223 | 13:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 246 | 01:00 | 240 | 18:30 | Rampura | 244 | 04:00 | 231 | 12:00
| BSRM | 235 | 03:00 | 228 | 12:00 | Shikalbaha | 228 | 18:00 | 221 | 00:00
| Cumilla(N) | 240 | 03:00 | 229 | 12:00 | Shyampur | 244 | 03:00 | 229 | 12:00
| Fenchuganj | 244 | 17:00 | 234 | 01:00 | Siddhirganj | 247 | 05:00 | 234 | 15:00
| Ghorashal | 246 | 04:00 | 235 | 14:00 | Sirajgonj | 242 | 05:00 | 231 | 12:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 240 | 05:00 | 230 | 19:30
| GPH | 231 | 02:00 | 225 | 11:00 | Tongi | 236 | 00:00 | 218 | 11:00
| Haripur | 241 | 02:00 | 231 | 12:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 139 | 04:00 | 130 | 12:00 | Lalbag | 140 | 04:00 | 128 | 13:00
| Agargaon | 143 | 02:00 | 130 | 12:00 | Lalmonirhat | 130 | 02:00 | 120 | 08:00
| Agrabad | 137 | 04:00 | 132 | 11:00 | Madanganj | 138 | 00:00 | 130 | 12:00
| AKS | 134 | 17:00 | 130 | 10:00 | Madaripur | 136 | 00:00 | 130 | 11:00
| Aminbazar | 137 | 00:00 | 128 | 12:00 | Madartek | 138 | 02:00 | 130 | 12:00
| Amnura | 137 | 03:00 | 129 | 12:00 | Madunaghat | 137 | 03:00 | 132 | 10:00
| Ashuganj | 142 | 01:00 | 140 | 00:00 | Magura | 139 | 00:00 | 129 | 12:00
| Bagerhat | 133 | 00:00 | 124 | 12:00 | Mahasthangarh | 137 | 06:00 | 126 | 12:00
| Bakulia | 138 | 17:00 | 132 | 11:00 | Manikganj | 136 | 04:00 | 121 | 11:00
| Banani | 142 | 01:00 | 127 | 12:00 | Maniknagar | 136 | 00:00 | 128 | 12:00
| Bangabhaban | 137 | 06:00 | 128 | 12:00 | Matarbari | 130 | 03:00 | 124 | 11:00
| Barapukuria | 135 | 04:00 | 127 | 08:00 | Matuail | 139 | 04:00 | 131 | 12:00
| Barguna | 138 | 04:00 | 133 | 12:00 | Millgate | 142 | 03:00 | 126 | 12:00
| Barishal | 140 | 04:00 | 130 | 12:00 | Mirpur | 137 | 01:00 | 126 | 11:00
| Barishal-230 | 140 | 01:00 | 135 | 21:00 | Mirzapur | 137 | 03:00 | 125 | 11:00
| Baroaulia | 136 | 17:00 | 132 | 11:00 | Mithapukur | 134 | 02:00 | 126 | 15:00
| Baroirhat | 136 | 17:00 | 130 | 11:00 | MI_Cement | 140 | 03:00 | 130.6 | 12:00
| Bashundhara | 142 | 02:00 | 127 | 11:00 | Modern | 137 | 18:30 | 132 | 12:00
| BashundharaCement | 138 | 00:00 | 130 | 12:00 | Mogbazar | 140 | 03:00 | 138 | 00:00
| Beanibazar | 135 | 04:00 | 131 | 12:00 | Mongla | 133 | 01:00 | 123 | 12:00
| Benapole | 138 | 02:00 | 125 | 12:00 | Motijheel | 137 | 06:00 | 128 | 12:00
| Bhaluka | 134 | 17:00 | 128 | 12:00 | Munshiganj | 139 | 03:00 | 131 | 12:00
| Bhandaria | 136 | 04:00 | 130 | 10:00 | Mymensingh | 138 | 17:00 | 127 | 08:00
| Bhangura | 142 | 03:00 | 131 | 12:00 | Naogaon | 135 | 05:00 | 124 | 12:00
| Bheramara | 139 | 04:00 | 128 | 12:00 | Narail | 140 | 06:00 | 129 | 12:00
| Bheramara(GK) | 137 | 00:00 | 129 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 129 | 00:00 | 122 | 11:00 | Narshingdi | 136 | 01:00 | 125 | 12:00
| Bog-Sherpur | 139 | 03:00 | 126 | 12:00 | Natore | 138 | 03:00 | 129 | 12:00
| Bogura | 138 | 05:00 | 127 | 12:00 | Nawabganj | 139 | 04:00 | 127 | 12:00
| Bogura-230 | 138 | 03:00 | 128 | 12:00 | Netrakona | 136 | 22:00 | 129 | 08:00
| Brahmanbaria | 135 | 01:00 | 129 | 12:00 | New | 142 | 00:00 | 126 | 12:00
| Cantonment | 143 | 02:00 | 130 | 12:00 | Niamatpur | 134 | 05:00 | 123 | 12:00
| Chandpur | 139 | 17:00 | 129 | 12:00 | Noapara | 137 | 04:00 | 124 | 12:00
| Chandraghona | 137 | 05:00 | 132 | 12:00 | Pabna | 141 | 03:00 | 131 | 12:00
| Chapai | 137 | 04:00 | 131 | 20:00 | Palashbari | 135 | 03:00 | 123 | 08:00
| Charsaidpur | 140 | 02:00 | 131 | 12:00 | Panchagarh | 132 | 04:00 | 115 | 12:00
| Chauddagram | 139 | 18:00 | 130 | 11:00 | Patuakhali | 138 | 19:30 | 132 | 12:00
| Chhatak | 134 | 00:00 | 132 | 12:00 | Payra | 139 | 02:00 | 134 | 12:00
| Chowmuhani | 136 | 17:00 | 126 | 12:00 | PHP | 137 | 17:00 | 128 | 12:00
| Chuadanga | 138 | 03:00 | 127 | 12:00 | Postogola | 142 | 02:00 | 132 | 11:00
| Coxsbazar | 133 | 09:00 | 120 | 11:00 | Purbachal | 143 | 02:00 | 126 | 12:00
| Cumilla(N) | 141 | 17:00 | 133 | 12:00 | Purbasadipur | 132 | 17:00 | 117 | 08:00
| Cumilla(S) | 139 | 17:00 | 130 | 10:00 | Rahanpur | 137 | 02:00 | 133 | 08:00
| Daudkandi | 137 | 05:00 | 130 | 12:00 | Rahim | 138 | 02:00 | 131 | 12:00
| Dhaka | 138 | 03:00 | 130 | 12:00 | Rajbari | 137 | 03:00 | 127 | 12:00
| Dhamrai | 140 | 02:00 | 126 | 11:00 | Rajendrapur | 138 | 04:00 | 119 | 12:00
| Dhanmondi | 140 | 05:00 | 132 | 12:00 | Rajshahi | 137 | 03:00 | 129 | 12:00
| Dohazari | 134 | 00:00 | 131 | 12:00 | Rajshahi-230 | 138 | 04:00 | 127 | 06:00
| Faridpur | 135 | 00:00 | 129 | 12:00 | Ramganj | 135 | 17:00 | 126 | 12:00
| Fatullah | 140 | 01:00 | 132 | 12:00 | Rampur | 136 | 03:00 | 132 | 10:00
| Fenchuganj | 138 | 00:00 | 135 | 12:00 | Rampura | 139 | 03:00 | 130 | 12:00
| Feni | 136 | 18:00 | 130 | 12:00 | Rangamati | 137 | 04:00 | 131 | 12:00
| Ghorashal | 145 | 04:00 | 140 | 08:00 | Rangpur | 132 | 02:00 | 124 | 15:00
| Goalpara | 137 | 03:00 | 127 | 12:00 | Ruppur | 140 | 04:00 | 132 | 12:00
| Gollamari | 135 | 03:00 | 126 | 12:00 | Saidpur | 132 | 05:00 | 121 | 08:00
| Gopalganj | 135 | 03:00 | 127 | 12:00 | Satkhira | 135 | 04:00 | 130 | 19:30
| Gopalganj-400 | 136 | 03:00 | 128 | 12:00 | Satmasjid | 143 | 03:00 | 130 | 12:00
| Gulshan | 138 | 03:00 | 131 | 11:00 | Savar | 137 | 02:00 | 124 | 11:00
| Halishahar | 137 | 17:00 | 132 | 11:00 | SevenRings | 146 | 03:00 | 139 | 12:00
| Haripur | 138 | 02:00 | 131 | 12:00 | ShahCement | 140 | 02:00 | 131 | 12:00
| HaripurSBU | 138 | 02:00 | 131 | 12:00 | Shahjadpur | 143 | 03:00 | 136 | 10:00
| Hasnabad | 140 | 00:00 | 132 | 12:00 | Shahjibazar | 135 | 04:00 | 130 | 12:00
| Hathazari | 138 | 17:00 | 132 | 06:00 | Shahmirpur | 137 | 17:00 | 133 | 11:00
| Ishurdi | 141 | 04:00 | 132 | 12:00 | Shariatpur | 136 | 03:00 | 127 | 12:00
| Jaldhaka | 132 | 04:00 | 121 | 08:00 | Sherpur | 136 | 19:30 | 122 | 16:00
| Jamalpur | 137 | 19:30 | 126 | 16:00 | Shikalbaha | 126 | 03:00 | 121 | 11:00
| Jashore | 137 | 05:00 | 125 | 12:00 | Shikalbaha-230 | 138 | 03:00 | 133 | 12:00
| Jhenaidah | 139 | 00:00 | 130 | 12:00 | Shitalakhya | 140 | 03:00 | 130.6 | 12:00
| Jhenaidah-230 | 142 | 03:00 | 130 | 12:00 | Sholosohor | 136 | 02:00 | 132 | 11:00
| Joydebpur | 144 | 03:00 | 135 | 08:00 | Shyampur | 139 | 02:00 | 131 | 12:00
| Joypurhat | 137 | 06:00 | 124 | 12:00 | Shyampur-230 | 141 | 03:00 | 132 | 11:00
| Juldah | 137 | 02:00 | 133 | 11:00 | Siddhirganj | 138 | 00:00 | 131 | 12:00
| Kabirpur | 138 | 01:00 | 123 | 11:00 | Sirajganj | 138 | 00:00 | 127 | 16:00
| Kachua | 139 | 17:00 | 129 | 12:00 | Sonargaon | 138 | 03:00 | 131 | 15:00
| Kaliakoir | 141 | 02:00 | 126 | 11:00 | Sreemongol | 134 | 00:00 | 131 | 11:00
| Kallyanpur | 139 | 01:00 | 129 | 14:00 | Sreepur | 137 | 02:00 | 130 | 12:00
| Kalurghat | 137 | 19:30 | 132 | 02:00 | Srinagar | 139 | 04:00 | 127 | 12:00
| Kamrangirchar | 138 | 00:00 | 128 | 12:00 | SSM | 140 | 01:00 | 136 | 11:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 134 | 05:00 | 130 | 18:00
| Kazla | 136 | 00:00 | 128 | 12:00 | Sylhet | 135 | 01:00 | 133 | 12:00
| Keranigonj | 139 | 02:00 | 128 | 12:00 | Sylhet-132 | 135 | 00:00 | 133 | 11:00
| Khagrachori | 137 | 03:00 | 132 | 12:00 | Tangail | 136 | 04:00 | 125 | 16:00
| Khulna | 134 | 02:00 | 125 | 12:00 | Thakurgaon | 132 | 04:00 | 116 | 12:00
| Khulna(S) | 135 | 02:00 | 126 | 12:00 | TK | 137 | 14:00 | 132 | 12:00
| Khulshi | 136 | 17:00 | 130 | 12:00 | Tongi | 142 | 00:00 | 131 | 11:00
| Kishoreganj | 137 | 00:00 | 133 | 12:00 | Ullon | 137 | 00:00 | 130 | 12:00
| Kodda | 143 | 02:00 | 120 | 15:00 | Uttara | 138 | 03:00 | 125 | 12:00
| KSRM | 137 | 17:00 | 130 | 02:00 | UttaraNew | 143 | 04:00 | 126 | 12:00
| Kulaura | 137 | 01:00 | 134 | 11:00 | Zigatola | 140 | 04:00 | 134 | 18:30
| Kurigram | 131 | 04:00 | 118 | 08:00
| Kushtia | 139 | 02:00 | 129 | 12:00
19

## L-Curve
Date | 2023-12-17
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 210 | 4422 | 3261 | 7683 |  |  |  | QF-LDC-11
0:30 | 220 | 4079 | 2988.5 | 7067.5 | Date: | 2023-12-17
1:00 | 230 | 3736 | 2716 | 6452
1:30 | 225 | 3676.5 | 2634 | 6310.5
2:00 | 220 | 3617 | 2552 | 6169
2:30 | 205 | 3524 | 2521 | 6045 | [5 empty] | Gen. at Eve. Peak | 9648 | 9648 MW (19:00 )
3:00 | 190 | 3431 | 2490 | 5921 | [6 empty] | 19:00
3:30 | 192 | 3335 | 2472 | 5807 | [5 empty] | Gen. at Day Peak | 8567 | 8567 MW (12:00 )
4:00 | 194 | 3239 | 2454 | 5693 | [6 empty] | 12:00
4:30 | 192 | 3221 | 2443 | 5664 | [5 empty] | Highest Generation | 9648
5:00 | 190 | 3203 | 2432 | 5635 | [6 empty] | 19:00
5:30 | 170 | 3410.5 | 2462.5 | 5873
6:00 | 150 | 3618 | 2493 | 6111
6:30 | 139 | 3804.5 | 2570 | 6374.5
7:00 | 128 | 3991 | 2647 | 6638
7:30 | 184 | 4167 | 2930 | 7097
8:00 | 240 | 4343 | 3213 | 7556
8:30 | 290 | 4386.5 | 3330 | 7716.5
9:00 | 340 | 4430 | 3447 | 7877
9:30 | 355 | 4468.5 | 3454.5 | 7923
10:00 | 370 | 4507 | 3462 | 7969
10:30 | 410 | 4555 | 3479.5 | 8034.5
11:00 | 450 | 4603 | 3497 | 8100
11:30 | 451 | 4728.5 | 3605 | 8333.5
12:00 | 452 | 4854 | 3713 | 8567
12:30 | 386 | 4916.5 | 3752 | 8668.5
13:00 | 320 | 4979 | 3791 | 8770
13:30 | 353 | 4916 | 3718.5 | 8634.5
14:00 | 386 | 4853 | 3646 | 8499
14:30 | 440 | 4725 | 3526 | 8251
15:00 | 494 | 4597 | 3406 | 8003
15:30 | 475 | 4598 | 3357.5 | 7955.5
16:00 | 456 | 4599 | 3309 | 7908
16:30 | 453 | 4677.5 | 3395.5 | 8073
17:00 | 450 | 4756 | 3482 | 8238
17:30 | 325 | 5149.5 | 3788.5 | 8938
18:00 | 200 | 5543 | 4095 | 9638
18:30 | 190 | 5592 | 4051 | 9643
19:00 | 180 | 5641 | 4007 | 9648
19:30 | 190 | 5521 | 4059 | 9580
20:00 | 240 | 5319 | 4046 | 9365 |  |  |  | Executive Engineer
20:30 | 265 | 5216.5 | 4024 | 9240.5 |  |  |  | Network Operation Division
21:00 | 290 | 5114 | 4002 | 9116
21:30 | 325 | 4946.5 | 3979.5 | 8926
22:00 | 360 | 4779 | 3957 | 8736 |  |  |  |  | Page 6 of 7
22:30 | 335 | 4705.5 | 3757.5 | 8463
23:00 | 310 | 4632 | 3558 | 8190
23:30 | 260 | 4527 | 3409.5 | 7936.5
24:00 | 210 | 4422 | 3261 | 7683
9648 MW (19:00 )
8567 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-12-17 |  | Energy |  | 189311222
QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE | Date | 2023-12-17
0:00 | 3066 | 725 | 1574 | 0 | 0 | 2139 | 92 | 0 | 0 | 82 | 0 | 5 | 0
0:30 | 2939 | 658.5 | 1327.5 | 0 | 0 | 1969 | 92 | 0 | 0 | 76 | 0 | 5.5 | 0 |  |  | Date: | 43815
1:00 | 2812 | 592 | 1081 | 0 | 0 | 1799 | 92 | 0 | 0 | 70 | 0 | 6 | 0
1:30 | 2765.5 | 588 | 1046.5 | 0 | 0 | 1743 | 92 | 0 | 0 | 69 | 0 | 6.5 | 0 | [9 empty] | Total Energy | 189.3112 | 189.3112 | Total Energy Gen 189.311 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 189.311 MKWHr
2:00 | 2719 | 584 | 1012 | 0 | 0 | 1687 | 92 | 0 | 0 | 68 | 0 | 7 | 0 | [9 empty] | Energy not Served | 0 | 0
2:30 | 2638 | 584 | 983.5 | 0 | 0 | 1674.5 | 92 | 0 | 0 | 66 | 0 | 7 | 0 | [9 empty] | Energy Requirement | 189.3112 | 189.3112
3:00 | 2557 | 584 | 955 | 0 | 0 | 1662 | 92 | 0 | 0 | 64 | 0 | 7 | 0
3:30 | 2495 | 584 | 932 | 0 | 0 | 1656.5 | 69 | 0 | 0 | 62 | 0 | 8.5 | 0 | [8 empty] | Shortage
4:00 | 2433 | 584 | 909 | 0 | 0 | 1651 | 46 | 0 | 0 | 60 | 0 | 10 | 0
4:30 | 2433 | 584 | 879 | 0 | 0 | 1652.5 | 46 | 0 | 0 | 60 | 0 | 9.5 | 0
5:00 | 2433 | 584 | 849 | 0 | 0 | 1654 | 46 | 0 | 0 | 60 | 0 | 9 | 0
5:30 | 2579 | 583.5 | 938 | 0 | 0 | 1654 | 46 | 0 | 0 | 61 | 0 | 11.5 | 0
6:00 | 2725 | 583 | 1027 | 0 | 0 | 1654 | 46 | 0 | 0 | 62 | 0 | 14 | 0
6:30 | 2874.5 | 536.5 | 1130 | 0 | 0 | 1709 | 46 | 0 | 0 | 62 | 4.5 | 12 | 0 | [7 empty] | Coal
7:00 | 3024 | 490 | 1233 | 0 | 0 | 1764 | 46 | 0 | 0 | 62 | 9 | 10 | 0
7:30 | 3067.5 | 598 | 1358.5 | 0 | 12 | 1891 | 46 | 0 | 0 | 68 | 48 | 8 | 0 | [6 empty] | Oil
8:00 | 3111 | 706 | 1484 | 0 | 24 | 2018 | 46 | 0 | 0 | 74 | 87 | 6 | 0
8:30 | 3092.5 | 785 | 1432 | 0 | 69.5 | 2067 | 46 | 0 | 0 | 78 | 143 | 3.5 | 0
9:00 | 3074 | 864 | 1380 | 0 | 115 | 2116 | 46 | 0 | 0 | 82 | 199 | 1 | 0
9:30 | 3036.5 | 864 | 1378.5 | 0 | 137.5 | 2127.5 | 46 | 0 | 0 | 83 | 249.5 | 0.5 | 0
10:00 | 2999 | 864 | 1377 | 0 | 160 | 2139 | 46 | 0 | 0 | 84 | 300 | 0 | 0
10:30 | 3049.5 | 864.5 | 1375.5 | 0 | 169.5 | 2110 | 46 | 0 | 0 | 89 | 330.5 | 0 | 0
11:00 | 3100 | 865 | 1374 | 0 | 179 | 2081 | 46 | 0 | 0 | 94 | 361 | 0 | 0
11:30 | 3147.5 | 864 | 1467 | 0 | 232 | 2108.5 | 46 | 0 | 4 | 94 | 370.5 | 0 | 0
12:00 | 3195 | 863 | 1560 | 0 | 285 | 2136 | 46 | 0 | 8 | 94 | 380 | 0 | 0
12:30 | 3108.5 | 863 | 1567 | 0 | 397.5 | 2191 | 46 | 0 | 38 | 94 | 363.5 | 0 | 0
13:00 | 3022 | 863 | 1574 | 0 | 510 | 2246 | 46 | 0 | 68 | 94 | 347 | 0 | 0
13:30 | 3022 | 863 | 1574 | 0 | 510 | 2246 | 46 | 0 | 68 | 94 | 347 | 0 | 0
14:00 | 3022 | 863 | 1574 | 0 | 510 | 2246 | 46 | 0 | 68 | 94 | 347 | 0 | 0
14:30 | 2961 | 863 | 1490 | 0 | 437.5 | 2148 | 66 | 0 | 59 | 88 | 274 | 0 | 0
15:00 | 2900 | 863 | 1406 | 0 | 365 | 2050 | 86 | 0 | 50 | 82 | 201 | 0 | 0
15:30 | 2906.5 | 863 | 1446 | 0 | 335.5 | 2043.5 | 86 | 0 | 49 | 82 | 143 | 1 | 0
16:00 | 2913 | 863 | 1486 | 0 | 306 | 2037 | 86 | 0 | 48 | 82 | 85 | 2 | 0
16:30 | 2830 | 862.5 | 1382.5 | 0 | 601 | 2083.5 | 86 | 0 | 94 | 86 | 45.5 | 2 | 0
17:00 | 2747 | 862 | 1279 | 0 | 896 | 2130 | 86 | 0 | 140 | 90 | 6 | 2 | 0
17:30 | 2806.5 | 839 | 1374.5 | 0 | 1230 | 2304 | 86 | 0 | 203 | 89 | 3 | 3 | 0
18:00 | 2866 | 816 | 1470 | 0 | 1564 | 2478 | 86 | 0 | 266 | 88 | 0 | 4 | 0
18:30 | 3021 | 816 | 1505.5 | 0 | 1431.5 | 2509.5 | 89 | 0 | 176 | 90 | 0 | 4.5 | 0
19:00 | 3176 | 816 | 1541 | 0 | 1299 | 2541 | 92 | 0 | 86 | 92 | 0 | 5 | 0
19:30 | 3242 | 911 | 1501 | 0 | 1098 | 2564 | 92 | 0 | 75 | 92 | 0 | 5 | 0
20:00 | 3210 | 910 | 1640 | 0 | 860 | 2560 | 92 | 0 | 0 | 90 | 0 | 3 | 0
20:30 | 3191 | 910 | 1612.5 | 0 | 778 | 2562 | 92 | 0 | 0 | 93 | 0 | 2 | 0
21:00 | 3172 | 910 | 1585 | 0 | 696 | 2564 | 92 | 0 | 0 | 96 | 0 | 1 | 0
21:30 | 3125 | 910.5 | 1594 | 0 | 572 | 2536 | 92 | 0 | 0 | 93 | 0 | 3.5 | 0
22:00 | 3078 | 911 | 1603 | 0 | 448 | 2508 | 92 | 0 | 0 | 90 | 0 | 6 | 0
22:30 | 3120.5 | 911 | 1608.5 | 0 | 273 | 2363.5 | 92 | 0 | 0 | 90 | 0 | 4.5 | 0
23:00 | 3163 | 911 | 1614 | 0 | 98 | 2219 | 92 | 0 | 0 | 90 | 0 | 3 | 0
23:30 | 3114.5 | 818 | 1594 | 0 | 49 | 2179 | 92 | 0 | 0 | 86 | 0 | 4 | 0 |  |  | Max Temp. in Dhaka |  | 26.7°C
24:00 | 3066 | 725 | 1574 | 0 | 0 | 2139 | 92 | 0 | 0 | 82 | 0 | 5 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 189.311 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 189.311 MKWHr
Note on W13: Author:

## Generation
g | 2023-12-17
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 92 | 92 | 92 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 86 | 86 | 86 | 86 |  | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 1607040
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 90 |  | 100 | 100 | 102 | 100 | 100 | 90 | 93 | 1900000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [12 empty] | 7 | 8 |  |  | 2 | 15 |  | 17 | 17 |  |  |  |  | 0 | 71029
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 | 8 | 15 | 18 | 20 | 20 | 19 | 16 | 12 | 7 | 0 | [9 empty] | 136350
6 | Sikalbaha 225MW CCPP (Gas) | 221 | 223 | 223 | 194 | 194 | 226 | 226 | 225 | 226 | 226 | 227 | 228 | 228 | 229 | 221 | 221 | 218 | 218 |  | 218 | 218 | 218 | 224 | 223 | 227 | 225 | 5185865
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
Dohazari -Kalaish 100 MW Peaking
12 | Hathazari 100 MW peaking PP | [16 empty] | 37 | 41 | [8 empty] | 71712
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [11 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 198218
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [19 empty] | 97 | 186 | 101 | 105 | 62 | 140 | 138 | 649000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [11 empty] | 12 | 43 | 45 | 15 | 15 | 15 | 117 |  | 45 | 15 |  |  |  |  | 0 | 451636
19 | Ashuganj 195 MW PP (APSCL-United) | 16 | 8 | 8 | 8 | 8 | 8 | 16 | 45 | 45 | 45 | 45 | 73 | 73 | 73 | 73 | 73 | 73 | 73 |  | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 1221090
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 160 | 160 | 160 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 337 | 320 | 315 | 300 | 305 | 305 | 320 | 352 | 350 | 350 | 349 | 350 | 349 | 349 | 349 | 350 | 349 | 400 |  | 400 | 400 | 404 | 400 | 350 | 350 | 350 | 8410908
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 48 | 25 | 25 | 25 | 25 | 48 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 45 | 41 | 41 | 47 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 1046808
33 | Ashuganj 225 MW CCPP
34 | Ashuganj 450 MW CCPP(South) | 280 | 280 | 280 | 250 | 250 | 280 | 375 | 340 | 310 | 275 | 275 | 345 | 320 | 275 | 325 | 320 | 280 | 290 |  | 295 | 280 | 290 | 310 | 280 | 305 | 270 | 7137000
Ashuganj 450 MW CCPP(North)
| Ashuganj 420 MW CCPP(East) | 300 | 300 | 250 | 230 | 230 | 260 | 300 | 350 | 320 | 305 | 340 | 375 | 380 | 320 | 320 | 320 | 280 | 330 |  | 393 | 393 | 385 | 390 | 385 | 392 | 390 | 8002600
35 | Ashuganj 55 MW PP (Precision) | 6 | 6 | 6 | [5 empty] | 10 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 408960
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 342 | 334 | 304 | 304 | 304 | 332 | 352 | 374 | 404 | 400 | 384 | 386 | 400 | 393 | 375 | 381 | 395 | 313 |  | 402 | 399 | 401 | 400 | 399 | 352 | 352 | 8881200
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 300 | 300 | 300 | 300 | 250 | 280 | 320 | 400 | 400 | 400 | 370 | 420 | 420 | 370 | 370 | 400 | 320 | 350 |  | 420 | 420 | 450 | 450 | 450 | 450 | 450 | 9204600
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 218 | 218 | 148 | 147 | 147 | 219 | 218 | 218 | 217 | 217 | 212 | 190 | 147 | 148 | 111 | 112 | 111 | 112 |  | 112 | 112 | 112 | 112 | 113 | 112 | 73 | 3733440
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 5 | 11 | 27 | 41 | 43 | 41 | 32 | 22 | 9 | 1 | [9 empty] | 233590
44 | Fenchugonj CCPP Phase-1 | 42 | 42 | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 1006000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 64 | 63 | 63 | 62 | 62 | 62 | 61 | 61 | 40 | 40 | 40 | 40 | 62 |  | 63 | 63 | 63 | 62 | 63 | 66 | 67 | 1304352
48 | Shahjibazar 86 MW PP (Shahjibazar) | [7 empty] | 20 | 20 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 517440
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 128 | 128 | 128 | 128 | 128 | 128 |  | 128 | 128 | 128 | 130 | 130 | 130 | 130 | 3108030
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [5 empty] | 10 | 10 | 10 | 10 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 183960
54 | Hobiganj 11 MW PP Cofidence-E | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 3 |  | 5 | 5 | 8 | 5 | 5 | 5 | 8 | 159310
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 |  |  |  | 10 | 44 | 49 | 51 | 51 | 51 | 51 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 933000
56 | Shahjahanulla 25 MW PP | [5 empty] | 8 | 8 | 16 | 16 | 16 | 16 | 8 | 8 | 8 | 8 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 248640
57 | Bibiana-II 341 MW CCPP (Summit)
| Bibiyana South 400 MW | 400 | 350 | 330 | 330 | 330 | 360 | 360 | 400 | 400 | 400 | 400 | 400 | 400 | 360 | 350 | 370 | 340 | 375 |  | 400 | 400 | 400 | 380 | 400 | 400 | 400 | 9036500
58 | Nababganj 55 MW PP (Southern power ) | [11 empty] | 5 | 17 | 17 |  |  | 17 | 17 |  | 17 | 17 | 17 | 17 |  |  | 0 | 137101
59 | Tangail Palli Power Gen 22 MW | [12 empty] | 3 | 6 | 6 | 6 | 6 | 4 |  | 4 | 6 | 6 |  |  |  | 0 | 49440
60 | Barabkunda 22 MW PP (Regent) | 11 | 11 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 271632
61 | Narshingdi 22 MW PP (Doreen) | 15 | 15 | 15 | 10 | 10 | 10 | 10 | 10 | 10 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 10 | 10 | 10 | 10 | 10 | 10 | 268812
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 70 | 68 | 64 | 60 | 60 | 62 | 62 | 74 | 82 | 84 | 94 | 94 | 94 | 96 | 82 | 82 | 90 | 88 |  | 92 | 92 | 90 | 96 | 90 | 90 | 82 | 1938240
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 34 | 19 | 12 | 12 | 11 | 13 | 17 | 13 | 12 | 12 | 15 | 20 |  | 24 | 17 | 25 | 29 | 31 | 34 | 25 | 652320
65 | Feni 22 MW PP (Doreen) | [6 empty] | 15 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 318922
66 | Feni 11 MW PP (Doreen) | [6 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 184320
67 | Jangalia 33 MW PP (Summit) | [5 empty] | 7 | 33 | 33 | 33 | 33 | 33 |  |  |  | 21 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 484400
68 | Cumilla 25 MW PP (Summit) | 11 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 12 | 11 | 191930
69 | Summit Ashulia | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 22 | 22 | 22 | 22 | 22 | 21 | 20 |  | 17 | 17 | 15 | 15 | 15 | 15 | 20 | 48000
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 15 | 22 | 22 | 22 | 22 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 22 | 22 | 465480
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 25 | 25 | 25 | 25 | 21 | 21 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 527500
72 | Rupganj 33 MW PP(Summit) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 18 | 27 |  | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 716100
73 | Ghorashal 108 MW PP (Regent) | [5 empty] | 20 | 32 | 53 | 56 | 70 | 68 | 72 | 71 | 73 | 74 | 75 | 72 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1155227
| Feni Lanka Power | [12 empty] | 34 | 24 |  |  | 17 | 34 | [7 empty] | 0 | 103740
| Chowmuhani 113 MW | [11 empty] | 2 | 9 | 9 |  |  | 16 | 47 |  | 47 | 47 | 48 | 49 | 49 | 9 | 0 | 325080
| Manikgonj 162MW PP(MPGL) | [12 empty] | 17 | 17 | 35 | 35 | 35 | 54 |  | 54 | 54 | 54 | 17 | 17 |  | 0 | 361440
77 | Siddhirganj 100 PP(Dutch Bangla) | [16 empty] | 8 | 40 | [7 empty] | 0 | 64320
78 | Gazipur 52 MW PP | [9 empty] | 3 | 8 | 8 | 8 | 8 |  |  | 16 | 16 |  | 16 | 16 | 8 | 8 |  |  | 0 | 113280
79 | Kodda 150 MW PP | [11 empty] | 8 | 32 | 32 |  |  | 55 | 98 |  | 48 | 37 |  |  |  |  | 0 | 275040
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [12 empty] | 4 | 25 |  |  |  | 25 | [8 empty] | 98126
| Gazipur 100 MW PP | [7 empty] | 2 | 17 | 17 | 17 | 17 | 17 | 17 |  |  | 40 | 50 |  | 50 | 50 | 17 | 17 | 17 |  |  | 342019
| Kaptai 7 MW Solar PP | [7 empty] | 1 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 25918
| Jodiac Power | [13 empty] | 17 |  |  | 3 | 17 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 138886
| Karnaphuli Power Ltd. | [8 empty] | 7 | 17 | 15 | 4 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 |  | 247562
82 | Madanganj 102 PP(Summit) | [16 empty] | 8 | 24 |  | 17 | [5 empty] | 0 | 42746
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 16 | [7 empty] | 0 | 19667
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | [16 empty] | 3 | 24 | [7 empty] | 0 | 41280
| Meghnaghat 104 MW PP (OPCL) | [12 empty] | 1 | 12 |  |  | 15 | 46 |  | 51 | 35 | 33 | 17 |  |  | 0 | 193920
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [11 empty] | 5 | 12 | 12 |  |  | 12 | 12 | [7 empty] | 0 | 49560
92 | Fenchuganj 44 MW (Energyprima) | [5 empty] | 10 | 23 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 43 |  | 39 | 39 | 43 | 43 | 43 | 43 | 43 | 786240
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 15 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 43 | 51 | 51 | 51 | 1060362
94 | Gagnagar 102 MW PP (Digital Power) | [16 empty] | 16 | 24 | [7 empty] | 0 | 30384
95 | Patenga 50MW PP (Baraka) | [8 empty] | 2 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 10 | 19 |  | 19 | 19 | 19 | 19 | 19 | 2 | 0 | 172320
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 | [15 empty] | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [12 empty] | 15 | 35 | 15 | 15 | 15 | 46 |  | 55 | 55 | 30 |  |  |  | 0 | 309732
100 | Manikganj 55 MW PP (Northern) | [11 empty] | 17 | 17 | 35 | 35 | 35 | 35 | [8 empty] | 0 | 143846
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 120 | 120 | 120 | 120 | 120 | 140 | 140 | 140 | 120 | 120 | 163 | 120 | 120 | 163 | 120 | 163 |  | 163 | 163 | 163 | 163 | 120 | 120 | 120 | 3456900
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 11500
103 | Kamalaghat 54 MW PP(Banco Energy) | [11 empty] | 10 | 17 | 17 |  |  | 17 | 35 |  | 35 | 17 | 17 |  |  |  | 0 | 129600
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [7 empty] | 14 | 24 | 24 | 30 | 56 | 56 | 57 | 24 | 24 | 54 | 75 |  | 75 | 75 | 75 | 75 | 56 | 24 | 0 | 782400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [11 empty] | 12 | 17 | 17 | 17 | 17 | 17 | 28 |  | 44 | 45 | 45 | 44 | 17 |  |  | 291168
115 | Juldah 100 MW PP Unit-3 (Acorn) | [10 empty] | 2 | 12 | 12 | 12 |  |  | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 |  | 0 | 126720
116 | Chandpur 200 MW (Desh energy) | [8 empty] | 6 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 19 | 24 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 277920
117 | Ashuganj 150 MW PP (Midland) | [10 empty] | 5 | 6 | 20 | 50 | 50 | 6 | 23 | 112 |  | 142 | 50 | 50 | 50 |  |  | 0 | 572072
118 | Bibiyana-III 400 MW CCPP | 324 | 324 | 325 | 305 | 305 | 312 | 346 | 346 | 330 | 322 | 400 | 394 | 348 | 330 | 365 | 371 | 332 | 338 |  | 332 | 332 | 372 | 360 | 332 | 347 | 320 | 8117000
| Jamalpur 115 MW PP (United) | [7 empty] | 8 | 38 | 47 | 37 | 9 | 9 | 9 |  |  | 19 | 28 |  | 28 | 28 | 8 |  |  |  | 0 | 250800
| Anwara 300 MW PP (United) | [11 empty] | 15 | 16 | 32 | 30 | 15 | 96 | 100 |  | 100 | 100 | 50 | 15 |  |  | 0 | 526909
| Juldah unit-2 (Acorn) | [8 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 0 | 191040
| Anlima Energy Ltd. | [8 empty] | 9 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 258436
| Bhairob 54.5 MW | [12 empty] | 13 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  |  | 189720
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 7 | 16 | 23 | 27 | 29 | 28 | 27 | 16 | 7 | 0 | [9 empty] | 179682
| Chandpur 115(Doreen) | [10 empty] | 13 | 18 | 18 | 18 | 18 | 18 | 18 | 19 |  | 34 | 36 | 36 | 22 | 18 |  | 0 | 268800
| Kanchan Purbachal Power Generation Ltd. | [16 empty] | 15 | 35 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 134640
Mirsharai 150 MW (Oil)
| Mirsharai 150 MW (Gas) | [8 empty] | 10 | 36 | 36 | 36 |  | 36 | 36 | 13 |  | 10 |  | 36 | 36 | 36 |  |  |  | 0 | 301091
| Cox's Bazar Wind | 6 | 7 | 7 | 10 | 9 | 14 | 10 | 6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 4 |  | 5 | 5 | 3 | 1 | 6 | 3 | 5 | 107040
Matarbari 2*600 MW (CPGCL)
120 | Eastern Zone Total | 3736 | 3617 | 3431 | 3239 | 3203 | 3618 | 3991 | 4343 | 4430 | 4507 | 4603 | 4854 | 4979 | 4853 | 4597 | 4599 | 4756 | 5543 |  | 5641 | 5521 | 5319 | 5114 | 4779 | 4632 | 4422 | 107923608
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [16 empty] | 13 | 16 | [8 empty] | 30720
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 20 | [8 empty] | 24480
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [12 empty] | 1 | 13 | 17 | 15 | 17 | 17 | [7 empty] | 0 | 91680
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 2 | 18 | 38 | 55 | 65 | 68 | 57 | 52 | 35 | 16 | 2 | [9 empty] | 415440
131 | Rampal 1320 MW (BIFPCL) | 364 | 361 | 360 | 363 | 363 | 362 | 407 | 460 | 510 | 506 | 457 | 510 | 575 | 554 | 463 | 453 | 456 | 610 |  | 628 | 627 | 627 | 630 | 627 | 505 | 514 | 11578180
132 | United Payra Power Ltd. | [15 empty] | 2 | 35 | 45 |  | 75 | 82 | 35 | 35 |  |  | 0 | 242400
133 | Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 180 | 180 | 180 | 222 | 222 | 180 | 180 | 180 | 220 | 220 | 180 | 180 | 180 | 180 | 220 |  | 222 | 222 | 222 | 223 | 223 | 220 | 220 | 4913427
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [25 empty] | 0 | 0
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3381800
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 80 | 80 | 80 | 80 | 80 | 80 | 120 | 120 | 120 | 80 | 80 | 120 | 80 | 80 | 80 | 80 | 80 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2289000
140 | Bhola 33 MW PP (Venture) | 17 | 16 | 14 | 14 | 14 | 16 | 1 | 15 | 13 | 14 | 15 | 15 | 16 | 15 | 13 | 13 | 14 | 18 |  | 18 | 19 | 20 | 20 | 20 | 19 | 18 | 376728
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [16 empty] | 8 | 8 | [8 empty] | 14625
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 592 | 584 | 584 | 584 | 584 | 583 | 490 | 706 | 864 | 864 | 865 | 863 | 863 | 863 | 863 | 863 | 862 | 816 |  | 816 | 911 | 910 | 910 | 911 | 911 | 725 | 18834909
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 360 | 270 | 250 | 250 | 250 | 250 | 300 | 470 | 520 | 550 | 550 | 550 | 590 | 560 | 500 | 490 | 490 | 560 |  | 622 | 622 | 622 | 622 | 622 | 550 | 490 | 12428600
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4130500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 2 | 3 | 4 | 5 | 5 | 3 | 2 | 0 | [10 empty] | 30180
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 380 | 320 | 280 | 240 | 220 | 280 | 360 | 414 | 346 | 304 | 353 | 414 | 379 | 297 | 349 | 355 | 270 | 342 |  | 341 | 307 | 403 | 351 | 402 | 414 | 384 | 8377900
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 11 | 11 | 11 | 5 | 5 | 143892
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern) | [12 empty] | 8 |  |  |  | 25 | 34 | [8 empty] | 46817
167 | Katakhali 50 MW Peaking PP | [12 empty] | 36 | 50 | 50 | 48 | 48 | 48 | [8 empty] | 268858
168 | Santahar 50 MW Peaking PP | [17 empty] | 38 |  | 38 | 38 | [5 empty] | 85678
169 | Natore 52 MW PP (Rajlanka) | [11 empty] | 8 | 8 | 8 |  |  | 17 | 17 |  | 17 | 17 | 8 | 8 | 8 |  | 0 | 100546
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 21 | [7 empty] | 0 | 25712
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [12 empty] | 25 | 35 |  |  | 12 | 35 |  | 35 | 35 | 35 | 35 | 35 |  | 0 | 332352
172 | Confidence Power Bogura Unit-1 113 MW | [13 empty] | 35 |  |  | 35 | 55 |  | 55 | 55 | 55 | 55 | 35 |  | 0 | 340128
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 40 | 70 |  | 89 | 49 | 36 | 35 | 34 |  |  | 313372
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 4 | 5 | 5 | 5 | 4 | 3 | 1 | 0 | [9 empty] | 30659
178 | Energypac Power Venture Thakurgaon Ltd. | [16 empty] | 35 | 72 |  | 35 | 35 | 35 | 35 |  |  | 0 | 190080
| Intraco Solar 30 MW | [6 empty] | 0 | 5 | 15 | 22 | 27 | 30 | 26 | 21 | 15 | 6 | 0 | [9 empty] | 168601
| Adani Power Jharkhanda Ltd | 428 | 426 | 427 | 428 | 426 | 427 | 427 | 426 | 426 | 423 | 415 | 416 | 422 | 421 | 428 | 434 | 525 | 598 |  | 581 | 605 | 597 | 602 | 599 | 504 | 475 | 11121540
178 | Teesta Solar Limited | [6 empty] | 3 | 41 | 96 | 142 | 166 | 174 | 160 | 140 | 93 | 38 | 3 | [9 empty] | 1058810