## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-12-23 | Saturday
|  | Date (day): | 2023-12-23 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10516.6 | MW |  |  | (b) At Evening Peak Hour : |  | 11779 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-12-22 | 2023-12-23 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 67 | 72 | 71 | 72 | 36 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 322 | 281 | 0 | 200 | 212
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 420 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 80 | 80 |  | 22 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 17 | 15 | 55 | 0
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 45 | 45 | 30 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 15 | 15 |  | 7 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 80 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 90 | 90 |  | 10 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 90 | 90 |  | 12 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 17 | 17 | 37 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 32 | 48 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 17 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 17 | 35 | 20 |  | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 11 | 0 | 34 | 34 |  | 46 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 17 | 17 | 17 |  | 16 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 32 | 32 | 32 | 32
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 17 | 8 | 17 | 35 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 130 | 130 | 170 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 11 | 17 | 17 | 132 |  | Fuel shortage
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 17 | 17 | 105
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 0 | 17 | 17 | 87 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 0 | 0 | 162 |  | Fuel shortage
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 27 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 5763 | 5422 | 1022 | 1147 | 1639 | 1999 | 2015 | 1053
38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
39 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 0 | 8 | 17 | 8 |  | Fuel shortage
40 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 17 | 0 | 20 | 0
41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 6 | 6 | 18 | 32 |  | Fuel shortage
42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 86 | 86 | 86 | 86 | 144 |  | Low water lavel
43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 229 | 225 | 225 | 225
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 17 | 17 | 88 |  | Fuel shortage
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 40 | 60 | 38 |  | Fuel shortage
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 0 | 17 | 85 |  | Fuel shortage
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 0 | 12 | 12 | 88 |  | Fuel shortage
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 15 | 12 | 12 | 88 |  | Fuel shortage
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 15 | 15 | 15 | 7 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 17 | 16 | 10 | 20
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 30 | 100 | 200 | 100 |  | Fuel shortage
54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 17 | 17 | 37 |  | Fuel shortage
55 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 11 | 17 | 17 | 93 |  | Fuel shortage
56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 12 | 12 | 12 | 88 |  | Fuel shortage
57 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 17 | 99 |  | Fuel shortage
58 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 0 | 90 | 163
59 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 320 | 330 | 300 | 350 | 874 |  | Coal Shortage.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 1 | 0 | 10 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 587 | 585 | 580 | 585 |  |  | On test.
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 3829 | 3769 | 1309 | 1365 | 1599 | 1870 | 2157 | 330
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 0 | 0 |  | 221 | Under maint.
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 290 | 330 | 360 |  |  | FGMO
63 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 305 | 310 | 380 | 380
64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 48 | 48 | 48 | 48
65 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 0 | 51 | 36 | 50 | 50
66 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 38 | 8 | 8 | 187 |  | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 30 | 38 | 43 | 43 |  | 8 | Engine problem
68 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 8 | 6 | 150
69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 30
70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
71 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 17 | 17 | 17 | 183 |  | Fuel shortage
72 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 15 | 18 | 18 |  | 4 | Engine problem
73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 108 | 88 | 128 | 140
74 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 52 | 52
76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 11 | 10 | 10 |  | 15 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 17 | 100 | 100 | 14
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 28 | 48 | 65 |  | Fuel shortage
79 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 17 | 17 | 17 |  | 37 | Engine problem
80 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 1 | 18 | 18 | 18 | 97 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2896 | 972 | 992 | 1296 | 1532 | 546 | 808
81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 61 | 75 | 80 | 80 | 122 |  | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 28 | 9 | 28 | 172 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 75 | 57 | 79 | 36 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 48 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 6 | 6 |  |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 179 | 184 | 203.6 | 193 | 122 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 0 | 0 |  | 70 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 53 | 51 | 51
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 36 | 38 | 40 | 40
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 5 | 5 | 5 |  | 6 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 62 | 63 | 63
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 30 | 30 | 60 | 60 | 26 |  | Gas shortage
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 210 | 210 | 210 | 210 |  | 21 | Machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 22 | 24
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  | 341 | Under maint.
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 388 | 365 | 400 | 400 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1323 | 1360 | 1424 | 1426 | 26 | 958
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 707 | 718 | 721 | 818
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 0 | 16 | 99 |  | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 40
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 |  | 109 | Under maint.
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 8 | 32 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 35 | 70 | 35 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 65 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 452 | 567 | 510 | 600
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 1224 | 1285 | 1366 | 1552 | 1263 | 109
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 19 | 20 | 20 | 20 |  | 20 | Engine problem
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 80 | 118 | 120 | 120 |  | 74 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 390 | 430 | 622 | 622 |  | 622 | #01 Under maint.
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 180 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 75
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 140 | 236 | 200 | 200 | 107 |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 809 | 1024 | 1309 | 1367 | 107 | 716
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 30 | 22 |  | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 20 |  | 51 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 28 | 28
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 34 | 40 |  | 10 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 40 |  | 10 | Engine problem
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 340 | 400 | 300 | 300 |  |  | FGMO
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 38 | 12 |  | Fuel shortage
136 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 5 | 11 | 11
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 8 | 8 | 44 |  | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 50 | 82 |  | 22 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 35 | 35 | 78 |  | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 0 | 55 | 58 |  | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 573 | 762 | 720 | 760
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 924 | 1167 | 1222 | 1447 | 1235 | 93
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 50 | 113
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 0 | 70 | 110
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 168 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 411 | 170 | 458 | 393 | 125 | 189
| Total |  |  |  |  | 25951 | 25211 | 8173 | 8694 | 10516.6 | 11779 | 7596 | 4256
A. |  | 2023-12-22 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 8737 | MW at | 13:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 6628 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8694 | MW
3 | Day peak Generation : |  |  | 8173 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8402.03 | MW
4 | Evening peak Generation : |  |  | 8694 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 185.1883 | MKWHr | By Solar | 2.3127 | MKWHr
| By Gas : | 96.0345 | MKWHr |  | By Oil: | 2.2351 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 65.9479 | MKWHr |  | By Hydro: | 2.0807 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.00672 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 7596 | MW | Dhaka | 2915.23 | 2915.23 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 4256 | MW | Chittagong | 876.4 | 876.4 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 11852 | MW | Khulna | 1044 | 1044 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 704.72 | MMCFD |  |  | Rajshahi | 863 | 863 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 98060098.204 | ii) Oil : | Taka | 29243934.34 | Comilla | 758 | 758 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 393661625.4 | Total | Taka | 520965657.944 | Mymensingh | 718 | 718 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.099 | MKWHr. | Sylhet | 330 | 330 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 206 | MW (W to E) at | 18:00 | hrs | Barisal | 258.4 | 258.4 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 110 | MW at | 7:00 | hrs | Rangpur | 639 | 639 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 27.5°C |  |  | Total | 8402.03 | 8402.03 |  | 0
B. |  | 2023-12-23 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 30.5°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 11779 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8500 | MW
4 | Reserve(Generation end) |  |  |  | 2279 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 201.3607 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6197 | MW at | 4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 14.5047 | MKWHr. | ii) HVDC Flow at Peak Time |  | 718 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0659 | MKWHr. | iii) Maximum HVDC Flow : |  | 815 | MW at | 23:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 95.12 |  | (b) Today: | 94.9 |  | (c) Rule Curve: |  | 104
.

## YesterdayGen
2023-12-22 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 289 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 22 | 17 | 30 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 19 | 0 | 0 | 0 | 0 | 270 | 0 | 8 | 0 | 45 | 54 | 0 | 43 | 0 | 0 | 0 | 15 | 10 | 33 | 11 | 82 | 75 | 0 | 0 | 0 | 43 | 0 | 51 | 20 | 163 | 0 | 63 | 30 | 0 | 209 | 0 | 0 | 10 | 0 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 320 | 0 | 586 | 0 | 0 |  | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 501 | 0 | 140 | 703 | 0 | 0 |  | 4565 | 3031 | 7596 | 2743 | 480 | 1335 | 0 | 0 | 2870 | 86 | 0 | 0 | 82 | 0 | 0 | 0 | 95.17
2:00 | 0 | 0 | 0 | 180 | 0 | 69 | 0 | 278 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 22 | 17 | 30 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 16 | 0 | 0 | 0 | 0 | 270 | 0 | 8 | 0 | 47 | 54 | 0 | 43 | 0 | 0 | 0 | 15 | 0 | 33 | 11 | 66 | 75 | 0 | 0 | 0 | 43 | 0 | 51 | 20 | 163 | 0 | 61 | 30 | 0 | 209 | 0 | 0 | 10 | 0 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 320 | 0 | 584 | 0 | 0 |  | 475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 140 | 596 | 0 | 0 |  | 4520 | 2759 | 7279 | 2722 | 475 | 1312 | 0 | 0 | 2618 | 86 | 0 | 0 | 66 | 0 | 0 | 0 | 95.16
3:00 | 0 | 0 | 0 | 180 | 0 | 69 | 0 | 270 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 22 | 17 | 30 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 270 | 0 | 8 | 0 | 47 | 34 | 0 | 43 | 0 | 0 | 0 | 15 | 0 | 33 | 11 | 78 | 75 | 0 | 0 | 0 | 43 | 0 | 51 | 20 | 163 | 0 | 61 | 30 | 0 | 209 | 0 | 0 | 10 | 0 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 320 | 0 | 587 | 0 | 0 |  | 474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 140 | 505 | 0 | 0 |  | 4514 | 2549 | 7063 | 2715 | 474 | 1309 | 0 | 0 | 2401 | 86 | 0 | 0 | 78 | 0 | 0 | 0 | 95.15
4:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 259 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 22 | 17 | 27 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 34 | 0 | 0 | 0 | 0 | 270 | 0 | 8 | 0 | 47 | 6 | 0 | 43 | 0 | 0 | 0 | 15 | 0 | 33 | 11 | 72 | 75 | 0 | 0 | 0 | 43 | 0 | 5 | 5 | 120 | 0 | 61 | 30 | 0 | 209 | 0 | 0 | 10 | 0 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 320 | 0 | 585 | 0 | 0 |  | 474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 140 | 419 | 0 | 0 |  | 4283 | 2544 | 6827 | 2660 | 474 | 1232 | 0 | 0 | 2303 | 86 | 0 | 0 | 72 | 0 | 0 | 0 | 95.14
5:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 256 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 22 | 17 | 27 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 34 | 0 | 0 | 0 | 0 | 270 | 0 | 8 | 0 | 47 | 6 | 0 | 10 | 0 | 0 | 0 | 13 | 0 | 33 | 11 | 72 | 86 | 0 | 0 | 0 | 43 | 0 | 5 | 5 | 120 | 0 | 40 | 30 | 0 | 209 | 0 | 0 | 10 | 0 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 320 | 0 | 581 | 0 | 0 |  | 474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 140 | 419 | 0 | 0 |  | 4178 | 2450 | 6628 | 2611 | 474 | 1131 | 0 | 0 | 2254 | 86 | 0 | 0 | 72 | 0 | 0 | 0 | 95.13
6:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 247 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 22 | 17 | 27 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 34 | 0 | 0 | 0 | 0 | 315 | 0 | 8 | 0 | 47 | 6 | 0 | 10 | 0 | 0 | 0 | 13 | 0 | 33 | 11 | 74 | 86 | 0 | 0 | 0 | 43 | 0 | 5 | 5 | 120 | 0 | 40 | 30 | 0 | 209 | 0 | 0 | 10 | 0 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 320 | 0 | 585 | 0 | 0 |  | 474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 140 | 419 | 0 | 0 |  | 4262 | 2574 | 6836 | 2689 | 474 | 1245 | 0 | 0 | 2268 | 86 | 0 | 0 | 74 | 0 | 0 | 0 | 95.12
7:00 | 0 | 0 | 0 | 180 | 0 | 65 | 0 | 254 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 22 | 17 | 27 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 37 | 0 | 0 | 0 | 0 | 345 | 0 | 8 | 0 | 47 | 6 | 0 | 10 | 0 | 0 | 0 | 15 | 0 | 33 | 11 | 76 | 73 | 0 | 0 | 0 | 43 | 0 | 5 | 5 | 120 | 0 | 63 | 30 | 0 | 209 | 0 | 0 | 10 | 0 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 320 | 0 | 0 | 320 | 0 | 585 | 0 | 0 |  | 474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 222 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 381 | 1 | 140 | 419 | 5 | 0 |  | 4384 | 2577 | 6961 | 2750 | 474 | 1299 | 0 | 0 | 2265 | 86 | 0 | 0 | 76 | 11 | 0 | 0 | 95.11
8:00 | 0 | 0 | 0 | 180 | 0 | 65 | 0 | 273 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 22 | 17 | 27 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 38 | 0 | 0 | 0 | 0 | 305 | 0 | 8 | 0 | 47 | 15 | 0 | 43 | 0 | 0 | 0 | 15 | 0 | 33 | 11 | 78 | 71 | 0 | 0 | 1 | 43 | 0 | 42 | 42 | 163 | 0 | 63 | 30 | 0 | 209 | 0 | 0 | 10 | 0 | 22 | 8 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 6 | 0 | 0 | 0 | 333 | 57 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 13 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 360 | 0 | 0 | 320 | 0 | 585 | 0 | 0 |  | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 370 | 220 | 0 | 0 | 1 | 15 | 0 | 0 | 0 | 461 | 7 | 140 | 615 | 37 | 0 |  | 4620 | 2831 | 7451 | 2778 | 236 | 1457 | 0 | 66 | 2661 | 86 | 0 | 0 | 78 | 89 | 0 | 0 | 95.1
9:00 | 0 | 0 | 0 | 180 | 0 | 65 | 0 | 309 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 17 | 27 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 38 | 0 | 0 | 0 | 0 | 275 | 0 | 8 | 0 | 47 | 36 | 0 | 43 | 0 | 0 | 0 | 15 | 0 | 33 | 11 | 74 | 64 | 0 | 0 | 1 | 43 | 0 | 42 | 20 | 120 | 0 | 40 | 30 | 0 | 209 | 0 | 0 | 10 | 0 | 22 | 8 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 12 | 0 | 2 | 0 | 335 | 57 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 400 | 0 | 25 | 0 | 5 | 0 | 0 | 17 | 0 | 0 | 390 | 0 | 0 | 320 | 0 | 580 | 0 | 0 |  | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 430 | 180 | 0 | 0 | 1 | 35 | 0 | 0 | 0 | 430 | 18 | 140 | 604 | 101 | 0 |  | 4632 | 2825 | 7457 | 2760 | 236 | 1338 | 0 | 75 | 2674 | 86 | 0 | 0 | 74 | 214 | 0 | 0 | 95.09
10:00 | 0 | 0 | 0 | 180 | 0 | 22 | 0 | 323 | 0 |  | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 27 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 32 | 0 | 0 | 0 | 0 | 285 | 0 | 8 | 0 | 47 | 50 | 0 | 10 | 0 | 0 | 0 | 15 | 0 | 33 | 11 | 80 | 66 | 0 | 0 | 2 | 43 | 0 | 20 | 20 | 163 | 0 | 40 | 10 | 0 | 210 | 0 | 0 | 10 | 0 | 22 | 8 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 15 | 0 | 17 | 0 | 325 | 57 | 0 | 0 | 2 | 0 | 0 | 16 | 0 | 0 | 0 | 400 | 0 | 41 | 0 | 17 | 0 | 0 | 24 | 0 | 0 | 350 | 0 | 0 | 320 | 0 | 584 | 0 | 0 |  | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 400 | 180 | 0 | 0 | 2 | 50 | 0 | 0 | 0 | 379 | 25 | 140 | 616 | 139 | 0 |  | 4639 | 2777 | 7416 | 2726 | 236 | 1259 | 0 | 116 | 2609 | 86 | 0 | 0 | 80 | 304 | 0 | 0 | 95.08
11:00 | 0 | 0 | 0 | 180 | 0 | 22 | 0 | 322 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 32 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 31 | 0 | 0 | 0 | 0 | 275 | 0 | 8 | 0 | 47 | 53 | 0 | 10 | 0 | 0 | 0 | 15 | 0 | 33 | 11 | 90 | 61 | 0 | 0 | 2 | 43 | 0 | 20 | 20 | 130 | 0 | 40 | 10 | 0 | 210 | 0 | 0 | 9 | 0 | 22 | 8 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 17 | 0 | 17 | 0 | 320 | 59 | 0 | 0 | 2 | 0 | 0 | 17 | 0 | 0 | 0 | 360 | 0 | 43 | 0 | 17 | 0 | 0 | 21 | 0 | 0 | 300 | 0 | 0 | 320 | 3 | 584 | 0 | 0 |  | 680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 380 | 180 | 0 | 0 | 4 | 64 | 0 | 0 | 0 | 378 | 30 | 140 | 518 | 165 | 0 |  | 4489 | 3137 | 7626 | 2627 | 680 | 1178 | 0 | 119 | 2490 | 86 | 0 | 0 | 90 | 353 | 3 | 0 | 95.07
12:00 | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 322 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 17 | 32 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 17 | 0 | 0 | 0 | 0 | 345 | 0 | 8 | 0 | 48 | 51 | 0 | 30 | 0 | 0 | 0 | 15 | 0 | 33 | 11 | 108 | 61 | 0 | 0 | 2 | 0 | 0 | 48 | 36 | 130 | 0 | 40 | 30 | 0 | 210 | 0 | 0 | 9 | 0 | 24 | 8 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 17 | 0 | 17 | 0 | 388 | 59 | 0 | 0 | 3 | 0 | 0 | 17 | 0 | 0 | 0 | 400 | 0 | 48 | 0 | 17 | 0 | 0 | 27 | 1 | 0 | 305 | 0 | 0 | 320 | 1 | 587 | 0 | 0 |  | 707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 390 | 180 | 0 | 0 | 3 | 65 | 35 | 0 | 0 | 452 | 33 | 140 | 573 | 168 | 0 |  | 4805 | 3368 | 8173 | 2782 | 707 | 1315 | 0 | 155 | 2632 | 86 | 0 | 16 | 108 | 371 | 1 | 0 | 95.06
13:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 348 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 32 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 201 | 0 | 0 | 0 |  | 6 | 0 | 4 | 0 | 0 | 3 | 15 | 8 | 0 | 0 | 0 | 0 | 280 | 0 | 45 | 0 | 48 | 49 | 0 | 43 | 0 | 0 | 9 | 15 | 0 | 33 | 11 | 112 | 61 | 0 | 0 | 2 | 0 | 0 | 51 | 42 | 130 | 0 | 62 | 30 | 0 | 210 | 0 | 0 | 10 | 0 | 24 | 8 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 17 | 0 | 17 | 1 | 332 | 59 | 18 | 0 | 2 | 0 | 0 | 17 | 23 | 0 | 12 | 370 | 0 | 46 | 0 | 17 | 0 | 14 | 27 | 17 | 0 | 370 | 0 | 0 | 350 | 0 | 580 | 0 | 0 |  | 708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 520 | 180 | 0 | 0 | 4 | 60 | 35 | 0 | 0 | 547 | 28 | 140 | 666 | 159 | 0 |  | 5027 | 3710 | 8737 | 2705 | 708 | 1510 | 0 | 257 | 2973 | 86 | 0 | 36 | 112 | 350 | 0 | 0 | 95.05
14:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 303 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 32 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 201 | 0 | 0 | 0 |  | 6 | 0 | 8 | 0 | 0 | 6 | 15 | 14 | 0 | 0 | 0 | 0 | 275 | 0 | 8 | 0 | 48 | 31 | 0 | 20 | 0 | 0 | 8 | 15 | 0 | 33 | 11 | 94 | 61 | 0 | 0 | 2 | 0 | 0 | 10 | 10 | 120 | 0 | 40 | 10 | 0 | 210 | 0 | 0 | 10 | 0 | 24 | 8 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 15 | 0 | 17 | 11 | 319 | 24 | 0 | 0 | 3 | 0 | 0 | 0 | 17 | 0 | 0 | 345 | 0 | 39 | 0 | 0 | 0 | 17 | 24 | 18 | 0 | 240 | 0 | 0 | 310 | 2 | 585 | 0 | 0 |  | 666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 440 | 180 | 0 | 0 | 1 | 50 | 0 | 0 | 0 | 412 | 25 | 140 | 568 | 136 | 0 |  | 4259 | 3126 | 7385 | 2465 | 666 | 990 | 0 | 133 | 2625 | 86 | 0 | 24 | 94 | 300 | 2 | 0 | 95.07
15:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 291 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 32 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 201 | 0 | 0 | 0 |  | 0 | 0 | 3 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 305 | 0 | 8 | 0 | 10 | 10 | 0 | 20 | 0 | 0 | 0 | 15 | 0 | 33 | 11 | 76 | 67 | 0 | 0 | 1 | 0 | 0 | 10 | 10 | 120 | 0 | 40 | 10 | 0 | 210 | 0 | 0 | 10 | 0 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 17 | 0 | 0 | 355 | 0 | 29 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 240 | 0 | 0 | 310 | 1 | 586 | 0 | 0 |  | 669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 300 | 180 | 0 | 0 | 1 | 21 | 0 | 0 | 0 | 375 | 17 | 140 | 519 | 94 | 0 |  | 4120 | 2818 | 6938 | 2505 | 669 | 968 | 0 | 34 | 2400 | 86 | 0 | 3 | 76 | 196 | 1 | 0 | 95.03
16:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 282 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 32 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 201 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 325 | 0 | 8 | 0 | 10 | 10 | 0 | 20 | 0 | 0 | 0 | 15 | 0 | 33 | 11 | 76 | 75 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 120 | 0 | 40 | 10 | 0 | 211 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 11 | 0 | 0 | 0 | 17 | 7 | 0 | 0 | 240 | 0 | 0 | 310 | 0 | 585 | 0 | 0 |  | 668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 280 | 180 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 371 | 8 | 140 | 528 | 36 | 0 |  | 4072 | 2759 | 6831 | 2508 | 668 | 989 | 0 | 17 | 2384 | 86 | 0 | 17 | 76 | 86 | 0 | 0 | 95.02
17:00 | 0 | 0 | 0 | 180 | 0 | 60 | 0 | 300 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 5 | 0 | 0 | 0 | 17 | 32 | 8 | 0 | 46 | 40 | 0 | 0 | 0 | 201 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 5 | 15 | 20 | 0 | 0 | 0 | 0 | 305 | 0 | 8 | 0 | 10 | 10 | 0 | 20 | 0 | 0 | 2 | 15 | 0 | 33 | 11 | 76 | 75 | 0 | 0 | 0 | 0 | 0 | 14 | 32 | 120 | 0 | 63 | 30 | 0 | 210 | 0 | 0 | 10 | 0 | 16 | 5 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 5 | 17 | 2 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 1 | 0 | 1 | 0 | 17 | 1 | 1 | 7 | 240 | 0 | 0 | 310 | 0 | 584 | 0 | 0 |  | 671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 320 | 180 | 0 | 0 | 0 | 3 | 5 | 0 | 0 | 451 | 0 | 160 | 693 | 5 | 0 |  | 4308 | 3030 | 7338 | 2569 | 671 | 1078 | 0 | 143 | 2688 | 86 | 0 | 17 | 76 | 10 | 0 | 0 | 95.02
18:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 281 | 0 |  | 0 | 420 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 17 | 32 | 17 | 0 | 46 | 40 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 6 | 15 | 16 | 0 | 0 | 0 | 0 | 290 | 0 | 38 | 0 | 48 | 36 | 0 | 38 | 0 | 0 | 8 | 15 | 0 | 33 | 11 | 88 | 75 | 0 | 0 | 0 | 0 | 0 | 53 | 38 | 163 | 0 | 62 | 30 | 0 | 210 | 0 | 0 | 10 | 0 | 24 | 5 | 0 | 0 | 0 | 0 | 28 | 0 | 11 | 0 | 15 | 17 | 8 | 365 | 75 | 17 | 17 | 0 | 30 | 0 | 11 | 17 | 0 | 12 | 400 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 18 | 17 | 310 | 0 | 0 | 330 | 0 | 585 | 0 | 0 |  | 718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 567 | 0 | 236 | 762 | 0 | 0 |  | 5048 | 3646 | 8694 | 2721 | 718 | 1554 | 0 | 415 | 3080 | 86 | 0 | 32 | 88 | 0 | 0 | 0 | 95
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 273 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 33 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 17 | 0 | 0 | 0 | 0 | 330 | 0 | 45 | 0 | 48 | 50 | 0 | 43 | 0 | 0 | 0 | 15 | 11 | 33 | 11 | 90 | 75 | 0 | 0 | 0 | 0 | 0 | 53 | 39 | 163 | 0 | 62 | 60 | 0 | 210 | 0 | 0 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 350 | 0 | 0 | 335 | 0 | 587 | 0 | 0 |  | 719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619 | 0 | 307 | 759 | 0 | 0 |  | 4808 | 3855 | 8663 | 2790 | 719 | 1583 | 0 | 78 | 3317 | 86 | 0 | 0 | 90 | 0 | 0 | 0 | 94.97
19:30 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 269 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 17 | 33 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 315 | 0 | 45 | 0 | 48 | 53 | 0 | 43 | 0 | 0 | 0 | 15 | 11 | 33 | 11 | 90 | 75 | 0 | 0 | 0 | 0 | 0 | 53 | 39 | 163 | 0 | 62 | 60 | 0 | 210 | 0 | 0 | 10 | 0 | 16 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 350 | 0 | 0 | 310 | 0 | 587 | 0 | 0 |  | 698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 621 | 0 | 307 | 755 | 0 | 0 |  | 4770 | 3914 | 8684 | 2785 | 698 | 1583 | 0 | 70 | 3372 | 86 | 0 | 0 | 90 | 0 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 264 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 33 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 18 | 0 | 0 | 0 | 0 | 305 | 0 | 45 | 0 | 48 | 53 | 0 | 43 | 0 | 0 | 0 | 16 | 11 | 33 | 11 | 100 | 76 | 0 | 0 | 0 | 0 | 0 | 53 | 43 | 163 | 0 | 63 | 60 | 0 | 210 | 0 | 0 | 10 | 0 | 16 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 350 | 0 | 0 | 305 | 0 | 585 | 0 | 0 |  | 698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 0 | 307 | 762 | 0 | 0 |  | 4763 | 3914 | 8677 | 2762 | 698 | 1592 | 0 | 70 | 3369 | 86 | 0 | 0 | 100 | 0 | 0 | 0 | 94.98
21:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 251 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 33 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 18 | 0 | 0 | 0 | 0 | 305 | 0 | 45 | 0 | 48 | 53 | 0 | 43 | 0 | 0 | 0 | 16 | 11 | 33 | 11 | 102 | 75 | 0 | 0 | 0 | 0 | 0 | 53 | 44 | 163 | 0 | 62 | 60 | 0 | 209 | 0 | 0 | 10 | 0 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 350 | 0 | 0 | 305 | 0 | 585 | 0 | 0 |  | 814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 548 | 0 | 268 | 760 | 0 | 0 |  | 4773 | 3817 | 8590 | 2777 | 814 | 1593 | 0 | 62 | 3156 | 86 | 0 | 0 | 102 | 0 | 0 | 0 | 94.97
22:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 270 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 17 | 33 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 26 | 0 | 0 | 0 | 0 | 305 | 0 | 45 | 0 | 48 | 53 | 0 | 43 | 0 | 0 | 0 | 16 | 11 | 33 | 11 | 98 | 75 | 0 | 0 | 0 | 0 | 0 | 53 | 45 | 163 | 0 | 63 | 60 | 0 | 210 | 0 | 0 | 10 | 0 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 350 | 0 | 0 | 305 | 0 | 586 | 0 | 0 |  | 813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 466 | 0 | 168 | 767 | 0 | 0 |  | 4695 | 3541 | 8236 | 2738 | 813 | 1602 | 0 | 17 | 2882 | 86 | 0 | 0 | 98 | 0 | 0 | 0 | 94.96
23:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 271 | 0 |  | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 17 | 33 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 48 | 34 | 0 | 43 | 0 | 0 | 0 | 16 | 11 | 33 | 11 | 88 | 96 | 0 | 0 | 0 | 0 | 0 | 53 | 5 | 163 | 0 | 63 | 60 | 0 | 210 | 0 | 0 | 10 | 0 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 307 | 0 | 585 | 0 | 0 |  | 815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 140 | 755 | 0 | 0 |  | 4384 | 3466 | 7850 | 2553 | 815 | 1532 | 0 | 0 | 2776 | 86 | 0 | 0 | 88 | 0 | 0 | 0 | 94.95
24:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 262 | 0 |  | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 15 | 17 | 33 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 48 | 3 | 0 | 5 | 0 | 0 | 0 | 16 | 11 | 33 | 11 | 84 | 97 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 120 | 0 | 40 | 20 | 0 | 209 | 0 | 0 | 10 | 0 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 350 | 0 | 0 | 307 | 0 | 584 | 0 | 0 |  | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 140 | 758 | 0 | 0 |  | 4151 | 3326 | 7477 | 2499 | 720 | 1286 | 0 | 17 | 2785 | 86 | 0 | 0 | 84 | 0 | 0 | 0 | 94.94
KWH | 0 | 0 | 0 | 4347000 | 0 | 1208545 | 0 | 6908400 | 0 |  | 0 | 9038500 | 0 | 0 | 0 | 29568 | 0 | 0 | 0 | 0 | 0 | 90720 | 0 | 0 | 0 | 0 | 0 | 36701 | 31150 | 0 | 48000 | 275400 | 405360 | 776300 | 21600 | 0 | 1108680 | 972000 | 0 | 0 | 0 | 5255411 | 0 | 0 | 0 |  | 26400 | 0 | 55595 | 0 | 960 | 25440 | 359664 | 595680 | 0 | 0 | 0 | 0 | 6706000 | 0 | 468364 | 0 | 1020456 | 765120 | 0 | 869634 | 0 | 0 | 44429 | 346716 | 75240 | 815600 | 282060 | 2065920 | 1730880 | 0 | 0 | 10650 | 465000 | 0 | 779400 | 628344 | 3641318 | 0 | 1276512 | 779520 | 0 | 4229450 | 0 | 0 | 234540 | 0 | 479928 | 165360 | 0 | 0 | 0 | 0 | 117600 | 0 | 18144 | 116235 | 15360 | 138240 | 33454 | 8243000 | 613200 | 42240 | 31781 | 18840 | 40145 | 0 | 103710 | 86640 | 18480 | 29760 | 9072300 | 0 | 296410 | 0 | 111655 | 0 | 200520 | 169096 | 85440 | 49320 | 7878000 | 0 | 0 | 7690908 | 6720 | 14159999 | 0 | 0 |  | 14504727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2381000 | 429800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104742 | 0 | 0 | 4143600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8276700 | 0 | 0 | 0 | 0 | 28627 | 0 | 34621 | 21600 | 10684800 | 4671300 | 0 | 0 | 23700 | 393840 | 86592 | 0 | 0 | 10720000 | 199369 | 4036400 | 14512228 | 1049910 | 0 |  | 108884712 | 76303556 | 185188268 | 63647779 | 14504727 | 32386765 | 0 | 2088756 | 65947935 | 2080680 | 0 | 146315 | 2065920 | 2312671 | 6720 | 0
Fuel Cost | 0 | 0 | 0 | 6477030 | 0 | 1607364.85 | 0 | 7253820 | 0 |  | 0 | 9851965 | 0 | 0 | 0 | 391776 | 0 | 0 | 0 | 0 | 0 | 1470571.2 | 0 | 0 | 0 | 0 | 0 | 495463.5 | 417721.5 | 0 | 36000 | 0 | 0 | 0 | 367416 | 0 | 299343.6 | 262440 | 0 | 0 | 0 | 5465627.44 | 0 | 0 | 0 |  | 344520 | 0 | 946226.9 | 0 | 12172.8 | 294340.8 | 456773.28 | 1983614.4 | 0 | 0 | 0 | 0 | 7309540 | 0 | 604189.56 | 0 | 1153115.28 | 1140028.8 | 0 | 1452288.78 | 0 | 0 | 597570.05 | 475000.92 | 56430 | 1427300 | 211545 | 14833305.6 | 1886659.2 | 0 | 0 | 169761 | 637050 | 0 | 1356156 | 1087035.12 | 4187515.7 | 0 | 2476433.28 | 1777305.6 | 0 | 4271744.5 | 0 | 0 | 464389.2 | 0 | 359946 | 125673.6 | 0 | 0 | 0 | 0 | 1585248 | 0 | 251294.4 | 1358787.15 | 158515.2 | 1888358.4 | 443934.58 | 7583560 | 7456512 | 610790.4 | 402029.65 | 293150.4 | 471302.3 | 0 | 1102437.3 | 1175704.8 | 238207.2 | 350572.8 | 8346516 | 0 | 4283124.5 | 0 | 1270633.9 | 0 | 2618791.2 | 2020697.2 | 1279036.8 | 649544.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 43514181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2666720 | 833812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79289.694 | 0 | 0 | 35137728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8193933 | 0 | 0 | 0 | 0 | 363562.9 | 0 | 382562.05 | 262224 | 88683840 | 4764726 | 0 | 0 | 268047 | 4619743.2 | 1327455.36 | 0 | 0 | 97444800 | 0 | 48315708 | 124079549.4 | 0 | 0 |  | 132332919.04 | 460937881.604 | 593270800.644 | 58755774.194 | 43514181 | 39304324.01 | 0 | 26827136.24 | 393661625.4 | 561783.6 | 0 | 2416798.1 | 14833305.6 | 13395872.5 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 322 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 17 | 32 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 17 | 0 | 0 | 0 | 0 | 345 | 0 | 8 | 0 | 48 | 51 | 0 | 30 | 0 | 0 | 0 | 15 | 0 | 33 | 11 | 108 | 61 | 0 | 0 | 2 | 0 | 0 | 48 | 36 | 130 | 0 | 40 | 30 | 0 | 210 | 0 | 0 | 9 | 0 | 24 | 8 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 17 | 0 | 17 | 0 | 388 | 59 | 0 | 0 | 3 | 0 | 0 | 17 | 0 | 0 | 0 | 400 | 0 | 48 | 0 | 17 | 0 | 0 | 27 | 1 | 0 | 305 | 0 | 0 | 320 | 1 | 587 | 0 | 0 |  | 707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 390 | 180 | 0 | 0 | 3 | 65 | 35 | 0 | 0 | 452 | 33 | 140 | 573 | 168 | 0 |  | 8173 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 281 | 0 |  | 0 | 420 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 17 | 32 | 17 | 0 | 46 | 40 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 15 | 16 | 0 | 0 | 0 | 0 | 290 | 0 | 38 | 0 | 48 | 36 | 0 | 38 | 0 | 0 | 8 | 15 | 0 | 33 | 11 | 88 | 75 | 0 | 0 | 0 | 0 | 0 | 53 | 38 | 163 | 0 | 62 | 30 | 0 | 210 | 0 | 0 | 10 | 0 | 24 | 5 | 0 | 0 | 0 | 0 | 28 | 0 | 11 | 0 | 15 | 17 | 8 | 365 | 75 | 17 | 17 | 0 | 30 | 0 | 11 | 17 | 0 | 12 | 400 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 18 | 17 | 310 | 0 | 0 | 330 | 0 | 585 | 0 | 0 |  | 718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 567 | 0 | 236 | 762 | 0 | 0 |  | 8694 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 200 | 0 |  | 0 | 450 | 0 | 100 | 80 | 55 | 0 | 0 | 0 | 90 | 90 | 149 | 45 | 0 | 0 | 0 | 17 | 35 | 35 | 15 | 12 | 22 | 17 | 32 | 17 | 0 | 46 | 40 | 0 | 0 | 17 | 225 | 0 | 0 | 0 |  | 6 | 60 | 17 | 12 | 0 | 18 | 15 | 20 | 0 | 0 | 0 | 0 | 360 | 0 | 8 | 0 | 48 | 50 | 0 | 43 | 0 | 30 | 52 | 18 | 10 | 33 | 10 | 140 | 80 | 0 | 0 | 0 | 0 | 0 | 51 | 40 | 163 | 0 | 63 | 60 | 0 | 210 | 0 | 0 | 10 | 0 | 24 | 5 | 0 | 130 | 0 | 0 | 28 | 0 | 17 | 0 | 12 | 17 | 150 | 400 | 79 | 105 | 17 | 0 | 200 | 17 | 17 | 100 | 48 | 12 | 400 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 18 | 17 | 380 | 163 | 0 | 350 | 10 | 585 | 0 | 0 |  | 818 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 40 | 0 | 8 | 120 | 20 | 110 | 0 | 0 | 0 | 30 | 20 | 82 | 28 | 40 | 40 | 8 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 70 | 0 | 35 | 0 | 113 | 0 | 0 | 55 | 622 | 220 | 0 | 75 | 0 | 0 | 110 | 0 | 0 | 600 | 0 | 200 | 760 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 100 | 80 | 15 | 0 | 0 | 80 | 90 | 90 | 48 | 45 | 0 | 0 | 0 | 17 | 17 | 17 | 15 | 12 | 22 | 17 | 32 | 8 | 0 | 46 | 40 | 0 | 0 | 8 | 225 |  | 0 | 0 | 0 | 6 | 40 | 0 | 12 | 0 | 6 | 15 | 10 | 0 | 0 | 0 | 0 | 330 | 0 | 8 | 0 | 48 | 50 | 0 | 43 | 0 | 0 | 52 | 18 | 10 | 33 | 10 | 128 | 80 | 0 | 0 | 1.6 | 0 | 0 | 51 | 40 | 163 | 0 | 63 | 60 | 0 | 210 | 0 | 0 | 10 | 0 | 22 | 5 | 0 | 130 | 0 | 0 | 9 | 0 | 17 | 20 | 12 | 17 | 6 | 400 | 57 | 17 | 17 | 5 | 100 | 17 | 17 | 100 | 28 | 12 | 400 | 17 | 50 | 0 | 17 | 0 | 17 | 35 | 18 | 17 | 380 | 90 | 0 | 300 | 10 | 580 | 0 | 0 |  | 721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 20 | 110 | 0 | 0 | 0 | 0 | 0 | 50 | 28 | 34 | 30 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 35 | 0 | 35 | 0 | 50 | 0 | 8 | 0 | 622 | 220 |  | 17 | 6 | 100 | 70 | 0 |  | 510 | 30 | 200 | 720 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 22 | 17 | 25 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 360 | 0 | 13 | 0 | 38 | 3 | 0 | 28 | 0 | 0 | 0 | 16 | 0 | 33 | 11 | 86 | 88 | 0 | 0 | 0 | 0 | 0 | 51 | 39 | 163 | 0 | 62 | 60 | 0 | 210 | 0 | 0 | 10 | 0 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 6 | 0 | 0 | 0 | 17 | 8 | 0 | 0 | 393 | 0 | 0 | 305 | 0 | 586 | 0 | 0 | 0 | 482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 180 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 500 | 3 | 144 | 581 | 25 | 0 | 0 |  |  |  | 96034544 | 14504727 | 0 | 65947935 | 2235071 | 2065920 | 2312671 | 6720 | 2080680
[8 empty] | 299430 | [13 empty] | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | [15 empty] | 299772 | [10 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 |  | 399747 |  |  |  | 399575 | 399337 | 399467 | 399589 | 299230 | 765 | [6 empty] | 399245 |  | 299282 | 399274 |  | 399223 |  | 399630 | [12 empty] | 599468 | [32 empty] | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 | [8 empty] | 599726 | [9 empty] | 96.0345 | 14.5047 | 0 | 65.9479 | 2.2351 | 2.0659 | 2.3127 | 0.00672 | 2.0807
| Minimum Generation |  | 6628 | 5:00
| Highest Generation |  | 8737 | 13:00 | [200 empty] | 185.1883
| Day Peak Generation |  | 8173 | 12:00
| Evening Peak Generation |  | 8694 | 18:00 | [200 empty] | 202699852
| HVDC Max Flow |  | 815 | 23:00 | [200 empty] | 202.6999
| HVDC EvPeak Flow |  | 718 | 18:00
| Load factor L.F |  | 88.32% | [166 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-12-23
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-12-22 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 8173 | MW Hour : | 12:00 | Min. Gen. at | 4:00 | 6197
Evening Peak Generation : |  |  | 8694 | MW Hour : | 18:00 | Available Max Generation : |  | 11779
E.P. Demand (at gen end) : |  |  | 8694 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 9500
Maximum Generation : |  |  | 8737 | MW Hour : | 13:00 | Reserve(Generation end) |  | 2279
Total Gen. (MKWH) : |  |  | 185.1883 | System Load Factor : | 88.32% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 110 | MW at | 7:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-12-23
Actual : |  | 94.9 | Ft.(MSL) , | Rule curve : | 104 | Ft.( MSL )
Gas Consumed : |  | Total = | 704.72 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 98060098.204
: |  |  | Coal : | 393661625.4 | Oil : | 29243934.34 | Total : | 520965657.944
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3499.7913 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 955.1576 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1336.0395 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1159.4645 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 954.9506 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 709.2906 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 398.5972 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 331.2534 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 647.895 |  |  | 0 | 0%
Total |  | 0 |  | 9992.4397 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:11 | 10:33 | Madaripur 132/33kV S/S T3-426T LT Forced S/D Due to Red hot maintenance
08:12 | 10:32 | Madaripur 132/33kV S/S T3-426T HT Forced S/D Due to Red hot maintenance
08:24 | 14:51 | Chowmuhani 132/33kV S/S TR1 Scheduled S/D Due to 132 kv bus shutdown for annual maintenance. |  |  |  |  | 32.0MW load interruption.
08:25 | 15:53 | Amnura-Rajshahi 132kV Ckt-1 Scheduled S/D from Rajshahi 230/132/33kV end. and from Amnura 132/33kV
end Due to Annual maintenance.
08:25 | 11:30 | Chowmuhani 132/33kV S/S TR2 Scheduled S/D Due to 132 kv bus shutdown for annual maintenance.
08:26 | 17:20 | Chowmuhani 132/33kV S/S HFPL line Scheduled S/D Due to 132 kv bus shutdown for annual maintenance.
08:29 | 15:46 | Chowmuhani-Feni 132 kV Ckt-1 Scheduled S/D from Chowmuhani 132/33kV end Due to 132 kv bus shutdown |  |  |  |  | 44.0MW load interruption.
for annual maintenance.
08:30 | 10:04 | Aminbazar 400/230/132kV S/S 132 kv Bus 02 Scheduled S/D Due to Annual Maintenance
08:30 | 11:21 | Chowmuhani-Feni 132 kV Ckt-2 Scheduled S/D from Chowmuhani 132/33kV end Due to 132 kv bus
shutdown for annual maintenance.
08:31 | 15:32 | Chowmuhani-Ramganj 132 kV Ckt-1 Scheduled S/D from Chowmuhani 132/33kV end Due to 132 kv
bus shutdown for annual maintenance.
08:33 |  | Chandpur 200MW (Desh energy) Syncronized
08:38 |  | Anlima Energy Ltd. Syncronized
08:42 | 17:18 | Chowmuhani 132/33kV S/S TR3 Scheduled S/D Due to 132 kv bus shutdown for annual maintenance. |  |  |  |  | 24.0MW load interruption.
08:43 |  | Karnaphuli Power Ltd. Syncronized
08:45 | 15:30 | Chowmuhani-Ramganj 132 kV Ckt-2 Scheduled S/D from Chowmuhani 132/33kV end Due to 132 kv bus
shutdown for annual maintenance.
08:45 | 17:12 | Chowmuhani 132/33kV S/S Main Bus Scheduled S/D Due to 132 kv bus shutdown for annual maintenance. |  |  |  |  | 88.0MW load interruption.
08:57 | 15:51 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-1 Scheduled S/D from Purbasadipur 132/33kV end. and from
Thakurgaon 132/33kV end Due to Annual Maintenance
09:24 |  | Tongi 230/132/33kV S/S T-01 LT Project Work S/D Due to DFDR work
09:25 |  | Tongi 230/132/33kV S/S T-01 HT Project Work S/D Due to DFDR work
| 09:54 | Aminbazar-Mirpur 132kV Ckt-2 is restored.
10:10 | 18:21 | Shitalakhya 132/33kV S/S 132/33 kV GT-1 HT Scheduled S/D Due to Annual maintenance
10:12 |  | Aminbazar-Mirpur 132kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to Ds loop cobnection
10:24 | 18:28 | Maniknagar 132/33kV S/S Transformer GT-1 HT Scheduled S/D Due to Annual Maintenance schedule by DPDC
10:28 |  | Chattogram 108 MW PP (ECPV) Syncronized
11:00 | 12:39 | Madaripur 132/33kV S/S T1-405T HT Forced S/D Due to Red hot maintenance
11:01 | 12:40 | Madaripur 132/33kV S/S T1-405T LT Forced S/D Due to Red hot maintenance
11:05 |  | Chattogram 108 MW PP (ECPV) Shutdown
11:10 |  | Fenchugonj CCPP Phase-1 Tripped with remarks:- manual update
11:15 |  | Energypac Power Venture Thakurgaon Ltd. Syncronized
11:17 |  | Bogura 400kv bus Reactor S/D.
11:34 |  | Tangail Palli Power Gen 22 MW Syncronized
11:46 |  | Kodda 150 MW PP B-R Syncronized
11:49 |  | Chandpur 115(Doreen) Syncronized
12:00 |  | Day peak generation = 8173 MW.
12:03 |  | Patenga 50MW PP (Baraka) Syncronized
12:06 |  | Bhairob 54.5 MW Syncronized
| 12:10 | Keranigonj 230/132/33kV S/S TR-1 HT is restored.
| 12:11 | Keranigonj 230/132/33kV S/S TR-1 LT is restored.
12:20 |  | Jangalia 52 MW PP (Lakdanavi) Syncronized
12:24 |  | Feni Lanka Power Syncronized
12:35 |  | Gazipur 100 MW PP Syncronized
12:40 |  | Confidence Power Bogura Unit-1 113 MW Syncronized
12:45 |  | Confidence Power Bogura Unit-1 113 MW Shutdown
12:45 |  | Ashuganj 150MW PP (Midland) Syncronized
12:50 |  | Dohazari -Kalaish 100 MW Peaking Syncronized
12:52 |  | Juldah unit-2 (Acorn) Syncronized
13:12 |  | Energypac Power Venture Thakurgaon Ltd. Shutdown
13:18 |  | Anlima Energy Ltd. Shutdown
13:27 |  | Karnaphuli Power Ltd. Shutdown
13:34 |  | Gazipur 100 MW PP Shutdown
13:42 |  | Juldah unit-2 (Acorn) Shutdown
14:25 |  | Mymensingh 200 MW PP (United) Shutdown
14:26 |  | Jangalia 52 MW PP (Lakdanavi) Shutdown
14:29 |  | Jamalpur 115 MW PP (United) Shutdown
14:31 |  | Kodda 150 MW PP B-R Shutdown
14:37 |  | Patenga 50MW PP (Baraka) Shutdown
14:38 |  | Chandpur 200MW (Desh energy) Shutdown
14:40 |  | Tangail Palli Power Gen 22 MW Shutdown
14:40 |  | Ashuganj 150MW PP (Midland) Shutdown
14:46 |  | Chandpur 115(Doreen) Shutdown
14:53 | 17:17 | Chowmuhani 132/33kV S/S TR2 Scheduled S/D Due to 132 kv bus shutdown for annual maintenance.
15:20 | 21:33 | Sylhet 132/33kV S/S T1 LT Tripped showing 51 relays Due to 132 kV Transformer side LA Burst
15:20 | 21:20 | Sylhet 132/33kV S/S T1 HT Tripped showing 51 relays Due to 132 kV Transformer side LA Burst
15:22 |  | Sylhet 10MW PP (Desh) Tripped with remarks:- Grid side feeder trip.
15:42 |  | Feni Lanka Power Shutdown
15:50 |  | Fenchuganj 44MW (Energyprima) Syncronized
| 15:55 | Barishal(N)-Madaripur 132 kV Ckt-1 is restored.
16:10 |  | Sylhet 10MW PP (Desh) Syncronized with remarks:- NLDC demand .
16:21 |  | Gazipur 100 MW PP Syncronized
16:25 |  | Manikganj 55 MW PP (Northern) Syncronized
16:31 |  | Kanchan Purbachal Power Generation Ltd. Syncronized
16:32 |  | Anwara 300 MW PP (United) Syncronized
| 16:33 | Mirpur 132/33kV S/S T1 LT is restored.
| 16:33 | Mirpur 132/33kV S/S T1 HT is restored.
16:35 |  | Patenga 50MW PP (Baraka) Syncronized
16:40 |  | Rangpur 113 MW PP (Confidence) Syncronized
16:41 |  | Jangalia 52 MW PP (Lakdanavi) Syncronized
16:41 |  | Kaptai 7 MW Solar PP Shutdown
16:43 |  | Sikalbaha 105 MW PP (Baraka Sikalbaha) Syncronized
16:45 |  | Gazipur 52 MW PP Syncronized
16:45 |  | Energypac Power Venture Thakurgaon Ltd. Syncronized
16:49 |  | Chandpur 115(Doreen) Syncronized
16:50 |  | Sarishabari 3 MW Solar Plant Shutdown
16:51 |  | Mymensingh 200 MW PP (United) Syncronized
16:51 |  | Nababganj 55 MW PP (Southern power ) Syncronized
16:52 |  | Anlima Energy Ltd. Syncronized
16:55 |  | Jamalpur 115 MW PP (United) Syncronized
17:00 |  | Feni Lanka Power Syncronized
17:00 |  | Ashuganj 150MW PP (Midland) Syncronized
17:01 |  | Chandpur 200MW (Desh energy) Syncronized
17:01 |  | Juldah unit-2 (Acorn) Syncronized
17:01 |  | Tangail Palli Power Gen 22 MW Syncronized
17:01 |  | Kodda 149 MW PP Unit-1 (Summit) Syncronized
17:01 |  | Kodda 150 MW PP B-R Syncronized
17:03 |  | Confidence Power Bogura Unit-1 113 MW Syncronized
17:07 |  | Madanganj-55 MW PP(Summit) Syncronized
17:10 |  | Karnaphuli Power Ltd. Syncronized
17:15 |  | Sympa Solar Power 8 MW Shutdown
17:17 |  | Teesta Solar Limited Shutdown
17:18 |  | Sirajgonj 6.55 MW Solar Shutdown
17:18 |  | Teknaf 20MW PP (Solartech) Shutdown
17:21 |  | Dohazari -Kalaish 100 MW Peaking Shutdown
17:24 |  | Spectra Solar Plant Ltd. Shutdown
17:24 |  | Juldah 100 MW PP Unit-3 (Acorn) Syncronized
17:27 |  | Bogura West 400 kv bus Reactor synchronous.
17:31 |  | Intraco Solar 30 MW Shutdown
17:32 |  | Mongla Orion 100 MW Solar PP Shutdown
17:33 |  | Sutiakhali 50 MW Solar PP Shutdown
17:37 |  | Energypac Power Venture Thakurgaon Ltd. Shutdown
17:45 |  | Confidence Power Bogura Unit-1 113 MW Shutdown
17:50 |  | Rangpur 113 MW PP (Confidence) Shutdown
18:00 |  | Evening Peak Gen. 8694 MW
18:05 |  | Feni 11 MW PP (Doreen) Syncronized
18:15 |  | Feni Lanka Power Shutdown
18:16 |  | Anwara 300 MW PP (United) Shutdown
18:16 |  | Jangalia 52 MW PP (Lakdanavi) Shutdown
18:16 |  | Gazipur 100 MW PP Shutdown
18:17 |  | Madanganj-55 MW PP(Summit) Shutdown
18:21 |  | Gazipur 52 MW PP Shutdown
18:22 |  | Kodda 149 MW PP Unit-1 (Summit) Shutdown
18:23 |  | Chowmuhani 113 MW Syncronized
18:30 |  | Juldah 100 MW PP Unit-3 (Acorn) Shutdown
18:35 |  | Kanchan Purbachal Power Generation Ltd. Shutdown
18:40 |  | Ashuganj 150MW PP (Midland) Shutdown
18:41 |  | Kodda 150 MW PP B-R Shutdown
18:41 |  | Nababganj 55 MW PP (Southern power ) Shutdown
18:42 |  | Tangail Palli Power Gen 22 MW Shutdown
18:42 |  | Juldah unit-2 (Acorn) Shutdown
18:43 |  | Anlima Energy Ltd. Shutdown
18:44 |  | Sikalbaha 105 MW PP (Baraka Sikalbaha) Shutdown
18:45 |  | Manikganj 55 MW PP (Northern) Shutdown
18:48 |  | Chandpur 200MW (Desh energy) Shutdown
18:49 |  | Patenga 50MW PP (Baraka) Shutdown
18:51 |  | Karnaphuli Power Ltd. Shutdown
18:54 |  | Chandpur 115(Doreen) Shutdown
19:03 |  | Chowmuhani 113 MW Shutdown
20:06 |  | Mymensingh 200 MW PP (United) Shutdown
21:27 |  | Jamalpur 115 MW PP (United) Shutdown
21:28 |  | Natore-Rajshahi 132kV Ckt-1 Forced S/D from Rajshahi 132/33kV end Due to Red hot in BCB
Bay (CT-Y-Phase).(132 KV Raj (New) Ckt-2 is ON through BCB)
21:28 |  | Natore-Rajshahi 132kV Ckt-2 Forced S/D from Rajshahi 132/33kV end Due to Red hot in BCB
Bay (CT-Y-Phase).(132 KV Raj (New) Ckt-2 is ON through BCB)
22:01 |  | Bhairob 54.5 MW Shutdown
22:26 |  | Ashuganj 450 MW CCPP(South) Tripped with remarks:- GT
23:01 |  | Bhairob 54.5 MW Syncronized
23:06 | 04:30 | Rajshahi 132/33kV S/S 132 kV Bus Coupler Forced S/D Due to Red hot maintenance
23:14 | 00:40 | Kishoreganj 132/33kV S/S Tr-1 (404T) HT Forced S/D Due to 33 kv Bus- Section T-1 and Bus- Section T-3 |  |  |  |  | 30.0MW load interruption.
D/S B-Phase Red hot
01:05 |  | Haripur 412 MW CCPP Shutdown with remarks:- ST
01:21 |  | Haripur 412 MW CCPP Shutdown with remarks:- GT
01:47 |  | Ashuganj 450 MW CCPP(South) Syncronized with remarks:- GT
04:00 |  | Minimum generation is 6197MW
06:27 |  | Teknaf 20MW PP (Solartech) Syncronized
06:27 |  | Kaptai 7 MW Solar PP Syncronized
06:28 |  | Sutiakhali 50 MW Solar PP Syncronized
06:31 |  | Purbasadipur 132/33kV S/S T-3 Transformer (423T) HT Scheduled S/D Due to Annual maintenance
of 132 kV bus
06:31 |  | Purbasadipur 132/33kV S/S T-1 Transformer (403T) HT Scheduled S/D Due to Annual maintenance
of 132 kV bus
06:32 |  | Purbasadipur 132/33kV S/S T-4 Transformer HT Scheduled S/D Due to Annual maintenance of 132 kV bus
06:33 |  | Spectra Solar Plant Ltd. Syncronized
06:37 |  | Intraco Solar 30 MW Syncronized
06:40 |  | Sympa Solar Power 8 MW Syncronized
06:40 |  | Purbasadipur-Thakurgaon-EPV 132kV Ckt-1 Scheduled S/D from Purbasadipur 132/33kV end Due to
Annual maintenance of 132 kV bus
06:41 |  | Sympa Solar Power 8 MW Tripped with remarks:- Panchagarh to Tetulia 33 KV grid line tripped due to
maintenance work in Purbo Sadipur 132 KV grid line.
06:41 |  | Purbasadipur-Thakurgaon-EPV 132kV Ckt-2 Scheduled S/D from Purbasadipur 132/33kV end Due to
Annual maintenance of 132 kV bus
06:42 |  | Purbasadipur 132/33kV S/S Single Bus Scheduled S/D Due to Annual maintenance of 132 kV bus
06:42 |  | Purbasadipur-Saidpur 132kV Ckt-2 Scheduled S/D from Purbasadipur 132/33kV end Due to Annual maintenance |  |  |  |  | 75.0MW load interruption.
of 132 kV bus and from Saidpur 132/33kV end Due to Maintanance work at 132Kv busbar of purbasadipur
06:42 |  | Purbasadipur-Saidpur 132kV Ckt-1 Scheduled S/D from Purbasadipur 132/33kV end Due to Annual maintenance
of 132 kV bus and from Saidpur 132/33kV end Due to Maintanance work at 132Kv busbar of purbasadipur
06:44 |  | Siddhirgonj 2*120 MW GTPP Syncronized with remarks:- GT-2
06:46 |  | Sirajgonj 6.55 MW Solar Syncronized
06:47 |  | Mongla Orion 100 MW Solar PP Syncronized
06:50 |  | Sarishabari 3 MW Solar Plant Syncronized
06:51 |  | Teesta Solar Limited Syncronized
07:17 |  | Feni 11 MW PP (Doreen) Tripped
07:20 |  | Chandpur 132/33kV S/S 402T HT Scheduled S/D Due to 33kv bus section Tr-1& Tr-2 annual maintenance work by BPDB |  |  |  |  | 14.0MW load interruption.
07:20 |  | Chandpur 132/33kV S/S 402T LT Scheduled S/D Due to 33kv bus section Tr-1& Tr-2 annual maintenance work by BPDB
07:31 |  | Siddhirgonj 2*120 MW GTPP Syncronized with remarks:- GT-1
07:33 |  | Ishurdi 132/33kV S/S 132/33 kV T-1 LT Scheduled S/D Due to A/M |  |  |  |  | 18.0MW load interruption.
07:33 |  | Ishurdi 132/33kV S/S 132/33 kV T-1 HT Scheduled S/D Due to A/M
07:38 |  | Bagerhat-Labanchura 132 kV Ckt-2 Scheduled S/D from Bagerhat 132/33kV end Due to Annual maintenance work
07:40 |  | Madunaghat-TKCL 132kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end Due to Reconductoring of
Modunaghat-Shikalbaha 132kV line in Karnafuly river.
07:54 |  | Sreemongol 132/33kV S/S 132/33kv T-2 LT Scheduled S/D Due to PBS works.
07:54 |  | Sreemongol 132/33kV S/S 132/33kv T-3 LT Scheduled S/D Due to PBS works.
07:55 |  | Sreemongol 132/33kV S/S 132/33kv T-3 HT Scheduled S/D Due to PBS works.
07:55 |  | Sreemongol 132/33kV S/S 132/33kv T-2 HT Scheduled S/D Due to PBS works.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-12-22 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 72 | 1208545 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 281 | 6908400 | Machine problem
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9038500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 17 | 29568 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 0 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 90720 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 36701 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 31150 | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 0 | 323400 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 405360 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 32 | 776300
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 17 | 21600 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 11 | 18144 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 42240 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 0 | Reserve
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | Reserve
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 169096
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 49320
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5422 | 1147 | 23496044
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 0 | Reserve
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 116235
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 6 | 25440 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 86 | 2080680 | Unit-3 under maint.
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 225 | 5255411
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 31781 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 55595 | Reserve
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 0 | Reserve
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 15 | 15360 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 15 | 359664 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 16 | 595680
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 960 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 18840
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 30 | 40145 | Low demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 11 | 103710 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 29760 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 111655 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 0 | 0 | Reserve
| SS Power I |  | SS Power | 2*612 | 1224 | 330 | 7690908 | Coal shortage
| Cox's Bazar Wind |  | IPP | 66 | 0 | 0 | 6720 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 585 | 14159999 | On test.
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 3769 | 1365 | 30698543
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 0 | Under maint.
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 290 | 6706000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 310 | 7878000 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 48 | 1020456
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 0 | 36 | 765120
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 38 | 468364 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 38 | 869634 | Gas shortage
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 8 | 33454 | Low demand
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 138240 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 15 | 346716 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 75240
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 88 | 2065920
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 815600
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 44429 | Low demand
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 11 | 282060 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 86640 | Low demand
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 18480 | Reserve
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 200520 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 18 | 85440 | Fuel shortage
| Cumilla Area Total |  |  |  | 2896 | 992 | 21900313
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 75 | 1730880 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Contract Expired
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10650
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 28 | 117600 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 75 | 613200 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 296410
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 26400 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 184 | 2795140
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 465000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3641318
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 779400
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 38 | 628344
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 165360 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1276512
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 30 | 779520 | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 210 | 4229450 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 479928 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Under maint.
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 365 | 8243000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 234540
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9072300
| Sylhet Area Total |  |  |  | 2427 | 1360 | 29994672
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 718 | 14504727
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 0 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Machine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 393840
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | Fuel shortage
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 567 | 10720000
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 1285 | 25618567
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 20 | 429800 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 118 | 2381000 | ST Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 430 | 10684800 | Unit-2 under maint.
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4671300
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve
| Barisal 307 MW |  | IPP | 307*1 | 307 | 236 | 4036400 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1024 | 22203300
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 400 | 8276700 | FGMO
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 104742
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 21600 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 23700
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 762 | 14512228
| Rajshahi Area Total |  |  |  | 3631 | 1167 | 22938970
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4143600 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 28627 | Reserve
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 34621
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 0 | 86592 | Reserve
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 199369
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1049910
| Rangpur Area Total |  |  |  | 950 | 170 | 5542719
| Total |  |  |  | 25211 | 8694 | 185188268
| Eastern Grid Total |  |  |  | 15128 | 5048 | 108884712
| Western Grid Total |  |  |  | 10083 | 3646 | 76303556
| National Grid Total |  |  |  | 25211 | 8694 | 185188268
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-12-22
| (a) ENTIRE EASTERN GRID : |  | 5597.63 | MW | (b) ENTIRE WESTERN GRID : |  | 2804.4 | MW
| i) Dhaka area |  | 2915.23 | MW | i) Khulna area |  | 1044 | MW
| ii) Chittagong area |  | 876.4 | MW | ii) Rajshahi area |  | 863 | MW
| iii) Comilla area |  | 758 | MW | iii) Barisal area |  | 258.4 | MW
| iv) Mymensingh area |  | 718 | MW | iv) Rangpur area |  | 639 | MW
| v) Sylhet area |  | 330 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8402.03 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 17 | 18:00 | Kamrangirchar | 36 | 12:00 | Narinda | 34 | 12:00 | Sherpur | 88 | 18:00
2 | AKSML | 13 | 16:00 | Chowmuhani | 122 | 19:00 | Kaptai | N/A | N/A | Narshingdi | 128 | 00:00 | Shikalbaha | 14 | 13:00
3 | Aftabnagar | 24 | 12:00 | Chuadanga | 64 | 18:00 | Kazla | 68 | 13:00 | Natore | 86 | 18:00 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 54 | 13:00 | Coxsbazar | 87 | 18:00 | Keranigonj | 44 | 13:00 | Nawabganj | 34.4 | 13:00 | Shitalakhya | 50.8 | 00:00
5 | Agrabad | 38 | 12:00 | Cumilla(N) | 96 | 20:00 | Khagrachori | 18 | 18:00 | Netrakona | 94 | 18:30 | Sholosohor | 23 | 12:00
6 | Amnura | 30 | 19:30 | Cumilla(S) | 112 | 13:00 | Khulna | 65 | 13:00 | New | 11.5 | 18:30 | Shyampur | 128 | 09:00
7 | Ashuganj | 55 | 01:00 | Daudkandi | 84 | 19:00 | Khulshi | 128 | 12:00 | Niamatpur | 50 | 18:00 | Siddhirganj | 76 | 12:00
8 | BIPTC | N/A | N/A | Dhaka | 8 | 11:00 | Kishoreganj | 90 | 18:30 | Noapara | 28 | 18:00 | Sirajganj | 66 | 18:00
9 | BSRM | 63 | 13:00 | Dhamrai | 78 | 12:00 | Kodda | 171 | 00:00 | PHP | 4 | 00:00 | Sonargaon | 80 | 01:00
10 | Bagerhat | 68 | 20:00 | Dhanmondi | 78 | 13:00 | Kulaura | 28 | 18:00 | Pabna | 65 | 18:30 | Sreemongol | 38 | 18:30
11 | Bakulia | 51 | 13:00 | Dohazari | 48 | 18:00 | Kurigram | 46 | 18:00 | Palashbari | 78 | 18:00 | Sreepur | 46 | 00:00
12 | Banani | 16 | 13:00 | Faridpur | 93 | 20:00 | Kushtia | 94 | 18:30 | Panchagarh | 41 | 18:00 | Srinagar | 33 | 13:00
13 | Bangabhaban | 3 | 08:00 | Fatullah | 44 | 00:00 | Lalbag | 47 | 00:00 | Patuakhali | 65.1 | 21:00 | Sunamganj | 32 | 19:00
14 | Barapukuria | 41 | 09:00 | Fenchuganj | 21 | 18:00 | Lalmonirhat | 30 | 18:00 | Payra | 17.6 | 00:00 | Sylhet | 8 | 11:00
15 | Barguna | 12 | 18:00 | Feni | 70 | 13:00 | MI_Cement | 19.4 | 11:00 | Postogola | 36 | 13:00 | Sylhet-132 | 78 | 18:00
16 | Barishal | 65 | 13:00 | GPH | 92 | 22:00 | Madanganj | 25 | 13:00 | Purbachal | 10 | 12:00 | TK | 17.8 | 20:00
17 | Barishal-230 | 58 | 19:30 | Ghorashal | 47 | 00:00 | Madaripur | 58 | 19:30 | Purbasadipur | 98 | 18:00 | Tangail | 124 | 18:30
18 | Baroaulia | 55 | 11:00 | Goalpara | 20 | 09:00 | Madartek | 57.52 | 13:00 | Rahim | 32 | 01:00 | Thakurgaon | 70 | 18:30
19 | Baroirhat | 38 | 18:00 | Gollamari | 38 | 13:00 | Madunaghat | 23 | 11:00 | Rajbari | 44 | 18:00 | Tongi | 83 | 00:00
20 | Bashundhara | 119 | 13:00 | Gopalganj | 70 | 18:30 | Magura | 39 | 18:00 | Rajendrapur | 60 | 01:00 | Ullon | 30 | 12:00
21 | BashundharaCement | 0 | 01:00 | Gulshan | 56 | 12:00 | Mahasthangarh | 48 | 18:00 | Rajshahi | 92 | 13:00 | Uttara | 46 | 12:00
22 | Beanibazar | 40 | 18:00 | Halishahar | 43 | 18:30 | Manikganj | 78 | 18:30 | Rajshahi-230 | 21 | 13:00 | UttaraNew | 30 | 12:00
23 | Benapole | 38 | 18:00 | HaripurSBU | 138 | 02:00 | Maniknagar | 50 | 13:00 | Ramganj | 90 | 13:00 | Zigatola | 69 | 13:00
24 | Bhaluka | 90 | 00:00 | Hasnabad | 57 | 12:00 | Matarbari | 30 | 18:00 | Rampur | 16 | 13:00
25 | Bhandaria | 33 | 21:00 | Hathazari | 53 | 12:00 | Matuail | 52 | 00:00 | Rangamati | 14 | 18:00
26 | Bhangura | 19 | 18:30 | Ishurdi | 46 | 18:00 | Millgate | 74 | 12:00 | Rangpur | 102 | 13:00
27 | Bheramara(GK) | 38 | 18:00 | Jaldhaka | 50 | 18:00 | Mirpur | 68 | 12:00 | Ruppur | 4 | 09:00
28 | Bhulta | 200 | 00:00 | Jamalpur | 108 | 18:30 | Mirsorai | 1 | 00:00 | SSM | 10 | 01:00
29 | Bog-Sherpur | 46 | 18:30 | Jashore | 90 | 13:00 | Mirzapur | 32 | 08:00 | Saidpur | 69 | 12:00
30 | Bogura | 93 | 18:00 | Jhenaidah | 84 | 18:00 | Mithapukur | 38 | 08:00 | Satkhira | 79 | 18:00
31 | Borhanuddin | 31 | 21:00 | Joydebpur | 112 | 12:00 | Modern | 0 | 00:00 | Satmasjid | 68 | 13:00
32 | Brahmanbaria | 97 | 20:00 | Joypurhat | 42 | 18:00 | Mogbazar | 58.5 | 18:00 | Savar | 112 | 12:00
33 | Cantonment | 104 | 13:00 | Juldah | 19 | 11:00 | Mongla | 24 | 11:00 | SevenRings | 4.07 | 10:00
34 | Chandpur | 38 | 18:30 | KSRM | 33.5 | 11:00 | Motijheel | 23 | 13:00 | ShahCement | 25 | 23:00
35 | Chandraghona | 21 | 18:00 | Kabirpur | 156 | 12:00 | Munshiganj | 60 | 00:00 | Shahjadpur | 56 | 18:00
36 | Chapai | 42 | 08:00 | Kachua | 43 | 13:00 | Mymensingh | 156 | 13:00 | Shahjibazar | 74 | 19:30
37 | Charsaidpur | 25 | 08:00 | Kallyanpur | 72 | 13:00 | Naogaon | 84 | 18:30 | Shahmirpur | 30.5 | 18:00
38 | Chauddagram | 32 | 12:00 | Kalurghat | 18 | 00:00 | Narail | 36 | 18:00 | Shariatpur | 52 | 13:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-12-22 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 406 | 05:00 | 392 | 18:30 | Gopalganj | 413 | 04:00 | 400 | 19:30
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 402 | 14:00 | 390 | 12:00
| Bhulta | 415 | 17:00 | 402 | 12:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 418 | 04:00 | 404 | 12:00 | Payra | 419 | 04:00 | 409 | 19:30
| BIPTC | 409 | 02:00 | 396 | 12:00 | Rahanpur | 416 | 14:00 | 398 | 18:00
| Bogura | N/A | N/A | N/A | N/A | Rampal | 413 | 01:00 | 402 | 20:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 240 | 05:00 | 230 | 12:00 | Hasnabad | 240 | 17:00 | 224 | 18:00
| AKSML | 231 | 17:00 | 221 | 19:00 | Hathazari | 229 | 06:00 | 222 | 18:30
| Aminbazar | 240 | 17:00 | 235 | 18:30 | Ishurdi | 239 | 05:00 | 227 | 18:00
| Ashuganj | 237 | 02:00 | 232 | 12:00 | Jhenaidah | 239 | 05:00 | 223 | 00:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 237 | 17:00 | 230 | 12:00
| Baghabari | 236 | 05:00 | 226 | 12:00 | Keranigonj | 240 | 05:00 | 230 | 12:00
| Barapukuria | 227 | 17:00 | 214 | 18:00 | Khulna(S) | 244 | 02:00 | 224 | 09:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 244 | 03:00 | 238 | 20:00 | Maniknagar | 241 | 06:00 | 233 | 12:00
| Bheramara | 238 | 05:00 | 225 | 18:00 | Meghnaghat | 245 | 17:00 | 240 | 00:00
| Bhulta | 243 | 04:00 | 234 | 12:00 | Mirsorai | 234 | 04:00 | 224 | 19:30
| Bibiana | 237 | 18:00 | 231 | 12:00 | Rajshahi | 237 | 05:00 | 223 | 19:00
| BIPTC | 238 | 04:00 | 225 | 18:00 | Rampal | 240 | 03:00 | 231 | 12:00
| Bogura | 233 | 05:00 | 221 | 18:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 247 | 17:00 | 242 | 13:00 | Rampura | 241 | 04:00 | 232 | 12:00
| BSRM | 233 | 04:00 | 226 | 12:00 | Shikalbaha | 226 | 05:00 | 220 | 13:00
| Cumilla(N) | 238 | 17:00 | 230 | 12:00 | Shyampur | 241 | 05:00 | 234 | 00:00
| Fenchuganj | 242 | 17:00 | 236 | 12:00 | Siddhirganj | 242 | 06:00 | 235 | 11:00
| Ghorashal | 242 | 01:00 | 238 | 16:00 | Sirajgonj | 240 | 03:00 | 232 | 19:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 236 | 14:00 | 225 | 13:00
| GPH | 230 | 05:00 | 221 | 19:00 | Tongi | 238 | 05:00 | 228 | 11:00
| Haripur | 241 | 17:00 | 233 | 12:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 138 | 05:00 | 130 | 12:00 | Lalbag | 138 | 05:00 | 133 | 00:00
| Agargaon | 141 | 04:00 | 135 | 11:00 | Lalmonirhat | 130 | 03:00 | 122 | 08:00
| Agrabad | 135 | 05:00 | 131 | 19:00 | Madanganj | 137 | 17:00 | 132 | 12:00
| AKS | 134 | 09:00 | 129 | 12:00 | Madaripur | 135 | 07:00 | 130 | 12:00
| Aminbazar | 140 | 17:00 | 134 | 11:00 | Madartek | 137 | 05:00 | 129 | 12:00
| Amnura | 137 | 04:00 | 130 | 18:00 | Madunaghat | 136 | 04:00 | 131 | 19:00
| Ashuganj | 141 | 03:00 | 138 | 12:00 | Magura | 140 | 04:00 | 132 | 12:00
| Bagerhat | 134 | 04:00 | 126 | 20:00 | Mahasthangarh | 136 | 05:00 | 126 | 18:00
| Bakulia | 136 | 05:00 | 132 | 12:00 | Manikganj | 134 | 14:00 | 126 | 18:30
| Banani | 141 | 04:00 | 135 | 12:00 | Maniknagar | 134 | 04:00 | 129 | 12:00
| Bangabhaban | 135 | 04:00 | 129 | 12:00 | Matarbari | 130 | 09:00 | 122 | 19:30
| Barapukuria | 136 | 14:00 | 126 | 18:00 | Matuail | 137.4 | 17:00 | 132 | 12:00
| Barguna | 137 | 05:00 | 133 | 19:30 | Millgate | 141 | 04:00 | 133 | 12:00
| Barishal | 140 | 06:00 | 131 | 19:00 | Mirpur | 138 | 06:00 | 133 | 12:00
| Barishal-230 | 140 | 03:00 | 135 | 20:00 | Mirzapur | 135 | 04:00 | 130 | 12:00
| Baroaulia | 135 | 06:00 | 130 | 19:00 | Mithapukur | 134 | 17:00 | 123 | 18:00
| Baroirhat | 134 | 05:00 | 126 | 19:30 | MI_Cement | 137.6 | 05:00 | 132 | 12:00
| Bashundhara | 141 | 04:00 | 131 | 12:00 | Modern | 137 | 05:00 | 131 | 12:00
| BashundharaCement | 139 | 07:00 | 132 | 12:00 | Mogbazar | 137 | 03:00 | 115 | 22:00
| Beanibazar | 133 | 00:00 | 131 | 12:00 | Mongla | 134 | 14:00 | 126 | 18:00
| Benapole | 136 | 03:00 | 129 | 12:00 | Motijheel | 135 | 04:00 | 130 | 13:00
| Bhaluka | 135 | 04:00 | 130 | 12:00 | Munshiganj | 137 | 18:00 | 133 | 00:00
| Bhandaria | 136 | 02:00 | 130 | 19:30 | Mymensingh | 137 | 09:00 | 128 | 12:00
| Bhangura | 141 | 04:00 | 133 | 19:00 | Naogaon | 134 | 02:00 | 124 | 18:00
| Bheramara | 138 | 03:00 | 130 | 19:00 | Narail | 139 | 02:00 | 130 | 19:00
| Bheramara(GK) | 136 | 04:00 | 130 | 19:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 127 | 14:00 | 123 | 00:00 | Narshingdi | 134 | 14:00 | 127 | 00:00
| Bog-Sherpur | 138 | 05:00 | 128 | 08:00 | Natore | 138 | 05:00 | 130 | 18:00
| Bogura | 137 | 04:00 | 129 | 18:00 | Nawabganj | 137 | 04:00 | 131 | 12:00
| Bogura-230 | 137 | 04:00 | 129 | 18:00 | Netrakona | 137 | 11:00 | 131 | 06:00
| Brahmanbaria | 131 | 04:00 | 129 | 12:00 | New | 141 | 03:00 | 133 | 12:00
| Cantonment | 141 | 04:00 | 135 | 12:00 | Niamatpur | 134 | 14:00 | 124 | 18:00
| Chandpur | 133 | 07:00 | 116 | 12:00 | Noapara | 136 | 05:00 | 130 | 12:00
| Chandraghona | 137 | 05:00 | 132 | 19:00 | Pabna | 140 | 04:00 | 133 | 18:30
| Chapai | 137 | 06:00 | 130 | 19:00 | Palashbari | 133 | 04:00 | 122 | 18:30
| Charsaidpur | 137 | 04:00 | 133 | 00:00 | Panchagarh | 131 | 05:00 | 113 | 10:00
| Chauddagram | 135 | 09:00 | 127 | 20:00 | Patuakhali | 136 | 04:00 | 133 | 18:00
| Chhatak | 134 | 00:00 | 131 | 12:00 | Payra | 138 | 03:00 | 135 | 12:00
| Chowmuhani | 130 | 07:00 | 115 | 12:00 | PHP | 135 | 09:00 | 126 | 21:00
| Chuadanga | 140 | 05:00 | 129 | 12:00 | Postogola | 138 | 04:00 | 130 | 13:00
| Coxsbazar | 128 | 03:00 | 122 | 19:00 | Purbachal | 142 | 04:00 | 131 | 12:00
| Cumilla(N) | 139 | 17:00 | 131 | 12:00 | Purbasadipur | 132 | 17:00 | 116 | 18:00
| Cumilla(S) | 137 | 09:00 | 129 | 12:00 | Rahanpur | 136 | 02:00 | 132 | 08:00
| Daudkandi | 136 | 14:00 | 129 | 12:00 | Rahim | 137 | 14:00 | 124 | 19:00
| Dhaka | 137 | 05:00 | 131 | 12:00 | Rajbari | 136 | 04:00 | 130 | 11:00
| Dhamrai | 138 | 04:00 | 131 | 12:00 | Rajendrapur | 134 | 05:00 | 128 | 19:30
| Dhanmondi | 138 | 17:00 | 133 | 12:00 | Rajshahi | 137 | 05:00 | 130 | 18:00
| Dohazari | 133 | 14:00 | 129 | 12:00 | Rajshahi-230 | 138 | 04:00 | 129 | 18:00
| Faridpur | 135 | 03:00 | 130 | 12:00 | Ramganj | 134 | 09:00 | 105 | 12:00
| Fatullah | 138 | 04:00 | 133 | 12:00 | Rampur | 135 | 03:00 | 130 | 19:00
| Fenchuganj | 137 | 17:00 | 134 | 13:00 | Rampura | 137 | 04:00 | 130 | 12:00
| Feni | 134 | 10:00 | 125 | 20:00 | Rangamati | 136 | 04:00 | 131 | 13:00
| Ghorashal | 143 | 01:00 | 139 | 11:00 | Rangpur | 132 | 14:00 | 121 | 08:00
| Goalpara | 138 | 04:00 | 128 | 19:00 | Ruppur | 140 | 05:00 | 133 | 18:30
| Gollamari | 136 | 05:00 | 130 | 12:00 | Saidpur | 132 | 04:00 | 118 | 18:00
| Gopalganj | 136 | 05:00 | 129 | 12:00 | Satkhira | 135 | 04:00 | 127 | 18:30
| Gopalganj-400 | 136 | 05:00 | 130 | 12:00 | Satmasjid | 141 | 04:00 | 135 | 12:00
| Gulshan | 136 | 04:00 | 131 | 12:00 | Savar | 137 | 01:00 | 132 | 12:00
| Halishahar | 136 | 05:00 | 130 | 19:00 | SevenRings | 144 | 04:00 | 139 | 12:00
| Haripur | 137 | 14:00 | 133 | 12:00 | ShahCement | 137 | 04:00 | 133 | 00:00
| HaripurSBU | 137 | 14:00 | 133 | 12:00 | Shahjadpur | 143 | 03:00 | 136 | 18:30
| Hasnabad | 139 | 17:00 | 134 | 12:00 | Shahjibazar | 133 | 04:00 | 130 | 00:00
| Hathazari | 137 | 09:00 | 131 | 19:00 | Shahmirpur | 136 | 09:00 | 131 | 12:00
| Ishurdi | 141 | 05:00 | 134 | 12:00 | Shariatpur | 136 | 03:00 | 130 | 12:00
| Jaldhaka | 132 | 04:00 | 117 | 18:00 | Sherpur | 134 | 11:00 | 120 | 16:00
| Jamalpur | 136 | 11:00 | 124 | 16:00 | Shikalbaha | 126 | 09:00 | 120 | 18:30
| Jashore | 137 | 05:00 | 128 | 19:00 | Shikalbaha-230 | 137 | 04:00 | 132 | 19:30
| Jhenaidah | 140 | 06:00 | 132 | 19:00 | Shitalakhya | 137.6 | 05:00 | 132 | 12:00
| Jhenaidah-230 | 141 | 04:00 | 133 | 12:00 | Sholosohor | 136 | 09:00 | 131 | 12:00
| Joydebpur | 142 | 18:00 | 135 | 12:00 | Shyampur | 137 | 17:00 | 134 | 00:00
| Joypurhat | 134 | 02:00 | 124 | 08:00 | Shyampur-230 | 138 | 04:00 | 135 | 00:00
| Juldah | 136 | 17:00 | 131 | 19:00 | Siddhirganj | 137 | 14:00 | 132 | 12:00
| Kabirpur | 138 | 14:00 | 130 | 12:00 | Sirajganj | 138 | 03:00 | 128 | 18:30
| Kachua | 134 | 03:00 | 119 | 12:00 | Sonargaon | 135 | 05:00 | 132 | 00:00
| Kaliakoir | 137 | 17:00 | 133 | 15:00 | Sreemongol | 133 | 01:00 | 131 | 10:00
| Kallyanpur | 135 | 02:00 | 130 | 12:00 | Sreepur | 135 | 14:00 | 130 | 12:00
| Kalurghat | 136 | 05:00 | 130 | 19:00 | Srinagar | 136 | 06:00 | 131 | 12:00
| Kamrangirchar | 137 | 17:00 | 128 | 13:00 | SSM | 139 | 18:00 | 135 | 19:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 133 | 04:00 | 130 | 16:00
| Kazla | 135 | 05:00 | 129 | 13:00 | Sylhet | 135 | 05:00 | 132 | 11:00
| Keranigonj | 137 | 05:00 | 131 | 12:00 | Sylhet-132 | 134 | 02:00 | 132 | 16:00
| Khagrachori | 136 | 04:00 | 131 | 19:00 | Tangail | 134 | 14:00 | 128 | 18:30
| Khulna | 135 | 15:00 | 128 | 20:00 | Thakurgaon | 132 | 17:00 | 112 | 18:00
| Khulna(S) | 137 | 05:00 | 130 | 12:00 | TK | 136 | 05:00 | 130 | 12:00
| Khulshi | 135 | 06:00 | 129 | 19:00 | Tongi | 140 | 05:00 | 134 | 11:00
| Kishoreganj | 138 | 02:00 | 132 | 12:00 | Ullon | 138 | 12:00 | 132 | 11:00
| Kodda | 142 | 17:00 | 128 | 19:00 | Uttara | 140 | 04:00 | 133 | 12:00
| KSRM | 135 | 04:00 | 129 | 19:00 | UttaraNew | 141 | 04:00 | 132 | 12:00
| Kulaura | 135 | 01:00 | 133 | 15:00 | Zigatola | 137 | 04:00 | 131 | 13:00
| Kurigram | 132 | 05:00 | 119 | 18:00
| Kushtia | 139 | 04:00 | 131 | 18:00

## L-Curve
Date | 2023-12-22
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 554 | 4151 | 3326 | 7477 |  |  |  | QF-LDC-11
0:30 | 402 | 4358 | 3178.5 | 7536.5 | Date: | 2023-12-22
1:00 | 250 | 4565 | 3031 | 7596
1:30 | 235 | 4542.5 | 2895 | 7437.5
2:00 | 220 | 4520 | 2759 | 7279
2:30 | 206 | 4517 | 2654 | 7171 | [5 empty] | Gen. at Eve. Peak | 8694 | 8694 MW (18:00 )
3:00 | 192 | 4514 | 2549 | 7063 | [6 empty] | 18:00
3:30 | 186 | 4398.5 | 2546.5 | 6945 | [5 empty] | Gen. at Day Peak | 8173 | 8173 MW (12:00 )
4:00 | 180 | 4283 | 2544 | 6827 | [6 empty] | 12:00
4:30 | 182 | 4230.5 | 2497 | 6727.5 | [5 empty] | Highest Generation | 8737
5:00 | 184 | 4178 | 2450 | 6628 | [6 empty] | 13:00
5:30 | 187 | 4220 | 2512 | 6732
6:00 | 190 | 4262 | 2574 | 6836
6:30 | 150 | 4323 | 2575.5 | 6898.5
7:00 | 110 | 4384 | 2577 | 6961
7:30 | 177 | 4502 | 2704 | 7206
8:00 | 244 | 4620 | 2831 | 7451
8:30 | 212 | 4626 | 2828 | 7454
9:00 | 180 | 4632 | 2825 | 7457
9:30 | 177 | 4635.5 | 2801 | 7436.5
10:00 | 174 | 4639 | 2777 | 7416
10:30 | 291 | 4564 | 2957 | 7521
11:00 | 408 | 4489 | 3137 | 7626
11:30 | 422 | 4647 | 3252.5 | 7899.5
12:00 | 436 | 4805 | 3368 | 8173
12:30 | 448 | 4916 | 3539 | 8455
13:00 | 460 | 5027 | 3710 | 8737
13:30 | 480 | 4643 | 3418 | 8061
14:00 | 500 | 4259 | 3126 | 7385
14:30 | 460 | 4189.5 | 2972 | 7161.5
15:00 | 420 | 4120 | 2818 | 6938
15:30 | 417 | 4096 | 2788.5 | 6884.5
16:00 | 414 | 4072 | 2759 | 6831
16:30 | 432 | 4190 | 2894.5 | 7084.5
17:00 | 450 | 4308 | 3030 | 7338
17:30 | 328 | 4678 | 3338 | 8016
18:00 | 206 | 5048 | 3646 | 8694
18:30 | 230 | 4928 | 3750.5 | 8678.5
19:00 | 254 | 4808 | 3855 | 8663
19:30 | 240 | 4770 | 3914 | 8684
20:00 | 260 | 4763 | 3914 | 8677 |  |  |  | Executive Engineer
20:30 | 320 | 4768 | 3865.5 | 8633.5 |  |  |  | Network Operation Division
21:00 | 380 | 4773 | 3817 | 8590
21:30 | 400 | 4734 | 3679 | 8413
22:00 | 420 | 4695 | 3541 | 8236 |  |  |  |  | Page 6 of 7
22:30 | 488 | 4539.5 | 3503.5 | 8043
23:00 | 556 | 4384 | 3466 | 7850
23:30 | 555 | 4267.5 | 3396 | 7663.5
24:00 | 554 | 4151 | 3326 | 7477
8694 MW (18:00 )
8173 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-12-22 |  | Energy |  | 185188268
QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 2499 | 720 | 1286 | 0 | 17 | 2785 | 86 | 0 | 0 | 84 | 0 | 0 | 0
0:30 | 2621 | 600 | 1310.5 | 0 | 8.5 | 2827.5 | 86 | 0 | 0 | 83 | 0 | 0 | 0 |  | Date: | 43820
1:00 | 2743 | 480 | 1335 | 0 | 0 | 2870 | 86 | 0 | 0 | 82 | 0 | 0 | 0
1:30 | 2732.5 | 477.5 | 1323.5 | 0 | 0 | 2744 | 86 | 0 | 0 | 74 | 0 | 0 | 0 | [8 empty] | Total Energy | 185.1883 | 185.1883 | Total Energy Gen 185.188 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 185.188 MKWHr
2:00 | 2722 | 475 | 1312 | 0 | 0 | 2618 | 86 | 0 | 0 | 66 | 0 | 0 | 0 | [8 empty] | Energy not Served | 0 | 0
2:30 | 2718.5 | 474.5 | 1310.5 | 0 | 0 | 2509.5 | 86 | 0 | 0 | 72 | 0 | 0 | 0 | [8 empty] | Energy Requirement | 185.1883 | 185.1883
3:00 | 2715 | 474 | 1309 | 0 | 0 | 2401 | 86 | 0 | 0 | 78 | 0 | 0 | 0
3:30 | 2687.5 | 474 | 1270.5 | 0 | 0 | 2352 | 86 | 0 | 0 | 75 | 0 | 0 | 0 | [7 empty] | Shortage
4:00 | 2660 | 474 | 1232 | 0 | 0 | 2303 | 86 | 0 | 0 | 72 | 0 | 0 | 0
4:30 | 2635.5 | 474 | 1181.5 | 0 | 0 | 2278.5 | 86 | 0 | 0 | 72 | 0 | 0 | 0
5:00 | 2611 | 474 | 1131 | 0 | 0 | 2254 | 86 | 0 | 0 | 72 | 0 | 0 | 0
5:30 | 2650 | 474 | 1188 | 0 | 0 | 2261 | 86 | 0 | 0 | 73 | 0 | 0 | 0
6:00 | 2689 | 474 | 1245 | 0 | 0 | 2268 | 86 | 0 | 0 | 74 | 0 | 0 | 0
6:30 | 2719.5 | 474 | 1272 | 0 | 0 | 2266.5 | 86 | 0 | 0 | 75 | 5.5 | 0 | 0 | [6 empty] | Coal
7:00 | 2750 | 474 | 1299 | 0 | 0 | 2265 | 86 | 0 | 0 | 76 | 11 | 0 | 0
7:30 | 2764 | 355 | 1378 | 0 | 33 | 2463 | 86 | 0 | 0 | 77 | 50 | 0 | 0 | [5 empty] | Oil
8:00 | 2778 | 236 | 1457 | 0 | 66 | 2661 | 86 | 0 | 0 | 78 | 89 | 0 | 0
8:30 | 2769 | 236 | 1397.5 | 0 | 70.5 | 2667.5 | 86 | 0 | 0 | 76 | 151.5 | 0 | 0
9:00 | 2760 | 236 | 1338 | 0 | 75 | 2674 | 86 | 0 | 0 | 74 | 214 | 0 | 0
9:30 | 2743 | 236 | 1298.5 | 0 | 95.5 | 2641.5 | 86 | 0 | 0 | 77 | 259 | 0 | 0
10:00 | 2726 | 236 | 1259 | 0 | 116 | 2609 | 86 | 0 | 0 | 80 | 304 | 0 | 0
10:30 | 2676.5 | 458 | 1218.5 | 0 | 117.5 | 2549.5 | 86 | 0 | 0 | 85 | 328.5 | 1.5 | 0
11:00 | 2627 | 680 | 1178 | 0 | 119 | 2490 | 86 | 0 | 0 | 90 | 353 | 3 | 0
11:30 | 2704.5 | 693.5 | 1246.5 | 0 | 137 | 2561 | 86 | 0 | 8 | 99 | 362 | 2 | 0
12:00 | 2782 | 707 | 1315 | 0 | 155 | 2632 | 86 | 0 | 16 | 108 | 371 | 1 | 0
12:30 | 2743.5 | 707.5 | 1412.5 | 0 | 206 | 2802.5 | 86 | 0 | 26 | 110 | 360.5 | 0.5 | 0
13:00 | 2705 | 708 | 1510 | 0 | 257 | 2973 | 86 | 0 | 36 | 112 | 350 | 0 | 0
13:30 | 2705 | 708 | 1510 | 0 | 257 | 2973 | 86 | 0 | 36 | 112 | 350 | 0 | 0
14:00 | 2705 | 708 | 1510 | 0 | 257 | 2973 | 86 | 0 | 36 | 112 | 350 | 0 | 0
14:30 | 2605 | 688.5 | 1239 | 0 | 145.5 | 2686.5 | 86 | 0 | 19.5 | 94 | 273 | 0.5 | 0
15:00 | 2505 | 669 | 968 | 0 | 34 | 2400 | 86 | 0 | 3 | 76 | 196 | 1 | 0
15:30 | 2506.5 | 668.5 | 978.5 | 0 | 25.5 | 2392 | 86 | 0 | 10 | 76 | 141 | 0.5 | 0
16:00 | 2508 | 668 | 989 | 0 | 17 | 2384 | 86 | 0 | 17 | 76 | 86 | 0 | 0
16:30 | 2538.5 | 669.5 | 1033.5 | 0 | 80 | 2536 | 86 | 0 | 17 | 76 | 48 | 0 | 0
17:00 | 2569 | 671 | 1078 | 0 | 143 | 2688 | 86 | 0 | 17 | 76 | 10 | 0 | 0
17:30 | 2645 | 694.5 | 1316 | 0 | 279 | 2884 | 86 | 0 | 24.5 | 82 | 5 | 0 | 0
18:00 | 2721 | 718 | 1554 | 0 | 415 | 3080 | 86 | 0 | 32 | 88 | 0 | 0 | 0
18:30 | 2755.5 | 718.5 | 1568.5 | 0 | 246.5 | 3198.5 | 86 | 0 | 16 | 89 | 0 | 0 | 0
19:00 | 2790 | 719 | 1583 | 0 | 78 | 3317 | 86 | 0 | 0 | 90 | 0 | 0 | 0
19:30 | 2785 | 698 | 1583 | 0 | 70 | 3372 | 86 | 0 | 0 | 90 | 0 | 0 | 0
20:00 | 2762 | 698 | 1592 | 0 | 70 | 3369 | 86 | 0 | 0 | 100 | 0 | 0 | 0
20:30 | 2769.5 | 756 | 1592.5 | 0 | 66 | 3262.5 | 86 | 0 | 0 | 101 | 0 | 0 | 0
21:00 | 2777 | 814 | 1593 | 0 | 62 | 3156 | 86 | 0 | 0 | 102 | 0 | 0 | 0
21:30 | 2757.5 | 813.5 | 1597.5 | 0 | 39.5 | 3019 | 86 | 0 | 0 | 100 | 0 | 0 | 0
22:00 | 2738 | 813 | 1602 | 0 | 17 | 2882 | 86 | 0 | 0 | 98 | 0 | 0 | 0
22:30 | 2645.5 | 814 | 1567 | 0 | 8.5 | 2829 | 86 | 0 | 0 | 93 | 0 | 0 | 0
23:00 | 2553 | 815 | 1532 | 0 | 0 | 2776 | 86 | 0 | 0 | 88 | 0 | 0 | 0
23:30 | 2526 | 767.5 | 1409 | 0 | 8.5 | 2780.5 | 86 | 0 | 0 | 86 | 0 | 0 | 0 |  | Max Temp. in Dhaka |  | 27.5°C
24:00 | 2499 | 720 | 1286 | 0 | 17 | 2785 | 86 | 0 | 0 | 84 | 0 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 185.188 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 185.188 MKWHr
Note on W13: Author:

## Generation
g | 2023-12-22
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1108680
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 972000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 6 | 12 | 15 | 17 | 17 | 17 | 15 | 11 | 5 | 0 | [9 empty] | 116235
6 | Sikalbaha 225MW CCPP (Gas) | 226 | 226 | 227 | 226 | 226 | 226 | 226 | 226 | 227 | 227 | 228 | 229 | 201 | 201 | 201 | 201 | 201 | 225 |  | 227 | 226 | 226 | 226 | 224 | 226 | 227 | 5255411
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [12 empty] | 4 | 8 | 3 | 17 | 17 |  |  |  | 0 | [5 empty] | 55595
12 | Hathazari 100 MW peaking PP | [26 empty] | 0
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [16 empty] | 2 | 17 | [8 empty] | 31781
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [25 empty] | 0 | 0
19 | Ashuganj 195 MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 45 | 8 | 8 | 8 | 8 | 38 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 468364
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 350 | 310 | 310 | 310 | 310 | 330 |  | 335 | 310 | 305 | 305 | 305 | 307 | 307 | 7690908
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 45 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 48 | 48 | 48 | 10 | 10 | 10 | 48 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 1020456
33 | Ashuganj 225 MW CCPP
34 | Ashuganj 450 MW CCPP(South) | 270 | 270 | 270 | 270 | 270 | 315 | 345 | 305 | 275 | 285 | 275 | 345 | 280 | 275 | 305 | 325 | 305 | 290 |  | 330 | 315 | 305 | 305 | 305 |  | 0 | 6706000
Ashuganj 450 MW CCPP(North)
| Ashuganj 420 MW CCPP(East) | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 360 | 390 | 350 | 300 | 305 | 370 | 240 | 240 | 240 | 240 | 310 |  | 350 | 350 | 350 | 350 | 350 | 393 | 350 | 7878000
35 | Ashuganj 55 MW PP (Precision) | 54 | 54 | 34 | 6 | 6 | 6 | 6 | 15 | 36 | 50 | 53 | 51 | 49 | 31 | 10 | 10 | 10 | 36 |  | 50 | 53 | 53 | 53 | 53 | 34 | 3 | 765120
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 289 | 278 | 270 | 259 | 256 | 247 | 254 | 273 | 309 | 323 | 322 | 322 | 348 | 303 | 291 | 282 | 300 | 281 |  | 273 | 269 | 264 | 251 | 270 | 271 | 262 | 6908400
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 400 | 400 | 400 | 350 | 350 | 350 | 350 | 350 | 350 | 380 | 350 | 350 | 450 | 320 | 320 | 320 | 320 | 420 |  | 420 | 420 | 420 | 420 | 420 | 370 | 370 | 9038500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 75 | 75 | 75 | 75 | 86 | 86 | 73 | 71 | 64 | 66 | 61 | 61 | 61 | 61 | 67 | 75 | 75 | 75 |  | 75 | 75 | 76 | 75 | 75 | 96 | 97 | 1730880
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 13 | 25 | 41 | 43 | 48 | 46 | 39 | 29 | 11 | 1 | [9 empty] | 296410
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 0 | [14 empty] | 465000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 63 | 61 | 61 | 61 | 40 | 40 | 63 | 63 | 40 | 40 | 40 | 40 | 62 | 40 | 40 | 40 | 63 | 62 |  | 62 | 62 | 63 | 62 | 63 | 63 | 40 | 1276512
48 | Shahjibazar 86 MW PP (Shahjibazar) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 10 | 10 | 30 | 30 | 10 | 10 | 10 | 30 | 30 |  | 60 | 60 | 60 | 60 | 60 | 60 | 20 | 779520
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 210 | 210 | 210 | 210 | 210 | 210 | 211 | 210 | 210 |  | 210 | 210 | 210 | 209 | 210 | 210 | 209 | 4229450
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 10 | 10 | 10 |  | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 234540
54 | Hobiganj 11 MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 165360
55 | Fenchugonj 51 MW PP (Barakatullah) | 51 | 51 | 51 | 5 | 5 | 5 | 5 | 42 | 42 | 20 | 20 | 48 | 51 | 10 | 10 | 10 | 14 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 5 | 779400
56 | Shahjahanulla 25 MW PP | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 24 | 24 | 24 | 24 | 0 | 16 | 24 |  | 0 | 16 | 16 | 16 | 16 | 21 | 21 | 479928
57 | Bibiana-II 341 MW CCPP (Summit)
| Bibiyana South 400 MW | 400 | 400 | 400 | 360 | 360 | 360 | 360 | 360 | 400 | 400 | 360 | 400 | 370 | 345 | 355 | 365 | 400 | 400 |  | 370 | 370 | 370 | 400 | 400 | 400 | 400 | 9072300
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 5 | 17 | [7 empty] | 0 | 31150
59 | Tangail Palli Power Gen 22 MW | [11 empty] | 0 | 6 | 6 |  |  |  | 6 | [7 empty] | 0 | 26400
60 | Barabkunda 22 MW PP (Regent) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 359664
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 82 | 66 | 78 | 72 | 72 | 74 | 76 | 78 | 74 | 80 | 90 | 108 | 112 | 94 | 76 | 76 | 76 | 88 |  | 90 | 90 | 100 | 102 | 98 | 88 | 84 | 2065920
64 | Malancha, Ctg. EPZ (United) | 19 | 16 | 22 | 34 | 34 | 34 | 37 | 38 | 38 | 32 | 31 | 17 | 8 | 14 | 15 | 15 | 20 | 16 |  | 17 | 14 | 18 | 18 | 26 | 32 | 41 | 595680
65 | Feni 22 MW PP (Doreen) | 15 | 15 | 15 | 15 | 13 | 13 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 16 | 16 | 16 | 16 | 16 | 346716
66 | Feni 11 MW PP (Doreen) | 10 | [18 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 75240
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 815600
68 | Cumilla 25 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 282060
69 | Summit Ashulia | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 48000
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 9 | 22 | 22 | 15 | 15 | 15 | 275400
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 405360
72 | Rupganj 33 MW PP(Summit) | 30 | 30 | 30 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 776300
73 | Ghorashal 108 MW PP (Regent) | 72 | 69 | 69 | 71 | 12 | 12 | 65 | 65 | 65 | 22 | 22 | 67 | 72 | 12 | 12 | 12 | 60 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1208545
| Feni Lanka Power | [12 empty] | 23 | 17 | 17 |  |  | 17 | [7 empty] | 0 | 86640
| Chowmuhani 113 MW | [19 empty] | 8 | [5 empty] | 0 | 18480
| Manikgonj 162MW PP(MPGL) | [25 empty] | 0 | 0
77 | Siddhirganj 100 PP(Dutch Bangla) | [25 empty] | 0 | 0
78 | Gazipur 52 MW PP | [16 empty] | 8 | 17 | [7 empty] | 0 | 21600
79 | Kodda 150 MW PP | [11 empty] | 16 | 32 | 16 |  |  |  | 32 | [7 empty] | 0 | 90720
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [12 empty] | 9 | 8 |  |  | 2 | 8 | [8 empty] | 44429
| Gazipur 100 MW PP | [12 empty] | 18 |  |  |  | 17 | 17 | [7 empty] | 0 | 42240
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 2 | 2 | 3 | 2 | 3 | 1 | 0 | [10 empty] | 18840
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [8 empty] | 2 | 16 | 17 | 17 | 17 |  |  |  |  | 11 | [7 empty] | 0 | 103710
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | [25 empty] | 0 | 0
| Meghnaghat 104 MW PP (OPCL) | [25 empty] | 0 | 0
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44 MW (Energyprima) | 20 | 20 | 20 | 5 | 5 | 5 | 5 | 42 | 20 | 20 | 20 | 36 | 42 | 10 | 10 | 10 | 32 | 38 |  | 39 | 39 | 43 | 44 | 45 | 5 | 5 | 628344
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 10 | 10 | 10 | 43 | 43 | 10 | 10 | 30 | 43 | 20 | 20 | 20 | 20 | 38 |  | 43 | 43 | 43 | 43 | 43 | 43 | 5 | 869634
94 | Gagnagar 102 MW PP (Digital Power) | [25 empty] | 0 | 0
95 | Patenga 50MW PP (Baraka) | [10 empty] | 0 |  | 3 | 6 |  |  | 5 | 6 | [7 empty] | 0 | 25440
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 | [14 empty] | 0 | 960
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 17 | [7 empty] | 0 | 29568
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 17 | 17 | [7 empty] | 0 | 36701
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 120 | 120 | 120 | 120 | 163 | 120 | 163 | 130 | 130 | 130 | 120 | 120 | 120 | 120 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 120 | 3641318
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 10650
103 | Kamalaghat 54 MW PP(Banco Energy) | [25 empty] | 0 | 0
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [7 empty] | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  |  | 3 | 28 |  | 8 | 8 | 8 |  |  |  | 0 | 117600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [17 empty] | 11 | [7 empty] | 0 | 18144
115 | Juldah 100 MW PP Unit-3 (Acorn) | [16 empty] | 0 | 15 | [7 empty] | 0 | 15360
116 | Chandpur 200 MW (Desh energy) | [8 empty] | 2 | 17 | 17 | 17 | 17 | 17 |  |  |  | 17 | [7 empty] | 0 | 138240
117 | Ashuganj 150 MW PP (Midland) | [12 empty] | 1 | 11 |  |  |  | 8 | [7 empty] | 0 | 33454
118 | Bibiyana-III 400 MW CCPP | 307 | 307 | 307 | 307 | 313 | 355 | 367 | 333 | 335 | 325 | 320 | 388 | 332 | 319 | 366 | 366 | 356 | 365 |  | 395 | 385 | 366 | 367 | 316 | 367 | 367 | 8243000
| Jamalpur 115 MW PP (United) | [7 empty] | 57 | 57 | 57 | 59 | 59 | 59 | 24 |  |  | 5 | 75 |  | 45 | 45 | 45 | 45 |  |  | 0 | 613200
| Anwara 300 MW PP (United) | [16 empty] | 15 | 30 | [7 empty] | 0 | 40145
| Juldah unit-2 (Acorn) | [12 empty] | 12 |  |  |  |  | 12 | [7 empty] | 0 | 29760
| Anlima Energy Ltd. | [8 empty] | 5 | 17 | 17 | 17 | 17 |  |  |  | 1 | 17 | [7 empty] | 0 | 111655
| Bhairob 54.5 MW | [12 empty] | 14 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  | 17 | 200520
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 7 | 17 | 24 | 21 | 27 | 27 | 24 | 17 | 7 | 1 | [9 empty] | 169096
| Chandpur 115(Doreen) | [11 empty] | 1 | 17 | 18 |  |  | 1 | 18 | [7 empty] | 0 | 85440
| Kanchan Purbachal Power Generation Ltd. | [16 empty] | 7 | 17 | [7 empty] | 0 | 49320
| Mirsharai 150 MW (Oil) | [25 empty] | 0 | 0
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 2 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6720
| Matarbari 2*600 MW (CPGCL) | 586 | 584 | 587 | 585 | 581 | 585 | 585 | 585 | 580 | 584 | 584 | 587 | 580 | 585 | 586 | 585 | 584 | 585 |  | 587 | 587 | 585 | 585 | 586 | 585 | 584 | 14159999
120 | Eastern Zone Total | 4565 | 4520 | 4514 | 4283 | 4178 | 4262 | 4384 | 4620 | 4632 | 4639 | 4489 | 4805 | 5027 | 4259 | 4120 | 4072 | 4308 | 5048 |  | 4808 | 4770 | 4763 | 4773 | 4695 | 4384 | 4151 | 108884712
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
Khulna 115 PP MW (KPCL-2)
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [26 empty] | 0
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 2 | 15 | 35 | 50 | 64 | 65 | 60 | 50 | 21 | 17 | 3 | [9 empty] | 393840
131 | Rampal 1320 MW (BIFPCL) | 501 | 408 | 379 | 379 | 374 | 384 | 381 | 461 | 430 | 379 | 378 | 452 | 547 | 412 | 375 | 371 | 451 | 567 |  | 619 | 621 | 618 | 548 | 466 | 409 | 406 | 10720000
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 110 | 110 | 128 | 220 | 220 | 222 | 222 | 220 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 4671300
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [25 empty] | 0 | 0
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 160 | 236 |  | 307 | 307 | 307 | 268 | 168 | 140 | 140 | 4036400
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 120 | 120 | 120 | 120 | 80 | 80 | 80 | 125 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 118 |  | 125 | 125 | 120 | 120 | 120 | 120 | 120 | 2381000
140 | Bhola 33 MW PP (Venture) | 19 | 19 | 17 | 17 | 17 | 19 | 17 | 17 | 16 | 14 | 15 | 19 | 20 | 15 | 13 | 14 | 14 | 20 |  | 21 | 21 | 22 | 22 | 22 | 23 | 20 | 429800
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 480 | 475 | 474 | 474 | 474 | 474 | 474 | 236 | 236 | 236 | 680 | 707 | 708 | 666 | 669 | 668 | 671 | 718 |  | 719 | 698 | 698 | 814 | 813 | 815 | 720 | 14504727
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 450 | 400 | 300 | 290 | 250 | 250 | 250 | 370 | 430 | 400 | 380 | 390 | 520 | 440 | 300 | 280 | 320 | 430 |  | 540 | 622 | 622 | 520 | 420 | 410 | 420 | 10684800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4143600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 1 | 2 | 4 | 3 | 4 | 1 | 1 | 0 | 0 | [9 empty] | 23700
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 336 | 319 | 314 | 313 | 304 | 414 | 414 | 414 | 380 | 340 | 320 | 340 | 380 | 230 | 230 | 260 | 240 | 400 |  | 370 | 370 | 370 | 370 | 370 | 402 | 350 | 8276700
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 104742
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern) | [25 empty] | 0 | 0
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [26 empty] | 0
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [25 empty] | 0 | 0
172 | Confidence Power Bogura Unit-1 113 MW | [25 empty] | 0 | 21600
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 33 | [9 empty] | 28627
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 4 | 5 | 5 | 5 | 5 | 4 | 2 | 0 | [9 empty] | 34621
178 | Energypac Power Venture Thakurgaon Ltd. | [11 empty] | 35 | 35 |  |  |  | 5 | [8 empty] | 0 | 86592
| Intraco Solar 30 MW | [6 empty] | 1 | 7 | 18 | 25 | 30 | 33 | 28 | 25 | 17 | 8 | 0 | [9 empty] | 199369
| Adani Power Jharkhanda Ltd | 703 | 596 | 505 | 419 | 419 | 419 | 419 | 615 | 604 | 616 | 518 | 573 | 666 | 568 | 519 | 528 | 693 | 762 |  | 759 | 755 | 762 | 760 | 767 | 755 | 758 | 14512228
178 | Teesta Solar Limited | [6 empty] | 5 | 37 | 101 | 139 | 165 | 168 | 159 | 136 | 94 | 36 | 5 | [9 empty] | 1049910