## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:November 2023
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2023-11-01 |  | 2023-10-01 |  | 2022-11-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 12608 | 2023-11-02 | 14356 | 2023-10-11 | 11816 | 2022-11-02 | 15648 | 2023-04-19
|  |  | 18:00 |  | 20:00 |  | 19:30 |  | 21:00
2 | Minimum Generation (MW) | 5719 | 2023-11-18 | 8008 | 2023-10-06 | 6286 | 2022-11-26 | - | -
|  |  | 6:00 |  | 6:00 |  | 5:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 12608 | 2023-11-02 | 14356 | 2023-10-11 | 11816 | 2022-11-02 | 15648 | 2023-04-19
|  |  | 18:00 |  | 20:00 |  | 19:30 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 11209 | 2023-11-02 | 12530 | 2023-10-01 | 10385 | 2022-11-06 | 13415 | 2023-04-19
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 12650 | 2023-11-30 | 14470 | 2023-10-30 | 12350 | 2022-11-30 | 16096 | 2023-04-19
|  |  | 18:00 |  | 18:00 |  | 19:30 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 11024.2667 |  | 12963.6129 |  | 10542.4667 |  | - | -
7 | Average Generation (MW) at Day Peak | 9678.8333 |  | 11283.7097 |  | 9065 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 928 | 2023-11-12 | 920 | 2023-10-11 | 934 | 2022-11-03 | 956 | 27/3/2019
|  |  | 5:00 |  | 4:30 |  | 14:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 158 | 2023-11-02 | 160 | 2023-10-01 | 164 | 2022-11-02 | 194 | 12/06/19
|  |  | 18:00 |  | 15:00 |  | 18:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 44 | 2023-11-01 | 244 | 2023-10-12 | 590 | 2022-11-01 | 4395 | 04/10/2022
|  |  | 19:00 |  | 19:00 |  | 20:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 12524 | 2023-11-01 | 13944 | 2023-10-12 | 11710 | 2022-11-01 | 13200 | 04/10/2022
|  | - | 19:00 | - | 19:30 | - | 20:00 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2023-11-05 | 0 | 2023-10-13 | 0 | 2022-11-03 | - | -
|  |  | 19:00 |  | 20:00 |  | 19:00 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 12197 | 2023-11-05 | 12852 | 2023-10-13 | 11389 | 2022-11-03 | - | -
|  |  | 19:00 |  | 20:00 |  | 19:00 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 324 | 2023-11-08 | 469 | 2023-10-23 | 687 | 2022-11-01 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 9911 | 2023-11-08 | 11359 | 2023-10-23 | 9755 | 2022-11-01 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2023-11-05 | 0 | 2023-10-13 | 0 | 2022-11-03 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 10908 | 2023-11-05 | 10593 | 2023-10-13 | 9802 | 2022-11-03 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 5 |  | 17 |  | 6 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 6 |  | 8 |  | 9 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 1832.996 |  | 2096.5113 |  | 1533.0853 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 22.2246 |  | 34.051 |  | 55.0324 |  | - | -
22 | Net Generation of BPDB (MKWH) | 1810.7714 |  | 2062.4603 |  | 1478.0529 |  | - | -
23 | Net Generation of IPP (MKWH) | 3456.7822 |  | 4679.0652 |  | 3716.1938 |  | - | -
24 | Net Generation of REB (MKWH) | 102.6847 |  | 117.5706 |  | 121.4005 |  | - | -
24 | Net Generation of Rental Power Plant (MKWH) | 101.6965 |  | 198.4182 |  | 303.1191 |  | - | -
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 5471.9348 |  | 7057.5143 |  | 5618.7664 |  | 7842.9924 | April'22
26 | Energy Generation by Gas (MKWH) | 3323.4316 |  | 4220.4017 |  | 3245.2459 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 7.0767 |  | 47.9579 |  | 89.5319 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 495.1555 |  | 944.7542 |  | 1539.4443 |  | 2365.7466 | April'22
29 | Energy Generation by Hydro (MKWH) | 87.2163 |  | 134.4035 |  | 69.4238 |  | 104.66 | Sep-22
30 | Energy Generation by Solar (MKWH) | 37.3187 |  | 72.0839 |  | 40.0437 |  | 40.58 | March-22
31 | Energy Generation by Coal (MKWH) | 835.1367 |  | 906.2581 |  | 690.1091 |  | 950.96 | Sep'22
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 641.9939 |  | 723.4527 |  | 667.8391 |  | 776.67 | August-22
33 | Monthly Load Factor (%) | 70.0491 |  | 78.905 |  | 80.1744 |  | 92.62 | August-22

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:November 2023
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 12608 | 2023-11-02 | 18:00
Generation Period
| Dhaka | MW | 4640.2
| Chattogram | MW | 1347.55
| Cumilla | MW | 1185
| Mymensingh | MW | 984
| Sylhet | MW | 497
a) | Total supply in East zone | MW | 8653.75
| Khulna | MW | 1443.6
| Barisal | MW | 375
| Rajshahi | MW | 1142.8
| Rangpur | MW | 745
b) | Total supply in West zone | MW | 3706.4
c) | Total supply in both zone ( a+b) | MW | 12360.15
Ref: | 27.21.0000.603.16.087.20.742 | Date: 17/12/2023
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:November 2023
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 300 | 2023-11-16 | 18:00
| b) Ishurdi end | MW | 338 | 2023-11-07 | 15:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 1100 | 2023-11-07 | 15:00
| b) Ishurdi end | MW | 110 | 2023-11-16 | 18:30
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 1.0295
| b) Ishurdi end | MKWH | 116.6242
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 113.1255
| b) Ishurdi end | MKWH | 0.99952
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 20 | 2023-11-16 | 18:00
| b)Serajganj end | MW | 630 | 2023-11-07 | 14:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 350 | 2023-11-07 | 16:00
| b)Sirajganj end | MW | 16 | 2023-11-16 | 18:30
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 0.0078
| b)Sirajganj end | MKWH | 264.354
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 261.2234
| b)Sirajganj end | MKWH | 0.008
30 | Transmission loss of EWI /NO-2 | % | 1.184%
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 2122 | 26.11.2023 | 14:30
|  | MW | 1396
| b) Aminbazar end | AMPS | -
|  | MW | -
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | -
|  | MW | -
| b) Aminbazar end | AMPS | 2102 | 26.11.2023 | 14:30
|  | MW | 1390
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 23425.536 | 28.11.2023 | N/A
| a) Aminbazar end | MWh | - | -
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | - | - | N/A
| a) Aminbazar end | MWh | 23395.454 | 28.11.2023
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MWh | 639704.45
| b) Aminbazar end (ckt-1 ) | MWh | -
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | -
| b) Aminbazar end (ckt-2 ) | MWh | 635750.001
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | 0.0465
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
[9 empty] | QF-LDC-23 | 8
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: November 2023
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kabirpur 132/33kV Grid Sub-Station | XFR, T-3 HT | 2023-11-11 09:05 | 2023-11-11 11:14 | 2:09 | E/O | Shutdown taken by DPBS-1 due to 33 kV Radio feeder fault. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-3 LT | 2023-11-11 07:28 | 2023-11-11 07:28 | 0:00 | T | 33kv radio feeder loopout from 33kv bus to 33kv source DS Y-phase | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-I HT | 2023-11-26 20:26 | 2023-11-26 22:14 | 1:48 | E/O | 33 KV bus Shutdown | 35 | 63 | Power interruption
Kaliakoir 400/230/132kV Grid Sub-Station | 400kV Bus 2 | 2023-11-25 16:54 | 2023-11-26 09:50 | 16:56 | E/O | Emergency Maintenance. | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-1 (404T) LT | 2023-11-24 17:15 | 2023-11-24 18:06 | 0:51 | E/O | 33 kv T3 Bus coupler DS Sparking problem | 9 | 7.65 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) HT | 2023-11-16 19:51 | 2023-11-16 22:50 | 2:59 | E/O | 33kv katiadi feeder(pbs) bus loop out | 22 | 65.6333 | Power interruption
Mirpur 132/33kV Grid Sub-Station | T1 HT | 2023-11-14 20:20 | 2023-11-15 17:28 | 21:08 | E/O | 132 KV CB Problem ( Hydrolic Unit faulty). | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T1 HT | 2023-11-23 19:41 | 2023-11-24 14:29 | 18:48 | E/O | Hydraulic Pressure Leakage | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T1 HT | 2023-11-25 08:07 | 2023-11-28 16:23 | 80:16 | E/O | T-1 Transformer hydraulic pressure low, motor pump problem. | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-01(E05) HT | 2023-11-18 12:30 | 2023-11-18 14:12 | 1:42 | E/O | shutdown taken by PBS for 33kv CT&PT test purpose. | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-2 LT | 2023-11-18 12:19 | 2023-11-18 12:29 | 0:10 | T | df/dt | 54 | 9 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-1 LT | 2023-11-16 20:02 | 2023-11-16 20:26 | 0:24 | T | 33kV Korotia feeder Earth Fault | 43 | 17.2 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 HT | 2023-11-17 15:53 | 2023-11-17 19:44 | 3:51 | E/O | 33kv bus loop and connector are damaged.(Responsible for BPDB & PBS) | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 LT | 2023-11-16 20:02 | 2023-11-16 20:26 | 0:24 | T | 33kV Korotia feeder Earth Fault | 43 | 17.2 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | 132 kV Bus-1 | 2023-11-05 10:35 | 2023-11-05 16:28 | 5:53 | E/O | Tongi-Basundhara ckt-1 'Bus CT Changing | 0 | 0 | No interruption
|  |  | Total : | 157:19 |  | Unserved Energy: |  | 179.6833
Dhaka (South) Grid Circle :
Haripur 230/132kV Grid Sub-Station | Auto TR-1 HT | 2023-11-17 09:54 | 2023-11-17 11:58 | 2:04 | T | df/dt | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 404 T-1 HT | 2023-11-17 15:05 | 2023-11-17 15:05 | 0:00 | T | 33kv incoming CB exploded. | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 404 T-1 LT | 2023-11-05 15:42 | 2023-11-05 15:58 | 0:16 | T | 33kv aganagar feeder fault | 22 | 5.8667 | Power interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 404 T-1 LT | 2023-11-17 15:05 | 2023-11-17 15:05 | 0:00 | T | Earth fault, 33 kv incoming CB exploded | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 424 T-5 HT | 2023-11-06 08:22 | 2023-11-06 19:13 | 10:51 | E/O | T- 5, 132 kv CT side B phase sparking causes. | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 424 T-5 HT | 2023-11-22 15:36 | 2023-11-22 16:54 | 1:18 | E/O | Red hot 33 kv main bus Isolator, R phase. | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 424 T-5 LT | 2023-11-05 15:42 | 2023-11-05 15:58 | 0:16 | T | 33kv aganagar feeder fault | 22 | 5.8667 | Power interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 424 T-5 LT | 2023-11-17 15:05 | 2023-11-17 17:04 | 1:59 | T | T-1 33 kv incoming CB exploded. | 20 | 39.6667 | Power interruption
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 HT | 2023-11-10 21:10 | 2023-11-10 21:50 | 0:40 | T | Tertiary cable fault | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-1 LT | 2023-11-06 05:42 | 2023-11-06 06:09 | 0:27 | T | 33 kV Hazratpur Feeder Flash | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-2 LT | 2023-11-06 05:42 | 2023-11-06 06:09 | 0:27 | T | 33kV hazaratpur Feeder Flash | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | 132 kV Busbar-2 | 2023-11-08 05:35 | 2023-11-08 07:29 | 1:54 | E/O | Du to raising Temparature at 639 Bus DS | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 HT | 2023-11-08 05:20 | 2023-11-08 07:30 | 2:10 | E/O | Du to raising Temparature at 639 Bus DS | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 HT | 2023-11-17 15:20 | 2023-11-17 16:05 | 0:45 | T | Over voltage due to stormy weather. | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 HT | 2023-11-17 15:26 | 2023-11-17 16:01 | 0:35 | T | Over voltage due to stormy weather | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 HT | 2023-11-16 10:36 | 2023-11-16 11:02 | 0:26 | T | Trip | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2023-11-04 13:27 | 2023-11-04 13:33 | 0:06 | T | PBS 33 kv kabilgonj feeder earth fault trip | 32 | 3.2 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2023-11-25 11:12 | 2023-11-25 12:44 | 1:32 | E/O | Corrective Maintenance at R Phase 33 Kv CT due to high temperature | 36 | 55.2 | Power interruption
|  |  | Total : | 25:46 |  | Unserved Energy: |  | 109.8
Chattogram Grid Circle :
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-1 LT | 2023-11-09 07:34 | 2023-11-09 08:04 | 0:30 | T | Due to Banshkhali 33 kv breaker not tripped. | 20 | 10 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 LT | 2023-11-09 07:34 | 2023-11-09 08:04 | 0:30 | T | Due to Banshkhali 33 Kv breaker not trtipped. | 20 | 10 | Power interruption
GPH 230/33kV Grid Sub-Station | Transformer-01(D05) HT | 2023-11-29 09:49 | 2023-11-29 11:10 | 1:21 | E/O | bushing oil testing | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | 403T(TR-1) LT | 2023-11-04 14:20 | 2023-11-04 15:23 | 1:03 | E/O | Due to red-hot at the point of 33KV CT clamp. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | 403T(TR-1) LT | 2023-11-17 20:52 | 2023-11-17 21:03 | 0:11 | E/O | PDB taken shutdown for emergency work. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | 413T(TR-2) HT | 2023-11-09 12:47 | 2023-11-09 17:43 | 4:56 | E/O | Emergency S/D Due to 132 kV Primary CT (R & Y) Phase Abnormal Sound And no Current Output . | 10 | 49.3333 | Power interruption
Halishahar 132/33kV Grid Sub-Station | 413T(TR-2) LT | 2023-11-17 20:43 | 2023-11-17 21:10 | 0:27 | E/O | PDB taken shutdown for emergency work. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | T-01 HT | 2023-11-09 07:15 | 2023-11-09 10:25 | 3:10 | T | Y Phase Cable puncture, | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | T-01 HT | 2023-11-10 08:10 | 2023-11-10 09:34 | 1:24 | E/O | 33kv XLPE cable reconnection. | 0 | 0 | No interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-01(506T) HT | 2023-11-29 15:02 | 2023-11-29 16:33 | 1:31 | E/O | Bus connector change by bpdb | 0 | 0 | No interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-02(516T) HT | 2023-11-29 11:50 | 2023-11-29 14:32 | 2:42 | E/O | red hot maintainance due to BPDB | 0 | 0 | No interruption
|  |  | Total : | 17:45 |  | Unserved Energy: |  | 69.3333
Cumilla Grid Circle :
Beanibazar 132/33kV Grid Sub-Station | 132 KV BUS-2 | 2023-11-17 11:35 | 2023-11-18 11:22 | 23:47 | E/O | Interlock test for New line-2 Bay with BUS Coupler. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 402T LT | 2023-11-04 07:14 | 2023-11-04 07:18 | 0:04 | T | Trip | 45 | 3 | Power interruption
Brahmanbaria 132/33kV Grid Sub-Station | 403T LT | 2023-11-02 13:47 | 2023-11-02 13:49 | 0:02 | E/O | independent all transformer. | 44 | 1.4667 | Power interruption
Chandpur 132/33kV Grid Sub-Station | 200KVA Aux. T-2 LT | 2023-11-19 22:00 | 2023-11-19 22:00 | 0:00 | E/O | Source alternate | 0 | 0 | No interruption
Chauddagram 132/33kV Grid Sub-Station | 132 kv T-2 LT | 2023-11-24 06:41 | 2023-11-24 06:54 | 0:13 | T | Tripping happened due to 33 KV outgoing feeder fault. | 14 | 3.0333 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | TR1 | 2023-11-10 16:42 | 2023-11-10 18:53 | 2:11 | E/O | 132/33 KV Tr-01 shutdown for Red-hot maintenance | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | TR1-415T HT | 2023-11-13 07:10 | 2023-11-13 17:36 | 10:26 | E/O | For Maintenance Works | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | TR2-425T HT | 2023-11-18 22:22 | 2023-11-18 23:35 | 1:13 | E/O | Red hot maintenance work | 30 | 36.5 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-03 HT | 2023-11-26 21:59 | 2023-11-26 23:07 | 1:08 | T | R phase underground cable blast | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-02 HT | 2023-11-06 12:28 | 2023-11-06 14:47 | 2:19 | E/O | Due to emergency work | 45 | 104.25 | Power interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) HT | 2023-11-08 07:26 | 2023-11-08 07:26 | 0:00 | T | Trip | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) HT | 2023-11-08 08:15 | 2023-11-08 19:12 | 10:57 | E/O | S/D Taken for Maintenance work | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) LT | 2023-11-08 07:26 | 2023-11-08 07:26 | 0:00 | T | Trip | 0 | 0 | No interruption
Ramganj 132/33kV Grid Sub-Station | Transformer -02 LT | 2023-11-30 08:26 | 2023-11-30 09:30 | 1:04 | E/O | Red hot point maintenance at 33 KV bus side | 15 | 16 | Power interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-11-27 17:30 | 2023-11-27 17:36 | 0:06 | T | 10 MW And 28 MW PS Trip | 0 | 0 | No interruption
|  |  | Total : | 53:30 |  | Unserved Energy: |  | 164.25
Khulna Grid Circle :
Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 2023-11-21 07:08 | 2023-11-21 07:15 | 0:07 | T | 33kV Nolcity,Jhalokathi and Dopdabia-2 WZPDCL Feeder fault. | 33 | 3.85 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2023-11-21 07:08 | 2023-11-21 07:15 | 0:07 | T | Nolcity,Jhalokathi and Dopdabia-2 WZPDCL 33kV Feeder fault. | 20 | 2.3333 | Power interruption
Benapole 132/33kV Grid Sub-Station | Transformer-1(406T) LT | 2023-11-12 14:40 | 2023-11-12 15:02 | 0:22 | T | Benapole 33 kv feeder fault | 38 | 13.9333 | Power interruption
Benapole 132/33kV Grid Sub-Station | Transformer-1(406T) LT | 2023-11-30 19:39 | 2023-11-30 20:11 | 0:32 | E/O | VT MCB fail maintenance | 0 | 0 | No interruption
Benapole 132/33kV Grid Sub-Station | Transformer-2(416T) LT | 2023-11-12 14:40 | 2023-11-12 15:05 | 0:25 | T | Benapole 33 KV feeder fault | 38 | 15.8333 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-11-17 09:13 | 2023-11-17 09:21 | 0:08 | T | T-1A trip due to Rajapur 33kv feeder. | 2 | 0.26667 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-11-17 09:13 | 2023-11-17 09:21 | 0:08 | T | T-1A trip due to Rajapur 33kv feeder. | 2 | 0.26667 | Power interruption
Goalpara 132/33kV Grid Sub-Station | T-6 LT | 2023-11-21 13:01 | 2023-11-21 13:37 | 0:36 | T | over load | 29 | 17.4 | Power interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-2 HT | 2023-11-26 10:42 | 2023-11-26 14:03 | 3:21 | E/O | CT oil leakage Maintenance work | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T1-405T HT | 2023-11-24 20:56 | 2023-11-24 21:36 | 0:40 | E/O | WZ 33 kv bus Ds fault maintenance | 17 | 11.3333 | Power interruption
Madaripur 132/33kV Grid Sub-Station | T1-405T LT | 2023-11-16 17:10 | 2023-11-16 17:43 | 0:33 | T | None | 44 | 24.2 | Power interruption
Madaripur 132/33kV Grid Sub-Station | T2-415T HT | 2023-11-16 17:10 | 2023-11-17 09:25 | 16:15 | T | None | 44 | 715 | Power interruption
Madaripur 132/33kV Grid Sub-Station | T3-426T HT | 2023-11-26 14:13 | 2023-11-26 14:15 | 0:02 | T | CT Firing. | 10 | 0.33333 | Power interruption
Mongla 132/33kV Grid Sub-Station | T-2 LT | 2023-11-13 10:08 | 2023-11-13 10:42 | 0:34 | T | Mongla cement factory feeder trip. | 18 | 10.2 | Power interruption
Narail 132/33kV Grid Sub-Station | TR2 (413-T) HT | 2023-11-16 17:38 | 2023-11-16 19:06 | 1:28 | E/O | Emergency S/D.Sky wire breakdown maintenance work done by Jashore PBS-2 | 10 | 14.6667 | Power interruption
Patuakhali 132/33kV Grid Sub-Station | 405T (T-1) LT | 2023-11-17 15:48 | 2023-11-17 15:57 | 0:09 | T | 33kv incomers tripped due to patuakhali 33kv feeder fault. i.e. there is no load in substation then. Substation load was zero. | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 415T (T-2) HT | 2023-11-21 11:46 | 2023-11-21 12:25 | 0:39 | E/O | T-2 33 kV bussing oil leackge | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 415T (T-2) LT | 2023-11-17 15:48 | 2023-11-17 15:57 | 0:09 | T | 33kv incomers tripped due to patuakhali 33kv feeder fault. i.e. there is no load in substation then. Substation load was zero. | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 425T (T-3) LT | 2023-11-17 15:48 | 2023-11-17 15:57 | 0:09 | T | 33kv incomers tripped due to patuakhali 33kv feeder fault. i.e. there is no load in substation then. Substation load was zero. | 0 | 0 | No interruption
Shariatpur 132/33kV Grid Sub-Station | T2-416T HT | 2023-11-24 10:30 | 2023-11-24 10:41 | 0:11 | E/O | Maintenance by PBS | 10 | 1.8333 | Power interruption
Shariatpur 132/33kV Grid Sub-Station | T2-416T LT | 2023-11-24 10:29 | 2023-11-24 10:42 | 0:13 | E/O | Maintenance by PBS | 10 | 2.1667 | Power interruption
|  |  | Total : | 26:48 |  | Unserved Energy: |  | 833.6167
HVDC Grid Circle :
Ishurdi 230/132kV Grid Sub-Station | 230 kV Bus 1 | 2023-11-19 12:14 | 2023-11-19 19:20 | 7:06 | E/O | PT oil leakage maintanance | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 HT | 2023-11-25 17:33 | 2023-11-25 18:10 | 0:37 | T | None | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 HT | 2023-11-05 05:47 | 2023-11-05 12:15 | 6:28 | T | None | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 HT | 2023-11-19 11:45 | 2023-11-19 19:24 | 7:39 | E/O | 230 kv bus pt R phase oil leakage maintenance | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 HT | 2023-11-19 19:58 | 2023-11-19 20:02 | 0:04 | E/O | Bus DS Red hot | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Bus-A | 2023-11-02 08:43 | 2023-11-02 10:24 | 1:41 | E/O | 33 KV T2A Incomer (Y-Phase) Maintenence For Loop Counductor | 28 | 47.1333 | Power interruption
Jhenaidah 132/33kV Grid Sub-Station | Bus-B | 2023-11-02 08:43 | 2023-11-02 10:24 | 1:41 | E/O | 33 KV T2A Incomer (Y-Phase) Maintenence For Loop Counductor | 28 | 47.1333 | Power interruption
Jhenaidah 132/33kV Grid Sub-Station | Transformer T-2 LT | 2023-11-02 08:35 | 2023-11-02 10:27 | 1:52 | E/O | 33 KV T2A Incomer (Y-Phase) Maintenence For Loop Counductor | 28 | 52.2667 | Power interruption
Ruppur 132/11kV Grid Sub-Station | TR-01 HT | 2023-11-06 06:25 | 2023-11-06 07:32 | 1:07 | E/O | 11 Kv incoming connection point B Phase Red Hot. | 2.5 | 2.7917 | Power interruption
|  |  | Total : | 28:15 |  | Unserved Energy: |  | 149.325
Bogura Grid Circle:
Amnura 132/33kV Grid Sub-Station | Bus-2 | 2023-11-05 14:53 | 2023-11-05 16:58 | 2:05 | E/O | Due to emergency maint. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T HT | 2023-11-14 12:25 | 2023-11-14 12:25 | 0:00 | T | Bucholz Trip OLTC | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T HT | 2023-11-14 12:54 | 2023-11-14 13:28 | 0:34 | E/O | OLTC Bucholz Trip | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T LT | 2023-11-14 12:25 | 2023-11-14 12:25 | 0:00 | T | Bucholz Trip OLTC | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-1 (404T) LT | 2023-11-02 07:15 | 2023-11-02 07:40 | 0:25 | T | 33 KV Nandigram Feeder fault | 38 | 15.8333 | Power interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-2 (414T) LT | 2023-11-02 07:15 | 2023-11-02 07:42 | 0:27 | T | 33 KV Nandigram Feeder fault | 38 | 17.1 | Power interruption
Bogura 132/33kV Grid Sub-Station | 132KV Bus-B | 2023-11-24 07:56 | 2023-11-24 11:05 | 3:09 | E/O | 132/33 kV Transformer-3 HT Forced S/D due to Red hot to Auxiliary DS.. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-3 HT | 2023-11-24 08:07 | 2023-11-24 11:27 | 3:20 | E/O | Red hot to Auxiliary DS. | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2023-11-01 11:35 | 2023-11-01 14:06 | 2:31 | E/O | T1 33 kV bus PT maintenance. | 25 | 62.9167 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2023-11-02 14:28 | 2023-11-02 17:13 | 2:45 | E/O | PT maintenance | 25 | 68.75 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2023-11-05 10:55 | 2023-11-05 12:36 | 1:41 | E/O | PT fuse maintenance. | 21 | 35.35 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2023-11-29 15:49 | 2023-11-29 17:21 | 1:32 | E/O | Emergency maintenance work of T1 33 kV incoming CB. | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-2 LT | 2023-11-26 08:55 | 2023-11-29 14:53 | 77:58 | E/O | 33 kv incoming CB fault | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 33 kV T-3 Bus | 2023-11-16 21:38 | 2023-11-16 23:02 | 1:24 | E/O | Post insulator of Durgapur & Bagha feeder adjacent to 33 Kv BUS are cracked. | 25 | 35 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-1(405T) LT | 2023-11-18 09:55 | 2023-11-18 10:01 | 0:06 | T | Bucholz Trip OLTC | 15 | 1.5 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) LT | 2023-11-16 19:18 | 2023-11-16 23:02 | 3:44 | T | Insulator of BUS D/S of Durgapur & Bagha feeder is cracked. | 25 | 93.3333 | Power interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132/33 kV T-01 (406T) HT | 2023-11-05 11:28 | 2023-11-05 12:24 | 0:56 | E/O | 132/33 kV T-1, NIFPS MAINTAINING | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-01 LT | 2023-11-17 16:10 | 2023-11-17 17:27 | 1:17 | E/O | Gt black outTest. | 0 | 0 | No interruption
|  |  | Total : | 103:54 |  | Unserved Energy: |  | 329.7833
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 413:17 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance | [9 empty] | 498.6333
Month: November 2023 | [9 empty] | 75.4667
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks | 574.1
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mirzapur 132/33kV GIS Grid Sub-Station | Mirzapur-Tangail-ckt-2A(E04) | 2023-11-19 15:20 | 2023-11-19 15:39 | 0:19 | T | Relay Definitive Trip/AR Lockout Under Voltage Stage-1 Trip R-Ph Fault B-Ph Fault Relay General Pickup (R,Y and B-Ph) | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Mirzapur-Tangail-ckt-2A(E04) | 2023-11-20 11:47 | 2023-11-20 12:06 | 0:19 | T | Do not find reason | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Mirzapur-Tangail-ckt-2B(E03) | 2023-11-19 15:20 | 2023-11-19 15:39 | 0:19 | T | Relay Definitive Trip/AR Lockout Under Voltage Stage-1 Trip R-Ph Fault B-Ph Fault Relay General Pickup (R,Y and B-Ph) | 47 | 14.8833 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Mirzapur-Tangail-ckt-2B(E03) | 2023-11-20 11:47 | 2023-11-20 12:06 | 0:19 | T | Donâ€™t find out the Reason | 37 | 11.7167 | Power interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-1 | 2023-11-05 06:32 | 2023-11-05 15:52 | 9:20 | T | OC/EF Fault | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-2 | 2023-11-05 13:22 | 2023-11-05 15:52 | 2:30 | E/O | Due to Sreepur -Ashuganj Ckt-1 trip | 120 | 300 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-1 | 2023-11-05 11:32 | 2023-11-05 17:10 | 5:38 | E/O | Tongi-Basundhara Ckt-1'Y-Phase CT Replace | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Mill Gate Ckt-1 | 2023-11-02 13:39 | 2023-11-02 14:43 | 1:04 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 19:48 |  | Unserved Energy: |  | 326.6
Dhaka (South) Grid Circle :
Fatullah 132/33kV Grid Sub-Station | 132 kV Shyampur-2 | 2023-11-13 12:17 | 2023-11-13 12:26 | 0:09 | T | Trip. | 0 | 0 | No interruption |  | 120.3333 | 251.2167
Haripur 230/132kV Grid Sub-Station | Narsingdi | 2023-11-01 12:53 | 2023-11-01 13:03 | 0:10 | T | Trip. | 0 | 0 | No interruption |  | 14.7833
Haripur 230/132kV Grid Sub-Station | Narsingdi | 2023-11-01 13:43 | 2023-11-01 14:46 | 1:03 | T | Trip. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2023-11-14 07:16 | 2023-11-14 07:26 | 0:10 | T | Trip. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2023-11-17 15:02 | 2023-11-17 15:54 | 0:52 | T | Trip. | 15 | 13 | Power interruption
Hasnabad 132/33kV Grid Substation | Shitallakhya | 2023-11-21 12:21 | 2023-11-21 12:32 | 0:11 | T | Unknown | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Hasnabad-Keraniganj Ckt-1 | 2023-11-07 21:24 | 2023-11-07 23:03 | 1:39 | E/O | oil leakase of CT-8112,B-Ph | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad | 2023-11-21 10:02 | 2023-11-21 11:06 | 1:04 | T | Showing Distance relay of 15.40km | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Lalbagh-3 | 2023-11-25 11:04 | 2023-11-25 11:17 | 0:13 | T | Trip. | 81 | 17.55 | Power interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Bashundhara 132 kv Ckt | 2023-11-16 19:34 | 2023-11-16 21:24 | 1:50 | T | Earth Fault Problem at Mill side of Bashundhara Cement | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Bashundhara 132 kv Ckt | 2023-11-20 09:59 | 2023-11-20 13:58 | 3:59 | E/O | Red hot maintenance | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -DPDC Char sayedpur 132k Ckt-1 | 2023-11-06 11:47 | 2023-11-06 12:13 | 0:26 | E/O | Red hot maintenance | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -DPDC Char sayedpur 132k Ckt-2 | 2023-11-06 12:46 | 2023-11-06 14:12 | 1:26 | E/O | Red hot maintenance | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Munshiganj 132 kv Ckt-1 | 2023-11-23 09:42 | 2023-11-23 10:30 | 0:48 | T | Trip. | 24 | 19.2 | Power interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Munshiganj 132 kv Ckt-2 | 2023-11-23 09:42 | 2023-11-23 11:08 | 1:26 | T | Trip. | 24 | 34.4 | Power interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Shitalakhya 132 kv Ckt | 2023-11-02 05:47 | 2023-11-02 08:45 | 2:58 | E/O | Load management purpose (order by NLDC) | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Shitalakhya 132 kv Ckt | 2023-11-28 12:55 | 2023-11-28 21:29 | 8:34 | T | Hydraulic pressure pipe leakage | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2023-11-02 05:45 | 2023-11-02 08:44 | 2:59 | E/O | Load management purpose (order by NLDC) | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2023-11-17 03:15 | 2023-11-17 03:16 | 0:01 | E/O | Order by NLDC due to load management. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Kazla Ckt -2 | 2023-11-18 19:02 | 2023-11-18 21:25 | 2:23 | E/O | Kazla Ckt-2 Blue phase Line CT side Red hot. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Matuail Single Ckt | 2023-11-17 14:07 | 2023-11-17 19:14 | 5:07 | T | Unknown | 0 | 0 | No interruption
Mogbazar 132/33kV Grid Sub-Station | Rampura 1 | 2023-11-19 06:10 | 2023-11-19 18:31 | 12:21 | E/O | Due to CB problem | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | Haripur | 2023-11-01 18:14 | 2023-11-01 18:41 | 0:27 | E/O | Due to short circuit of 132 kv haripur line with 11 kv palli biddhut line. | 100 | 45 | Power interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2023-11-17 16:30 | 2023-11-17 16:49 | 0:19 | T | Unknown | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Moghbazar-01 | 2023-11-26 14:46 | 2023-11-26 19:52 | 5:06 | T | B phase LA blasted | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Moghbazar-02 | 2023-11-17 07:17 | 2023-11-17 10:13 | 2:56 | T | Unknown | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Moghbazar-02 | 2023-11-19 18:35 | 2023-11-19 19:40 | 1:05 | E/O | Moghbazar 132kV Ckt-2 shutdown due work at Moghbazar End (S/D taken by NLDC). | 0 | 0 | No interruption
Shitalakhya 132/33kV Grid Sub-Station | 132 kV Madanganj | 2023-11-12 10:14 | 2023-11-12 16:30 | 6:16 | E/O | Duet emergency maint.work | 0 | 0 | No interruption
Shitalakhya 132/33kV Grid Sub-Station | 132 kV Madanganj | 2023-11-28 13:09 | 2023-11-28 21:31 | 8:22 | E/O | By NLDC | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 132 kV Shyampur old-2(E10) | 2023-11-20 08:53 | 2023-11-20 09:50 | 0:57 | E/O | Emergency Maintenance | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 100MW Dutch Bangla | 2023-11-08 06:03 | 2023-11-08 09:13 | 3:10 | E/O | Maintenace work. | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2023-11-20 10:10 | 2023-11-20 16:37 | 6:27 | E/O | Oil Licage X-Former EGCB ends. | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 132kV MTR 2 | 2023-11-16 10:36 | 2023-11-16 11:06 | 0:30 | T | Trip | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Haripur 2 | 2023-11-17 09:15 | 2023-11-17 11:58 | 2:43 | E/O | Corrective maintenance of DS 676M | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Ullon 1 | 2023-11-01 06:19 | 2023-11-01 07:33 | 1:14 | E/O | S/D taken by Ullon end | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | 335MW EGCB 1 | 2023-11-17 15:55 | 2023-11-17 17:33 | 1:38 | T | Over voltage | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | 335MW EGCB 2 | 2023-11-17 15:55 | 2023-11-17 17:35 | 1:40 | T | Over Voltage | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Bashundhara Line | 2023-11-18 17:53 | 2023-11-19 16:50 | 22:57 | T | Trip | 0 | 0 | No interruption
|  |  | Total : | 115:36 |  | Unserved Energy: |  | 129.15
Chattogram Grid Circle :
Baroaulia 132/33kV Grid Sub-Station | Kulshi | 2023-11-03 08:11 | 2023-11-03 10:28 | 2:17 | E/O | Red hot | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Feni-1 | 2023-11-03 08:46 | 2023-11-03 09:08 | 0:22 | T | Distance trip | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Feni-1 | 2023-11-08 07:26 | 2023-11-08 07:39 | 0:13 | T | Unknown | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Feni-1 | 2023-11-17 16:33 | 2023-11-17 16:49 | 0:16 | T | Distance trip | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-1 | 2023-11-17 16:54 | 2023-11-17 18:57 | 2:03 | T | Distance Trip | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-2 | 2023-11-17 18:44 | 2023-11-17 18:58 | 0:14 | T | Distance Trip | 6 | 1.4 | Power interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona- Rangamati Ckt-01 | 2023-11-07 14:46 | 2023-11-07 15:16 | 0:30 | T | Distance Trip | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona- Rangamati Ckt-02 | 2023-11-07 14:46 | 2023-11-07 15:21 | 0:35 | T | Distance Trip | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-1 | 2023-11-17 17:32 | 2023-11-17 19:33 | 2:01 | T | Tripped | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Kaptai-01 | 2023-11-28 12:19 | 2023-11-28 13:29 | 1:10 | E/O | Bamboo trimming near to line. | 0 | 0 | No interruption
KSRM 132/33kV Grid Sub-Station | Baraulia Feeder | 2023-11-01 08:41 | 2023-11-01 14:40 | 5:59 | E/O | Barawlia to KSRM line red hot Found | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Chandraghona-2 | 2023-11-20 16:08 | 2023-11-20 16:59 | 0:51 | T | Tripped | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Kulshi-2 | 2023-11-23 12:59 | 2023-11-23 13:13 | 0:14 | T | Tripped | 0 | 0 | No interruption
Sholosohor 132/33kV Grid Sub-Station | Sholoshahar-Khulshi Ckt-1 | 2023-11-05 18:44 | 2023-11-06 00:08 | 5:24 | T | None | 0 | 0 | No interruption
|  |  | Total : | 22:09 |  | Unserved Energy: |  | 1.4
Cumilla Grid Circle :
Beanibazar 132/33kV Grid Sub-Station | Sylhet-Fenchugang -T -Branibazar-1 | 2023-11-16 15:57 | 2023-11-16 16:24 | 0:27 | T | Tripped | 38 | 17.1 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni line-01 | 2023-11-13 11:29 | 2023-11-13 11:43 | 0:14 | T | Tripped | 36 | 8.4 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni line-02 | 2023-11-08 07:28 | 2023-11-08 07:40 | 0:12 | T | Heavy Rain | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Daudkandi Ckt-1 | 2023-11-17 16:38 | 2023-11-17 17:55 | 1:17 | T | Heavy Rain | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Daudkandi Ckt-1 | 2023-11-17 17:57 | 2023-11-17 20:10 | 2:13 | T | Heavy Rain | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sylhet-2 | 2023-11-16 15:55 | 2023-11-16 16:26 | 0:31 | T | Heavy Rain | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Chowmuhani Ckt-2 | 2023-11-13 11:29 | 2023-11-13 11:43 | 0:14 | T | Heavy Rain | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | 132 Fenchuganj-1 | 2023-11-17 15:31 | 2023-11-17 16:14 | 0:43 | T | due to 33kv PDB-2 feeder fault | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | 132 Fenchuganj-2 | 2023-11-17 18:31 | 2023-11-18 00:51 | 6:20 | T | for heavy rain | 0 | 0 | No interruption
Ramganj 132/33kV Grid Sub-Station | Ramgonj- Desh Energy Ckt-01 | 2023-11-18 09:58 | 2023-11-18 14:17 | 4:19 | E/O | tree fallen over the 123 kv line | 0 | 0 | No interruption
Ramganj 132/33kV Grid Sub-Station | Ramgonj-Desh Energy Ckt-02 | 2023-11-18 09:59 | 2023-11-18 14:17 | 4:18 | E/O | tree fallen over the 123 kv line | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-90MW P/S | 2023-11-11 05:17 | 2023-11-11 05:33 | 0:16 | T | Distance Trip | 0 | 0 | No interruption
|  |  | Total : | 21:04 |  | Unserved Energy: |  | 25.5
Khulna Grid Circle :
Barishal 132/33kV Grid Sub-Station | 132kv Bhandaria ckt | 2023-11-17 11:46 | 2023-11-17 11:46 | 0:00 | T | Methily cyclone. | 3 | 0 | Power interruption
Barishal 132/33kV Grid Sub-Station | 132kv Bhandaria ckt | 2023-11-17 11:52 | 2023-11-17 17:27 | 5:35 | E/O | Line faulty. | 3 | 16.75 | Power interruption
Barishal 230/132kV Grid Sub-Station | Bhola Ckt-2 | 2023-11-19 13:00 | 2023-11-19 13:42 | 0:42 | T | Heavy Rain | 0 | 0 | No interruption
Benapole 132/33kV Grid Sub-Station | Jashore-1 | 2023-11-30 17:55 | 2023-11-30 19:04 | 1:09 | E/O | PT Maintenance | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV 50MW Power Station ckt-1 | 2023-11-10 11:52 | 2023-11-11 03:40 | 15:48 | E/O | Unknown | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-1 | 2023-11-26 14:13 | 2023-11-26 14:58 | 0:45 | T | Tripped showing Main protection relays | 3 | 2.25 | Power interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-2 | 2023-11-26 14:13 | 2023-11-26 15:30 | 1:17 | T | Tripped showing Main protection relays | 3 | 3.85 | Power interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-3 | 2023-11-26 14:13 | 2023-11-26 15:34 | 1:21 | T | Tripped showing Main protection relays | 2 | 2.7 | Power interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-4 | 2023-11-26 14:13 | 2023-11-26 15:36 | 1:23 | T | Tripped showing Main protection relays | 2 | 2.7667 | Power interruption
Madaripur 132/33kV Grid Sub-Station | Barishal CKT-01 | 2023-11-19 16:06 | 2023-11-19 16:56 | 0:50 | E/O | Instruction by ALDC. | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | Barishal CKT-01 | 2023-11-26 14:13 | 2023-11-26 16:00 | 1:47 | T | CT Firing. | 40 | 71.3333 | Power interruption
Madaripur 132/33kV Grid Sub-Station | Barishal CKT-02 | 2023-11-18 16:39 | 2023-11-18 17:17 | 0:38 | T | Phase C, zone 01 | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | Barishal CKT-02 | 2023-11-26 14:13 | 2023-11-26 16:01 | 1:48 | T | CT Firing. | 40 | 72 | Power interruption
Shariatpur 132/33kV Grid Sub-Station | Madaripur-Shariatpur CKT-01 | 2023-11-26 14:13 | 2023-11-26 15:07 | 0:54 | T | Grid Fail for Madaripur Tr-03 R Phase CT Blust. | 20 | 18 | Power interruption
Shariatpur 132/33kV Grid Sub-Station | Madaripur-Shariatpur CKT-02 | 2023-11-26 14:13 | 2023-11-26 15:17 | 1:04 | T | Grid Fail for Madaripur Tr-03 R Phase CT Blust. | 20 | 21.3333 | Power interruption
|  |  | Total : | 35:01 |  | Unserved Energy: |  | 210.9833
HVDC Grid Circle :
BIPTC | Rajshahi-1 | 2023-11-08 11:04 | 2023-11-08 11:41 | 0:37 | T | Distance Trip | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Ishurdi 1 | 2023-11-03 18:12 | 2023-11-03 18:51 | 0:39 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Rajbari 1 | 2023-11-03 17:33 | 2023-11-03 17:55 | 0:22 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Rajbari 2 | 2023-11-03 16:40 | 2023-11-03 17:28 | 0:48 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | JH-1(L2) | 2023-11-16 09:32 | 2023-11-16 15:10 | 5:38 | E/O | Jashore -Jhenaidah CKY-1 B-Phase Armaring | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | JH-2(L1) | 2023-11-09 09:18 | 2023-11-09 12:49 | 3:31 | E/O | 132 kv B-Bus S/D for changing of T3 B-Bus DS | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah2-Jashore Ckt-2 | 2023-11-09 09:18 | 2023-11-09 12:46 | 3:28 | E/O | As per ALDC order | 0 | 0 | No interruption
Pabna 132/33kV Grid Sub-Station | Pabna-Shahjadpur Line | 2023-11-27 08:29 | 2023-11-27 16:28 | 7:59 | E/O | only CB Open as per ALDC Bogura Instruction. | 0 | 0 | No interruption
|  |  | Total : | 23:02 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Amnura 132/33kV Grid Sub-Station | Amnura - 100MW PPP | 2023-11-05 14:53 | 2023-11-05 16:58 | 2:05 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | Amnura - 50MW RPP | 2023-11-04 16:18 | 2023-11-04 16:35 | 0:17 | E/O | B phase voltage missing | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | Amnura - 50MW RPP | 2023-11-05 14:53 | 2023-11-05 16:59 | 2:06 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | Amnura - Rajshahi | 2023-11-05 14:53 | 2023-11-05 16:58 | 2:05 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-1 | 2023-11-05 11:32 | 2023-11-05 15:24 | 3:52 | E/O | For red hot occurred at Sherpur to Bogura circuit 2. Also Sherpur to Bogura circuit 1 shutdown for annual maintenance. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-2 | 2023-11-05 11:33 | 2023-11-05 15:25 | 3:52 | E/O | For red hot occurred at Sherpur to Bogura circuit 2. Also Sherpur to Bogura circuit 1 shutdown for annual maintenance. | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai Rahanpur ckt 1 | 2023-11-04 10:35 | 2023-11-04 10:51 | 0:16 | T | Zone 4 | 34 | 9.0667 | Power interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132 kV Rajshahi ckt-02 | 2023-11-18 16:55 | 2023-11-19 17:07 | 24:12 | E/O | Shutdown Rajshahi 132/33kV grid s/s | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-GTPS | 2023-11-02 12:50 | 2023-11-02 16:20 | 3:30 | E/O | According to Demand of 20mw GT power Station. | 0 | 0 | No interruption
|  |  | Total : | 42:15 |  | Unserved Energy: |  | 9.0667
Others :
Ashuganj 230/132/33kV Sub-Station | Sreepur 230 kV Ckt-1 | 2023-11-05 06:33 | 2023-11-05 06:33 | 0:00 | T |  | 0 | 0 | No interruption
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 278:55 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: November 2023
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 01 | 2023-11-28 07:27 | 2023-11-28 15:02 | 7:35 | S/O | AM | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 01 | 2023-11-02 10:53 | 2023-11-02 20:44 | 9:51 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 01 | 2023-11-05 10:19 | 2023-11-05 20:40 | 10:21 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 01 | 2023-11-06 08:34 | 2023-11-06 20:28 | 11:54 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 01 | 2023-11-07 08:36 | 2023-11-07 17:14 | 8:38 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 01 | 2023-11-08 09:23 | 2023-11-08 17:27 | 8:04 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 01 | 2023-11-09 07:58 | 2023-11-09 15:14 | 7:16 | S/O | annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 01 | 2023-11-13 09:45 | 2023-11-13 22:20 | 12:35 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 01 | 2023-11-15 08:55 | 2023-11-26 15:06 | 270:11 | S/O | Bus Conductor change work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 02 | 2023-11-28 09:05 | 2023-11-28 09:05 | 0:00 | S/O | Bus conductor change | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-01 HT | 2023-11-15 09:49 | 2023-11-15 18:40 | 8:51 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-01 LT | 2023-11-16 08:27 | 2023-11-16 17:01 | 8:34 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 HT | 2023-11-18 09:01 | 2023-11-18 17:56 | 8:55 | S/O | Annual maintanence | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 HT | 2023-11-19 07:29 | 2023-11-20 01:03 | 17:34 | S/O | Annual maintanence | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 HT | 2023-11-28 06:36 | 2023-11-28 17:04 | 10:28 | S/O | Annual maintanence | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 HT | 2023-11-20 09:41 | 2023-11-20 16:31 | 6:50 | S/O | Annual maintanence | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 LT | 2023-11-21 08:40 | 2023-11-21 17:55 | 9:15 | S/O | Annul Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Bus-1 (400kV) | 2023-11-06 12:22 | 2023-11-06 13:26 | 1:04 | S/O | Annual maintanence | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Bus-2 (400kV) | 2023-11-07 10:50 | 2023-11-07 11:20 | 0:30 | S/O | Purpose of transformer shifting | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Bus-2 (400kV) | 2023-11-28 09:05 | 2023-11-28 09:29 | 0:24 | S/O | Annual maintanence | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Bus-A | 2023-11-11 12:25 | 2023-11-11 15:25 | 3:00 | S/O | annual maintenace | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Bus-A | 2023-11-28 11:20 | 2023-11-28 12:50 | 1:30 | D/W | 132 KV T-4 transformer bay G2G project work | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Bus-B | 2023-11-11 08:30 | 2023-11-11 12:20 | 3:50 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Bus-B | 2023-11-28 10:52 | 2023-11-28 11:15 | 0:23 | D/W | Annual maintanence | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-1 HT | 2023-11-07 09:02 | 2023-11-07 16:20 | 7:18 | S/O | Annual maintenance. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-1 HT | 2023-11-09 09:25 | 2023-11-09 14:10 | 4:45 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-2 HT | 2023-11-01 09:20 | 2023-11-01 16:14 | 6:54 | S/O | Annual maintenance. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-2 HT | 2023-11-02 09:38 | 2023-11-02 16:22 | 6:44 | S/O | Annual maintenance. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-2 HT | 2023-11-09 14:27 | 2023-11-09 15:19 | 0:52 | D/W | T4 Transformer transportation work | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-3 HT | 2023-11-04 10:27 | 2023-11-04 13:15 | 2:48 | S/O | Annual maintenance work | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-3 HT | 2023-11-08 10:10 | 2023-11-08 17:05 | 6:55 | S/O | T-4 Transformer shifting due to capacity improvement. | 6 | 41.5 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-3 HT | 2023-11-12 20:05 | 2023-11-12 20:38 | 0:33 | S/O | 33kv bus coupler D.S. red hot . | 12 | 6.6 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-4 HT | 2023-11-05 10:20 | 2023-11-05 10:20 | 0:00 | D/W | Transformer up-gradation work purpose. from 25/41 MVA To 50/75MVA . | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-4 LT | 2023-11-05 10:20 | 2023-11-05 10:20 | 0:00 | D/W | Transformer up-gradation work purpose. from 25/41 MVA To 50/75MVA . | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | GT-2 HT | 2023-11-09 09:20 | 2023-11-09 17:25 | 8:05 | S/O | Annual maintenance. | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | GT-2 HT | 2023-11-30 07:42 | 2023-11-30 18:30 | 10:48 | S/O | CT Change | 15 | 37.5 | Power interruption 17:00 to 18:30
Joydebpur 132/33kV Grid Sub-Station | GT-3 HT | 2023-11-02 08:52 | 2023-11-02 16:42 | 7:50 | S/O | Annual maintenance | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | GT-3 HT | 2023-11-16 09:14 | 2023-11-16 11:36 | 2:22 | S/O | Annual Maintenance | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | GT-4 HT | 2023-11-06 09:11 | 2023-11-06 16:23 | 7:12 | S/O | Annual maintenance. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Aux. X-former-1 HT | 2023-11-12 12:56 | 2023-11-12 12:56 | 0:00 | S/O | Relay and tan delta test work done by spmd | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Aux. X-former-1 HT | 2023-11-12 13:56 | 2023-11-12 13:56 | 0:00 | S/O | Relay and tan delta test work done by spmd | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-3 HT | 2023-11-12 09:49 | 2023-11-12 11:49 | 2:00 | S/O | Tan Delta test work done by SPMD-1 of T-3 | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-I HT | 2023-11-12 13:56 | 2023-11-12 15:24 | 1:28 | S/O | Annual maintenance (Relay testing) | 70 | 102.6667 | Power interruption
Kaliakoir 400/230/132kV Grid Sub-Station | 230kV Bus 1 | 2023-11-22 07:45 | 2023-11-22 14:40 | 6:55 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR1 LT | 2023-11-26 14:44 | 2023-11-26 16:28 | 1:44 | S/O | Relay Testing by SPMD | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR2 HT | 2023-11-26 16:31 | 2023-11-26 17:49 | 1:18 | S/O | Relay Testing by SPMD | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | 400kV Bus 1 | 2023-11-18 07:56 | 2023-11-18 16:10 | 8:14 | S/O | annual maintenance | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | 400kV Bus 1 | 2023-11-19 08:29 | 2023-11-19 14:40 | 6:11 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | 400kV Bus 2 | 2023-11-20 07:47 | 2023-11-20 14:23 | 6:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-1 (132kV) HT | 2023-11-13 10:06 | 2023-11-13 18:09 | 8:03 | S/O | annual maintenance/DPDC | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-1 (132kV) HT | 2023-11-25 09:26 | 2023-11-25 09:26 | 0:00 | S/O | centrifuging work | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-2 (132kV) HT | 2023-11-12 09:28 | 2023-11-12 20:08 | 10:40 | S/O | Annual Maintenance 33 kv Right Bus by DPDC. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-3 (132kV) HT | 2023-11-13 10:06 | 2023-11-13 18:11 | 8:05 | S/O | annual maintenance/DPDC | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-3 (132kV) HT | 2023-11-19 11:50 | 2023-11-19 16:31 | 4:41 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-1 (404T) HT | 2023-11-02 08:52 | 2023-11-02 10:42 | 1:50 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-1 (404T) HT | 2023-11-07 09:28 | 2023-11-07 13:32 | 4:04 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-2 (414T) HT | 2023-11-05 09:02 | 2023-11-05 13:30 | 4:28 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-2 (414T) HT | 2023-11-22 08:53 | 2023-11-22 16:08 | 7:15 | S/O | G To G Project work | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-2 (414T) HT | 2023-11-24 07:20 | 2023-11-24 15:50 | 8:30 | D/W | Transformers replacement work by G to G project. | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-2 (414T) HT | 2023-11-25 08:32 | 2023-11-25 13:34 | 5:02 | S/O | Annual maintenance of 33 kv T2 bus sec by PDB | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-2 (414T) LT | 2023-11-01 08:19 | 2023-11-01 15:21 | 7:02 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) HT | 2023-11-23 08:37 | 2023-11-24 15:38 | 31:01 | D/W | G to G Project work | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-5 (446T) HT | 2023-11-20 08:51 | 2023-11-22 14:06 | 53:15 | S/O | T5 oil centrifuge | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) LT | 2023-11-05 06:24 | 2023-11-05 07:42 | 1:18 | S/O | Redhot removal by 33kV Bus work done by MPBS | 15 | 19.5 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) HT | 2023-11-26 06:50 | 2023-11-26 17:10 | 10:20 | S/O | Annual Maintenance | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) LT | 2023-11-10 17:16 | 2023-11-10 18:46 | 1:30 | S/O | PBS 33kv Bus Riser change. | 15 | 22.5 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) LT | 2023-11-25 07:10 | 2023-11-25 17:15 | 10:05 | S/O |  | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) LT | 2023-11-29 12:20 | 2023-11-29 15:45 | 3:25 | S/O | 33 kV incomer GT-4 Circuit Breaker Mechanical & Electical problem. | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) HT | 2023-11-27 07:06 | 2023-11-27 18:07 | 11:01 | S/O | Annual maintenance | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) HT | 2023-11-29 07:30 | 2023-11-29 12:49 | 5:19 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) HT | 2023-11-30 06:50 | 2023-11-30 17:06 | 10:16 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Main Bus | 2023-11-16 10:20 | 2023-11-16 16:25 | 6:05 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Reserve Bus | 2023-11-26 10:19 | 2023-11-26 16:46 | 6:27 | S/O | 132 KV Uttara Sector-18 Ckt Res.bus DS With Reserve Bus Bay Epuipement Annual Maintenance Work. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Reserve Bus | 2023-11-28 09:48 | 2023-11-28 16:52 | 7:04 | S/O | Annual maintenance work . | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T2 HT | 2023-11-06 09:12 | 2023-11-06 09:48 | 0:36 | S/O | SF6 Gas Filling Work, | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-1 (404T) HT | 2023-11-08 08:22 | 2023-11-08 12:22 | 4:00 | S/O |  | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-1 (404T) LT | 2023-11-02 07:24 | 2023-11-02 10:56 | 3:32 | S/O | S/D taken by Mr. Golam Mohammed Samdani,SDE, Div-2 due to 33kV bus DS(T1 &T3 X-F) change work | 15 | 53 | Power interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-1 (404T) LT | 2023-11-04 13:53 | 2023-11-04 16:58 | 3:05 | S/O | S/D taken by Mr. Golam Mohammad Samdani, SDE, Div-2, PDB due to 33kV Bus Coupler DS(T1 & T3 X-F) Replacement work | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-2 (414T) HT | 2023-11-08 13:39 | 2023-11-08 15:52 | 2:13 | S/O | S/D due to Realay functional Test purposes by SPMD | 0 | 0 | No interruption
New Tongi 132/33kV Grid Sub-Station | Bus-1 | 2023-11-26 09:10 | 2023-11-26 16:36 | 7:26 | S/O | Annual Maintenance | 0 | 0 | No interruption
New Tongi 132/33kV Grid Sub-Station | Bus-1 | 2023-11-27 09:14 | 2023-11-27 15:11 | 5:57 | S/O | Annual maintenance | 0 | 0 | No interruption
New Tongi 132/33kV Grid Sub-Station | T1(403T) HT | 2023-11-05 09:13 | 2023-11-05 15:04 | 5:51 | S/O | Annual Maintenance | 0 | 0 | No interruption
New Tongi 132/33kV Grid Sub-Station | T1(403T) HT | 2023-11-21 09:20 | 2023-11-21 10:59 | 1:39 | S/O | Yearly Maintenance work. | 0 | 0 | No interruption
Rajendrapur 132/33kV Grid Sub-Station | MTR-1 LT | 2023-11-11 09:03 | 2023-11-11 14:54 | 5:51 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rajendrapur 132/33kV Grid Sub-Station | MTR-2 HT | 2023-11-19 09:10 | 2023-11-19 15:35 | 6:25 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rajendrapur 132/33kV Grid Sub-Station | MTR-3 HT | 2023-11-21 09:30 | 2023-11-21 14:25 | 4:55 | S/O | Annual Maintenance of MTR-03 | 0 | 0 | No interruption
Rajendrapur 132/33kV Grid Sub-Station | STR-2 LT | 2023-11-19 09:09 | 2023-11-19 15:36 | 6:27 | S/O | Annual Maintenance | 0 | 0 | No interruption
Satmasjid 132/33kV Grid Sub-Station | 132/33 KV Transformer-1 HT | 2023-11-19 09:19 | 2023-11-19 15:02 | 5:43 | S/O | Annual Maintenance | 0 | 0 | No interruption
Satmasjid 132/33kV Grid Sub-Station | 132/33 KV Transformer-2 LT | 2023-11-19 15:12 | 2023-11-19 19:23 | 4:11 | S/O | Annual Maintenance | 0 | 0 | No interruption
Satmasjid 132/33kV Grid Sub-Station | 132/33 KV Transformer-2 LT | 2023-11-27 09:40 | 2023-11-27 16:34 | 6:54 | S/O | Annual Maintenance of Satmosjid grid S/S. | 0 | 0 | No interruption
Satmasjid 132/33kV Grid Sub-Station | Auxiliary Tr-2 HT | 2023-11-27 09:39 | 2023-11-27 16:40 | 7:01 | S/O | Annual Maintenance of Satmosjid grid S/S. | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-3 HT | 2023-11-25 09:59 | 2023-11-25 12:25 | 2:26 | S/O | Hot spot maintenance & Measurement of Bucholtz relay of 132/33 KV Transformer-3 | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Bus B | 2023-11-13 08:50 | 2023-11-13 15:20 | 6:30 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 01 LT | 2023-11-07 08:24 | 2023-11-07 16:04 | 7:40 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 01 LT | 2023-11-08 08:23 | 2023-11-08 16:10 | 7:47 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 01 LT | 2023-11-09 08:39 | 2023-11-09 15:30 | 6:51 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 02 HT | 2023-11-01 08:30 | 2023-11-01 16:08 | 7:38 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 02 HT | 2023-11-02 08:36 | 2023-11-02 16:05 | 7:29 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 03 HT | 2023-11-05 08:24 | 2023-11-05 16:10 | 7:46 | S/O |  | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 03 HT | 2023-11-06 08:30 | 2023-11-06 20:45 | 12:15 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 03 LT | 2023-11-04 08:37 | 2023-11-04 16:18 | 7:41 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-1 HT | 2023-11-11 08:27 | 2023-11-11 15:07 | 6:40 | S/O | Annual Maintenance | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-1 HT | 2023-11-12 08:29 | 2023-11-12 14:06 | 5:37 | S/O | Annual Maintenance | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-1 LT | 2023-11-13 08:35 | 2023-11-13 15:20 | 6:45 | S/O | annual maintenance | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 HT | 2023-11-14 08:34 | 2023-11-14 15:16 | 6:42 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 HT | 2023-11-15 08:34 | 2023-11-15 15:12 | 6:38 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 HT | 2023-11-16 08:41 | 2023-11-16 14:12 | 5:31 | S/O | Annual Maintenance | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-3 HT | 2023-11-20 08:50 | 2023-11-20 15:34 | 6:44 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-3 HT | 2023-11-21 08:50 | 2023-11-21 15:28 | 6:38 | S/O | Annual Maintenance | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-3 HT | 2023-11-22 08:44 | 2023-11-22 15:30 | 6:46 | S/O | Annual Maintenance | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-4 HT | 2023-11-18 08:55 | 2023-11-18 15:21 | 6:26 | S/O | Annual Maintenance | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-4 HT | 2023-11-19 08:45 | 2023-11-19 15:09 | 6:24 | S/O | Annual maintenance. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | 132 kV Bus-1 | 2023-11-30 09:40 | 2023-11-30 16:46 | 7:06 | S/O | Annual maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | 132 kV Bus-2 | 2023-11-13 09:48 | 2023-11-13 18:55 | 9:07 | S/O | Annual Maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | T-03 HT | 2023-11-09 05:02 | 2023-11-09 06:12 | 1:10 | S/O | Temperature rising maintenance work (DS-613S,R-Phase) | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | T-1 LT | 2023-11-14 09:33 | 2023-11-14 15:14 | 5:41 | S/O | Annual maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | T-2 HT | 2023-11-18 09:13 | 2023-11-18 16:29 | 7:16 | S/O | Annual maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | T-3 LT | 2023-11-20 09:49 | 2023-11-20 15:33 | 5:44 | S/O | Annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 1024:35 |  | Unserved Energy: |  | 283.2667
Dhaka (South) Grid Circle : | [11 empty] | 39.3333
Gulshan 132/33kV Grid Sub-Station | MT-1 LT | 2023-11-26 08:15 | 2023-11-26 15:24 | 7:09 | S/O | Yearly maintenance. | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 404 T-1 HT | 2023-11-06 07:30 | 2023-11-06 08:18 | 0:48 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 404 T-1 HT | 2023-11-08 08:25 | 2023-11-08 20:35 | 12:10 | S/O | Annual maintenance | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 404 T-1 LT | 2023-11-07 05:54 | 2023-11-07 20:05 | 14:11 | S/O | annual maintenance | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 414 T-2 HT | 2023-11-09 06:45 | 2023-11-09 19:10 | 12:25 | S/O | Annual maintenance | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 414 T-2 HT | 2023-11-11 07:18 | 2023-11-11 17:31 | 10:13 | S/O | Annual maintanence | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 414 T-2 HT | 2023-11-12 06:43 | 2023-11-12 20:08 | 13:25 | S/O | Annual maintenance | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 414 T-2 HT | 2023-11-29 10:13 | 2023-11-29 16:55 | 6:42 | S/O | 33kv main bus DS finger maintenance | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 424 T-5 HT | 2023-11-02 10:09 | 2023-11-02 18:19 | 8:10 | S/O | Annual maintenance | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 424 T-5 HT | 2023-11-03 07:50 | 2023-11-03 16:54 | 9:04 | S/O | Annual Maintenance | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 HT | 2023-11-28 07:19 | 2023-11-28 19:57 | 12:38 | S/O | annual maintenance | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 HT | 2023-11-29 07:13 | 2023-11-29 16:42 | 9:29 | S/O | Annual Maintenance | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 HT | 2023-11-30 07:24 | 2023-11-30 17:01 | 9:37 | S/O | Annual Maintenance | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 HT | 2023-11-09 07:22 | 2023-11-09 07:22 | 0:00 | S/O | Maintenance work | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-1 HT | 2023-11-10 08:03 | 2023-11-10 12:09 | 4:06 | S/O | High Temperature maintenance on several points. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-2 HT | 2023-11-24 07:55 | 2023-11-24 11:07 | 3:12 | S/O | Maientence work at junction point | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | GT-1 LT | 2023-11-11 09:10 | 2023-11-11 17:16 | 8:06 | S/O |  | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | GT-2 LT | 2023-11-18 09:56 | 2023-11-18 14:40 | 4:44 | S/O | Annual maintenance | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Transformer GT-1 HT | 2023-11-03 07:18 | 2023-11-03 09:53 | 2:35 | S/O | LA(Y-ph and B-ph) replace work by DPDC. Shut down taken by Mr. Rokonul Islam, SDE, DPDC. | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) HT | 2023-11-29 07:08 | 2023-11-29 13:46 | 6:38 | S/O | Oil filling work of Transformer-2. | 0 | 0 | No interruption
Matuail 132/33kV Grid Sub-Station | 132/33 kV GT-1 HT | 2023-11-24 09:37 | 2023-11-24 21:39 | 12:02 | S/O | Schedule maintenance work | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Bus2 | 2023-11-26 09:16 | 2023-11-26 13:41 | 4:25 | S/O | Bus-2 shutdown due to annual maintenance | 0 | 0 | No interruption
Munshiganj 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-11-14 05:59 | 2023-11-14 07:42 | 1:43 | S/O | 13 Grid SCADA Integration Work | 0 | 0 | No interruption
Munshiganj 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-11-14 07:47 | 2023-11-14 08:46 | 0:59 | S/O | SCADA Integration | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | 132 kV Main Bus-1 | 2023-11-03 06:34 | 2023-11-07 07:55 | 97:21 | S/O | Dismantle Equipment (ct, pt, ds, cb) related to bus ckt-01 | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | 132 kV Main Bus-2 | 2023-11-07 07:40 | 2023-11-21 11:34 | 339:54 | S/O | Dismantle Equipment and installation (ct, pt, ds, cb) related to bus ckt-02 | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | T-1 LT | 2023-11-25 08:44 | 2023-11-25 16:18 | 7:34 | S/O | For Annual Maintenance purpose. | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | T-1 LT | 2023-11-26 08:54 | 2023-11-26 15:52 | 6:58 | S/O | For Annual Maintenance Purpose. | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | T-2 HT | 2023-11-29 08:54 | 2023-11-29 16:34 | 7:40 | S/O | annual maintenance on T-2 bay. | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | T-2 HT | 2023-11-30 09:48 | 2023-11-30 14:47 | 4:59 | S/O | For Annual Maintenance Purpose. | 0 | 0 | No interruption
Nawabganj 132/33kV Grid Sub-Station | TR-1 LT | 2023-11-30 07:01 | 2023-11-30 10:27 | 3:26 | S/O | 33 kv Bus sec-01 S/D due to DS maintanance of Agla Feeder Taken by Dhaka PBS-02 | 12 | 41.2 | Power interruption
Postogola 132/33kV Grid Sub-Station | GT-2 HT | 2023-11-09 14:04 | 2023-11-09 14:36 | 0:32 | D/W | Nldc communication works | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | 132 kV Busbar-2 | 2023-11-03 14:58 | 2023-11-03 19:16 | 4:18 | D/W | 132kV Bus-02 Shutdown for Commissioning of Interim Transformer and Upgradation of Substation capacity | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | 132 kV Busbar-2 | 2023-11-18 06:55 | 2023-11-18 12:06 | 5:11 | D/W | Clamp Change work of 132kV Bus-2 DS 639(B Phase), due to temperature rise in new Interim Transformer ds clamp connection. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | 132 kV Busbar-2 | 2023-11-26 20:26 | 2023-11-26 23:16 | 2:50 | S/O | Red hot Maintenance in 230kV LA Y-Phase Upper loop of new Interim Transformer | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 01 HT | 2023-11-30 07:08 | 2023-11-30 22:24 | 15:16 | S/O | Shutdown for Annual Maintenance | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 HT | 2023-11-05 13:13 | 2023-11-05 14:30 | 1:17 | D/W | Commissioning of Interim Transformer and Upgradation of Substation capacity | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 HT | 2023-11-26 20:29 | 2023-11-26 23:14 | 2:45 | S/O | Red hot Maintenance in 230kV LA Y-Phase Upper loop | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 2023-11-18 06:52 | 2023-11-18 12:12 | 5:20 | D/W | Clamp Change work of 132kV Bus-2 DS 639(B Phase), due to temperature rise in new Interim Transformer ds clamp connection. | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 LT | 2023-11-11 08:44 | 2023-11-11 20:27 | 11:43 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 LT | 2023-11-05 10:05 | 2023-11-05 18:43 | 8:38 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | Aux TR-1 LT | 2023-11-11 09:25 | 2023-11-11 20:29 | 11:04 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | Aux TR-2 HT | 2023-11-05 10:02 | 2023-11-05 18:44 | 8:42 | S/O | Annual Maintenance | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 132kV Bus A | 2023-11-17 09:36 | 2023-11-17 15:09 | 5:33 | D/W | 132/33 kV T-3 Transformer jack bus connection with Bus-A | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 132kV Bus B | 2023-11-18 07:35 | 2023-11-18 16:55 | 9:20 | D/W | G2G PROJECT WORK. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | BUS A | 2023-11-29 09:30 | 2023-11-29 18:30 | 9:00 | S/O | Erection of beam structure of Tasnim Chemical under BUS-01. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 HT | 2023-11-14 11:28 | 2023-11-22 21:05 | 201:37 | D/W | Upgradation work of Transformer-1 | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2023-11-02 09:32 | 2023-11-02 12:17 | 2:45 | S/O | Scada integration. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 HT | 2023-11-02 12:25 | 2023-11-02 14:13 | 1:48 | S/O | Scada integration. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 HT | 2023-11-06 10:12 | 2023-11-06 13:39 | 3:27 | S/O | R-ph CT loop change at 33kv side of Transformer -2 | 35 | 120.75 | Power interruption
|  |  | Total : | 953:29 |  | Unserved Energy: |  | 161.95
Chattogram Grid Circle :
Agrabad 132/33kV Grid Sub-Station | Auxiliary Transformer-01 LT | 2023-11-01 09:28 | 2023-11-01 15:38 | 6:10 | S/O | 132/33 kV MTR-01 (406T) Shutdown for Annual Maintenance | 0 | 0 | No interruption | 14:20
Agrabad 132/33kV Grid Sub-Station | Auxiliary Transformer-02 HT | 2023-11-02 08:22 | 2023-11-02 18:54 | 10:32 | S/O | 132/33 KV MTR-02 (416T) Shutdown For Annual Maintenance | 0 | 0 | No interruption
Agrabad 132/33kV Grid Sub-Station | MTR-01 (406T) LT | 2023-11-01 09:17 | 2023-11-01 15:40 | 6:23 | S/O | Annual Maintenance | 0 | 0 | No interruption
Agrabad 132/33kV Grid Sub-Station | MTR-02 (416T) LT | 2023-11-02 08:20 | 2023-11-02 19:08 | 10:48 | S/O | 132/33kV MTR-02(416T) Shutdown for Annual Maintenance | 0 | 0 | No interruption
Agrabad 132/33kV Grid Sub-Station | MTR-02 (416T) LT | 2023-11-09 10:34 | 2023-11-09 15:58 | 5:24 | S/O | Whole Differential Relay of MTR-02 integration With SAS | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bus-A | 2023-11-21 08:35 | 2023-11-21 12:55 | 4:20 | S/O | Annual maintenance. | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bus-B | 2023-11-22 08:27 | 2023-11-22 13:29 | 5:02 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | T-1 (402T) LT | 2023-11-18 07:49 | 2023-11-18 14:10 | 6:21 | S/O | FOR Annual Maintenance 2023-2024. | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | T-2 (412T) HT | 2023-11-18 07:50 | 2023-11-18 14:08 | 6:18 | S/O | Annual Maintencance | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | T-2 (412T) LT | 2023-11-25 07:26 | 2023-11-25 17:51 | 10:25 | S/O | Annual Maintenance | 0 | 0 | No interruption
Baroaulia 132/33kV Grid Sub-Station | T-1(405T) HT | 2023-11-05 08:29 | 2023-11-05 15:26 | 6:57 | S/O | Annual Maintenance | 12 | 83.4 | Power interruption
Baroaulia 132/33kV Grid Sub-Station | T2(415T) HT | 2023-11-12 08:04 | 2023-11-12 16:51 | 8:47 | S/O | Annual maintenance | 10 | 87.8333 | Power interruption
Baroirhat 132/33kV Grid Sub-Station | TR-2, 416T HT | 2023-11-02 07:10 | 2023-11-02 17:40 | 10:30 | S/O | Annual Maintenance Schedule S/D | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-1 HT | 2023-11-30 11:02 | 2023-11-30 21:19 | 10:17 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 HT | 2023-11-09 08:46 | 2023-11-09 09:35 | 0:49 | S/O | For Satkania 33 kv feeder redhot maintenance work. | 30 | 24.5 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 HT | 2023-11-12 06:10 | 2023-11-12 07:35 | 1:25 | S/O | Redhot Maintenance by Keranihat PBS | 30 | 42.5 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 HT | 2023-11-28 06:20 | 2023-11-28 17:03 | 10:43 | D/W | Due to project work | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | 403T(TR-1) LT | 2023-11-17 22:11 | 2023-11-17 23:29 | 1:18 | S/O | due to pdb maintenance work | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | 413T(TR-2) LT | 2023-11-04 07:45 | 2023-11-04 14:10 | 6:25 | S/O | Due to annual maintenance. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | 423T(TR-3) HT | 2023-11-12 08:05 | 2023-11-12 13:16 | 5:11 | S/O | Due To 132/33 kV Tr-03 Transformer Annual Maintenance. | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132/33 KV 406T T-1 HT | 2023-11-14 07:55 | 2023-11-14 12:42 | 4:47 | S/O | Annual mantanance | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 133/33 KV T-2 416T LT | 2023-11-15 08:11 | 2023-11-15 12:30 | 4:19 | S/O | Annual Maintenance. | 0 | 0 | No interruption
KSRM 132/33kV Grid Sub-Station | Transformer-02 HT | 2023-11-26 09:19 | 2023-11-26 09:19 | 0:00 | S/O | Due to maintenance 33 kv side. | 0 | 0 | No interruption
Khagrachori 132/33kV Grid Sub-Station | MAIN BUS-1 | 2023-11-03 10:13 | 2023-11-03 14:48 | 4:35 | S/O | Annual maintenance | 0 | 0 | No interruption
Khagrachori 132/33kV Grid Sub-Station | MAIN BUS-2 | 2023-11-03 14:50 | 2023-11-03 16:19 | 1:29 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khagrachori 132/33kV Grid Sub-Station | TR-2 HT | 2023-11-04 08:21 | 2023-11-04 16:28 | 8:07 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | 405T (T1) HT | 2023-11-14 06:19 | 2023-11-14 08:59 | 2:40 | S/O | Loop connection in-between 33kV Outdoor Bus to station supply's new installed isolator. | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | 405T (T1) LT | 2023-11-25 07:50 | 2023-11-25 16:36 | 8:46 | S/O | Change VCB by PDB | 0 | 0 | No interruption
Mirsorai 230/33kV Grid Sub-Station | TR-1, 718T HT | 2023-11-20 08:42 | 2023-11-20 16:04 | 7:22 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mirsorai 230/33kV Grid Sub-Station | TR-2, 728T HT | 2023-11-21 08:05 | 2023-11-21 15:35 | 7:30 | S/O | Annual Maintenance | 3 | 22.5 | Power interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) HT | 2023-11-01 11:16 | 2023-11-01 12:14 | 0:58 | S/O | Oil sample collection. | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) HT | 2023-11-06 07:50 | 2023-11-06 15:46 | 7:56 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) HT | 2023-11-01 11:15 | 2023-11-01 12:12 | 0:57 | S/O | Oil sample collection | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) HT | 2023-11-07 07:18 | 2023-11-07 15:04 | 7:46 | S/O | Annual maintenance | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | TR-1 LT | 2023-11-08 07:53 | 2023-11-08 14:32 | 6:39 | S/O | Annual maintenance. | 0 | 0 | No interruption
Rangamati 132/33kV Grid Sub-Station | Power Transformer TR1 (405T) HT | 2023-11-06 09:06 | 2023-11-06 17:30 | 8:24 | S/O | Annual maintenance | 0 | 0 | No interruption
Rangamati 132/33kV Grid Sub-Station | Power Transformer TR2 (415T) LT | 2023-11-07 09:04 | 2023-11-07 15:29 | 6:25 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | 406T HT | 2023-11-22 14:31 | 2023-11-22 15:58 | 1:27 | S/O | Multifunction Meter installation | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | 406T HT | 2023-11-26 08:10 | 2023-11-26 16:02 | 7:52 | S/O | Annual maintenance | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | 406T LT | 2023-11-13 12:06 | 2023-11-13 16:35 | 4:29 | S/O | Annual Maintenance. 33kv In coming2 DS(GIS,ABB) opened at 12:06 | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | 416T HT | 2023-11-13 08:09 | 2023-11-13 16:33 | 8:24 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | 416T LT | 2023-11-22 14:34 | 2023-11-22 15:59 | 1:25 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | 416T LT | 2023-11-27 10:43 | 2023-11-27 13:11 | 2:28 | S/O | TRANSFORMER -2 SECONDARY BUS DS | 0 | 0 | No interruption
|  |  | Total : | 248:50 |  |  |  | 260.7333
Cumilla Grid Circle :
Beanibazar 132/33kV Grid Sub-Station | 132 KV BUS-1 | 2023-11-14 09:36 | 2023-11-14 16:36 | 7:00 | S/O | Annual maintenance | 0 | 0 | No interruption
Beanibazar 132/33kV Grid Sub-Station | 132 KV BUS-1 | 2023-11-18 11:59 | 2023-11-18 15:57 | 3:58 | S/O | Maintenance work | 0 | 0 | No interruption
Beanibazar 132/33kV Grid Sub-Station | 132 KV BUS-2 | 2023-11-12 09:17 | 2023-11-12 16:28 | 7:11 | S/O | Maintenance work | 0 | 0 | No interruption | Check
Beanibazar 132/33kV Grid Sub-Station | 132 KV BUS-2 | 2023-11-13 09:23 | 2023-11-13 14:23 | 5:00 | S/O | Annual maintenance | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | ICT-01 HT | 2023-11-08 09:08 | 2023-11-08 14:19 | 5:11 | S/O | AM | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | ICT-01 HT | 2023-11-09 08:26 | 2023-11-09 15:48 | 7:22 | S/O | AM | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | ICT-02 HT | 2023-11-21 08:24 | 2023-11-21 14:27 | 6:03 | S/O | AM | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | ICT-02 HT | 2023-11-22 08:38 | 2023-11-22 14:51 | 6:13 | S/O | AM | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 401T HT | 2023-11-09 09:09 | 2023-11-09 15:39 | 6:30 | S/O | Annual Maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 401T HT | 2023-11-11 08:42 | 2023-11-11 16:32 | 7:50 | S/O | Annual Maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 401T LT | 2023-11-01 09:13 | 2023-11-01 14:43 | 5:30 | S/O | Tan-delta test | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 401T LT | 2023-11-08 10:08 | 2023-11-08 16:44 | 6:36 | S/O | annual maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 402T HT | 2023-11-21 09:08 | 2023-11-21 15:50 | 6:42 | S/O | Annual maintenance. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 402T HT | 2023-11-22 09:13 | 2023-11-22 16:25 | 7:12 | S/O | annual maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 402T HT | 2023-11-23 08:58 | 2023-11-23 14:21 | 5:23 | S/O | annual maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 402T LT | 2023-11-02 08:47 | 2023-11-02 13:49 | 5:02 | S/O | Tandelta test. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 403T HT | 2023-11-01 14:45 | 2023-11-01 17:48 | 3:03 | S/O | tan delta test | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 403T HT | 2023-11-28 08:59 | 2023-11-28 13:35 | 4:36 | S/O | Annual maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 403T HT | 2023-11-29 09:18 | 2023-11-29 12:22 | 3:04 | S/O | annual maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 403T LT | 2023-11-27 09:20 | 2023-11-27 15:58 | 6:38 | S/O | annual maintenance | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | Bus A | 2023-11-08 09:27 | 2023-11-08 16:42 | 7:15 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | Bus A | 2023-11-13 14:17 | 2023-11-13 15:24 | 1:07 | D/W | make loop from 132KV Sunamganj-02 BUS-1 DS to 132KV BUSBAR | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | Bus-B | 2023-11-13 15:44 | 2023-11-13 16:33 | 0:49 | D/W | make loop from 132KV Sunamganj-02 BUS DS to 132KV BUSBAR | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | T-1 LT | 2023-11-14 15:40 | 2023-11-14 15:40 | 0:00 | S/O | Change pin Insulator of 33kv Disconnector Switch. | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | T-1 LT | 2023-11-14 15:45 | 2023-11-14 16:36 | 0:51 | S/O | Change Pin Insulator of 33kv Disconnector Switch. | 1.5 | 1.275 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | TR2 | 2023-11-26 10:00 | 2023-11-26 11:50 | 1:50 | S/O | Annual maintenance relay test by SPMD | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-03 HT | 2023-11-30 19:16 | 2023-11-30 20:04 | 0:48 | D/W | 33 KV UGC Connected R- Phase | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-02 HT | 2023-11-27 16:05 | 2023-11-27 17:17 | 1:12 | S/O | Oil leakage Maintenance | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) LT | 2023-11-25 08:15 | 2023-11-25 10:38 | 2:23 | S/O | Maintenance work by BPDB | 25 | 59.5833 | Power interruption
Kulaura 132/33kV Grid Sub-Station | TR-1 HT | 2023-11-08 08:41 | 2023-11-08 15:31 | 6:50 | S/O | Annual maintenence | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | TR-1 HT | 2023-11-09 08:56 | 2023-11-09 15:31 | 6:35 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | TR-1 HT | 2023-11-11 08:48 | 2023-11-11 13:40 | 4:52 | S/O | Annual maintenance. | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | TR-1 HT | 2023-11-23 09:08 | 2023-11-23 14:34 | 5:26 | S/O | Annual maintenance. | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | TR-1 LT | 2023-11-07 08:36 | 2023-11-07 13:15 | 4:39 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | TR-1 LT | 2023-11-21 08:57 | 2023-11-21 14:55 | 5:58 | S/O | Annual maintenance. | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | TR-1 LT | 2023-11-25 08:46 | 2023-11-25 16:50 | 8:04 | S/O | Annual maintenance and C.T changed | 10 | 80.6667 | Power interruption
Kulaura 132/33kV Grid Sub-Station | TR-2 HT | 2023-11-07 08:36 | 2023-11-07 13:15 | 4:39 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | TR-2 HT | 2023-11-07 13:22 | 2023-11-07 17:57 | 4:35 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | TR-2 HT | 2023-11-21 08:57 | 2023-11-21 14:54 | 5:57 | S/O | Annual maintenance. | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | TR-2 HT | 2023-11-22 09:12 | 2023-11-22 14:31 | 5:19 | S/O | Annual maintenance | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | TR-2 LT | 2023-11-23 09:08 | 2023-11-23 14:34 | 5:26 | S/O | Annual maintenance. | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 HT | 2023-11-04 08:45 | 2023-11-04 11:50 | 3:05 | S/O | TR-02 Tan delta test | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 HT | 2023-11-19 08:32 | 2023-11-19 15:56 | 7:24 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 HT | 2023-11-20 07:16 | 2023-11-20 15:12 | 7:56 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 LT | 2023-11-05 08:31 | 2023-11-05 13:17 | 4:46 | S/O | Tan delta test | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 LT | 2023-11-25 08:04 | 2023-11-25 17:17 | 9:13 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-06 HT | 2023-11-12 15:15 | 2023-11-13 13:47 | 22:32 | S/O | TR-06 33KV side B phase Incoming heat shrink burn. Load flow by TR-04. | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-06 HT | 2023-11-28 08:27 | 2023-11-28 13:06 | 4:39 | S/O | Annual Maintenance. Load flow by TR-04 | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-06 LT | 2023-11-04 12:13 | 2023-11-04 16:04 | 3:51 | S/O | Ten delta test | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-06 LT | 2023-11-27 07:57 | 2023-11-28 16:10 | 32:13 | S/O | Annual Maintenance. Load flow by TR-04 | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-1AB HT | 2023-11-06 08:43 | 2023-11-06 13:03 | 4:20 | S/O | Ten dalta test of annual maintanance works. | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-1AB HT | 2023-11-12 08:42 | 2023-11-12 16:35 | 7:53 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-1AB HT | 2023-11-13 08:30 | 2023-11-13 16:24 | 7:54 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-1AB HT | 2023-11-27 11:15 | 2023-11-27 16:30 | 5:15 | D/W | 33 Kv DS change | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-1AB LT | 2023-11-14 08:28 | 2023-11-14 16:43 | 8:15 | S/O | Annual maintence | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-2 HT | 2023-11-06 13:05 | 2023-11-06 17:07 | 4:02 | S/O | tan delta test | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-2 LT | 2023-11-15 08:29 | 2023-11-15 16:50 | 8:21 | S/O | Annual maintenance | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-2 LT | 2023-11-16 08:29 | 2023-11-16 16:56 | 8:27 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-2 LT | 2023-11-18 08:26 | 2023-11-18 16:20 | 7:54 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-3 HT | 2023-11-06 13:05 | 2023-11-06 17:07 | 4:02 | S/O | tan delta test | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-3 LT | 2023-11-15 08:29 | 2023-11-15 16:50 | 8:21 | S/O | Annual maintenance | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-3 LT | 2023-11-16 08:29 | 2023-11-16 16:56 | 8:27 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-3 LT | 2023-11-18 08:26 | 2023-11-18 16:20 | 7:54 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T1 LT | 2023-11-23 08:49 | 2023-11-29 15:48 | 150:59 | S/O | Relay Testing Purpose. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T2 LT | 2023-11-21 09:33 | 2023-11-21 12:51 | 3:18 | S/O | Relay Testing | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-11-18 15:30 | 2023-11-18 17:08 | 1:38 | S/O | for 33/11KV T-9 operation | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-11-21 12:53 | 2023-11-21 15:45 | 2:52 | S/O | Maintenance Works | 0 | 0 | No interruption
|  |  | Total : | 546:10 |  | Unserved Energy: |  | 141.525
Khulna Grid Circle : | [10 empty] | 251.2167
Barguna 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-11-01 06:58 | 2023-11-01 17:24 | 10:26 | S/O | Annual Maintenance | 0 | 0 | No interruption |  | 113.55
Barguna 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-11-02 06:51 | 2023-11-02 17:31 | 10:40 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barguna 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-11-04 13:47 | 2023-11-04 17:10 | 3:23 | S/O | Annual Maintenance (Tan-Delta Test) | 0 | 0 | No interruption
Barguna 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-11-04 17:11 | 2023-11-04 18:01 | 0:50 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barguna 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-11-05 07:10 | 2023-11-05 18:24 | 11:14 | S/O | Annual Maintenance | 0 | 0 | No interruption |  | 364.7667
Barguna 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-11-04 07:03 | 2023-11-04 13:45 | 6:42 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 2023-11-23 07:36 | 2023-11-23 08:57 | 1:21 | S/O | 33kV Dopdabia-2 feeder Red hot maintenance | 20 | 27 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 2023-11-24 07:20 | 2023-11-24 16:14 | 8:54 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 2023-11-25 07:15 | 2023-11-25 16:24 | 9:09 | S/O | For Annual Maintenance | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2023-11-26 07:41 | 2023-11-26 16:21 | 8:40 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2023-11-27 07:11 | 2023-11-27 15:41 | 8:30 | S/O | For annual maintenance | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | 132 kV BUS | 2023-11-26 07:56 | 2023-11-26 16:36 | 8:40 | S/O | annual maintenance of 132 kV bus coupler | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | 230kV BUS | 2023-11-27 07:52 | 2023-11-27 16:47 | 8:55 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | 230kV BUS | 2023-11-28 08:22 | 2023-11-28 16:44 | 8:22 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-4 HT | 2023-11-25 07:24 | 2023-11-25 17:08 | 9:44 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-4 LT | 2023-11-11 07:28 | 2023-11-11 17:32 | 10:04 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-4 LT | 2023-11-12 07:48 | 2023-11-12 17:10 | 9:22 | S/O | Annual maintenance work | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-4 LT | 2023-11-15 13:15 | 2023-11-15 17:04 | 3:49 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-5 HT | 2023-11-15 07:30 | 2023-11-15 13:08 | 5:38 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-5 HT | 2023-11-16 07:41 | 2023-11-16 17:00 | 9:19 | S/O | Annual maintenance | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-5 LT | 2023-11-14 06:41 | 2023-11-14 16:54 | 10:13 | S/O | Annual Maintenance | 0 | 0 | No interruption
Benapole 132/33kV Grid Sub-Station | Transformer-1(406T) LT | 2023-11-18 08:14 | 2023-11-18 16:21 | 8:07 | S/O | Annual Maintenance | 0 | 0 | No interruption
Benapole 132/33kV Grid Sub-Station | Transformer-1(406T) LT | 2023-11-19 08:10 | 2023-11-19 16:59 | 8:49 | S/O | Annual Maintenance | 0 | 0 | No interruption
Benapole 132/33kV Grid Sub-Station | Transformer-2(416T) HT | 2023-11-26 08:27 | 2023-11-26 16:30 | 8:03 | S/O | Annual Maintenance | 0 | 0 | No interruption
Benapole 132/33kV Grid Sub-Station | Transformer-2(416T) LT | 2023-11-27 08:11 | 2023-11-27 16:41 | 8:30 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-11-22 09:50 | 2023-11-22 13:57 | 4:07 | S/O | Rajapur feeder CB change | 11 | 45.2833 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Bus-A | 2023-11-19 09:50 | 2023-11-19 14:54 | 5:04 | S/O | Yearly Maintenance | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Bus-B | 2023-11-21 10:47 | 2023-11-21 15:40 | 4:53 | S/O | Annual maintenance | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-11-04 07:29 | 2023-11-04 10:05 | 2:36 | S/O | 33kV Bus Section-1 DS Repair | 38 | 98.8 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-11-12 08:08 | 2023-11-12 16:30 | 8:22 | S/O | Annual Maintenance | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-11-20 08:32 | 2023-11-20 16:07 | 7:35 | S/O | Tan Delta Test | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-11-14 08:21 | 2023-11-14 15:12 | 6:51 | S/O | Annual maintenance | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-3 HT | 2023-11-16 09:42 | 2023-11-16 14:14 | 4:32 | S/O | Annual Maintenance | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-3 HT | 2023-11-20 11:45 | 2023-11-21 15:42 | 27:57 | S/O | Tan delta test | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-3 LT | 2023-11-15 08:25 | 2023-11-16 20:35 | 36:10 | S/O | Annual Maintenance | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | T-5 LT | 2023-11-03 08:19 | 2023-11-03 16:39 | 8:20 | S/O | Annual Maintenance | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | T-5 LT | 2023-11-04 08:29 | 2023-11-04 15:31 | 7:02 | S/O | Annual Maintenance works. | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | T-5 LT | 2023-11-21 08:10 | 2023-11-21 15:20 | 7:10 | S/O | Annualmaimtenance | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | T-6 LT | 2023-11-22 08:14 | 2023-11-22 14:51 | 6:37 | S/O | Yearly Maintanance | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | T-6 LT | 2023-11-23 10:09 | 2023-11-23 15:10 | 5:01 | S/O | Yearly maintenance | 0 | 0 | No interruption
Gollamari 132/33kV Grid Sub-Station | Tr-1 LT | 2023-11-01 08:13 | 2023-11-01 16:07 | 7:54 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gollamari 132/33kV Grid Sub-Station | Tr-2 LT | 2023-11-02 08:03 | 2023-11-02 14:13 | 6:10 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-01 HT | 2023-11-25 08:39 | 2023-11-25 13:53 | 5:14 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-02 LT | 2023-11-15 09:15 | 2023-11-15 20:46 | 11:31 | D/W | SAS Commissioning | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-02 LT | 2023-11-28 08:38 | 2023-11-28 14:37 | 5:59 | S/O | Annual maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-03 HT | 2023-11-07 11:52 | 2023-11-12 15:54 | 124:02 | D/W | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-03 LT | 2023-11-29 09:37 | 2023-11-29 17:26 | 7:49 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T HT | 2023-11-23 10:05 | 2023-11-23 12:01 | 1:56 | S/O | FOR TAN-DELTA TEST | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T LT | 2023-11-05 09:04 | 2023-11-11 15:45 | 150:41 | S/O | Due to Oil centifusing work. | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T LT | 2023-11-15 09:21 | 2023-11-20 17:28 | 128:07 | S/O | Annual maintenance. | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | Tr-2 415 T LT | 2023-11-24 11:12 | 2023-11-27 12:15 | 73:03 | S/O | For Oil Centrifuging | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | Tr-3 405T HT | 2023-11-28 09:09 | 2023-11-28 09:09 | 0:00 | S/O | Oil Centrifuging | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | Tr-3 405T LT | 2023-11-28 09:08 | 2023-11-28 09:08 | 0:00 | S/O | Due to oil Centrifuging | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-1 LT | 2023-11-12 07:42 | 2023-11-12 12:12 | 4:30 | S/O | TR-1 Oil leakage maintenance work. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-1 LT | 2023-11-14 10:48 | 2023-11-14 15:05 | 4:17 | S/O | Oil leakage maintenance work | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-1 LT | 2023-11-22 07:31 | 2023-11-22 17:11 | 9:40 | S/O | Emergency Maintenance Work. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-1 LT | 2023-11-25 09:32 | 2023-11-25 14:44 | 5:12 | S/O | TAN-DELTA TEST. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-3 HT | 2023-11-25 14:46 | 2023-11-25 17:14 | 2:28 | S/O | Annual Maintenance | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | Aux Tr-01 HT | 2023-11-07 09:40 | 2023-11-07 16:15 | 6:35 | S/O | Annual maintenance | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | BUS - A | 2023-11-08 10:08 | 2023-11-08 16:00 | 5:52 | S/O | Annual maintenance | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T2-415T HT | 2023-11-01 08:28 | 2023-11-01 16:13 | 7:45 | S/O | Annual Maintenance | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T2-415T LT | 2023-11-21 06:27 | 2023-11-21 11:22 | 4:55 | S/O | Auxiliary Transformer 2 loop maintenance | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T3-426T HT | 2023-11-05 08:26 | 2023-11-05 15:56 | 7:30 | S/O | Annual Maintenance | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T3-426T LT | 2023-11-04 08:30 | 2023-11-04 17:16 | 8:46 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mongla 132/33kV Grid Sub-Station | T-1 LT | 2023-11-25 08:48 | 2023-11-25 14:48 | 6:00 | S/O | Annual Maintenance of 33 KV Bus. | 10 | 60 | Power interruption
Mongla 132/33kV Grid Sub-Station | T-2 LT | 2023-11-25 08:49 | 2023-11-25 14:49 | 6:00 | S/O | Annual Maintenance of 33KV Bus. | 10 | 60 | Power interruption
Narail 132/33kV Grid Sub-Station | TR1 (403-T) LT | 2023-11-02 08:26 | 2023-11-02 15:28 | 7:02 | S/O | 132 KV Bus Section -01 Annual Maintenance(Tr-01 Shutdown) | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | BUS-B | 2023-11-25 09:24 | 2023-11-25 14:11 | 4:47 | S/O | Annual Maintenance.. | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 405T (T-1) HT | 2023-11-26 08:02 | 2023-11-26 17:50 | 9:48 | S/O | Annual maintenance work | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 405T (T-1) HT | 2023-11-27 07:22 | 2023-11-27 16:33 | 9:11 | S/O | T1 Transformer yearly maintenance work | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 405T (T-1) HT | 2023-11-28 11:35 | 2023-11-28 13:53 | 2:18 | S/O | TAN-DELTA test | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 405T (T-1) LT | 2023-11-25 08:10 | 2023-11-25 15:47 | 7:37 | S/O | T- Transformer yearly maintenance | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 415T (T-2) HT | 2023-11-28 08:05 | 2023-11-28 16:52 | 8:47 | S/O | Annual maintenance-2023 | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 415T (T-2) HT | 2023-11-29 07:43 | 2023-11-29 17:49 | 10:06 | S/O | Annual maintenance-2023 | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 415T (T-2) LT | 2023-11-30 08:16 | 2023-11-30 15:53 | 7:37 | S/O | Annual Maintenance-2023 | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | 132/33 kV Transformer-03 LT | 2023-11-01 13:32 | 2023-11-01 16:16 | 2:44 | S/O | Annual Maintenance | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | 132/33 kV Transformer-04 HT | 2023-11-01 08:29 | 2023-11-01 13:30 | 5:01 | S/O | Anual maintenance | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 HT | 2023-11-09 12:14 | 2023-11-09 15:19 | 3:05 | S/O | Annual maintenance | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 LT | 2023-11-04 08:48 | 2023-11-04 21:06 | 12:18 | S/O | Anual maintenance | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 LT | 2023-11-05 08:02 | 2023-11-05 19:08 | 11:06 | S/O | Annual maintenance | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 LT | 2023-11-06 07:45 | 2023-11-06 20:24 | 12:39 | S/O | Annual maintenance | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 LT | 2023-11-08 07:07 | 2023-11-08 19:07 | 12:00 | S/O | Anual maintenance | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 LT | 2023-11-07 06:46 | 2023-11-07 22:55 | 16:09 | S/O | Anual maintenance | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | BUS-2 (230 kV) | 2023-11-01 08:18 | 2023-11-01 16:19 | 8:01 | S/O | Anual maintenance | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | Bus-I ( 132KV Bus) | 2023-11-02 09:51 | 2023-11-02 21:05 | 11:14 | S/O | Annual maintenance | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | ICT-1 LT | 2023-11-15 08:26 | 2023-11-15 17:20 | 8:54 | S/O | Preventive maintenance purpose. | 0 | 0 | No interruption
Shariatpur 132/33kV Grid Sub-Station | T1-406T LT | 2023-11-15 07:59 | 2023-11-15 17:45 | 9:46 | S/O | Emergency Maintenance | 0 | 0 | No interruption
|  |  | Total : | 1121:47 |  | Unserved Energy : |  | 291.0833
HVDC Grid Circle
BIPTC | 230kV Bus-1 | 2023-11-27 11:24 | 2023-11-27 19:53 | 8:29 | S/O | ANNUAL MAINTENANCE | 0 | 0 | No interruption
BIPTC | 400kV Bus-1 | 2023-11-26 10:02 | 2023-11-26 17:29 | 7:27 | S/O | Annual Maintenance | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Bus-2 | 2023-11-07 13:03 | 2023-11-07 13:03 | 0:00 | D/W | Ruppur project work. | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-1 HT | 2023-11-07 10:09 | 2023-11-07 13:11 | 3:02 | S/O | incoming 33 kv CT oil leakage work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-1 LT | 2023-11-24 06:41 | 2023-11-24 07:52 | 1:11 | S/O | Request by pbs | 11 | 13.0167 | Power interruption
Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-2 HT | 2023-11-25 07:43 | 2023-11-25 11:00 | 3:17 | S/O | 33 kv bus 2 A/M | 10 | 32.8333 | Power interruption
Magura 132/33kV Grid Sub-Station | T-1 (405T) HT | 2023-11-29 11:13 | 2023-11-29 21:15 | 10:02 | D/W | Scada integration | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | T-2 (415T) HT | 2023-11-30 12:45 | 2023-11-30 16:38 | 3:53 | D/W | SCADA Integration | 0 | 0 | No interruption
Ruppur 132/11kV Grid Sub-Station | TR-02 HT | 2023-11-02 10:17 | 2023-11-02 18:32 | 8:15 | S/O | Annual maintenance | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | T-1(405T) HT | 2023-11-18 07:48 | 2023-11-22 16:19 | 104:31 | S/O | Annual maintenance | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | T-2(415T) LT | 2023-11-29 07:46 | 2023-11-30 17:17 | 33:31 | S/O | Annual maintenance work. | 0 | 0 | No interruption
|  |  | Total : | 183:38 |  | Unserved Energy : |  | 45.85
Bogura Grid Circle:
Amnura 132/33kV Grid Sub-Station | Bus-1 | 2023-11-13 09:56 | 2023-11-13 14:05 | 4:09 | S/O | Annual maintenance | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | T-1 (406T) HT | 2023-11-06 08:38 | 2023-11-06 16:35 | 7:57 | S/O | Annual Maintenance | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | T-1 (406T) HT | 2023-11-07 08:18 | 2023-11-07 16:11 | 7:53 | S/O | Annual Maintenance, Clearance from Md. Raton Ali, SAE, ALDC, Bogura. | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | T-2 (416T) HT | 2023-11-08 08:38 | 2023-11-08 16:45 | 8:07 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | T-2 (416T) HT | 2023-11-09 09:41 | 2023-11-09 16:23 | 6:42 | S/O | Annual maintenance | 0 | 0 | Power interruption
Amnura 132/33kV Grid Sub-Station | T-3 (426T) HT | 2023-11-11 08:23 | 2023-11-11 16:39 | 8:16 | S/O | Annual maintenance | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | T-3 (426T) HT | 2023-11-12 08:17 | 2023-11-12 16:35 | 8:18 | S/O | Annual maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132 KV Bus A | 2023-11-19 08:55 | 2023-11-19 16:06 | 7:11 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132 KV Bus A | 2023-11-22 09:18 | 2023-11-22 16:29 | 7:11 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132 KV Bus A | 2023-11-26 15:35 | 2023-11-26 16:11 | 0:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132 KV Bus A | 2023-11-29 14:20 | 2023-11-29 15:51 | 1:31 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132 KV Bus B | 2023-11-26 09:14 | 2023-11-26 15:28 | 6:14 | S/O | Annual Maintenance . | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132 KV Bus B | 2023-11-29 09:28 | 2023-11-29 14:07 | 4:39 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | 132KV Bus-A | 2023-11-01 08:20 | 2023-11-01 12:50 | 4:30 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | 132KV Bus-B | 2023-11-01 13:20 | 2023-11-01 16:35 | 3:15 | S/O | annual maintenance | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 2 | 2023-11-16 09:04 | 2023-11-16 16:15 | 7:11 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 2 | 2023-11-21 09:10 | 2023-11-21 15:36 | 6:26 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-01 HT | 2023-11-23 08:17 | 2023-11-23 09:08 | 0:51 | S/O | Aux. Transformer Oil Filling. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-02 HT | 2023-11-03 07:10 | 2023-11-03 09:56 | 2:46 | S/O | Red hot Maintenance | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | T-3 (425T) LT | 2023-11-05 19:36 | 2023-11-05 21:15 | 1:39 | S/O | 33 kv Bus3 Bus4 Section Ds Red Hot Maintenance | 14 | 23.1 | Power interruption
Chapai 132/33kV Grid Sub-Station | T-4 (435T) LT | 2023-11-05 19:36 | 2023-11-05 21:15 | 1:39 | S/O | 33 kv Bus3 Bus4 Section Ds Red Hot Maintenance | 6 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Main Bus | 2023-11-26 07:35 | 2023-11-26 08:13 | 0:38 | S/O | Bogura ckt1 bus ds change. | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Main Bus | 2023-11-29 07:15 | 2023-11-29 08:45 | 1:30 | S/O | 132KV Bus DS change | 50 | 75 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2023-11-20 08:41 | 2023-11-20 17:17 | 8:36 | S/O | Annual maintenance | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2023-11-21 08:16 | 2023-11-21 16:29 | 8:13 | S/O | Annual maintenance. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | TR-3 (425 T) HT | 2023-11-14 06:48 | 2023-11-14 16:49 | 10:01 | S/O | Annual Maintenance | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | TR-3 (425 T) LT | 2023-11-13 07:45 | 2023-11-14 16:55 | 33:10 | S/O | Year maintenance | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | TR-3 (425 T) LT | 2023-11-21 07:11 | 2023-11-21 11:04 | 3:53 | S/O | Maintenance | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 407T HT | 2023-11-13 08:57 | 2023-11-13 16:52 | 7:55 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 407T HT | 2023-11-14 08:22 | 2023-11-14 16:44 | 8:22 | S/O | annual maintenance | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 417T HT | 2023-11-15 07:55 | 2023-11-15 16:06 | 8:11 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 417T HT | 2023-11-16 06:55 | 2023-11-16 15:45 | 8:50 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | TR1-414T HT | 2023-11-28 06:57 | 2023-11-28 08:59 | 2:02 | S/O | 33 Kv Bus Maintenance. | 30 | 61 | Power interruption
Palashbari 132/33kV Grid Sub-Station | TR2-404T HT | 2023-11-28 06:56 | 2023-11-28 08:59 | 2:03 | S/O | 33 Kv Bus Maintenance. | 30 | 61.5 | Power interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2023-11-21 09:12 | 2023-11-21 17:05 | 7:53 | S/O | Online scheduled shutdown due to oil leakage maintenance. | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | T-1 Transformer (403T) LT | 2023-11-03 08:26 | 2023-11-03 16:22 | 7:56 | S/O | Annual Maintenance 2023 Load serve by T-4 transformer. | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | T-1 Transformer (403T) LT | 2023-11-04 08:56 | 2023-11-04 18:12 | 9:16 | S/O | annual maintenance | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | T-4 Transformer LT | 2023-11-15 08:42 | 2023-11-15 17:52 | 9:10 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | AT-02 LT | 2023-11-23 13:07 | 2023-11-23 16:22 | 3:15 | D/W | Oil level low problem | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-1(405T) LT | 2023-11-02 07:50 | 2023-11-02 15:55 | 8:05 | S/O | For annual maintenance work. | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-1(405T) LT | 2023-11-04 08:14 | 2023-11-04 16:18 | 8:04 | S/O | Yearly maintenance | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-2(415T) LT | 2023-11-01 07:49 | 2023-11-01 15:57 | 8:08 | S/O | For annual maintenance work | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-2(415T) LT | 2023-11-05 07:44 | 2023-11-05 16:25 | 8:41 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) HT | 2023-11-23 08:19 | 2023-11-23 15:53 | 7:34 | S/O | For annual maintenance work. | 10 | 75.6667 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) LT | 2023-11-22 08:15 | 2023-11-22 16:50 | 8:35 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132 kV Main BUS-01 | 2023-11-15 08:39 | 2023-11-15 17:11 | 8:32 | S/O | A/M | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132 kV Main BUS-02 | 2023-11-16 08:31 | 2023-11-16 16:18 | 7:47 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132/33 kV T-01 (406T) HT | 2023-11-29 08:11 | 2023-11-29 16:46 | 8:35 | S/O | A/M | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132/33 kV T-01 (406T) HT | 2023-11-30 08:16 | 2023-11-30 16:25 | 8:09 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) LT | 2023-11-25 08:13 | 2023-11-25 17:17 | 9:04 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) LT | 2023-11-26 08:27 | 2023-11-26 17:19 | 8:52 | S/O | A/M | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) HT | 2023-11-28 08:28 | 2023-11-28 16:34 | 8:06 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) LT | 2023-11-27 08:10 | 2023-11-27 20:08 | 11:58 | S/O | Anual maintenance. | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | BUS B | 2023-11-11 09:05 | 2023-11-11 10:01 | 0:56 | S/O | For 132kv RNP CKT-1 'B' Bus DS Maintenance. | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-01 HT | 2023-11-16 17:28 | 2023-11-16 17:53 | 0:25 | S/O | For testing Black start drill | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-01 HT | 2023-11-17 12:01 | 2023-11-17 12:50 | 0:49 | S/O | For testing Black start drill . | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-01 HT | 2023-11-18 15:40 | 2023-11-18 17:18 | 1:38 | S/O | For black start test | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-3 (424T) HT | 2023-11-26 07:07 | 2023-11-26 09:07 | 2:00 | S/O | Due to 33kv bus shutdown by saidpur NESCO. | 10 | 20 | Power interruption
Sirajgonj 230 kV Switching Station | Bus-1 | 2023-11-14 08:50 | 2023-11-14 18:39 | 9:49 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sirajgonj 230 kV Switching Station | Bus-2 | 2023-11-22 08:32 | 2023-11-22 17:55 | 9:23 | S/O | Annual Maintenance | 0 | 0 | No interruption
|  |  | Total : | 393:05 |  | Unserved Energy : |  | 316.2667
Others :Nil
|  |  | Total : | 0:00 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 4471:34 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: November 2023
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV Grid Sub-Station | Aminbazar Ckt-1 | 2023-11-30 07:29 | 2023-11-30 16:32 | 9:03 | S/O | Anual Maintenance | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Aminbazar Ckt-2 | 2023-11-16 10:35 | 2023-11-16 21:49 | 11:14 | S/O | Annual Maintenance & Relay Testing | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Satmosjid Ckt-1 | 2023-11-08 10:41 | 2023-11-08 16:20 | 5:39 | S/O | Annual Maintenance | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Satmosjid Ckt-1 | 2023-11-09 09:41 | 2023-11-09 16:11 | 6:30 | S/O | Annual Maintenance | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Satmosjid Ckt-2 | 2023-11-16 09:17 | 2023-11-16 15:25 | 6:08 | S/O | Annual Maintenance & Relay Testing | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Satmosjid Ckt-2 | 2023-11-18 09:25 | 2023-11-18 16:04 | 6:39 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Agargaon-01 | 2023-11-23 08:34 | 2023-11-23 14:05 | 5:31 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Agargaon-02 | 2023-11-13 07:54 | 2023-11-13 22:15 | 14:21 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir-01 | 2023-11-02 07:30 | 2023-11-02 20:30 | 13:00 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir-02 | 2023-11-05 09:36 | 2023-11-05 20:01 | 10:25 | S/O | A/M bay equipment work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Keranigonj-01 | 2023-11-06 08:20 | 2023-11-06 20:08 | 11:48 | S/O | Annual maintenance | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | B.Baria 132 kV Ckt-1 | 2023-11-13 08:48 | 2023-11-14 16:37 | 31:49 | S/O | Shutdown by NLDC for annual maintenance work. | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Cumilla(N) 230 kV Ckt-1 | 2023-11-13 09:15 | 2023-11-14 16:19 | 31:04 | S/O | Shutdown by NLDC for annual maintenance work. | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Sreepur 230 kV Ckt-1 | 2023-11-09 09:52 | 2023-11-09 16:38 | 6:46 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Sreepur 230 kV Ckt-1 | 2023-11-11 08:46 | 2023-11-11 16:21 | 7:35 | S/O | Annual maintenance work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Sreepur 230 kV Ckt-2 | 2023-11-14 08:45 | 2023-11-14 18:15 | 9:30 | S/O | Shutdown by NLDC for annual maintenance work. | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Sreepur 230 kV Ckt-2 | 2023-11-15 08:45 | 2023-11-15 19:06 | 10:21 | S/O | As per instruction of NLDC | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Mymensingh- Bhaluka 132 kV Ckt- 01 | 2023-11-04 08:30 | 2023-11-04 16:39 | 8:09 | S/O | Annual maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Mymensingh- Bhaluka 132 kV Ckt- 02 | 2023-11-01 09:20 | 2023-11-01 16:37 | 7:17 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Mymensingh- Bhaluka 132 kV Ckt- 02 | 2023-11-02 08:29 | 2023-11-02 16:10 | 7:41 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Mymensingh- Bhaluka 132 kV Ckt- 02 | 2023-11-07 08:34 | 2023-11-07 16:29 | 7:55 | S/O | OPGW work | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Sreepur- Bhaluka 132 kV Ckt- 01 | 2023-11-25 08:52 | 2023-11-25 17:19 | 8:27 | S/O | Dead Line Checking | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | 132KV UMPL Ckt-01 | 2023-11-18 09:12 | 2023-11-18 15:50 | 6:38 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | 132KV UMPL Ckt-01 | 2023-11-19 09:01 | 2023-11-19 16:13 | 7:12 | S/O | Annual maintenance. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | 132KV UMPL Ckt-01 | 2023-11-20 09:15 | 2023-11-20 16:36 | 7:21 | S/O | Annual Maintenance for Sherpur Grid. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | 132KV UMPL Ckt-01 | 2023-11-23 10:15 | 2023-11-23 16:52 | 6:37 | S/O | A/M | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh Ckt-01 | 2023-11-08 13:20 | 2023-11-08 14:15 | 0:55 | S/O | System protection work will be done in Mymensingh end. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh Ckt-02 | 2023-11-08 14:16 | 2023-11-08 14:53 | 0:37 | S/O | system protection work mym ckt grid side. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh Ckt-02 | 2023-11-13 17:14 | 2023-11-14 21:40 | 28:26 | S/O | CVT Oil Leakage Maintenance Work. | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Ghorashal ckt-2 | 2023-11-10 07:07 | 2023-11-10 16:52 | 9:45 | S/O | Shutdown taken from Ghorasal end | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Kodda ckt-1 | 2023-11-13 06:58 | 2023-11-13 17:21 | 10:23 | S/O | OPGW Cable Change | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Kodda ckt-1 | 2023-11-14 07:25 | 2023-11-14 23:14 | 15:49 | S/O | OPGW work | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Kodda ckt-1 | 2023-11-15 07:36 | 2023-11-15 23:23 | 15:47 | S/O | OPGW Cable Change | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Kodda ckt-1 | 2023-11-19 06:19 | 2023-11-20 19:09 | 36:50 | S/O | OPGW Change | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Kodda ckt-1 | 2023-11-22 06:23 | 2023-11-24 12:34 | 54:11 | S/O | OPGW Change | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Kodda ckt-2 | 2023-11-12 09:36 | 2023-11-12 16:50 | 7:14 | S/O | Annual Maintenance | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Kodda ckt-2 | 2023-11-13 06:58 | 2023-11-13 17:17 | 10:19 | S/O | OPGW Cable Change | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Kodda ckt-2 | 2023-11-14 07:25 | 2023-11-14 23:12 | 15:47 | S/O | OPGW work | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Kodda ckt-2 | 2023-11-15 07:36 | 2023-11-15 23:26 | 15:50 | S/O | OPGW Cable Change | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Kodda ckt-2 | 2023-11-19 06:19 | 2023-11-20 19:06 | 36:47 | S/O | OPGW Change | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Kodda ckt-2 | 2023-11-22 06:23 | 2023-11-24 12:34 | 54:11 | S/O | OPGW Change | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Kadda-1 | 2023-11-28 07:05 | 2023-11-28 16:58 | 9:53 | S/O | OPGW work | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Kadda-1 | 2023-11-29 06:16 | 2023-11-30 12:25 | 30:09 | S/O | OPGW work | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Kadda-2 | 2023-11-28 07:06 | 2023-11-28 16:58 | 9:52 | S/O | OPGW work | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Kadda-2 | 2023-11-29 06:16 | 2023-11-30 12:24 | 30:08 | S/O | OPGW work | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Kaliakair-1 | 2023-11-29 07:08 | 2023-11-29 16:15 | 9:07 | S/O | Annual maintenance | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Manikganj-1 | 2023-11-12 10:39 | 2023-11-12 12:41 | 2:02 | S/O | Relay test done by Spmd | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Manikganj-1 | 2023-11-28 07:18 | 2023-11-28 17:03 | 9:45 | S/O | A/M | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Manikganj-2 | 2023-11-12 11:54 | 2023-11-12 14:56 | 3:02 | S/O | To relay test work done by spmd 2 | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Tongi-1 | 2023-11-21 08:00 | 2023-11-21 17:20 | 9:20 | S/O | Annual maintenance and relay testing. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Tongi-2 | 2023-11-22 08:54 | 2023-11-22 15:59 | 7:05 | S/O | Annual maintenance and relay test. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Bibiyana 2 | 2023-11-28 16:30 | 2023-11-28 17:25 | 0:55 | S/O | Relay Test. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Bibiyana1 | 2023-11-28 13:32 | 2023-11-28 16:23 | 2:51 | S/O | Relay Testing by SPMD | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Tangail-1 | 2023-11-29 10:22 | 2023-11-29 17:16 | 6:54 | S/O | Relay Test by SPMD | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Lalbag Ckt-01 | 2023-11-20 14:40 | 2023-11-20 16:19 | 1:39 | S/O | annual maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Lalbag Ckt-02 | 2023-11-20 16:28 | 2023-11-20 16:51 | 0:23 | S/O | annual maintenance | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-2 | 2023-11-01 09:21 | 2023-11-01 09:44 | 0:23 | S/O | relay test by SPMD | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-2 | 2023-11-06 09:34 | 2023-11-06 14:59 | 5:25 | S/O | For annual maintenance work | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Mymensingh Ckt-1 | 2023-11-08 09:17 | 2023-11-08 10:28 | 1:11 | S/O | Work in Mymensingh Substation | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Mymensingh Ckt-2 | 2023-11-08 10:29 | 2023-11-08 11:13 | 0:44 | S/O | Work in Mymensingh Substation | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Rajendrapur Ckt-1 | 2023-11-05 08:33 | 2023-11-05 17:50 | 9:17 | S/O | Dead line checking | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Rajendrapur Ckt-2 | 2023-11-07 08:21 | 2023-11-07 16:02 | 7:41 | S/O | Dead line checking | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Rajendrapur Ckt-2 | 2023-11-08 08:17 | 2023-11-08 17:30 | 9:13 | S/O | Dead line checking | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2023-11-27 07:06 | 2023-11-27 18:07 | 11:01 | S/O | Annual Maintenance | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2023-11-29 07:30 | 2023-11-29 12:49 | 5:19 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2023-11-30 07:20 | 2023-11-30 17:06 | 9:46 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Aminbazar-1 | 2023-11-16 09:35 | 2023-11-16 17:14 | 7:39 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Aminbazar-2 | 2023-11-19 09:27 | 2023-11-19 16:38 | 7:11 | S/O | Annual maintenance Work. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Aminbazar-2 | 2023-11-22 09:23 | 2023-11-22 18:11 | 8:48 | S/O | Annual Maintenance work on 132Kv Mirpur - Aminbazar ckt 2. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Sector-18 | 2023-11-10 09:05 | 2023-11-10 15:22 | 6:17 | S/O | Annual Maintenance Work (CB&Bay) on 132 KV Mirpur-Uttara sector 18 Ckt . | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Sector-18 | 2023-11-12 09:36 | 2023-11-12 16:45 | 7:09 | S/O | Annual maintenance | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Sector-18 | 2023-11-21 09:14 | 2023-11-21 18:36 | 9:22 | S/O | Annual maintenance works. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Sector-18 | 2023-11-26 09:47 | 2023-11-26 16:47 | 7:00 | S/O | 132 KV Reserve Bus DS(102S) Maintenance Work. | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Bhaluka Ckt-1 | 2023-11-05 08:20 | 2023-11-05 15:56 | 7:36 | S/O | Annual maintenance work on bhaluka grid | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Bhaluka Ckt-1 | 2023-11-08 12:41 | 2023-11-08 13:03 | 0:22 | S/O | S/D due to Realay functional Test purposes by SPMD | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Bhaluka Ckt-2 | 2023-11-06 09:19 | 2023-11-06 16:25 | 7:06 | S/O | Annual maintenance work on bhaluka grid | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Bhaluka Ckt-2 | 2023-11-08 13:14 | 2023-11-08 13:17 | 0:03 | S/O | S/D due to Realay functional Test purposes by SPMD | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Netrakona Ckt-1 | 2023-11-09 09:32 | 2023-11-09 10:24 | 0:52 | S/O | None | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Netrakona Ckt-1 | 2023-11-13 09:52 | 2023-11-13 16:52 | 7:00 | S/O | A/M | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Netrakona Ckt-2 | 2023-11-08 14:57 | 2023-11-08 15:40 | 0:43 | S/O | S/D due to Realay functional Test purposes by SPMD | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Netrakona Ckt-2 | 2023-11-09 11:29 | 2023-11-11 17:15 | 53:46 | S/O | A/M | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Netrakona Ckt-2 | 2023-11-19 09:13 | 2023-11-21 17:17 | 56:04 | S/O | A/M | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Netrakona Ckt-2 | 2023-11-22 09:23 | 2023-11-22 17:30 | 8:07 | S/O | A/M | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-RPCL Ckt-1 | 2023-11-08 11:21 | 2023-11-08 11:52 | 0:31 | S/O | S/D due to Realay functional Test purposes by SPMD | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-RPCL Ckt-1 | 2023-11-25 09:31 | 2023-11-25 17:16 | 7:45 | S/O | Annual maintenance work | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-RPCL Ckt-1 | 2023-11-26 09:29 | 2023-11-26 17:01 | 7:32 | S/O | A/M | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-RPCL Ckt-2 | 2023-11-08 11:53 | 2023-11-08 12:13 | 0:20 | S/O | S/D due to Realay functional Test purposes by SPMD | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-RPCL Ckt-2 | 2023-11-30 09:22 | 2023-11-30 17:08 | 7:46 | S/O | Annual maintenance work | 0 | 0 | No interruption
Netrakona 132/33kV Grid Sub-Station | Mymensingh-Netrokona Ckt-1 | 2023-11-12 09:21 | 2023-11-12 16:39 | 7:18 | S/O | Annual Maintenance | 0 | 0 | No interruption
Netrakona 132/33kV Grid Sub-Station | Mymensingh-Netrokona Ckt-2 | 2023-11-21 09:08 | 2023-11-21 17:18 | 8:10 | S/O | Annual maintenance | 0 | 0 | No interruption
New Tongi 132/33kV Grid Sub-Station | New Tongi L-1 | 2023-11-20 09:13 | 2023-11-20 15:22 | 6:09 | S/O | Annual Maintenance | 0 | 0 | No interruption
New Tongi 132/33kV Grid Sub-Station | New Tongi L-1 | 2023-11-21 11:04 | 2023-11-27 15:08 | 148:04 | S/O | Yearly maintenance | 0 | 0 | No interruption
New Tongi 132/33kV Grid Sub-Station | New Tongi L-2 | 2023-11-09 09:26 | 2023-11-09 16:27 | 7:01 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rajendrapur 132/33kV Grid Sub-Station | Kodda-1 | 2023-11-06 07:25 | 2023-11-06 17:08 | 9:43 | S/O | Dead line checking from kodda sub-station. | 0 | 0 | No interruption
Rajendrapur 132/33kV Grid Sub-Station | Kodda-1 | 2023-11-25 09:25 | 2023-11-25 15:52 | 6:27 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rajendrapur 132/33kV Grid Sub-Station | Kodda-2 | 2023-11-26 09:02 | 2023-11-26 15:04 | 6:02 | D/W | kodda end work purpose | 0 | 0 | No interruption
Satmasjid 132/33kV Grid Sub-Station | 132 KV Agargaon-Satmasjid Line-1 | 2023-11-08 10:40 | 2023-11-08 16:21 | 5:41 | S/O | Agargon -Samasjid LINE-1 S/D from Agargoan S/S. | 0 | 0 | No interruption
Satmasjid 132/33kV Grid Sub-Station | 132 KV Agargaon-Satmasjid Line-1 | 2023-11-09 09:40 | 2023-11-09 16:15 | 6:35 | S/O | Annual Maintenance. Agargaon 230/132 kV Grid S/S demands. | 0 | 0 | No interruption
Satmasjid 132/33kV Grid Sub-Station | 132 KV Agargaon-Satmasjid Line-2 | 2023-11-16 09:21 | 2023-11-16 15:27 | 6:06 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-1 | 2023-11-09 09:53 | 2023-11-09 16:39 | 6:46 | S/O | Sreepur-Ashuganj ckt-1 line maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-1 | 2023-11-11 09:27 | 2023-11-11 16:16 | 6:49 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-2 | 2023-11-14 08:59 | 2023-11-14 18:15 | 9:16 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-2 | 2023-11-15 09:13 | 2023-11-15 19:06 | 9:53 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Valuka Ckt-1 | 2023-11-25 08:54 | 2023-11-25 17:17 | 8:23 | S/O | Annual Maintenance (Line) | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-2 | 2023-11-02 08:44 | 2023-11-02 16:57 | 8:13 | S/O | Maintenance work(jumper Tower-22) | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-1 | 2023-11-26 10:10 | 2023-11-26 15:44 | 5:34 | S/O | Protection work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-2 | 2023-11-28 11:22 | 2023-11-28 12:39 | 1:17 | S/O | Annual maintenance work | 0 | 0 | No interruption
|  |  | Total : | 1263:02 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Bhulta 132/33kV Grid Sub-Station | Haripur | 2023-11-25 08:58 | 2023-11-25 16:30 | 7:32 | S/O | Annual Maintenance | 0 | 0 | Power interruption
Bhulta 400/230kV Grid Sub-Station | Ghorashal-01 | 2023-11-20 08:51 | 2023-11-20 17:00 | 8:09 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | Ghorashal-02 | 2023-11-22 08:20 | 2023-11-22 16:56 | 8:36 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | Horipur-02 | 2023-11-18 09:16 | 2023-11-18 16:38 | 7:22 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | Rampura-03 | 2023-11-09 07:09 | 2023-11-09 17:25 | 10:16 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | 132 kV Shyampur-1 | 2023-11-14 07:42 | 2023-11-14 15:14 | 7:32 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | 132 kV Shyampur-2 | 2023-11-15 09:01 | 2023-11-15 13:35 | 4:34 | S/O | Annual winter maintenance | 0 | 0 | No interruption
Gulshan 132/33kV Grid Sub-Station | Rampura-2 | 2023-11-23 08:25 | 2023-11-23 15:45 | 7:20 | S/O | Annual maintenance | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 230kV Bhulta-1 | 2023-11-05 09:55 | 2023-11-05 15:36 | 5:41 | S/O | Annual Maintenance | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 230kV Bhulta-1 | 2023-11-15 08:48 | 2023-11-15 19:10 | 10:22 | S/O | Work on other side. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 230kV Bhulta-1 | 2023-11-29 11:22 | 2023-11-29 15:50 | 4:28 | S/O | Relay changing work by SPMD. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 230kV Bhulta-2 | 2023-11-08 09:47 | 2023-11-08 16:03 | 6:16 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Meghnaghat-1 | 2023-11-06 10:40 | 2023-11-06 13:47 | 3:07 | S/O | High Temperature maintenance. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Meghnaghat-1 | 2023-11-13 09:27 | 2023-11-13 14:50 | 5:23 | S/O | Another Side by NLDC. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Narsingdi | 2023-11-27 09:02 | 2023-11-27 15:18 | 6:16 | S/O | From other end. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Sonargaon 2 | 2023-11-03 11:54 | 2023-11-03 12:50 | 0:56 | S/O | SCADA Integration work at Sonargaon end. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2023-11-23 08:48 | 2023-11-23 16:32 | 7:44 | S/O | By NLDC (Another Side) | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | Fatulla (Pre-Brahmongaon) | 2023-11-14 11:59 | 2023-11-14 12:54 | 0:55 | D/W | Tariff meter change | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | Keraniganj-2 (Pre- Aourahati) | 2023-11-16 07:41 | 2023-11-16 07:41 | 0:00 | S/O | From Keraniganj ending CB OPEN at 07:34 hrs and from our hasnabad Ending E/S Close at 07:41 hrs | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aggreko | 2023-11-16 07:34 | 2023-11-16 14:43 | 7:09 | S/O | Annual maientence work | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aminbazar-1 | 2023-11-07 07:43 | 2023-11-07 17:04 | 9:21 | S/O | Annula Maintenance Work. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aminbazar-2 | 2023-11-08 07:39 | 2023-11-08 17:25 | 9:46 | S/O | Yearly maintenance. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aminbazar-2 | 2023-11-09 07:37 | 2023-11-09 15:06 | 7:29 | S/O | Annual maintenance at Aminbazar end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad | 2023-11-15 07:49 | 2023-11-15 13:57 | 6:08 | S/O | Annual maintenance work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Haripur 132 kv Ckt-1 | 2023-11-02 10:36 | 2023-11-02 17:43 | 7:07 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Munshiganj 132 kv Ckt-1 | 2023-11-23 12:18 | 2023-11-23 16:20 | 4:02 | S/O | Annual Maintenance | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Munshiganj 132 kv Ckt-1 | 2023-11-25 09:28 | 2023-11-25 13:09 | 3:41 | S/O | Due maint.work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Shitalakhya 132 kv Ckt | 2023-11-12 10:16 | 2023-11-12 16:32 | 6:16 | S/O | Due maint.work | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Haripur Ckt-2 | 2023-11-23 09:08 | 2023-11-23 17:02 | 7:54 | S/O | Annual Maintenance schedule 2023-24 | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Kazla Ckt -1 | 2023-11-26 08:34 | 2023-11-26 12:34 | 4:00 | S/O | Annual Maintenance Shutdown 2023-24. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Kazla Ckt -2 | 2023-11-03 10:36 | 2023-11-03 12:14 | 1:38 | S/O | CB loop conductor replacement work by DPDC. Shut down taken by Mr. Rokonul Islam, SDE, DPPDC. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Matuail Single Ckt | 2023-11-29 07:39 | 2023-11-29 15:12 | 7:33 | S/O | Annual schedule maintenance. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Motijheel Ckt-2 | 2023-11-24 08:47 | 2023-11-24 16:25 | 7:38 | S/O | Annual Maintenance schedule 2023-24 | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Narinda Ckt-1 | 2023-11-27 09:30 | 2023-11-27 14:43 | 5:13 | S/O | Annual Maintenance Works by shutdown. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Narinda Ckt-2 | 2023-11-30 09:43 | 2023-11-30 17:42 | 7:59 | S/O | Annaul Maintenance Work . | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | 230kV Siddhirganj-Maniknagar ckt-2 | 2023-11-29 07:15 | 2023-11-29 13:46 | 6:31 | S/O | Oil filling work of Transformer-2 | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Comilla-01 | 2023-11-05 08:20 | 2023-11-05 15:38 | 7:18 | S/O | For Annual Maintenance | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Haripur-02 | 2023-11-19 09:18 | 2023-11-19 14:04 | 4:46 | S/O | For annual maintenance | 0 | 0 | No interruption
Munshiganj 132/33kV Grid Sub-Station | Madanganj- Munshiganj- Ckt-2 | 2023-11-27 09:38 | 2023-11-27 15:36 | 5:58 | S/O | Annual Maintenance | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | Ghorasal-01 | 2023-11-29 09:14 | 2023-11-29 16:49 | 7:35 | S/O | CV Open from Ghorashal side | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | Ghorasal-02 | 2023-11-30 09:35 | 2023-11-30 16:32 | 6:57 | S/O | For Bhulta 132kV Dead line Cheeking Purpose. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2023-11-30 07:24 | 2023-11-30 21:56 | 14:32 | S/O | Shutdown for Annual Maintenance | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-02 | 2023-11-19 12:38 | 2023-11-19 19:44 | 7:06 | S/O | Dead line check. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-02 | 2023-11-20 08:30 | 2023-11-20 15:16 | 6:46 | S/O | Basundhara 132kV Ckt-2 Shutdown for Annual maintenance. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Bhulta Ckt-02 | 2023-11-07 07:13 | 2023-11-07 19:23 | 12:10 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Bhulta Ckt-04 | 2023-11-13 07:40 | 2023-11-13 18:43 | 11:03 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Bhulta Ckt-04 | 2023-11-14 07:11 | 2023-11-14 17:23 | 10:12 | S/O | Annual maintenance | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 230 kV Meghnaghat-2(D05) | 2023-11-02 05:49 | 2023-11-02 08:39 | 2:50 | S/O | Annual Maintenance | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT2 | 2023-11-09 09:25 | 2023-11-09 13:27 | 4:02 | S/O | Inspection of unit Transformer -2, Work done by EGCB | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Matuail | 2023-11-17 09:07 | 2023-11-17 15:18 | 6:11 | D/W | 132/33 kV T-3 Transformer jack bus connection with Bus-A | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | Haripur 2 | 2023-11-14 09:16 | 2023-11-14 16:13 | 6:57 | S/O | Annual maintenance | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Bashundhara Line | 2023-11-09 14:35 | 2023-11-09 17:20 | 2:45 | S/O | Red hot at bus DS-1189 Bashundhara line | 5 | 13.75 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Daudkandi-2 | 2023-11-01 09:35 | 2023-11-01 12:32 | 2:57 | S/O | Scada status integration work. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Haripur-1 | 2023-11-01 15:01 | 2023-11-01 17:20 | 2:19 | S/O | Scada status integration work. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | OPML(IEL-1) | 2023-11-03 07:28 | 2023-11-03 10:01 | 2:33 | S/O | Scada status integration work. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | OPSL(IEL-2) | 2023-11-03 10:19 | 2023-11-03 11:29 | 1:10 | S/O | Scada Integration Work | 0 | 0 | No interruption
|  |  | Total : | 348:01 |  | Unserved Energy: |  | 13.75
Chattogram Grid Circle :
AKS 132/33kV Grid Sub-Station | Bar Aulia | 2023-11-17 09:10 | 2023-11-17 17:05 | 7:55 | S/O | AKSPL-Khulshi 132 kv Line & AKSPL-Baraulia 132 kv Line Shutdown due to Baraulia Line CT (R-Phase) Replace. | 0 | 0 | No interruption
AKS 132/33kV Grid Sub-Station | Khulshi | 2023-11-17 09:08 | 2023-11-17 17:05 | 7:57 | S/O | AKSPL-Khulshi 132 kv Line & AKSPL-Baraulia 132 kv Line Shutdown due to Baraulia Line CT (R-Phase) Replace. | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | Cumilla Ckt-1 | 2023-11-02 08:57 | 2023-11-02 16:24 | 7:27 | S/O | Scheduled S/D , S/D taken by NLDC AE. | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | Cumilla Ckt-2 | 2023-11-06 09:52 | 2023-11-06 14:53 | 5:01 | S/O | Deadline Checking, S/D taken by Mirsarai EZ Incharge. | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | Cumilla Ckt-2 | 2023-11-08 08:40 | 2023-11-08 14:33 | 5:53 | S/O | Yearly Maintenance | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-2 | 2023-11-01 08:51 | 2023-11-01 16:52 | 8:01 | S/O | Yearly Maintenance | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | PHP | 2023-11-22 09:37 | 2023-11-22 16:16 | 6:39 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona- Rangamati Ckt-01 | 2023-11-13 08:44 | 2023-11-13 16:25 | 7:41 | S/O | Dead line check | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona- Rangamati Ckt-01 | 2023-11-15 08:33 | 2023-11-15 15:35 | 7:02 | S/O | Dead line check | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona- Rangamati Ckt-02 | 2023-11-26 07:53 | 2023-11-26 15:58 | 8:05 | S/O | Maintenance by Rangamati ss | 0 | 0 | No interruption
Coxsbazar 132/33kV Grid Sub-Station | Doh-Cox Ckt-1 | 2023-11-22 08:58 | 2023-11-22 10:51 | 1:53 | S/O | annual maintenance | 0 | 0 | No interruption
Coxsbazar 132/33kV Grid Sub-Station | Doh-Cox Ckt-1 | 2023-11-26 15:51 | 2023-11-26 17:18 | 1:27 | S/O | Annual maintenance (Dohazari side) | 0 | 0 | No interruption
Coxsbazar 132/33kV Grid Sub-Station | Doh-Cox Ckt-1 | 2023-11-27 10:04 | 2023-11-30 17:21 | 79:17 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Cox's Bazar ckt-1 | 2023-11-29 09:23 | 2023-11-29 17:17 | 7:54 | S/O | Annual maintenance taken by Matarbari SS | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Cox's Bazar ckt-1 | 2023-11-30 09:12 | 2023-11-30 17:20 | 8:08 | S/O | annual maintenance taken by matarbari ss | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-1 | 2023-11-09 08:58 | 2023-11-09 17:14 | 8:16 | S/O | Annual Maintenance (Taken by Shikalbaha grid). | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-1 | 2023-11-12 08:54 | 2023-11-12 16:37 | 7:43 | S/O | Annual Maintenance Dead Line Checking | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-1 | 2023-11-14 09:20 | 2023-11-14 17:15 | 7:55 | S/O | S/D taken by shikalbaha 230 kv grid.. | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-1 | 2023-11-18 11:46 | 2023-11-18 14:12 | 2:26 | S/O | SD taken by shikalbaha 230kv SS | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-2 | 2023-11-15 09:04 | 2023-11-15 16:35 | 7:31 | S/O | Annual Deadline checking. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Julda Ckt. line | 2023-11-22 11:12 | 2023-11-22 13:10 | 1:58 | S/O | Due to multifunction meter installation work at julda sub-station end. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Rampur Ckt-2 | 2023-11-29 09:39 | 2023-11-29 16:07 | 6:28 | S/O | for annual maintenance work. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Rampur Ckt-2 | 2023-11-30 08:12 | 2023-11-30 15:59 | 7:47 | S/O | Halishahar Rampur Ckt-2 given S/D for annual maintenance work. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Baroiarhat-01 | 2023-11-18 09:30 | 2023-11-18 12:56 | 3:26 | S/O | Baroierhat-01 S/S Requirement | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Kaptai-01 | 2023-11-20 09:17 | 2023-11-20 19:16 | 9:59 | S/O | Annual maintenance. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Kaptai-02 | 2023-11-21 09:07 | 2023-11-21 15:47 | 6:40 | S/O | Annual maintenance | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Madunaghat GIS-01 | 2023-11-06 10:41 | 2023-11-06 17:44 | 7:03 | S/O | Modunaghat ss requirement. | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Shahmirpur 1 | 2023-11-21 11:19 | 2023-11-21 13:02 | 1:43 | S/O | Multi function meter gnstallation | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Shahmirpur 2 | 2023-11-21 13:05 | 2023-11-21 14:42 | 1:37 | S/O | multi function meter installation | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Sikalbaha | 2023-11-21 14:53 | 2023-11-21 16:31 | 1:38 | S/O | Multi-function meter install. | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Halishahar CKT-1(Rampur) | 2023-11-23 07:15 | 2023-11-23 16:33 | 9:18 | S/O | Annual maintenance | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Sholoshahar CKT-1(Madunaghat) | 2023-11-23 12:43 | 2023-11-25 14:56 | 50:13 | D/W | ESPNCA Pailing | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Hathazari-1 | 2023-11-04 08:39 | 2023-11-04 16:14 | 7:35 | S/O | For annual deadline checking and maintenance work. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Kulshi-2 | 2023-11-02 06:11 | 2023-11-23 10:39 | 508:28 | D/W | by Kulshi Grid sub-station for project work purposes. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-T.K. chemical complex | 2023-11-06 08:30 | 2023-11-06 18:19 | 9:49 | S/O | Corrective Red hot maintanence work at Tk chemical Grid end. | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-1 | 2023-11-23 07:43 | 2023-11-23 16:35 | 8:52 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-1 | 2023-11-27 08:19 | 2023-11-27 15:36 | 7:17 | S/O | Annual Maintenance at Halishahar grid | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-1 | 2023-11-28 08:45 | 2023-11-28 17:36 | 8:51 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-2 | 2023-11-29 09:40 | 2023-11-29 15:55 | 6:15 | S/O | Annual maintenance | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-2 | 2023-11-30 08:14 | 2023-11-30 16:00 | 7:46 | S/O | Annual maintenance, Halishahor s/s. | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Khulshi-1 | 2023-11-23 07:16 | 2023-11-23 16:34 | 9:18 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Khulshi-1 | 2023-11-28 09:39 | 2023-11-28 17:33 | 7:54 | S/O | Replacing jumper over monopole. | 0 | 0 | No interruption
Rangamati 132/33kV Grid Sub-Station | Chandraghona Ckt-01 | 2023-11-14 08:32 | 2023-11-14 16:01 | 7:29 | S/O | Annual maintenance Dead line checking | 0 | 0 | No interruption
Rangamati 132/33kV Grid Sub-Station | Chandraghona Ckt-01 | 2023-11-16 08:35 | 2023-11-16 16:32 | 7:57 | S/O | Annual deadline checking. | 0 | 0 | No interruption
Rangamati 132/33kV Grid Sub-Station | Chandraghona Ckt-02 | 2023-11-27 08:58 | 2023-11-27 16:44 | 7:46 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rangamati 132/33kV Grid Sub-Station | Chandraghona Ckt-02 | 2023-11-28 08:37 | 2023-11-28 16:01 | 7:24 | S/O | Rangamati-Chandraghona Ckt-02 taken shutdown due to annual deadline Checking. | 0 | 0 | No interruption
Rangamati 132/33kV Grid Sub-Station | Chandraghona Ckt-02 | 2023-11-29 08:48 | 2023-11-29 16:53 | 8:05 | S/O | Annual deadline checking | 0 | 0 | No interruption
Rangamati 132/33kV Grid Sub-Station | Khagrachari Ckt-02 | 2023-11-30 09:48 | 2023-11-30 16:45 | 6:57 | S/O | Annual maintenance | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Dohazari Ckt-2 | 2023-11-19 09:17 | 2023-11-19 16:54 | 7:37 | S/O | Dead line checking. | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Dohazari Ckt-2 | 2023-11-20 09:05 | 2023-11-20 17:11 | 8:06 | S/O | Yearly Maintenance | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Dohazari ckt-1 | 2023-11-08 09:12 | 2023-11-08 16:22 | 7:10 | S/O | Annual maintenance | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Dohazari ckt-1 | 2023-11-13 08:46 | 2023-11-13 17:08 | 8:22 | S/O | Deadline Checking | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Modunaghat Ckt-2(T.K Chemical) | 2023-11-01 09:00 | 2023-11-01 17:11 | 8:11 | S/O | Deadline Checking | 0 | 0 | No interruption
Sholosohor 132/33kV Grid Sub-Station | Sholoshahar-Khulshi Ckt-1 | 2023-11-23 12:44 | 2023-11-25 14:57 | 50:13 | D/W | Project work at Khulshi Grid | 0 | 0 | No interruption
|  |  | Total : | 1029:23 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-1 | 2023-11-14 09:01 | 2023-11-14 16:38 | 7:37 | S/O | Annual maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-1 | 2023-11-15 09:20 | 2023-11-15 15:10 | 5:50 | S/O | Annual maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-2 | 2023-11-16 09:02 | 2023-11-16 20:59 | 11:57 | S/O | Annual maintenance. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-2 | 2023-11-17 10:52 | 2023-11-21 17:27 | 102:35 | S/O | NLDC AE. | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 50MW(ST) Power Plant Incomer(T3) | 2023-11-08 12:42 | 2023-11-08 12:42 | 0:00 | S/O | Maintenance work. S/D taken by Md. Tazul Islam Raju, AE, BPDB, Chandpur 150MW CCPP | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | Chandpur-Kachua Ckt-1 | 2023-11-03 06:55 | 2023-11-03 17:45 | 10:50 | D/W | Kachua to Gazaria 230KV line Project work | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | Chandpur-Kachua Ckt-2 | 2023-11-03 06:55 | 2023-11-03 17:45 | 10:50 | D/W | Kachua to Gazaria 230KV line Project work | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | Sunamganj 1 | 2023-11-09 08:11 | 2023-11-09 11:10 | 2:59 | S/O | Removal of short loop between phase to phase chhatak-sunamganj Ckt-1. | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | Sylhet 01 | 2023-11-18 08:40 | 2023-11-18 14:43 | 6:03 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | Sylhet 01 | 2023-11-19 07:38 | 2023-11-19 14:47 | 7:09 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni line-01 | 2023-11-25 06:35 | 2023-11-25 11:43 | 5:08 | D/W | ERS install of 47 no Tower for Dismantle of tower. | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni line-02 | 2023-11-24 06:38 | 2023-11-24 15:50 | 9:12 | D/W | Annual maintenance | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Daudkandi Ckt-1 | 2023-11-28 08:13 | 2023-11-28 16:23 | 8:10 | S/O | Annual maintenance | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Kachua Ckt-1 | 2023-11-20 08:48 | 2023-11-20 16:08 | 7:20 | S/O | Annual Maintenance | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Kachua Ckt-1 | 2023-11-21 08:38 | 2023-11-21 16:52 | 8:14 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Kachua Ckt-1 | 2023-11-22 08:39 | 2023-11-22 16:08 | 7:29 | S/O | Annual maintenance | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Ashuganj Ckt-1 | 2023-11-11 08:51 | 2023-11-11 16:01 | 7:10 | S/O | annual maintenance | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Ashuganj Ckt-2 | 2023-11-15 09:08 | 2023-11-15 15:56 | 6:48 | S/O | Annual Maintenance & Deadline Checking | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Ashuganj Ckt-2 | 2023-11-16 08:27 | 2023-11-16 16:38 | 8:11 | S/O | Deadline checking(AM) | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Ashuganj Ckt-2 | 2023-11-19 08:52 | 2023-11-19 15:26 | 6:34 | S/O | Annual Bay Maintenance | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-BSRM Ckt-1 | 2023-11-01 08:50 | 2023-11-01 16:20 | 7:30 | S/O | Deadline Checking | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-BSRM Ckt-1 | 2023-11-04 08:36 | 2023-11-04 14:55 | 6:19 | S/O | Annual maintenance. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-BSRM Ckt-1 | 2023-11-05 08:57 | 2023-11-05 12:25 | 3:28 | S/O | AM of Cumilla (N) SS | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Tripura Ckt-2 | 2023-11-10 09:15 | 2023-11-10 19:49 | 10:34 | S/O | Maintenance Work at Tripura end. | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-1 | 2023-11-27 07:40 | 2023-11-27 15:37 | 7:57 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-1 | 2023-11-29 08:23 | 2023-11-29 17:02 | 8:39 | S/O | Annual Maintenance | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-2 | 2023-11-30 08:32 | 2023-11-30 16:43 | 8:11 | S/O | for annual maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Kulaura-1 | 2023-11-25 09:41 | 2023-11-25 15:54 | 6:13 | S/O | Annual Maintenance by Kulaura S/S | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Kulaura-1 | 2023-11-26 08:48 | 2023-11-26 17:30 | 8:42 | S/O | Annual Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Power Station-1 | 2023-11-06 06:57 | 2023-11-06 13:22 | 6:25 | S/O | Red hot maintenance at Power station SS end Bus-bar. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Power Station-2 | 2023-11-06 06:57 | 2023-11-06 13:29 | 6:32 | S/O | Red hot maintenance at Power station SS end Bus-bar. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Power Station-3 | 2023-11-06 06:57 | 2023-11-20 19:23 | 348:26 | S/O | Red hot maintenance at Power station SS end Bus-bar. | 0 | 0 | No interruption
Kachua 132/33kV Grid Sub-Station | Cumilla North CKT | 2023-11-20 08:47 | 2023-11-20 16:18 | 7:31 | S/O | Annual maintenance | 0 | 0 | No interruption
Kachua 132/33kV Grid Sub-Station | Cumilla North CKT | 2023-11-21 08:38 | 2023-11-21 16:52 | 8:14 | S/O | Annual maintenance | 0 | 0 | No interruption
Kachua 132/33kV Grid Sub-Station | Cumilla North CKT | 2023-11-22 08:37 | 2023-11-22 16:07 | 7:30 | S/O | Annual maintenance | 0 | 0 | No interruption
Kachua 132/33kV Grid Sub-Station | Cumilla South CKT | 2023-11-23 08:27 | 2023-11-23 17:08 | 8:41 | S/O | Annual maintenance | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | 132 Fenchuganj-1 | 2023-11-27 08:48 | 2023-11-27 16:52 | 8:04 | S/O | Annual maintenance | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | 132 Fenchuganj-1 | 2023-11-28 08:41 | 2023-11-28 17:02 | 8:21 | S/O | Annual maintenance. | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | 132 Fenchuganj-2 | 2023-11-29 09:20 | 2023-11-29 16:50 | 7:30 | S/O | Annual maintenance | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | 132 Fenchuganj-2 | 2023-11-30 09:20 | 2023-11-30 17:13 | 7:53 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Ramganj 132/33kV Grid Sub-Station | Ramgonj-Desh Energy Ckt-02 | 2023-11-21 09:52 | 2023-11-21 13:23 | 3:31 | S/O | Armouring conductor at ramgonj -desh energy ckt-02 line | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-1 | 2023-11-25 08:51 | 2023-11-25 16:50 | 7:59 | S/O | For dead line checking. | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-1 | 2023-11-26 08:23 | 2023-11-26 17:12 | 8:49 | S/O | for dead line checking | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-1 | 2023-11-27 09:05 | 2023-11-27 16:56 | 7:51 | S/O | Annual Maintanance Works | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-1 | 2023-11-28 09:26 | 2023-11-28 17:01 | 7:35 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-2 | 2023-11-29 08:27 | 2023-11-29 16:23 | 7:56 | S/O | Annual Maintenance and Dead line Checking. | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-2 | 2023-11-30 09:17 | 2023-11-30 15:33 | 6:16 | S/O | for deadline checkimg | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Chhatak-Sunamgonj CKT-1 | 2023-11-09 08:11 | 2023-11-09 11:12 | 3:01 | D/W | 132kv ckt-1 shutdown due to project work ckt-2 bay . | 22 | 66.3667 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Chhatak-Sunamgonj CKT-1 | 2023-11-14 13:15 | 2023-11-14 14:03 | 0:48 | D/W | 132kv ckt-1 shutdown due to project work ckt-2 bay . | 20 | 16 | Power interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-90MW P/S | 2023-11-06 07:46 | 2023-11-06 13:28 | 5:42 | S/O | 132 KV Bus Maintenance by 90 MW PS. SD operation direction by NLDC ( 299724) | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-90MW P/S | 2023-11-22 08:56 | 2023-11-22 10:41 | 1:45 | S/O | Due to relay testing | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Chhatak Ckt-1 | 2023-11-23 12:50 | 2023-11-23 13:40 | 0:50 | S/O | Maintenance work | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Chhatak Ckt-2 | 2023-11-23 11:36 | 2023-11-23 12:46 | 1:10 | S/O | Relay Test | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Fenchuganj SS | 2023-11-05 05:34 | 2023-11-05 15:16 | 9:42 | S/O | Yearly maintenance. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Fenchuganj SS | 2023-11-07 08:44 | 2023-11-07 14:46 | 6:02 | S/O | Yearly Maintenance | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Fenchuganj SS | 2023-11-22 11:07 | 2023-11-22 12:10 | 1:03 | S/O | Relay Testing Purpose. | 0 | 0 | No interruption
|  |  | Total : | 812:46 |  | Unserved Energy: |  | 82.3667
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Bagerhat-Mongla 1 | 2023-11-07 08:21 | 2023-11-07 16:03 | 7:42 | S/O | Annual maintenance work | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Bagerhat-Mongla 2 | 2023-11-12 07:28 | 2023-11-12 13:57 | 6:29 | S/O | Annual maintenance work | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | Bhola Ckt-2 | 2023-11-20 14:05 | 2023-11-20 16:28 | 2:23 | S/O | Emergency ROW | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Gopalganj (400kv) ckt-2 | 2023-11-16 09:18 | 2023-11-16 19:52 | 10:34 | D/W | Maintenance work at Gopalganj 400kV SS end. | 0 | 0 | No interruption
Gollamari 132/33kV Grid Sub-Station | E01 Gollamari-Gopalgonj Line - 1 | 2023-11-25 08:11 | 2023-11-25 17:02 | 8:51 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Gollamari 132/33kV Grid Sub-Station | E01 Gollamari-Gopalgonj Line - 1 | 2023-11-27 08:07 | 2023-11-27 16:34 | 8:27 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Gollamari 132/33kV Grid Sub-Station | E03 Gollamari-Khulna(S) Line-1 | 2023-11-08 07:46 | 2023-11-08 16:07 | 8:21 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gollamari 132/33kV Grid Sub-Station | E05 Gollamari-Khulna(S) Line-2 | 2023-11-11 08:21 | 2023-11-11 15:30 | 7:09 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Gallamari-1 | 2023-11-25 08:12 | 2023-11-25 17:01 | 8:49 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Gallamari-1 | 2023-11-26 08:16 | 2023-11-26 16:43 | 8:27 | S/O | Yearly maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Gallamari-1 | 2023-11-27 08:06 | 2023-11-27 16:33 | 8:27 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Gallamari-2 | 2023-11-28 08:16 | 2023-11-28 16:01 | 7:45 | S/O | Annual maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Gallamari-2 | 2023-11-29 08:09 | 2023-11-29 16:08 | 7:59 | S/O | Yearly maintenance. | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Gallamari-2 | 2023-11-30 08:19 | 2023-11-30 14:48 | 6:29 | S/O | Y/M | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Gopalganj Ckt-1 | 2023-11-06 09:26 | 2023-11-06 20:46 | 11:20 | D/W | SAS commissioning | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-3 | 2023-11-16 09:24 | 2023-11-16 19:32 | 10:08 | D/W | SAS & DFDR Commissioning | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-4 | 2023-11-05 09:27 | 2023-11-05 21:36 | 12:09 | D/W | SAS & DFDR Commissioning | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-4 | 2023-11-06 09:22 | 2023-11-06 20:39 | 11:17 | D/W | SAS Commissioning | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Aminbazar Ckt-2 | 2023-11-20 11:55 | 2023-11-20 20:40 | 8:45 | D/W | SAS COMMISSIONING | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Rampal Ckt-1 | 2023-11-18 10:07 | 2023-11-18 21:14 | 11:07 | D/W | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Rampal Ckt-1 | 2023-11-19 09:30 | 2023-11-19 21:23 | 11:53 | D/W | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Rampal Ckt-1 | 2023-11-20 09:30 | 2023-11-20 21:12 | 11:42 | D/W | Sas commissioning | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Rampal Ckt-2 | 2023-11-07 11:44 | 2023-11-09 22:40 | 58:56 | D/W | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Rampal Ckt-2 | 2023-11-10 10:13 | 2023-11-10 22:42 | 12:29 | D/W | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Rampal Ckt-2 | 2023-11-11 09:35 | 2023-11-11 20:14 | 10:39 | D/W | Due to maint.work | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | 132kV Central-Noapara-1 | 2023-11-22 07:37 | 2023-11-22 15:43 | 8:06 | S/O | Due to annual maintenance. | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | 132kV Central-Noapara-1 | 2023-11-23 07:44 | 2023-11-23 15:50 | 8:06 | S/O | Annual maintenance | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | KPCL-2 | 2023-11-14 09:45 | 2023-11-14 14:47 | 5:02 | S/O | Due to Maintenance work of kpcl end. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Jhenaidah Ckt-1 | 2023-11-20 08:16 | 2023-11-20 15:41 | 7:25 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | PDB 330MW CCPP | 2023-11-03 09:45 | 2023-11-03 17:17 | 7:32 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | Gopaganj North CKT-04 | 2023-11-05 09:29 | 2023-11-06 20:38 | 35:09 | S/O | Sus comssing | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | khulna central - 1 | 2023-11-21 07:50 | 2023-11-21 15:39 | 7:49 | S/O | S/D from Khulna Central S/S | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | Payra -Payra PGCB Grid 400kV Line 01 | 2023-11-05 08:04 | 2023-11-05 19:07 | 11:03 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | Gopalganj Line-2 | 2023-11-11 09:39 | 2023-11-11 20:14 | 10:35 | D/W | NLDC REQUIREMENT. | 0 | 0 | No interruption
|  |  | Total : | 379:04 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Baghabari 230/132kV Grid Sub-Station | Baghabari- Ishurdi -1 | 2023-11-19 08:34 | 2023-11-19 19:39 | 11:05 | S/O | Annual Maintenance | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Baghabari- Ishurdi -1 | 2023-11-20 08:48 | 2023-11-20 16:31 | 7:43 | S/O | A/M | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Baghabari- Ishurdi-2 | 2023-11-23 08:46 | 2023-11-23 16:47 | 8:01 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Ishurdi 1 | 2023-11-02 08:38 | 2023-11-02 15:46 | 7:08 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chuadanga 132/33kV Grid Sub-Station | Jhenaidah-Chuadanga Ckt-1 | 2023-11-04 08:17 | 2023-11-04 15:04 | 6:47 | S/O | Annual Maintenance | 70 | 474.8333 | Power interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Bheramara -1 | 2023-11-01 08:40 | 2023-11-01 15:19 | 6:39 | S/O | Annual Maintanance Work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Bheramara -2 | 2023-11-06 08:22 | 2023-11-06 13:54 | 5:32 | S/O | Annual maintenance | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Bheramara -2 | 2023-11-07 08:28 | 2023-11-07 13:32 | 5:04 | S/O | maintenance work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Pabna | 2023-11-12 08:28 | 2023-11-12 16:28 | 8:00 | S/O | A/M | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Rupppur-1 | 2023-11-12 08:52 | 2023-11-12 16:54 | 8:02 | S/O | A/M | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Rupppur-2 | 2023-11-15 08:28 | 2023-11-15 16:29 | 8:01 | S/O | A/M | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Rupppur-2 | 2023-11-16 08:19 | 2023-11-16 16:19 | 8:00 | S/O | A/M | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV Baghabari 2 | 2023-11-22 09:01 | 2023-11-22 16:45 | 7:44 | S/O | A/M | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV Ghorashal 1 | 2023-11-24 07:09 | 2023-11-24 17:00 | 9:51 | S/O | Request By NLDC | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV Ghorashal 1 | 2023-11-25 07:06 | 2023-11-25 17:56 | 10:50 | S/O | annual maintanance | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV Ghorashal 1 | 2023-11-26 07:49 | 2023-11-26 15:39 | 7:50 | S/O | A/M | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV Ghorashal 2 | 2023-11-27 07:17 | 2023-11-27 16:53 | 9:36 | S/O | A/M | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV Ghorashal 2 | 2023-11-28 07:21 | 2023-11-28 18:08 | 10:47 | S/O | Annual maintenance | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV Ghorashal 2 | 2023-11-29 08:55 | 2023-11-29 17:31 | 8:36 | S/O | A/M | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | JH-1(L2) | 2023-11-11 08:05 | 2023-11-11 15:49 | 7:44 | S/O | Annual Maintanance | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | JH-1(L2) | 2023-11-12 07:53 | 2023-11-12 16:07 | 8:14 | S/O | Annual Maintanance | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | JH-2(L1) | 2023-11-14 07:52 | 2023-11-14 15:37 | 7:45 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | JH-2(L1) | 2023-11-15 08:08 | 2023-11-15 13:44 | 5:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Jhenaidah-Jhenaidah New-1,132kV Circuit-1(L4) | 2023-11-18 08:07 | 2023-11-18 13:53 | 5:46 | S/O | annual maintainance | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Jhenaidah-Jhenaidah New-1,132kV Circuit-1(L4) | 2023-11-19 08:24 | 2023-11-19 13:05 | 4:41 | S/O | Annual Maintenance-2023 | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Jhenaidah-Jhenaidah New-2,132kV Circuit-2(L3) | 2023-11-29 08:18 | 2023-11-29 14:07 | 5:49 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Jhenaidah-Jhenaidah New-3,132kV Circuit-3(L5) | 2023-11-08 08:19 | 2023-11-08 14:48 | 6:29 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah (New)-Jhenaidah (Old) Ckt-1 | 2023-11-18 08:08 | 2023-11-18 13:53 | 5:45 | S/O | annual maintenance | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah (New)-Jhenaidah (Old) Ckt-2 | 2023-11-29 08:18 | 2023-11-29 14:06 | 5:48 | S/O | Annual bay maintenance | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah (New)-Jhenaidah (Old) Ckt-3 | 2023-11-09 09:11 | 2023-11-09 13:49 | 4:38 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah (New)-Khulna (South) Ckt-1 | 2023-11-21 08:13 | 2023-11-21 15:36 | 7:23 | S/O | Annual Maintanance | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah (New)-Khulna (South) Ckt-2 | 2023-11-25 08:14 | 2023-11-25 16:05 | 7:51 | S/O | A/M works | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah (New)-Khulna (South) Ckt-2 | 2023-11-26 08:04 | 2023-11-26 16:13 | 8:09 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah2-Jashore Ckt-1 | 2023-11-11 08:06 | 2023-11-11 16:07 | 8:01 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah2-Jashore Ckt-1 | 2023-11-12 07:53 | 2023-11-12 16:07 | 8:14 | S/O | Annual maintenance | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah2-Jashore Ckt-1 | 2023-11-16 09:33 | 2023-11-16 15:10 | 5:37 | S/O | Annul Maintenance | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah2-Jashore Ckt-2 | 2023-11-14 07:53 | 2023-11-14 15:35 | 7:42 | S/O | Annual line maintenance | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah2-Jashore Ckt-2 | 2023-11-15 08:08 | 2023-11-15 13:44 | 5:36 | S/O | Annual maintenance | 0 | 0 | No interruption
Pabna 132/33kV Grid Sub-Station | Pabna-Ishwardi Line | 2023-11-11 08:23 | 2023-11-11 17:41 | 9:18 | S/O | annual maintenence | 0 | 0 | No interruption
Ruppur 132/11kV Grid Sub-Station | 132kv Ishurdi Line-1 | 2023-11-13 08:33 | 2023-11-13 15:07 | 6:34 | S/O | Annual Maintenance | 0 | 0 | No interruption
Ruppur 132/11kV Grid Sub-Station | 132kv Ishurdi Line-2 | 2023-11-15 08:26 | 2023-11-15 16:30 | 8:04 | S/O | Annual maintenances | 0 | 0 | No interruption
Ruppur 132/11kV Grid Sub-Station | 132kv Ishurdi Line-2 | 2023-11-16 08:17 | 2023-11-16 16:05 | 7:48 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | 132 KV Shahjadpur-Bghabari-1 | 2023-11-14 08:26 | 2023-11-14 15:50 | 7:24 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | 132 KV Shahjadpur-Bghabari-2 | 2023-11-27 08:28 | 2023-11-27 16:22 | 7:54 | S/O | Annual Maintenance | 0 | 0 | No interruption
|  |  | Total : | 329:06 |  | Unserved Energy: |  | 474.8333
Bogura Grid Circle :
Amnura 132/33kV Grid Sub-Station | Amnura - 100MW PPP | 2023-11-04 08:26 | 2023-11-04 16:01 | 7:35 | S/O | Annual Maintenance | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | Amnura - 50MW RPP | 2023-11-02 08:30 | 2023-11-02 15:57 | 7:27 | S/O | Annual maintenance. | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | Amnura - 50MW RPP | 2023-11-04 08:46 | 2023-11-04 15:43 | 6:57 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Rangpur 132 KV Ckt1 | 2023-11-19 08:21 | 2023-11-19 16:36 | 8:15 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Rangpur 132 KV Ckt1 | 2023-11-20 08:28 | 2023-11-20 15:55 | 7:27 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Rangpur 132 KV Ckt1 | 2023-11-21 08:38 | 2023-11-21 16:44 | 8:06 | S/O | Annual maintenance work | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Rangpur 132 KV Ckt2 | 2023-11-22 08:49 | 2023-11-22 16:50 | 8:01 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Rangpur 132 KV Ckt2 | 2023-11-23 08:20 | 2023-11-23 15:59 | 7:39 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Rangpur 132 KV Ckt2 | 2023-11-25 08:25 | 2023-11-25 16:12 | 7:47 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Saidpur 132 KV Ckt1 | 2023-11-26 08:29 | 2023-11-26 16:36 | 8:07 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Saidpur 132 KV Ckt1 | 2023-11-27 09:08 | 2023-11-27 16:15 | 7:07 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Saidpur 132 KV Ckt1 | 2023-11-28 08:49 | 2023-11-28 15:50 | 7:01 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Bogura Ckt-1 | 2023-11-05 08:34 | 2023-11-05 15:20 | 6:46 | S/O | For annual maintenance. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Bogura Ckt-1 | 2023-11-07 08:50 | 2023-11-07 15:14 | 6:24 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Bogura Ckt-2 | 2023-11-09 09:29 | 2023-11-09 15:13 | 5:44 | S/O | For annual maintenance. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-1 | 2023-11-12 08:40 | 2023-11-12 16:42 | 8:02 | S/O | Annual maintenance | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-1 | 2023-11-13 09:37 | 2023-11-13 14:26 | 4:49 | S/O | Deadline checking & CB switching Test | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-1 | 2023-11-14 10:28 | 2023-11-14 17:58 | 7:30 | S/O | For Annual Maintenance | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-2 | 2023-11-15 07:29 | 2023-11-15 17:22 | 9:53 | D/W | A/M | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-2 | 2023-11-16 07:08 | 2023-11-16 16:44 | 9:36 | D/W | A/M | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-2 | 2023-11-17 07:03 | 2023-11-17 16:19 | 9:16 | D/W | For project work | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-2 | 2023-11-18 07:22 | 2023-11-18 17:28 | 10:06 | D/W | project work related schedule shutdown | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-2 | 2023-11-19 07:12 | 2023-11-19 16:33 | 9:21 | S/O | For Annual Maintenance. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-2 | 2023-11-23 07:38 | 2023-11-23 17:27 | 9:49 | S/O | ALDC Recommendation | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-2 | 2023-11-24 07:06 | 2023-11-24 16:46 | 9:40 | S/O | According to ALDC's instruction. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-2 | 2023-11-25 07:17 | 2023-11-25 16:50 | 9:33 | S/O | According to ALDC's instructions. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-2 | 2023-11-26 07:35 | 2023-11-26 16:50 | 9:15 | D/W | Project work | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-2 | 2023-11-27 07:16 | 2023-11-27 16:53 | 9:37 | S/O | ALDC recommendation | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-2 | 2023-11-28 07:12 | 2023-11-28 17:01 | 9:49 | S/O | None | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-2 | 2023-11-29 07:07 | 2023-11-29 16:59 | 9:52 | S/O | A/M | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Naogaon 132 KV Line-1 | 2023-11-25 08:13 | 2023-11-25 16:40 | 8:27 | S/O | A/M | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Naogaon 132 KV Line-2 | 2023-11-30 08:17 | 2023-11-30 16:52 | 8:35 | S/O | A/M | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Serajganj Line-1 | 2023-11-15 07:46 | 2023-11-15 16:30 | 8:44 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Serajganj Line-1 | 2023-11-16 07:45 | 2023-11-16 16:12 | 8:27 | S/O | Annual maintenance work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Serajganj Line-1 | 2023-11-18 07:45 | 2023-11-18 16:57 | 9:12 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Serajganj Line-2 | 2023-11-19 07:43 | 2023-11-19 16:15 | 8:32 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Sherpur 132 KV Line-2 | 2023-11-06 08:23 | 2023-11-06 14:56 | 6:33 | S/O | annual maintenance | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Sherpur 132 KV Line-2 | 2023-11-08 08:29 | 2023-11-08 14:26 | 5:57 | S/O | A/M | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai Rahanpur ckt 1 | 2023-11-01 08:38 | 2023-11-01 15:02 | 6:24 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai Rahanpur ckt 1 | 2023-11-02 08:24 | 2023-11-02 20:14 | 11:50 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai Rahanpur ckt 1 | 2023-11-03 08:27 | 2023-11-03 18:36 | 10:09 | S/O | Annual maintenance | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai Rahanpur ckt 2 | 2023-11-04 08:30 | 2023-11-04 17:38 | 9:08 | S/O | Annual maintenance | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai Rahanpur ckt 2 | 2023-11-05 08:37 | 2023-11-05 17:30 | 8:53 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai Rahanpur ckt 2 | 2023-11-06 08:37 | 2023-11-06 17:04 | 8:27 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Mithapukur 132/33kV Grid Sub-Station | Confidence-1 | 2023-11-06 09:26 | 2023-11-06 16:43 | 7:17 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mithapukur 132/33kV Grid Sub-Station | Confidence-1 | 2023-11-07 09:34 | 2023-11-07 16:40 | 7:06 | S/O | Annual maintenance work | 0 | 0 | No interruption
Mithapukur 132/33kV Grid Sub-Station | Confidence-2 | 2023-11-08 10:14 | 2023-11-08 15:52 | 5:38 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Mithapukur 132/33kV Grid Sub-Station | Confidence-2 | 2023-11-09 10:15 | 2023-11-09 15:26 | 5:11 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Bog Ckt-1 | 2023-11-26 06:36 | 2023-11-26 16:58 | 10:22 | S/O | annual maintenacne. | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Bog Ckt-2 | 2023-11-28 08:15 | 2023-11-28 16:23 | 8:08 | S/O | Annual Maintenance | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Bog Ckt-2 | 2023-11-29 06:45 | 2023-11-29 16:40 | 9:55 | S/O | Annual maintenance | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Joy Ckt-1 | 2023-11-18 08:03 | 2023-11-18 16:45 | 8:42 | S/O | Annual maintenance. | 28 | 243.6 | Power interruption
Naogaon 132/33kV Grid Sub-Station | Nao-SPPP Ckt-1 | 2023-11-22 08:31 | 2023-11-22 16:38 | 8:07 | S/O | Annual Maintenance | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Nao-SPPP Ckt-1 | 2023-11-23 09:31 | 2023-11-23 16:05 | 6:34 | S/O | annual maintenance | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Rajshahi-1 | 2023-11-05 07:50 | 2023-11-05 16:30 | 8:40 | S/O | Yearly Maintenance. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Rajshahi-1 | 2023-11-06 07:48 | 2023-11-06 16:13 | 8:25 | S/O | Yearly maintenance work. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Rajshahi-1 | 2023-11-07 07:48 | 2023-11-07 16:29 | 8:41 | S/O | Yearly maintenance | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Rajshahi-2 | 2023-11-09 08:11 | 2023-11-09 16:13 | 8:02 | S/O | Yearly maintenance work. | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | Rahanpur-Chapainawabganj 132 KV Line Ckt-02 | 2023-11-04 08:30 | 2023-11-04 17:38 | 9:08 | S/O | Annual maintenance | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | Rahanpur-Chapainawabganj 132 KV Line Ckt-02 | 2023-11-05 08:36 | 2023-11-05 17:30 | 8:54 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | Rahanpur-Chapainawabganj 132 KV Line Ckt-02 | 2023-11-06 08:40 | 2023-11-06 17:05 | 8:25 | S/O | Annual maintenance | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Natore-2 | 2023-11-08 07:46 | 2023-11-08 16:26 | 8:40 | S/O | For annual maintenance work. | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Natore-2 | 2023-11-11 08:20 | 2023-11-11 17:16 | 8:56 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV PPP 50 Mw | 2023-11-13 07:33 | 2023-11-13 15:41 | 8:08 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV PPP 50 Mw | 2023-11-14 08:25 | 2023-11-14 16:23 | 7:58 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV RPP 50 Mw | 2023-11-12 08:26 | 2023-11-12 15:45 | 7:19 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Raj(new)-1 | 2023-11-15 08:17 | 2023-11-15 17:22 | 9:05 | S/O | AnnualMaintenance | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Raj(new)-1 | 2023-11-16 08:35 | 2023-11-16 17:22 | 8:47 | S/O | Annual maintenance | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Raj(new)-2 | 2023-11-18 08:29 | 2023-11-19 17:07 | 32:38 | S/O | For annual maintenance work. | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Raj(new)-2 | 2023-11-20 08:31 | 2023-11-20 16:15 | 7:44 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132 kV Rajshahi ckt-02 | 2023-11-18 08:28 | 2023-11-18 16:51 | 8:23 | S/O | Anual maintenance. | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132 kV Rajshahi ckt-02 | 2023-11-20 08:33 | 2023-11-20 16:14 | 7:41 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Teesta Solar-1 | 2023-11-02 17:10 | 2023-11-02 18:49 | 1:39 | D/W | maintenance work | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Teesta Solar-2 | 2023-11-04 17:46 | 2023-11-04 21:24 | 3:38 | S/O | Annual Maintenance works | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Baropukuria CKT-01 | 2023-11-26 08:29 | 2023-11-26 16:37 | 8:08 | S/O | QF-GMD-39 and as the instructions of ALDC, Bogura | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Baropukuria CKT-01 | 2023-11-27 09:07 | 2023-11-27 16:14 | 7:07 | S/O | Due to annual maintanance | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Baropukuria CKT-01 | 2023-11-28 08:48 | 2023-11-28 15:48 | 7:00 | S/O | Annual maintenance | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Baropukuria CKT-02 | 2023-11-29 08:45 | 2023-11-29 16:20 | 7:35 | S/O | A/M | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Baropukuria CKT-02 | 2023-11-30 08:15 | 2023-11-30 16:45 | 8:30 | S/O | A/M | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Rangpur CKT-01 | 2023-11-11 08:26 | 2023-11-11 16:55 | 8:29 | S/O | Annual Maintenance | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Rangpur CKT-01 | 2023-11-12 08:24 | 2023-11-12 16:46 | 8:22 | S/O | As the instructions of ALDC, Bogura and QF-GMD-39 | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Rangpur CKT-01 | 2023-11-13 08:20 | 2023-11-13 16:38 | 8:18 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Rangpur CKT-02 | 2023-11-14 08:14 | 2023-11-14 16:42 | 8:28 | S/O | QF-GMD-39 and instructions of ALDC Bogura | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Rangpur CKT-02 | 2023-11-15 08:22 | 2023-11-15 16:58 | 8:36 | S/O | For annual maintanance purpose. | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Rangpur CKT-02 | 2023-11-16 08:26 | 2023-11-16 16:37 | 8:11 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Baghabari Express | 2023-11-15 07:33 | 2023-11-15 17:01 | 9:28 | S/O | Due to project work. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Baghabari Express | 2023-11-16 07:03 | 2023-11-16 16:59 | 9:56 | D/W | BCRECL has taken S/D for tower erection | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Baghabari Express | 2023-11-17 07:06 | 2023-11-17 16:17 | 9:11 | D/W | BCRECL has taken S/D for tower erection | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Baghabari Express | 2023-11-18 07:04 | 2023-11-18 17:12 | 10:08 | D/W | Project work and annual maintenance. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Baghabari Express | 2023-11-19 07:13 | 2023-11-19 16:24 | 9:11 | D/W | Project work and annual maintenance. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Baghabari Express | 2023-11-23 07:18 | 2023-11-23 17:15 | 9:57 | D/W | S/D taken by BCRECL. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Baghabari Express | 2023-11-24 07:01 | 2023-11-24 16:45 | 9:44 | D/W | Due to project work. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Baghabari Express | 2023-11-25 07:17 | 2023-11-25 16:52 | 9:35 | D/W | Tower erection of 68 MW solar power plant. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Baghabari Express | 2023-11-26 07:18 | 2023-11-26 16:52 | 9:34 | D/W | Tower erection of 68 MW solar power plant. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Baghabari Express | 2023-11-27 07:15 | 2023-11-27 17:01 | 9:46 | D/W | Due to project work. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Baghabari Express | 2023-11-28 07:14 | 2023-11-28 17:00 | 9:46 | D/W | Solar Project work | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Baghabari Express | 2023-11-29 07:09 | 2023-11-29 16:57 | 9:48 | D/W | BCRECL has taken Shutdown | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-1 | 2023-11-12 08:35 | 2023-11-12 16:43 | 8:08 | S/O | Annual maintenance work | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-1 | 2023-11-13 09:39 | 2023-11-13 14:29 | 4:50 | S/O | S/D taken for annual maintenance | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-1 | 2023-11-14 10:32 | 2023-11-14 17:59 | 7:27 | S/O | Annual maintenance of sherpur grid sub station | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 2023-11-15 07:29 | 2023-11-15 17:24 | 9:55 | S/O | Due to project work. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 2023-11-16 07:09 | 2023-11-16 16:44 | 9:35 | D/W | BCRECL has taken S/D for tower erection | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 2023-11-17 07:07 | 2023-11-17 16:20 | 9:13 | D/W | BCRECL has taken S/D for tower erection | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 2023-11-18 07:18 | 2023-11-18 17:29 | 10:11 | D/W | project work . | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 2023-11-19 07:15 | 2023-11-19 16:33 | 9:18 | D/W | project work . | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 2023-11-23 07:23 | 2023-11-23 17:27 | 10:04 | D/W | S/D taken by BCRECL. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 2023-11-24 07:05 | 2023-11-24 16:47 | 9:42 | D/W | project work . | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 2023-11-25 07:12 | 2023-11-25 16:50 | 9:38 | D/W | Tower erection of 68 MW solar power plant. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 2023-11-26 07:22 | 2023-11-26 16:51 | 9:29 | D/W | Tower erection of 68 MW solar power plant. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 2023-11-27 07:17 | 2023-11-27 16:54 | 9:37 | D/W | project work . | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 2023-11-28 07:12 | 2023-11-28 17:01 | 9:49 | D/W | Solar project work | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 2023-11-29 07:06 | 2023-11-29 16:59 | 9:53 | D/W | BCRECL has taken Shutdown | 0 | 0 | No interruption
Sirajgonj 230 kV Switching Station | Bogura -02 | 2023-11-20 08:12 | 2023-11-20 15:48 | 7:36 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Sirajgonj 230 kV Switching Station | Bogura -02 | 2023-11-21 07:42 | 2023-11-21 16:04 | 8:22 | S/O | Annual Maintenance | 0 | 0 | No interruption
|  |  | Total : | 981:15 |  | Unserved Energy: |  | 243.6
Others :NIL
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 5142:37 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:November 2023
| Area | Previous Month (October' 2023) |  |  |  | Current Month (November '2023)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 26 | 13 | 89 | 128 | 9 | 13 | 225 | 247
2 | Dhaka (South) Grid Circle. | 30 | 16 | 54 | 100 | 32 | 23 | 106 | 161
3 | Chattogram Grid Circle. | 25 | 8 | 45 | 78 | 14 | 11 | 97 | 122
4 | Cumilla Grid Circle. | 14 | 3 | 46 | 63 | 16 | 11 | 123 | 150
5 | Khulna Grid Circle. | 20 | 5 | 92 | 117 | 25 | 11 | 121 | 157
6 | HVDC Grid Circle | 11 | 19 | 14 | 44 | 3 | 14 | 55 | 72
7 | Bogura Grid Circle. | 21 | 21 | 93 | 135 | 9 | 20 | 174 | 203
8 | Others | 0 | 0 |  | 0 | 1 | 0 | 0 | 1
9 | Total | 147 | 85 | 433 | 665 | 109 | 103 | 901 | 1113
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:November 2023
| Area | Previous Month (October' 2023) |  |  |  | Current Month (November '2023)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 3057.88 | 905.37 | 879.63 | 4842.88 | 70 | 436.28 | 283.27 | 789.55
2 | Dhaka (South) Grid Circle. | 626.53 | 124.75 | 225.83 | 977.11 | 138.75 | 100.2 | 175.7 | 414.65
3 | Chattogram Grid Circle. | 28.5 | 63.3 | 203.55 | 295.35 | 21.4 | 49.33 | 260.73 | 331.46
4 | Cumilla Grid Circle. | 752.21 | 0 | 894.67 | 1646.88 | 31.53 | 158.22 | 223.9 | 413.65
5 | Khulna Grid Circle. | 668.55 | 43.92 | 406.75 | 1119.22 | 997.85 | 46.75 | 291.08 | 1335.68
6 | HVDC Grid Circle | 98.62 | 283.1 | 0 | 381.72 | 0 | 149.32 | 520.68 | 670
7 | Bogura Grid Circle. | 420.22 | 759.69 | 550 | 1729.91 | 136.83 | 202.02 | 559.87 | 898.72
8 | Others | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Total | 5652.51 | 2180.13 | 3160.43 | 10993.07 | 1396.36 | 1142.12 | 2315.23 | 4853.71
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:November 2023
A) Power Interruption | [10 empty] | 2 | 1
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 6 | 6 | 12 | 3 | 1 | 8 | 462.95
2 | Dhaka (South) | 5031.6 | 5 | 2 | 7 | 3 | 3 | 4 | 271.75
3 | Chattogram | 2042 | 3 | 5 | 8 | 2 | 1 | 5 | 330.06
4 | Khulna | 2434 | 15 | 4 | 19 | 9 | 4 | 6 | 1124.7
5 | HVDC | 5954.3 | 4 | 2 | 6 | - | - | 6 | 195.17
6 | Bogura | 3145.6 | 6 | 6 | 12 | 1 |  | 11 | 646.05
7 | Cumilla | 2981 | 6 | 3 | 9 | 3 | 1 | 5 | 305.78
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 3336.46
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.95%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.97%
4 | Khulna | 99.95%
5 | HVDC | 99.98% | [6 empty] | Executive Engineer
6 | Bogura | 99.98% | [6 empty] | Information Management Division
7 | Cumilla | 99.96% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:November 2023
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 3 | - | 3 | 2 | - | 1 | 326.6
2 | Dhaka (South) | 990.29 | - | 5 | 1 | 6 | 2 | 2 | 2 | 142.9
3 | Chattogram | 917 | - | 1 | - | 1 | 1 | - |  | 1.4
4 | Khulna | 1238.4 | - | 9 | - | 9 | - | 2 | 7 | 210.9833
5 | HVDC | 1325 | - | - | 1 | 1 | - | - | 1 | 474.8333
6 | Bogura | 1803.3 | - | 1 | 1 | 2 | 1 |  | 1 | 252.67
7 | Cumilla | 1648.16 | - | 1 |  | 1 | - | - | 1 | 107.87
8 | Others | - | - | 2 | 2 | 4 | - | - | 1 | -
| Total | 10176.6215 | [7 empty] | 1517.2567
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.97%
3 | Chattogram | 99.99%
4 | Khulna | 99.96%
5 | Bheramara (HVDC) | 100%
6 | Bogura | 99.99%
7 | Cumilla | 99.97%
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:November 2023
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2023-11-01 | 22 | - | 4 | 07hr58 min | 2 | 8hr05 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:November 2023
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Kabirpur 132/33kV Grid Sub-Station | 1 | 1:48 | 63
Kishoreganj 132/33kV Grid Sub-Station | 2 | 3:50 | 7.65
Kishoreganj 132/33kV Grid Sub-Station | 1 | 2:59 | 65.6333
Sreepur 230/132/33kV Grid Sub-Station | 1 | 0:10 | 9
Tangail 132/33kV Grid Sub-Station | 2 | 0:48 | 34.4
Mirzapur 132/33kV GIS Grid Sub-Station | 2 | 0:38 | 26.6
Sreepur 230/132/33kV Grid Sub-Station | 1 | 2:30 | 300
Jamalpur 132/33kV Grid Sub-Station | 2 | 7:28 | 48.1
Joydebpur 132/33kV Grid Sub-Station | 1 | 1:30 | 37.5
Kabirpur 132/33kV Grid Sub-Station | 1 | 1:28 | 102.6667
Manikganj 132/33kV Grid Sub-Station | 2 | 2:48 | 42
Mymensingh 132/33kV Grid Sub-Station | 1 | 3:32 | 53
Hasnabad 132/33kV Grid Substation | 3 | 2:31 | 51.4
Sonargaon 132/33kV Grid Sub-Station | 2 | 1:38 | 58.4
Haripur 230/132kV Grid Sub-Station | 1 | 0:52 | 13
Keranigonj 230/132/33kV Grid Sub-Station | 1 | 0:13 | 17.55
Madanganj 132/33kV Grid Sub-Station | 2 | 2:14 | 53.6
Narshingdi 132/33kV Grid Sub-Station | 1 | 2:27 | 45
Nawabganj 132/33kV Grid Sub-Station | 1 | 3:26 | 41.2
Sonargaon 132/33kV Grid Sub-Station | 2 | 6:12 | 134.5
Dohazari 132/33kV Grid Sub-Station | 2 | 1:00 | 20
Halishahar 132/33kV Grid Sub-Station | 1 | 4:56 | 49.3333
Baroirhat 132/33kV Grid Sub-Station | 1 | 0:14 | 1.4
Baroaulia 132/33kV Grid Sub-Station | 2 | 15:44 | 171.23
Dohazari 132/33kV Grid Sub-Station | 2 | 2:14 | 67
Mirsorai 230/33kV Grid Sub-Station | 1 | 7:30 | 22.5
Brahmanbaria 132/33kV Grid Sub-Station | 2 | 0:06 | 4.47
Chauddagram 132/33kV Grid Sub-Station | 1 | 0:13 | 3.0333
Chowmuhani 132/33kV Grid Sub-Station | 1 | 1:13 | 36.5
Cumilla(N) 230/132/33kV Grid Sub-Station | 1 | 2:19 | 104.25
Ramganj 132/33kV Grid Sub-Station | 1 | 1:04 | 16
Beanibazar 132/33kV Grid Sub-Station | 1 | 0:27 | 17.1
Chowmuhani 132/33kV Grid Sub-Station | 1 | 0:14 | 8.4
Chhatak 132/33kV Grid Sub-Station | 1 | 0:51 | 1.275
Chowmuhani 132/33kV Grid Sub-Station | 1 | 2:23 | 59.5833
Kulaura 132/33kV Grid Sub-Station | 1 | 8:04 | 80.6667
Sunamganj 132/33kV Grid Sub-Station | 2 | 3:49 | 82.37
Barishal 132/33kV Grid Sub-Station | 2 | 0:14 | 6.18
Benapole 132/33kV Grid Sub-Station | 2 | 0:47 | 29.77
Bhandaria 132/33kV Grid Sub-Station | 2 | 0:16 | 0.53
Goalpara 132/33kV Grid Sub-Station | 1 | 0:36 | 17.4
Madaripur 132/33kV Grid Sub-Station | 4 | 17:30 | 750.87
Mongla 132/33kV Grid Sub-Station | 1 | 0:34 | 10.2
Narail 132/33kV Grid Sub-Station | 1 | 1:28 | 14.6667
Shariatpur 132/33kV Grid Sub-Station | 2 | 0:24 | 4
Barishal 132/33kV Grid Sub-Station | 1 | 5:35 | 16.75
Gopalganj 400/132kV Grid Sub-Station | 4 | 4:46 | 11.57
Madaripur 132/33kV Grid Sub-Station | 2 | 3:35 | 143.33
Shariatpur 132/33kV Grid Sub-Station | 2 | 1:58 | 39.33
Barishal 132/33kV Grid Sub-Station | 1 | 1:21 | 27
Bhandaria 132/33kV Grid Sub-Station | 1 | 4:07 | 45.2833
Faridpur 132/33kV Grid Sub-Station | 1 | 2:36 | 98.8
Mongla 132/33kV Grid Sub-Station | 2 | 12:00 | 120
Jhenaidah 132/33kV Grid Sub-Station | 3 | 5:14 | 146.53
Ruppur 132/11kV Grid Sub-Station | 1 | 1:07 | 2.7917
Ishurdi 132/33kV Grid Sub-Station | 2 | 4:28 | 45.85
Chuadanga 132/33kV Grid Sub-Station | 1 | 6:47 | 474.8333
Bog-Sherpur 132/33kV Grid Sub-Station | 2 | 0:52 | 32.93
Naogaon 132/33kV Grid Sub-Station | 3 | 6:57 | 167.02
Rajshahi 132/33kV Grid Sub-Station | 2 | 1:30 | 36.5
Rajshahi 132/33kV Grid Sub-Station | 1 | 3:44 | 93.3333
Chapai 132/33kV Grid Sub-Station | 2 | 1:55 | 32.17
Naogaon 132/33kV Grid Sub-Station | 1 | 1:30 | 75
Palashbari 132/33kV Grid Sub-Station | 2 | 4:05 | 122.5
Rajshahi 132/33kV Grid Sub-Station | 1 | 7:34 | 75.6667
Saidpur 132/33kV Grid Sub-Station | 1 | 2:00 | 20
Naogaon 132/33kV Grid Sub-Station | 1 | 8:42 | 243.6
Total Unserved energy : | 104 | 215:35 | 4853.7167
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:November 2023
Sl. No | name | date_time | ss_MW
1 | Aftabnagar 132/33kV Grid Sub-Station | 2023-11-02 13:00 | 34
2 | Agargaon 230/132kV Grid Sub-Station | 2023-11-01 17:00 | 92
3 | Banani 132/33kV Grid Sub-Station | 2023-11-29 12:00 | 38
4 | Bangabhaban 132/33kV Grid Sub-Station | 2023-11-29 11:00 | 16
5 | Bashundhara 132/33kV Grid Sub-Station | 2023-11-20 13:00 | 147
6 | BashundharaCement 132/33kV Sub-Station | 2023-11-15 11:00 | 11
7 | Bhulta 132/33kV Grid Sub-Station | 2023-11-22 19:00 | 242
8 | Cantonment 132/33kV GIS Grid Sub-Station | 2023-11-01 13:00 | 136
9 | Charsaidpur 132/33kV Sub-Station | 2023-11-15 | 30
10 | Dhaka University 132/33kV Grid Sub-Station | 2023-11-12 12:00 | 36
11 | Dhamrai 132/33kV Grid Sub-Station | 2023-11-08 18:00 | 118
12 | Dhanmondi 132/33kV Grid Sub-Station | 2023-11-04 13:00 | 131
13 | Fatullah 132/33kV Grid Sub-Station | 2023-11-05 12:00 | 71
14 | Ghorashal 230/132/33kV Sub-Station | 2023-11-08 14:00 | 80
15 | Gulshan 132/33kV Grid Sub-Station | 2023-11-01 13:00 | 114
16 | HaripurSBU 132/33kV Sub-Station | 2023-11-06 12:00 | 171
17 | Hasnabad 132/33kV Grid Substation | 2023-11-16 23:00 | 85
18 | Joydebpur 132/33kV Grid Sub-Station | 2023-11-04 18:00 | 170
19 | Kabirpur 132/33kV Grid Sub-Station | 2023-11-28 15:00 | 274
20 | Kallyanpur 132/33kV Grid Sub-Station | 2023-11-05 18:30 | 103
21 | Kamrangirchar 132/33kV Grid Sub-Station | 2023-11-01 13:00 | 54
22 | Kazla 132/33kV Grid Sub-Station | 2023-11-01 18:00 | 104
23 | Keranigonj 230/132/33kV Grid Sub-Station | 2023-11-05 18:00 | 82
24 | Kodda 132/33kV Grid Sub-Station | 2023-11-21 18:00 | 292
25 | Lalbag 132/33kV Grid Sub-Station | 2023-11-02 14:00 | 100
26 | Madanganj 132/33kV Grid Sub-Station | 2023-11-15 11:00 | 42
27 | Madartek 132/33kV Grid Sub-Station | 2023-11-11 19:30 | 74.29
28 | Manikganj 132/33kV Grid Sub-Station | 2023-11-15 19:00 | 95
29 | Maniknagar 132/33kV Grid Sub-Station | 2023-11-01 13:00 | 82
30 | Matuail 132/33kV Grid Sub-Station | 2023-11-09 12:00 | 74
31 | Millgate Tongi 132/33kV Grid Sub-Station | 2023-11-01 17:00 | 99
32 | Mirpur 132/33kV Grid Sub-Station | 2023-11-15 18:30 | 122
33 | Mirzapur 132/33kV GIS Grid Sub-Station | 2023-11-26 18:00 | 17.04
34 | MI_Cement 132/33kV Grid Sub-Station | 2023-11-01 15:00 | 20.2
35 | Mogbazar 132/33kV Grid Sub-Station | 2023-11-02 15:00 | 109
36 | Motijheel 132/33kV Grid Sub-Station | 2023-11-01 13:00 | 52
37 | Munshiganj 132/33kV Grid Sub-Station | 2023-11-04 21:00 | 93
38 | Narinda 132/33kV Grid Sub-Station | 2023-11-05 13:00 | 83
39 | Narshingdi 132/33kV Grid Sub-Station | 2023-11-01 21:00 | 168
40 | Nawabganj 132/33kV Grid Sub-Station | 2023-11-20 18:00 | 36.4
41 | New Tongi 132/33kV Grid Sub-Station | 2023-11-02 12:00 | 73.4
42 | Postogola 132/33kV Grid Sub-Station | 2023-11-02 13:00 | 55
43 | Purbachal 132/33kV Grid Sub-Station | 2023-11-01 18:00 | 19
44 | Rahim Steel 132/33kV Sub-Station | 2023-11-28 12:00 | 54
45 | Rajendrapur 132/33kV Grid Sub-Station | 2023-11-09 18:30 | 106
46 | Satmasjid 132/33kV Grid Sub-Station | 2023-11-01 18:30 | 105
47 | Savar 132/33kV Grid Sub-Station | 2023-11-05 12:00 | 180
48 | SevenRings 132/11kV Sub-Station | 2023-11-20 12:00 | 20.14
49 | ShahCement 132/33kV Grid Sub-Station | 2023-11-30 17:00 | 38
50 | Shitalakhya 132/33kV Grid Sub-Station | 2023-11-02 16:00 | 104
51 | Shyampur 132/33kV Grid Sub-Station | 2023-11-15 12:00 | 172
52 | Siddhirganj 132/33kV Grid Sub-Station | 2023-11-01 12:00 | 116
53 | Sonargaon 132/33kV Grid Sub-Station | 2023-11-27 07:00 | 107
54 | Sreepur 230/132/33kV Grid Sub-Station | 2023-11-15 18:00 | 66
55 | Srinagar 132/33kV Grid Sub-Station | 2023-11-01 20:00 | 37.22
56 | Tongi 230/132/33kV Grid Sub-Station | 2023-11-13 15:00 | 122
57 | Ullon 132/33kV Grid Sub-Station | 2023-11-20 19:30 | 48
58 | Uttara 132/33kV Grid Sub-Station | 2023-11-02 14:00 | 79
59 | UttaraNew 132/33kV Grid Sub-Station | 2023-11-12 13:00 | 56
60 | Zigatola 132/33kV Grid Sub-Station | 2023-11-13 12:00 | 94
61 | Agrabad 132/33kV Grid Sub-Station | 2023-11-12 14:00 | 80
62 | AKS 132/33kV Grid Sub-Station | 2023-11-18 19:00 | 12
63 | AKSML 230/33kV Grid Sub-Station | 2023-11-29 17:00 | 118.5
64 | Bakulia 132/33kV Grid Sub-Station | 2023-11-01 18:00 | 99
65 | Baroaulia 132/33kV Grid Sub-Station | 2023-11-24 | 80
66 | Baroirhat 132/33kV Grid Sub-Station | 2023-11-01 18:30 | 55
67 | BSRM 230/33kV Grid Sub-Station | 2023-11-02 17:00 | 143
68 | Chandraghona 132/33kV Grid Sub-Station | 2023-11-01 19:30 | 30
69 | Coxsbazar 132/33kV Grid Sub-Station | 2023-11-14 18:00 | 123
70 | Dohazari 132/33kV Grid Sub-Station | 2023-11-20 19:00 | 86
71 | GPH 230/33kV Grid Sub-Station | 2023-11-19 05:00 | 98
72 | Halishahar 132/33kV Grid Sub-Station | 2023-11-15 15:00 | 108
73 | Hathazari 230/132/33kV Grid Sub-Station | 2023-11-02 18:00 | 98
74 | Juldah 132/33kV Grid Sub-Station | 2023-11-13 15:00 | 28
75 | Kalurghat 132/33kV Grid Sub-Station | 2023-11-02 10:00 | 38
76 | Khagrachori 132/33kV Grid Sub-Station | 2023-11-02 18:00 | 30
77 | Khulshi 132/33kV Grid Sub-Station | 2023-11-01 19:00 | 179
78 | KSRM 132/33kV Grid Sub-Station | 2023-11-27 10:00 | 42
79 | Madunaghat 132/33kV Grid Sub-Station | 2023-11-16 07:00 | 58
80 | Matarbari 132/33kV Sub-Station | 2023-11-30 18:00 | 38
81 | Mirsorai 230/33kV Grid Sub-Station | 2023-11-04 18:30 | 5
82 | Modern Steel 132/11kV Grid Sub-Station | 2023-11-07 10:00 | 0.38
83 | Rampur 230/132/33 kV GIS Grid Sub-Station | 2023-11-20 18:30 | 31
84 | Rangamati 132/33kV Grid Sub-Station | 2023-11-02 18:00 | 16
85 | Shahmirpur 132/33kV Grid Sub-Station | 2023-11-02 18:30 | 54
86 | Shikalbaha 132/33kV Sub-Station | 2023-11-14 01:00 | 32
87 | Sholosohor 132/33kV Grid Sub-Station | 2023-11-01 18:30 | 42
88 | SSM 132/33kV Grid Sub-Station | 2023-11-18 23:00 | 16
89 | TK chemical 132kV Grid Sub-Station | 2023-11-01 20:00 | 28
90 | Ashuganj 230/132/33kV Sub-Station | 2023-11-14 | 73
91 | Brahmanbaria 132/33kV Grid Sub-Station | 2023-11-01 23:00 | 143
92 | Chandpur 132/33kV Grid Sub-Station | 2023-11-01 18:00 | 62
93 | Chauddagram 132/33kV Grid Sub-Station | 2023-11-01 19:30 | 55
94 | Chowmuhani 132/33kV Grid Sub-Station | 2023-11-02 18:00 | 202
95 | Cumilla(N) 230/132/33kV Grid Sub-Station | 2023-11-01 19:00 | 168
96 | Cumilla(S) 132/33kV Grid Sub-Station | 2023-11-01 15:00 | 158
97 | Daudkandi 132/33kV Grid Sub-Station | 2023-11-01 19:00 | 144
98 | Feni 132/33kV Grid Sub-Station | 2023-11-02 18:00 | 109
99 | Kachua 132/33kV Grid Sub-Station | 2023-11-02 19:00 | 64
100 | PHP 132/33kV Sub-Station | 2023-11-25 11:00 | 10
101 | Ramganj 132/33kV Grid Sub-Station | 2023-11-02 18:00 | 96
102 | Bhaluka 132/33kV Grid Sub-Station | 2023-11-06 18:00 | 142
103 | Jamalpur 132/33kV Grid Sub-Station | 2023-11-01 18:00 | 142
104 | Kishoreganj 132/33kV Grid Sub-Station | 2023-11-01 19:30 | 140
105 | Mymensingh 132/33kV Grid Sub-Station | 2023-11-01 18:00 | 203
106 | Netrakona 132/33kV Grid Sub-Station | 2023-11-01 18:00 | 118
107 | Sherpur 132/33kV Grid Sub-Station | 2023-11-02 18:00 | 122
108 | Tangail 132/33kV Grid Sub-Station | 2023-11-01 18:00 | 206
109 | Beanibazar 132/33kV Grid Sub-Station | 2023-11-02 18:00 | 60
110 | Chhatak 132/33kV Grid Sub-Station | 2023-11-01 18:30 | 26
111 | Fenchuganj 230/132/33kV Grid Sub-Station | 2023-11-01 18:30 | 35
112 | Kulaura 132/33kV Grid Sub-Station | 2023-11-01 18:30 | 40
113 | Shahjibazar 132/33kV Grid Sub-Station | 2023-11-01 19:00 | 102
114 | Sreemongol 132/33kV Grid Sub-Station | 2023-11-02 18:00 | 64
115 | Sunamganj 132/33kV Grid Sub-Station | 2023-11-01 21:00 | 47
116 | Sylhet (South) 132/33kV GIS Grid Sub-Station | 2023-11-05 18:00 | 20
117 | Sylhet 132/33kV Grid Sub-Station | 2023-11-02 18:00 | 135
118 | Bagerhat 132/33kV Grid Sub-Station | 2023-11-04 18:00 | 86
119 | Benapole 132/33kV Grid Sub-Station | 2023-11-01 18:00 | 52
120 | Bheramara(GK) 132/33kV Grid Sub-Station | 2023-11-01 18:00 | 52
121 | Chuadanga 132/33kV Grid Sub-Station | 2023-11-01 18:00 | 92
122 | Faridpur 132/33kV Grid Sub-Station | 2023-11-01 18:00 | 128
123 | Goalpara 132/33kV Grid Sub-Station | 2023-11-05 13:00 | 36
124 | Gollamari 132/33kV Grid Sub-Station | 2023-11-05 13:00 | 62
125 | Gopalganj 132/33kV Grid Sub-Station | 2023-11-01 18:00 | 93.2
126 | Jashore 132/33kV Grid Sub-Station | 2023-11-01 18:00 | 121
127 | Jhenaidah 132/33kV Grid Sub-Station | 2023-11-01 18:00 | 115
128 | Khulna (C) 132/33kV Grid Sub-Station | 2023-11-02 13:00 | 96
129 | Kushtia 132/33kV Grid Sub-Station | 2023-11-04 18:00 | 130
130 | Madaripur 132/33kV Grid Sub-Station | 2023-11-01 18:00 | 83
131 | Magura 132/33kV Grid Sub-Station | 2023-11-01 18:00 | 60
132 | Mongla 132/33kV Grid Sub-Station | 2023-11-21 12:00 | 38
133 | Narail 132/33kV Grid Sub-Station | 2023-11-02 18:30 | 49
134 | Noapara 132/33kV Grid Sub-Station | 2023-11-05 18:00 | 48.5
135 | Rajbari 132/33kV Grid Sub-Station | 2023-11-01 18:00 | 58
136 | Satkhira 132/33kV Grid Sub-Station | 2023-11-01 18:00 | 105
137 | Shariatpur 132/33kV Grid Sub-Station | 2023-11-01 20:00 | 63
138 | Barguna 132/33kV Grid Sub-Station | 2023-11-01 18:00 | 16
139 | Barishal 132/33kV Grid Sub-Station | 2023-11-04 18:00 | 95
140 | Barishal 230/132kV Grid Sub-Station | 2023-11-01 18:30 | 78
141 | Bhandaria 132/33kV Grid Sub-Station | 2023-11-01 18:00 | 42
142 | Borhanuddin 230/33kV Grid Sub-Station | 2023-11-01 20:00 | 48
143 | Patuakhali 132/33kV Grid Sub-Station | 2023-11-01 22:00 | 85
144 | Payra 400/132/33kV Grid Sub-Station | 2023-11-18 21:00 | 23
145 | Amnura 132/33kV Grid Sub-Station | 2023-11-04 13:00 | 50
146 | Bhangura 132/33kV Grid Sub-Station | 2023-11-02 18:00 | 28
147 | Bog-Sherpur 132/33kV Grid Sub-Station | 2023-11-10 18:00 | 54
148 | Bogura 132/33kV Grid Sub-Station | 2023-11-04 19:00 | 136
149 | Chapai 132/33kV Grid Sub-Station | 2023-11-04 20:00 | 57
150 | Ishurdi 132/33kV Grid Sub-Station | 2023-11-01 18:00 | 65
151 | Joypurhat 132/33kV Grid Sub-Station | 2023-11-02 18:00 | 46
152 | Mahasthangarh 132/33kV Grid Sub-Station | 2023-11-08 02:00 | 70
153 | Naogaon 132/33kV Grid Sub-Station | 2023-11-01 18:30 | 104
154 | Natore 132/33kV Grid Sub-Station | 2023-11-21 07:00 | 129
155 | Niamatpur 132/33kV Grid Sub-Station | 2023-11-01 14:00 | 67
156 | Pabna 132/33kV Grid Sub-Station | 2023-11-02 18:00 | 105
157 | Rajshahi 132/33kV Grid Sub-Station | 2023-11-04 19:00 | 123
158 | Rajshahi 230/132/33kV Grid Sub-Station | 2023-11-01 13:00 | 35
159 | Ruppur 132/11kV Grid Sub-Station | 2023-11-01 16:00 | 6
160 | Shahjadpur 132/33kV Grid Sub-Station | 2023-11-01 18:30 | 92
161 | Sirajganj 132/33kV Grid Sub-Station | 2023-11-01 18:30 | 96
162 | Barapukuria 230/132/33kV Grid Sub-Station | 2023-11-27 19:00 | 75
163 | Jaldhaka 132/33kV Grid Sub-Station | 2023-11-01 18:00 | 60
164 | Kurigram 132/33kV Grid Sub-Station | 2023-11-02 18:00 | 56
165 | Lalmonirhat 132/33kV Grid Sub-Station | 2023-11-01 18:00 | 41
166 | Mithapukur 132/33kV Grid Sub-Station | 2023-11-24 16:00 | 78
167 | Palashbari 132/33kV Grid Sub-Station | 2023-11-01 18:30 | 95
168 | Panchagarh 132/33kV Grid Sub-Station | 2023-11-01 18:00 | 50
169 | Purbasadipur 132/33kV Grid Sub-Station | 2023-11-28 18:00 | 101
170 | Rangpur 132/33kV Grid Sub-Station | 2023-11-01 18:30 | 119
171 | Saidpur 132/33kV Grid Sub-Station | 2023-11-16 18:00 | 91
172 | Thakurgaon 132/33kV Grid Sub-Station | 2023-11-26 18:00 | 76
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:November 2023
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 4722.82 | 2023-11-01 | 18:00
Chattogram | 1347.55 | 2023-11-02 | 18:00
Cumilla | 1193 | 2023-11-01 | 19:00
Mymensingh | 1043 | 2023-11-01 | 18:00
Sylhet | 499 | 2023-11-01 | 19:00
Khulna | 1465.2 | 2023-11-01 | 18:00
Barishal | 375 | 2023-11-01 | 18:00
Rajshahi | 1173.8 | 2023-11-01 | 18:30
Rangpur | 754 | 2023-11-01 | 18:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month:November 2023
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar 400/230/132kV Grid Sub-Station | 400 | 418 | 2023-11-17 16:00 | 367 | 2023-11-08
2 | Bhulta 400/230kV Grid Sub-Station | 400 | 422 | 2023-11-17 16:00 | 386 | 2023-11-01 14:00
3 | Bibiana 400/230kV Sub-Station | 400 | 417 | 2023-11-17 17:00 | 394 | 2023-11-01 13:00
4 | BIPTC | 400 | 410 | 2023-11-27 04:00 | 389 | 2023-11-29 09:00
5 | Gopalganj 400/132kV Grid Sub-Station | 400 | 421 | 2023-11-17 16:00 | 379 | 2023-11-02 18:00
6 | Kaliakoir 400/230/132kV Grid Sub-Station | 400 | 406 | 2023-11-17 17:00 | 364 | 2023-11-21 18:00
7 | Payra 400kV Sub-Station | 400 | 424 | 2023-11-17 16:00 | 405 | 2023-11-05 12:00
8 | Rahanpur 400/132kV Grid Sub-Station | 400 | 414 | 2023-11-11 02:00 | 393 | 2023-11-02 21:00
9 | Rampal 400/230kV Grid Sub-Station | 400 | 419 | 2023-11-17 16:00 | 384 | 2023-11-09 12:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon 230/132kV Grid Sub-Station | 230 | 249 | 2023-11-17 16:00 | 219 | 2023-11-20 12:00
2 | AKSML 230/33kV Grid Sub-Station | 230 | 237 | 2023-11-03 18:00 | 210 | 2023-11-27 10:00
3 | Baghabari 230/132kV Grid Sub-Station | 230 | 231 | 2023-11-10 03:00 | 220 | 2023-11-08 11:00
4 | Barapukuria 230/132/33kV Grid Sub-Station | 230 | 229 | 2023-11-20 17:00 | 214 | 2023-11-02 21:00
5 | Barishal 230/132kV Grid Sub-Station | 230 | 246 | 2023-11-17 16:00 | 228 | 2023-11-26 16:00
6 | Bheramara 230/132kV Grid Sub-Station | 230 | 239 | 2023-11-17 16:00 | 221 | 2023-11-15 10:00
7 | Bogura 230/132kV Grid Sub-Station | 230 | 237 | 2023-11-17 05:00 | 221 | 2023-11-02 21:00
8 | BSRM 230/33kV Grid Sub-Station | 230 | 238 | 2023-11-05 20:00 | 205 | 2023-11-27 10:00
9 | Cumilla(N) 230/132/33kV Grid Sub-Station | 230 | 243 | 2023-11-17 16:00 | 220 | 2023-11-27 10:00
10 | Fenchuganj 230/132/33kV Grid Sub-Station | 230 | 241 | 2023-11-17 16:00 | 226 | 2023-11-16 10:00
11 | Ghorashal 230/132/33kV Sub-Station | 230 | 248 | 2023-11-17 15:00 | 230 | 2023-11-06 01:00
12 | GPH 230/33kV Grid Sub-Station | 230 | 237 | 2023-11-05 18:30 | 203 | 2023-11-27 10:00
13 | Haripur 230/132kV Grid Sub-Station | 230 | 246 | 2023-11-17 15:00 | 224 | 2023-11-18 12:00
14 | Hasnabad 230/132kV Grid Sub-Station | 230 | 248 | 2023-11-17 16:00 | 221 | 2023-11-19 15:00
15 | Hathazari 230/132/33kV Grid Sub-Station | 230 | 239 | 2023-11-05 20:00 | 205 | 2023-11-27 10:00
16 | Ishurdi 230/132kV Grid Sub-Station | 230 | 238 | 2023-11-17 16:00 | 222 | 2023-11-12 11:00
17 | Jhenaidah 230/132kV Grid Sub-Station | 230 | 237 | 2023-11-17 16:00 | 215 | 2023-11-05 12:00
18 | Keranigonj 230/132/33kV Grid Sub-Station | 230 | 247 | 2023-11-17 16:00 | 219 | 2023-11-20 12:00
19 | Khulna(S) 230/132kV Grid Sub-Station | 230 | 244 | 2023-11-25 02:00 | 221 | 2023-11-09 11:00
20 | Maniknagar 230/132kV Grid Sub-Station | 230 | 246 | 2023-11-17 15:00 | 223 | 2023-11-20 12:00
21 | Meghnaghat 230/132kV Grid Sub-Station | 230 | 251 | 2023-11-17 15:00 | 230 | 2023-11-20 11:00
22 | Mirsorai 230/33kV Grid Sub-Station | 230 | 237 | 2023-11-01 20:00 | 204 | 2023-11-27 10:00
23 | Rajshahi 230/132/33kV Grid Sub-Station | 230 | 237 | 2023-11-17 16:00 | 219 | 2023-11-05 11:00
24 | Rampura 230/132kV Grid Sub-Station | 230 | 246 | 2023-11-17 15:00 | 223 | 2023-11-18 12:00
25 | Shikalbaha 230/132kV Grid Sub-Station | 230 | 237 | 2023-11-05 19:30 | 211 | 2023-11-14 11:00
26 | Shyampur 230/132kV Grid Sub-Station | 230 | 246 | 2023-11-17 15:00 | 222 | 2023-11-20 12:00
27 | Siddhirganj 230/132kV Grid Sub-Station | 230 | 247 | 2023-11-17 15:00 | 226 | 2023-11-19 15:00
28 | Sirajgonj 230 kV Switching Station | 230 | 241 | 2023-11-03 17:00 | 230 | 2023-11-05 12:00
29 | Sreepur 230/132/33kV Grid Sub-Station | 230 | 239 | 2023-11-17 16:00 | 221 | 2023-11-20 12:00
30 | Tongi 230/132/33kV Grid Sub-Station | 230 | 241 | 2023-11-17 15:00 | 215 | 2023-11-20 12:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar 132/33kV Grid Sub-Station | 132 | 142 | 2023-11-17 14:00 | 124 | 2023-11-18 11:00
2 | Agrabad 132/33kV Grid Sub-Station | 132 | 143 | 2023-11-17 16:00 | 120 | 2023-11-27 10:00
3 | AKS 132/33kV Grid Sub-Station | 132 | 134 | 2023-11-03 17:00 | 119 | 2023-11-27 10:00
4 | Amnura 132/33kV Grid Sub-Station | 132 | 142 | 2023-11-07 18:30 | 121 | 2023-11-02 18:30
5 | Ashuganj 230/132/33kV Sub-Station | 132 | 145 | 2023-11-17 15:00 | 133 | 2023-11-29 12:00
6 | Bagerhat 132/33kV Grid Sub-Station | 132 | 137 | 2023-11-07 19:00 | 122 | 2023-11-18 12:00
7 | Bakulia 132/33kV Grid Sub-Station | 132 | 142 | 2023-11-17 16:00 | 124 | 2023-11-14 10:00
8 | Banani 132/33kV Grid Sub-Station | 132 | 140 | 2023-11-03 17:00 | 122 | 2023-11-20 12:00
9 | Bangabhaban 132/33kV Grid Sub-Station | 132 | 143 | 2023-11-17 14:00 | 123 | 2023-11-29 12:00
10 | Barguna 132/33kV Grid Sub-Station | 132 | 139 | 2023-11-03 08:00 | 130 | 2023-11-22 19:30
11 | Barishal 132/33kV Grid Sub-Station | 132 | 142 | 2023-11-17 17:00 | 127 | 2023-11-11 21:00
12 | Baroaulia 132/33kV Grid Sub-Station | 132 | 142 | 2023-11-17 16:00 | 120 | 2023-11-27 10:00
13 | Baroirhat 132/33kV Grid Sub-Station | 132 | 142 | 2023-11-17 16:00 | 118 | 2023-11-27 10:00
14 | Bashundhara 132/33kV Grid Sub-Station | 132 | 143 | 2023-11-17 15:00 | 122 | 2023-11-20 12:00
15 | BashundharaCement 132/33kV Sub-Station | 132 | 142 | 2023-11-17 15:00 | 125 | 2023-11-28 11:00
16 | Beanibazar 132/33kV Grid Sub-Station | 132 | 132 | 2023-11-17 17:00 | 124 | 2023-11-01 12:00
17 | Benapole 132/33kV Grid Sub-Station | 132 | 139 | 2023-11-08 17:00 | 123 | 2023-11-15 12:00
18 | Bhaluka 132/33kV Grid Sub-Station | 132 | 136 | 2023-11-17 14:00 | 120 | 2023-11-01 14:00
19 | Bhandaria 132/33kV Grid Sub-Station | 132 | 139 | 2023-11-17 11:00 | 126 | 2023-11-01 22:00
20 | Bhangura 132/33kV Grid Sub-Station | 132 | 142 | 2023-11-11 01:00 | 130 | 2023-11-28 19:00
21 | Bheramara(GK) 132/33kV Grid Sub-Station | 132 | 138 | 2023-11-17 16:00 | 127 | 2023-11-01 12:00
22 | Bhulta 132/33kV Grid Sub-Station | 132 | 135 | 2023-11-17 15:00 | 115 | 2023-11-02 11:00
23 | Bog-Sherpur 132/33kV Grid Sub-Station | 132 | 140 | 2023-11-18 04:00 | 128 | 2023-11-01 11:00
24 | Bogura 132/33kV Grid Sub-Station | 132 | 140 | 2023-11-25 18:30 | 125 | 2023-11-03 10:00
25 | Brahmanbaria 132/33kV Grid Sub-Station | 132 | 137 | 2023-11-17 16:00 | 118 | 2023-11-01 21:00
26 | Cantonment 132/33kV GIS Grid Sub-Station | 132 | 140 | 2023-11-17 16:00 | 123 | 2023-11-19 15:00
27 | Chandpur 132/33kV Grid Sub-Station | 132 | 146 | 2023-11-17 16:00 | 115 | 2023-11-03 15:00
28 | Chandraghona 132/33kV Grid Sub-Station | 132 | 142 | 2023-11-17 16:00 | 120 | 2023-11-25 15:00
29 | Chapai 132/33kV Grid Sub-Station | 132 | 136 | 2023-11-17 05:00 | 122 | 2023-11-02 20:00
30 | Charsaidpur 132/33kV Sub-Station | 132 | 142 | 2023-11-17 15:00 | 127 | 2023-11-13 12:00
31 | Chauddagram 132/33kV Grid Sub-Station | 132 | 145 | 2023-11-17 16:00 | 122 | 2023-11-01 13:00
32 | Chhatak 132/33kV Grid Sub-Station | 132 | 134 | 2023-11-17 20:00 | 124 | 2023-11-01 13:00
33 | Chowmuhani 132/33kV Grid Sub-Station | 132 | 145 | 2023-11-17 17:00 | 117 | 2023-11-03 14:00
34 | Chuadanga 132/33kV Grid Sub-Station | 132 | 140 | 2023-11-11 06:00 | 124 | 2023-11-19 14:00
35 | Coxsbazar 132/33kV Grid Sub-Station | 132 | 137 | 2023-11-17 16:00 | 113 | 2023-11-15 12:00
36 | Cumilla(S) 132/33kV Grid Sub-Station | 132 | 144 | 2023-11-17 16:00 | 123 | 2023-11-01 15:00
37 | Daudkandi 132/33kV Grid Sub-Station | 132 | 143 | 2023-11-17 15:00 | 117 | 2023-11-01 23:00
38 | Dhaka University 132/33kV Grid Sub-Station | 132 | 143 | 2023-11-17 15:00 | 124 | 2023-11-18 11:00
39 | Dhamrai 132/33kV Grid Sub-Station | 132 | 142 | 2023-11-17 16:00 | 123 | 2023-11-20 12:00
40 | Dhanmondi 132/33kV Grid Sub-Station | 132 | 142 | 2023-11-17 15:00 | 124 | 2023-11-05 13:00
41 | Dohazari 132/33kV Grid Sub-Station | 132 | 140 | 2023-11-17 17:00 | 116 | 2023-11-14 13:00
42 | Faridpur 132/33kV Grid Sub-Station | 132 | 135 | 2023-11-17 15:00 | 125 | 2023-11-02 21:00
43 | Fatullah 132/33kV Grid Sub-Station | 132 | 144 | 2023-11-17 16:00 | 127 | 2023-11-28 12:00
44 | Feni 132/33kV Grid Sub-Station | 132 | 143 | 2023-11-17 16:00 | 120 | 2023-11-27 10:00
45 | Goalpara 132/33kV Grid Sub-Station | 132 | 140 | 2023-11-07 05:00 | 125 | 2023-11-18 11:00
46 | Gollamari 132/33kV Grid Sub-Station | 132 | 139 | 2023-11-07 19:00 | 125 | 2023-11-16 12:00
47 | Gopalganj 132/33kV Grid Sub-Station | 132 | 136 | 2023-11-07 19:00 | 124 | 2023-11-16 12:00
48 | Gulshan 132/33kV Grid Sub-Station | 132 | 142 | 2023-11-17 15:00 | 124 | 2023-11-18 12:00
49 | Halishahar 132/33kV Grid Sub-Station | 132 | 142 | 2023-11-17 16:00 | 122 | 2023-11-14 10:00
50 | HaripurSBU 132/33kV Sub-Station | 132 | 142 | 2023-11-17 15:00 | 126 | 2023-11-21 12:00
51 | Hasnabad 132/33kV Grid Substation | 132 | 142 | 2023-11-17 14:00 | 127 | 2023-11-22 12:00
52 | Ishurdi 132/33kV Grid Sub-Station | 132 | 140 | 2023-11-03 06:00 | 130 | 2023-11-05 12:00
53 | Jaldhaka 132/33kV Grid Sub-Station | 132 | 136 | 2023-11-06 16:00 | 115 | 2023-11-26 12:00
54 | Jamalpur 132/33kV Grid Sub-Station | 132 | 140 | 2023-11-06 20:00 | 116 | 2023-11-29 07:00
55 | Jashore 132/33kV Grid Sub-Station | 132 | 139 | 2023-11-08 17:00 | 124 | 2023-11-11 12:00
56 | Jhenaidah 132/33kV Grid Sub-Station | 132 | 142 | 2023-11-12 22:00 | 126 | 2023-11-18 02:00
57 | Joydebpur 132/33kV Grid Sub-Station | 132 | 145 | 2023-11-17 15:00 | 129 | 2023-11-28 12:00
58 | Joypurhat 132/33kV Grid Sub-Station | 132 | 136 | 2023-11-20 17:00 | 119 | 2023-11-29 13:00
59 | Juldah 132/33kV Grid Sub-Station | 132 | 143 | 2023-11-17 16:00 | 124 | 2023-11-14 09:00
60 | Kabirpur 132/33kV Grid Sub-Station | 132 | 140 | 2023-11-17 16:00 | 119 | 2023-11-20 12:00
61 | Kachua 132/33kV Grid Sub-Station | 132 | 145 | 2023-11-17 17:00 | 120 | 2023-11-30 11:00
62 | Kallyanpur 132/33kV Grid Sub-Station | 132 | 145 | 2023-11-17 14:00 | 125 | 2023-11-18 12:00
63 | Kalurghat 132/33kV Grid Sub-Station | 132 | 140 | 2023-11-17 17:00 | 120 | 2023-11-27 10:00
64 | Kamrangirchar 132/33kV Grid Sub-Station | 132 | 142 | 2023-11-17 15:00 | 122 | 2023-11-18 12:00
65 | Kazla 132/33kV Grid Sub-Station | 132 | 142 | 2023-11-17 07:00 | 122 | 2023-11-29 13:00
66 | Khagrachori 132/33kV Grid Sub-Station | 132 | 141 | 2023-11-17 16:00 | 123 | 2023-11-14 11:00
67 | Khulna (C) 132/33kV Grid Sub-Station | 132 | 138 | 2023-11-06 04:00 | 124 | 2023-11-18 12:00
68 | Khulshi 132/33kV Grid Sub-Station | 132 | 140 | 2023-11-17 17:00 | 120 | 2023-11-27 10:00
69 | Kishoreganj 132/33kV Grid Sub-Station | 132 | 140 | 2023-11-17 09:00 | 125 | 2023-11-01 19:30
70 | Kodda 132/33kV Grid Sub-Station | 132 | 143 | 2023-11-17 13:00 | 120 | 2023-11-20 12:00
71 | KSRM 132/33kV Grid Sub-Station | 132 | 141 | 2023-11-17 16:00 | 120 | 2023-11-27 10:00
72 | Kulaura 132/33kV Grid Sub-Station | 132 | 136 | 2023-11-17 16:00 | 127 | 2023-11-01 15:00
73 | Kurigram 132/33kV Grid Sub-Station | 132 | 136 | 2023-11-06 16:00 | 119 | 2023-11-26 12:00
74 | Kushtia 132/33kV Grid Sub-Station | 132 | 139 | 2023-11-11 01:00 | 128 | 2023-11-01 12:00
75 | Lalbag 132/33kV Grid Sub-Station | 132 | 140 | 2023-11-17 14:00 | 122 | 2023-11-18 11:00
76 | Lalmonirhat 132/33kV Grid Sub-Station | 132 | 135 | 2023-11-18 03:00 | 120 | 2023-11-26 09:00
77 | Madanganj 132/33kV Grid Sub-Station | 132 | 142 | 2023-11-17 15:00 | 125 | 2023-11-28 11:00
78 | Madaripur 132/33kV Grid Sub-Station | 132 | 138 | 2023-11-17 18:00 | 119 | 2023-11-12 13:00
79 | Madartek 132/33kV Grid Sub-Station | 132 | 141 | 2023-11-17 14:00 | 123 | 2023-11-20 12:00
80 | Madunaghat 132/33kV Grid Sub-Station | 132 | 141 | 2023-11-17 16:00 | 120 | 2023-11-27 10:00
81 | Magura 132/33kV Grid Sub-Station | 132 | 141 | 2023-11-07 03:00 | 120 | 2023-11-18 11:00
82 | Mahasthangarh 132/33kV Grid Sub-Station | 132 | 138 | 2023-11-17 05:00 | 126 | 2023-11-02 21:00
83 | Manikganj 132/33kV Grid Sub-Station | 132 | 138 | 2023-11-17 16:00 | 119 | 2023-11-14 09:00
84 | Maniknagar 132/33kV Grid Sub-Station | 132 | 143 | 2023-11-17 14:00 | 123 | 2023-11-29 12:00
85 | Matarbari 132/33kV Sub-Station | 132 | 140 | 2023-11-17 16:00 | 113 | 2023-11-14 11:00
86 | Matuail 132/33kV Grid Sub-Station | 132 | 142.3 | 2023-11-17 14:00 | 126.2 | 2023-11-19 09:00
87 | Millgate Tongi 132/33kV Grid Sub-Station | 132 | 140 | 2023-11-03 17:00 | 122 | 2023-11-20 12:00
88 | Mirpur 132/33kV Grid Sub-Station | 132 | 142 | 2023-11-17 14:00 | 122 | 2023-11-18 12:00
89 | Mirzapur 132/33kV GIS Grid Sub-Station | 132 | 142 | 2023-11-17 16:00 | 124 | 2023-11-19 15:00
90 | Mithapukur 132/33kV Grid Sub-Station | 132 | 138 | 2023-11-07 19:00 | 113 | 2023-11-12 23:00
91 | MI_Cement 132/33kV Grid Sub-Station | 132 | 142.5 | 2023-11-17 16:00 | 126 | 2023-11-30 11:00
92 | Modern Steel 132/11kV Grid Sub-Station | 132 | 139 | 2023-11-17 17:00 | 122 | 2023-11-27 10:00
93 | Mogbazar 132/33kV Grid Sub-Station | 132 | 143 | 2023-11-17 15:00 | 123 | 2023-11-19 15:00
94 | Mongla 132/33kV Grid Sub-Station | 132 | 138 | 2023-11-07 19:00 | 121 | 2023-11-19 14:00
95 | Motijheel 132/33kV Grid Sub-Station | 132 | 143 | 2023-11-17 14:00 | 123 | 2023-11-29 12:00
96 | Munshiganj 132/33kV Grid Sub-Station | 132 | 142 | 2023-11-17 15:00 | 125 | 2023-11-21 16:00
97 | Mymensingh 132/33kV Grid Sub-Station | 132 | 138 | 2023-11-04 20:00 | 117 | 2023-11-25 17:00
98 | Naogaon 132/33kV Grid Sub-Station | 132 | 136 | 2023-11-10 06:00 | 121 | 2023-11-26 13:00
99 | Narail 132/33kV Grid Sub-Station | 132 | 141 | 2023-11-07 03:00 | 127 | 2023-11-01 14:00
100 | Narshingdi 132/33kV Grid Sub-Station | 132 | 136 | 2023-11-17 14:00 | 120 | 2023-11-01 15:00
101 | Natore 132/33kV Grid Sub-Station | 132 | 138 | 2023-11-05 18:30 | 128 | 2023-11-01 12:00
102 | Nawabganj 132/33kV Grid Sub-Station | 132 | 141 | 2023-11-17 14:00 | 123 | 2023-11-18 11:00
103 | Netrakona 132/33kV Grid Sub-Station | 132 | 136 | 2023-11-04 20:00 | 124 | 2023-11-01 22:00
104 | New Tongi 132/33kV Grid Sub-Station | 132 | 142 | 2023-11-03 17:00 | 123 | 2023-11-20 12:00
105 | Niamatpur 132/33kV Grid Sub-Station | 132 | 138 | 2023-11-21 06:00 | 118 | 2023-11-26 13:00
106 | Noapara 132/33kV Grid Sub-Station | 132 | 139 | 2023-11-08 17:00 | 124 | 2023-11-15 12:00
107 | Pabna 132/33kV Grid Sub-Station | 132 | 140 | 2023-11-17 16:00 | 126 | 2023-11-12 12:00
108 | Palashbari 132/33kV Grid Sub-Station | 132 | 137 | 2023-11-17 06:00 | 123 | 2023-11-26 13:00
109 | Panchagarh 132/33kV Grid Sub-Station | 132 | 137 | 2023-11-18 21:00 | 113 | 2023-11-26 11:00
110 | Patuakhali 132/33kV Grid Sub-Station | 132 | 140 | 2023-11-06 16:00 | 130 | 2023-11-09 12:00
111 | PHP 132/33kV Sub-Station | 132 | 143 | 2023-11-17 16:00 | 119 | 2023-11-14 11:00
112 | Postogola 132/33kV Grid Sub-Station | 132 | 145 | 2023-11-17 16:00 | 128 | 2023-11-16 12:00
113 | Purbachal 132/33kV Grid Sub-Station | 132 | 143 | 2023-11-17 14:00 | 123 | 2023-11-18 12:00
114 | Purbasadipur 132/33kV Grid Sub-Station | 132 | 136 | 2023-11-01 14:00 | 114 | 2023-11-26 13:00
115 | Rahim Steel 132/33kV Sub-Station | 132 | 142 | 2023-11-17 16:00 | 126 | 2023-11-21 12:00
116 | Rajbari 132/33kV Grid Sub-Station | 132 | 138 | 2023-11-10 21:00 | 125 | 2023-11-01 11:00
117 | Rajendrapur 132/33kV Grid Sub-Station | 132 | 139 | 2023-11-17 16:00 | 118 | 2023-11-26 13:00
118 | Rajshahi 132/33kV Grid Sub-Station | 132 | 139 | 2023-11-09 18:00 | 127 | 2023-11-05 12:00
119 | Ramganj 132/33kV Grid Sub-Station | 132 | 142 | 2023-11-17 16:00 | 114 | 2023-11-03 15:00
120 | Rangamati 132/33kV Grid Sub-Station | 132 | 142 | 2023-11-17 16:00 | 121 | 2023-11-27 10:00
121 | Rangpur 132/33kV Grid Sub-Station | 132 | 138 | 2023-11-18 15:00 | 120 | 2023-11-26 12:00
122 | Ruppur 132/11kV Grid Sub-Station | 132 | 141 | 2023-11-17 15:00 | 131 | 2023-11-02 21:00
123 | Saidpur 132/33kV Grid Sub-Station | 132 | 137 | 2023-11-04 06:00 | 117 | 2023-11-26 12:00
124 | Satkhira 132/33kV Grid Sub-Station | 132 | 137 | 2023-11-07 04:00 | 120 | 2023-11-17 23:00
125 | Satmasjid 132/33kV Grid Sub-Station | 132 | 141 | 2023-11-17 16:00 | 123 | 2023-11-19 15:00
126 | Savar 132/33kV Grid Sub-Station | 132 | 142 | 2023-11-11 19:30 | 121 | 2023-11-18 12:00
127 | SevenRings 132/11kV Sub-Station | 132 | 147 | 2023-11-17 15:00 | 132 | 2023-11-20 12:00
128 | ShahCement 132/33kV Grid Sub-Station | 132 | 143 | 2023-11-17 16:00 | 127 | 2023-11-13 12:00
129 | Shahjadpur 132/33kV Grid Sub-Station | 132 | 145 | 2023-11-13 04:00 | 133 | 2023-11-01 12:00
130 | Shahjibazar 132/33kV Grid Sub-Station | 132 | 135 | 2023-11-17 18:30 | 119 | 2023-11-01 21:00
131 | Shahmirpur 132/33kV Grid Sub-Station | 132 | 141 | 2023-11-17 16:00 | 121 | 2023-11-27 10:00
132 | Shariatpur 132/33kV Grid Sub-Station | 132 | 136 | 2023-11-17 16:00 | 124 | 2023-11-09 12:00
133 | Sherpur 132/33kV Grid Sub-Station | 132 | 138 | 2023-11-04 20:00 | 114 | 2023-11-29 07:00
134 | Shitalakhya 132/33kV Grid Sub-Station | 132 | 142.5 | 2023-11-17 16:00 | 126 | 2023-11-30 11:00
135 | Sholosohor 132/33kV Grid Sub-Station | 132 | 142 | 2023-11-17 16:00 | 120 | 2023-11-27 10:00
136 | Shyampur 132/33kV Grid Sub-Station | 132 | 141 | 2023-11-17 15:00 | 125 | 2023-11-11 22:00
137 | Siddhirganj 132/33kV Grid Sub-Station | 132 | 142 | 2023-11-17 15:00 | 127 | 2023-11-09 12:00
138 | Sirajganj 132/33kV Grid Sub-Station | 132 | 140 | 2023-11-17 02:00 | 128 | 2023-11-01 11:00
139 | Sonargaon 132/33kV Grid Sub-Station | 132 | 143 | 2023-11-17 16:00 | 124 | 2023-11-08 12:00
140 | Sreemongol 132/33kV Grid Sub-Station | 132 | 135 | 2023-11-17 15:00 | 122 | 2023-11-03
141 | Srinagar 132/33kV Grid Sub-Station | 132 | 141 | 2023-11-17 14:00 | 124 | 2023-11-20 12:00
142 | SSM 132/33kV Grid Sub-Station | 132 | 145 | 2023-11-17 16:00 | 128 | 2023-11-14 10:00
143 | Sunamganj 132/33kV Grid Sub-Station | 132 | 132 | 2023-11-17 18:30 | 121 | 2023-11-01 14:00
144 | Sylhet (South) 132/33kV GIS Grid Sub-Station | 132 | 133 | 2023-11-17 15:00 | 126 | 2023-11-01 12:00
145 | Sylhet 132/33kV Grid Sub-Station | 132 | 132 | 2023-11-17 16:00 | 127 | 2023-11-01
146 | Tangail 132/33kV Grid Sub-Station | 132 | 140 | 2023-11-17 16:00 | 124 | 2023-11-13 12:00
147 | Thakurgaon 132/33kV Grid Sub-Station | 132 | 139 | 2023-11-04 18:30 | 114 | 2023-11-17 18:00
148 | TK chemical 132kV Grid Sub-Station | 132 | 140 | 2023-11-17 17:00 | 125 | 2023-11-13 11:00
149 | Ullon 132/33kV Grid Sub-Station | 132 | 142 | 2023-11-17 15:00 | 124 | 2023-11-18 12:00
150 | Uttara 132/33kV Grid Sub-Station | 132 | 141 | 2023-11-17 16:00 | 121 | 2023-11-20 12:00
151 | UttaraNew 132/33kV Grid Sub-Station | 132 | 143 | 2023-11-17 14:00 | 121 | 2023-11-20 12:00
152 | Zigatola 132/33kV Grid Sub-Station | 132 | 140 | 2023-11-17 15:00 | 124 | 2023-11-18 11:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:November 2023
substation | transformer | voltage_level | mw | mva | date_time
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 | 400/230 | 460 | 474.1571 | 2023-11-01 18:30
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 | 400/230 | 460 | 474.1571 | 2023-11-01 18:30
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | -269 | 315.5725 | 2023-11-16 12:00
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | -269 | 315.5725 | 2023-11-16 12:00
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | -243 | 244.4954 | 2023-11-22 12:00
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | -221 | 221.1108 | 2023-11-08 14:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 293 | 297.7549 | 2023-11-18 11:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 123 | 343.7586 | 2023-11-25 07:00
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | -269.41 | 271.3921 | 2023-11-27 18:30
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | -266.86 | 268.6707 | 2023-11-27 18:30
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 321 | 328.7583 | 2023-11-19 15:00
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | -179 | 179.4714 | 2023-11-26 18:00
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | -179 | 179.4714 | 2023-11-26 18:00
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | -179 | 179.4714 | 2023-11-26 18:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 300 | 304.1381 | 2023-11-22 07:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 300 | 304.1381 | 2023-11-22 07:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | -81 | 81.1542 | 2023-11-07 21:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | -107 | 108.6738 | 2023-11-05 19:00
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 404 | 417.4218 | 2023-11-16 08:00
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 37 | 103.8171 | 2023-11-22 06:00
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
substation | transformer | voltage_level | mw | mva | date_time
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 180 | 181.1077 | 2023-11-19 07:00
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 180 | 181.1077 | 2023-11-19 07:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 202 | 212.5088 | 2023-11-19 12:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 209 | 231.6916 | 2023-11-15 10:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 218 | 228.6591 | 2023-11-15 10:00
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 120 | 144.2221 | 2023-11-01 19:00
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 160 | 188.6796 | 2023-11-16 01:00
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 119 | 130.269 | 2023-11-05 15:00
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 89 | 97.5756 | 2023-11-05 15:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 157 | 162.2652 | 2023-11-10 19:30
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 202 | 230.9719 | 2023-11-14 13:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 183 | 191.3766 | 2023-11-11 18:00
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 165 | 165.4358 | 2023-11-29 11:00
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 165 | 165.4358 | 2023-11-29 11:00
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | -80 | 113.1371 | 2023-11-01 18:30
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | -83 | 103.6002 | 2023-11-12 19:00
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 188 | 190.3786 | 2023-11-02 21:00
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 138 | 195.1615 | 2023-11-05 16:00
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 160 | 256.9066 | 2023-11-28 17:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-01 | 230/132 | 200 | 205 | 2023-11-06 14:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-02 | 230/132 | 190 | 198.6555 | 2023-11-10 19:00
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 187 | 206.2474 | 2023-11-02 18:00
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 100 | 100 | 2023-11-28 12:00
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 100 | 100 | 2023-11-28 12:00
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 175 | 188.1117 | 2023-11-16 11:00
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 83 | 95.8801 | 2023-11-19 06:00
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 175 | 188.1117 | 2023-11-16 11:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 84 | 118.7939 | 2023-11-11 17:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 108 | 115.8792 | 2023-11-11 12:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 60 | 105.6835 | 2023-11-21
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 110 | 111.463 | 2023-11-21 18:30
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 110 | 111.463 | 2023-11-21 18:30
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 110 | 111.463 | 2023-11-21 18:30
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 110 | 111.463 | 2023-11-21 18:30
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 100 | 129.9577 | 2023-11-19 18:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 100 | 129.9577 | 2023-11-19 18:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 79 | 112.4322 | 2023-11-25 18:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | -174 | 197.7675 | 2023-11-01 18:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | -174 | 197.7675 | 2023-11-01 18:00
Kaliakoir 400/230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 56 | 165.7468 | 2023-11-10 14:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 156 | 164.4384 | 2023-11-01 19:30
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 0 | 0 | 2023-11-01
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 156 | 164.4384 | 2023-11-01 19:30
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | -108 | 111.0856 | 2023-11-01 19:00
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | -108 | 111.0856 | 2023-11-01 19:00
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | -139 | 142.2006 | 2023-11-01 19:00
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 82 | 266.9082 | 2023-11-22
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 157 | 172.3079 | 2023-11-01 13:00
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | -96 | 96.2549 | 2023-11-11 07:00
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | -96 | 96.2549 | 2023-11-11 07:00
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 1 | 10.0499 | 2023-11-28 18:00
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 1 | 1 | 2023-11-06 06:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 01 | 230/132 | 187 | 206.2474 | 2023-11-18 12:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 | 230/132 | 295 | 303.898 | 2023-11-28 13:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 | 230/132 | 192 | 197.9091 | 2023-11-02 13:00
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 234 | 255.6658 | 2023-11-15 18:30
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 234 | 255.6658 | 2023-11-15 18:30
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 133 | 214.2732 | 2023-11-09 09:00
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 212 | 238.8389 | 2023-11-11 12:00
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 157 | 185.6071 | 2023-11-13
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 236 | 243.2632 | 2023-11-02 04:00
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 162 | 165.9518 | 2023-11-01 18:00
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 231 | 231.1385 | 2023-11-03 02:00
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 205 | 206.4001 | 2023-11-20 18:30
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 205 | 206.4001 | 2023-11-20 18:30
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 205 | 206.4001 | 2023-11-20 18:30
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-37
|  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month: November 2023 | [6 empty] | (For Evening Peak) | [7 empty] | Month: November 2023 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2023-11-01 | 12524 | 12570 | 44 | 19:00 | 0 | 0 | 0 | 0 | 16 | 10 | 18 | 0 | 0 | - | 2023-11-01 | 10963 | 10963 | 64 | 12:00 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | -
2023-11-02 | 12608 | 12650 | 40 | 18:00 | 0 | 0 | 0 | 0 | 30 | 0 | 10 | 0 | 0 | - | 2023-11-02 | 11209 | 11209 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-11-03 | 11014 | 11040 | 25 | 19:00 | 0 | 0 | 0 | 0 | 20 | 0 | 5 | 0 | 0 | - | 2023-11-03 | 9790 | 9790 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-11-04 | 12247 | 12270 | 22 | 18:00 | 0 | 0 | 0 | 0 | 12 | 0 | 10 | 0 | 0 | - | 2023-11-04 | 10302 | 10302 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-11-05 | 12197 | 12197 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-11-05 | 10908 | 10908 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-11-06 | 11725 | 11741 | 15 | 21:00 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | - | 2023-11-06 | 10465 | 10465 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-11-07 | 11253 | 11253 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-11-07 | 10318 | 10339 | 20 | 12:00 | 0 | 15 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | -
2023-11-08 | 11315 | 11315 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-11-08 | 9911 | 10250 | 324 | 12:00 | 102 | 52 | 0 | 0 | 62 | 52 | 56 | 0 | 0 | -
2023-11-09 | 11740 | 11740 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-11-09 | 10048 | 10048 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-11-10 | 9556 | 9556 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-11-10 | 8735 | 8735 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-11-11 | 11207 | 11207 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-11-11 | 9414 | 9414 | 0 | 13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-11-12 | 11680 | 11680 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-11-12 | 10201 | 10201 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-11-13 | 11553 | 11553 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-11-13 | 10157 | 10157 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-11-14 | 11657 | 11657 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-11-14 | 10298 | 10298 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-11-15 | 11892 | 11892 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-11-15 | 10345 | 10363 | 17 | 12:00 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-11-16 | 11088 | 11088 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-11-16 | 9805 | 9805 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-11-17 | 6897 | 6897 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-11-17 | 7098 | 7098 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-11-18 | 10596 | 10596 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-11-18 | 8588 | 8588 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-11-19 | 11033 | 11033 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-11-19 | 9557 | 9557 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-11-20 | 11253 | 11253 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-11-20 | 9710 | 9737 | 26 | 12:00 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-11-21 | 11034 | 11034 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-11-21 | 9707 | 9707 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-11-22 | 10696 | 10696 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-11-22 | 9436 | 9436 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-11-23 | 10409 | 10409 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-11-23 | 9340 | 9340 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-11-24 | 9061 | 9061 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-11-24 | 8215 | 8215 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-11-25 | 10583 | 10583 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-11-25 | 8140 | 8140 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-11-26 | 10721 | 10721 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-11-26 | 9325 | 9325 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-11-27 | 10831 | 10831 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-11-27 | 9553 | 9553 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-11-28 | 10847 | 10847 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-11-28 | 9651 | 9651 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-11-29 | 10786 | 10786 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2023-11-29 | 9568 | 9615 | 45 | 12:00 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023-11-30 | 10725 | 10725 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2023-11-30 | 9608 | 9608 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15456
| Max. L/S | - | 1537 | - | [10 empty] | Max. L/S | - |  | 1638
| Min. L/S | - | 54 | - | [10 empty] | Min. L/S | - |  | 0
| No. of Days | - | 31 | - | [10 empty] | No. of Days | - | 31
| Average L/S |  | 21566 | [11 empty] | Average L/S |  | 19669
|  | - | - | - | [11 empty] | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:November 2023
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 12608 | 2023-11-02 | 18:00
2 | Maximum Day Peak Genaration | MW | 11209 | 2023-11-02 | 12:00
3 | Maximum Evening Peak Demand | MW | 12650 | 2023-11-30 | 18:00
4 | Minimum Generation | MW | 5719 | 2023-11-18 | 6:00
5 | Average of the daily evening peak Genaration | MW | 11024.2667 | - | -
6 | Average of the daily day peak Genaration | MW | 9678.8333 | - | -
7 | Maximum load shed | MW | 44 | 2023-11-01 | 19:00
8 | Minimum load shed | MW | 0 | 2023-11-05 | 19:00
9 | Total nos. of load shed days | Day | 5 | - | -
10 | Average load shed ( Avg. of the 30 days in the month) | MW/Day | 4.8667 | - | -
11 | Total Generation | MkWh | 6783.8637 | - | -
12 | Total Generation by BPDB | MkWh | 1832.996 | % of total Gen. | 27.02%
13 | Total Generation by IPP | MkWh | 1571.2114 | '' | 23.16%
14 | A) Total Generation by Generation Companies | MkWh | 1885.5707 | '' | 27.79%
| B) Total Generation by REB | MkWh | 102.6847 | " | 1.514%
| C) Total Generation by RENTAL | MkWh | 101.6965 | " | 1.499%
| D) Total Imported from India (BIPTC) | MkWh | 540.9076 | " | 7.973%
| E) Total Imported from Tripura, India (A.C) | MkWh | 748.7967 | " | 11.04%
15 | Fuel wise Generation.
| A) Gas | MkWh | 3301.4949 | % of total Gen. | 48.68%
| B) Oil | MkWh | 479.6 | '' | 7.072%
| C) Hydro | MkWh | 81.581 | '' | 1.203%
| D) Solar | MkWh | 70.8296 | '' | 1.044%
| E) Coal | MkWh | 2227.5458 | '' | 32.85%
| F) BIPTC (Import from India) | MkWh | 540.9076 | '' | 7.976%
| G) A.C (Import from Tripura, India) | MkWh | 79.7285 | '' | 1.176%
| H) Wind |  | 2.1667 |  | 0.06222%
16 | Maximun of the daily total Generation . | MkWh | 263.483 | 2023-11-02
17 | Monthly Load factor | % | 70.0491 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 26931.5229 | - | -
| A) Gas | M.Taka | 3376.6508 | - | -
| B) Liquid fuel | M.Taka | 6002.9592 | - | -
| C) Coal | M.Taka | 14411.0864 | - | -
| D) BIPTC (Import from India) | M.Taka | 2559.0056 | - | -
| E) Tripura(Import from India) | M.Taka | 581.8209 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1077.6094 | 2023-11-01
| A) Gas | M.Taka | 126.8745 | 2023-11-01
| B) Liquid fuel | M.Taka | 366.8724 | 2023-11-01
| C) Coal | M.Taka | 631.8879 | 2023-11-21
| D) BIPTC (Import from India) | M.Taka | 101.3348 | 2023-11-05
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 3.9699
| B) Excluding Hydro & Solar | Taka/kWhR | 4.0625
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 106.1 | 30/11/2023 | 06:00
b) | Actual | FT (MSL) | 98.1 | 30/11/2023 | 6:00
22 | Peak Genaration of November 2022 | MW | 11816 | 2022-11-02 | 19:30
23 | Peak Demand of November 2022 | MW | 12350 | 2022-11-30 | 19:30
24 | Maximum peak Generation recorded upto 30/11/2023 | MW | 15648 | 19/04/2023 | 21:00
25 | Maximum peak Demand recorded upto 30/11/2023 | MW | 16096 | 19/04/2023 | 21:00
26 | Maximum load shed recorded upto 30/11/2023 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## FGMO
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month:November 2023
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
1 | Bibiyana-III 400 MW CCPP | BPDB | 400 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220
6 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
7 | Meghnaghat CCPP(Summit) | IPP | 335
8 | Ashuganj 225 MW CCPP | APSCL | 221
9 | Ashuganj 450 MW CCPP(North) | APSCL | 361
10 | Ashuganj 450 MW CCPP(South) | APSCL | 360
11 | Ashuganj 420 MW CCPP(East) | APSCL | 400
12 | Ashuganj 55 MW PP (Precision) | QRPP | 55
13 | Bheramara 410 MW CCPP | NWPGCL | 410
14 | Haripur 412 MW CCPP | EGCB | 412
15 | Fenchugonj CCPP Phase-1 | BPDB | 97
16 | Fenchugonj CCPP Phase-2 | BPDB | 104
17 | Siddhirganj 2x120 MW GTPP | EGCB | 210
18 | Shikalbaha 225 MW CCPP | BPDB | 225
19 | Shikalbaha Peaking GT | BPDB | 150
20 | Shahjibazar 330 MW CCPP | BPDB | 330
21 | Chandpur 150 MW CCPP | BPDB | 163
22 | Bhola 225 MW CCPP | BPDB | 194
23 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
24 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
25 | Siddhirganj 335 MW CCPP | EGCB | 335
26 | Bibiyana-III 400 MW CCPP | BPDB | 400
27 | Sylhet 225 MW CCPP | BPDB | 231
28 | RPCL 210 MW CCPP | IPP | 210
29 | Khulna 225 MW CCPP | NWPGCL | 230
30 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
31 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
32 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
33 | Bibiyana South 400 MW CCPP | BPDB | 383
34 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
35 | Shajibazar 100 MW PP | BPDB | 100
36 | Payra 1320 MW Unit-1 | BCPCL | 622
37 | Kushiara 163 MW CCPP (KP) | IPP | 163
38 | Haripur 360MW CCPP(HPL) | IPP | 360
39 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450
due to gas shortage

## FGMO Weekly
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status |  |  |  |  | SR at 50 Hz (MW)
SL | Plant Name | Owner | Installed capacity | Capability Status of Last Week | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
(MW)
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | Capable | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70 | Capable
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | Capable |  | 60
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220 | Capable
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220 | Capable
6 | Meghnaghat CCPP(Summit) | IPP | 335 | Capable | [5 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
7 | Ashuganj 450 MW CCPP(North) | APSCL | 360 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
8 | Ashuganj 225 MW CCPP | APSCL | 221 | Capable | [5 empty] | 20 | 20 | 20 | 20 | 20 | 20
9 | Bheramara 410 MW CCPP | NWPGCL | 410 | Capable
10 | Haripur 412 MW CCPP | EGCB | 412 | Capable
11 | Fenchugonj CCPP Phase-1 | BPDB | 97 | Capable | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
12 | Chandpur 150 MW CCPP | BPDB | 163 | Capable
13 | Siddhirganj 2x120 MW GTPP | EGCB | 210 | Capable
14 | Shikalbaha 225 MW CCPP | BPDB | 225 | Capable
15 | Shikalbaha Peaking GT | BPDB | 150 | Capable
16 | Shahjibazar 330 MW CCPP | BPDB | 330 | Capable
17 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | Capable | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
18 | Fenchugonj CCPP Phase-2 | BPDB | 104 | Capable | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
19 | Bhola 225 MW CCPP | BPDB | 194 | Capable
20 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365 | Capable
21 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 | Capable
22 | Siddhirganj 335 MW CCPP | EGCB | 335 | Capable but not tested recently
23 | Bibiyana-III 400 MW CCPP | BPDB | 400 | Capable | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
24 | Sylhet 225 MW CCPP | BPDB | 231 | Capable
25 | RPCL 210 MW CCPP | IPP | 210 | Capable but not tested recently
26 | Khulna 225 MW CCPP | NWPGCL | 230 | Capable but not tested recently
27 | a) Baghabari 71 MW GTPP | BPDB | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | 100 | Not Capable but feasible
28 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50 | Not Capable but feasible
29 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410 | Not Capable but feasible
30 | Bibiyana South 400 MW CCPP | BPDB | 383 | Capable
31 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274 | Not Capable but feasible
32 | Shajibazar 100 MW PP | BPDB | 100 | Not Capable but feasible
33 | Payra 1320 MW Unit-1 | BCPCL | 622 | Capable
34 | Kushiara 163 MW CCPP (KP) | IPP | 163 | Not Capable but feasible
35 | Bhola Nutan Bidyut | IPP | 220 | Capable
36 | Haripur 360MW CCPP(HPL) | IPP | 360 | Not Capable but feasible
37 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450 | Not Capable but feasible
Total Spinning Reserve |  |  |  |  | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO |  |  |  |  | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list |  |  |  |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list |  |  |  |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable |  |  |  |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently |  |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible |  |  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD