## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2024-01-07 | Sunday
|  | Date (day): | 2024-01-07 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10099.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12011 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-01-06 | 2024-01-07 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 67 | 73 | 70 | 72 | 36 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 385 | 333 | 300 | 350 | 62 |  | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 360 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 85 | 85 |  | 17 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 5 | 15 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 35 | 40 | 35 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 0 | 90 | 90 |  | 12 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 0 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 115 | 98 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 0 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 18 | 40 | 40 | 40 |  | 40 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 25 | 17 | 25 |  | 8 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 21 | 24 | 24 |  | 9 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 17 | 8 | 17 | 35 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 45 | 0 | 80 | 130 | 170 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 43 | 17 | 45 | 104 |  | Fuel shortage
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 105 | 17 | 105
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 42 | 68 | 0 | 72 | 32 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 35 | 17 | 35 | 127 |  | Fuel shortage
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 26 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 306 | 299 | 300 | 300
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 5763 | 5422 | 1739 | 1781 | 2046 | 2428 | 1792 | 1126
38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
39 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 17 | 8 | 17 | 8 |  | Fuel shortage
40 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 19 | 6 | 20 | 30 |  | Fuel shortage
42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 81 | 81 | 81 | 81 | 149 |  | Low water lavel
43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 33 | 65 | 100 | 125 | 100 | 75 | ST Under maint
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 17 | 17 | 88 |  | Fuel shortage
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 32 | 0 | 32 | 70 | 28 |  | Fuel shortage
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 34 | 17 | 51 | 51 | 51 |  | Fuel shortage
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 45 | 55 |  | Fuel shortage
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 12 | 80 | 20 |  | Fuel shortage
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 | 4 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 16 | 30 | 20 | 30
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 32 | 0 | 33 | 75 |  | Fuel shortage
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 80 | 115 | 150 | 200 | 100 |  | Fuel shortage
54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 0 | 17 | 17 | 37 |  | Fuel shortage
55 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 17 | 17 | 93 |  | Fuel shortage
56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 12 | 50 | 50 |  | Fuel shortage
57 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 17 | 99 |  | Fuel shortage
58 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 35 | 17 | 17 | 17 | 146 |  | Fuel shortage
59 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 270 | 390 | 300 | 420 | 804 |  | Coal Shortage.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 1 | 9 | 10 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 311 | 310 | 312 | 312 |  |  | On test.
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 3829 | 3769 | 1041 | 1195 | 1222 | 1647 | 2117 | 405
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 76 | 71 | 96 | 100 | 121 |  | Gas shortage
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 280 | 300 | 300 |  |  | FGMO
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 150 | 150 | 280 | 280 | 80 |  | Gas shortage
63 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 | 400 |  | Gas shortage
64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 45 | 48 | 38 | 48
65 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 0 | 9 | 20 | 15 | 20
66 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 0 | 0 | 0 | 195 |  | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 43 | 51
68 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 13 | 50 | 13 | 60 | 90 |  | Fuel shortage
69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 25 | 0 | 0 | 30 | 22 |  | Fuel shortage
70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
71 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 17 | 17 | 17 | 183 |  | Fuel shortage
72 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 6 | 10 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 94 | 92 | 128 | 140
74 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 16 | 52 | 52
76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 16 | 15 | 11 | 15 |  | 10 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 62 | 17 | 100 | 100 | 14 |  | Engine problem
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 114 | 9 | 114
79 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 17 | 17 | 17 |  | 37 | Engine problem
80 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 1 | 36 | 17 | 36 | 79 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2896 | 957 | 1055 | 1197 | 1441 | 1184 | 214
81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 34 | 75 | 80 | 80 | 122 |  | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 28 | 19 | 30 | 170 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 79 | 57 | 80 | 35 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 47 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 167 | 188 | 213.6 | 196 | 122 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 120 | 120 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 53 | 0 | 50
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 11
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 60 | 63 | 63
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 50 | 50 | 0 | 50 | 36 |  | Gas shortage
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 211 | 209 | 210 | 210
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 9 |  | Gas shortage
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 295 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 334 | 399 | 300 | 400
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 0 | 0 | 0 | 0 |  | 383 | Under maint
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1215 | 1263 | 1113 | 1316 | 95 | 930
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 807 | 789 | 824 | 920
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 0 | 32 | 83 |  | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 40
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 |  | 109 | Under maint.
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 8 | 32 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 69 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 330 | 329 | 400 | 750
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 1206 | 1118 | 1429 | 1855 | 1212 | 109
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 16 | 16
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 15 | 19 | 20 | 20 |  | 20 | Engine problem
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 120 | 80 | 120 | 120 |  | 74 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 450 | 622 | 622 | 622 |  | 622 | #01 Under maint.
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 180 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 17 | 72 | 78 |  | Fuel shortage
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 140 | 140 | 250 | 250 | 57 |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 945 | 1076 | 1265 | 1320 | 135 | 716
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 34 | 18 |  | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 5 | 0 | 20 |  | 51 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 35 | 35
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 0 | 50
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 315 | 250 | 300 | 300 |  |  | Gas shortage
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 0 | 38 | 12 |  | Engine problem
136 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 50 | 0 | 50 | 90 |  | 14 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 0 | 50 | 63 |  | Project work
142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 0 | 35 | 78 |  | Project work
143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 740 | 771 | 748 | 750
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 1125 | 1146 | 1200 | 1463 | 1236 | 73
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 6 | 67 | 6 | 60 | 53 |  | Fuel shortage
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 54 | 70 | 115 | 0 |  | Fuel shortage
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 15 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 123 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 317 | 291 | 414 | 345 | 178 | 189
| Total |  |  |  |  | 25951 | 25211 | 8712 | 9113 | 10099.6 | 12011 | 8071 | 3762
A. |  | 2024-01-06 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 9219 | MW at | 13:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 6149 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9113 | MW
3 | Day peak Generation : |  |  | 8712 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8715.46 | MW
4 | Evening peak Generation : |  |  | 9113 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 191.1812 | MKWHr | By Solar | 2.0424 | MKWHr
| By Gas : | 97.4342 | MKWHr |  | By Oil: | 11.622 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 59.0456 | MKWHr |  | By Hydro: | 1.9846 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.29616 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 8071 | MW | Dhaka | 3038.96 | 3038.96 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3762 | MW | Chittagong | 852.5 | 852.5 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 11833 | MW | Khulna | 1083 | 1083 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 742.04 | MMCFD |  |  | Rajshahi | 914.2 | 914.2 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 101492064.676 | ii) Oil : | Taka | 154259329.6 | Comilla | 785 | 785 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 390109703.52 | Total | Taka | 645861097.796 | Mymensingh | 784 | 784 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 349 | 349 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 200 | MW (W to E) at | 19:00 | hrs | Barisal | 280.8 | 280.8 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 130 | MW at | 7:00 | hrs | Rangpur | 628 | 628 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 26.7°C |  |  | Total | 8715.46 | 8715.46 |  | 0
B. |  | 2024-01-07 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 22.6°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12011 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6600 | MW
4 | Reserve(Generation end) |  |  |  | 3011 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 186.6396 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5639 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 16.6865 | MKWHr. | ii) HVDC Flow at Peak Time |  | 789 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0698 | MKWHr. | iii) Maximum HVDC Flow : |  | 903 | MW at | 21:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 92.37 |  | (b) Today: | 92.13 |  | (c) Rule Curve: |  | 101.86
.

## YesterdayGen
2024-01-06 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 361 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 17 | 21 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 125 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 33 | 0 | 0 | 0 | 280 | 180 | 96 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 7 | 33 | 10 | 84 | 77 | 0 | 0 | 0 | 43 | 0 | 53 | 0 | 120 | 0 | 40 | 50 | 0 | 211 | 0 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 25 | 355 | 295 | 0 |  | 630 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 625 | 0 | 0 |  | 4265 | 2797 | 7062 | 2227 | 630 | 1768 | 0 | 0 | 2242 | 86 | 0 | 0 | 84 | 0 | 25 | 0 | 92.42
2:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 361 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 17 | 21 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 126 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 33 | 0 | 0 | 0 | 280 | 180 | 96 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 10 | 78 | 77 | 0 | 0 | 0 | 43 | 0 | 5 | 0 | 163 | 0 | 40 | 5 | 0 | 211 | 0 | 0 | 0 | 285 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 26 | 313 | 303 | 0 |  | 476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 212 | 523 | 0 | 0 |  | 4067 | 2633 | 6700 | 2180 | 476 | 1747 | 0 | 0 | 2107 | 86 | 0 | 0 | 78 | 0 | 26 | 0 | 92.41
3:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 360 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 17 | 21 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 126 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 30 | 0 | 0 | 0 | 280 | 180 | 96 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 76 | 77 | 0 | 0 | 0 | 43 | 0 | 5 | 0 | 120 | 0 | 40 | 5 | 0 | 211 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 26 | 313 | 300 | 0 |  | 476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 150 | 422 | 0 | 0 |  | 3870 | 2494 | 6364 | 2118 | 476 | 1556 | 0 | 0 | 2026 | 86 | 0 | 0 | 76 | 0 | 26 | 0 | 92.4
4:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 360 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 17 | 21 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 126 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 33 | 0 | 0 | 0 | 280 | 180 | 96 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 72 | 77 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 120 | 0 | 40 | 5 | 0 | 211 | 0 | 0 | 0 | 290 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 25 | 314 | 301 | 0 |  | 476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 150 | 424 | 0 | 0 |  | 3845 | 2421 | 6266 | 2087 | 476 | 1534 | 0 | 0 | 1986 | 86 | 0 | 0 | 72 | 0 | 25 | 0 | 92.39
5:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 321 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 17 | 21 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 126 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 28 | 0 | 0 | 0 | 280 | 180 | 96 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 68 | 77 | 0 | 0 | 0 | 43 | 0 | 5 | 0 | 120 | 0 | 40 | 5 | 0 | 211 | 0 | 0 | 0 | 295 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 21 | 312 | 305 | 0 |  | 476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 150 | 420 | 0 | 0 |  | 3759 | 2390 | 6149 | 2003 | 476 | 1542 | 0 | 0 | 1953 | 86 | 0 | 0 | 68 | 0 | 21 | 0 | 92.38
6:00 | 0 | 0 | 0 | 180 | 0 | 14 | 0 | 333 | 0 |  | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 17 | 25 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 75 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 0 | 0 | 0 | 310 | 275 | 96 | 0 | 0 | 5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6 | 10 | 74 | 77 | 0 | 0 | 0 | 43 | 0 | 50 | 0 | 140 | 0 | 62 | 50 | 0 | 211 | 0 | 0 | 10 | 290 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 19 | 311 | 300 | 0 |  | 476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 150 | 423 | 0 | 0 |  | 4062 | 2456 | 6518 | 2116 | 476 | 1801 | 0 | 0 | 1946 | 86 | 0 | 0 | 74 | 0 | 19 | 0 | 92.37
7:00 | 0 | 0 | 0 | 180 | 0 | 14 | 0 | 364 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 17 | 25 | 0 | 0 | 46 | 40 | 0 | 0 | 0 | 25 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 41 | 0 | 0 | 0 | 330 | 270 | 96 | 0 | 0 | 5 | 0 | 0 | 10 | 0 | 0 | 0 | 13 | 6 | 33 | 10 | 76 | 71 | 0 | 0 | 0 | 43 | 0 | 53 | 0 | 140 | 0 | 62 | 50 | 0 | 211 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 277 | 20 | 312 | 300 | 0 |  | 477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 180 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 356 | 0 | 150 | 531 | 2 | 0 |  | 4183 | 2617 | 6800 | 2166 | 477 | 1863 | 0 | 0 | 2106 | 86 | 0 | 0 | 76 | 6 | 20 | 0 | 92.36
8:00 | 0 | 0 | 0 | 180 | 0 | 37 | 0 | 364 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 17 | 24 | 0 | 0 | 46 | 40 | 0 | 0 | 1 | 25 | 0 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 18 | 33 | 0 | 0 | 0 | 360 | 280 | 96 | 0 | 0 | 38 | 0 | 0 | 28 | 0 | 0 | 0 | 16 | 6 | 33 | 10 | 82 | 69 | 0 | 0 | 0 | 43 | 0 | 53 | 0 | 140 | 0 | 63 | 50 | 0 | 211 | 0 | 0 | 10 | 310 | 16 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 8 | 12 | 7 | 1 | 239 | 10 | 0 | 3 | 1 | 5 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 9 | 0 | 4 | 0 | 0 | 6 | 0 | 0 | 0 | 5 | 0 | 275 | 21 | 313 | 285 | 0 |  | 477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 0 | 6 | 0 | 1 | 0 | 510 | 180 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 354 | 5 | 266 | 747 | 32 | 0 |  | 4421 | 3288 | 7709 | 2261 | 477 | 1987 | 0 | 77 | 2635 | 86 | 0 | 5 | 82 | 78 | 21 | 0 | 92.35
9:00 | 0 | 0 | 0 | 180 | 0 | 37 | 0 | 382 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 17 | 24 | 0 | 0 | 46 | 40 | 0 | 0 | 7 | 27 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 6 | 18 | 25 | 0 | 0 | 0 | 290 | 200 | 97 | 0 | 0 | 45 | 0 | 0 | 51 | 0 | 0 | 4 | 18 | 6 | 33 | 10 | 82 | 35 | 0 | 0 | 1 | 43 | 0 | 50 | 0 | 163 | 0 | 63 | 50 | 0 | 211 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 14 | 12 | 17 | 8 | 239 | 56 | 14 | 17 | 1 | 30 | 0 | 5 | 38 | 9 | 12 | 0 | 16 | 22 | 17 | 17 | 0 | 0 | 15 | 0 | 0 | 0 | 35 | 0 | 280 | 13 | 310 | 283 | 0 |  | 512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 6 | 0 | 3 | 0 | 580 | 220 | 0 | 0 | 2 | 37 | 0 | 0 | 0 | 353 | 15 | 271 | 766 | 84 | 0 |  | 4660 | 3537 | 8197 | 2127 | 512 | 2024 | 0 | 324 | 2730 | 86 | 0 | 105 | 82 | 194 | 13 | 0 | 92.34
10:00 | 0 | 0 | 0 | 180 | 0 | 48 | 0 | 400 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 17 | 25 | 2 | 0 | 46 | 40 | 0 | 0 | 8 | 31 | 0 | 0 | 0 |  | 6 | 8 | 17 | 0 | 0 | 6 | 18 | 37 | 0 | 0 | 0 | 280 | 200 | 97 | 0 | 0 | 44 | 0 | 0 | 51 | 0 | 0 | 37 | 18 | 6 | 25 | 10 | 90 | 35 | 0 | 0 | 2 | 43 | 0 | 10 | 0 | 163 | 0 | 40 | 50 | 0 | 212 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 19 | 0 | 15 | 17 | 12 | 17 | 10 | 239 | 56 | 17 | 17 | 2 | 48 | 0 | 17 | 52 | 9 | 12 | 0 | 25 | 32 | 35 | 17 | 0 | 0 | 20 | 0 | 0 | 0 | 35 | 0 | 280 | 4 | 312 | 306 | 0 |  | 544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 6 | 0 | 3 | 0 | 510 | 180 | 0 | 0 | 3 | 56 | 0 | 0 | 0 | 355 | 13 | 180 | 758 | 118 | 0 |  | 4833 | 3360 | 8193 | 2072 | 544 | 1963 | 0 | 461 | 2565 | 86 | 0 | 142 | 90 | 266 | 4 | 0 | 93.33
11:00 | 0 | 0 | 0 | 180 | 0 | 62 | 0 | 375 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 17 | 25 | 8 | 0 | 46 | 40 | 0 | 0 | 8 | 35 | 0 | 0 | 0 |  | 6 | 32 | 17 | 0 | 0 | 6 | 18 | 22 | 0 | 0 | 0 | 310 | 215 | 70 | 8 | 0 | 44 | 1 | 0 | 51 | 0 | 25 | 52 | 18 | 6 | 25 | 10 | 92 | 35 | 0 | 0 | 2 | 43 | 0 | 10 | 0 | 120 | 0 | 40 | 10 | 0 | 212 | 0 | 0 | 10 | 295 | 16 | 8 | 0 | 30 | 0 | 0 | 19 | 0 | 17 | 19 | 12 | 17 | 13 | 244 | 56 | 17 | 17 | 5 | 48 | 17 | 17 | 52 | 9 | 12 | 0 | 34 | 37 | 17 | 17 | 0 | 0 | 24 | 0 | 0 | 0 | 35 | 0 | 280 | 2 | 313 | 305 | 0 |  | 683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 0 | 450 | 180 | 0 | 0 | 4 | 67 | 0 | 0 | 0 | 324 | 20 | 140 | 674 | 140 | 0 |  | 4876 | 3289 | 8165 | 2052 | 683 | 1855 | 0 | 530 | 2351 | 86 | 0 | 191 | 92 | 323 | 2 | 0 | 93.32
12:00 | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 385 | 0 |  | 0 | 450 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 16 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 17 | 25 | 8 | 0 | 46 | 35 | 0 | 0 | 8 | 33 | 0 | 0 | 0 |  | 6 | 32 | 34 | 0 | 0 | 6 | 18 | 16 | 0 | 0 | 0 | 280 | 150 | 76 | 8 | 0 | 45 | 9 | 0 | 51 | 0 | 25 | 52 | 18 | 6 | 25 | 16 | 94 | 34 | 0 | 0 | 2 | 43 | 0 | 47 | 0 | 120 | 0 | 61 | 50 | 0 | 211 | 0 | 0 | 10 | 315 | 16 | 8 | 0 | 45 | 0 | 0 | 19 | 0 | 17 | 20 | 12 | 17 | 13 | 334 | 59 | 17 | 17 | 4 | 80 | 17 | 17 | 62 | 9 | 12 | 0 | 42 | 47 | 0 | 17 | 0 | 0 | 26 | 1 | 0 | 0 | 35 | 0 | 270 | 1 | 311 | 306 | 0 |  | 807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 6 | 0 | 3 | 0 | 450 | 220 | 0 | 0 | 4 | 69 | 0 | 0 | 0 | 330 | 15 | 140 | 740 | 123 | 0 |  | 5119 | 3593 | 8712 | 2127 | 807 | 1999 | 0 | 588 | 2411 | 81 | 0 | 291 | 94 | 313 | 1 | 0 | 93.31
13:00 | 0 | 0 | 0 | 180 | 0 | 65 | 0 | 400 | 0 |  | 0 | 450 | 0 | 1 | 6 | 15 | 0 | 0 | 0 | 0 | 66 | 149 | 11 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 18 | 14 | 25 | 21 | 8 | 0 | 46 | 35 | 0 | 0 | 8 | 58 | 0 | 0 | 0 |  | 6 | 35 | 34 | 25 | 0 | 6 | 18 | 11 | 0 | 0 | 0 | 280 | 150 | 52 | 0 | 0 | 45 | 35 | 0 | 10 | 0 | 25 | 52 | 18 | 6 | 25 | 10 | 104 | 35 | 0 | 0 | 2 | 43 | 0 | 47 | 0 | 163 | 0 | 61 | 50 | 0 | 209 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 55 | 0 | 0 | 19 | 0 | 17 | 19 | 12 | 17 | 13 | 400 | 59 | 17 | 17 | 4 | 136 | 17 | 17 | 114 | 9 | 12 | 0 | 53 | 42 | 0 | 17 | 0 | 12 | 24 | 18 | 0 | 0 | 35 | 0 | 270 | 0 | 308 | 288 | 0 |  | 807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 24 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 0 | 6 | 0 | 2 | 0 | 550 | 180 | 0 | 0 | 4 | 63 | 17 | 0 | 0 | 316 | 9 | 180 | 762 | 159 | 0 |  | 5505 | 3714 | 9219 | 2180 | 807 | 1928 | 0 | 907 | 2556 | 81 | 0 | 328 | 104 | 328 | 0 | 0 | 93.3
14:00 | 0 | 0 | 0 | 180 | 0 | 22 | 0 | 400 | 0 |  | 0 | 450 | 0 | 9 | 34 | 15 | 0 | 0 | 0 | 0 | 32 | 64 | 25 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 18 | 22 | 25 | 21 | 8 | 0 | 46 | 35 | 0 | 0 | 8 | 86 | 0 | 0 | 0 |  | 6 | 57 | 34 | 25 | 0 | 6 | 18 | 6 | 0 | 0 | 0 | 280 | 150 | 71 | 0 | 0 | 45 | 23 | 0 | 10 | 0 | 18 | 16 | 18 | 6 | 25 | 15 | 104 | 34 | 0 | 0 | 0 | 43 | 0 | 47 | 0 | 120 | 0 | 40 | 50 | 0 | 208 | 0 | 0 | 10 | 275 | 16 | 8 | 0 | 45 | 0 | 0 | 19 | 0 | 29 | 16 | 12 | 17 | 13 | 353 | 59 | 17 | 17 | 3 | 65 | 0 | 17 | 34 | 9 | 12 | 0 | 53 | 32 | 0 | 17 | 0 | 0 | 21 | 18 | 0 | 0 | 35 | 0 | 270 | 0 | 310 | 301 | 0 |  | 807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 16 | 0 | 0 | 0 | 0 | 26 | 0 | 50 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 287 | 0 | 0 | 0 | 0 | 33 | 0 | 3 | 0 | 500 | 180 | 0 | 0 | 4 | 53 | 35 | 0 | 0 | 331 | 25 | 140 | 767 | 131 | 0 |  | 5095 | 3662 | 8757 | 2170 | 807 | 1797 | 0 | 738 | 2488 | 81 | 0 | 284 | 104 | 288 | 0 | 0 | 93.32
15:00 | 0 | 0 | 0 | 180 | 0 | 14 | 0 | 400 | 0 |  | 0 | 450 | 0 | 0 | 7 | 15 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 18 | 22 | 25 | 21 | 8 | 0 | 18 | 35 | 0 | 0 | 0 | 115 | 0 | 0 | 0 |  | 6 | 64 | 0 | 0 | 0 | 0 | 18 | 6 | 0 | 0 | 0 | 280 | 150 | 73 | 0 | 0 | 48 | 20 | 0 | 10 | 0 | 0 | 0 | 18 | 8 | 30 | 15 | 96 | 35 | 0 | 0 | 1 | 43 | 0 | 47 | 0 | 163 | 0 | 59 | 50 | 0 | 209 | 0 | 0 | 10 | 275 | 16 | 8 | 0 | 0 | 0 | 0 | 19 | 0 | 20 | 12 | 0 | 0 | 13 | 415 | 45 | 17 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 24 | 0 | 0 | 0 | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 311 | 305 | 0 |  | 807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 14 | 0 | 0 | 0 | 0 | 31 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 470 | 180 | 0 | 0 | 2 | 36 | 0 | 0 | 0 | 331 | 6 | 140 | 775 | 60 | 0 |  | 4639 | 3438 | 8077 | 2294 | 807 | 1819 | 0 | 186 | 2467 | 53 | 0 | 193 | 96 | 162 | 0 | 0 | 93.28
16:00 | 0 | 0 | 0 | 180 | 0 | 14 | 0 | 401 | 0 |  | 0 | 400 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 25 | 21 | 8 | 0 | 46 | 35 | 0 | 0 | 0 | 126 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 18 | 13 | 0 | 0 | 0 | 280 | 150 | 80 | 0 | 0 | 43 | 20 | 0 | 10 | 0 | 0 | 0 | 18 | 8 | 33 | 15 | 90 | 35 | 0 | 0 | 1 | 43 | 0 | 50 | 0 | 120 | 0 | 58 | 50 | 0 | 209 | 0 | 0 | 10 | 285 | 16 | 8 | 0 | 0 | 0 | 0 | 28 | 0 | 17 | 7 | 0 | 0 | 0 | 415 | 45 | 17 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 10 | 0 | 0 | 0 | 17 | 7 | 0 | 0 | 0 | 0 | 0 | 270 | 5 | 313 | 308 | 0 |  | 807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 420 | 180 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 330 | 4 | 140 | 658 | 24 | 0 |  | 4505 | 3128 | 7633 | 2310 | 807 | 1748 | 0 | 170 | 2301 | 81 | 0 | 48 | 90 | 73 | 5 | 0 | 93.27
17:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 384 | 0 |  | 0 | 400 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 18 | 22 | 25 | 21 | 17 | 0 | 46 | 35 | 0 | 0 | 0 | 35 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 18 | 20 | 0 | 0 | 0 | 280 | 150 | 79 | 0 | 0 | 43 | 20 | 0 | 10 | 0 | 0 | 2 | 18 | 8 | 33 | 15 | 86 | 36 | 0 | 0 | 0 | 43 | 0 | 24 | 0 | 163 | 0 | 58 | 50 | 0 | 207 | 0 | 0 | 10 | 305 | 16 | 8 | 0 | 0 | 0 | 0 | 19 | 0 | 17 | 1 | 0 | 0 | 0 | 402 | 59 | 25 | 0 | 0 | 15 | 0 | 0 | 13 | 0 | 0 | 0 | 17 | 1 | 0 | 0 | 0 | 17 | 1 | 0 | 29 | 0 | 0 | 0 | 270 | 7 | 310 | 300 | 0 |  | 807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 120 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 220 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 329 | 1 | 140 | 662 | 4 | 0 |  | 4607 | 3198 | 7805 | 2227 | 807 | 1893 | 0 | 261 | 2311 | 81 | 0 | 121 | 86 | 11 | 7 | 0 | 92.26
18:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 330 | 0 |  | 0 | 330 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 16 | 149 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 18 | 18 | 25 | 21 | 17 | 0 | 46 | 35 | 0 | 0 | 13 | 41 | 0 | 0 | 0 |  | 6 | 0 | 17 | 0 | 13 | 12 | 18 | 26 | 0 | 0 | 0 | 280 | 150 | 74 | 0 | 0 | 48 | 20 | 0 | 51 | 0 | 0 | 37 | 18 | 8 | 33 | 15 | 94 | 72 | 0 | 0 | 0 | 43 | 0 | 45 | 0 | 120 | 0 | 59 | 50 | 0 | 206 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 30 | 0 | 0 | 28 | 0 | 43 | 0 | 12 | 9 | 16 | 365 | 79 | 105 | 6 | 0 | 100 | 9 | 6 | 58 | 44 | 12 | 0 | 50 | 0 | 0 | 12 | 0 | 17 | 0 | 17 | 24 | 0 | 54 | 0 | 300 | 13 | 310 | 301 | 0 |  | 883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 80 | 19 | 16 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 10 | 8 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 0 | 15 | 0 | 60 | 0 | 0 | 35 | 520 | 180 | 0 | 18 | 0 | 0 | 40 | 0 | 0 | 331 | 0 | 140 | 757 | 0 | 0 |  | 5248 | 3580 | 8828 | 2137 | 883 | 1725 | 0 | 1060 | 2528 | 81 | 0 | 307 | 94 | 0 | 13 | 0 | 92.25
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 333 | 0 |  | 0 | 360 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 18 | 22 | 25 | 21 | 17 | 0 | 46 | 35 | 0 | 0 | 17 | 65 | 0 | 0 | 0 |  | 6 | 0 | 17 | 0 | 32 | 19 | 18 | 30 | 0 | 0 | 0 | 280 | 150 | 71 | 0 | 0 | 48 | 20 | 0 | 51 | 0 | 0 | 16 | 18 | 10 | 33 | 15 | 92 | 75 | 0 | 0 | 0 | 43 | 0 | 53 | 0 | 120 | 0 | 60 | 50 | 0 | 209 | 0 | 0 | 10 | 295 | 16 | 8 | 0 | 0 | 0 | 0 | 28 | 0 | 43 | 0 | 12 | 17 | 50 | 399 | 79 | 105 | 17 | 0 | 115 | 0 | 17 | 17 | 114 | 12 | 0 | 68 | 0 | 35 | 17 | 0 | 17 | 0 | 36 | 17 | 0 | 17 | 0 | 390 | 9 | 310 | 299 | 0 |  | 789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 19 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 28 | 8 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 35 | 622 | 180 | 0 | 35 | 0 | 0 | 54 | 0 | 0 | 329 | 0 | 140 | 771 | 0 | 0 |  | 5482 | 3631 | 9113 | 2208 | 789 | 1810 | 0 | 1189 | 2732 | 81 | 0 | 203 | 92 | 0 | 9 | 0 | 92.22
19:30 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 332 | 0 |  | 0 | 360 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 18 | 22 | 25 | 21 | 17 | 0 | 46 | 35 | 0 | 0 | 17 | 84 | 0 | 0 | 0 |  | 6 | 0 | 17 | 0 | 32 | 20 | 18 | 30 | 0 | 0 | 0 | 280 | 150 | 71 | 0 | 0 | 48 | 20 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 15 | 92 | 76 | 0 | 0 | 0 | 43 | 0 | 53 | 0 | 120 | 0 | 60 | 50 | 0 | 209 | 0 | 0 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 28 | 0 | 43 | 0 | 12 | 17 | 58 | 401 | 79 | 105 | 17 | 0 | 65 | 0 | 17 | 0 | 114 | 12 | 0 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 36 | 17 | 0 | 0 | 0 | 430 | 10 | 311 | 301 | 0 |  | 789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 19 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 48 | 8 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 35 | 622 | 180 | 0 | 35 | 0 | 0 | 54 | 0 | 0 | 331 | 0 | 140 | 768 | 0 | 0 |  | 5360 | 3641 | 9001 | 2232 | 789 | 1827 | 0 | 992 | 2772 | 81 | 0 | 206 | 92 | 0 | 10 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 331 | 0 |  | 0 | 360 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 18 | 22 | 17 | 21 | 17 | 0 | 46 | 35 | 0 | 0 | 17 | 83 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 34 | 20 | 18 | 33 | 0 | 0 | 0 | 280 | 150 | 71 | 0 | 0 | 48 | 20 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 15 | 90 | 75 | 0 | 0 | 0 | 43 | 0 | 53 | 0 | 150 | 0 | 60 | 50 | 0 | 209 | 0 | 0 | 10 | 295 | 16 | 11 | 0 | 0 | 0 | 0 | 28 | 0 | 44 | 0 | 12 | 17 | 55 | 401 | 79 | 105 | 17 | 0 | 15 | 0 | 17 | 0 | 118 | 12 | 0 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 31 | 17 | 0 | 0 | 0 | 430 | 9 | 312 | 302 | 0 |  | 789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 20 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 35 | 622 | 180 | 0 | 17 | 0 | 0 | 54 | 0 | 0 | 332 | 0 | 140 | 761 | 0 | 0 |  | 5308 | 3546 | 8854 | 2221 | 789 | 1847 | 0 | 924 | 2767 | 81 | 0 | 126 | 90 | 0 | 9 | 0 | 92.23
21:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 354 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 25 | 21 | 0 | 0 | 46 | 35 | 0 | 0 | 0 | 83 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 32 | 20 | 18 | 40 | 0 | 0 | 0 | 280 | 150 | 71 | 0 | 0 | 48 | 20 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 15 | 90 | 75 | 0 | 0 | 0 | 43 | 0 | 53 | 0 | 163 | 0 | 60 | 50 | 0 | 209 | 0 | 0 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 28 | 0 | 35 | 0 | 12 | 17 | 56 | 401 | 79 | 88 | 0 | 0 | 0 | 0 | 17 | 0 | 109 | 12 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 18 | 17 | 0 | 0 | 0 | 420 | 9 | 312 | 304 | 0 |  | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 20 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 140 | 766 | 0 | 0 |  | 5230 | 3613 | 8843 | 2292 | 903 | 2103 | 0 | 595 | 2718 | 81 | 0 | 52 | 90 | 0 | 9 | 0 | 92.22
22:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 404 | 0 |  | 0 | 350 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 25 | 21 | 0 | 0 | 46 | 35 | 0 | 0 | 0 | 67 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 23 | 20 | 18 | 27 | 0 | 0 | 0 | 280 | 150 | 71 | 0 | 0 | 48 | 20 | 0 | 51 | 0 | 0 | 0 | 18 | 10 | 33 | 15 | 88 | 74 | 0 | 0 | 0 | 43 | 0 | 53 | 0 | 120 | 0 | 61 | 50 | 0 | 208 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 17 | 28 | 401 | 59 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 59 | 12 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 18 | 0 | 0 | 0 | 0 | 420 | 13 | 309 | 291 | 0 |  | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 140 | 764 | 0 | 0 |  | 4767 | 3568 | 8335 | 2315 | 902 | 1933 | 0 | 327 | 2676 | 81 | 0 | 0 | 88 | 0 | 13 | 0 | 92.21
23:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 378 | 0 |  | 0 | 350 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 18 | 17 | 24 | 0 | 0 | 46 | 35 | 0 | 0 | 0 | 95 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 38 | 0 | 0 | 0 | 280 | 150 | 80 | 0 | 0 | 48 | 20 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 15 | 84 | 87 | 0 | 0 | 0 | 42 | 0 | 10 | 0 | 120 | 0 | 61 | 5 | 0 | 208 | 0 | 0 | 10 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 16 | 311 | 307 | 0 |  | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 140 | 642 | 0 | 0 |  | 4369 | 3333 | 7702 | 2237 | 902 | 1870 | 0 | 32 | 2480 | 81 | 0 | 0 | 84 | 0 | 16 | 0 | 92.2
24:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 361 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 17 | 25 | 0 | 0 | 46 | 35 | 0 | 0 | 0 | 120 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 0 | 0 | 0 | 280 | 150 | 86 | 0 | 0 | 48 | 5 | 0 | 5 | 0 | 0 | 0 | 18 | 5 | 33 | 15 | 76 | 100 | 0 | 0 | 0 | 43 | 0 | 5 | 0 | 120 | 0 | 60 | 5 | 0 | 208 | 0 | 0 | 0 | 285 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 418 | 12 | 312 | 280 | 0 |  | 713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 140 | 488 | 0 | 0 |  | 4253 | 2942 | 7195 | 2253 | 713 | 1765 | 0 | 17 | 2278 | 81 | 0 | 0 | 76 | 0 | 12 | 0 | 92.19
KWH | 0 | 0 | 0 | 4362750 | 0 | 886545 | 0 | 9014400 | 0 |  | 0 | 9300000 | 0 | 13440 | 35038 | 205379 | 0 | 0 | 0 | 0 | 169632 | 1237920 | 34764 | 0 | 0 | 0 | 51120 | 66984 | 64497 | 0 | 432000 | 455760 | 510400 | 534500 | 127680 | 0 | 1080600 | 904000 | 0 | 0 | 117934 | 1842160 | 0 | 0 | 0 |  | 92160 | 204048 | 162697 | 39480 | 138240 | 141120 | 415200 | 690720 | 0 | 0 | 0 | 7298000 | 4488000 | 2068000 | 16727 | 0 | 772704 | 250080 | 0 | 776752 | 0 | 113680 | 328627 | 362016 | 153540 | 627300 | 315070 | 2069760 | 1399680 | 0 | 0 | 10400 | 1013000 | 0 | 863400 | 0 | 3554754 | 0 | 1270944 | 913920 | 0 | 5259080 | 0 | 0 | 201240 | 7216000 | 312288 | 193440 | 0 | 313636 | 0 | 0 | 316800 | 0 | 331344 | 134865 | 151680 | 223200 | 302763 | 7926000 | 906000 | 574080 | 184836 | 21723 | 740182 | 78133 | 198220 | 448020 | 525840 | 152640 | 0 | 415680 | 254590 | 89280 | 220800 | 0 | 192240 | 161824 | 178560 | 121680 | 0 | 306109 | 0 | 7423635 | 296160 | 7716363 | 6741818 | 0 |  | 16686545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31200 | 0 | 0 | 2157000 | 379400 | 18624 | 0 | 0 | 0 | 51020 | 26183 | 201696 | 0 | 24793 | 48903 | 87739 | 82136 | 0 | 0 | 169668 | 0 | 0 | 4131600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7554000 | 19200 | 0 | 48096 | 0 | 245500 | 0 | 25891 | 96768 | 12472200 | 4735909 | 0 | 92400 | 26040 | 424800 | 231552 | 0 | 0 | 7447273 | 122831 | 4123600 | 15730909 | 859410 | 0 |  | 112828271 | 78352886 | 191181157 | 53352900 | 16686545 | 44081265 | 0 | 9156381 | 59045580 | 1984600 | 0 | 2465592 | 2069760 | 2042374 | 296160 | 0
Fuel Cost | 0 | 0 | 0 | 6500497.5 | 0 | 1179104.85 | 0 | 9465120 | 0 |  | 0 | 10137000 | 0 | 150259.2 | 464253.5 | 2721271.75 | 0 | 0 | 0 | 0 | 2386722.24 | 20066683.2 | 320524.08 | 0 | 0 | 0 | 650246.4 | 904284 | 864904.77 | 0 | 324000 | 0 | 0 | 0 | 2171836.8 | 0 | 291762 | 244080 | 0 | 0 | 1928220.9 | 1915846.4 | 0 | 0 | 0 |  | 1202688 | 3403520.64 | 2769102.94 | 533374.8 | 1752883.2 | 1632758.4 | 527304 | 2300097.6 | 0 | 0 | 0 | 8100780 | 4891920 | 2398880 | 21577.83 | 0 | 873155.52 | 372619.2 | 0 | 1297175.84 | 0 | 1963253.6 | 4420033.15 | 495961.92 | 115155 | 1097775 | 236302.5 | 14860876.8 | 1525651.2 | 0 | 0 | 165776 | 1387810 | 0 | 1502316 | 0 | 4087967.1 | 0 | 2465631.36 | 2083737.6 | 0 | 5311670.8 | 0 | 0 | 398455.2 | 7216000 | 234216 | 147014.4 | 0 | 4281131.4 | 0 | 0 | 4270464 | 0 | 4589114.4 | 1576571.85 | 1565337.6 | 3048912 | 4017665.01 | 7291920 | 11016960 | 8301196.8 | 2338175.4 | 338009.88 | 8689736.68 | 850868.37 | 2107078.6 | 6079631.4 | 6778077.6 | 1798099.2 | 0 | 5383056 | 3678825.5 | 1132963.2 | 2512704 | 0 | 2510654.4 | 1933796.8 | 2673043.2 | 1602525.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 50059635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 561912 | 0 | 0 | 2415840 | 736036 | 203001.6 | 0 | 0 | 0 | 855605.4 | 457940.67 | 3154525.44 | 0 | 410572.08 | 826949.73 | 1195882.57 | 1385634.32 | 0 | 0 | 128438.676 | 0 | 0 | 35035968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7478460 | 258048 | 0 | 568975.68 | 0 | 3117850 | 0 | 286095.55 | 1174763.52 | 103519260 | 4830627.18 | 0 | 683760 | 294512.4 | 4982904 | 3549692.16 | 0 | 0 | 67695711.57 | 0 | 49359492 | 134499271.95 | 0 | 0 |  | 244846578.08 | 479727365.496 | 724573943.576 | 57850890.276 | 50059635 | 43641174.4 | 0 | 118814201.66 | 390109703.52 | 535842 | 0 | 35445127.94 | 14860876.8 | 13256491.98 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 385 | 0 |  | 0 | 450 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 16 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 17 | 25 | 8 | 0 | 46 | 35 | 0 | 0 | 8 | 33 | 0 | 0 | 0 |  | 6 | 32 | 34 | 0 | 0 | 6 | 18 | 16 | 0 | 0 | 0 | 280 | 150 | 76 | 8 | 0 | 45 | 9 | 0 | 51 | 0 | 25 | 52 | 18 | 6 | 25 | 16 | 94 | 34 | 0 | 0 | 2 | 43 | 0 | 47 | 0 | 120 | 0 | 61 | 50 | 0 | 211 | 0 | 0 | 10 | 315 | 16 | 8 | 0 | 45 | 0 | 0 | 19 | 0 | 17 | 20 | 12 | 17 | 13 | 334 | 59 | 17 | 17 | 4 | 80 | 17 | 17 | 62 | 9 | 12 | 0 | 42 | 47 | 0 | 17 | 0 | 0 | 26 | 1 | 0 | 0 | 35 | 0 | 270 | 1 | 311 | 306 | 0 |  | 807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 6 | 0 | 3 | 0 | 450 | 220 | 0 | 0 | 4 | 69 | 0 | 0 | 0 | 330 | 15 | 140 | 740 | 123 | 0 |  | 8712 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 333 | 0 |  | 0 | 360 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 18 | 22 | 25 | 21 | 17 | 0 | 46 | 35 | 0 | 0 | 17 | 65 | 0 | 0 | 0 | 0 | 6 | 0 | 17 | 0 | 32 | 19 | 18 | 30 | 0 | 0 | 0 | 280 | 150 | 71 | 0 | 0 | 48 | 20 | 0 | 51 | 0 | 0 | 16 | 18 | 10 | 33 | 15 | 92 | 75 | 0 | 0 | 0 | 43 | 0 | 53 | 0 | 120 | 0 | 60 | 50 | 0 | 209 | 0 | 0 | 10 | 295 | 16 | 8 | 0 | 0 | 0 | 0 | 28 | 0 | 43 | 0 | 12 | 17 | 50 | 399 | 79 | 105 | 17 | 0 | 115 | 0 | 17 | 17 | 114 | 12 | 0 | 68 | 0 | 35 | 17 | 0 | 17 | 0 | 36 | 17 | 0 | 17 | 0 | 390 | 9 | 310 | 299 | 0 |  | 789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 19 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 28 | 8 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 35 | 622 | 180 | 0 | 35 | 0 | 0 | 54 | 0 | 0 | 329 | 0 | 140 | 771 | 0 | 0 |  | 9113 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 350 | 0 |  | 0 | 450 | 0 | 100 | 85 | 15 | 0 | 0 | 0 | 0 | 90 | 149 | 40 | 0 | 0 | 0 | 35 | 35 | 17 | 0 | 18 | 22 | 25 | 24 | 17 | 0 | 46 | 35 | 0 | 0 | 17 | 125 | 0 | 0 | 0 |  | 6 | 70 | 51 | 45 | 33 | 20 | 18 | 30 | 0 | 0 | 0 | 300 | 280 | 100 | 0 | 0 | 48 | 20 | 0 | 51 | 0 | 30 | 52 | 18 | 10 | 33 | 15 | 140 | 80 | 0 | 0 | 0 | 43 | 0 | 50 | 0 | 163 | 0 | 63 | 50 | 0 | 210 | 0 | 0 | 10 | 300 | 16 | 11 | 0 | 130 | 0 | 0 | 30 | 0 | 45 | 0 | 80 | 17 | 60 | 400 | 80 | 105 | 17 | 0 | 200 | 17 | 17 | 100 | 114 | 50 | 0 | 72 | 0 | 35 | 17 | 0 | 17 | 0 | 36 | 17 | 0 | 17 | 0 | 420 | 10 | 312 | 300 | 0 |  | 920 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 40 | 0 | 8 | 120 | 20 | 16 | 0 | 0 | 0 | 34 | 20 | 90 | 35 | 42 | 50 | 8 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 105 | 0 | 50 | 0 | 60 | 0 | 0 | 35 | 622 | 220 | 0 | 72 | 0 | 0 | 115 | 0 | 0 | 750 | 0 | 250 | 750 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 300 | 0 | 0 | 0 | 450 | 0 | 100 | 85 | 15 | 0 | 0 | 0 | 0 | 90 | 149 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 17 | 24 | 8 | 0 | 46 | 35 | 0 | 0 | 8 | 100 |  | 0 | 0 | 0 | 6 | 32 | 51 | 0 | 0 | 6 | 18 | 20 | 0 | 0 | 0 | 300 | 280 | 96 | 0 | 0 | 38 | 15 | 0 | 43 | 0 | 0 | 52 | 18 | 10 | 33 | 11 | 128 | 80 | 0 | 0 | 1.6 | 43 | 0 | 0 | 0 | 163 | 0 | 63 | 0 | 0 | 210 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 80 | 0 | 0 | 19 | 0 | 17 | 20 | 12 | 17 | 13 | 300 | 57 | 17 | 17 | 5 | 150 | 17 | 17 | 100 | 9 | 12 | 0 | 0 | 50 | 17 | 17 | 0 | 17 | 35 | 17 | 17 | 0 | 17 | 0 | 300 | 10 | 312 | 300 | 0 |  | 824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 42 | 0 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 105 | 0 | 0 | 0 | 6 | 0 | 8 | 0 | 622 | 220 |  | 17 | 6 | 100 | 70 | 0 |  | 400 | 30 | 250 | 748 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 283 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 18 | 17 | 17 | 0 | 0 | 46 | 35 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 42 | 0 | 0 | 0 | 290 | 100 | 81 | 0 | 0 | 40 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 62 | 101 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 208 | 0 | 0 | 0 | 300 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 244 | 9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 270 | 24 | 310 | 309 | 0 | 0 | 614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 280 | 180 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 329 | 2 | 140 | 421 | 28 | 0 | 0 |  |  |  | 97434165 | 16686545 | 0 | 59045580 | 11621973 | 2069760 | 2042374 | 296160 | 1984600
[8 empty] | 299430 | [13 empty] | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | [15 empty] | 299772 | [10 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 |  | 399747 |  |  |  | 399575 | 399337 | 399467 | 399589 | 299230 | 765 | [6 empty] | 399245 |  | 299282 | 399274 |  | 399223 |  | 399630 | [12 empty] | 599468 |  |  |  | 230 | [27 empty] | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 | [8 empty] | 599726 | [9 empty] | 97.4342 | 16.6865 | 0 | 59.0456 | 11.622 | 2.0698 | 2.0424 | 0.29616 | 1.9846
| Minimum Generation |  | 6149 | 5:00
| Highest Generation |  | 9219 | 13:00 | [200 empty] | 191.1812
| Day Peak Generation |  | 8712 | 12:00
| Evening Peak Generation |  | 9113 | 19:00 | [200 empty] | 202699852
| HVDC Max Flow |  | 903 | 21:00 | [200 empty] | 202.6999
| HVDC EvPeak Flow |  | 789 | 19:00
| Load factor L.F |  | 86.41% | [166 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-01-07
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2024-01-06 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 8712 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 5639
Evening Peak Generation : |  |  | 9113 | MW Hour : | 19:00 | Available Max Generation : |  | 12011
E.P. Demand (at gen end) : |  |  | 9113 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9000
Maximum Generation : |  |  | 9219 | MW Hour : | 13:00 | Reserve(Generation end) |  | 3011
Total Gen. (MKWH) : |  |  | 191.1812 | System Load Factor : | 86.41% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 130 | MW at | 7:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-01-07
Actual : |  | 92.13 | Ft.(MSL) , | Rule curve : | 101.86 | Ft.( MSL )
Gas Consumed : |  | Total = | 742.04 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 101492064.676
: |  |  | Coal : | 390109703.52 | Oil : | 154259329.6 | Total : | 645861097.796
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3467.4632 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 946.0784 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1323.2624 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1148.3047 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 945.7957 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 702.4528 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 394.7953 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 328.0568 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 641.6436 |  |  | 0 | 0%
Total |  | 0 |  | 9897.8529 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
10:50 |  | Ghorashal 230/132 kV T-2 transformer tripped.
12:00 |  | Day peak generation: 8712 MW.
18:55 |  | Sikalbaha Gas 225 MW ST was sync.
19:00 |  | Evening Peak Gen. 9113 MW
19:04 |  | Ghorashal 230/132 kV T-2 transformer was switched on.
19:53 |  | Sikalbaha 225MW CCPP Tripped with remarks:- ST
19:53 |  | Sikalbaha 225MW CCPP Syncronized with remarks:- ST was trip at 19:53
19:55 |  | Sikalbaha Gas 225 MW ST tripped.
01:40 |  | Ghorashal 230/132 kV ATR-2 transformer tripped.
| 06:14 | Ashuganj 230/132/33kV S/S SHUNT REACTOR-3 is restored.
07:00 |  | Minimum generation is 5639 MW
07:37 |  | Bangladesh holds general election Today.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-01-06 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4362750
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 73 | 886545 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 333 | 9014400
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 360 | 9300000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 0 | 13440 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 35038 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 205379 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 34764 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 0 | 0 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 169632 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 51120 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 98 | 1237920 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 66984 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 64497 | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 40 | 887760 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 510400 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 21 | 534500 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 17 | 127680 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 313636 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 43 | 331344 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 574080
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 68 | 415680 | Low demand
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 89280
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 161824
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 121680 | Fuel shortage
| Meghnaghat Unique power |  | IPP | 586 | 0 | 299 | 6741818 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5422 | 1781 | 36252151
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 117934 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 134865
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 141120 | Low demand
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 81 | 1984600 | Unit-3 under maint.
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 65 | 1842160 | ST was sync 18:55.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 184836 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 204048 | Reserve
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 162697 | Low demand
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 39480 | Reserve
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 151680 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 415200 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 30 | 690720
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 32 | 138240 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 21723
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 115 | 740182 | Low demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 78133 | Reserve
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 198220 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 152640 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 220800 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 17 | 306109 | Fuel shortage
| SS Power I |  | SS Power | 2*612 | 1224 | 390 | 7423635 | Coal shortage
| Cox's Bazar Wind |  | IPP | 66 | 0 | 9 | 296160 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 310 | 7716363 | On test.
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 3769 | 1195 | 23361545
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 71 | 2068000 | ST Under maint.
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7298000 | GT sync at 18:35.
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 150 | 4488000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 48 | 772704 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 0 | 20 | 250080 | Gas shortage
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 16727 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 776752 | Engine problem
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 50 | 302763 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 113680 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 223200 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 362016 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 153540
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 92 | 2069760
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 627300
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 16 | 328627 | Low demand
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 15 | 315070 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 448020 | Low demand
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 114 | 525840 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 192240 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 36 | 178560 | Fuel shortage
| Cumilla Area Total |  |  |  | 2896 | 1055 | 21510879
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 75 | 1399680 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Contract Expired
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10400
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 28 | 316800 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 79 | 906000 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 254590
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 92160 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 188 | 2979630
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1013000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 120 | 3554754
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 863400
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 193440
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1270944
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 50 | 913920 | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 209 | 5259080
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 312288 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7216000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 399 | 7926000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 201240
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 0 | 0 | Under maint.
| Sylhet Area Total |  |  |  | 2427 | 1263 | 28724066
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 789 | 16686545
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 0 | Reserve
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 31200 | Reserve
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Machine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Reserve
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 19200 | Reserve
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 424800
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 329 | 7447273 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 1118 | 24609018
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 18624 | Reserve
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 19 | 379400 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 80 | 2157000 | GT-1 & ST Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 622 | 12472200 | Unit-2 under maint.
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 180 | 4735909
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 92400 | Low demand
| Barisal 307 MW |  | IPP | 307*1 | 307 | 140 | 4123600 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1076 | 23979133
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 51020 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 5 | 26183 | Fuel shortage
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 24793 | Reserve
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 48903 | Fuel shortage
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 250 | 7554000 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 82136 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 169668
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 87739 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 201696 | Reserve
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 48096 | Reserve
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 96768 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 26040
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 771 | 15730909
| Rajshahi Area Total |  |  |  | 3631 | 1146 | 24147951
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4131600 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 67 | 245500 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 25891
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 54 | 231552 | Fuel shortage
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 122831
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 859410
| Rangpur Area Total |  |  |  | 950 | 291 | 5616784
| Total |  |  |  | 25211 | 9113 | 191181157
| Eastern Grid Total |  |  |  | 15128 | 5482 | 112828271
| Western Grid Total |  |  |  | 10083 | 3631 | 78352886
| National Grid Total |  |  |  | 25211 | 9113 | 191181157
*Data collected from respective power station over telephone.
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2024-01-06
| (a) ENTIRE EASTERN GRID : |  | 5809.46 | MW | (b) ENTIRE WESTERN GRID : |  | 2906 | MW
| i) Dhaka area |  | 3038.96 | MW | i) Khulna area |  | 1083 | MW
| ii) Chittagong area |  | 852.5 | MW | ii) Rajshahi area |  | 914.2 | MW
| iii) Comilla area |  | 785 | MW | iii) Barisal area |  | 280.8 | MW
| iv) Mymensingh area |  | 784 | MW | iv) Rangpur area |  | 628 | MW
| v) Sylhet area |  | 349 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8715.46 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 12 | 04:00 | Chhatak | 23 | 20:00 | Kamrangirchar | 36.6 | 13:00 | Narinda | 35 | 14:00 | Sherpur | 108 | 18:30
2 | AKSML | 6 | 03:00 | Chowmuhani | 118 | 19:00 | Kaptai | N/A | N/A | Narshingdi | 140 | 19:00 | Shikalbaha | 20 | 13:00
3 | Aftabnagar | 22 | 13:00 | Chuadanga | 67 | 13:00 | Kazla | 72 | 13:00 | Natore | 95 | 18:30 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 52 | 13:00 | Coxsbazar | 73 | 09:00 | Keranigonj | 66 | 13:00 | Nawabganj | 27.4 | 13:00 | Shitalakhya | 69.8 | 12:00
5 | Agrabad | 40 | 14:00 | Cumilla(N) | 86 | 18:30 | Khagrachori | 22 | 18:00 | Netrakona | 107 | 09:00 | Sholosohor | 25 | 13:00
6 | Amnura | 40 | 13:00 | Cumilla(S) | 104 | 13:00 | Khulna | 62 | 13:00 | New | 15.4 | 11:00 | Shyampur | 128 | 11:00
7 | Ashuganj | 41 | 14:00 | Daudkandi | 96 | 18:30 | Khulshi | 130 | 11:00 | Niamatpur | 59 | 09:00 | Siddhirganj | 78 | 13:00
8 | BIPTC | N/A | N/A | Dhaka | 10 | 13:00 | Kishoreganj | 108 | 20:00 | Noapara | 34 | 18:00 | Sirajganj | 76 | 19:00
9 | BSRM | 84 | 18:30 | Dhamrai | 74 | 12:00 | Kodda | 201 | 18:00 | PHP | 6 | 02:00 | Sonargaon | 72 | 00:00
10 | Bagerhat | 62 | 18:00 | Dhanmondi | 78.6 | 13:00 | Kulaura | 26 | 18:00 | Pabna | 78 | 18:30 | Sreemongol | 46 | 18:00
11 | Bakulia | 53 | 13:00 | Dohazari | 48 | 18:00 | Kurigram | 50 | 18:00 | Palashbari | 73 | 18:30 | Sreepur | 49 | 01:00
12 | Banani | 17.4 | 13:00 | Faridpur | 101 | 18:30 | Kushtia | 90 | 18:30 | Panchagarh | 41 | 18:00 | Srinagar | 27.96 | 20:00
13 | Bangabhaban | 3 | 00:00 | Fatullah | 41 | 12:00 | Lalbag | 55 | 13:00 | Patuakhali | 64.6 | 20:00 | Sunamganj | 34 | 18:00
14 | Barapukuria | 44 | 18:30 | Fenchuganj | 23 | 18:00 | Lalmonirhat | 33 | 18:00 | Payra | 14 | 18:30 | Sylhet | 12 | 16:00
15 | Barguna | 14 | 21:00 | Feni | 66 | 18:00 | MI_Cement | 18.8 | 00:00 | Postogola | 37 | 13:00 | Sylhet-132 | 78 | 13:00
16 | Barishal | 74 | 13:00 | GPH | 96 | 17:00 | Madanganj | 28 | 10:00 | Purbachal | 12 | 13:00 | TK | 19 | 18:00
17 | Barishal-230 | 60 | 20:00 | Ghorashal | 54 | 10:00 | Madaripur | 61 | 19:30 | Purbasadipur | 102 | 13:00 | Tangail | 126 | 18:00
18 | Baroaulia | 54 | 09:00 | Goalpara | 24 | 13:00 | Madartek | 60.17 | 13:00 | Rahim | 0 | 00:00 | Thakurgaon | 73 | 18:30
19 | Baroirhat | 36 | 18:00 | Gollamari | 42 | 13:00 | Madunaghat | 32 | 13:00 | Rajbari | 47 | 18:30 | Tongi | 104 | 11:00
20 | Bashundhara | 115 | 13:00 | Gopalganj | 71 | 18:30 | Magura | 43 | 18:00 | Rajendrapur | 64 | 13:00 | Ullahpara | 0 | 00:00
21 | BashundharaCement | 6 | 12:00 | Gulshan | 54 | 13:00 | Mahasthangarh | 46 | 08:00 | Rajshahi | 98 | 13:00 | Ullon | 29 | 13:00
22 | Beanibazar | 40 | 18:00 | Halishahar | 39.5 | 10:00 | Manikganj | 79 | 19:00 | Rajshahi-230 | 21 | 13:00 | Uttara | 36 | 13:00
23 | Benapole | 50 | 08:00 | HaripurSBU | 133 | 00:00 | Maniknagar | 44 | 13:00 | Ramganj | 82 | 18:00 | UttaraNew | 26 | 13:00
24 | Bhaluka | 94 | 18:30 | Hasnabad | 53 | 11:00 | Matarbari | 30 | 18:00 | Rampur | 16 | 18:00 | Zigatola | 48 | 13:00
25 | Bhandaria | 34 | 21:00 | Hathazari | 46 | 18:00 | Matuail | 53 | 12:00 | Rangamati | 13 | 18:00
26 | Bhangura | 20 | 18:00 | Ishurdi | 39 | 00:00 | Millgate | 69 | 11:00 | Rangpur | 92 | 18:00
27 | Bheramara(GK) | 37 | 18:30 | Jaldhaka | 56 | 18:00 | Mirpur | 81 | 13:00 | Ruppur | 3.2 | 10:00
28 | Bhulta | 211 | 13:00 | Jamalpur | 106 | 18:00 | Mirsorai | 4 | 19:00 | SSM | 13 | 01:00
29 | Bog-Sherpur | 46 | 18:00 | Jashore | 91 | 13:00 | Mirzapur | 37.2 | 19:30 | Saidpur | 79 | 12:00
30 | Bogura | 103 | 19:30 | Jhenaidah | 85 | 18:30 | Mithapukur | 40 | 18:00 | Satkhira | 81 | 18:00
31 | Borhanuddin | 36 | 21:00 | Joydebpur | 113 | 14:00 | Modern | 0 | 00:00 | Satmasjid | 78 | 12:00
32 | Brahmanbaria | 101 | 18:30 | Joypurhat | 39 | 08:00 | Mogbazar | 62.1 | 13:00 | Savar | 102 | 15:00
33 | Cantonment | 88 | 13:00 | Juldah | 18 | 07:00 | Mongla | 22 | 12:00 | SevenRings | 4.12 | 04:00
34 | Chandpur | 44 | 20:00 | KSRM | 38 | 12:00 | Motijheel | 22 | 13:00 | ShahCement | 16 | 12:00
35 | Chandraghona | 23 | 18:00 | Kabirpur | 149 | 12:00 | Munshiganj | 65 | 13:00 | Shahjadpur | 65 | 12:00
36 | Chapai | 47 | 13:00 | Kachua | 45 | 18:00 | Mymensingh | 163 | 13:00 | Shahjibazar | 80 | 20:00
37 | Charsaidpur | 25 | 00:00 | Kallyanpur | 63 | 13:00 | Naogaon | 92 | 09:00 | Shahmirpur | 34 | 18:00
38 | Chauddagram | 33 | 18:00 | Kalurghat | 18 | 12:00 | Narail | 39 | 18:00 | Shariatpur | 49 | 20:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-01-06 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 408 | 05:00 | 394 | 12:00 | Gopalganj | 414 | 06:00 | 402 | 12:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 411 | 05:00 | 398 | 15:00
| Bhulta | 406 | 00:00 | 391 | 12:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 421 | 10:00 | 408 | 15:00 | Payra | 419 | 03:00 | 412 | 12:00
| BIPTC | 409 | 02:00 | 394 | 13:00 | Rahanpur | 415 | 02:00 | 400 | 12:00
| Bogura | N/A | N/A | N/A | N/A | Rampal | 414 | 01:00 | 403 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 242 | 05:00 | 231 | 15:00 | Hasnabad | 243 | 05:00 | 233 | 12:00
| AKSML | 240 | 18:00 | 228 | 15:00 | Hathazari | 241 | 18:00 | 228 | 16:00
| Aminbazar | 243 | 01:00 | 233 | 15:00 | Ishurdi | 240 | 03:00 | 225 | 12:00
| Ashuganj | 241 | 05:00 | 235 | 12:00 | Jhenaidah | 238 | 03:00 | 223 | 12:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 240 | 05:00 | 228 | 15:00
| Baghabari | 237 | 04:00 | 225 | 12:00 | Keranigonj | 241 | 03:00 | 231 | 15:00
| Barapukuria | 224 | 00:00 | 216 | 09:00 | Khulna(S) | 242 | 01:00 | 230 | 12:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 244 | 02:00 | 238 | 12:00 | Maniknagar | 242 | 00:00 | 234 | 12:00
| Bheramara | 239 | 03:00 | 226 | 11:00 | Meghnaghat | 247 | 04:00 | 240 | 11:00
| Bhulta | 244 | 05:00 | 235 | 12:00 | Mirsorai | 240 | 18:00 | 230 | 16:00
| Bibiana | 241 | 00:00 | 234 | 15:00 | Rajshahi | 238 | 03:00 | 222 | 12:00
| BIPTC | 239 | 03:00 | 223 | 12:00 | Rampal | 240 | 01:00 | 229 | 12:00
| Bogura | 234 | 04:00 | 221 | 12:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 246 | 23:00 | 243 | 00:00 | Rampura | 240 | 00:00 | 233 | 12:00
| BSRM | 241 | 18:00 | 230 | 16:00 | Shikalbaha | 237 | 18:00 | 227 | 01:00
| Cumilla(N) | 241 | 18:00 | 233 | 15:00 | Shyampur | 242 | 03:00 | 232 | 15:00
| Fenchuganj | 244 | 00:00 | 239 | 02:00 | Siddhirganj | 243 | 00:00 | 8 | 20:00
| Ghorashal | 242 | 00:00 | 242 | 00:00 | Sirajgonj | 242 | 05:00 | 232 | 12:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 239 | 03:00 | 230 | 12:00
| GPH | 238 | 18:00 | 227 | 16:00 | Tongi | 237 | 00:00 | 226 | 15:00
| Haripur | 241 | 00:00 | 234 | 12:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 137 | 01:00 | 131 | 12:00 | Lalbag | 139 | 05:00 | 132 | 15:00
| Agargaon | 143 | 05:00 | 136 | 12:00 | Lalmonirhat | 132 | 04:00 | 122 | 08:00
| Agrabad | 139 | 09:00 | 132 | 16:00 | Madanganj | 139 | 03:00 | 134 | 10:00
| AKS | 136 | 07:00 | 132 | 15:00 | Madaripur | 137 | 06:00 | 132 | 12:00
| Aminbazar | 141 | 01:00 | 132 | 16:00 | Madartek | 137 | 02:00 | 130 | 12:00
| Amnura | 137 | 03:00 | 130 | 09:00 | Madunaghat | 140 | 18:00 | 132 | 15:00
| Ashuganj | 143 | 03:00 | 140 | 08:00 | Magura | 139 | 00:00 | 129 | 12:00
| Bagerhat | 135 | 01:00 | 126 | 12:00 | Mahasthangarh | 136 | 03:00 | 127 | 09:00
| Bakulia | 139 | 09:00 | 132 | 15:00 | Manikganj | 138 | 10:00 | 130 | 15:00
| Banani | 142 | 00:00 | 135 | 12:00 | Maniknagar | 136 | 00:00 | 131 | 12:00
| Bangabhaban | 136 | 00:00 | 131 | 12:00 | Matarbari | 132 | 10:00 | 125 | 15:00
| Barapukuria | 135 | 00:00 | 128 | 09:00 | Matuail | 139 | 03:00 | 134.1 | 15:00
| Barguna | 137 | 01:00 | 134 | 12:00 | Millgate | 142 | 02:00 | 134 | 16:00
| Barishal | 140 | 00:00 | 132 | 11:00 | Mirpur | 140 | 01:00 | 131 | 16:00
| Barishal-230 | 140 | 02:00 | 136 | 12:00 | Mirzapur | 138 | 05:00 | 132 | 07:00
| Baroaulia | 140 | 18:00 | 133 | 17:00 | Mithapukur | 135 | 03:00 | 124 | 07:00
| Baroirhat | 140 | 18:00 | 130 | 16:00 | MI_Cement | 140 | 04:00 | 134 | 12:00
| Bashundhara | 142 | 02:00 | 132 | 12:00 | Modern | 138 | 00:00 | 132 | 16:00
| BashundharaCement | 139 | 03:00 | 134 | 10:00 | Mogbazar | 140 | 04:00 | 15 | 08:00
| Beanibazar | 134 | 00:00 | 131 | 15:00 | Mongla | 134 | 00:00 | 126 | 12:00
| Benapole | 137 | 02:00 | 125 | 12:00 | Motijheel | 136 | 00:00 | 131 | 12:00
| Bhaluka | 134 | 00:00 | 129 | 12:00 | Munshiganj | 139 | 04:00 | 134 | 12:00
| Bhandaria | 136 | 00:00 | 132 | 12:00 | Mymensingh | 137 | 10:00 | 126 | 12:00
| Bhangura | 141 | 02:00 | 132 | 12:00 | Naogaon | 135 | 02:00 | 123 | 12:00
| Bheramara | 139 | 03:00 | 129 | 12:00 | Narail | 140 | 02:00 | 127 | 13:00
| Bheramara(GK) | 137 | 00:00 | 130 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 131 | 17:00 | 126 | 12:00 | Narshingdi | 136 | 06:00 | 126 | 11:00
| Bog-Sherpur | 140 | 04:00 | 128 | 12:00 | Natore | 138 | 03:00 | 129 | 12:00
| Bogura | 137 | 05:00 | 128 | 12:00 | Nawabganj | 139 | 05:00 | 131 | 16:00
| Bogura-230 | 138 | 04:00 | 129 | 09:00 | Netrakona | 136 | 09:00 | 125 | 07:00
| Brahmanbaria | 135 | 01:00 | 130 | 12:00 | New | 142 | 00:00 | 135 | 15:00
| Cantonment | 142 | 01:00 | 136 | 12:00 | Niamatpur | 134 | 03:00 | 121 | 12:00
| Chandpur | 141 | 18:00 | 128 | 16:00 | Noapara | 137 | 04:00 | 127 | 12:00
| Chandraghona | 140 | 18:00 | 134 | 17:00 | Pabna | 140 | 02:00 | 131 | 12:00
| Chapai | 138 | 04:00 | 131 | 11:00 | Palashbari | 134 | 05:00 | 124 | 08:00
| Charsaidpur | 140 | 03:00 | 134 | 12:00 | Panchagarh | 133 | 20:00 | 116 | 10:00
| Chauddagram | 141 | 18:00 | 133 | 15:00 | Patuakhali | 136 | 00:00 | 133 | 07:00
| Chhatak | 135 | 00:00 | 131 | 18:00 | Payra | 138 | 03:00 | 135 | 12:00
| Chowmuhani | 140 | 18:00 | 128 | 15:00 | PHP | 139 | 18:00 | 130 | 15:00
| Chuadanga | 139 | 04:00 | 126 | 12:00 | Postogola | 140 | 00:00 | 135 | 12:00
| Coxsbazar | 130 | 02:00 | 125 | 15:00 | Purbachal | 143 | 05:00 | 132 | 12:00
| Cumilla(N) | 143 | 18:00 | 136 | 15:00 | Purbasadipur | 131 | 00:00 | 118 | 09:00
| Cumilla(S) | 143 | 18:00 | 129 | 13:00 | Rahanpur | 138 | 02:00 | 133 | 12:00
| Daudkandi | 139 | 03:00 | 133 | 15:00 | Rahim | 139 | 03:00 | 135 | 12:00
| Dhaka | 137 | 00:00 | 132 | 12:00 | Rajbari | 138 | 05:00 | 130 | 12:00
| Dhamrai | 137 | 00:00 | 131 | 15:00 | Rajendrapur | 139 | 11:00 | 132 | 08:00
| Dhanmondi | 140.5 | 06:00 | 135.5 | 12:00 | Rajshahi | 138 | 03:00 | 129 | 12:00
| Dohazari | 135 | 00:00 | 132 | 13:00 | Rajshahi-230 | 138 | 03:00 | 129 | 12:00
| Faridpur | 137 | 06:00 | 131 | 12:00 | Ramganj | 139 | 18:00 | 129 | 15:00
| Fatullah | 140 | 01:00 | 135 | 12:00 | Rampur | 138 | 01:00 | 133 | 15:00
| Fenchuganj | 140 | 00:00 | 134 | 13:00 | Rampura | 137 | 00:00 | 131 | 12:00
| Feni | 139 | 18:30 | 130 | 15:00 | Rangamati | 139 | 14:00 | 134 | 15:00
| Ghorashal | 145 | 20:00 | 138 | 13:00 | Rangpur | 132 | 00:00 | 123 | 11:00
| Goalpara | 138 | 03:00 | 129 | 12:00 | Ruppur | 141 | 02:00 | 131 | 12:00
| Gollamari | 137 | 00:00 | 128 | 12:00 | Saidpur | 132 | 05:00 | 122 | 08:00
| Gopalganj | 136 | 01:00 | 129 | 12:00 | Satkhira | 136 | 01:00 | 126 | 08:00
| Gopalganj-400 | 135 | 00:00 | 131 | 12:00 | Satmasjid | 142 | 05:00 | 136 | 15:00
| Gulshan | 137 | 00:00 | 132 | 12:00 | Savar | 139 | 00:00 | 129 | 16:00
| Halishahar | 139 | 09:00 | 132 | 15:00 | SevenRings | 145 | 05:00 | 139 | 12:00
| Haripur | 139 | 03:00 | 135 | 12:00 | ShahCement | 140 | 03:00 | 134 | 12:00
| HaripurSBU | 139 | 03:00 | 135 | 12:00 | Shahjadpur | 143 | 02:00 | 135 | 12:00
| Hasnabad | 140 | 01:00 | 135 | 13:00 | Shahjibazar | 137 | 05:00 | 131 | 11:00
| Hathazari | 141 | 18:00 | 135 | 16:00 | Shahmirpur | 140 | 09:00 | 132 | 15:00
| Ishurdi | 142 | 05:00 | 132 | 12:00 | Shariatpur | 136 | 03:00 | 131 | 12:00
| Jaldhaka | 131 | 00:00 | 119 | 09:00 | Sherpur | 132 | 09:00 | 120 | 07:00
| Jamalpur | 134 | 10:00 | 123 | 23:00 | Shikalbaha | 128 | 10:00 | 121 | 16:00
| Jashore | 137 | 02:00 | 126 | 12:00 | Shikalbaha-230 | 140 | 10:00 | 133 | 16:00
| Jhenaidah | 140 | 04:00 | 130 | 12:00 | Shitalakhya | 140 | 04:00 | 134 | 12:00
| Jhenaidah-230 | 141 | 01:00 | 130 | 13:00 | Sholosohor | 138 | 03:00 | 132 | 16:00
| Joydebpur | 142 | 02:00 | 131 | 15:00 | Shyampur | 137 | 00:00 | 133 | 14:00
| Joypurhat | 135 | 06:00 | 122 | 12:00 | Shyampur-230 | 140 | 03:00 | 104 | 06:00
| Juldah | 140 | 10:00 | 132 | 15:00 | Siddhirganj | 140 | 04:00 | 135 | 12:00
| Kabirpur | 139 | 09:00 | 132 | 12:00 | Sirajganj | 138 | 02:00 | 128 | 12:00
| Kachua | 140 | 10:00 | 130 | 16:00 | Sonargaon | 138 | 00:00 | 133 | 11:00
| Kaliakoir | 141 | 05:00 | 13 | 08:00 | Sreemongol | 137 | 06:00 | 132 | 17:00
| Kallyanpur | 136 | 03:00 | 131 | 12:00 | Sreepur | 137 | 05:00 | 131 | 12:00
| Kalurghat | 139 | 03:00 | 134 | 15:00 | Srinagar | 139 | 03:00 | 132 | 12:00
| Kamrangirchar | 138 | 00:00 | 131 | 11:00 | SSM | 142 | 18:00 | 135 | 17:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 133 | 00:00 | 130 | 11:00
| Kazla | 136 | 02:00 | 131 | 12:00 | Sylhet | 134 | 00:00 | 133 | 11:00
| Keranigonj | 139 | 05:00 | 132 | 15:00 | Sylhet-132 | 134 | 00:00 | 132 | 11:00
| Khagrachori | 139 | 18:00 | 133 | 15:00 | Tangail | 136 | 09:00 | 130 | 08:00
| Khulna | 136 | 00:00 | 127 | 13:00 | Thakurgaon | 132 | 00:00 | 116 | 10:00
| Khulna(S) | 137 | 01:00 | 128 | 12:00 | TK | 140 | 10:00 | 131 | 16:00
| Khulshi | 138 | 09:00 | 131 | 16:00 | Tongi | 141 | 00:00 | 136 | 11:00
| Kishoreganj | 137 | 00:00 | 131 | 12:00 | Ullahpara | 140 | 00:00 | 131 | 12:00
| Kodda | 141 | 03:00 | 130 | 08:00 | Ullon | 137 | 00:00 | 132 | 12:00
| KSRM | 139 | 14:00 | 133 | 12:00 | Uttara | 141 | 03:00 | 14 | 02:00
| Kulaura | 137 | 00:00 | 135 | 11:00 | UttaraNew | 142 | 02:00 | 134 | 15:00
| Kurigram | 132 | 05:00 | 120 | 08:00 | Zigatola | 139 | 05:00 | 132 | 13:00
| Kushtia | 139 | 03:00 | 130 | 12:00

## L-Curve
Date | 2024-01-06
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 270 | 4253 | 2942 | 7195 |  |  |  | QF-LDC-11
0:30 | 305 | 4259 | 2869.5 | 7128.5 | Date: | 2024-01-06
1:00 | 340 | 4265 | 2797 | 7062
1:30 | 330 | 4166 | 2715 | 6881
2:00 | 320 | 4067 | 2633 | 6700
2:30 | 300 | 3968.5 | 2563.5 | 6532 | [5 empty] | Gen. at Eve. Peak | 9113 | 9113 MW (19:00 )
3:00 | 280 | 3870 | 2494 | 6364 | [6 empty] | 19:00
3:30 | 275 | 3857.5 | 2457.5 | 6315 | [5 empty] | Gen. at Day Peak | 8712 | 8712 MW (12:00 )
4:00 | 270 | 3845 | 2421 | 6266 | [6 empty] | 12:00
4:30 | 250 | 3802 | 2405.5 | 6207.5 | [5 empty] | Highest Generation | 9219
5:00 | 230 | 3759 | 2390 | 6149 | [6 empty] | 13:00
5:30 | 210 | 3910.5 | 2423 | 6333.5
6:00 | 190 | 4062 | 2456 | 6518
6:30 | 160 | 4122.5 | 2536.5 | 6659
7:00 | 130 | 4183 | 2617 | 6800
7:30 | 145 | 4302 | 2952.5 | 7254.5
8:00 | 160 | 4421 | 3288 | 7709
8:30 | 190 | 4540.5 | 3412.5 | 7953
9:00 | 220 | 4660 | 3537 | 8197
9:30 | 275 | 4746.5 | 3448.5 | 8195
10:00 | 330 | 4833 | 3360 | 8193
10:30 | 375 | 4854.5 | 3324.5 | 8179
11:00 | 420 | 4876 | 3289 | 8165
11:30 | 420 | 4997.5 | 3441 | 8438.5
12:00 | 420 | 5119 | 3593 | 8712
12:30 | 395 | 5312 | 3653.5 | 8965.5
13:00 | 370 | 5505 | 3714 | 9219
13:30 | 485 | 5300 | 3688 | 8988
14:00 | 600 | 5095 | 3662 | 8757
14:30 | 610 | 4867 | 3550 | 8417
15:00 | 620 | 4639 | 3438 | 8077
15:30 | 535 | 4572 | 3283 | 7855
16:00 | 450 | 4505 | 3128 | 7633
16:30 | 425 | 4556 | 3163 | 7719
17:00 | 400 | 4607 | 3198 | 7805
17:30 | 295 | 4927.5 | 3389 | 8316.5
18:00 | 190 | 5248 | 3580 | 8828
18:30 | 195 | 5365 | 3605.5 | 8970.5
19:00 | 200 | 5482 | 3631 | 9113
19:30 | 190 | 5360 | 3641 | 9001
20:00 | 170 | 5308 | 3546 | 8854
20:30 | 210 | 5269 | 3579.5 | 8848.5
21:00 | 250 | 5230 | 3613 | 8843
21:30 | 370 | 4998.5 | 3590.5 | 8589
22:00 | 490 | 4767 | 3568 | 8335 |  |  |  |  | Page 6 of 7
22:30 | 490 | 4568 | 3450.5 | 8018.5
23:00 | 490 | 4369 | 3333 | 7702
23:30 | 380 | 4311 | 3137.5 | 7448.5
24:00 | 270 | 4253 | 2942 | 7195
9113 MW (19:00 )
8712 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-01-06 |  | Energy |  | 191181157
QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 2253 | 713 | 1765 | 0 | 17 | 2278 | 81 | 0 | 0 | 76 | 0 | 12 | 0
0:30 | 2240 | 671.5 | 1766.5 | 0 | 8.5 | 2260 | 83.5 | 0 | 0 | 80 | 0 | 18.5 | 0 |  | Date: | 43835
1:00 | 2227 | 630 | 1768 | 0 | 0 | 2242 | 86 | 0 | 0 | 84 | 0 | 25 | 0
1:30 | 2203.5 | 553 | 1757.5 | 0 | 0 | 2174.5 | 86 | 0 | 0 | 81 | 0 | 25.5 | 0 | [8 empty] | Total Energy | 191.1812 | 191.1812 | Total Energy Gen 191.181 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 191.181 MKWHr
2:00 | 2180 | 476 | 1747 | 0 | 0 | 2107 | 86 | 0 | 0 | 78 | 0 | 26 | 0 | [8 empty] | Energy not Served | 0 | 0
2:30 | 2149 | 476 | 1651.5 | 0 | 0 | 2066.5 | 86 | 0 | 0 | 77 | 0 | 26 | 0 | [8 empty] | Energy Requirement | 191.1812 | 191.1812
3:00 | 2118 | 476 | 1556 | 0 | 0 | 2026 | 86 | 0 | 0 | 76 | 0 | 26 | 0
3:30 | 2102.5 | 476 | 1545 | 0 | 0 | 2006 | 86 | 0 | 0 | 74 | 0 | 25.5 | 0 | [7 empty] | Shortage
4:00 | 2087 | 476 | 1534 | 0 | 0 | 1986 | 86 | 0 | 0 | 72 | 0 | 25 | 0
4:30 | 2045 | 476 | 1538 | 0 | 0 | 1969.5 | 86 | 0 | 0 | 70 | 0 | 23 | 0
5:00 | 2003 | 476 | 1542 | 0 | 0 | 1953 | 86 | 0 | 0 | 68 | 0 | 21 | 0
5:30 | 2059.5 | 476 | 1671.5 | 0 | 0 | 1949.5 | 86 | 0 | 0 | 71 | 0 | 20 | 0
6:00 | 2116 | 476 | 1801 | 0 | 0 | 1946 | 86 | 0 | 0 | 74 | 0 | 19 | 0
6:30 | 2141 | 476.5 | 1832 | 0 | 0 | 2026 | 86 | 0 | 0 | 75 | 3 | 19.5 | 0 | [6 empty] | Coal
7:00 | 2166 | 477 | 1863 | 0 | 0 | 2106 | 86 | 0 | 0 | 76 | 6 | 20 | 0
7:30 | 2213.5 | 477 | 1925 | 0 | 38.5 | 2370.5 | 86 | 0 | 2.5 | 79 | 42 | 20.5 | 0 | [5 empty] | Oil
8:00 | 2261 | 477 | 1987 | 0 | 77 | 2635 | 86 | 0 | 5 | 82 | 78 | 21 | 0
8:30 | 2194 | 494.5 | 2005.5 | 0 | 200.5 | 2682.5 | 86 | 0 | 55 | 82 | 136 | 17 | 0
9:00 | 2127 | 512 | 2024 | 0 | 324 | 2730 | 86 | 0 | 105 | 82 | 194 | 13 | 0
9:30 | 2099.5 | 528 | 1993.5 | 0 | 392.5 | 2647.5 | 86 | 0 | 123.5 | 86 | 230 | 8.5 | 0
10:00 | 2072 | 544 | 1963 | 0 | 461 | 2565 | 86 | 0 | 142 | 90 | 266 | 4 | 0
10:30 | 2062 | 613.5 | 1909 | 0 | 495.5 | 2458 | 86 | 0 | 166.5 | 91 | 294.5 | 3 | 0
11:00 | 2052 | 683 | 1855 | 0 | 530 | 2351 | 86 | 0 | 191 | 92 | 323 | 2 | 0
11:30 | 2089.5 | 745 | 1927 | 0 | 559 | 2381 | 83.5 | 0 | 241 | 93 | 318 | 1.5 | 0
12:00 | 2127 | 807 | 1999 | 0 | 588 | 2411 | 81 | 0 | 291 | 94 | 313 | 1 | 0
12:30 | 2153.5 | 807 | 1963.5 | 0 | 747.5 | 2483.5 | 81 | 0 | 309.5 | 99 | 320.5 | 0.5 | 0
13:00 | 2180 | 807 | 1928 | 0 | 907 | 2556 | 81 | 0 | 328 | 104 | 328 | 0 | 0
13:30 | 2180 | 807 | 1928 | 0 | 907 | 2556 | 81 | 0 | 328 | 104 | 328 | 0 | 0
14:00 | 2180 | 807 | 1928 | 0 | 907 | 2556 | 81 | 0 | 328 | 104 | 328 | 0 | 0
14:30 | 2237 | 807 | 1873.5 | 0 | 546.5 | 2511.5 | 67 | 0 | 260.5 | 100 | 245 | 0 | 0
15:00 | 2294 | 807 | 1819 | 0 | 186 | 2467 | 53 | 0 | 193 | 96 | 162 | 0 | 0
15:30 | 2302 | 807 | 1783.5 | 0 | 178 | 2384 | 67 | 0 | 120.5 | 93 | 117.5 | 2.5 | 0
16:00 | 2310 | 807 | 1748 | 0 | 170 | 2301 | 81 | 0 | 48 | 90 | 73 | 5 | 0
16:30 | 2268.5 | 807 | 1820.5 | 0 | 215.5 | 2306 | 81 | 0 | 84.5 | 88 | 42 | 6 | 0
17:00 | 2227 | 807 | 1893 | 0 | 261 | 2311 | 81 | 0 | 121 | 86 | 11 | 7 | 0
17:30 | 2182 | 845 | 1809 | 0 | 660.5 | 2419.5 | 81 | 0 | 214 | 90 | 5.5 | 10 | 0
18:00 | 2137 | 883 | 1725 | 0 | 1060 | 2528 | 81 | 0 | 307 | 94 | 0 | 13 | 0
18:30 | 2172.5 | 836 | 1767.5 | 0 | 1124.5 | 2630 | 81 | 0 | 255 | 93 | 0 | 11 | 0
19:00 | 2208 | 789 | 1810 | 0 | 1189 | 2732 | 81 | 0 | 203 | 92 | 0 | 9 | 0
19:30 | 2232 | 789 | 1827 | 0 | 992 | 2772 | 81 | 0 | 206 | 92 | 0 | 10 | 0
20:00 | 2221 | 789 | 1847 | 0 | 924 | 2767 | 81 | 0 | 126 | 90 | 0 | 9 | 0
20:30 | 2256.5 | 846 | 1975 | 0 | 759.5 | 2742.5 | 81 | 0 | 89 | 90 | 0 | 9 | 0
21:00 | 2292 | 903 | 2103 | 0 | 595 | 2718 | 81 | 0 | 52 | 90 | 0 | 9 | 0
21:30 | 2303.5 | 902.5 | 2018 | 0 | 461 | 2697 | 81 | 0 | 26 | 89 | 0 | 11 | 0
22:00 | 2315 | 902 | 1933 | 0 | 327 | 2676 | 81 | 0 | 0 | 88 | 0 | 13 | 0
22:30 | 2276 | 902 | 1901.5 | 0 | 179.5 | 2578 | 81 | 0 | 0 | 86 | 0 | 14.5 | 0
23:00 | 2237 | 902 | 1870 | 0 | 32 | 2480 | 81 | 0 | 0 | 84 | 0 | 16 | 0
23:30 | 2245 | 807.5 | 1817.5 | 0 | 24.5 | 2379 | 81 | 0 | 0 | 80 | 0 | 14 | 0 |  | Max Temp. in Dhaka |  | 26.7°C
24:00 | 2253 | 713 | 1765 | 0 | 17 | 2278 | 81 | 0 | 0 | 76 | 0 | 12 | 0
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 191.181 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 191.181 MKWHr
Note on W13: Author:

## Generation
g | 2024-01-06
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 18 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1080600
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 904000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [7 empty] | 1 | 7 | 8 | 8 | 8 | 8 | 8 |  |  |  | 13 |  | 17 | 17 | 17 |  |  |  |  | 117934
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 8 | 14 | 17 | 19 | 20 | 19 | 16 | 12 | 7 | 1 | [9 empty] | 134865
6 | Sikalbaha 225MW CCPP (Gas) | 125 | 126 | 126 | 126 | 126 | 75 | 25 | 25 | 27 | 31 | 35 | 33 | 58 | 86 | 115 | 126 | 35 | 41 |  | 65 | 84 | 83 | 83 | 67 | 95 | 120 | 1842160
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [9 empty] | 17 | 17 | 34 | 34 | 34 |  |  |  | 17 |  | 17 | 17 |  |  |  |  | 0 | 162697
12 | Hathazari 100 MW peaking PP | [9 empty] | 8 | 32 | 32 | 35 | 57 | 64 | [11 empty] | 204048
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [7 empty] | 3 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 6 |  | 17 | 17 | 17 |  |  |  | 0 | 184836
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [10 empty] | 25 | 25 | 25 | 18 | 0 | [10 empty] | 0 | 113680
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [10 empty] | 30 | 45 | 55 | 45 |  |  |  | 30 | [7 empty] | 0 | 313636
19 | Ashuganj 195 MW PP (APSCL-United) | [10 empty] | 8 | 8 | [13 empty] | 0 | 16727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4362750
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 272 | 275 | 276 | 277 | 276 | 276 | 277 | 275 | 280 | 280 | 280 | 270 | 270 | 270 | 270 | 270 | 270 | 300 |  | 390 | 430 | 430 | 420 | 420 | 420 | 418 | 7423635
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 38 | 45 | 44 | 44 | 45 | 45 | 45 | 48 | 43 | 43 | 48 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 772704
33 | Ashuganj 225 MW CCPP | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 97 | 97 | 70 | 76 | 52 | 71 | 73 | 80 | 79 | 74 |  | 71 | 71 | 71 | 71 | 71 | 80 | 86 | 2068000
34 | Ashuganj 450 MW CCPP(South) | 180 | 180 | 180 | 180 | 180 | 275 | 270 | 280 | 200 | 200 | 215 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 4488000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 310 | 330 | 360 | 290 | 280 | 310 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 7298000
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | [10 empty] | 1 | 9 | 35 | 23 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 5 | 250080
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 361 | 361 | 360 | 360 | 321 | 333 | 364 | 364 | 382 | 400 | 375 | 385 | 400 | 400 | 400 | 401 | 384 | 330 |  | 333 | 332 | 331 | 354 | 404 | 378 | 361 | 9014400
| Meghnaghat Unique power | 295 | 303 | 300 | 301 | 305 | 300 | 300 | 285 | 283 | 306 | 305 | 306 | 288 | 301 | 305 | 308 | 300 | 301 |  | 299 | 301 | 302 | 304 | 291 | 307 | 280 | 6741818
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 400 | 320 | 320 | 320 | 370 | 420 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 400 | 400 | 330 |  | 360 | 360 | 360 | 450 | 350 | 350 | 350 | 9300000
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 77 | 77 | 77 | 77 | 77 | 77 | 71 | 69 | 35 | 35 | 35 | 34 | 35 | 34 | 35 | 35 | 36 | 72 |  | 75 | 76 | 75 | 75 | 74 | 87 | 100 | 1399680
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 9 | 22 | 32 | 37 | 47 | 42 | 32 | 24 | 10 | 1 | [9 empty] | 254590
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 42 | 43 | 1013000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 62 | 62 | 63 | 63 | 40 | 40 | 61 | 61 | 40 | 59 | 58 | 58 | 59 |  | 60 | 60 | 60 | 60 | 61 | 61 | 60 | 1270944
48 | Shahjibazar 86 MW PP (Shahjibazar) | 50 | 5 | 5 | 5 | 5 | 50 | 50 | 50 | 50 | 50 | 10 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 5 | 5 | 913920
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 212 | 212 | 211 | 209 | 208 | 209 | 209 | 207 | 206 |  | 209 | 209 | 209 | 209 | 208 | 208 | 208 | 5259080
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 |  |  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 201240
54 | Hobiganj 11 MW PP Cofidence-E | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 8 | 8 | 8 | 193440
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 5 | 5 |  | 5 | 50 | 53 | 53 | 50 | 10 | 10 | 47 | 47 | 47 | 47 | 50 | 24 | 45 |  | 53 | 53 | 53 | 53 | 53 | 10 | 5 | 863400
56 | Shahjahanulla 25 MW PP | 16 | [5 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 312288
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 285 | 280 | 290 | 295 | 290 | 290 | 310 | 300 | 290 | 295 | 315 | 300 | 275 | 275 | 285 | 305 | 300 |  | 295 | 300 | 295 | 300 | 300 | 290 | 285 | 7216000
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 10 | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 64497
59 | Tangail Palli Power Gen 22 MW | [7 empty] | 1 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 |  | 0 | 92160
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 415200
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 84 | 78 | 76 | 72 | 68 | 74 | 76 | 82 | 82 | 90 | 92 | 94 | 104 | 104 | 96 | 90 | 86 | 94 |  | 92 | 92 | 90 | 90 | 88 | 84 | 76 | 2069760
64 | Malancha, Ctg. EPZ (United) | 33 | 33 | 30 | 33 | 28 | 40 | 41 | 33 | 25 | 37 | 22 | 16 | 11 | 6 | 6 | 13 | 20 | 26 |  | 30 | 30 | 33 | 40 | 27 | 38 | 42 | 690720
65 | Feni 22 MW PP (Doreen) | 18 | 18 |  |  |  |  | 13 | 16 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 362016
66 | Feni 11 MW PP (Doreen) | 7 | [5 empty] | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 8 | 8 | 8 | 8 |  | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 153540
67 | Jangalia 33 MW PP (Summit) | 33 | 8 |  |  |  | 6 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 30 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 627300
68 | Cumilla 25 MW PP (Summit) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 16 | 10 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 315070
69 | Summit Ashulia | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 432000
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 0 | 14 | 22 | 22 | 22 | 22 | 18 |  | 22 | 22 | 22 | 22 | 15 | 18 | 22 | 455760
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 17 | 25 | 25 | 17 | 17 | 510400
72 | Rupganj 33 MW PP(Summit) | 21 | 21 | 21 | 21 | 21 | 25 | 25 | 24 | 24 | 25 | 25 | 25 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 24 | 25 | 534500
73 | Ghorashal 108 MW PP (Regent) | [5 empty] | 14 | 14 | 37 | 37 | 48 | 62 | 67 | 65 | 22 | 14 | 14 | 73 | 73 |  | 73 | 73 | 73 | 73 | 73 | 72 | 72 | 886545
| Feni Lanka Power | [8 empty] | 38 | 52 | 52 | 62 | 114 | 34 |  |  | 13 | 58 |  | 17 | [5 empty] | 0 | 448020
| Chowmuhani 113 MW | [8 empty] | 9 | 9 | 9 | 9 | 9 | 9 |  |  |  | 44 |  | 114 | 114 | 118 | 109 | 59 |  |  | 525840
| Manikgonj 162MW PP(MPGL) | [8 empty] | 17 | 35 | 17 | [8 empty] | 35 | [5 empty] | 0 | 89280
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [9 empty] | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 17 | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 127680
79 | Kodda 150 MW PP | [8 empty] | 70 | 82 | 82 | 115 | 149 | 64 | 48 | 48 | 115 | 149 |  | 98 | 98 | 98 | 48 |  |  | 0 | 1237920
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [8 empty] | 4 | 37 | 52 | 52 | 52 | 16 |  |  | 2 | 37 |  | 16 | [6 empty] | 328627
| Gazipur 100 MW PP | [8 empty] | 14 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 105 |  | 105 | 105 | 105 | 88 |  |  |  | 574080
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 1 | 2 | 5 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 21723
| Jodiac Power | [9 empty] | 0 | 17 | 17 | 17 |  |  |  |  | 9 | [7 empty] | 0 | 78133
| Karnaphuli Power Ltd. | [8 empty] | 5 | 17 | 17 | 17 | 17 | 17 |  |  |  | 6 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 198220
82 | Madanganj 102 PP(Summit) | [12 empty] | 6 | 34 | 7 | [11 empty] | 35038
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [12 empty] | 11 | 25 | [12 empty] | 34764
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | [12 empty] | 1 | 9 | [11 empty] | 0 | 13440
| Meghnaghat 104 MW PP (OPCL) | [8 empty] | 16 | 25 | 34 | 42 | 53 | 53 | 17 | 17 | 17 | 50 |  | 68 | 17 | 17 |  |  |  |  | 415680
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [12 empty] | 25 | 25 | [11 empty] | 0 | 39480
92 | Fenchuganj 44 MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | [5 empty] | 1 | 10 | 28 | 51 | 51 | 51 | 51 | 10 | 10 | 10 | 10 | 10 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 5 | 776752
94 | Gagnagar 102 MW PP (Digital Power) | [9 empty] | 10 | 16 | 16 | 66 | 32 |  |  |  | 16 | [7 empty] | 0 | 169632
95 | Patenga 50MW PP (Baraka) | [8 empty] | 6 | 6 | 6 | 6 | 6 | 6 |  |  |  | 12 |  | 19 | 20 | 20 | 20 | 20 |  | 0 | 141120
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 | [6 empty] | 13 |  | 32 | 32 | 34 | 32 | 23 |  | 0 | 138240
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [11 empty] | 5 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 205379
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 35 |  | 35 | 17 | 17 |  |  |  | 0 | 66984
101 | Kushiara 163 MW CCPP (KP) | 120 | 163 | 120 | 120 | 120 | 140 | 140 | 140 | 163 | 163 | 120 | 120 | 163 | 120 | 163 | 120 | 163 | 120 |  | 120 | 120 | 150 | 163 | 120 | 120 | 120 | 3554754
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 |  | 1 | 1 | 0 | [9 empty] | 10400
103 | Kamalaghat 54 MW PP(Banco Energy) | [12 empty] | 17 | 17 | 17 | [10 empty] | 0 | 51120
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [7 empty] | 7 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 28 | 19 | 28 |  | 28 | 28 | 28 | 28 | 19 |  | 0 | 316800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [9 empty] | 15 | 17 | 17 | 17 | 29 | 20 | 17 | 17 | 43 |  | 43 | 43 | 44 | 35 |  |  | 0 | 331344
115 | Juldah 100 MW PP Unit-3 (Acorn) | [7 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  |  |  | 12 |  | 12 | 12 | 12 | 12 |  |  | 0 | 151680
116 | Chandpur 200 MW (Desh energy) | [7 empty] | 7 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 9 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 223200
117 | Ashuganj 150 MW PP (Midland) | [7 empty] | 1 | 8 | 10 | 13 | 13 | 13 | 13 | 13 |  |  | 16 |  | 50 | 58 | 55 | 56 | 28 |  | 0 | 302763
118 | Bibiyana-III 400 MW CCPP | 353 | 353 | 318 | 290 | 245 | 240 | 238 | 239 | 239 | 239 | 244 | 334 | 400 | 353 | 415 | 415 | 402 | 365 |  | 399 | 401 | 401 | 401 | 401 | 353 | 353 | 7926000
| Jamalpur 115 MW PP (United) | [7 empty] | 10 | 56 | 56 | 56 | 59 | 59 | 59 | 45 | 45 | 59 | 79 |  | 79 | 79 | 79 | 79 | 59 |  |  | 906000
| Anwara 300 MW PP (United) | [7 empty] | 5 | 30 | 48 | 48 | 80 | 136 | 65 |  |  | 15 | 100 |  | 115 | 65 | 15 |  |  |  | 0 | 740182
| Juldah unit-2 (Acorn) | [7 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  |  |  | 12 |  | 12 | 12 | 12 | 12 | 12 |  | 0 | 152640
| Anlima Energy Ltd. | [7 empty] | 4 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 12 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 220800
| Bhairob 54.5 MW | [12 empty] | 12 |  | 2 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 192240
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 6 | 15 | 20 | 24 | 26 | 24 | 21 | 16 | 7 | 1 | [9 empty] | 161824
| Chandpur 115(Doreen) | [11 empty] | 1 | 18 | 18 |  |  |  | 17 |  | 36 | 36 | 31 | 18 | 18 |  | 0 | 178560
| Kanchan Purbachal Power Generation Ltd. | [16 empty] | 29 | 24 |  | 17 | 17 | 17 | 17 |  |  | 0 | 121680
| Mirsharai 150 MW (Oil) | [7 empty] | 5 | 35 | 35 | 35 | 35 | 35 | 35 |  |  |  | 54 |  | 17 | [5 empty] | 0 | 306109
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 25 | 26 | 26 | 25 | 21 | 19 | 20 | 21 | 13 | 4 | 2 | 1 | 0 | 0 | 0 | 5 | 7 | 13 |  | 9 | 10 | 9 | 9 | 13 | 16 | 12 | 296160
| Matarbari 2*600 MW (CPGCL) | 355 | 313 | 313 | 314 | 312 | 311 | 312 | 313 | 310 | 312 | 313 | 311 | 308 | 310 | 311 | 313 | 310 | 310 |  | 310 | 311 | 312 | 312 | 309 | 311 | 312 | 7716363
120 | Eastern Zone Total | 4265 | 4067 | 3870 | 3845 | 3759 | 4062 | 4183 | 4421 | 4660 | 4833 | 4876 | 5119 | 5505 | 5095 | 4639 | 4505 | 4607 | 5248 |  | 5482 | 5360 | 5308 | 5230 | 4767 | 4369 | 4253 | 112828271
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [25 empty] | 0 | 0
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 6 | 34 | [8 empty] | 31200
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [17 empty] | 10 | [7 empty] | 0 | 19200
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 1 | 16 | 37 | 56 | 67 | 69 | 63 | 53 | 36 | 17 | 3 | [9 empty] | 424800
131 | Rampal 1320 MW (BIFPCL) |  | 164 | 345 | 351 | 355 | 356 | 356 | 354 | 353 | 355 | 324 | 330 | 316 | 331 | 331 | 330 | 329 | 331 |  | 329 | 331 | 332 | 330 | 333 | 327 | 330 | 7447273
132 | United Payra Power Ltd. | [17 empty] | 18 |  | 35 | 35 | 17 |  |  |  | 0 | 92400
133 | Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 180 | 180 | 220 | 180 | 180 | 180 | 180 | 220 | 180 |  | 180 | 180 | 180 | 200 | 200 | 200 | 200 | 4735909
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 | [7 empty] | 0 | 18624
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 260 | 212 | 150 | 150 | 150 | 150 | 150 | 266 | 271 | 180 | 140 | 140 | 180 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 4123600
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 120 | 80 | 80 | 120 | 80 | 80 | 80 | 80 | 120 | 80 |  | 80 | 80 | 80 | 120 | 120 | 80 | 80 | 2157000
140 | Bhola 33 MW PP (Venture) | 17 | 16 | 16 | 15 | 14 | 16 | 15 | 14 | 15 | 15 | 14 | 15 | 17 | 16 | 14 | 12 | 12 | 19 |  | 19 | 19 | 20 | 20 | 20 | 18 | 17 | 379400
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 630 | 476 | 476 | 476 | 476 | 476 | 477 | 477 | 512 | 544 | 683 | 807 | 807 | 807 | 807 | 807 | 807 | 883 |  | 789 | 789 | 789 | 903 | 902 | 902 | 713 | 16686545
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 560 | 450 | 350 | 300 | 270 | 260 | 310 | 510 | 580 | 510 | 450 | 450 | 550 | 500 | 470 | 420 | 430 | 520 |  | 622 | 622 | 622 | 580 | 540 | 470 | 420 | 12472200
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4131600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [13 empty] | 26 | 31 | [11 empty] | 51020
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 2 | 3 | 4 | 4 | 4 | 4 | 2 | 0 | 0 | [9 empty] | 26040
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 270 | 357 | 300 | 270 | 270 | 340 | 340 | 397 | 370 | 353 | 317 | 315 | 302 | 287 | 275 | 276 | 286 | 200 |  | 250 | 260 | 250 | 369 | 368 | 379 | 379 | 7554000
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 5 |  | 5 | 5 | 10 | 4 |  |  |  | 26183
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 5 | 5 | 169668
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [12 empty] | 24 | 8 | [12 empty] | 24793
167 | Katakhali 50 MW Peaking PP | [17 empty] | 10 |  | 28 | 48 | 18 |  |  |  |  | 48903
168 | Santahar 50 MW Peaking PP | [17 empty] | 38 |  | 38 | 38 | [5 empty] | 82136
169 | Natore 52 MW PP (Rajlanka) | [7 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  |  | 8 |  | 8 | 8 | 8 |  |  |  | 0 | 87739
170 | Chapainawabganj 100 MW Peaking PP | [11 empty] | 50 | 50 | 50 | 50 | [10 empty] | 0 | 201696
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [17 empty] | 15 | [7 empty] | 0 | 48096
172 | Confidence Power Bogura Unit-1 113 MW | [17 empty] | 35 |  | 35 | 35 | 35 |  |  |  | 0 | 96768
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [7 empty] | 6 | 6 | 6 | 5 | 6 | 6 | 33 |  |  |  | 60 |  | 67 | 48 | 49 |  |  |  | 0 | 245500
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 3 | 5 | 3 | 2 | 3 | 3 | 2 | 0 | [9 empty] | 25891
178 | Energypac Power Venture Thakurgaon Ltd. | [12 empty] | 17 | 35 |  |  |  | 40 |  | 54 | 54 | 54 |  |  |  | 0 | 231552
| Intraco Solar 30 MW | [6 empty] | 0 | 5 | 15 | 13 | 20 | 15 | 9 | 25 | 6 | 4 | 1 | [9 empty] | 122831
| Adani Power Jharkhanda Ltd | 625 | 523 | 422 | 424 | 420 | 423 | 531 | 747 | 766 | 758 | 674 | 740 | 762 | 767 | 775 | 658 | 662 | 757 |  | 771 | 768 | 761 | 766 | 764 | 642 | 488 | 15730909
178 | Teesta Solar Limited | [6 empty] | 2 | 32 | 84 | 118 | 140 | 123 | 159 | 131 | 60 | 24 | 4 | [9 empty] | 859410