## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2019-04-03 | Wednesday
|  | Date (day): | 2019-04-03 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13376 | MW |  |  | (b) At Evening Peak Hour : |  | 14302 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-04-02 | 2019-04-03 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 74 | 74 | 74 | 74
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 133 | 94 | 100 | 100 |  |  | On test.
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 50 | 100 | 100 |  |  | On test.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 120 | 120 | 120
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 380 | 220 | 240 | 300
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 69 | 40 | 78 | 78
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 105 | 12 | 108 | 108
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 353 | 320 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 0 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 350 | 313 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 405 | 340 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 92 | 92 |  | 8 | Engine problem
11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 150 | 160 | 305 | 305
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 23 | 0 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 0 | 0 | 19
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 190 | 0 | 210 | 210
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 0 | 0 | 0 |  | 217 | Under maint.
0 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
21 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 70 | 7 | 102 | 102
22 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 6 | 6 | 49 | 49
23 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
24 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 25 | 0 | 149 | 149
25 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 0 | 55 | 55
26 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 0 | 55 | 55
27 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 47 | 0 | 49 | 49 |  | 59 | Engine problem
28 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 25 | 57 | 57 |  | 23 | Engine problem
29 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 24 | 33 | 33
30 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
31 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 43 | 0 | 51 | 51
32 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
33 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 31 | 0 | 200 | 300
34 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
35 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
36 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
37 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 50 | 0 | 149 | 149
| Dhaka area Total |  |  |  |  | 6034 | 5798 | 2842 | 1892 | 4650 | 4929 | 260 | 307
38 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 105 | 110 | 110 | 70 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 100 | 100 | 100 | 80 |  | Gas shortage
39 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 16 | 16 | 16 |  | 9 | Engine problem
40 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
41 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 81 | 80 | 130 | 130 |  | 100 | Low water lavel
43 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
44 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 203 | 225 | 225 |  |  | FGMO
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under S/D
46 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 41 | 41 | 41 | 41 |  | 10 | Engine problem
47 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 9 | 50 | 72 | 72
48 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 80 | 85 | 85
49 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 10 | 78 | 78 |  | 22 | Engine problem
50 | Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 100 | 100 | 90 | 70 | 100 | 100
51 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 21 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 16 | 5 | 15
52 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 14 | 26 | 105 | 105
| Chattogram area Total |  |  |  |  | 1761 | 1681 | 780 | 868 | 1159 | 1149 | 150 | 331
53 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 110 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 80 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 55 | 100 | 100 | 34
54 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 186 | 184 | 221 | 221 |  |  | FGMO
55 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 360 | 360 | 360
56 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 360 | 360 | 360
57 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 31 | 40 | 40 | 40
58 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
59 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage
60 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 16 | 16 | 16 | 16 | 179 |  | Gas Shortage
61 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 7 | 35 | 35 |  | 16 | Gas Shortage
62 | Midland 150MW |  | HFO | IPP | 23*7.015 | 150 | 150 | 53 | 0 | 150 | 150
63 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
64 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 0 | 100 | 100 |  | 63 | ST Under maint.
66 | Chandpur Desh 200MW |  | HFO | IPP | 0 | 200 | 200 | 40 | 0 | 200 | 200
67 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 0 | 22 | 22
68 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 0 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 114 | 44 | 134 | 168
69 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 0 | 0 | 33
70 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
71 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 10 | 0 | 21 | 21
72 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1172 | 1076 | 1932 | 2149 | 575 | 79
73 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 192 | 147 | 202 | 202
74 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
75 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 7 | 87 | 87 |  | 8 | Enjgine problem
76 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 1.6 | 0 | 2 | 0
77 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 0 | 0 | 200 | 200
78 | United Jamalpur PPL |  | HFO | IPP | 115 MW | 115 | 115 | 106 | 0 | 112 | 112
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 319.6 | 174 | 623 | 621 | 0 | 8
79 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 30 | 30 | 30
80 | Fenchugonj CCPP-2 |  | Gas | PDB | !F71 | 104 | 90 | 50 | 51 | 60 | 60
81 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
82 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 266 | 150 | 330 | 330 |  |  | FGMO
83 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 45 | 0 | 51 | 51
84 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 47 | 5 | 44 | 44
85 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 8 | 8 |  | 3 | Engine problem
86 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 20 | 40 | 66 | 66 |  |  | FGMO
87 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 5 | 86 | 86
88 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 32 | 5 | 47 | 47
89 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 84 | 0 | 120 | 120
90 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 20
91 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 47 | 0 | 46 | 46
92 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 0 | 0 | 25
93 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 12 | 340 | 340 |  |  | FGMO
| Bibiyana-3 285MW |  | Gas | PDB | 285 MW | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
94 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 824 | 461 | 1391 | 1446 | 0 | 3
95 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 46
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 858 | 744 | 869 | 966
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
96 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 32 | 115 | 115
97 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 31 | 35 | 35
98 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 |  |  | Reserve
99 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 2 | 40 | 80
100 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 270 | 220 | 410 | 410
101 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 24 | 24 | 40 | 40
0 | Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
102 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 100 | 100
103 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 90 | 105 | 105
| Madhumati Power Plant |  | HFO | IPP | 100 MW | 0 | 0 | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  |  | 2223 | 2209 | 1205 | 1143 | 1714 | 1897 | 0 | 0
104 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 80 | 80 | 110 | 110
105 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 26
106 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 23 | 32 | 28 | 32
107 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 179 | 167 | 150 | 190
108 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 95 | 97 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 377 | 376 | 383 | 453 | 0 | 0
109 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage.
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage.
110 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
111 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 54
112 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 43 | 43 |  | 10 | Engine problem
113 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
114 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
115 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 193 | 172 | 200 | 200 |  |  | FGMO
116 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 194 | 132 | 225 | 225 |  |  | FGMO
117 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
118 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282 | 282 | 282 | 418 | 435 | 414 | 414 |  |  | ON test
119 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 30
120 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 5 | 22 | 22
121 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 15 | 3 | 17 | 17
122 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
123 | Rajlanka 52 MW |  | HFO | IPP | 52 | 52 | 52 | 0 | 8 | 43 | 43 |  | 9 | Engine problem
124 | Chapainawabganj-100 MW |  | HFO | PDB | 104 | 104 | 104 | 33 | 100 | 100 | 100
125 | Paramount Baghabari |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Reserve
| Confidence CPBL-2 |  | HFO | IPP | 113 MW | 0 | 0 | 91 | 0 | 113 | 113 |  |  | On test
| Rajshahi Area Total |  |  |  |  | 1835 | 1825 | 971 | 863 | 1278 | 1412 | 391 | 19
126 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under overhauling
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 64 | 62 | 62 | 62
127 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 149 | 149 | 149 | 125 |  | Coal shortage
128 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 17 | 17
129 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 18 | 18 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 213 | 246 | 246 | 246 | 125 | 85
| Total |  |  |  |  | 18079 | 17536 | 8703.6 | 7099 | 13376 | 14302 | 1501 | 832
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8452.2635 | 6894 | 12989.7371 | 13888.9968
A. |  | 2019-04-02 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 8721.9 | MW at | 13:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 6766.3 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 7099 | MW
3 | Day peak Generation : |  |  | 8703.6 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 6894 | MW
4 | Evening peak Generation : |  |  | 7099 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 175.0363 | MKWHr | By Solar | 0.089165 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 131.5877 | MKWHr |  | By Oil: | 17.684 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 5.189 | MKWHr |  | By Hydro: | 1.8418 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1501 | MW | Dhaka | 2717 | 2717 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 832 | MW | Chittagong | 1002 | 1002 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2333 | MW | Khulna | 930 | 930 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1090.47 | MMCFD |  |  | Rajshahi | 777 | 777 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 88937283.08 | ii) Oil : | Taka | 140787669.4 | Comilla | 175 | 175 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 23445309.93 | Total | Taka | 253170262.41 | Mymensingh | 369 | 369 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.1175 | MKWHr. | Sylhet | 139 | 139 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -100 | MW (E to W) at | 21:00 | hrs | Barisal | 254 | 254 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -190 | MW at | 20:00 | hrs | Rangpur | 531 | 531 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 32° C |  |  | Total | 6894 | 6894 |  | 0
B. |  | 2019-04-03 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 30.9° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14302 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8000 | MW
4 | Reserve(Generation end) |  |  |  | 4402 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 198.6791 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5674.2 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 16.7535 | MKWHr. | ii) HVDC Flow at Peak Time |  | 744 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.8912 | MKWHr. | iii) Maximum HVDC Flow : |  | 858 | MW at | 9:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 85.5 |  | (b) Today: | 85.32 |  | (c) Rule Curve: |  | 87.6
.

## YesterdayGen
2019-04-02
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285MW | United Jamalpur PPL | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | Paramount Baghabari | Confidence CPBL-2 | Madhumati Power Plant | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 74 | 134 | 0 | 110 | 203 | 107 | 40 | 340 | 281 | 0 | 0 | 330 | 150 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 35 | 17 | 17 | 19 | 25 | 32 | 28 | 33 | 33 | 0 | 79 | 0 | 110 | 150 | 0 | 215 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 10 | 19 | 50 | 19 | 37 | 110 | 80 | 0 | 280 | 0 | 194 | 16 | 100 | 40 | 5 | 5 | 7 | 0 | 0 | 0 | 22 | 5 | 0 | 13 | 104 | 212 | 0 | 20 | 0 | 59 | 40 | 53 | 50 | 130 | 264 | 69 | 83 | 47 | 93 | 0 | 47 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 |  | 708 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 30 | 40 | 0 | 180 | 25 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 16 | 5 | 0 | 66 | 149 | 0 | 0 | 187 | 0 | 189 | 0 | 97 | 0 | 0 | 0 | 431 | 53 | 0 | 0 | 0 |  | 5155 | 2462 | 7617 | 4017 | 708 | 1829 | 595 | 215 | 79 | 70 | 104 | 0 | 0 | 85.55
2:00 | 74 | 133 | 0 | 110 | 202 | 107 | 40 | 345 | 283 | 0 | 0 | 330 | 150 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 35 | 17 | 17 | 19 | 25 | 32 | 28 | 33 | 16 | 0 | 79 | 0 | 110 | 150 | 0 | 204 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 10 | 12 | 50 | 19 | 37 | 110 | 80 | 0 | 280 | 0 | 193 | 16 | 100 | 40 | 5 | 5 | 7 | 0 | 0 | 0 | 22 | 5 | 0 | 13 | 100 | 211 | 0 | 20 | 0 | 59 | 40 | 53 | 50 | 130 | 273 | 67 | 83 | 47 | 89 | 0 | 47 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 |  | 563 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 30 | 5 | 0 | 181 | 25 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 16 | 5 | 0 | 65 | 149 | 0 | 0 | 194 | 0 | 196 | 0 | 97 | 0 | 0 | 0 | 433 | 53 | 0 | 0 | 0 |  | 5082 | 2298 | 7380 | 4025 | 563 | 1833 | 531 | 214 | 79 | 35 | 100 | 0 | 0 | 85.54
3:00 | 74 | 134 | 0 | 110 | 202 | 107 | 40 | 340 | 283 | 0 | 0 | 330 | 150 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 35 | 17 | 17 | 19 | 25 | 32 | 28 | 33 | 8 | 0 | 79 | 0 | 110 | 150 | 0 | 204 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 10 | 12 | 50 | 20 | 37 | 110 | 80 | 0 | 280 | 0 | 195 | 16 | 100 | 40 | 5 | 5 | 7 | 0 | 0 | 0 | 22 | 5 | 0 | 13 | 96 | 213 | 0 | 20 | 0 | 60 | 40 | 53 | 50 | 100 | 274 | 67 | 10 | 47 | 93 | 0 | 47 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 |  | 562 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 182 | 23 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 16 | 3 | 0 | 66 | 149 | 0 | 0 | 188 | 0 | 190 | 0 | 97 | 0 | 0 | 0 | 434 | 28 | 0 | 0 | 0 |  | 4852 | 2219 | 7071 | 3947 | 562 | 1729 | 416 | 215 | 79 | 27 | 96 | 0 | 0 | 85.53
4:00 | 74 | 134 | 0 | 110 | 202 | 107 | 40 | 355 | 283 | 0 | 0 | 330 | 120 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 17 | 18 | 17 | 19 | 25 | 32 | 28 | 33 | 8 | 0 | 80 | 0 | 110 | 150 | 0 | 203 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 10 | 12 | 50 | 19 | 37 | 110 | 80 | 0 | 280 | 0 | 181 | 16 | 100 | 40 | 5 | 5 | 7 | 0 | 0 | 0 | 22 | 5 | 0 | 13 | 94 | 213 | 0 | 20 | 0 | 60 | 40 | 5 | 50 | 100 | 266 | 67 | 10 | 47 | 91 | 0 | 47 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 |  | 561 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 181 | 23 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 16 | 3 | 0 | 66 | 149 | 0 | 0 | 196 | 0 | 199 | 0 | 98 | 0 | 0 | 0 | 435 | 17 | 0 | 0 | 0 |  | 4745 | 2225 | 6970 | 3952 | 561 | 1683 | 358 | 215 | 80 | 27 | 94 | 0 | 0 | 85.52
5:00 | 74 | 134 | 0 | 110 | 202 | 107 | 40 | 343 | 283 | 0 | 0 | 330 | 150 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 17 | 17 | 17 | 19 | 25 | 32 | 28 | 33 | 0 | 0 | 80 | 0 | 110 | 150 | 0 | 203 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 10 | 0 | 19 | 19 | 36 | 110 | 80 | 0 | 280 | 0 | 185 | 16 | 100 | 40 | 5 | 5 | 7 | 0 | 0 | 0 | 22 | 5 | 0 | 13 | 90 | 213 | 0 | 20 | 0 | 60 | 40 | 5 | 5 | 100 | 267 | 67 | 10 | 47 | 85 | 0 | 6 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 |  | 562 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 181 | 23 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 13 | 3 | 0 | 67 | 149 | 0 | 0 | 189 | 0 | 193 | 0 | 97 | 0 | 0 | 0 | 430 | 17 | 0 | 0 | 0 |  | 4619 | 2205 | 6824 | 3926 | 562 | 1587 | 336 | 216 | 80 | 27 | 90 | 0 | 0 | 85.51
6:00 | 74 | 134 | 0 | 110 | 202 | 107 | 40 | 342 | 282 | 0 | 0 | 330 | 150 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 17 | 17 | 17 | 19 | 25 | 32 | 28 | 33 | 0 | 0 | 82 | 0 | 110 | 150 | 0 | 202 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 10 | 0 | 18 | 20 | 25 | 110 | 80 | 0 | 280 | 0 | 182 | 16 | 100 | 40 | 5 | 5 | 7 | 0 | 0 | 0 | 22 | 5 | 0 | 13 | 92 | 213 | 0 | 20 | 0 | 60 | 40 | 5 | 5 | 100 | 268 | 57 | 10 | 47 | 85 | 0 | 6 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 10 | 0 | 0 | 0 | 0 |  | 562 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 163 | 20 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 13 | 3 | 0 | 66 | 149 | 0 | 0 | 187 | 0 | 190 | 0 | 97 | 0 | 0 | 0 | 434 | 17 | 0 | 0 | 0 |  | 4584.3 | 2182 | 6766.3 | 3877 | 562 | 1576 | 335 | 215 | 82 | 27 | 92 | 0.3 | 0 | 85.5
7:00 | 74 | 134 | 0 | 110 | 225 | 108 | 40 | 354 | 322 | 0 | 0 | 360 | 150 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 17 | 18 | 17 | 19 | 25 | 32 | 28 | 33 | 4 | 0 | 80 | 0 | 110 | 150 | 0 | 204 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 10 | 0 | 18 | 19 | 30 | 110 | 80 | 0 | 280 | 0 | 197 | 16 | 100 | 40 | 5 | 5 | 7 | 0 | 0 | 0 | 22 | 8 | 0 | 13 | 88 | 211 | 0 | 20 | 0.1 | 60 | 40 | 5 | 5 | 100 | 267 | 67 | 10 | 47 | 89 | 0 | 7 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 10 | 0 | 0 | 0 | 0 |  | 562 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 181 | 19 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 5 | 0 | 66 | 149 | 0 | 0 | 194 | 0 | 197 | 0 | 96 | 0 | 0 | 0 | 425 | 17 | 0 | 0 | 0 |  | 4778.8 | 2209 | 6987.8 | 4026 | 562 | 1646 | 340 | 215 | 80 | 27 | 88 | 3.8 | 0 | 85.49
8:00 | 74 | 134 | 0 | 110 | 240 | 107 | 40 | 343 | 323 | 0 | 0 | 360 | 150 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 17 | 17 | 17 | 0 | 25 | 32 | 28 | 33 | 25 | 0 | 80 | 0 | 110 | 150 | 0 | 218 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 10 | 0 | 18 | 19 | 2 | 110 | 80 | 0 | 320 | 0 | 200 | 16 | 100 | 40 | 5 | 5 | 7 | 0 | 0 | 0 | 21 | 8 | 0 | 10 | 92 | 210 | 0 | 20 | 0.6 | 60 | 40 | 5 | 5 | 100 | 269 | 66 | 10 | 47 | 98 | 0 | 7 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 10 | 0 | 0 | 0 | 0 |  | 561 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 180 | 18 | 32 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 5 | 0 | 65 | 149 | 0 | 0 | 189 | 0 | 192 | 0 | 96 | 0 | 0 | 0 | 425 | 17 | 0 | 0 | 0 |  | 4818.1 | 2219 | 7037.1 | 4062 | 561 | 1617 | 351 | 214 | 80 | 51 | 92 | 9.1 | 0 | 85.48
9:00 | 74 | 134 | 0 | 110 | 300 | 104 | 40 | 356 | 320 | 0 | 0 | 400 | 150 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 3 | 6 | 0 | 0 | 0 | 6 | 17 | 17 | 0 | 16 | 25 | 32 | 28 | 33 | 31 | 0 | 81 | 0 | 110 | 150 | 0 | 205 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 10 | 0 | 18 | 19 | 2 | 110 | 80 | 0 | 360 | 0 | 190 | 16 | 100 | 40 | 5 | 5 | 7 | 0 | 0 | 0 | 21 | 8 | 0 | 10 | 96 | 210 | 0 | 20 | 0.8 | 60 | 40 | 5 | 5 | 100 | 266 | 65 | 10 | 47 | 95 | 0 | 7 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.3 | 20 | 0 | 0 | 0 | 0 |  | 858 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 180 | 20 | 32 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 0 | 0 | 66 | 149 | 0 | 0 | 195 | 0 | 202 | 0 | 97 | 0 | 0 | 0 | 425 | 17 | 0 | 0 | 0 |  | 4999.1 | 2564 | 7563.1 | 4232 | 858 | 1654 | 353 | 215 | 81 | 60 | 96 | 14.1 | 0 | 85.47
10:00 | 74 | 133 | 0 | 110 | 300 | 104 | 40 | 358 | 355 | 0 | 0 | 400 | 150 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 7 | 16 | 0 | 43 | 0 | 6 | 17 | 17 | 17 | 16 | 25 | 8 | 33 | 33 | 51 | 0 | 83 | 0 | 110 | 150 | 0 | 199 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 10 | 0 | 26 | 19 | 2 | 110 | 80 | 0 | 360 | 0 | 219 | 16 | 100 | 33 | 5 | 5 | 7 | 0 | 0 | 0 | 18 | 8 | 0 | 10 | 112 | 208 | 0 | 20 | 0.5 | 60 | 40 | 31 | 16 | 163 | 270 | 65 | 10 | 46 | 85 | 0 | 42 | 0 | 0 | 0 | 8 | 0 | 7 | 0 | 0 | 0 | 0 | 16 | 16.8 | 75 | 0 | 0 | 0 | 0 |  | 858 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 161 | 21 | 48 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 5 | 0 | 65 | 149 | 0 | 0 | 194 | 0 | 200 | 0 | 96 | 0 | 0 | 0 | 425 | 17 | 0 | 0 | 0 |  | 5396.3 | 2562 | 7958.3 | 4242 | 858 | 1823 | 539 | 214 | 83 | 70 | 112 | 17.3 | 0 | 85.46
11:00 | 74 | 133 | 0 | 110 | 340 | 108 | 60 | 356 | 352 | 0 | 0 | 405 | 150 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 25 | 16 | 0 | 41 | 0 | 6 | 54 | 17 | 17 | 16 | 25 | 25 | 33 | 33 | 51 | 0 | 83 | 0 | 110 | 150 | 0 | 209 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 10 | 9 | 50 | 19 | 2 | 110 | 80 | 0 | 360 | 0 | 205 | 16 | 100 | 40 | 5 | 5 | 14 | 0 | 0 | 0 | 18 | 8 | 0 | 10 | 114 | 193 | 0 | 20 | 0.7 | 60 | 40 | 45 | 50 | 163 | 272 | 0 | 0 | 0 | 97 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 50 | 0 | 90 | 0 | 3 | 0 | 9 |  | 857 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 178 | 21 | 48 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 5 | 0 | 63 | 148 | 0 | 0 | 195 | 0 | 198 | 0 | 95 | 0 | 0 | 0 | 418 | 17 | 0 | 11 | 0 |  | 5574.7 | 2630 | 8204.7 | 4317 | 857 | 1837 | 729 | 211 | 83 | 56 | 114 | 0.7 | 0 | 85.45
12:00 | 74 | 133 | 0 | 110 | 380 | 105 | 69 | 353 | 350 | 0 | 0 | 405 | 150 | 0 | 0 | 23 | 0 | 0 | 190 | 0 | 0 | 70 | 25 | 0 | 47 | 0 | 6 | 54 | 17 | 17 | 19 | 25 | 30 | 33 | 33 | 43 | 0 | 81 | 0 | 110 | 150 | 0 | 204 | 0 | 0 | 0 | 0 | 41 | 9 | 0 | 10 | 14 | 50 | 19 | 2 | 110 | 80 | 0 | 360 | 0 | 186 | 16 | 100 | 31 | 5 | 5 | 35 | 0 | 0 | 0 | 19 | 8 | 0 | 10 | 114 | 192 | 0 | 20 | 1.6 | 60 | 50 | 45 | 47 | 163 | 266 | 20 | 10 | 32 | 84 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 50 | 0 | 90 | 40 | 53 | 0 | 106 |  | 858 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 179 | 23 | 80 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 22 | 15 | 5 | 0 | 64 | 149 | 0 | 0 | 193 | 0 | 194 | 0 | 95 | 0 | 0 | 0 | 418 | 53 | 0 | 91 | 0 |  | 5937.6 | 2766 | 8703.6 | 4300 | 858 | 1909 | 1160 | 213 | 81 | 67 | 114 | 1.6 | 0 | 85.44
13:00 | 74 | 135 | 0 | 110 | 340 | 105 | 69 | 353 | 320 | 0 | 0 | 405 | 150 | 0 | 0 | 31 | 0 | 0 | 190 | 0 | 0 | 70 | 32 | 0 | 47 | 0 | 6 | 54 | 18 | 17 | 19 | 25 | 30 | 33 | 33 | 50 | 0 | 80 | 0 | 110 | 150 | 0 | 208 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 10 | 30 | 50 | 19 | 5 | 110 | 80 | 0 | 330 | 0 | 187 | 16 | 100 | 37 | 20 | 5 | 35 | 0 | 0 | 0 | 19 | 8 | 0 | 10 | 120 | 177 | 0 | 20 | 1.3 | 60 | 50 | 48 | 47 | 163 | 264 | 50 | 10 | 45 | 83 | 0 | 47 | 0 | 0 | 0 | 8 | 0 | 31 | 0 | 0 | 0 | 0 | 50 | 14.6 | 100 | 52 | 70 | 0 | 104 |  | 858 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 178 | 23 | 80 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 68 | 149 | 0 | 0 | 185 | 0 | 181 | 0 | 94 | 0 | 0 | 0 | 415 | 53 | 0 | 90 | 0 |  | 5990.9 | 2731 | 8721.9 | 4244 | 858 | 1894 | 1228 | 217 | 80 | 65 | 120 | 15.9 | 0 | 85.43
14:00 | 74 | 134 | 0 | 110 | 275 | 52 | 40 | 300 | 281 | 0 | 0 | 320 | 150 | 0 | 0 | 15 | 0 | 0 | 105 | 0 | 0 | 50 | 32 | 0 | 46 | 0 | 6 | 54 | 0 | 17 | 0 | 25 | 31 | 33 | 33 | 50 | 0 | 79 | 0 | 105 | 150 | 0 | 195 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 10 | 30 | 50 | 19 | 2 | 80 | 80 | 0 | 315 | 36 | 183 | 16 | 100 | 37 | 5 | 5 | 7 | 0 | 0 | 0 | 18 | 8 | 8 | 10 | 90 | 177 | 0 | 20 | 2 | 60 | 50 | 31 | 30 | 100 | 264 | 44 | 10 | 10 | 84 | 0 | 12 | 0 | 0 | 0 | 8 | 0 | 13 | 0 | 0 | 0 | 0 | 50 | 0 | 100 | 44 | 48 | 0 | 104 |  | 858 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 153 | 23 | 80 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 22 | 9 | 8 | 0 | 66 | 144 | 0 | 0 | 171 | 0 | 151 | 0 | 96 | 0 | 0 | 0 | 416 | 53 | 0 | 90 | 0 |  | 5173 | 2627 | 7800 | 3884 | 858 | 1487 | 1125 | 210 | 79 | 65 | 90 | 2 | 0 | 85.42
15:00 | 74 | 134 | 40 | 110 | 300 | 13 | 40 | 300 | 250 | 0 | 0 | 280 | 150 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 0 | 24 | 16 | 0 | 8 | 0 | 6 | 54 | 0 | 17 | 0 | 25 | 32 | 33 | 17 | 8 | 0 | 79 | 0 | 105 | 150 | 0 | 217 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 10 | 15 | 50 | 20 | 2 | 80 | 80 | 0 | 270 | 88 | 187 | 16 | 0 | 40 | 5 | 5 | 7 | 0 | 0 | 0 | 18 | 0 | 8 | 10 | 78 | 176 | 0 | 20 | 1.2 | 60 | 60 | 28 | 30 | 130 | 268 | 66 | 10 | 10 | 96 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 20 | 12 | 100 | 17 | 0 | 0 | 110 |  | 858 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 178 | 15 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 8 | 0 | 67 | 149 | 0 | 0 | 191 | 0 | 199 | 0 | 95 | 0 | 0 | 0 | 415 | 53 | 0 | 54 | 0 |  | 4823.2 | 2625 | 7448.2 | 3933 | 858 | 1401 | 854 | 216 | 79 | 16 | 78 | 13.2 | 0 | 85.41
16:00 | 74 | 134 | 72 | 110 | 280 | 12 | 40 | 345 | 240 | 0 | 0 | 280 | 155 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 24 | 16 | 0 | 8 | 0 | 6 | 54 | 0 | 17 | 0 | 25 | 32 | 33 | 33 | 8 | 0 | 79 | 0 | 105 | 150 | 0 | 203 | 0 | 0 | 0 | 0 | 41 | 0 | 4 | 10 | 32 | 50 | 20 | 2 | 80 | 80 | 0 | 270 | 99 | 175 | 16 | 0 | 10 | 5 | 5 | 7 | 0 | 0 | 0 | 19 | 8 | 0 | 10 | 8 | 177 | 0 | 20 | 0 | 58 | 60 | 5 | 5 | 100 | 267 | 52 | 10 | 10 | 84 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 17 | 8 | 100 | 35 | 0 | 0 | 54 |  | 858 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 177 | 15 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 66 | 149 | 0 | 0 | 176 | 0 | 188 | 0 | 95 | 0 | 0 | 0 | 415 | 53 | 0 | 18 | 0 |  | 4645 | 2558 | 7203 | 3914 | 858 | 1303 | 798 | 215 | 79 | 20 | 8 | 8 | 0 | 85.4
17:00 | 74 | 94 | 95 | 110 | 140 | 12 | 40 | 320 | 210 | 0 | 0 | 280 | 155 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 32 | 16 | 0 | 8 | 0 | 6 | 54 | 0 | 17 | 0 | 25 | 32 | 33 | 33 | 8 | 0 | 79 | 0 | 105 | 150 | 0 | 190 | 0 | 0 | 0 | 0 | 41 | 0 | 17 | 10 | 45 | 50 | 20 | 2 | 80 | 80 | 36 | 230 | 128 | 155 | 16 | 0 | 10 | 5 | 5 | 7 | 0 | 0 | 0 | 22 | 8 | 0 | 0 | 26 | 183 | 0 | 0 | 0 | 30 | 50 | 0 | 5 | 100 | 235 | 40 | 10 | 5 | 84 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 16 | 2.6 | 100 | 17 | 0 | 0 | 0 |  | 858 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 8 | 155 | 23 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 66 | 149 | 0 | 0 | 130 | 0 | 135 | 0 | 96 | 0 | 0 | 0 | 420 | 53 | 0 | 18 | 0 |  | 4292.6 | 2319 | 6611.6 | 3392 | 858 | 1250 | 731 | 215 | 79 | 58 | 26 | 2.6 | 0 | 85.39
18:00 | 74 | 95 | 30 | 110 | 40 | 12 | 40 | 250 | 190 | 0 | 0 | 250 | 120 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 42 | 16 | 0 | 0 | 0 | 6 | 54 | 18 | 35 | 0 | 0 | 32 | 33 | 0 | 0 | 0 | 79 | 0 | 105 | 120 | 0 | 170 | 0 | 0 | 0 | 0 | 41 | 9 | 21 | 10 | 25 | 50 | 20 | 2 | 80 | 0 | 37 | 210 | 154 | 145 | 16 | 0 | 10 | 5 | 5 | 7 | 0 | 0 | 0 | 22 | 8 | 0 | 0 | 46 | 152 | 0 | 0 | 0 | 30 | 51 | 0 | 5 | 100 | 214 | 35 | 5 | 5 | 76 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 12 | 0 | 70 | 17 | 0 | 0 | 0 |  | 858 | 0 | 100 | 0 | 2 | 0 | 0 | 0 | 13 | 40 | 8 | 161 | 24 | 80 | 0 | 0 | 0 | 0 | 5 | 9 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 60 | 149 | 0 | 0 | 125 | 0 | 132 | 0 | 52 | 0 | 0 | 0 | 442 | 17 | 0 | 0 | 0 |  | 3705 | 2280 | 5985 | 2891 | 858 | 1169 | 620 | 209 | 79 | 113 | 46 | 0 | 0 | 85.38
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 74 | 95 | 30 | 110 | 120 | 12 | 40 | 230 | 290 | 0 | 0 | 240 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 6 | 54 | 0 | 0 | 0 | 25 | 32 | 0 | 0 | 0 | 0 | 80 | 0 | 105 | 100 | 12 | 187 | 0 | 0 | 0 | 0 | 41 | 51 | 68 | 10 | 27 | 50 | 20 | 7 | 0 | 0 | 55 | 250 | 270 | 182 | 16 | 100 | 10 | 5 | 5 | 7 | 0 | 0 | 0 | 22 | 8 | 0 | 0 | 32 | 150 | 7 | 0 | 0 | 30 | 51 | 0 | 5 | 100 | 171 | 52 | 5 | 0 | 95 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 |  | 598 | 0 | 220 | 0 | 19 | 0 | 0 | 0 | 35 | 55 | 24 | 181 | 31 | 110 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 8 | 0 | 3 | 0 | 0 | 0 | 63 | 149 | 17 | 18 | 125 | 0 | 131 | 0 | 97 | 0 | 0 | 0 | 435 | 17 | 0 | 0 | 0 |  | 3964 | 2429 | 6393 | 3231 | 598 | 1304 | 599 | 212 | 80 | 337 | 32 | 0 | 0 | 85.37
19:30 | 74 | 95 | 44 | 110 | 200 | 12 | 40 | 340 | 310 | 0 | 0 | 300 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 6 | 54 | 0 | 0 | 0 | 25 | 32 | 0 | 0 | 0 | 0 | 80 | 0 | 105 | 100 | 16 | 204 | 0 | 0 | 0 | 0 | 41 | 51 | 80 | 10 | 27 | 50 | 20 | 13 | 0 | 0 | 55 | 300 | 300 | 188 | 16 | 100 | 10 | 5 | 5 | 7 | 0 | 0 | 0 | 22 | 8 | 0 | 0 | 8 | 150 | 7 | 0 | 0 | 30 | 51 | 0 | 5 | 100 | 171 | 69 | 0 | 0 | 28 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 |  | 599 | 0 | 220 | 0 | 32 | 0 | 0 | 0 | 34 | 70 | 24 | 182 | 31 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 8 | 0 | 3 | 3 | 8 | 0 | 60 | 149 | 17 | 18 | 130 | 0 | 132 | 0 | 97 | 0 | 0 | 0 | 430 | 90 | 0 | 0 | 0 |  | 4329 | 2547 | 6876 | 3503 | 599 | 1383 | 724 | 209 | 80 | 370 | 8 | 0 | 0 | 0
20:00 | 74 | 95 | 50 | 110 | 220 | 12 | 40 | 320 | 310 | 0 | 0 | 300 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 6 | 54 | 0 | 0 | 0 | 25 | 0 | 6 | 0 | 0 | 0 | 80 | 0 | 105 | 100 | 16 | 214 | 0 | 0 | 0 | 0 | 41 | 51 | 80 | 10 | 27 | 50 | 21 | 15 | 0 | 0 | 55 | 300 | 300 | 200 | 16 | 0 | 40 | 5 | 5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 150 | 7 | 20 | 0 | 30 | 51 | 0 | 5 | 100 | 171 | 68 | 5 | 5 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 |  | 599 | 0 | 220 | 0 | 32 | 0 | 0 | 0 | 33 | 0 | 24 | 181 | 34 | 80 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 8 | 0 | 3 | 3 | 8 | 0 | 61 | 149 | 17 | 18 | 150 | 0 | 132 | 0 | 97 | 0 | 0 | 0 | 435 | 90 | 0 | 0 | 0 |  | 4258 | 2474 | 6732 | 3416 | 599 | 1407 | 699 | 210 | 80 | 299 | 22 | 0 | 0 | 85.36
21:00 | 74 | 94 | 50 | 120 | 220 | 12 | 40 | 320 | 313 | 0 | 0 | 340 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 54 | 0 | 0 | 0 | 25 | 0 | 24 | 33 | 0 | 0 | 80 | 0 | 105 | 100 | 16 | 203 | 0 | 0 | 0 | 0 | 41 | 50 | 80 | 10 | 26 | 50 | 21 | 16 | 0 | 0 | 55 | 360 | 360 | 184 | 16 | 0 | 40 | 5 | 5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 147 | 7 | 20 | 0 | 30 | 51 | 0 | 5 | 163 | 150 | 40 | 5 | 5 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 |  | 744 | 0 | 220 | 0 | 32 | 0 | 0 | 0 | 31 | 2 | 24 | 167 | 32 | 80 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 8 | 0 | 5 | 3 | 8 | 0 | 62 | 149 | 17 | 18 | 172 | 0 | 132 | 0 | 97 | 0 | 0 | 0 | 435 | 90 | 0 | 0 | 0 |  | 4471 | 2628 | 7099 | 3525 | 744 | 1516 | 681 | 211 | 80 | 298 | 44 | 0 | 0 | 85.35
22:00 | 74 | 94 | 36 | 120 | 220 | 12 | 40 | 335 | 256 | 0 | 0 | 340 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 17 | 0 | 0 | 0 | 25 | 16 | 33 | 33 | 0 | 0 | 80 | 0 | 105 | 100 | 8 | 184 | 0 | 0 | 0 | 0 | 41 | 0 | 17 | 10 | 20 | 50 | 0 | 16 | 0 | 0 | 80 | 260 | 300 | 184 | 16 | 0 | 40 | 5 | 5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 147 | 0 | 20 | 0 | 30 | 51 | 0 | 5 | 163 | 150 | 40 | 5 | 5 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 |  | 744 | 0 | 220 | 0 | 32 | 0 | 0 | 0 | 29 | 12 | 0 | 178 | 32 | 80 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 8 | 0 | 62 | 149 | 0 | 0 | 180 | 0 | 132 | 0 | 96 | 0 | 0 | 0 | 441 | 90 | 0 | 0 | 0 |  | 4086 | 2593 | 6679 | 3395 | 744 | 1467 | 564 | 211 | 80 | 158 | 60 | 0 | 0 | 85.34
23:00 | 74 | 94 | 50 | 120 | 220 | 12 | 40 | 360 | 308 | 0 | 0 | 330 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 17 | 0 | 0 | 0 | 25 | 32 | 33 | 33 | 0 | 0 | 83 | 0 | 105 | 100 | 0 | 178 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 10 | 13 | 19 | 20 | 20 | 0 | 0 | 80 | 280 | 300 | 170 | 16 | 100 | 40 | 5 | 5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 147 | 0 | 20 | 0 | 30 | 51 | 5 | 5 | 163 | 150 | 53 | 5 | 5 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 |  | 647 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 29 | 20 | 0 | 128 | 24 | 80 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 8 | 0 | 61 | 149 | 0 | 0 | 166 | 0 | 148 | 0 | 97 | 0 | 0 | 0 | 435 | 0 | 0 | 0 | 0 |  | 4318 | 2270 | 6588 | 3545 | 647 | 1530 | 414 | 210 | 83 | 89 | 70 | 0 | 0 | 85.33
24:00 | 74 | 93 | 48 | 120 | 220 | 12 | 40 | 344 | 308 | 0 | 0 | 330 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 17 | 0 | 0 | 0 | 25 | 32 | 33 | 33 | 0 | 0 | 83 | 0 | 105 | 100 | 0 | 203 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 10 | 13 | 18 | 21 | 26 | 0 | 0 | 80 | 300 | 300 | 183 | 16 | 100 | 37 | 5 | 5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 147 | 0 | 20 | 0 | 30 | 51 | 5 | 5 | 130 | 137 | 53 | 5 | 5 | 0 | 0 | 7 | 0 | 55 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 |  | 647 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 29 | 20 | 0 | 136 | 26 | 48 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 5 | 0 | 61 | 149 | 0 | 0 | 164 | 0 | 154 | 0 | 96 | 0 | 0 | 0 | 443 | 0 | 0 | 0 | 0 |  | 4372 | 2234 | 6606 | 3582 | 647 | 1534 | 421 | 210 | 83 | 67 | 62 | 0 | 0 | 85.32
KWH | 1716000 | 3076800 | 495000 | 2787750 | 5730436 | 1590136 | 1417472 | 8258560 | 6959000 | 0 | 0 | 7936000 | 3750924 | 0 | 0 | 95719 | 0 | 0 | 2376000 | 0 | 0 | 480384 | 188160 | 0 | 242880 | 0 | 156528 | 893520 | 248651 | 315247 | 221760 | 575000 | 600480 | 705000 | 707600 | 430176 | 0 | 1841765 | 0 | 2500000 | 3300000 | 68286 | 4817638 | 0 | 0 | 0 | 0 | 926400 | 161578 | 296796 | 255480 | 420480 | 945440 | 441210 | 368160 | 1937665 | 1375405 | 440792 | 7362000 | 2219500 | 4545000 | 434909 | 1710040 | 760464 | 159360 | 120000 | 366740 | 0 | 0 | 0 | 389340 | 135540 | 16000 | 200050 | 1891200 | 4377600 | 23040 | 388728 | 8300 | 1199000 | 1109234 | 447000 | 490000 | 3255921 | 5442000 | 1299648 | 415680 | 666000 | 1805430 | 0 | 491080 | 6840 | 78732 | 75213 | 111168 | 0 | 198220 | 0 | 0 | 0 | 0 | 305280 | 80865 | 1448640 | 241440 | 222470 | 0 | 598800 |  | 16753454 | 0 | 5495904 | 0 | 119040 | 0 | 0 | 0 | 441120 | 245888 | 201375 | 2947000 | 528259 | 1516800 | 0 | 0 | 0 | 8437 | 7688 | 669987 | 14100 | 5148 | 6098 | 31200 | 6040 | 379440 | 240624 | 127170 | 0 | 1545599 | 3643400 | 50000 | 68000 | 4517673 | 0 | 4362973 | 0 | 2264163 | 0 | 0 | 0 | 10312364 | 960960 | 0 | 417600 | 0 |  | 117148750 | 57887504 | 175036254 | 92659771 | 16753454 | 38927880 | 15534228 | 5188999 | 1841765 | 2149792 | 1891200 | 89165 | 0
Fuel Cost | 1475760 | 2646048 | 425700 | 2397465 | 3667479.04 | 1288010.16 | 1332423.68 | 5037721.6 | 4244990 | 0 | 0 | 5317120 | 56976535.56 | 0 | 0 | 584843.09 | 0 | 0 | 2637360 | 0 | 0 | 3165730.56 | 1819507.2 | 0 | 1454851.2 | 0 | 1044041.76 | 6370797.6 | 1554068.75 | 1976598.69 | 166320 | 431250 | 0 | 0 | 0 | 4069464.96 | 0 | 0 | 0 | 2750000 | 3630000 | 646668.42 | 3179641.08 | 0 | 0 | 0 | 0 | 8143056 | 1740195.06 | 2887825.08 | 1581421.2 | 2716300.8 | 6183177.6 | 375028.5 | 0 | 1763275.15 | 1251618.55 | 401120.72 | 4564440 | 1531455 | 3181500 | 300087.21 | 1641638.4 | 509510.88 | 137049.6 | 110400 | 300726.8 | 0 | 0 | 0 | 299791.8 | 101655 | 12320 | 150037.5 | 12935808 | 3283200 | 211737.6 | 299320.56 | 0 | 1246960 | 1153603.36 | 429120 | 441000 | 2539618.38 | 3809400 | 1481598.72 | 444777.6 | 732600 | 2058190.2 | 0 | 456704.4 | 6361.2 | 50388.48 | 56409.75 | 84487.68 | 0 | 1439077.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2255049.6 | 2077869.8 | 0 | 0 |  | 85442615.4 | 0 | 3682255.68 | 0 | 986841.6 | 0 | 0 | 0 | 4967011.2 | 2896560.64 | 1586835 | 2033430 | 522976.41 | 11224320 | 0 | 0 | 0 | 96603.65 | 82415.36 | 6003083.52 | 121965 | 45817.2 | 64943.7 | 309504 | 71090.8 | 417384 | 226186.56 | 96267.69 | 0 | 9381785.93 | 14063524 | 1611500 | 1820360 | 3072017.64 | 0 | 3054081.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 197667309.73 | 153881376.08 | 351548685.81 | 69639358.6 | 85442615.4 | 19297924.48 | 116726573.19 | 23445309.93 | 0 | 24061096.21 | 12935808 | 0 | 0
Yesterday Day Peak | 74 | 133 | 0 | 110 | 380 | 105 | 69 | 353 | 350 | 0 | 0 | 405 | 150 | 0 | 0 | 23 | 0 | 0 | 190 | 0 | 0 | 70 | 25 | 0 | 47 | 0 | 6 | 54 | 17 | 17 | 19 | 25 | 30 | 33 | 33 | 43 | 0 | 81 | 0 | 110 | 150 | 0 | 204 | 0 | 0 | 0 | 0 | 41 | 9 | 0 | 10 | 14 | 50 | 19 | 2 | 110 | 80 | 0 | 360 | 0 | 186 | 16 | 100 | 31 | 5 | 5 | 35 | 0 | 0 | 0 | 19 | 8 | 0 | 10 | 114 | 192 | 0 | 20 | 1.6 | 60 | 50 | 45 | 47 | 163 | 266 | 20 | 10 | 32 | 84 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 50 | 0 | 90 | 40 | 53 | 0 | 106 |  | 858 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 179 | 23 | 80 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 22 | 15 | 5 | 0 | 64 | 149 | 0 | 0 | 193 | 0 | 194 | 0 | 95 | 0 | 0 | 0 | 418 | 53 | 0 | 91 | 0 |  | 8703.6 | DayPeak
Yesterday Evening Peak | 74 | 94 | 50 | 120 | 220 | 12 | 40 | 320 | 313 | 0 | 0 | 340 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 54 | 0 | 0 | 0 | 25 | 0 | 24 | 33 | 0 | 0 | 80 | 0 | 105 | 100 | 16 | 203 | 0 | 0 | 0 | 0 | 41 | 50 | 80 | 10 | 26 | 50 | 21 | 16 | 0 | 0 | 55 | 360 | 360 | 184 | 16 | 0 | 40 | 5 | 5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 147 | 7 | 20 | 0 | 30 | 51 | 0 | 5 | 163 | 150 | 40 | 5 | 5 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 |  | 744 | 0 | 220 | 0 | 32 | 0 | 0 | 0 | 31 | 2 | 24 | 167 | 32 | 80 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 8 | 0 | 5 | 3 | 8 | 0 | 62 | 149 | 17 | 18 | 172 | 0 | 132 | 0 | 97 | 0 | 0 | 0 | 435 | 90 | 0 | 0 | 0 |  | 7099 | EvPeak
Forecast for Evening | 74 | 100 | 100 | 120 | 300 | 108 | 78 | 412 | 360 | 110 | 0 | 450 | 305 | 92 | 100 | 55 | 0 | 0 | 210 | 100 | 100 | 102 | 149 | 100 | 49 | 0 | 49 | 54 | 55 | 55 | 19 | 25 | 32 | 33 | 33 | 51 | 0 | 100 | 30 | 110 | 100 | 16 | 225 | 0 | 0 | 0 | 0 | 41 | 72 | 85 | 78 | 105 | 50 | 22 | 15 | 0 | 0 | 100 | 360 | 360 | 221 | 16 | 100 | 40 | 5 | 5 | 35 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 168 | 202 | 87 | 20 | 0 | 30 | 60 | 51 | 44 | 163 | 330 | 66 | 86 | 47 | 120 | 20 | 46 | 10 | 340 | 25 | 8 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 112 |  | 966 | 46 | 410 | 0 | 115 | 0 | 0 | 0 | 35 | 80 | 40 | 190 | 32 | 110 | 26 | 0 | 0 | 50 | 54 | 100 | 43 | 50 | 40 | 43 | 30 | 22 | 17 | 11 | 0 | 62 | 149 | 17 | 18 | 200 | 0 | 225 | 0 | 95 | 100 | 0 | 0 | 414 | 105 | 0 | 113 | 0
Forecast for Day | 74 | 100 | 100 | 120 | 240 | 108 | 78 | 412 | 360 | 110 | 0 | 450 | 305 | 92 | 100 | 55 | 0 | 0 | 210 | 100 | 100 | 102 | 149 | 100 | 49 | 0 | 49 | 54 | 55 | 55 | 0 | 25 | 32 | 33 | 33 | 51 | 0 | 100 | 30 | 110 | 100 | 16 | 225 | 0 | 0 | 0 | 0 | 41 | 72 | 85 | 78 | 105 | 50 | 22 | 5 | 0 | 0 | 100 | 360 | 360 | 221 | 16 | 100 | 40 | 5 | 5 | 35 | 0 | 0 | 52 | 22 | 11 | 0 | 21 | 134 | 202 | 87 | 20 | 2 | 30 | 60 | 51 | 44 | 163 | 330 | 66 | 86 | 47 | 120 | 0 | 46 | 0 | 340 | 0 | 8 | 100 | 200 | 200 | 100 | 200 | 100 | 149 | 20 | 100 | 200 | 150 | 0 | 112 |  | 869 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 35 | 40 | 40 | 150 | 28 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 43 | 50 | 40 | 43 | 0 | 22 | 17 | 11 | 0 | 62 | 149 | 17 | 18 | 200 | 0 | 225 | 0 | 95 | 100 | 0 | 0 | 414 | 105 | 0 | 113 | 0
Generation at 08:00(Today) | 0 | 94 | 50 | 120 | 130 | 0 | 0 | 349 | 218 | 0 | 0 | 300 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 17 | 0 | 0 | 0 | 25 | 32 | 33 | 33 | 0 | 0 | 41 | 0 | 105 | 100 | 0 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 21 | 6 | 0 | 0 | 80 | 230 | 250 | 225 | 8 | 100 | 15 | 5 | 5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 182 | 0 | 0 | 1.1 | 25 | 51 | 5 | 5 | 100 | 135 | 20 | 5 | 5 | 0 | 0 | 7 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.51 | 0 | 0 | 0 | 0 | 0 | 0 | 840 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 120 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 8 | 0 | 64 | 149 | 0 | 0 | 153 | 0 | 146 | 0 | 71 | 0 | 0 | 0 | 430 | 0 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 6766.3 | 6:00
| Highest Generation |  | 8721.9 | 13:00
| Day Peak Generation |  | 8703.6 | 12:00
| Evening Peak Generation |  | 7099 | 21:00
| HVDC Max Flow |  | 858 | 9:00
| HVDC EvPeak Flow |  | 744 | 21:00
| Load factor L.F |  | 83.62%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-04-03
Till now the maximum generation is : - |  |  | 11623 MW | 19:30 | Hrs on | 2018-09-19
The Summary of Yesterday's |  | 2019-04-02 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8703.6 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 5674.2 | MW
Evening Peak Generation : |  | 7099 | MW Hour : | 21:00 | Available Max Generation : |  | 14302 | MW
E.P. Demand (at gen end) : |  | 7099 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 9900 | MW
Maximum Generation : |  | 8721.9 | MW Hour : | 13:00 | Reserve(Generation end) |  | 4402 | MW
Total Gen. (MKWH) : |  | 175.0363 | System Load Factor : | 83.62% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -190 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-04-03
Actual : | 85.32 | Ft.(MSL) , | Rule curve : | 87.6 | Ft.( MSL )
Gas Consumed : | Total = | 1090.47 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 88937283.08
|  | Coal : | 23445309.93 | Oil : | 140787669.4 | Total : | 253170262.41
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3583.0281 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1215.7822 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1088.8291 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 983.6816 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 889.0311 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 717.41 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 404.5449 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 184.8039 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 553.2859 |  |  | 0 | 0%
Total | 0 |  | 9620.3969 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1
2) Khulna ST 110 MW
3) Siddirganj-335 MW
4) Bhagabari 100 & 71 MW
5) Siddhirganj ST
6) Ashuganj #3,4
7) Raozan #02.
8) Haripur SBU-1,2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Madanganj-Haripur 132 kV Ckt was under shut down from 11:27 to 20:54 for C/M.
b) Rangpur-Palashbari 132 kV Ckt-2 was under shut down from 11:25 to 15:20 for conductor armouring.
c) After maintenance Ashuganj (South)-360 MW CCPP GT was synchronized at 13:18.
d) Bheramara-Ishurdi 132 kV Ckt-1 tripped at 21:30 showing dist.T-phase,E/F relay as 132 kV B-phase L/A of Ruppur 132/33 kV T-2
transformer burst and was switched on at 23:15.
e) Summit Megnaghat-305 MW GT-1 was synchronized at 21:51.
f) Chandpur-163 MW CCPP GT tripped at 14:30 due to outlet temperature of GBC high and was synchronized at 18:30.
g) After maintenance Ghorasal #4 was synchronized at 14:40.
h) After maintenance Ghorasal #7 CCPP ST was synchronized at 17:10.
i) Tongi-Uttara(Third phase) 132 kV Ckt tripped at 18:00 showing dist.Z,E/F relay and was switched on at 18:53.
j) Tongi-Kabirpur 132 kV Ckt-1 tripped at 18:40 showing dist.Z1 at from both end and was switched on at 18:48.
k) Mymensing 132/33 kV T-3 transformer tripped at 18:40 showing O/C, E/F relays. |  |  |  | About 5 MW power interruption occurred under Mymensing S/S area
l) Sreemongal-Fenchuganj 132 kV Ckt-2 tripped at 19:03 showing dist.C-phase,Z2 and was switched on at 21:37.
m) Chandpur-Cumilla(N) 132 kV Ckt-2 tripped at 19:30 showing dist.Z1,Z2 at Chandpur end & dist.Z2,B-phase at Cumilla(N) end and.
n) Summit Bibiyana #2 CCPP GT ST were synchronized at 19:42 & 21:37 respectively.
o) Ashuganj #3 & #4 were shut down at 18:20 & 17:15 respectively.
p) Bhola-225 MW CCPP ST was shut down at 22:57 for maintenance.
q) Kulshi-AKS steel 132 kV Ckt tripped at 23:53 showing no signal and was switched on at 00:35(3/4/19).
r) Cox's Bazar 132/33 kV T-2 transformer was shut down at 02:00(3/4/19) for 132 kV CB problem.
s) Khulna(S)-Satkhira 132 kV Ckt-1 tripped at 23:27 showing dist.Z1 & E/F relay and was switched on at 23:47.
t) Hasnabad 230 KV Bus-2 is under shut down since 07:11(3/4/19) for red hot maintenance.
u) Kustia 132/33 kV T-1 transformer is under shut down since 07:22(3/4/19) due to red hot maintenance at 33 kV Bus DS and was |  |  |  | About 35 MW power interruption occurred under Kustia S/S area
switched on at 08:10(3/4/19). |  |  |  | from 07:22 to 08:10(3/4/19).
v) Ghorasal 132/33 kV 1-T transformer tripped at 07:30(3/4/19) showing E/F relay.
w) Ghorasal 230/132 kV AT-1 transformer tripped at 07:30(3/4/19) showing 1PY, 11PY & transformer protection due to B-phase
conductor grounded at 132 kV end.
x) Ghorasal-Joydevpur 132 kV Ckt-1 tripped at 07:30(3/4/19) showing E/F relay.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-04-02 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 74 | 1716000
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 94 | 3076800 | On test
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 50 | 495000 | On test
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 120 | 2787750
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 220 | 5730436 | Low demand
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 40 | 1417472
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 12 | 1590136 | Low demand
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 320 | 8258560 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 0 | 0 | Reserve
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 313 | 6959000 | Frequency control
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 340 | 7936000 | Frequency control
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 160 | 3750924 | Low demand
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 95719 | Reserve
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 221760 | tripped at 18:00
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 0 | 2376000 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 0 | Reserve
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 0 | 0 | Under maint.
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 7 | 480384 | Low demand
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 6 | 156528
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 893520
25 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 188160 | Reserve
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 0 | 248651 | Reserve
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 0 | 315247 | Reserve
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 242880 | Reserve
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 25 | 1175480 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 24 | 705000
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 707600
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 0 | 430176 | Low demand
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
34 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 0 | 198220 | Reserve
35 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
36 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
37 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
38 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 0 | 305280 | Reserve
| Dhaka area Total |  |  |  | 5798 | 1892 | 52458683
39 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 105 | 2500000 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 100 | 3300000 | Gas shortage
40 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 16 | 68286 | Engine problem
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 80865
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 50 | 945440
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1841765 | Low water lavel
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4817638 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under S/D
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 41 | 926400 | Engine problem
47 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 50 | 161578
48 | Dohazari Peaking |  | PDB | 6*17 | 102 | 80 | 296796
49 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 255480 | Low demand
| Juldah 100 MW Unit-3 |  | IPP | 0 | 100 | 70 | 1448640
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 441210
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 16 | 368160
51 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 26 | 420480 | Low demand
| Chattogram area Total |  |  |  | 1681 | 868 | 17872738
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 1937665 | tripped at 18:20
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 1375405 | tripped at 17:15
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 55 | 440792 | synchronized at 16:08
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 184 | 4545000 | FGMO
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 360 | 7362000
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 360 | 2219500
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 40 | 760464 | Engine problem
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 5 | 159360 | Gas shortage
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 16 | 434909 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 7 | 366740 | Gas shortage
| Midland 150MW |  | IPP | 23*7.015 | 150 | 0 | 222470 | Reserve
61 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
62 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
63 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 1710040 | Reserve
| Chandpur Desh 200MW |  | IPP | 0 | 200 | 0 | 241440 | Reserve
64 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 0 | 389340 | tripped at 19:48
65 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 135540 | tripped at 14:30.
** | Tripura |  | Imported power | 0 | 160 | 44 | 1891200 | Low demand
66 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 0 | 16000 | tripped at 15:05
67 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
68 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 0 | 200050 | Machine problem
69 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1076 | 24527915
70 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 147 | 4377600 | Gas shortage
71 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 20 | 388728
72 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 7 | 23040 | Low demand
73 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 8300
74 | United Mymensingh PPL |  | IPP | 200 | 200 | 0 | 0 | Reserve
| United Jamalpur PPL |  | IPP | 115 MW | 115 | 0 | 598800 | Reserve
| Mymensingh Area Total |  |  |  | 637 | 174 | 5396468
75 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 30 | 1199000
76 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 51 | 1109234
77 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 163 | 3255921
78 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 150 | 5442000 | FGMO
79 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 0 | 447000
80 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 5 | 490000 | tripped at 16:20
81 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 0 | 111168 | tripped at 14:50
82 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 40 | 1299648 | FGMO
83 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 5 | 415680 | Frequency control
84 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 5 | 666000 | Frequency control
85 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 0 | 1805430 | tripped at 19:42
86 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 0 | Machine problem
87 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 0 | 491080 | tripped at 19:45
88 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 0 | 75213 | Under S/D
89 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 12 | 78732 | synchronized at 19:42
| Bibiyana-3 285MW |  | PDB | 285 MW | 0 | 0 | 0 | On test
90 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 0 | 6840 | under S/D
| Sylhet Area Total |  |  |  | 1549 | 461 | 16892946
91 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 744 | 16753454
92 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
93 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 32 | 119040 | Low demand
94 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 31 | 441120 | Low demand
95 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
96 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 2 | 245888 | Low demand
97 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 220 | 5495904 | Line O/L
98 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 24 | 201375 | Low demand
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
99 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
| Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 90 | 960960 | Low demand
| Madhumati Power Plant |  | IPP | 100 MW | 0 | 0 | 0 | On test
| Khulna Area Total |  |  |  | 2209 | 1143 | 24217741
100 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 80 | 1516800
101 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
102 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 32 | 528259
103 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 167 | 2947000
104 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 97 | 2264163
| Barisal Area Total |  |  |  | 462 | 376 | 7256222
105 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
106 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 0 | 8437 | Reserve
107 | Bera Peaking |  | PDB | 9*8.29 | 71 | 0 | 7688 | Reserve
108 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 0 | 14100 | Reserve
109 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 5148 | Reserve
110 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 0 | 6098 | Reserve
111 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 172 | 4517673 | FGMO
112 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 132 | 4362973 | FGMO
113 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282 | 282 | 435 | 10312364 | On test
114 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 0 | 6040 | Reserve
115 | Bogra (GBB) |  | RPP | 6*4 | 22 | 5 | 379440 | Low demand
116 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 3 | 240624 | Low demand
117 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 127170 | Low demand
118 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 8 | 31200 | Low demand
119 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 100 | 669987 | Reserve
| Paramount Baghabari |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
| Confidence CPBL-2 |  | IPP | 113 MW | 0 | 0 | 417600 | on test
| Rajshahi Area Total |  |  |  | 1825 | 863 | 21106542
120 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 62 | 1545599
121 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 149 | 3643400 | Coal Shortage
122 | Rangpur GT |  | PDB | 1*20 | 20 | 17 | 50000
123 | Saidpur GT |  | PDB | 1*20 | 20 | 18 | 68000
| Rangpur Area Total |  |  |  | 484 | 246 | 5306999
| Total |  |  |  | 17536 | 7099 | 175036254
| Eastern Grid Total |  |  |  | 12556 | 4471 | 117148750
| Western Grid Total |  |  |  | 4980 | 2628 | 57887504
| National Grid Total |  |  |  | 17536 | 7099 | 175036254
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2019-04-02 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 4402 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2492 | MW
i) Dhaka area |  |  | 2717 | MW | i) Khulna area |  |  | 930 | MW
ii) Chittagong area |  |  | 1002 | MW | ii) Rajshahi area |  |  | 777 | MW
iii) Comilla area |  |  | 175 | MW | iii) Barisal area |  |  | 254 | MW
iv) Mymensingh area |  |  | 369 | MW | iv) Rangpur area |  |  | 531 | MW
v) Sylhet area |  |  | 139 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 6894 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 118 | 1200 | Netrokona | 40 | 2200 | Central s/s | 69 | 1830
Munsiganj | 94 | 1900 | Jamalpur | 64 | 1500 | Noapara | 71 | 1930
Sonargaon | 60 | 1200 | Sherpur | 54 | 2100 | Jessore | 145 | 1900
Shyampur | 182 | 900 | Srimongal | 24 | 1800 | Jhenida | 66 | 100
Bhulta | 161 | 1100 | Shahjibazar | 70 | 1200 | Bottail | 90 | 1200
Madanganj | 56 | 100 | Fenchuganj | 21 | 1300 | G.K Project | 34 | 2000
Shitalakhya | 111 | 1000 | Kulawara | 18 | 1830 | Faridpur | 110 | 1900
Rahim steel | 25 | 2000 | Sylhet | 87 | 2000 | Madaripur | 93 | 1830
Matuail | 96 | 1000 | Chatak | 14 | 2100 | Gopalganj | 67 | 1900
Ghorasal | 50 | 100 | Sunamganj | 16 | 2200 | Bagerhat | 67 | 1930
Narsingdi | 88 | 1000 | Biani Bazar | 25 | 1930 | Mongla | 38 | 1000
Haripur (SBU) | 98 | 1200 | Comilla (S) | 120 | 1300 | Satkhira | 92 | 2200
Ullon | 65 | 1300 | Comilla(N) | 84 | 1100 | Gallamari | 39 | 2100
Hasnabad | 142 | 1300 | Chandpur | 64 | 1300 | Magura | 40 | 2000
Magbazar | 125 | 1300 | Feni | 98 | 1900 | Chuadanga | 62 | 2200
Maniknagar | 110 | 1200 | Chowmuhani | 132 | 1900 | Barisal | 114 | 1930
Bangabhaban | 28 | 1200 | Ashuganj | 40 | 1200 | Patuakhali | 75 | 1900
Narinda | 86 | 1200 | Daudkandi | 82 | 1300 | Bhandaria | 48 | 2000
Dhanmondi | 112 | 1300 | B.Baria | 76 | 1100 | Ishurdi | 35 | 1500
Lalbag | 86 | 1300 | Ramganj | 34 | 1830 | Ruppur Paromanobik | 1 | 100
Madartek | 39 | 1400 | Madunaghat | 51 | 1900 | Natore | 65 | 1300
Mirpur | 92 | 1200 | Hathazari | 82 | 1900 | Bogra | 146 | 1200
Kalyanpur | 75 | 1200 | Khulshi | 200 | 1400 | Noagaon | 86 | 1900
Gulshan | 132 | 1100 | Halishahar | 131 | 1600 | Rajshahi | 114 | 2000
Uttara | 59 | 900 | Baraulia | 121 | 1400 | C.Nawabganj | 66 | 1930
Uttara(New) | 14 | 1100 | Sikalbaha | 42 | 1830 | Amnura | 37 | 1930
Kamrangirchar | 67 | 1100 | Dohazari | 83 | 2100 | Pabna | 73 | 1500
Savar | 114 | 1100 | Cox'sbazar | 88 | 2100 | Shahjadpur | 66 | 1600
Bhasantec | 164 | 1300 | Chandraghona | 23 | 1900 | Serajganj | 68 | 1500
Agargaon | 50 | 1200 | Kaptai | 5 | 1830 | Niyamatpur | 71 | 2000
Satmosjid | 85 | 1300 | A. Khaer Stl. | 0 | 0 | Joypurhat | 33 | 1930
Tongi | 94 | 900 | Bakulia | 99 | 2100 | Mohastangor | 7 | 2000
Kabirpur | 176 | 1000 | Julda | 0 | 0 | Rangpur | 101 | 1930
Basundhara | 130 | 1200 | TK chemical | 5 | 1500 | Lalmonirhat | 69 | 2000
Manikganj | 56 | 2100 | Modern Steel | 15 | 1200 | Saidpur | 78 | 1900
Joydevpur | 193 | 1100 | Shahmirpur | 27 | 100 | Purbasadipur | 88 | 1930
New Tongi | 106 | 1200 | Khagrachhari | 11 | 1000 | Thakurgaon | 57 | 1930
Kodda | 217 | 1200 | Matarbari | 26 | 2100 | Palashbari | 73 | 1930
Dhamrai | 40 | 1200 | Baroiar Hat | 18 | 1800 | Barapukuria | 44 | 2000
Valuka | 52 | 1400 | Rangamati | 12 | 1900 | Panchagar | 37 | 2000
Tangail | 129 | 1500 | Abul Khair 230 | 127 | 1300 | Joldhaka | 12 | 1930
Mymensing | 135 | 1300 | BSRM | 157 | 2100
Kishorganj | 46 | 100 | Goalpara | 22 | 1930
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-04-02
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 389 | 18:30 | 367 | 11:00 | Kaliakoir | 381 | 18:00 | 356 | 12:00
Bheramara | 403 | 3:00 | 384 | 9:00 | Bhulta | 400 | 24:00 | 378 | 12:00
Ashuganj(N) | 400 | 21:00 | 382 | 11:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 235 | 19:30 | 224 | 10:00 | Hathazari | 223 | 23:00 | 212 | 11:00
Ishurdi | 239 | 17:00 | 227 | 12:00 | Megnaghat | 230 | 23:00 | 218 | 12:00
Ashuganj | 240 | 24:00 | 228 | 11:00 | Fenchuganj | 236 | 21:00 | 226 | 11:00
Serajganj | 239 | 17:00 | 227 | 11:00 | Siddhirganj | 227 | 21:00 | 215 | 11:00
Baghabari | 235 | 17:00 | 225 | 11:00 | Maniknagar | 224 | 20:00 | 213 | 15:00
Barapukuria | 230 | 1:00 | 225 | 11:00 | Old Airport | 225 | 18:30 | 212 | 11:00
Bogra | 234 | 17:00 | 222 | 11:00 | Barisal | 241 | 6:00 | 230 | 11:00
Khulna South | 232 | 17:00 | 213 | 11:00 | AKSML | 223 | 22:00 | 211 | 15:00
Rampura | 226 | 23:00 | 216 | 12:00 | BSRM | 227 | 22:00 | 211 | 11:00
Haripur | 224 | 18:30 | 215 | 12:00 | Bibiyana | 235 | 18:00 | 222 | 11:00
Hasnabad | 228 | 18:00 | 215 | 10:00 | Bhulta | 226 | 21:00 | 215 | 12:00
Aminbazar | 227 | 18:30 | 214 | 12:00 | Ashuganj (S) | 237 | 21:00 | 227 | 11:00
Tongi | 224 | 18:00 | 213 | 11:00 | Kaliakoir | 229 | 18:00 | 216 | 11:00
Comilla (N) | 235 | 21:00 | 222 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 132 | 1830 | 125 | 1200 | Madanhat | 133 | 2100 | 127 | 1100
Munsiganj | 134 | 1900 | 124 | 1600 | Hathazari | 131 | 100 | 127 | 1000
Megnaghat | 132 | 2100 | 125 | 1200 | Khulshi | 129 | 2100 | 123 | 1000
Shyampur | 132 | 2100 | 124 | 1200 | Halishahar | 131 | 2100 | 126 | 900
Bhulta | 130 | 1830 | 121 | 1200 | Baraulia | 131 | 2100 | 124 | 1500
Madanganj | 132 | 1800 | 123 | 1600 | Sikalbaha | 132 | 2100 | 125 | 900
Shitalakhya | 134 | 1830 | 122 | 1000 | Dohazari | 130 | 2100 | 124 | 1500
Rahim steal | 133 | 1830 | 126 | 1200 | Cox'sbazar | 123 | 700 | 116 | 1930
Matuail | 130 | 300 | 123 | 2100 | Chandraghona | 134 | 2100 | 126 | 1200
Ghorasal | 145 | 2000 | 133 | 1200 | Kaptai | 135 | 2100 | 126 | 1100
Narsinghdi | 142 | 1900 | 126 | 1100 | A. Khaer Stl. | 131 | 2100 | 126 | 800
Haripur (SBU) | 132 | 1800 | 128 | 1700 | Bakulia | 130 | 2100 | 124 | 900
Ullon | 133 | 1830 | 124 | 1200 | Julda | 132 | 2100 | 126 | 900
Hasnabad | 133 | 1830 | 124 | 1300 | TK Chemical | 133 | 100 | 126 | 1100
Magbazar | 134 | 600 | 125 | 1200 | Modern Steel | 131 | 2100 | 124 | 1100
Maniknagar | 133 | 400 | 126 | 1200 | Shahmirpur | 130 | 100 | 125 | 1100
Bangabhaban | 129 | 600 | 119 | 1300 | Khagrachhari | 134 | 2100 | 123 | 1900
Narinda | 133 | 600 | 124 | 1300 | Matarbari | 123 | 700 | 118 | 1500
Dhanmondi | 133 | 1830 | 124 | 1200 | Baroiar Hat | 129 | 500 | 123 | 1100
Lalbag | 129 | 600 | 119 | 1300 | Rangamati | 133 | 2100 | 126 | 1100
Madartek | 133 | 600 | 124 | 1300 | Goalpara | 137 | 2200 | 124 | 1100
Mirpur | 132 | 1830 | 122 | 1100 | Central s/s | 136 | 2200 | 123 | 1100
Kalyanpur | 135 | 1830 | 126 | 1100 | Noapara | 135 | 2200 | 121 | 1100
Gulshan | 133 | 1830 | 124 | 1200 | Jessore | 130 | 2200 | 118 | 1100
Uttara | 131 | 1830 | 121 | 1200 | Jhenida | 131 | 2200 | 119 | 1100
Uttara New | 132 | 1800 | 121 | 1200 | Bottail | 137 | 1700 | 128 | 1100
Kamrangirchar | 132 | 1830 | 121 | 1200 | G.K.Project | 142 | 600 | 136 | 1100
Savar | 131 | 1830 | 122 | 1200 | Faridpur | 131 | 700 | 122 | 1300
Bhasantec | 135 | 1830 | 125 | 1200 | Madaripur | 132 | 300 | 122 | 1100
Agargaon | 135 | 1900 | 126 | 1100 | Gopalganj | 134 | 2000 | 122 | 1100
Satmosjid | 135 | 1830 | 126 | 1200 | Bagerhat | 135 | 1930 | 120 | 1100
Tongi | 133 | 1800 | 126 | 1300 | Mongla | 130 | 1700 | 123 | 1000
Kabirpur | 140 | 1800 | 128 | 1100 | Satkhira | 134 | 500 | 123 | 1100
Basundhara | 129 | 2100 | 120 | 1100 | Gallamari | 137 | 600 | 125 | 1100
Manikganj | 138 | 1800 | 129 | 900 | Magura | 130 | 2200 | 119 | 1200
Joydevpur | 143 | 1800 | 130 | 1200 | Chuadanga | 128 | 1700 | 115 | 1100
New Tongi | 134 | 1800 | 124 | 1300 | Barisal | 139 | 1700 | 132 | 1100
Kodda | 144 | 1830 | 127 | 1100 | Patuakhali | 135 | 500 | 125 | 1100
Dhamrai | 140 | 1800 | 128 | 1100 | Bhandaria | 135 | 1700 | 124 | 1100
Valuka | 140 | 1800 | 125 | 1200 | Ishurdi | 141 | 1700 | 134 | 1100
Tangail | 145 | 1800 | 130 | 1000 | Ruppur Paromanobik | 141 | 200 | 134 | 1200
Mymensing | 140 | 1800 | 130 | 1000 | Natore | 139 | 1700 | 128 | 1100
Kishorganj | 140 | 1800 | 131 | 900 | Bogra | 142 | 1700 | 132 | 1100
Netrokona | 141 | 1800 | 130 | 900 | Noagaon | 138 | 1700 | 129 | 1100
Jamalpur | 138 | 1800 | 125 | 300 | Rajshahi | 135 | 1600 | 123 | 1100
Sherpur | 138 | 1800 | 125 | 1000 | C.Nawabganj | 128 | 1700 | 120 | 700
Srimongal | 140 | 1830 | 132 | 1100 | Amnura | 132 | 1600 | 120 | 1100
Shahjibazar | 140 | 1800 | 131 | 1100 | Pabna | 137 | 1700 | 126 | 1100
Fenchuganj | 136 | 600 | 132 | 1300 | Shahjadpur | 146 | 1700 | 135 | 1100
Khulawara | 135 | 100 | 131 | 1200 | Serajganj | 142 | 1700 | 132 | 1000
Sylhet | 134 | 100 | 130 | 2000 | Niyamatpur | 138 | 1700 | 125 | 2000
Chatak | 134 | 100 | 130 | 2000 | Joypurhat | 140 | 1700 | 129 | 1000
Sunamganj | 134 | 400 | 129 | 2200 | Mohastangor | 140 | 1700 | 130 | 1100
Biani Bazar | 135 | 100 | 130 | 1930 | Rangpur | 130 | 500 | 121 | 1300
Comilla(s) | 135 | 1600 | 123 | 1000 | Lalmonirhat | 130 | 1700 | 118 | 1000
Comilla(n) | 140 | 2000 | 129 | 1200 | Saidpur | 131 | 500 | 120 | 1000
Chandpur | 139 | 2000 | 124 | 1800 | Purbasadipur | 130 | 200 | 120 | 1000
Feni | 135 | 2100 | 123 | 1200 | Thakurgaon | 125 | 500 | 112 | 1100
Chowmuhani | 135 | 2000 | 122 | 1200 | Palashbari | 134 | 1700 | 121 | 1000
Ashuganj | 144 | 1830 | 135 | 1000 | Barapukuria | 130 | 100 | 125 | 1100
Daudkandi | 135 | 2000 | 123 | 1200 | Panchagar | 124 | 400 | 108 | 1100
B.Baria | 140 | 1900 | 129 | 1100 | Joldhaka | 128 | 200 | 118 | 1200

## L-Curve
Date | 2019-04-02
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 50 | 4372 | 2234 | 6606 |  |  |  | QF-LDC-12
0:30 | 97 | 4763.5 | 2348 | 7111.5 | Date: | 2019-04-02
1:00 | 144 | 5155 | 2462 | 7617
1:30 | 137 | 5118.5 | 2380 | 7498.5
2:00 | 130 | 5082 | 2298 | 7380
2:30 | 160 | 4967 | 2258.5 | 7225.5 | [5 empty] | Gen. at Eve. Peak | 7099 | 7099 MW (21:00 )
3:00 | 190 | 4852 | 2219 | 7071 | [6 empty] | 21:00
3:30 | 210 | 4798.5 | 2222 | 7020.5 | [5 empty] | Gen. at Day Peak | 8703.6 | 8703.6 MW (12:00 )
4:00 | 230 | 4745 | 2225 | 6970 | [6 empty] | 12:00
4:30 | 235 | 4682 | 2215 | 6897 | [5 empty] | Highest Generation | 8721.9
5:00 | 240 | 4619 | 2205 | 6824 | [6 empty] | 13:00
5:30 | 225 | 4601.65 | 2193.5 | 6795.15
6:00 | 210 | 4584.3 | 2182 | 6766.3
6:30 | 120 | 4681.55 | 2195.5 | 6877.05
7:00 | 30 | 4778.8 | 2209 | 6987.8
7:30 | 130 | 4798.45 | 2214 | 7012.45
8:00 | 230 | 4818.1 | 2219 | 7037.1
8:30 | 340 | 4908.6 | 2391.5 | 7300.1
9:00 | 450 | 4999.1 | 2564 | 7563.1
9:30 | 405 | 5197.7 | 2563 | 7760.7
10:00 | 360 | 5396.3 | 2562 | 7958.3
10:30 | 365 | 5485.5 | 2596 | 8081.5
11:00 | 370 | 5574.7 | 2630 | 8204.7
11:30 | 350 | 5756.15 | 2698 | 8454.15
12:00 | 330 | 5937.6 | 2766 | 8703.6
12:30 | 315 | 5964.25 | 2748.5 | 8712.75
13:00 | 300 | 5990.9 | 2731 | 8721.9
13:30 | 310 | 5581.95 | 2679 | 8260.95
14:00 | 320 | 5173 | 2627 | 7800
14:30 | 370 | 4998.1 | 2626 | 7624.1
15:00 | 420 | 4823.2 | 2625 | 7448.2
15:30 | 530 | 4734.1 | 2591.5 | 7325.6
16:00 | 640 | 4645 | 2558 | 7203
16:30 | 670 | 4468.8 | 2438.5 | 6907.3
17:00 | 700 | 4292.6 | 2319 | 6611.6
17:30 | 370 | 3998.8 | 2299.5 | 6298.3
18:00 | 40 | 3705 | 2280 | 5985
18:30 | 110 | 3834.5 | 2354.5 | 6189
19:00 | 180 | 3964 | 2429 | 6393
19:30 | 160 | 4329 | 2547 | 6876
20:00 | 190 | 4258 | 2474 | 6732 |  |  |  | Executive Engineer
20:30 | 145 | 4364.5 | 2551 | 6915.5 |  |  |  | Network Operation Division
21:00 | 100 | 4471 | 2628 | 7099
21:30 | 90 | 4278.5 | 2610.5 | 6889
22:00 | 80 | 4086 | 2593 | 6679 |  |  |  |  | Page 6 of 7
22:30 | 55 | 4202 | 2431.5 | 6633.5
23:00 | 30 | 4318 | 2270 | 6588
23:30 | 40 | 4345 | 2252 | 6597
24:00 | 50 | 4372 | 2234 | 6606
7099 MW (21:00 )
8703.6 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-04-02 |  | Energy | 175036254
[10 empty] | 2019-04-02 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3582 | 647 | 1534 | 421 | 210 | 83 | 67 | 0 | 62
0:30 | 3799.5 | 677.5 | 1681.5 | 508 | 212.5 | 81 | 68.5 | 0 | 83 | Date: | 2019-04-02
1:00 | 4017 | 708 | 1829 | 595 | 215 | 79 | 70 | 0 | 104
1:30 | 4021 | 635.5 | 1831 | 563 | 214.5 | 79 | 52.5 | 0 | 102 | [7 empty] | Total Energy | 175.0363 | Total Energy Gen 175.036 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 175.036 MKWHr
2:00 | 4025 | 563 | 1833 | 531 | 214 | 79 | 35 | 0 | 100 | [7 empty] | Energy not Served | 0
2:30 | 3986 | 562.5 | 1781 | 473.5 | 214.5 | 79 | 31 | 0 | 98 | [7 empty] | Energy Requirement | 175.0363
3:00 | 3947 | 562 | 1729 | 416 | 215 | 79 | 27 | 0 | 96
3:30 | 3949.5 | 561.5 | 1706 | 387 | 215 | 79.5 | 27 | 0 | 95 | [6 empty] | Shortage
4:00 | 3952 | 561 | 1683 | 358 | 215 | 80 | 27 | 0 | 94
4:30 | 3939 | 561.5 | 1635 | 347 | 215.5 | 80 | 27 | 0 | 92
5:00 | 3926 | 562 | 1587 | 336 | 216 | 80 | 27 | 0 | 90
5:30 | 3901.5 | 562 | 1581.5 | 335.5 | 215.5 | 81 | 27 | 0 | 91
6:00 | 3877 | 562 | 1576 | 335 | 215 | 82 | 27 | 0 | 92
6:30 | 3951.5 | 562 | 1611 | 337.5 | 215 | 81 | 27 | 0 | 90 |  |  |  |  | Coal
7:00 | 4026 | 562 | 1646 | 340 | 215 | 80 | 27 | 0 | 88
7:30 | 4044 | 561.5 | 1631.5 | 345.5 | 214.5 | 80 | 39 | 0 | 90 |  |  |  | Oil |  |  |  | ,
8:00 | 4062 | 561 | 1617 | 351 | 214 | 80 | 51 | 0 | 92
8:30 | 4147 | 709.5 | 1635.5 | 352 | 214.5 | 80.5 | 55.5 | 0 | 94
9:00 | 4232 | 858 | 1654 | 353 | 215 | 81 | 60 | 0 | 96
9:30 | 4237 | 858 | 1738.5 | 446 | 214.5 | 82 | 65 | 0 | 104
10:00 | 4242 | 858 | 1823 | 539 | 214 | 83 | 70 | 0 | 112
10:30 | 4279.5 | 857.5 | 1830 | 634 | 212.5 | 83 | 63 | 0 | 113
11:00 | 4317 | 857 | 1837 | 729 | 211 | 83 | 56 | 0 | 114
11:30 | 4308.5 | 857.5 | 1873 | 944.5 | 212 | 82 | 61.5 | 0 | 114
12:00 | 4300 | 858 | 1909 | 1160 | 213 | 81 | 67 | 0 | 114
12:30 | 4272 | 858 | 1901.5 | 1194 | 215 | 80.5 | 66 | 0 | 117
13:00 | 4244 | 858 | 1894 | 1228 | 217 | 80 | 65 | 0 | 120
13:30 | 4244 | 858 | 1894 | 1228 | 217 | 80 | 65 | 0 | 120
14:00 | 4244 | 858 | 1894 | 1228 | 217 | 80 | 65 | 0 | 120
14:30 | 4088.5 | 858 | 1647.5 | 1041 | 216.5 | 79.5 | 40.5 | 0 | 99
15:00 | 3933 | 858 | 1401 | 854 | 216 | 79 | 16 | 0 | 78
15:30 | 3923.5 | 858 | 1352 | 826 | 215.5 | 79 | 18 | 0 | 43
16:00 | 3914 | 858 | 1303 | 798 | 215 | 79 | 20 | 0 | 8
16:30 | 3653 | 858 | 1276.5 | 764.5 | 215 | 79 | 39 | 0 | 17
17:00 | 3392 | 858 | 1250 | 731 | 215 | 79 | 58 | 0 | 26
17:30 | 3141.5 | 858 | 1209.5 | 675.5 | 212 | 79 | 85.5 | 0 | 36
18:00 | 2891 | 858 | 1169 | 620 | 209 | 79 | 113 | 0 | 46
18:30 | 3061 | 728 | 1236.5 | 609.5 | 210.5 | 79.5 | 225 | 0 | 39
19:00 | 3231 | 598 | 1304 | 599 | 212 | 80 | 337 | 0 | 32
19:30 | 3503 | 599 | 1383 | 724 | 209 | 80 | 370 | 0 | 8
20:00 | 3416 | 599 | 1407 | 699 | 210 | 80 | 299 | 0 | 22
20:30 | 3470.5 | 671.5 | 1461.5 | 690 | 210.5 | 80 | 298.5 | 0 | 33
21:00 | 3525 | 744 | 1516 | 681 | 211 | 80 | 298 | 0 | 44
21:30 | 3460 | 744 | 1491.5 | 622.5 | 211 | 80 | 228 | 0 | 52
22:00 | 3395 | 744 | 1467 | 564 | 211 | 80 | 158 | 0 | 60
22:30 | 3470 | 695.5 | 1498.5 | 489 | 210.5 | 81.5 | 123.5 | 0 | 65
23:00 | 3545 | 647 | 1530 | 414 | 210 | 83 | 89 | 0 | 70
23:30 | 3563.5 | 647 | 1532 | 417.5 | 210 | 83 | 78 | 0 | 66 | Max Temp. in Dhaka |  | 32° C
24:00 | 3582 | 647 | 1534 | 421 | 210 | 83 | 67 | 0 | 62
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 175.036 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 175.036 MKWHr
Note on W13: Author:

## Generation
2019-04-02
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 79 | 79 | 79 | 80 | 80 | 82 | 80 | 80 | 81 | 83 | 83 | 81 | 80 | 79 | 79 | 79 | 79 | 79 |  | 80 | 80 | 80 | 80 | 80 | 83 | 83 | 1841765
2 | Kaptai Unit-4 & 5
3 | Chattogram ST-1 (Raozan) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2500000
4 | Chittgong ST-2 (Raozan) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 120 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 3300000
5 | Raozan 25 MW (RPCL) | [19 empty] | 12 | 16 | 16 | 16 | 8 | 0 | 0 | 68286
| Teknaf Solartech 20MW | [5 empty] | 0.3 | 3.7 | 8.5 | 13.3 | 16.8 | 0 | 0 | 14.6 | 0 | 12 | 8 | 2.6 | 0 | [8 empty] | 80865
6 | Sikalbaha 225MW (Gas) | 215 | 204 | 204 | 203 | 203 | 202 | 204 | 218 | 205 | 199 | 209 | 204 | 208 | 195 | 217 | 203 | 190 | 170 |  | 187 | 204 | 214 | 203 | 184 | 178 | 203 | 4817638
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | [15 empty] | 4 | 17 | 21 |  | 68 | 80 | 80 | 80 | 17 | 0 |  | 296796
12 | Hathazari peaking | [11 empty] | 9 | 0 |  |  |  |  | 9 |  | 51 | 51 | 51 | 50 | 0 |  |  | 161578
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 152 | 152 | 80 | 80 | 80 | 70 | 120 | 120 | 150 | 190 | 195 | 190 | 190 | 105 | 73 | 80 | 80 | 70 |  | 0 | 0 | [5 empty] | 2376000
17 | Siddhirganj CCPP-335 MW
18 | Summit Gazipur -2 | [9 empty] | 7 | 30 | 31 | 31 | 13 | 13 | 12 | 13 | 13 |  | 0 | [6 empty] | 198220
19 | Ashuganj 195MW Modular | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 434909
20 | Ghorasal ST: Unit-1,2 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 |  | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 1716000
21 | Ghorasal GT: Unit-3 | 134 | 133 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 133 | 133 | 133 | 135 | 134 | 134 | 134 | 94 | 95 |  | 95 | 95 | 95 | 94 | 94 | 94 | 93 | 3076800
22 | Ghorasal GT: Unit-4 | [13 empty] | 0 | 40 | 72 | 95 | 30 |  | 30 | 44 | 50 | 50 | 36 | 50 | 48 | 495000
23 | Ghorasal ST: Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 120 | 120 | 120 | 120 | 2787750
24
25 | Ghorasal ST: Unit-7 | 203 | 202 | 202 | 202 | 202 | 202 | 225 | 240 | 300 | 300 | 340 | 380 | 340 | 275 | 300 | 280 | 140 | 40 |  | 120 | 200 | 220 | 220 | 220 | 220 | 220 | 5730436
26
28 | Ashuganj ST: Unit- 3 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 80 | 80 | 80 | 80 | 80 |  | 0 | 0 | [5 empty] | 1937665
29 | Ashuganj ST: Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 0 | [8 empty] | 1375405
30 | Ashuganj ST: Unit- 5 | [16 empty] | 36 | 37 |  | 55 | 55 | 55 | 55 | 80 | 80 | 80 | 440792
32 | Ashuganj Engines TSK | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 33 | 40 | 31 | 37 | 37 | 40 | 10 | 10 | 10 |  | 10 | 10 | 40 | 40 | 40 | 40 | 37 | 760464
33 | Ashuganj CCPP 225 MW | 194 | 193 | 195 | 181 | 185 | 182 | 197 | 200 | 190 | 219 | 205 | 186 | 187 | 183 | 187 | 175 | 155 | 145 |  | 182 | 188 | 200 | 184 | 184 | 170 | 183 | 4545000
34 | Ashuganj CCPP(South) | [13 empty] | 36 | 88 | 99 | 128 | 154 |  | 270 | 300 | 300 | 360 | 300 | 300 | 300 | 2219500
| Ashuganj CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 320 | 360 | 360 | 360 | 360 | 330 | 315 | 270 | 270 | 230 | 210 |  | 250 | 300 | 300 | 360 | 260 | 280 | 300 | 7362000
35 | Ashuganj (Precision) 55MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 20 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 159360
36 | Chandpur CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 0 |  |  | 0 |  | 100 | 100 | 0 |  |  | 100 | 100 | 1710040
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 340 | 345 | 340 | 355 | 343 | 342 | 354 | 343 | 356 | 358 | 356 | 353 | 353 | 300 | 300 | 345 | 320 | 250 |  | 230 | 340 | 320 | 320 | 335 | 360 | 344 | 8258560
40 | Meghnaghat CCPP 450MW | 330 | 330 | 330 | 330 | 330 | 330 | 360 | 360 | 400 | 400 | 405 | 405 | 405 | 320 | 280 | 280 | 280 | 250 |  | 240 | 300 | 300 | 340 | 340 | 330 | 330 | 7936000
41 | Haripur Power CCPP 360MW | 281 | 283 | 283 | 283 | 283 | 282 | 322 | 323 | 320 | 355 | 352 | 350 | 320 | 281 | 250 | 240 | 210 | 190 |  | 290 | 310 | 310 | 313 | 256 | 308 | 308 | 6959000
42 | Mymensingh RPCL 210MW | 212 | 211 | 213 | 213 | 213 | 213 | 211 | 210 | 210 | 208 | 193 | 192 | 177 | 177 | 176 | 177 | 183 | 152 |  | 150 | 150 | 150 | 147 | 147 | 147 | 147 | 4377600
43 | Haripur NEPC 110MW
44 | Fenchugonj CCPP-1 | 59 | 59 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 58 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 1199000
45 | Fenchugonj CCPP-2 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 50 | 50 | 50 | 60 | 60 | 50 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1109234
46 | Shajibazar 330 MW | 264 | 273 | 274 | 266 | 267 | 268 | 267 | 269 | 266 | 270 | 272 | 266 | 264 | 264 | 268 | 267 | 235 | 214 |  | 171 | 171 | 171 | 150 | 150 | 150 | 137 | 5442000
47 | Shahjibazar GT: Unit- 8, 9 | 69 | 67 | 67 | 67 | 67 | 57 | 67 | 66 | 65 | 65 | 0 | 20 | 50 | 44 | 66 | 52 | 40 | 35 |  | 52 | 69 | 68 | 40 | 40 | 53 | 53 | 1299648
48 | Shahjibazar 86MW | 83 | 83 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 5 |  | 5 | 0 | 5 | 5 | 5 | 5 | 5 | 415680
49 | Shahjibazar (EPL) 50MW | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 46 | 0 | 32 | 45 | 10 | 10 | 10 | 5 | 5 |  | 0 | 0 | 5 | 5 | 5 | 5 | 5 | 666000
50 | Sylhet GT 150 MW | 93 | 89 | 93 | 91 | 85 | 85 | 89 | 98 | 95 | 85 | 97 | 84 | 83 | 84 | 96 | 84 | 84 | 76 |  | 95 | 28 | 0 |  |  |  |  | 1805430
51 | Sylhet GT 20 MW
52 | Sylhet (EPL) 50MW | 47 | 47 | 47 | 47 | 6 | 6 | 7 | 7 | 7 | 42 | 42 | 47 | 47 | 12 | 11 | 5 | 11 | 6 |  | 6 | 6 | 0 |  |  |  | 7 | 491080
53 | Sylhet (Desh) 10MW | 0 | [25 empty] | 6840
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 8 | 8 | 0 | [11 empty] | 111168
55 | Fenchugonj (Barakatullah) 51MW | 53 | 53 | 53 | 5 | 5 | 5 | 5 | 5 | 5 | 31 | 45 | 45 | 48 | 31 | 28 | 5 | 0 | [7 empty] | 5 | 5 | 447000
56 | Shahjahanulla 25 MW | [25 empty] | 4 | 75213
57 | Summit Bibiana- 2 | [21 empty] | 10 | 12 | 15 | 40 | 55 | 78732
58 | Southern 55MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 |  | 0 | [6 empty] | 315247
59 | Sikalbaha (Energis) | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 32 | 32 | 32 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 24 | 24 | 926400
60 | Barabkunda (Regent) | 19 | 19 | 20 | 19 | 19 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 20 | 20 |  | 20 | 20 | 21 | 21 | 0 | 20 | 21 | 441210
61 | Narshingdi (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 16 | 16 | 16 | 19 | 19 | 0 |  |  | 0 | [9 empty] | 221760
62 | Tangail (Doreen) 22MW | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 |  |  |  | 0 | 20 | 20 | 20 | 20 | 20 | 388728
63 | Tripura | 104 | 100 | 96 | 94 | 90 | 92 | 88 | 92 | 96 | 112 | 114 | 114 | 120 | 90 | 78 | 8 | 26 | 46 |  | 32 | 8 | 22 | 44 | 60 | 70 | 62 | 1891200
64 | Malancha, Ctg. EPZ (United) | 37 | 37 | 37 | 37 | 36 | 25 | 30 | 2 | 2 | 2 | 2 | 2 | 5 | 2 | 2 | 2 | 2 | 2 |  | 7 | 13 | 15 | 16 | 16 | 20 | 26 | 368160
65 | Feni (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 18 | 18 | 19 | 19 | 18 | 18 | 19 | 22 | 22 |  | 22 | 22 | 0 |  |  |  |  | 389340
66 | Feni, Mohipal (Doreen) | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 8 | 8 | 8 |  | 8 | 8 | 0 |  |  |  |  | 135540
67 | Jangalia (Summit) 33MW | [12 empty] | 0 | 8 | 8 | 0 | [10 empty] | 16000
68 | Summit Cumilla 25MW | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | [9 empty] | 200050
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 575000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 8 | 25 | 30 | 30 | 31 | 32 | 32 | 32 | 32 |  | 32 | 32 | 0 |  | 16 | 32 | 32 | 600480
71 | Summit Maona | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 0 |  | 6 | 24 | 33 | 33 | 33 | 705000
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 33 | 33 | 0 |  |  |  |  | 33 | 33 | 33 | 33 | 707600
73 | Ghorashal (Regent) | 107 | 107 | 107 | 107 | 107 | 107 | 108 | 107 | 104 | 104 | 108 | 105 | 105 | 52 | 13 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 1590136
76 | Siddhirganj (Desh)
77 | Siddhirganj (Dutch Bangla)
78 | Gazipur (RPCL) | 33 | 16 | 8 | 8 |  |  | 4 | 25 | 31 | 51 | 51 | 43 | 50 | 50 | 8 | 8 | 8 | 0 | [8 empty] | 430176
79 | Kodda 149MW | [8 empty] | 6 | 16 | 16 | 25 | 32 | 32 | 16 | 16 | 16 | 16 |  | 0 | [6 empty] | 188160
80 | Jamalpur 95MW | [19 empty] | 7 | 7 | 7 | 7 | 0 |  |  | 23040
81 | Lakdhanvi 52 MW
82 | Madanganj 102MW
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj (Powerpac) 100MW
86 | Meghnaghat CCPP(Summit) | 150 | 150 | 150 | 120 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 155 | 155 | 120 |  | 120 | 155 | 160 | 160 | 140 | 215 | 255 | 3750924
87 | Meghnaghat (IEL)
88 | Ghorashal 78MW (MAX) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 60 | 69 | 69 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 1417472
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 255480
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 50 | 5 | 5 | 5 | 5 | 5 | 16 | 50 | 47 | 47 | 30 | 30 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 490000
93 | Ashuganj (Midland) 51MW | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 14 | 35 | 35 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 366740
94 | Gagnagar (Orion) | [8 empty] | 3 | 7 | 25 | 70 | 70 | 50 | 24 | 24 | 32 | 42 |  | 24 | 24 | 24 | 7 | 0 |  |  | 480384
95 | Patenga 50MW | 50 | 50 | 50 | 50 | 19 | 18 | 18 | 18 | 18 | 26 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 19 | 18 | 945440
96 | Chattogram ECPV 108 MW | 19 | 12 | 12 | 12 | [6 empty] | 9 | 14 | 30 | 30 | 15 | 32 | 45 | 25 |  | 27 | 27 | 27 | 26 | 20 | 13 | 13 | 420480
97 | Katpotti 51 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 156528
98 | Bosila 108MW | [8 empty] | 0 | 43 | 41 | 47 | 47 | 46 | 8 | 8 | 8 | 0 | [8 empty] | 242880
99 | Madanganj-55 MW | [11 empty] | 23 | 31 | 15 | 0 | [11 empty] | 95719
100 | Northern 55 MW | 17 | 17 | 17 | 18 | 17 | 17 | 18 | 17 | 17 | 17 | 17 | 17 | 18 | 0 |  |  |  | 18 |  | 0 | [6 empty] | 248651
101 | Kushiara 163 MW CCPP GT | 130 | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 163 | 163 | 163 | 163 | 100 | 130 | 100 | 100 | 100 |  | 100 | 100 | 100 | 163 | 163 | 163 | 130 | 3255921
102 | Sarishabari (Solar) | [6 empty] | 0.1 | 0.6 | 0.8 | 0.5 | 0.7 | 1.6 | 1.3 | 2 | 1.2 | 0 | [10 empty] | 8300
103 | Banco Energy 54MW | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 893520
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW | [8 empty] | 0 | 16 | 50 | 50 | 50 | 50 | 20 | 17 | 16 | 12 |  | 0 | [6 empty] | 305280
115 | Juldah 100 MW Unit-3 | 100 | 60 | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 75 | 90 | 90 | 100 | 100 | 100 | 100 | 100 | 70 |  | 70 | 70 | 70 | 70 | 70 | 30 | 30 | 1448640
116 | Chandpur Desh 200MW | [10 empty] | 0 | 40 | 52 | 44 | 17 | 35 | 17 | 17 |  | 0 | [6 empty] | 241440
117 | Midland 150MW | [10 empty] | 3 | 53 | 70 | 48 | 0 | [11 empty] | 222470
118 | Bibiyana-3 285MW | [10 empty] | 0 | 0 | 0
| United Jamalpur PPL | [10 empty] | 9 | 106 | 104 | 104 | 110 | 54 | 0 | [9 empty] | 598800
120 | Eastern Zone Total | 5155 | 5082 | 4852 | 4745 | 4619 | 4584.3 | 4778.8 | 4818.1 | 4999.1 | 5396.3 | 5574.7 | 5937.6 | 5990.9 | 5173 | 4823.2 | 4645 | 4292.6 | 3705 |  | 3964 | 4329 | 4258 | 4471 | 4086 | 4318 | 4372 | 117148750
121
122 | o
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | [17 empty] | 2 |  | 19 | 32 | 32 | 32 | 32 | 0 |  | 119040
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | 30 | 30 | 27 | 27 | 27 | 27 | 27 | 21 | 21 | 21 | 7 | 0 | [5 empty] | 13 |  | 35 | 34 | 33 | 31 | 29 | 29 | 29 | 441120
Khulna CCPP 225MW
129 | Labon Chora 105 MW | 53 | 53 | 28 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 53 | 53 | 53 | 53 | 53 | 53 | 17 |  | 17 | 90 | 90 | 90 | 90 | 0 |  | 960960
130
131
132
133
| Summit Barisal 110 MW | 64 | 64 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 48 | 48 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 110 | 110 | 80 | 80 | 80 | 80 | 48 | 1516800
136 | Barisal GT: Unit-1, 2
137 | Bhola Aggreko 95MW | 97 | 97 | 97 | 98 | 97 | 97 | 96 | 96 | 97 | 96 | 95 | 95 | 94 | 96 | 95 | 95 | 96 | 52 |  | 97 | 97 | 97 | 97 | 96 | 97 | 96 | 2264163
| Bhola CCPP 194MW | 180 | 181 | 182 | 181 | 181 | 163 | 181 | 180 | 180 | 161 | 178 | 179 | 178 | 153 | 178 | 177 | 155 | 161 |  | 181 | 182 | 181 | 167 | 178 | 128 | 136 | 2947000
140 | Bhola (Venture) 33MW | 25 | 25 | 23 | 23 | 23 | 20 | 19 | 18 | 20 | 21 | 21 | 23 | 23 | 23 | 15 | 15 | 23 | 24 |  | 31 | 31 | 34 | 32 | 32 | 24 | 26 | 528259
141 | Bangla Trak Noapara
142 | Noapara (KZA) 40MW | [11 empty] | 24 | 24 | 24 | 24 | 24 | 8 | 8 |  | 24 | 24 | 24 | 24 | 0 |  |  | 201375
143 | Gopalganj Peaking | 40 | 5 | 0 | [13 empty] | 25 | 40 |  | 55 | 70 | 0 | 2 | 12 | 20 | 20 | 245888
144 | Bheramara GT-1,2,3
145 | Madhumati Power Plant
146 | Bheramara HVDC | 708 | 563 | 562 | 561 | 562 | 562 | 562 | 561 | 858 | 858 | 857 | 858 | 858 | 858 | 858 | 858 | 858 | 858 |  | 598 | 599 | 599 | 744 | 744 | 647 | 647 | 16753454
147 | Bheramara 360 MW | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 230 | 230 | 300 | 270 | 270 | 230 | 200 | 200 | 100 | 100 |  | 220 | 220 | 220 | 220 | 220 | 230 | 230 | 5495904
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2 | 66 | 65 | 66 | 66 | 67 | 66 | 66 | 65 | 66 | 65 | 63 | 64 | 68 | 66 | 67 | 66 | 66 | 60 |  | 63 | 60 | 61 | 62 | 62 | 61 | 61 | 1545599
152 | Barapukuria Unit-3 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 148 | 149 | 149 | 144 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3643400
153 | Baghabari GT 71MW
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | [17 empty] | 0 |  | 0 | [6 empty] | 8437
157 | Sirajgonj Unit-1 225MW (Gas) | 187 | 194 | 188 | 196 | 189 | 187 | 194 | 189 | 195 | 194 | 195 | 193 | 185 | 171 | 191 | 176 | 130 | 125 |  | 125 | 130 | 150 | 172 | 180 | 166 | 164 | 4517673
158 | Sirajgonj Unit-1 225MW (Oil)
| Sirajgonj Unit-2 225MW (Gas) | 189 | 196 | 190 | 199 | 193 | 190 | 197 | 192 | 202 | 200 | 198 | 194 | 181 | 151 | 199 | 188 | 135 | 132 |  | 131 | 132 | 132 | 132 | 132 | 148 | 154 | 4362973
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas)
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas) | 431 | 433 | 434 | 435 | 430 | 434 | 425 | 425 | 425 | 425 | 418 | 418 | 415 | 416 | 415 | 415 | 420 | 442 |  | 435 | 430 | 435 | 435 | 441 | 435 | 443 | 10312364
161 | Bera Peaking | [17 empty] | 5 |  | 0 | [6 empty] | 7688
162 | Bogra (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 3 | 3 |  | 3 | 3 | 3 | 5 | 5 | 5 | 5 | 379440
163 | Bogra (EPL) | 16 | 16 | 16 | 16 | 13 | 13 | 17 | 17 | 17 | 17 | 14 | 15 | 0 | 9 | 17 | 14 | 0 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 240624
164 | Ullapara (Summit) | 5 | 5 | 3 | 3 | 3 | 3 | 5 | 5 | 0 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 0 |  |  |  | 8 | 8 | 8 | 8 | 8 | 5 | 127170
165 | Amnura 50MW | [17 empty] | 0 |  | 0 | [6 empty] | 14100
166 | Katakhali (Northern) | [17 empty] | 0 |  | 0 | [6 empty] | 5148
167 | Katakhali Peaking | [26 empty] | 6098
168 | Santahar Peaking | [17 empty] | 0 |  | 0 | [6 empty] | 6040
169 | Rajlanka 52 MW | [17 empty] | 0 |  | 8 | 8 | 8 | 8 | 0 | 0 |  | 31200
170 | Chapainawabganj-100 MW | [7 empty] | 30 | 33 | 33 | 33 | 33 | 33 | 33 | 0 |  |  | 9 |  | 93 | 100 | 100 | 100 | 100 | 40 | 18 | 669987
171 | Paramount Baghabari
172 | Confidence CPBL-2 | [10 empty] | 11 | 91 | 90 | 90 | 54 | 18 | 18 | 0 | [8 empty] | 417600
173 | Rangpur GT | [17 empty] | 0 |  | 17 | 17 | 17 | 17 | 0 | 0 |  | 50000
175 | Saidpur GT | [17 empty] | 0 |  | 18 | 18 | 18 | 18 | 0 | 0 |  | 68000
176
177
178
178 | Western Zone Total | 2462 | 2298 | 2219 | 2225 | 2205 | 2182 | 2209 | 2219 | 2564 | 2562 | 2630 | 2766 | 2731 | 2627 | 2625 | 2558 | 2319 | 2280 |  | 2429 | 2547 | 2474 | 2628 | 2593 | 2270 | 2234 | 57887504