## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2024-01-22 | Monday
|  | Date (day): | 2024-01-22 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10329.6 | MW |  |  | (b) At Evening Peak Hour : |  | 11175 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-01-21 | 2024-01-22 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 100 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 12 | 15 | 93 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 25 | 400 | 412
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 81 | 53 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 82 | 30 | 82 |  | 20 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 2 | 15 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 22 | 25 | 30 | 30 | 45 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 75 | 73 | 70 | 73 |  | 27 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 58 | 91 | 70 | 90 |  | 12 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 17 | 0 | 54 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 82 | 149 | 32 | 149 |  |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 39 | 39 | 40 | 40 |  | 40 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 30 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 14 | 23 | 21 | 23 |  | 10 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 17 | 8 | 17 | 35 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 148 | 260 | 80 | 260 | 40 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 36 | 96 | 35 | 50 | 99 |  | Fuel shortage
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 105 | 17 | 105
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 39 | 72 | 35 | 51 | 53 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 17 | 17 | 17 | 145 |  | Fuel shortage
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 20 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 200 | 200 |  |  | on test
| Dhaka area Total |  |  |  |  | 5763 | 5062 | 1304 | 1868 | 1924 | 2443 | 1754 | 1049
38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
39 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 17 | 8 | 17 | 8 |  | Fuel shortage
40 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 17 | 0 | 20 | 0
41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 19 | 6 | 19 | 31 |  | Fuel shortage
42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 76 | 76 | 76 | 76 | 154 |  | Low water lavel
43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 16 | 16 | 15 | 16 | 89 |  | Fuel shortage
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 64 | 64 | 60 | 64 | 34 |  | Fuel shortage
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 51 | 51 | 51 | 51 | 51 |  | Fuel shortage
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 19 | 18 | 18
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 15 | 5 | 10
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 49 | 106 | 50 | 105 | 195 |  | Fuel shortage
54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 1 | 0 | 0 | 0 | 54 |  | Fuel shortage
55 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 17 | 17 | 93 |  | Fuel shortage
56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
57 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 17 | 99 |  | Fuel shortage
58 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 72 | 36 | 17 | 36 | 127 |  | Fuel shortage
59 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 396 | 480 | 400 | 480 | 744 |  | Coal Shortage.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 0 | 0 | 10 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 154 | 419 | 400 | 420 |  |  | On test.
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4404 | 4344 | 1048 | 1427 | 1250 | 1431 | 2417 | 330
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 156 | 147 | 130 | 145 |  | 76 | ST Under maint.
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 330 | 320 | 330 |  |  | FGMO
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Under maint
63 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 | 400 |  | Gas shortage
64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 0 | 0 | 0 | 45 |  | Gas shortage
65 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Gas shortage
66 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
68 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 12 | 13 | 6 | 13 | 137 |  | Fuel shortage
69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 25 | 25 | 25 | 25 |  | 27 | Engine problem
70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
71 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 17 | 17 | 17 | 183 |  | Fuel shortage
72 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 13 | 13 | 13 |  | 9 | Engine problem
73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 7 | 8 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 106 | 106 | 128 | 141
74 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 18 | 11 | 18 |  | 7 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 0 | 114 |  | Fuel shortage
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 78 | 9 | 78 | 35 |  | Fuel shortage
79 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
80 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 0 | 17 | 98 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2951 | 795 | 864 | 778 | 916 | 1666 | 319
81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 33 | 73 | 60 | 75 | 127 |  | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 78 | 56 | 78 | 122 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 28 | 9 | 28 | 87 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 26 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 2 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 126 | 185 | 178.6 | 187 | 127 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 40 | 40 | 40 |  | 50 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 60 | 60 | 60
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 82 | 84 | 84
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 |  | 231 | Under maint.
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 20 | 20 | 20 | 20
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 9 |  | Gas shortage
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 290 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 350 | 250 | 350
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1114 | 1074 | 986 | 1086 | 110 | 1138
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 765 | 671 | 789 | 789
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 33 | 16 | 33 | 82 |  | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 11 | 28 | 15 | 40 |  | 14 | Engine problem
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 10 | 20 | 20 |  | 89 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 16 | 0 | 16 | 24 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 93 | 93 | 93 | 93 |  | 12 | Engine problem
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 13 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 580 | 599 | 580 | 600 |  |  | Unit-2 test
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 1478 | 1450 | 1613 | 1591 | 1203 | 115
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 16 | 16
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 12 | 20 | 20 | 20 |  | 20 | Engine problem
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 67 | 67 | 67 | 67 |  | 127 | GT-2 & ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 622 | 622 | 622 | 622 |  | 622 | #01 Under maint.
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 17 | 17 | 133 |  | Fuel shortage
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 307 | 200 | 250 | 250
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1245 | 1162 | 1212 | 1212 | 133 | 769
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 32 | 32 | 32 | 32 | 20 |  | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 15 | 0 | 16 |  | 55 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 28 | 28 | 28 | 28
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 34 | 34 | 34 |  | 16 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 16 | 40 | 40 | 40 |  | 10 | Engine problem
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 242 | 218 | 300 | 300 | 114 |  | Gas shortage
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 25 | 38 | 12 |  | Engine problem
136 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 8 | 44 |  | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 52 | 92 | 90 | 92 |  | 12 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 0 | 35 | 78 |  | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 0 | 35 | 78 |  | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 1 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1404 | 1423 | 1400 | 1400
| Rajshahi Area Total |  |  |  |  | 3653 | 3631 | 1814 | 2006 | 1974 | 2069 | 1367 | 93
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 6 | 35 | 6 | 35 | 78 |  | Fuel shortage
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 35 | 70 | 35 | 80 |  | Fuel shortage
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 5 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 27 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 209 | 240 | 414 | 240 | 283 | 189
| Total |  |  |  |  | 26504 | 25481 | 9133 | 10276 | 10329.6 | 11175 | 9060 | 4002
A. |  | 2024-01-21 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 10276 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
2 | Minimum Generation : |  |  | 6956 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10276 | MW
3 | Day peak Generation : |  |  | 9133 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9714.16 | MW
4 | Evening peak Generation : |  |  | 10276 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 206.6334 | MKWHr | By Solar | 1.1239 | MKWHr
| By Gas : | 67.5232 | MKWHr |  | By Oil: | 32.1384 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 86.0561 | MKWHr |  | By Hydro: | 1.8439 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.09168 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 9060 | MW | Dhaka | 3586.76 | 3586.76 |  | 0 |  | 18:00 |  | 389
|  |  | For Plants S/D or M/C prob = |  |  | 4002 | MW | Chittagong | 930.7 | 930.7 |  | 0 |  | 19:00 |  | 443.12
|  |  | Total = |  |  | 13062 | MW | Khulna | 1157 | 1157 |  | 0 |  | 19:30 |  | 275.04
7 | Total Gas Supplied : |  |  | 599.6 | MMCFD |  |  | Rajshahi | 1004.6 | 1004.6 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 214701518.324 | ii) Oil : | Taka | 582583545.43 | Comilla | 853 | 853 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 567994402.68 | Total | Taka | 1365279466.434 | Mymensingh | 817 | 817 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 361 | 361 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 860 | MW (W to E) at | 20:00 | hrs | Barisal | 303.1 | 303.1 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 850 | MW at | 19:30 | hrs | Rangpur | 701 | 701 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 23.6°C |  |  | Total | 9714.16 | 9714.16 |  | 0
B. |  | 2024-01-22 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 30.3°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 11175 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10000 | MW
4 | Reserve(Generation end) |  |  |  | 375 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 217.1702 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6937 | MW at | 4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 15.6655 | MKWHr. | ii) HVDC Flow at Peak Time |  | 671 | MW at | 20:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.1907 | MKWHr. | iii) Maximum HVDC Flow : |  | 766 | MW at | 13:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 89.65 |  | (b) Today: | 89.44 |  | (c) Rule Curve: |  | 99
.

## YesterdayGen
2024-01-21 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 100 | 0 | 70 | 0 | 0 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 25 | 13 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 4 | 72 | 51 | 25 | 0 | 6 | 21 | 10 | 0 | 0 | 0 | 310 | 0 | 148 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 26 | 9 | 18 | 10 | 33 | 18 | 76 | 86 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 163 | 0 | 61 | 86 | 0 | 0 | 20 | 0 | 10 | 285 | 16 | 0 | 0 | 100 | 0 | 0 | 9 | 0 | 36 | 0 | 25 | 17 | 8 | 0 | 9 | 17 | 31 | 0 | 16 | 0 | 17 | 17 | 9 | 25 | 300 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 390 | 7 | 0 | 0 | 0 |  | 653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 22 | 8 | 67 | 17 | 0 | 0 | 0 | 0 | 34 | 15 | 0 | 28 | 0 | 24 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 288 | 93 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 622 | 220 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 557 | 0 | 307 | 1294 | 0 | 0 |  | 3617 | 4477 | 8094 | 1368 | 653 | 1650 | 0 | 625 | 3340 | 76 | 0 | 299 | 76 | 0 | 7 | 0 | 89.7
2:00 | 0 | 0 | 0 | 100 | 0 | 70 | 0 | 0 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 25 | 13 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 5 | 72 | 51 | 0 | 0 | 6 | 21 | 0 | 0 | 0 | 0 | 310 | 0 | 146 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 26 | 8 | 18 | 10 | 33 | 18 | 72 | 86 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 163 | 0 | 61 | 86 | 0 | 0 | 20 | 0 | 10 | 300 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 36 | 0 | 25 | 17 | 6 | 0 | 9 | 17 | 32 | 0 | 16 | 0 | 17 | 0 | 9 | 25 | 300 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 390 | 9 | 0 | 0 | 0 |  | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 16 | 0 | 0 | 0 | 0 | 34 | 15 | 0 | 28 | 0 | 22 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 53 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 600 | 220 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 579 | 0 | 307 | 1118 | 0 | 0 |  | 3475 | 4004 | 7479 | 1366 | 432 | 1673 | 0 | 434 | 3164 | 76 | 0 | 253 | 72 | 0 | 9 | 0 | 89.69
3:00 | 0 | 0 | 0 | 100 | 0 | 70 | 0 | 0 | 0 |  | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 25 | 13 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 6 | 72 | 51 | 0 | 0 | 6 | 21 | 0 | 0 | 0 | 0 | 305 | 0 | 151 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 26 | 8 | 18 | 10 | 33 | 18 | 70 | 96 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 163 | 0 | 60 | 86 | 0 | 0 | 20 | 0 | 10 | 300 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 36 | 0 | 25 | 17 | 6 | 0 | 9 | 17 | 32 | 0 | 16 | 0 | 17 | 0 | 9 | 25 | 300 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 388 | 11 | 0 | 0 | 0 |  | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 16 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 180 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 563 | 0 | 307 | 1074 | 0 | 0 |  | 3391 | 3822 | 7213 | 1375 | 432 | 1568 | 0 | 363 | 3102 | 76 | 0 | 216 | 70 | 0 | 11 | 0 | 89.68
4:00 | 0 | 0 | 0 | 100 | 0 | 68 | 0 | 0 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 0 | 13 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 6 | 72 | 51 | 0 | 0 | 6 | 21 | 16 | 0 | 0 | 0 | 340 | 0 | 146 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 25 | 8 | 18 | 10 | 33 | 18 | 68 | 92 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 140 | 0 | 60 | 86 | 0 | 0 | 20 | 0 | 10 | 300 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 36 | 0 | 25 | 17 | 5 | 0 | 9 | 17 | 33 | 0 | 16 | 0 | 17 | 0 | 9 | 25 | 280 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 388 | 12 | 0 | 0 | 0 |  | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 15 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 180 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 566 | 0 | 307 | 1024 | 0 | 0 |  | 3318 | 3642 | 6960 | 1356 | 432 | 1496 | 0 | 350 | 2955 | 76 | 0 | 215 | 68 | 0 | 12 | 0 | 89.67
5:00 | 0 | 0 | 0 | 100 | 0 | 70 | 0 | 0 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 0 | 13 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 6 | 72 | 51 | 0 | 0 | 6 | 21 | 8 | 0 | 0 | 0 | 320 | 0 | 137 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 25 | 8 | 18 | 10 | 33 | 18 | 70 | 93 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 140 | 0 | 60 | 86 | 0 | 0 | 20 | 0 | 10 | 315 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 36 | 0 | 25 | 17 | 6 | 0 | 9 | 17 | 33 | 0 | 16 | 0 | 17 | 0 | 9 | 25 | 280 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 390 | 12 | 0 | 0 | 0 |  | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 14 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 180 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 576 | 0 | 307 | 1026 | 0 | 0 |  | 3303 | 3653 | 6956 | 1328 | 432 | 1504 | 0 | 350 | 2969 | 76 | 0 | 215 | 70 | 0 | 12 | 0 | 89.66
6:00 | 0 | 0 | 0 | 100 | 0 | 70 | 0 | 0 | 0 |  | 0 | 400 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | 16 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 8 | 15 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 72 | 51 | 25 | 0 | 6 | 21 | 6 | 0 | 0 | 0 | 350 | 0 | 134 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 25 | 8 | 18 | 10 | 33 | 11 | 74 | 102 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 163 | 0 | 60 | 86 | 0 | 0 | 20 | 0 | 10 | 325 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 36 | 0 | 25 | 17 | 6 | 0 | 9 | 17 | 33 | 0 | 16 | 0 | 17 | 0 | 9 | 25 | 250 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 390 | 9 | 0 | 0 | 0 |  | 431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 16 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 28 | 34 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 26 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 520 | 220 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 572 | 0 | 307 | 1125 | 0 | 0 |  | 3438 | 3956 | 7394 | 1337 | 431 | 1717 | 0 | 451 | 3084 | 76 | 0 | 215 | 74 | 0 | 9 | 0 | 89.65
7:00 | 0 | 0 | 0 | 100 | 0 | 70 | 0 | 0 | 0 |  | 0 | 450 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 16 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 0 | 15 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 72 | 51 | 25 | 0 | 6 | 21 | 12 | 0 | 0 | 0 | 350 | 0 | 125 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 25 | 8 | 18 | 10 | 33 | 11 | 76 | 71 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 163 | 0 | 60 | 84 | 0 | 0 | 20 | 0 | 10 | 320 | 16 | 0 | 0 | 45 | 0 | 0 | 56 | 0 | 36 | 1 | 25 | 17 | 6 | 0 | 9 | 17 | 29 | 0 | 16 | 0 | 17 | 0 | 9 | 25 | 250 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 390 | 7 | 0 | 0 | 0 |  | 619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 16 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 28 | 34 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 70 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 610 | 220 | 0 | 17 | 0 | 1 | 0 | 0 | 0 | 571 | 0 | 307 | 1311 | 0 | 0 |  | 3613 | 4458 | 8071 | 1292 | 619 | 1757 | 0 | 668 | 3359 | 76 | 0 | 215 | 76 | 2 | 7 | 0 | 89.64
8:00 | 0 | 0 | 0 | 100 | 0 | 70 | 0 | 0 | 0 |  | 0 | 450 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 16 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 16 | 15 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 72 | 51 | 25 | 0 | 6 | 21 | 3 | 0 | 0 | 0 | 375 | 0 | 108 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 25 | 8 | 16 | 10 | 33 | 11 | 86 | 66 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 163 | 0 | 59 | 84 | 0 | 0 | 20 | 0 | 10 | 330 | 16 | 0 | 0 | 50 | 0 | 0 | 56 | 0 | 37 | 5 | 25 | 20 | 5 | 0 | 9 | 17 | 15 | 1 | 16 | 0 | 17 | 0 | 9 | 25 | 245 | 17 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 17 | 0 | 390 | 5 | 0 | 0 | 0 |  | 690 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 16 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 28 | 34 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 72 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 622 | 220 | 0 | 17 | 0 | 13 | 0 | 0 | 0 | 583 | 1 | 307 | 1454 | 4 | 0 |  | 3722 | 4690 | 8412 | 1303 | 690 | 1735 | 0 | 748 | 3526 | 76 | 0 | 213 | 86 | 30 | 5 | 322.79 | 89.63
9:00 | 0 | 0 | 0 | 100 | 0 | 70 | 0 | 0 | 0 |  | 0 | 450 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 65 | 50 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 16 | 15 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 72 | 51 | 25 | 0 | 6 | 21 | 2 | 0 | 0 | 0 | 330 | 0 | 129 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 25 | 8 | 16 | 10 | 33 | 18 | 92 | 65 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 163 | 0 | 59 | 84 | 0 | 0 | 20 | 0 | 10 | 320 | 16 | 0 | 0 | 47 | 0 | 0 | 56 | 0 | 36 | 11 | 25 | 18 | 6 | 0 | 9 | 17 | 15 | 2 | 16 | 5 | 17 | 0 | 9 | 25 | 260 | 17 | 5 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 17 | 0 | 390 | 0 | 0 | 0 | 0 |  | 690 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 16 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 28 | 34 | 0 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 72 | 0 | 0 | 0 | 6 | 0 | 1 | 0 | 622 | 220 | 0 | 17 | 0 | 30 | 0 | 0 | 0 | 580 | 2 | 307 | 1458 | 20 | 0 |  | 3726 | 4701 | 8427 | 1303 | 690 | 1696 | 0 | 752 | 3527 | 76 | 0 | 213 | 92 | 78 | 0 | 642.715 | 89.62
10:00 | 0 | 0 | 0 | 100 | 0 | 67 | 0 | 0 | 0 |  | 0 | 450 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 70 | 50 | 32 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 16 | 14 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 72 | 51 | 25 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 25 | 8 | 16 | 10 | 33 | 18 | 96 | 63 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 130 | 0 | 59 | 84 | 0 | 0 | 20 | 0 | 10 | 310 | 16 | 0 | 0 | 77 | 0 | 0 | 56 | 0 | 36 | 15 | 25 | 17 | 12 | 0 | 9 | 17 | 15 | 3 | 45 | 0 | 17 | 0 | 9 | 25 | 281 | 18 | 8 | 17 | 17 | 0 | 12 | 10 | 0 | 0 | 0 | 17 | 0 | 390 | 0 | 121 | 0 | 0 |  | 691 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 12 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 28 | 34 | 14 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 287 | 75 | 0 | 0 | 0 | 6 | 0 | 1 | 0 | 622 | 220 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 580 | 3 | 307 | 1408 | 30 | 0 |  | 3901 | 4673 | 8574 | 1258 | 691 | 1621 | 0 | 873 | 3598 | 76 | 0 | 243 | 96 | 118 | 0 | 788.83 | 89.61
11:00 | 0 | 0 | 0 | 100 | 0 | 67 | 0 | 0 | 0 |  | 0 | 450 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 70 | 50 | 82 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 3 | 14 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 64 | 51 | 25 | 0 | 6 | 13 | 0 | 0 | 0 | 0 | 290 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 25 | 8 | 16 | 7 | 33 | 18 | 100 | 32 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 130 | 0 | 59 | 84 | 0 | 0 | 20 | 0 | 10 | 310 | 16 | 0 | 0 | 92 | 0 | 0 | 57 | 0 | 36 | 18 | 25 | 17 | 12 | 0 | 9 | 50 | 16 | 4 | 49 | 0 | 17 | 0 | 9 | 25 | 330 | 30 | 11 | 35 | 17 | 0 | 17 | 15 | 0 | 0 | 0 | 17 | 0 | 396 | 0 | 122 | 0 | 0 |  | 690 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 11 | 0 | 0 | 67 | 12 | 0 | 0 | 0 | 0 | 32 | 0 | 52 | 28 | 34 | 16 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 93 | 0 | 0 | 0 | 6 | 0 | 1 | 0 | 622 | 220 | 0 | 17 | 0 | 47 | 0 | 0 | 0 | 579 | 6 | 307 | 1409 | 30 | 0 |  | 4074 | 4730 | 8804 | 1277 | 690 | 1594 | 0 | 980 | 3605 | 76 | 0 | 350 | 100 | 132 | 0 | 807.93 | 89.6
12:00 | 0 | 0 | 0 | 100 | 0 | 12 | 0 | 0 | 0 |  | 0 | 450 | 0 | 81 | 0 | 2 | 0 | 0 | 0 | 75 | 58 | 82 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 33 | 14 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 64 | 51 | 25 | 0 | 6 | 20 | 5 | 0 | 0 | 0 | 320 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 25 | 8 | 16 | 7 | 33 | 18 | 106 | 33 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 163 | 0 | 58 | 84 | 0 | 0 | 20 | 0 | 10 | 290 | 16 | 0 | 0 | 148 | 0 | 0 | 58 | 0 | 36 | 17 | 25 | 17 | 12 | 0 | 9 | 50 | 16 | 4 | 49 | 1 | 17 | 0 | 9 | 25 | 400 | 39 | 26 | 35 | 17 | 0 | 17 | 20 | 0 | 0 | 0 | 72 | 0 | 396 | 0 | 154 | 0 | 0 |  | 765 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 11 | 0 | 0 | 67 | 12 | 0 | 0 | 0 | 0 | 32 | 0 | 52 | 28 | 34 | 16 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242 | 93 | 0 | 0 | 0 | 6 | 0 | 1 | 0 | 622 | 220 | 0 | 17 | 1 | 13 | 0 | 0 | 0 | 580 | 5 | 307 | 1404 | 27 | 0 |  | 4387 | 4746 | 9133 | 1428 | 765 | 1539 | 0 | 1067 | 3633 | 76 | 0 | 405 | 106 | 114 | 0 | 732 | 89.59
13:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 0 | 0 |  | 0 | 450 | 0 | 82 | 0 | 15 | 0 | 0 | 0 | 75 | 58 | 82 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 33 | 14 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 68 | 51 | 25 | 0 | 6 | 20 | 7 | 0 | 0 | 0 | 305 | 0 | 141 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 25 | 8 | 16 | 10 | 33 | 18 | 112 | 33 | 0 | 0 | 1 | 43 | 30 | 0 | 0 | 163 | 0 | 59 | 84 | 0 | 0 | 20 | 0 | 10 | 310 | 16 | 0 | 0 | 153 | 0 | 0 | 58 | 0 | 36 | 17 | 25 | 17 | 12 | 0 | 9 | 50 | 16 | 4 | 51 | 17 | 17 | 0 | 9 | 25 | 400 | 45 | 29 | 0 | 17 | 0 | 17 | 23 | 0 | 0 | 0 | 72 | 0 | 391 | 0 | 270 | 0 | 0 |  | 766 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 11 | 0 | 0 | 67 | 19 | 0 | 0 | 0 | 0 | 32 | 4 | 52 | 28 | 34 | 20 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 93 | 0 | 0 | 0 | 6 | 0 | 2 | 0 | 622 | 220 | 0 | 17 | 1 | 25 | 0 | 0 | 0 | 577 | 7 | 307 | 1421 | 41 | 0 |  | 4602 | 4760 | 9362 | 1482 | 766 | 1523 | 0 | 1078 | 3758 | 76 | 0 | 417 | 112 | 150 | 0 | 800 | 89.58
14:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 0 | 0 |  | 0 | 450 | 0 | 89 | 17 | 15 | 0 | 0 | 0 | 79 | 58 | 48 | 25 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 18 | 21 | 33 | 14 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 73 | 51 | 25 | 0 | 6 | 21 | 0 | 0 | 0 | 0 | 280 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 25 | 0 | 16 | 5 | 33 | 18 | 106 | 33 | 0 | 0 | 0 | 43 | 20 | 0 | 0 | 130 | 0 | 59 | 84 | 0 | 0 | 20 | 0 | 10 | 280 | 16 | 0 | 0 | 162 | 0 | 0 | 58 | 0 | 36 | 14 | 25 | 17 | 6 | 0 | 9 | 50 | 16 | 3 | 51 | 17 | 17 | 0 | 9 | 25 | 360 | 53 | 34 | 0 | 17 | 0 | 17 | 19 | 0 | 0 | 0 | 36 | 0 | 327 | 0 | 363 | 0 | 0 |  | 766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 67 | 16 | 0 | 0 | 0 | 0 | 32 | 15 | 52 | 28 | 34 | 23 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 93 | 0 | 0 | 0 | 6 | 0 | 1 | 0 | 590 | 220 | 0 | 17 | 1 | 34 | 0 | 0 | 0 | 567 | 10 | 250 | 1381 | 67 | 0 |  | 4467 | 4634 | 9101 | 1415 | 766 | 1431 | 0 | 1110 | 3648 | 76 | 0 | 366 | 106 | 183 | 0 | 667.545 | 89.6
15:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 0 | 0 |  | 0 | 400 | 0 | 93 | 17 | 15 | 0 | 0 | 0 | 83 | 58 | 32 | 25 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 18 | 21 | 33 | 21 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 73 | 51 | 25 | 0 | 6 | 21 | 0 | 0 | 0 | 0 | 295 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 25 | 0 | 16 | 8 | 33 | 18 | 102 | 34 | 0 | 0 | 0 | 43 | 22 | 0 | 0 | 120 | 0 | 57 | 81 | 0 | 0 | 20 | 0 | 10 | 290 | 16 | 0 | 0 | 158 | 0 | 0 | 58 | 0 | 43 | 11 | 25 | 17 | 6 | 0 | 9 | 34 | 16 | 2 | 51 | 17 | 17 | 0 | 20 | 25 | 400 | 53 | 23 | 0 | 17 | 0 | 17 | 12 | 6 | 0 | 0 | 36 | 0 | 310 | 0 | 382 | 0 | 0 |  | 765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 67 | 14 | 0 | 0 | 0 | 0 | 32 | 15 | 52 | 28 | 34 | 22 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 93 | 0 | 0 | 0 | 6 | 0 | 2 | 20 | 580 | 180 | 0 | 17 | 0 | 27 | 17 | 0 | 0 | 543 | 15 | 217 | 1360 | 69 | 0 |  | 4451 | 4575 | 9026 | 1480 | 765 | 1372 | 0 | 1159 | 3562 | 76 | 0 | 349 | 102 | 161 | 0 | 357.17 | 89.56
16:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 0 | 0 |  | 0 | 400 | 0 | 92 | 42 | 15 | 0 | 0 | 0 | 83 | 66 | 32 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 18 | 21 | 33 | 21 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 73 | 48 | 25 | 0 | 6 | 21 | 2 | 0 | 0 | 0 | 285 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 25 | 0 | 16 | 8 | 33 | 12 | 98 | 34 | 0 | 0 | 0 | 43 | 22 | 0 | 0 | 163 | 0 | 40 | 84 | 0 | 0 | 18 | 0 | 10 | 305 | 16 | 0 | 0 | 163 | 0 | 0 | 58 | 0 | 53 | 7 | 25 | 17 | 6 | 0 | 9 | 34 | 16 | 1 | 51 | 17 | 7 | 0 | 37 | 25 | 400 | 53 | 11 | 0 | 17 | 0 | 17 | 6 | 18 | 0 | 0 | 36 | 0 | 346 | 1 | 417 | 0 | 0 |  | 766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 16 | 67 | 14 | 0 | 0 | 0 | 0 | 32 | 15 | 52 | 28 | 34 | 22 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208 | 93 | 0 | 0 | 0 | 6 | 0 | 1 | 35 | 580 | 180 | 0 | 17 | 0 | 11 | 17 | 0 | 0 | 576 | 8 | 200 | 1385 | 34 | 0 |  | 4604 | 4583 | 9187 | 1444 | 766 | 1429 | 0 | 1274 | 3674 | 76 | 0 | 346 | 98 | 79 | 1 | 0 | 89.55
17:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 0 | 0 |  | 0 | 420 | 0 | 93 | 82 | 15 | 0 | 0 | 0 | 77 | 66 | 32 | 25 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 18 | 21 | 33 | 21 | 17 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 1 | 73 | 46 | 25 | 0 | 6 | 19 | 5 | 0 | 0 | 0 | 280 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 25 | 4 | 13 | 8 | 33 | 18 | 96 | 35 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 163 | 0 | 40 | 81 | 0 | 0 | 18 | 0 | 10 | 310 | 16 | 0 | 0 | 175 | 0 | 0 | 58 | 0 | 55 | 1 | 25 | 17 | 12 | 0 | 9 | 50 | 16 | 0 | 80 | 17 | 17 | 0 | 37 | 25 | 400 | 53 | 2 | 0 | 17 | 0 | 17 | 2 | 22 | 13 | 0 | 36 | 0 | 350 | 1 | 419 | 0 | 0 |  | 766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 16 | 67 | 14 | 0 | 0 | 0 | 0 | 32 | 15 | 52 | 28 | 34 | 23 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 93 | 0 | 1 | 0 | 33 | 0 | 1 | 35 | 560 | 220 | 0 | 17 | 0 | 5 | 17 | 0 | 0 | 586 | 1 | 200 | 1358 | 8 | 0 |  | 4741 | 4589 | 9330 | 1458 | 766 | 1488 | 0 | 1418 | 3643 | 76 | 0 | 364 | 96 | 20 | 1 | 0 | 89.54
18:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 0 | 0 |  | 0 | 450 | 0 | 94 | 82 | 15 | 0 | 0 | 0 | 75 | 75 | 115 | 25 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 18 | 16 | 33 | 21 | 17 | 0 | 46 | 30 | 0 | 0 | 14 | 0 | 0 | 0 | 0 |  | 6 | 73 | 40 | 25 | 0 | 15 | 16 | 7 | 0 | 0 | 0 | 315 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 25 | 8 | 13 | 8 | 33 | 18 | 106 | 54 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 163 | 0 | 59 | 82 | 0 | 0 | 20 | 0 | 10 | 295 | 16 | 0 | 0 | 210 | 0 | 0 | 67 | 0 | 73 | 0 | 25 | 17 | 13 | 0 | 28 | 105 | 16 | 0 | 102 | 17 | 17 | 0 | 71 | 25 | 380 | 72 | 0 | 17 | 17 | 0 | 17 | 0 | 23 | 26 | 0 | 36 | 0 | 362 | 0 | 418 | 0 | 0 |  | 766 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 37 | 16 | 16 | 67 | 19 | 16 | 0 | 0 | 0 | 32 | 16 | 92 | 28 | 34 | 29 | 8 | 38 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 93 | 0 | 35 | 0 | 33 | 0 | 0 | 35 | 570 | 220 | 0 | 17 | 0 | 0 | 70 | 0 | 0 | 524 | 0 | 200 | 1471 | 0 | 0 |  | 5198 | 4895 | 10093 | 1509 | 766 | 1512 | 0 | 1860 | 3715 | 76 | 0 | 549 | 106 | 0 | 0 | 389 | 89.53
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 20 | 0 |  | 0 | 450 | 0 | 94 | 82 | 15 | 0 | 0 | 0 | 75 | 91 | 130 | 25 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 18 | 21 | 33 | 22 | 17 | 0 | 46 | 30 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 6 | 64 | 51 | 25 | 0 | 19 | 16 | 7 | 0 | 0 | 0 | 305 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 25 | 8 | 13 | 8 | 33 | 18 | 108 | 72 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 163 | 0 | 60 | 82 | 0 | 0 | 20 | 0 | 10 | 310 | 16 | 0 | 0 | 235 | 0 | 0 | 77 | 0 | 81 | 0 | 25 | 17 | 13 | 0 | 28 | 105 | 16 | 0 | 101 | 0 | 17 | 0 | 78 | 25 | 350 | 72 | 0 | 17 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 36 | 0 | 480 | 0 | 413 | 0 | 0 |  | 671 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 42 | 10 | 16 | 67 | 19 | 16 | 0 | 0 | 0 | 32 | 15 | 92 | 28 | 34 | 39 | 8 | 38 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 93 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 622 | 220 | 0 | 17 | 0 | 0 | 70 | 0 | 0 | 462 | 0 | 200 | 1510 | 0 | 0 |  | 5391 | 4845 | 10236 | 1514 | 671 | 1534 | 0 | 1902 | 3857 | 76 | 0 | 574 | 108 | 0 | 0 | 443.12 | 89.5
19:30 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 20 | 0 |  | 0 | 450 | 0 | 51 | 82 | 15 | 0 | 0 | 0 | 75 | 91 | 149 | 25 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 18 | 21 | 33 | 22 | 17 | 0 | 46 | 30 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 6 | 64 | 51 | 25 | 0 | 19 | 16 | 18 | 0 | 0 | 0 | 325 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 25 | 8 | 13 | 8 | 33 | 18 | 108 | 74 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 163 | 0 | 59 | 82 | 0 | 0 | 20 | 0 | 10 | 320 | 16 | 0 | 0 | 262 | 0 | 0 | 77 | 0 | 100 | 0 | 25 | 17 | 13 | 0 | 28 | 105 | 16 | 0 | 106 | 0 | 17 | 0 | 78 | 25 | 350 | 72 | 0 | 17 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 36 | 0 | 480 | 0 | 418 | 0 | 0 |  | 672 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 46 | 10 | 16 | 67 | 19 | 16 | 0 | 0 | 0 | 32 | 15 | 92 | 28 | 34 | 40 | 8 | 38 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 93 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 622 | 220 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 538 | 0 | 200 | 1426 | 0 | 0 |  | 5447 | 4815 | 10262 | 1535 | 672 | 1562 | 0 | 1857 | 3854 | 76 | 0 | 598 | 108 | 0 | 0 | 275.04 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 25 | 0 |  | 0 | 450 | 0 | 53 | 82 | 15 | 0 | 0 | 0 | 73 | 91 | 149 | 25 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 18 | 21 | 33 | 23 | 17 | 0 | 46 | 30 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 6 | 64 | 51 | 25 | 0 | 19 | 19 | 15 | 0 | 0 | 0 | 330 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 25 | 8 | 13 | 8 | 33 | 18 | 106 | 73 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 163 | 0 | 60 | 82 | 0 | 0 | 20 | 0 | 10 | 290 | 16 | 0 | 0 | 260 | 0 | 0 | 78 | 0 | 96 | 0 | 25 | 17 | 13 | 0 | 28 | 105 | 16 | 0 | 106 | 0 | 17 | 0 | 78 | 25 | 350 | 72 | 0 | 17 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 36 | 0 | 480 | 0 | 419 | 0 | 0 |  | 671 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 28 | 10 | 16 | 67 | 20 | 16 | 0 | 0 | 0 | 32 | 15 | 92 | 28 | 34 | 40 | 8 | 38 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 93 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 622 | 220 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 599 | 0 | 200 | 1423 | 0 | 0 |  | 5418 | 4858 | 10276 | 1545 | 671 | 1531 | 0 | 1854 | 3913 | 76 | 0 | 580 | 106 | 0 | 0 | 0 | 89.51
21:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 36 | 0 |  | 0 | 450 | 0 | 11 | 82 | 15 | 0 | 0 | 0 | 75 | 83 | 149 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 32 | 23 | 17 | 0 | 46 | 30 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 6 | 64 | 51 | 25 | 0 | 19 | 19 | 23 | 0 | 0 | 0 | 305 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 25 | 8 | 13 | 8 | 33 | 18 | 104 | 75 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 163 | 0 | 59 | 82 | 0 | 0 | 20 | 0 | 10 | 320 | 16 | 0 | 0 | 263 | 0 | 0 | 78 | 0 | 99 | 0 | 25 | 17 | 13 | 0 | 28 | 105 | 16 | 0 | 106 | 0 | 17 | 0 | 78 | 25 | 315 | 72 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 36 | 0 | 480 | 0 | 417 | 0 | 0 |  | 765 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 22 | 10 | 16 | 80 | 20 | 16 | 0 | 0 | 0 | 32 | 15 | 92 | 28 | 34 | 42 | 8 | 38 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237 | 93 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 622 | 220 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 536 | 0 | 200 | 1418 | 0 | 0 |  | 5278 | 4912 | 10190 | 1477 | 765 | 1588 | 0 | 1761 | 3843 | 76 | 0 | 576 | 104 | 0 | 0 | 0 | 89.5
22:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 94 | 0 |  | 0 | 350 | 0 | 9 | 82 | 15 | 0 | 0 | 0 | 51 | 8 | 16 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 32 | 9 | 17 | 0 | 46 | 30 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 6 | 64 | 51 | 25 | 0 | 19 | 18 | 12 | 0 | 0 | 0 | 305 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 25 | 8 | 13 | 8 | 33 | 18 | 100 | 75 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 120 | 0 | 58 | 82 | 0 | 0 | 20 | 0 | 10 | 285 | 16 | 0 | 0 | 195 | 0 | 0 | 58 | 0 | 99 | 0 | 25 | 17 | 13 | 0 | 9 | 105 | 16 | 0 | 51 | 0 | 17 | 0 | 72 | 25 | 300 | 72 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 481 | 0 | 417 | 0 | 65 |  | 764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 20 | 16 | 130 | 20 | 16 | 0 | 0 | 0 | 32 | 15 | 92 | 28 | 34 | 42 | 8 | 38 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251 | 35 | 0 | 35 | 0 | 6 | 0 | 0 | 35 | 622 | 220 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 600 | 0 | 200 | 1356 | 0 | 0 |  | 4786 | 4859 | 9645 | 1580 | 764 | 1478 | 0 | 1372 | 3846 | 76 | 0 | 429 | 100 | 0 | 0 | 0 | 89.49
23:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 156 | 0 |  | 0 | 350 | 0 | 8 | 36 | 15 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 32 | 21 | 17 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 6 | 64 | 51 | 25 | 0 | 19 | 18 | 10 | 0 | 0 | 0 | 345 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 8 | 13 | 8 | 33 | 18 | 98 | 76 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 120 | 0 | 58 | 82 | 0 | 0 | 20 | 0 | 10 | 285 | 16 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 76 | 0 | 25 | 17 | 13 | 0 | 9 | 70 | 16 | 0 | 16 | 0 | 17 | 0 | 46 | 25 | 280 | 23 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 480 | 3 | 420 | 0 | 42 |  | 765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 130 | 19 | 16 | 0 | 0 | 0 | 32 | 15 | 92 | 0 | 8 | 42 | 8 | 38 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 622 | 220 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 580 | 0 | 200 | 1307 | 0 | 0 |  | 4346 | 4611 | 8957 | 1673 | 765 | 1461 | 0 | 710 | 3779 | 76 | 0 | 392 | 98 | 0 | 3 | 0 | 89.48
24:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 171 | 0 |  | 0 | 350 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 32 | 33 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 6 | 64 | 17 | 25 | 0 | 6 | 18 | 10 | 0 | 0 | 0 | 305 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 8 | 13 | 8 | 33 | 18 | 96 | 76 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 140 | 0 | 60 | 82 | 0 | 0 | 20 | 0 | 10 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 42 | 0 | 25 | 17 | 10 | 0 | 9 | 17 | 16 | 0 | 0 | 0 | 17 | 0 | 38 | 25 | 260 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 0 | 13 | 0 | 480 | 4 | 418 | 0 | 0 |  | 747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 18 | 0 | 0 | 0 | 0 | 32 | 0 | 61 | 0 | 0 | 32 | 8 | 38 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 286 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 560 | 180 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 558 | 0 | 200 | 1250 | 0 | 0 |  | 4007 | 4317 | 8324 | 1646 | 747 | 1421 | 0 | 432 | 3636 | 76 | 0 | 266 | 96 | 0 | 4 | 0 | 89.47
KWH | 0 | 0 | 0 | 3433500 | 0 | 915818 | 0 | 507600 | 0 |  | 0 | 9572000 | 0 | 1208640 | 553768 | 198581 | 0 | 0 | 0 | 1094400 | 1056820 | 1179360 | 364533 | 0 | 0 | 0 | 64080 | 68563 | 65241 | 0 | 432000 | 493200 | 570100 | 407800 | 268320 | 0 | 1103880 | 740000 | 0 | 0 | 253130 | 0 | 0 | 0 | 0 |  | 72720 | 1316758 | 1183074 | 449160 | 0 | 227040 | 437136 | 218400 | 0 | 0 | 0 | 8000600 | 0 | 3425000 | 0 | 0 | 54000 | 0 | 0 | 1242899 | 0 | 600016 | 186322 | 366516 | 212400 | 811700 | 396280 | 2190720 | 1476480 | 0 | 0 | 2350 | 1015000 | 755000 | 0 | 0 | 3869018 | 0 | 1387488 | 2008320 | 0 | 0 | 481000 | 0 | 244620 | 7452000 | 391008 | 0 | 0 | 2760000 | 0 | 0 | 1125600 | 0 | 1240416 | 115695 | 624000 | 425280 | 227490 | 0 | 308400 | 1106880 | 511854 | 22684 | 1036255 | 124656 | 414000 | 67260 | 692160 | 611520 | 7692900 | 968640 | 157590 | 136800 | 260945 | 0 | 272880 | 116096 | 79680 | 132840 | 0 | 669091 | 0 | 9687271 | 91680 | 4981818 | 0 | 78494 |  | 15665454 | 0 | 0 | 0 | 184320 | 0 | 0 | 0 | 250080 | 95616 | 139125 | 1782000 | 382200 | 113376 | 0 | 0 | 0 | 777541 | 183769 | 970704 | 621340 | 577952 | 429912 | 103238 | 269629 | 0 | 0 | 159912 | 0 | 0 | 4133200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6336290 | 1681920 | 0 | 218688 | 0 | 274252 | 0 | 11052 | 263424 | 15379300 | 514489 | 0 | 439200 | 6840 | 303840 | 337152 | 0 | 0 | 13490910 | 59224 | 6349100 | 32034545 | 328560 | 0 |  | 101765234 | 104868154 | 206633388 | 34688620 | 15665454 | 32834548 | 0 | 24212861 | 86056144 | 1843880 | 0 | 7925550 | 2190720 | 1123931 | 91680 | 0
Fuel Cost | 0 | 0 | 0 | 15279075 | 0 | 3498424.76 | 0 | 1461888 | 0 |  | 0 | 30438960 | 0 | 24305750.4 | 9879221.12 | 3429493.87 | 0 | 0 | 0 | 21526848 | 21284354.8 | 21723811.2 | 6583465.98 | 0 | 0 | 0 | 1157284.8 | 1154600.92 | 1041898.77 | 0 | 324000 | 0 | 0 | 0 | 4805611.2 | 0 | 0 | 0 | 0 | 0 | 4561402.6 | 0 | 0 | 0 | 0 |  | 1276963.2 | 23188108.38 | 21188855.34 | 7622245.2 | 0 | 3525931.2 | 1626145.92 | 0 | 0 | 0 | 0 | 22321674 | 0 | 11371000 | 0 | 0 | 181980 | 0 | 0 | 4984024.99 | 0 | 10746286.56 | 3351932.78 | 1363439.52 | 159300 | 3019524 | 297210 | 14371123.2 | 4591852.8 | 0 | 0 | 37459 | 3958500 | 2816150 | 0 | 0 | 13232041.56 | 0 | 7700558.4 | 10483430.4 | 0 | 0 | 3164980 | 0 | 978480 | 23026680 | 293256 | 0 | 0 | 56994000 | 0 | 0 | 17401776 | 0 | 23468670.72 | 1352474.55 | 10214880 | 6847008 | 3516995.4 | 0 | 4567404 | 19923840 | 8880666.9 | 352963.04 | 19212167.7 | 2458216.32 | 6135480 | 1228840.2 | 10956892.8 | 10077849.6 | 20463114 | 17793916.8 | 2277175.5 | 2470608 | 3830672.6 | 0 | 4772671.2 | 1387347.2 | 1318704 | 2254294.8 | 0 | 12003492.54 | 0 | 67132788.03 | 0 | 0 | 0 | 0 |  | 43079998.5 | 0 | 0 | 0 | 3140812.8 | 0 | 0 | 0 | 4704004.8 | 1798536.96 | 2476425 | 5631120 | 1811628 | 2153010.24 | 0 | 0 | 0 | 13925759.31 | 3372161.15 | 16317534.24 | 12346025.8 | 10929072.32 | 7699723.92 | 1825247.84 | 4829055.39 | 0 | 0 | 121053.384 | 0 | 0 | 35049536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18501966.8 | 32494694.4 | 0 | 4200996.48 | 0 | 4563553.28 | 0 | 122124.6 | 4414986.24 | 88892354 | 1600060.79 | 0 | 7000848 | 77360.4 | 3564043.2 | 5707983.36 | 0 | 0 | 86476733.1 | 0 | 47300795 | 243142196.55 | 0 | 0 |  | 712630133.77 | 719271401.854 | 1431901535.624 | 106145821.024 | 43079998.5 | 108555697.3 | 0 | 441086215.64 | 567994402.68 | 0 | 0 | 141497329.79 | 14371123.2 | 9170947.49 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 100 | 0 | 12 | 0 | 0 | 0 |  | 0 | 450 | 0 | 81 | 0 | 2 | 0 | 0 | 0 | 75 | 58 | 82 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 33 | 14 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 64 | 51 | 25 | 0 | 6 | 20 | 5 | 0 | 0 | 0 | 320 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 25 | 8 | 16 | 7 | 33 | 18 | 106 | 33 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 163 | 0 | 58 | 84 | 0 | 0 | 20 | 0 | 10 | 290 | 16 | 0 | 0 | 148 | 0 | 0 | 58 | 0 | 36 | 17 | 25 | 17 | 12 | 0 | 9 | 50 | 16 | 4 | 49 | 1 | 17 | 0 | 9 | 25 | 400 | 39 | 26 | 35 | 17 | 0 | 17 | 20 | 0 | 0 | 0 | 72 | 0 | 396 | 0 | 154 | 0 | 0 |  | 765 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 11 | 0 | 0 | 67 | 12 | 0 | 0 | 0 | 0 | 32 | 0 | 52 | 28 | 34 | 16 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242 | 93 | 0 | 0 | 0 | 6 | 0 | 1 | 0 | 622 | 220 | 0 | 17 | 1 | 13 | 0 | 0 | 0 | 580 | 5 | 307 | 1404 | 27 | 0 |  | 9133 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 25 | 0 |  | 0 | 450 | 0 | 53 | 82 | 15 | 0 | 0 | 0 | 73 | 91 | 149 | 25 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 18 | 21 | 33 | 23 | 17 | 0 | 46 | 30 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 6 | 64 | 51 | 25 | 0 | 19 | 19 | 15 | 0 | 0 | 0 | 330 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 25 | 8 | 13 | 8 | 33 | 18 | 106 | 73 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 163 | 0 | 60 | 82 | 0 | 0 | 20 | 0 | 10 | 290 | 16 | 0 | 0 | 260 | 0 | 0 | 78 | 0 | 96 | 0 | 25 | 17 | 13 | 0 | 28 | 105 | 16 | 0 | 106 | 0 | 17 | 0 | 78 | 25 | 350 | 72 | 0 | 17 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 36 | 0 | 480 | 0 | 419 | 0 | 0 |  | 671 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 28 | 10 | 16 | 67 | 20 | 16 | 0 | 0 | 0 | 32 | 15 | 92 | 28 | 34 | 40 | 8 | 38 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 93 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 622 | 220 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 599 | 0 | 200 | 1423 | 0 | 0 |  | 10276 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 15 | 0 | 412 | 0 |  | 0 | 450 | 0 | 100 | 82 | 15 | 0 | 0 | 0 | 73 | 90 | 149 | 30 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 18 | 22 | 33 | 23 | 17 | 0 | 46 | 30 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 6 | 64 | 51 | 25 | 0 | 19 | 18 | 10 | 0 | 0 | 0 | 330 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 25 | 8 | 13 | 10 | 33 | 18 | 141 | 75 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 163 | 0 | 60 | 84 | 0 | 0 | 20 | 0 | 10 | 300 | 16 | 0 | 0 | 260 | 0 | 0 | 78 | 0 | 50 | 0 | 25 | 17 | 13 | 0 | 28 | 105 | 16 | 0 | 105 | 0 | 17 | 0 | 78 | 25 | 350 | 51 | 0 | 17 | 17 | 0 | 17 | 0 | 17 | 17 | 0 | 36 | 0 | 480 | 10 | 420 | 0 | 200 |  | 789 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 40 | 20 | 16 | 67 | 20 | 16 | 0 | 0 | 0 | 32 | 16 | 92 | 28 | 34 | 40 | 8 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 93 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 622 | 220 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 600 | 0 | 250 | 1400 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 400 | 0 | 0 | 0 | 450 | 0 | 100 | 30 | 15 | 0 | 0 | 0 | 70 | 70 | 32 | 30 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 18 | 22 | 30 | 21 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 |  | 0 | 0 | 0 | 2 | 60 | 51 | 25 | 0 | 6 | 18 | 5 | 0 | 0 | 0 | 320 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 25 | 8 | 13 | 10 | 33 | 11 | 128 | 60 | 0 | 0 | 1.6 | 43 | 40 | 0 | 0 | 163 | 0 | 60 | 84 | 0 | 0 | 20 | 0 | 10 | 300 | 16 | 0 | 0 | 80 | 0 | 0 | 56 | 0 | 35 | 20 | 25 | 17 | 6 | 0 | 9 | 17 | 15 | 5 | 50 | 0 | 17 | 0 | 9 | 25 | 250 | 35 | 50 | 17 | 17 | 0 | 17 | 35 | 0 | 0 | 0 | 17 | 0 | 400 | 10 | 400 | 0 | 200 |  | 789 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 15 | 20 | 0 | 67 | 20 | 16 | 0 | 0 | 0 | 32 | 0 | 90 | 28 | 34 | 40 | 8 | 25 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 93 | 0 | 0 | 0 | 6 | 0 | 8 | 0 | 622 | 220 |  | 17 | 6 | 100 | 70 | 0 |  | 580 | 30 | 250 | 1400 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 403 | 0 | 0 | 0 | 450 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 8 | 24 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 33 | 33 | 8 | 0 | 46 | 30 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 6 | 14 | 10 | 0 | 0 | 0 | 350 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 1 | 13 | 8 | 33 | 13 | 94 | 68 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 163 | 0 | 60 | 79 | 0 | 0 | 20 | 0 | 10 | 330 | 16 | 0 | 0 | 3 | 0 | 0 | 56 | 0 | 17 | 5 | 25 | 16 | 6 | 0 | 9 | 17 | 15 | 1 | 16 | 0 | 17 | 0 | 9 | 25 | 200 | 17 | 3 | 0 | 17 | 0 | 0 | 1 | 0 | 0 | 0 | 17 | 0 | 400 | 12 | 420 | 0 | 217 | 0 | 664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 7 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 622 | 220 | 0 | 17 | 0 | 13 | 0 | 0 | 0 | 571 | 1 | 250 | 1302 | 8 | 0 | 0 |  |  |  | 67523168 | 15665454 | 0 | 86056144 | 32138411 | 2190720 | 1123931 | 91680 | 1843880
[8 empty] | 299430 | [13 empty] | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 277 | [14 empty] | 299772 | [10 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 |  | 399747 |  |  |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 | [6 empty] | 399245 |  | 299282 | 399274 |  | 399223 |  | 399630 | 299864 | [11 empty] | 599468 |  |  |  | 230 | [27 empty] | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 | [8 empty] | 599726 | [9 empty] | 67.5232 | 15.6655 | 0 | 86.0561 | 32.1384 | 2.1907 | 1.1239 | 0.09168 | 1.8439
| Minimum Generation |  | 6956 | 5:00
| Highest Generation |  | 10276 | 20:00 | [200 empty] | 206.6334
| Day Peak Generation |  | 9133 | 12:00
| Evening Peak Generation |  | 10276 | 20:00 | [200 empty] | 202699852
| HVDC Max Flow |  | 766 | 13:00 | [200 empty] | 202.6999
| HVDC EvPeak Flow |  | 671 | 20:00
| Load factor L.F |  | 83.78% | [166 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-01-22
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2024-01-21 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9133 | MW Hour : | 12:00 | Min. Gen. at | 4:00 | 6937
Evening Peak Generation : |  |  | 10276 | MW Hour : | 20:00 | Available Max Generation : |  | 11175
E.P. Demand (at gen end) : |  |  | 10276 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 10800
Maximum Generation : |  |  | 10276 | MW Hour : | 20:00 | Reserve(Generation end) |  | 375
Total Gen. (MKWH) : |  |  | 206.6334 | System Load Factor : | 83.78% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 850 | MW at | 19:30 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-01-22
Actual : |  | 89.44 | Ft.(MSL) , | Rule curve : | 99 | Ft.( MSL )
Gas Consumed : |  | Total = | 599.6 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 214701518.324
: |  |  | Coal : | 567994402.68 | Oil : | 582583545.43 | Total : | 1365279466.434
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3499.7913 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 955.1576 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1336.0395 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1159.4645 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 954.9506 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 709.2906 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 398.5972 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 331.2534 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 647.895 |  |  | 0 | 0%
Total |  | 0 |  | 9992.4397 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Haripur 412 MW
8) Ashuganj East
9) Sikalbaha 225 MW
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:19 |  | Bhaluka 132/33kV S/S Transformer- 01 LT Scheduled S/D Due to Annual maintenance
08:19 |  | Bhaluka 132/33kV S/S Transformer- 02 HT Scheduled S/D Due to Annual maintenance
08:36 | 15:33 | Rajbari 132/33kV S/S Bheramara-2 Scheduled S/D Due to to Annual maintenance
08:36 | 15:32 | Bheramara P/S-Faridpur 132 kV Ckt-2 Scheduled S/D from Bheramara 230/132kV end Due to A/M
08:53 | 16:41 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Scheduled S/D from Brahmanbaria 132/33kV end Due to Annual
maintenance. and from Shahjibazar 132/33kV end Due to A/M
09:00 |  | Baroirhat-Hathazari 132 kV Ckt-1 Scheduled S/D from Baroirhat 132/33kV end Due to Dead line checking and from
Hathazari 230/132/33kV end Due to Dead line checking.
09:05 |  | Matarbari 2*600 MW (CPGCL) Syncronized
09:10 | 15:33 | Kabirpur-Kaliakoir 132kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to Annual Maintenance
09:15 |  | Bagerhat-Goalpara 132 kV Ckt-1 Scheduled S/D from Bagerhat 132/33kV end Due to Annual maintenance work.
and from Goalpara 132/33kV end Due to Annual maintenance
09:19 | 11:37 | Fenchuganj -Sylhet 132kV Ckt-1 Scheduled S/D from Sylhet 132/33kV end Due to Annual Maintenance Purpose.
09:30 |  | Mirpur 132/33kV S/S T3 LT Scheduled S/D Due to Annual Maintenance on 132kV T3 Main Bus DS
09:30 | 13:10 | Sonargaon 132/33kV S/S BUS A Scheduled S/D Due to Annual maintenance
09:34 | 15:07 | Ishurdi 132/33kV S/S 132/33 kV T-2 HT Scheduled S/D Due to Annual Maintanance
09:34 | 15:07 | Ishurdi 132/33kV S/S 132/33 kV T-2 LT Scheduled S/D Due to Annual Maintanance
09:37 |  | Allocation Rajshahi zone-830 MW & Rangpur zone-570 MW.
09:42 | 16:30 | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-2 Scheduled S/D Due to Dead line checking
09:43 | 15:22 | Cumilla(S) 132/33kV S/S Cumilla North-2 Scheduled S/D Due to Annual Maintenance
09:46 | 13:53 | Barishal-Bhola 230 kV Ckt-2 Scheduled S/D from Barishal 230/132kV end Due to Annual maintenance
09:49 | 16:05 | Barishal-Bhandaria 132 kV Ckt-1 Scheduled S/D from Barishal 132/33kV end Due to Annual Maintenance and from
Bhandaria 132/33kV end Due to Annual maintenance
10:02 | 17:05 | Mirpur 132/33kV S/S T3 HT Scheduled S/D Due to Annual Maintenance on 132kV T3 Main Bus DS
10:05 | 13:46 | Rajshahi 132/33kV S/S Transformer T-3 (425T) LT Project Work S/D Due to Due to T3 132 kv CB replacing work.
10:11 | 17:04 | Mirpur 132/33kV S/S Main Bus Scheduled S/D Due to Annual Maintenance on 132kV T3 Main Bus DS
10:25 | 18:30 | Haripur-Haripur (360MW) 230kV Ckt-2 Scheduled S/D from Haripur 230/132kV end Due to Annual Deadline
Checking(ES and local grounding close)
10:49 | 17:38 | BIPTC S/S Baharampur-1 Scheduled S/D Due to Annual Maintenance
11:42 | 15:34 | Sylhet (South) S/S Trafo-1 LT Scheduled S/D Due to siemens boundary lighting work on sylhet gis ss
11:42 | 15:34 | Sylhet (South) S/S Trafo-1 HT Scheduled S/D Due to siemens boundary lighting work on sylhet gis ss
12:00 | 13:13 | Kalurghat 132/33kV S/S TRFO-01(506T) LT Forced S/D Due to Redhot maintainance by bpdb
12:00 |  | Day Peak Generation: 9133 MW.
| 12:24 | Madanganj 132/33kV S/S Madanganj -Summit 102 MW 132 kv Ckt is restored.
| 13:25 | Kulaura 132/33kV S/S 132 kV Bus-A is restored.
| 13:30 | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT is restored.
14:12 | 16:06 | Beanibazar 132/33kV S/S 132 KV BUS-1 Forced S/D Due to For tightening loop of line 1 riser.
| 15:34 | Sylhet (South) S/S Trafo-1 LT is restored.
| 15:34 | Sylhet (South) S/S Trafo-1 LT is restored.
15:37 |  | Sylhet (South) S/S Trafo-1 LT Scheduled S/D Due to project lighting works.
15:37 |  | Sylhet (South) S/S Trafo-2 HT Scheduled S/D Due to project lighting works.
16:55 | 19:03 | Bogura 132/33kV S/S Transformer-2 LT Forced S/D Due to 132KV circuit breaker hydrolic oil leakage maintenance work.
16:55 | 19:02 | Bogura 132/33kV S/S Transformer-2 HT Forced S/D Due to 132KV circuit breaker hydrolic oil leakage maintenance work.
17:26 | 17:30 | Kallyanpur 132/33kV S/S GT-1 (132kV) HT Scheduled S/D Due to For Flag reset Standby Earth Fault Relay
| 17:39 | Khulna(S) 230/132kV S/S 230 KV Main Bus 1 is restored.
| 17:52 | Khulna(S) 230/132kV S/S TR-2 HT is restored.
| 17:54 | Khulna(S) 230/132kV S/S TR-2 LT is restored.
18:57 |  | Haripur 412 MW CCPP Syncronized with remarks:- GT
20:00 |  | Evening Peak Gen. 10276 MW
| 20:01 | Maniknagar-Narinda 132kV Ckt-1 is restored.
20:50 |  | Bhola 225 MW CCPP GT-2 was sync.
21:15 |  | Haripur 412 MW CCPP Syncronized with remarks:- ST
21:49 |  | Meghnaghat CCPP(Summit)-2 Syncronized with remarks:- GT
21:49 |  | Sum. Meghna-2 GT was sync.
23:28 |  | Meghnaghat CCPP(Summit)-2 Tripped
23:28 |  | Meghnaghat CCPP(Summit)-2 Tripped with remarks:- GT
23:28 |  | Meghnaghat CCPP(Summit)-2 Tripped with remarks:- GT
03:05 |  | Meghnaghat CCPP(Summit)-2 Syncronized with remarks:- GT
04:00 |  | Minimum generation 6937 MW.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-01-21 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 3433500 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 915818 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 25 | 507600 | Syncronized at 18:57.
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9572000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 53 | 1208640 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 82 | 553768
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 198581 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 25 | 364533 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 73 | 1094400 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 91 | 1056820 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 64080 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 1179360 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 68563 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 65241 | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 39 | 925200 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 570100
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 23 | 407800 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 17 | 268320 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 260 | 2760000 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 96 | 1240416 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1106880
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 72 | 968640 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 136800 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 116096
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 132840 | Fuel shortage
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 78494 | On test.
| Dhaka area Total |  |  |  | 5062 | 1868 | 28994490
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 253130 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 115695
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 227040 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 76 | 1843880 | Unit-3 under maint.
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 0 | 0 | Gas shortage
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 16 | 511854 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 64 | 1316758 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 1183074 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 25 | 449160 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 624000 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 437136 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 15 | 218400
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 22684
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 106 | 1036255 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 124656 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 414000 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 611520 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 260945 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 36 | 669091 | Fuel shortage
| SS Power I |  | SS Power | 2*612 | 1224 | 480 | 9687271 | Coal shortage
| Cox's Bazar Wind |  | IPP | 66 | 0 | 0 | 91680 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 419 | 4981818 | On test.
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4344 | 1427 | 25080047
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 147 | 3425000 | ST under shutdown
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 330 | 8000600 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 0 | 54000 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 0 | 0 | Gas shortage
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1242899
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 13 | 227490 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 25 | 600016 | Fuel shortage
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 425280 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 13 | 366516 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 212400
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 106 | 2190720
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 811700
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 186322
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 18 | 396280 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 67260
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 78 | 692160 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 272880 | Fuel shortage
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 79680 | Fuel shortage
| Cumilla Area Total |  |  |  | 2951 | 864 | 19251203
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 73 | 1476480 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Contract Expired
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 2350
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 78 | 1125600 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 28 | 308400 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 157590
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 72720 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 185 | 3143140
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1015000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 755000 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3869018
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1387488
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 2008320
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Under maint.
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 20 | 481000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 391008 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7452000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Under maint.
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 244620
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 350 | 7692900
| Sylhet Area Total |  |  |  | 2427 | 1074 | 25296354
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 671 | 15665454
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 33 | 184320 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 28 | 250080 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 10 | 95616 | Fuel shortage
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 16 | 139125 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 93 | 1681920 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 303840
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 599 | 13490910
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 1450 | 31811265
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 113376 | Fuel shortage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 20 | 382200 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 67 | 1782000 | Gt-1 & ST Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 622 | 15379300 | Unit-2 under maint.
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 514489
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 439200 | Fuel shortage
| Barisal 307 MW |  | IPP | 307*1 | 307 | 200 | 6349100 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1162 | 24959665
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 777541 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 15 | 183769 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 28 | 621340 | Fuel shortage
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 577952 | Fuel shortage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 429912
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 218 | 6336290 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 269629 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 159912
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 103238 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 970704 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 218688 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 263424 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 6840
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1423 | 32034545
| Rajshahi Area Total |  |  |  | 3631 | 2006 | 42953784
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4133200 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 35 | 274252 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 11052
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 35 | 337152 | Fuel shortage
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 59224
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 328560
| Rangpur Area Total |  |  |  | 950 | 240 | 5143440
| Total |  |  |  | 25481 | 10276 | 206633388
| Eastern Grid Total |  |  |  | 15398 | 5418 | 101765234
| Western Grid Total |  |  |  | 10083 | 4858 | 104868154
| National Grid Total |  |  |  | 25481 | 10276 | 206633388
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2024-01-21
| (a) ENTIRE EASTERN GRID : |  | 6548.46 | MW | (b) ENTIRE WESTERN GRID : |  | 3165.7 | MW
| i) Dhaka area |  | 3586.76 | MW | i) Khulna area |  | 1157 | MW
| ii) Chittagong area |  | 930.7 | MW | ii) Rajshahi area |  | 1004.6 | MW
| iii) Comilla area |  | 853 | MW | iii) Barisal area |  | 303.1 | MW
| iv) Mymensingh area |  | 817 | MW | iv) Rangpur area |  | 701 | MW
| v) Sylhet area |  | 361 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 9714.16 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 4 | 20:00 | Chhatak | 19 | 20:00 | Kamrangirchar | 46.2 | 13:00 | Narinda | 46 | 13:00 | Sherpur | 110 | 20:00
2 | AKSML | 119 | 08:00 | Chowmuhani | 146 | 19:30 | Kaptai | N/A | N/A | Narshingdi | 146 | 19:00 | Shikalbaha | 18 | 18:00
3 | Aftabnagar | 24 | 12:00 | Chuadanga | 66 | 19:30 | Kazla | 63 | 01:00 | Natore | 100 | 13:00 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 55 | 13:00 | Coxsbazar | 95 | 21:00 | Keranigonj | 62 | 13:00 | Nawabganj | 28 | 20:00 | Shitalakhya | 79.5 | 12:00
5 | Agrabad | 48 | 15:00 | Cumilla(N) | 90 | 18:00 | Khagrachori | 22 | 17:00 | Netrakona | 116 | 22:00 | Sholosohor | 32 | 18:00
6 | Amnura | 51 | 09:00 | Cumilla(S) | 112 | 13:00 | Khulna | 70 | 19:30 | New | 18 | 12:00 | Shyampur | 162 | 11:00
7 | Ashuganj | 45 | 13:00 | Daudkandi | 114 | 19:30 | Khulshi | 140 | 18:00 | Niamatpur | 68 | 22:00 | Siddhirganj | 94 | 11:00
8 | BIPTC | N/A | N/A | Dhaka | 14 | 11:00 | Kishoreganj | 110 | 21:00 | Noapara | 38 | 19:30 | Sirajganj | 84 | 19:30
9 | BSRM | 76 | 13:00 | Dhamrai | 94 | 15:00 | Kodda | 243 | 18:00 | PHP | 3 | 18:30 | Sonargaon | 94 | 21:00
10 | Bagerhat | 66 | 20:00 | Dhanmondi | 91 | 13:00 | Kulaura | 26 | 18:00 | Pabna | 69 | 18:30 | Sreemongol | 42 | 19:30
11 | Bakulia | 61 | 18:00 | Dohazari | 46 | 15:00 | Kurigram | 59 | 18:00 | Palashbari | 86 | 18:30 | Sreepur | 61 | 18:30
12 | Banani | 24 | 00:00 | Faridpur | 111 | 20:00 | Kushtia | 96 | 21:00 | Panchagarh | 45 | 18:00 | Srinagar | 29.02 | 20:00
13 | Bangabhaban | 7 | 11:00 | Fatullah | 54 | 12:00 | Lalbag | 69 | 13:00 | Patuakhali | 67.2 | 21:00 | Sunamganj | 35 | 19:30
14 | Barapukuria | 51 | 18:30 | Fenchuganj | 22 | 18:30 | Lalmonirhat | 43 | 18:30 | Payra | 14 | 18:00 | Sylhet | 14 | 13:00
15 | Barguna | 14 | 19:30 | Feni | 70 | 19:30 | MI_Cement | 12.3 | 13:00 | Postogola | 35 | 12:00 | Sylhet-132 | 84 | 18:00
16 | Barishal | 78 | 20:00 | GPH | 93 | 15:00 | Madanganj | 33 | 11:00 | Purbachal | 13 | 18:00 | TK | 20 | 21:00
17 | Barishal-230 | 64 | 19:30 | Ghorashal | 63 | 08:00 | Madaripur | 65 | 21:00 | Purbasadipur | 107 | 18:30 | Tangail | 148 | 18:00
18 | Baroaulia | 51 | 00:00 | Goalpara | 24 | 19:30 | Madartek | 49.7 | 13:00 | Rahim | 48 | 03:00 | Thakurgaon | 77 | 18:30
19 | Baroirhat | 40 | 20:00 | Gollamari | 39 | 13:00 | Madunaghat | 36 | 18:00 | Rajbari | 45 | 21:00 | Tongi | 108 | 11:00
20 | Bashundhara | 132 | 13:00 | Gopalganj | 75 | 20:00 | Magura | 41 | 20:00 | Rajendrapur | 70 | 18:30 | Ullahpara | 15 | 19:00
21 | BashundharaCement | 0 | 00:00 | Gulshan | 62 | 13:00 | Mahasthangarh | 44 | 20:00 | Rajshahi | 111 | 21:00 | Ullon | 29 | 13:00
22 | Beanibazar | 40 | 18:00 | Halishahar | 68 | 14:00 | Manikganj | 106 | 19:00 | Rajshahi-230 | 26 | 19:00 | Uttara | 28 | 18:00
23 | Benapole | 60 | 08:00 | HaripurSBU | 138 | 17:00 | Maniknagar | 50 | 12:00 | Ramganj | 68 | 19:30 | UttaraNew | 29 | 13:00
24 | Bhaluka | 110 | 21:00 | Hasnabad | 67 | 19:00 | Matarbari | 29 | 22:00 | Rampur | 17 | 18:30 | Zigatola | 47 | 20:00
25 | Bhandaria | 34 | 21:00 | Hathazari | 46 | 20:00 | Matuail | 52 | 09:00 | Rangamati | 12 | 19:30
26 | Bhangura | 28 | 18:30 | Ishurdi | 46 | 18:00 | Millgate | 80 | 12:00 | Rangpur | 110 | 18:30
27 | Bheramara(GK) | 39 | 20:00 | Jaldhaka | 62 | 18:30 | Mirpur | 84 | 12:00 | Ruppur | 3.8 | 15:00
28 | Bhulta | 240 | 02:00 | Jamalpur | 120 | 20:00 | Mirsorai | 4 | 00:00 | SSM | 14 | 23:00
29 | Bog-Sherpur | 48 | 18:00 | Jashore | 101 | 20:00 | Mirzapur | 48 | 18:00 | Saidpur | 96 | 18:00
30 | Bogura | 114 | 19:30 | Jhenaidah | 84 | 20:00 | Mithapukur | 44 | 18:30 | Satkhira | 89 | 18:30
31 | Borhanuddin | 37 | 19:30 | Joydebpur | 130 | 15:00 | Modern | 0 | 00:00 | Satmasjid | 85 | 13:00
32 | Brahmanbaria | 105 | 20:00 | Joypurhat | 44 | 20:00 | Mogbazar | 64.4 | 13:00 | Savar | 116 | 07:00
33 | Cantonment | 90 | 13:00 | Juldah | 15 | 23:00 | Mongla | 28 | 07:00 | SevenRings | 4.39 | 09:00
34 | Chandpur | 41 | 19:00 | KSRM | 69.5 | 00:00 | Motijheel | 27 | 13:00 | ShahCement | 31 | 03:00
35 | Chandraghona | 22 | 20:00 | Kabirpur | 206 | 19:00 | Munshiganj | 60 | 19:30 | Shahjadpur | 53 | 18:30
36 | Chapai | 51 | 09:00 | Kachua | 47 | 19:30 | Mymensingh | 166 | 18:00 | Shahjibazar | 91 | 20:00
37 | Charsaidpur | 37 | 16:00 | Kallyanpur | 69 | 13:00 | Naogaon | 95 | 21:00 | Shahmirpur | 38.7 | 18:00
38 | Chauddagram | 38 | 18:00 | Kalurghat | 26 | 12:00 | Narail | 38 | 20:00 | Shariatpur | 51 | 21:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-01-21 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 409 | 05:00 | 393 | 11:00 | Gopalganj | 412 | 05:00 | 398 | 10:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 422 | 19:00 | 403 | 16:00
| Bhulta | 406 | 03:00 | 386 | 15:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 423 | 19:00 | 412 | 16:00 | Payra | 417 | 05:00 | 408 | 12:00
| BIPTC | 409 | 02:00 | 391 | 12:00 | Rahanpur | 414 | 05:00 | 392 | 11:00
| Bogura | N/A | N/A | N/A | N/A | Rampal | 409 | 02:00 | 394 | 10:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 238 | 05:00 | 228 | 10:00 | Hasnabad | 239 | 05:00 | 228 | 11:00
| AKSML | 242 | 19:00 | 232 | 16:00 | Hathazari | 243 | 19:00 | 235 | 16:00
| Aminbazar | 240 | 02:00 | 227 | 22:00 | Ishurdi | 240 | 02:00 | 225 | 08:00
| Ashuganj | 240 | 02:00 | 230 | 11:00 | Jhenaidah | 236 | 02:00 | 221 | 08:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 238 | 19:00 | 227 | 16:00
| Baghabari | 236 | 03:00 | 223 | 11:00 | Keranigonj | 238 | 05:00 | 226 | 22:00
| Barapukuria | 225 | 04:00 | 212 | 12:00 | Khulna(S) | 240 | 05:00 | 231 | 08:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 242 | 01:00 | 234 | 12:00 | Maniknagar | 239 | 05:00 | 228 | 11:00
| Bheramara | 238 | 02:00 | 223 | 08:00 | Meghnaghat | 244 | 21:00 | 234 | 12:00
| Bhulta | 241 | 03:00 | 229 | 15:00 | Mirsorai | 242 | 19:00 | 232 | 16:00
| Bibiana | 241 | 00:00 | 235 | 16:00 | Rajshahi | 239 | 02:00 | 226 | 11:00
| BIPTC | 239 | 02:00 | 223 | 11:00 | Rampal | 237 | 19:00 | 227 | 08:00
| Bogura | 228 | 05:00 | 214 | 13:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 245 | 03:00 | 241 | 11:00 | Rampura | 239 | 04:00 | 228 | 11:00
| BSRM | 242 | 05:00 | 235 | 10:00 | Shikalbaha | 239 | 04:00 | 233 | 17:00
| Cumilla(N) | 241 | 02:00 | 231 | 16:00 | Shyampur | 239 | 05:00 | 228 | 11:00
| Fenchuganj | 246 | 00:00 | 240 | 15:00 | Siddhirganj | 239 | 19:00 | 228 | 07:00
| Ghorashal | 240 | 00:00 | 235 | 14:00 | Sirajgonj | 235 | 19:30 | 229 | 12:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 237 | 05:00 | 225 | 12:00
| GPH | 241 | 05:00 | 234 | 15:00 | Tongi | 240 | 18:30 | 228 | 10:00
| Haripur | 238 | 19:00 | 229 | 11:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 137 | 05:00 | 128 | 11:00 | Lalbag | 137 | 05:00 | 129 | 12:00
| Agargaon | 140 | 01:00 | 134 | 10:00 | Lalmonirhat | 130 | 03:00 | 119 | 13:00
| Agrabad | 140 | 01:00 | 135 | 16:00 | Madanganj | 137 | 19:30 | 129 | 11:00
| AKS | 137 | 21:00 | 135 | 23:00 | Madaripur | 136 | 03:00 | 131 | 15:00
| Aminbazar | 136 | 04:00 | 129 | 12:00 | Madartek | 136 | 03:00 | 128 | 11:00
| Amnura | 142 | 19:00 | 125 | 09:00 | Madunaghat | 141 | 01:00 | 137 | 14:00
| Ashuganj | 141 | 04:00 | 137 | 11:00 | Magura | 139 | 02:00 | 129 | 08:00
| Bagerhat | 137 | 01:00 | 125 | 23:00 | Mahasthangarh | 135 | 03:00 | 124 | 13:00
| Bakulia | 141 | 21:00 | 135 | 15:00 | Manikganj | 136 | 00:00 | 124 | 11:00
| Banani | 137 | 01:00 | 129 | 10:00 | Maniknagar | 133 | 22:00 | 126 | 11:00
| Bangabhaban | 133 | 02:00 | 126 | 12:00 | Matarbari | 132 | 19:00 | 127 | 15:00
| Barapukuria | 136 | 05:00 | 126 | 12:00 | Matuail | 135 | 05:00 | 128.5 | 11:00
| Barguna | 137 | 18:30 | 134 | 09:00 | Millgate | 137 | 01:00 | 129 | 10:00
| Barishal | 139 | 03:00 | 133 | 16:00 | Mirpur | 135 | 05:00 | 130 | 9:00
| Barishal-230 | 139 | 01:00 | 134 | 12:00 | Mirzapur | 136 | 03:00 | 128 | 07:00
| Baroaulia | 141 | 09:00 | 136 | 16:00 | Mithapukur | 133 | 03:00 | 122 | 12:00
| Baroirhat | 140 | 19:00 | 131 | 12:00 | MI_Cement | 138 | 19:00 | 130 | 11:00
| Bashundhara | 137 | 01:00 | 129 | 11:00 | Modern | 140 | 19:00 | 136 | 15:00
| BashundharaCement | 137 | 19:30 | 129 | 11:00 | Mogbazar | 138 | 02:00 | 130 | 11:00
| Beanibazar | 136 | 03:00 | 132 | 16:00 | Mongla | 136 | 19:00 | 127 | 23:00
| Benapole | 137 | 03:00 | 124 | 08:00 | Motijheel | 133 | 02:00 | 126 | 12:00
| Bhaluka | 133 | 05:00 | 124 | 16:00 | Munshiganj | 137 | 19:00 | 129 | 11:00
| Bhandaria | 137 | 03:00 | 128 | 12:00 | Mymensingh | 136 | 19:00 | 122 | 17:00
| Bhangura | 141 | 05:00 | 132 | 08:00 | Naogaon | 133 | 04:00 | 120 | 13:00
| Bheramara | 139 | 02:00 | 130 | 08:00 | Narail | 139 | 06:00 | 128 | 08:00
| Bheramara(GK) | 136 | 00:00 | 130 | 10:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 126 | 18:00 | 120 | 00:00 | Narshingdi | 136 | 02:00 | 123 | 16:00
| Bog-Sherpur | 137 | 03:00 | 126 | 11:00 | Natore | 137 | 01:00 | 129 | 08:00
| Bogura | 137 | 05:00 | 126 | 13:00 | Nawabganj | 137 | 04:00 | 129 | 13:00
| Bogura-230 | 136 | 05:00 | 125 | 13:00 | Netrakona | 136 | 18:30 | 121 | 17:00
| Brahmanbaria | 138 | 05:00 | 130 | 15:00 | New | 138 | 19:30 | 130 | 10:00
| Cantonment | 141 | 05:00 | 133 | 13:00 | Niamatpur | 132 | 01:00 | 118 | 08:00
| Chandpur | 138 | 01:00 | 131 | 11:00 | Noapara | 137 | 02:00 | 128 | 08:00
| Chandraghona | 142 | 04:00 | 138 | 08:00 | Pabna | 140 | 02:00 | 131 | 08:00
| Chapai | 135 | 05:00 | 126 | 15:00 | Palashbari | 133 | 03:00 | 121 | 12:00
| Charsaidpur | 137 | 19:00 | 129 | 11:00 | Panchagarh | 135 | 04:00 | 118 | 13:00
| Chauddagram | 142 | 03:00 | 133 | 12:00 | Patuakhali | 136 | 05:00 | 133 | 08:00
| Chhatak | 136 | 01:00 | 131 | 16:00 | Payra | 136 | 01:00 | 133 | 10:00
| Chowmuhani | 137 | 00:00 | 130 | 12:00 | PHP | 140 | 00:00 | 132 | 12:00
| Chuadanga | 138 | 04:00 | 126 | 08:00 | Postogola | 139 | 22:00 | 131 | 11:00
| Coxsbazar | 130 | 17:00 | 123 | 15:00 | Purbachal | 138 | 19:00 | 128 | 11:00
| Cumilla(N) | 143 | 01:00 | 137 | 16:00 | Purbasadipur | 129 | 03:00 | 117 | 12:00
| Cumilla(S) | 143 | 01:00 | 130 | 09:00 | Rahanpur | 135 | 05:00 | 130 | 12:00
| Daudkandi | 135 | 18:30 | 127 | 12:00 | Rahim | 135 | 22:00 | 129 | 11:00
| Dhaka | 137 | 03:00 | 129 | 11:00 | Rajbari | 137 | 02:00 | 130 | 08:00
| Dhamrai | 137 | 01:00 | 128 | 16:00 | Rajendrapur | 137 | 02:00 | 128 | 17:00
| Dhanmondi | 136 | 04:00 | 128 | 12:00 | Rajshahi | 137 | 19:00 | 130 | 10:00
| Dohazari | 139 | 09:00 | 133 | 17:00 | Rajshahi-230 | 137 | 01:00 | 123 | 08:00
| Faridpur | 136 | 04:00 | 130 | 12:00 | Ramganj | 138 | 19:00 | 130 | 12:00
| Fatullah | 138 | 19:00 | 131 | 11:00 | Rampur | 140 | 07:00 | 136 | 00:00
| Fenchuganj | 140 | 06:00 | 136 | 16:00 | Rampura | 136 | 04:00 | 129 | 10:00
| Feni | 138 | 00:00 | 132 | 12:00 | Rangamati | 141 | 02:00 | 137 | 12:00
| Ghorashal | 143 | 04:00 | 135 | 15:00 | Rangpur | 132 | 04:00 | 122 | 12:00
| Goalpara | 138 | 01:00 | 130 | 08:00 | Ruppur | 139 | 03:00 | 132 | 12:00
| Gollamari | 135 | 00:00 | 130 | 08:00 | Saidpur | 131 | 04:00 | 121 | 11:00
| Gopalganj | 135 | 01:00 | 129 | 08:00 | Satkhira | 134 | 00:00 | 125 | 08:00
| Gopalganj-400 | 135 | 02:00 | 130 | 10:00 | Satmasjid | 140 | 01:00 | 133 | 11:00
| Gulshan | 136 | 05:00 | 128 | 15:00 | Savar | 135 | 04:00 | 126 | 16:00
| Halishahar | 141 | 19:00 | 136 | 15:00 | SevenRings | 144 | 02:00 | 136 | 16:00
| Haripur | 135 | 21:00 | 129 | 11:00 | ShahCement | 137 | 19:00 | 129 | 11:00
| HaripurSBU | 135 | 22:00 | 129 | 11:00 | Shahjadpur | 141 | 02:00 | 134 | 11:00
| Hasnabad | 138 | 20:00 | 132 | 10:00 | Shahjibazar | 136 | 00:00 | 132 | 15:00
| Hathazari | 142 | 19:00 | 137 | 15:00 | Shahmirpur | 140 | 18:30 | 135 | 16:00
| Ishurdi | 141 | 02:00 | 132 | 11:00 | Shariatpur | 134 | 00:00 | 129 | 12:00
| Jaldhaka | 131 | 04:00 | 119 | 12:00 | Sherpur | 133 | 19:00 | 119 | 17:00
| Jamalpur | 136 | 18:30 | 121 | 17:00 | Shikalbaha | 129 | 09:00 | 123 | 15:00
| Jashore | 135 | 00:00 | 127 | 08:00 | Shikalbaha-230 | 141 | 03:00 | 137 | 16:00
| Jhenaidah | 138 | 01:00 | 131 | 11:00 | Shitalakhya | 138 | 19:00 | 130 | 11:00
| Jhenaidah-230 | 140 | 02:00 | 130 | 08:00 | Sholosohor | 141 | 03:00 | 136 | 15:00
| Joydebpur | 144 | 19:00 | 134 | 16:00 | Shyampur | 136 | 02:00 | 130 | 11:00
| Joypurhat | 134 | 05:00 | 120 | 09:00 | Shyampur-230 | 138 | 19:00 | 130 | 11:00
| Juldah | 140 | 19:00 | 137 | 12:00 | Siddhirganj | 135 | 18:00 | 130 | 10:00
| Kabirpur | 138 | 01:00 | 123 | 15:00 | Sirajganj | 138 | 02:00 | 128 | 13:00
| Kachua | 140 | 02:00 | 132 | 12:00 | Sonargaon | 133 | 19:30 | 129 | 00:00
| Kaliakoir | 140 | 04:00 | 132 | 12:00 | Sreemongol | 136 | 00:00 | 133 | 15:00
| Kallyanpur | 136 | 01:00 | 130 | 12:00 | Sreepur | 136 | 01:00 | 127 | 12:00
| Kalurghat | 142 | 01:00 | 136 | 12:00 | Srinagar | 137 | 01:00 | 130 | 11:00
| Kamrangirchar | 137 | 04:00 | 129 | 13:00 | SSM | 145 | 19:00 | 139 | 16:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 135 | 01:00 | 130 | 16:00
| Kazla | 134 | 04:00 | 126 | 12:00 | Sylhet | 137 | 01:00 | 133 | 15:00
| Keranigonj | 137 | 05:00 | 130 | 11:00 | Sylhet-132 | 137 | 02:00 | 132 | 15:00
| Khagrachori | 141 | 03:00 | 137 | 12:00 | Tangail | 134 | 19:00 | 126 | 16:00
| Khulna | 136 | 19:00 | 129 | 08:00 | Thakurgaon | 133 | 03:00 | 118 | 12:00
| Khulna(S) | 136 | 01:00 | 129 | 08:00 | TK | 141 | 19:00 | 137 | 04:00
| Khulshi | 140 | 04:00 | 135 | 12:00 | Tongi | 138 | 03:00 | 130 | 15:00
| Kishoreganj | 136 | 04:00 | 129 | 12:00 | Ullahpara | 137 | 00:00 | 130 | 10:00
| Kodda | 141 | 05:00 | 129 | 16:00 | Ullon | 136 | 03:00 | 128 | 12:00
| KSRM | 142 | 19:00 | 136 | 15:00 | Uttara | 137 | 01:00 | 129 | 14:00
| Kulaura | 139 | 01:00 | 135 | 16:00 | UttaraNew | 137 | 01:00 | 130 | 09:00
| Kurigram | 128 | 05:00 | 117 | 09:00 | Zigatola | 137 | 02:00 | 129 | 13:00
| Kushtia | 139 | 02:00 | 130 | 08:00

## L-Curve
Date | 2024-01-21
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1130 | 4007 | 4317 | 8324 |  |  |  | QF-LDC-11
0:30 | 1200 | 3812 | 4397 | 8209 | Date: | 2024-01-21
1:00 | 1270 | 3617 | 4477 | 8094
1:30 | 1230 | 3546 | 4240.5 | 7786.5
2:00 | 1190 | 3475 | 4004 | 7479
2:30 | 1175 | 3433 | 3913 | 7346 | [5 empty] | Gen. at Eve. Peak | 10276 | 10276 MW (20:00 )
3:00 | 1160 | 3391 | 3822 | 7213 | [6 empty] | 20:00
3:30 | 1080 | 3354.5 | 3732 | 7086.5 | [5 empty] | Gen. at Day Peak | 9133 | 9133 MW (12:00 )
4:00 | 1000 | 3318 | 3642 | 6960 | [6 empty] | 12:00
4:30 | 945 | 3310.5 | 3647.5 | 6958 | [5 empty] | Highest Generation | 10276
5:00 | 890 | 3303 | 3653 | 6956 | [6 empty] | 20:00
5:30 | 940 | 3370.5 | 3804.5 | 7175
6:00 | 990 | 3438 | 3956 | 7394
6:30 | 1010 | 3525.5 | 4207 | 7732.5
7:00 | 1030 | 3613 | 4458 | 8071
7:30 | 1115 | 3667.5 | 4574 | 8241.5
8:00 | 1200 | 3722 | 4690 | 8412
8:30 | 1180 | 3724 | 4695.5 | 8419.5
9:00 | 1160 | 3726 | 4701 | 8427
9:30 | 1150 | 3813.5 | 4687 | 8500.5
10:00 | 1140 | 3901 | 4673 | 8574
10:30 | 1160 | 3987.5 | 4701.5 | 8689
11:00 | 1180 | 4074 | 4730 | 8804
11:30 | 1145 | 4230.5 | 4738 | 8968.5
12:00 | 1110 | 4387 | 4746 | 9133
12:30 | 1110 | 4494.5 | 4753 | 9247.5
13:00 | 1110 | 4602 | 4760 | 9362
13:30 | 1170 | 4534.5 | 4697 | 9231.5
14:00 | 1230 | 4467 | 4634 | 9101
14:30 | 1305 | 4459 | 4604.5 | 9063.5
15:00 | 1380 | 4451 | 4575 | 9026
15:30 | 1340 | 4527.5 | 4579 | 9106.5
16:00 | 1300 | 4604 | 4583 | 9187
16:30 | 1265 | 4672.5 | 4586 | 9258.5
17:00 | 1230 | 4741 | 4589 | 9330
17:30 | 1165 | 4969.5 | 4742 | 9711.5
18:00 | 1100 | 5198 | 4895 | 10093
18:30 | 1020 | 5294.5 | 4870 | 10164.5
19:00 | 940 | 5391 | 4845 | 10236
19:30 | 850 | 5447 | 4815 | 10262
20:00 | 860 | 5418 | 4858 | 10276 |  |  |  | Executive Engineer
20:30 | 895 | 5348 | 4885 | 10233 |  |  |  | Network Operation Division
21:00 | 930 | 5278 | 4912 | 10190
21:30 | 1013 | 5032 | 4885.5 | 9917.5
22:00 | 1096 | 4786 | 4859 | 9645 |  |  |  |  | Page 6 of 7
22:30 | 1068 | 4566 | 4735 | 9301
23:00 | 1040 | 4346 | 4611 | 8957
23:30 | 1085 | 4176.5 | 4464 | 8640.5
24:00 | 1130 | 4007 | 4317 | 8324
10276 MW (20:00 )
9133 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-01-21 |  | Energy |  | 206633388
QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 1646 | 747 | 1421 | 0 | 432 | 3636 | 76 | 0 | 266 | 96 | 0 | 4 | 0
0:30 | 1507 | 700 | 1535.5 | 0 | 528.5 | 3488 | 76 | 0 | 282.5 | 86 | 0 | 5.5 | 0 |  | Date: | 43850
1:00 | 1368 | 653 | 1650 | 0 | 625 | 3340 | 76 | 0 | 299 | 76 | 0 | 7 | 0
1:30 | 1367 | 542.5 | 1661.5 | 0 | 529.5 | 3252 | 76 | 0 | 276 | 74 | 0 | 8 | 0 | [8 empty] | Total Energy | 206.6334 | 206.6334 | Total Energy Gen 206.633 MKWHr Energy Not Served 5.586 MKWHr Energy Requirement 212.219 MKWHr
2:00 | 1366 | 432 | 1673 | 0 | 434 | 3164 | 76 | 0 | 253 | 72 | 0 | 9 | 0 | [8 empty] | Energy not Served | 5.5859 | 5.5859
2:30 | 1370.5 | 432 | 1620.5 | 0 | 398.5 | 3133 | 76 | 0 | 234.5 | 71 | 0 | 10 | 0 | [8 empty] | Energy Requirement | 212.2193 | 212.2193
3:00 | 1375 | 432 | 1568 | 0 | 363 | 3102 | 76 | 0 | 216 | 70 | 0 | 11 | 0
3:30 | 1365.5 | 432 | 1532 | 0 | 356.5 | 3028.5 | 76 | 0 | 215.5 | 69 | 0 | 11.5 | 0 | [7 empty] | Shortage
4:00 | 1356 | 432 | 1496 | 0 | 350 | 2955 | 76 | 0 | 215 | 68 | 0 | 12 | 0
4:30 | 1342 | 432 | 1500 | 0 | 350 | 2962 | 76 | 0 | 215 | 69 | 0 | 12 | 0
5:00 | 1328 | 432 | 1504 | 0 | 350 | 2969 | 76 | 0 | 215 | 70 | 0 | 12 | 0
5:30 | 1332.5 | 431.5 | 1610.5 | 0 | 400.5 | 3026.5 | 76 | 0 | 215 | 72 | 0 | 10.5 | 0
6:00 | 1337 | 431 | 1717 | 0 | 451 | 3084 | 76 | 0 | 215 | 74 | 0 | 9 | 0
6:30 | 1314.5 | 525 | 1737 | 0 | 559.5 | 3221.5 | 76 | 0 | 215 | 75 | 1 | 8 | 0 | [6 empty] | Coal
7:00 | 1292 | 619 | 1757 | 0 | 668 | 3359 | 76 | 0 | 215 | 76 | 2 | 7 | 0
7:30 | 1297.5 | 654.5 | 1746 | 0 | 708 | 3442.5 | 76 | 0 | 214 | 81 | 16 | 6 | 161.395 | [5 empty] | Oil
8:00 | 1303 | 690 | 1735 | 0 | 748 | 3526 | 76 | 0 | 213 | 86 | 30 | 5 | 322.79
8:30 | 1303 | 690 | 1715.5 | 0 | 750 | 3526.5 | 76 | 0 | 213 | 89 | 54 | 2.5 | 482.7525
9:00 | 1303 | 690 | 1696 | 0 | 752 | 3527 | 76 | 0 | 213 | 92 | 78 | 0 | 642.715
9:30 | 1280.5 | 690.5 | 1658.5 | 0 | 812.5 | 3562.5 | 76 | 0 | 228 | 94 | 98 | 0 | 715.7725
10:00 | 1258 | 691 | 1621 | 0 | 873 | 3598 | 76 | 0 | 243 | 96 | 118 | 0 | 788.83
10:30 | 1267.5 | 690.5 | 1607.5 | 0 | 926.5 | 3601.5 | 76 | 0 | 296.5 | 98 | 125 | 0 | 798.38
11:00 | 1277 | 690 | 1594 | 0 | 980 | 3605 | 76 | 0 | 350 | 100 | 132 | 0 | 807.93
11:30 | 1352.5 | 727.5 | 1566.5 | 0 | 1023.5 | 3619 | 76 | 0 | 377.5 | 103 | 123 | 0 | 769.965
12:00 | 1428 | 765 | 1539 | 0 | 1067 | 3633 | 76 | 0 | 405 | 106 | 114 | 0 | 732
12:30 | 1455 | 765.5 | 1531 | 0 | 1072.5 | 3695.5 | 76 | 0 | 411 | 109 | 132 | 0 | 699.7725
13:00 | 1482 | 766 | 1523 | 0 | 1078 | 3758 | 76 | 0 | 417 | 112 | 150 | 0 | 667.545
13:30 | 1482 | 766 | 1523 | 0 | 1078 | 3758 | 76 | 0 | 417 | 112 | 150 | 0 | 667.545
14:00 | 1482 | 766 | 1523 | 0 | 1078 | 3758 | 76 | 0 | 417 | 112 | 150 | 0 | 667.545
14:30 | 1481 | 765.5 | 1447.5 | 0 | 1118.5 | 3660 | 76 | 0 | 383 | 107 | 155.5 | 0 | 512.3575
15:00 | 1480 | 765 | 1372 | 0 | 1159 | 3562 | 76 | 0 | 349 | 102 | 161 | 0 | 357.17
15:30 | 1462 | 765.5 | 1400.5 | 0 | 1216.5 | 3618 | 76 | 0 | 347.5 | 100 | 120 | 0.5 | 178.585
16:00 | 1444 | 766 | 1429 | 0 | 1274 | 3674 | 76 | 0 | 346 | 98 | 79 | 1 | 0
16:30 | 1451 | 766 | 1458.5 | 0 | 1346 | 3658.5 | 76 | 0 | 355 | 97 | 49.5 | 1 | 0
17:00 | 1458 | 766 | 1488 | 0 | 1418 | 3643 | 76 | 0 | 364 | 96 | 20 | 1 | 0
17:30 | 1483.5 | 766 | 1500 | 0 | 1639 | 3679 | 76 | 0 | 456.5 | 101 | 10 | 0.5 | 194.5
18:00 | 1509 | 766 | 1512 | 0 | 1860 | 3715 | 76 | 0 | 549 | 106 | 0 | 0 | 389
18:30 | 1511.5 | 718.5 | 1523 | 0 | 1881 | 3786 | 76 | 0 | 561.5 | 107 | 0 | 0 | 416.06
19:00 | 1514 | 671 | 1534 | 0 | 1902 | 3857 | 76 | 0 | 574 | 108 | 0 | 0 | 443.12
19:30 | 1535 | 672 | 1562 | 0 | 1857 | 3854 | 76 | 0 | 598 | 108 | 0 | 0 | 221.56
20:00 | 1545 | 671 | 1531 | 0 | 1854 | 3913 | 76 | 0 | 580 | 106 | 0 | 0 | 0
20:30 | 1511 | 718 | 1559.5 | 0 | 1807.5 | 3878 | 76 | 0 | 578 | 105 | 0 | 0 | 0
21:00 | 1477 | 765 | 1588 | 0 | 1761 | 3843 | 76 | 0 | 576 | 104 | 0 | 0 | 0
21:30 | 1528.5 | 764.5 | 1533 | 0 | 1566.5 | 3844.5 | 76 | 0 | 502.5 | 102 | 0 | 0 | 0
22:00 | 1580 | 764 | 1478 | 0 | 1372 | 3846 | 76 | 0 | 429 | 100 | 0 | 0 | 0
22:30 | 1626.5 | 764.5 | 1469.5 | 0 | 1041 | 3812.5 | 76 | 0 | 410.5 | 99 | 0 | 1.5 | 0
23:00 | 1673 | 765 | 1461 | 0 | 710 | 3779 | 76 | 0 | 392 | 98 | 0 | 3 | 0
23:30 | 1659.5 | 756 | 1441 | 0 | 571 | 3707.5 | 76 | 0 | 329 | 97 | 0 | 3.5 | 0 |  | Max Temp. in Dhaka |  | 23.6°C
24:00 | 1646 | 747 | 1421 | 0 | 432 | 3636 | 76 | 0 | 266 | 96 | 0 | 4 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 206.633 MKWHr Energy Not Served 5.586 MKWHr Energy Requirement 212.219 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2024-01-21
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1103880
2 | Karnaphuli Hydro PP Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 740000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 14 |  | 17 | 17 | 17 | 17 | 17 | 8 | 8 | 253130
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 5 | 11 | 15 | 18 | 17 | 17 | 14 | 11 | 7 | 1 | [9 empty] | 115695
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 48 | 46 | 40 |  | 51 | 51 | 51 | 51 | 51 | 51 | 17 | 1183074
12 | Hathazari 100 MW peaking PP | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 64 | 64 | 68 | 73 | 73 | 73 | 73 | 73 |  | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 1316758
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 31 | 32 | 32 | 33 | 33 | 33 | 29 | 15 | 15 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 511854
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 26 | 26 | 26 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 |  | 600016
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 100 | 0 |  |  |  |  | 45 | 50 | 47 | 77 | 92 | 148 | 153 | 162 | 158 | 163 | 175 | 210 |  | 235 | 262 | 260 | 263 | 195 |  |  | 2760000
19 | Ashuganj 195 MW PP (APSCL-United) | [26 empty] | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 3433500
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 390 | 390 | 388 | 388 | 390 | 390 | 390 | 390 | 390 | 390 | 396 | 396 | 391 | 327 | 310 | 346 | 350 | 362 |  | 480 | 480 | 480 | 480 | 481 | 480 | 480 | 9687271
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [17 empty] | 54000
33 | Ashuganj 225 MW CCPP | 148 | 146 | 151 | 146 | 137 | 134 | 125 | 108 | 129 | 133 | 142 | 156 | 141 | 153 | 152 | 151 | 150 | 151 |  | 151 | 151 | 147 | 115 | 144 | 142 | 144 | 3425000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 305 | 340 | 320 | 350 | 350 | 375 | 330 | 295 | 290 | 320 | 305 | 280 | 295 | 285 | 280 | 315 |  | 305 | 325 | 330 | 305 | 305 | 345 | 305 | 8000600
| Ashuganj 420 MW CCPP(East) | [26 empty] | 0
35 | Ashuganj 55 MW PP (Precision) | [26 empty] | 0
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | [16 empty] | 0 |  |  | 20 | 20 | 25 | 36 | 94 | 156 | 171 | 507600
Meghnaghat Unique power
| Summit Meghanghat-2 589 MW(Gas) | [23 empty] | 65 | 42 |  | 78494
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 380 | 350 | 350 | 400 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 400 | 400 | 420 | 450 |  | 450 | 450 | 450 | 450 | 350 | 350 | 350 | 9572000
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 86 | 86 | 96 | 92 | 93 | 102 | 71 | 66 | 65 | 63 | 32 | 33 | 33 | 33 | 34 | 34 | 35 | 54 |  | 72 | 74 | 73 | 75 | 75 | 76 | 76 | 1476480
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 0 | 3 | 5 | 8 | 11 | 26 | 29 | 34 | 23 | 11 | 2 | [9 empty] | 157590
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1015000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 20 | 22 | 22 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 755000
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 61 | 61 | 60 | 60 | 60 | 60 | 60 | 59 | 59 | 59 | 59 | 58 | 59 | 59 | 57 | 40 | 40 | 59 |  | 60 | 59 | 60 | 59 | 58 | 58 | 60 | 1387488
48 | Shahjibazar 86 MW PP (Shahjibazar) | 86 | 86 | 86 | 86 | 86 | 86 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 81 | 84 | 81 | 82 |  | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 2008320
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 18 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 481000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 244620
54 | Hobiganj 11 MW PP Cofidence-E
55 | Fenchugonj 51 MW PP (Barakatullah) | [26 empty] | 0
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 391008
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 300 | 300 | 300 | 315 | 325 | 320 | 330 | 320 | 310 | 310 | 290 | 310 | 280 | 290 | 305 | 310 | 295 |  | 310 | 320 | 290 | 320 | 285 | 285 | 290 | 7452000
| Bibiyana South 400 MW | 300 | 300 | 300 | 280 | 280 | 250 | 250 | 245 | 260 | 281 | 330 | 400 | 400 | 360 | 400 | 400 | 400 | 380 |  | 350 | 350 | 350 | 315 | 300 | 280 | 260 | 7692900
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 5 | 17 |  | 17 | 17 | 17 |  |  |  |  | 65241
59 | Tangail Palli Power Gen 22 MW | 4 | 5 | 6 | 6 | 6 | 0 | [10 empty] | 1 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 72720
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 13 | 20 | 20 | 21 | 21 | 21 | 19 | 16 |  | 16 | 16 | 19 | 19 | 18 | 18 | 18 | 437136
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 76 | 72 | 70 | 68 | 70 | 74 | 76 | 86 | 92 | 96 | 100 | 106 | 112 | 106 | 102 | 98 | 96 | 106 |  | 108 | 108 | 106 | 104 | 100 | 98 | 96 | 2190720
64 | Malancha, Ctg. EPZ (United) | 10 | 0 | 0 | 16 | 8 | 6 | 12 | 3 | 2 | 0 | 0 | 5 | 7 | 0 | 0 | 2 | 5 | 7 |  | 7 | 18 | 15 | 23 | 12 | 10 | 10 | 218400
65 | Feni 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 366516
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 7 | 7 | 10 | 5 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 212400
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 811700
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 18 | 18 | 11 | 11 | 11 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 12 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 396280
69 | Summit Ashulia | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 432000
70 | Summit Madhabdi | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 493200
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 0 | 0 | 8 | 0 | 16 | 16 | 16 | 3 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 32 | 32 | 32 | 32 | 570100
72 | Rupganj 33 MW PP(Summit) | 13 | 13 | 13 | 13 | 13 | 15 | 15 | 15 | 15 | 14 | 14 | 14 | 14 | 14 | 21 | 21 | 21 | 21 |  | 22 | 22 | 23 | 23 | 9 | 21 | 33 | 407800
73 | Ghorashal 108 MW PP (Regent) | 70 | 70 | 70 | 68 | 70 | 70 | 70 | 70 | 70 | 67 | 67 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 915818
| Feni Lanka Power | 17 | 0 | [24 empty] | 67260
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 20 | 37 | 37 | 71 |  | 78 | 78 | 78 | 78 | 72 | 46 | 38 | 692160
| Manikgonj 162MW PP(MPGL) | [9 empty] | 17 | 35 | 35 | [5 empty] | 17 |  | 17 | 17 | 17 |  |  |  |  | 136800
77 | Siddhirganj 100 PP(Dutch Bangla) | 0 |  |  |  |  | 5 | 17 | 50 | 65 | 70 | 70 | 75 | 75 | 79 | 83 | 83 | 77 | 75 |  | 75 | 75 | 73 | 75 | 51 |  |  | 1094400
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 8 | 268320
79 | Kodda 150 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 82 | 82 | 82 | 48 | 32 | 32 | 32 | 115 |  | 130 | 149 | 149 | 149 | 16 | 16 | 9 | 1179360
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 9 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  |  | 4 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 186322
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 50 | 50 | 50 | 50 | 34 | 34 | 50 | 105 |  | 105 | 105 | 105 | 105 | 105 | 70 | 17 | 1106880
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 22684
| Jodiac Power | [8 empty] | 5 |  |  | 1 | 17 | 17 | 17 | 17 | 17 | 17 | [8 empty] | 124656
| Karnaphuli Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 7 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 414000
82 | Madanganj 102 PP(Summit) | [13 empty] | 17 | 17 | 42 | 82 | 82 |  | 82 | 82 | 82 | 82 | 82 | 36 |  | 553768
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 0 |  |  |  |  | 15 | 25 | 25 | 15 | 13 | 13 | 22 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 |  |  | 364533
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 0 |  |  |  |  | 5 | 68 | 85 | 84 | 85 | 85 | 81 | 82 | 89 | 93 | 92 | 93 | 94 |  | 94 | 51 | 53 | 11 | 9 | 8 | 0 | 1208640
| Meghnaghat 104 MW PP (OPCL) | 53 | 53 | 31 | 18 | 17 | 17 | 17 | 17 | 17 | 18 | 30 | 39 | 45 | 53 | 53 | 53 | 53 | 72 |  | 72 | 72 | 72 | 72 | 72 | 23 |  | 968640
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 25 | 0 |  |  |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 449160
92 | Fenchuganj 44 MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 1242899
94 | Gagnagar 102 MW PP (Digital Power) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 50 | 50 | 50 | 50 | 58 | 58 | 58 | 58 | 66 | 66 | 75 |  | 91 | 91 | 91 | 83 | 8 |  |  | 1056820
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 15 |  | 19 | 19 | 19 | 19 | 19 | 19 | 6 | 227040
96 | Chattogram 108 MW PP (ECPV)
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 0 | [10 empty] | 2 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 198581
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 5 | 17 |  | 35 | 17 | 17 |  |  |  |  | 68563
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 140 | 140 | 163 | 163 | 163 | 163 | 130 | 130 | 163 | 163 | 130 | 120 | 163 | 163 | 163 |  | 163 | 163 | 163 | 163 | 120 | 120 | 140 | 3869018
102 | Sarishabari 3 MW Solar Plant | [7 empty] | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [9 empty] | 2350
103 | Kamalaghat 54 MW PP(Banco Energy) | [13 empty] | 17 | 17 | 35 | [10 empty] | 64080
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 9 | 9 | 9 | 9 | 9 | 9 | 56 | 56 | 56 | 56 | 57 | 58 | 58 | 58 | 58 | 58 | 58 | 67 |  | 77 | 77 | 78 | 78 | 58 | 58 | 58 | 1125600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 37 | 36 | 36 | 36 | 36 | 36 | 36 | 43 | 53 | 55 | 73 |  | 81 | 100 | 96 | 99 | 99 | 76 | 42 | 1240416
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 624000
116 | Chandpur 200 MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 425280
117 | Ashuganj 150 MW PP (Midland) | 8 | 6 | 6 | 5 | 6 | 6 | 6 | 5 | 6 | 12 | 12 | 12 | 12 | 6 | 6 | 6 | 12 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 10 | 227490
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 28 |  | 28 | 28 | 28 | 28 | 9 | 9 | 9 | 308400
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 45 | 49 | 49 | 51 | 51 | 51 | 51 | 80 | 102 |  | 101 | 106 | 106 | 106 | 51 | 16 |  | 1036255
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 611520
| Anlima Energy Ltd. | [9 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 260945
| Bhairob 54.5 MW | [9 empty] | 12 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 272880
| Spectra Solar Plant Ltd. | [6 empty] | 0 | 3 | 7 | 10 | 15 | 20 | 23 | 19 | 12 | 6 | 2 | [9 empty] | 116096
| Chandpur 115(Doreen) | [14 empty] | 6 | 18 | 22 | 23 | [8 empty] | 79680
| Kanchan Purbachal Power Generation Ltd. | [16 empty] | 13 | 26 |  | 17 | 17 | 17 | 17 | 17 | 17 |  | 132840
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 72 | 72 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 17 | 17 | 13 | 669091
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 7 | 9 | 11 | 12 | 12 | 9 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 91680
| Matarbari 2*600 MW (CPGCL) | [9 empty] | 121 | 122 | 154 | 270 | 363 | 382 | 417 | 419 | 418 |  | 413 | 418 | 419 | 417 | 417 | 420 | 418 | 4981818
120 | Eastern Zone Total | 3617 | 3475 | 3391 | 3318 | 3303 | 3438 | 3613 | 3722 | 3726 | 3901 | 4074 | 4387 | 4602 | 4467 | 4451 | 4604 | 4741 | 5198 |  | 5391 | 5447 | 5418 | 5278 | 4786 | 4346 | 4007 | 101765234
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [9 empty] | 16 | 16 | 16 | 16 |  |  |  |  | 32 |  | 32 | 32 | 33 | 33 |  |  |  | 184320
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 22 | 0 | [8 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 20 | 37 |  | 42 | 46 | 28 | 22 | 17 |  |  | 250080
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 93 | 53 | 17 | 17 | 17 | 26 | 70 | 72 | 72 | 75 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 35 |  |  | 1681920
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 1 | 13 | 30 | 48 | 47 | 13 | 25 | 34 | 27 | 11 | 5 | [9 empty] | 303840
131 | Rampal 1320 MW (BIFPCL) | 557 | 579 | 563 | 566 | 576 | 572 | 571 | 583 | 580 | 580 | 579 | 580 | 577 | 567 | 543 | 576 | 586 | 524 |  | 462 | 538 | 599 | 536 | 600 | 580 | 558 | 13490910
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 439200
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 514489
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 0 | [16 empty] | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 |  | 113376
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 250 | 217 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 6349100
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 |  | 67 | 67 | 67 | 80 | 130 | 130 | 132 | 1782000
140 | Bhola 33 MW PP (Venture) | 17 | 16 | 16 | 15 | 14 | 16 | 16 | 16 | 16 | 12 | 12 | 12 | 19 | 16 | 14 | 14 | 14 | 19 |  | 19 | 19 | 20 | 20 | 20 | 19 | 18 | 382200
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 0 | [13 empty] | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 |  | 139125
143 | Gopalganj 100 MW Peaking PP | 22 | 0 | [14 empty] | 10 | 16 |  | 10 | 10 | 10 | 10 | 20 |  |  | 95616
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 653 | 432 | 432 | 432 | 432 | 431 | 619 | 690 | 690 | 691 | 690 | 765 | 766 | 766 | 765 | 766 | 766 | 766 |  | 671 | 672 | 671 | 765 | 764 | 765 | 747 | 15665454
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 622 | 600 | 600 | 500 | 500 | 520 | 610 | 622 | 622 | 622 | 622 | 622 | 622 | 590 | 580 | 580 | 560 | 570 |  | 622 | 622 | 622 | 622 | 622 | 622 | 560 | 15379300
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4133200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 777541
| Sirajgonj 6.55 MW Solar | [7 empty] | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | [9 empty] | 6840
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 288 | 307 | 312 | 280 | 280 | 370 | 361 | 338 | 310 | 287 | 260 | 242 | 197 | 178 | 214 | 208 | 202 | 203 |  | 210 | 217 | 218 | 237 | 251 | 268 | 286 | 6336290
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 15 | 15 | 0 | [9 empty] | 4 | 15 | 15 | 15 | 15 | 16 |  | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 183769
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 |  | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 159912
165 | Amnura 50 MW PP(Sinha) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 |  |  | 621340
166 | Katakhali 50 MW PP (Northern) | 0 |  |  |  |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 8 |  | 577952
167 | Katakhali 50 MW Peaking PP | 24 | 22 | 0 | [6 empty] | 14 | 16 | 16 | 20 | 23 | 22 | 22 | 23 | 29 |  | 39 | 40 | 40 | 42 | 42 | 42 | 32 | 429912
168 | Santahar 50 MW Peaking PP | 0 | [16 empty] | 38 |  | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 269629
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 0 |  |  | 8 | 8 | 8 | 8 | [8 empty] | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 103238
170 | Chapainawabganj 100 MW Peaking PP | 0 | [9 empty] | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 92 |  | 92 | 92 | 92 | 92 | 92 | 92 | 61 | 970704
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [16 empty] | 1 | 35 |  | 35 | 35 | 35 | 35 | 35 |  |  | 218688
172 | Confidence Power Bogura Unit-1 113 MW | [14 empty] | 20 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 |  |  | 263424
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 6 | 6 | 0 |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 33 | 33 |  | 34 | 34 | 35 | 35 | 6 | 6 | 6 | 274252
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 1 | 1 | [9 empty] | 11052
178 | Energypac Power Venture Thakurgaon Ltd. | [14 empty] | 17 | 17 | 17 | 70 |  | 70 | 35 | 35 | 35 | 35 | 35 | 17 | 337152
| Intraco Solar 30 MW | [6 empty] | 0 | 1 | 2 | 3 | 6 | 5 | 7 | 10 | 15 | 8 | 1 | [9 empty] | 59224
| Adani Power Jharkhanda Ltd | 1294 | 1118 | 1074 | 1024 | 1026 | 1125 | 1311 | 1454 | 1458 | 1408 | 1409 | 1404 | 1421 | 1381 | 1360 | 1385 | 1358 | 1471 |  | 1510 | 1426 | 1423 | 1418 | 1356 | 1307 | 1250 | 32034545
178 | Teesta Solar Limited | [7 empty] | 4 | 20 | 30 | 30 | 27 | 41 | 67 | 69 | 34 | 8 | [9 empty] | 328560