## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2024-01-23 | Tuesday
|  | Date (day): | 2024-01-23 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10376.6 | MW |  |  | (b) At Evening Peak Hour : |  | 11008 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-01-22 | 2024-01-23 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 12 | 15 | 93 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 418 | 408 | 412 | 412
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 76 | 79 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 80 | 82 | 82 | 82 |  | 20 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 30 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 13 | 25 | 30 | 30 | 45 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 84 | 92 | 92 | 92 |  | 8 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 23 | 335 | 335 | 0
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 50 | 91 | 70 | 90 |  | 12 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 17 | 0 | 54 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 98 | 48 | 98 | 51 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 0 | 0 | 17 | 38 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 33 | 18 | 40 | 40 |  | 40 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 30 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 17 | 8 | 17 | 35 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 80 | 130 | 80 | 130 | 170 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 82 | 36 | 50 | 35 | 114 |  | Fuel shortage
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 105 | 17 | 105
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 54 | 54 | 35 | 72 | 32 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 17 | 17 | 17 | 145 |  | Fuel shortage
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 18 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 415 | 34 | 0 | 0 |  |  | on test
| Dhaka area Total |  |  |  |  | 5763 | 5062 | 2219 | 2081 | 2188 | 2432 | 1594 | 1020
38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
39 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 17 | 8 | 17 | 8 |  | Fuel shortage
40 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 19 | 6 | 19 | 31 |  | Fuel shortage
42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 76 | 76 | 76 | 76 | 154 |  | Low water lavel
43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 17 | 17 | 88 |  | Fuel shortage
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 48 | 64 | 60 | 64 | 34 |  | Fuel shortage
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 51 | 51 | 51 | 51 | 51 |  | Fuel shortage
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 35 | 25 | 25 | 25 | 75 |  | Fuel shortage
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 15 | 18 | 18
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 1 | 12 | 5 | 10
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 13 | 0 | 0 | 108 |  | Fuel shortage
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 49 | 104 | 50 | 105 | 195 |  | Fuel shortage
54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 0 | 0 | 0 | 54 |  | Fuel shortage
55 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 17 | 17 | 93 |  | Fuel shortage
56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
57 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 17 | 99 |  | Fuel shortage
58 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 17 | 17 | 17 | 17 | 146 |  | Fuel shortage
59 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 290 | 352 | 400 | 480 | 744 |  | Coal Shortage.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 4 | 1 | 10 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 419 | 419 | 415 | 420 |  |  | On test.
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4404 | 4344 | 1166 | 1286 | 1267 | 1413 | 2435 | 330
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 157 | 159 | 160 | 160 |  | 61 | ST Under maint.
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 360 | 320 | 330 |  |  | FGMO
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Under maint
63 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 | 400 |  | Gas shortage
64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 9 | 45 | 50 | 45 | 0
65 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 0 | 30 | 45 | 45 | 10
66 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 8 | 140 | 140 | 55 |  | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
68 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 10 | 13 | 6 | 20 | 130 |  | Fuel shortage
69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 18 | 25 | 25 | 25 |  | 27 | Engine problem
70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
71 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 17 | 17 | 17 | 183 |  | Fuel shortage
72 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 13 | 16 | 13 | 13 |  | 9 | Engine problem
73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 120 | 106 | 128 | 141
74 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 18 | 11 | 18 |  | 7 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 0 | 114 |  | Fuel shortage
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 79 | 9 | 78 | 35 |  | Fuel shortage
79 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
80 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 18 | 0 | 17 | 98 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2951 | 848 | 1011 | 1043 | 1168 | 1429 | 304
81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 33 | 36 | 35 | 60 | 142 |  | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 67 | 68 | 56 | 68 | 132 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 9 | 9 | 106 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 13 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 2 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 123 | 119 | 153.6 | 143 | 142 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 110 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 61 | 60 | 60
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 78 | 84 | 84
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 |  | 231 | Under maint.
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 20 | 20 | 20
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 16 | 16 | 16 | 9 |  | Gas shortage
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 300 | 310 | 310 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 390 | 320 | 250 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1090 | 1041 | 933 | 1136 | 110 | 1148
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 687 | 653 | 780 | 780
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 32 | 16 | 33 | 82 |  | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 12 | 34 | 15 | 40 |  | 14 | Engine problem
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 20 | 20 |  | 89 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 0 | 16 | 24 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 93 | 93 | 93 | 93 |  | 12 | Engine problem
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 39 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 588 | 579 | 0 | 0 |  |  | Unit-2 test
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 1435 | 1399 | 1024 | 982 | 1203 | 115
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 16 | 16
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 16 | 19 | 20 | 20 |  | 20 | Engine problem
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 67 | 135 | 135 | 135 |  | 59 | GT-2 & ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 622 | 610 | 622 | 622 |  | 622 | #01 Under maint.
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 54 | 17 | 54 | 96 |  | Fuel shortage
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 250 | 250 | 250 | 250 | 57 |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1192 | 1304 | 1280 | 1317 | 153 | 701
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 32 | 32 | 32 | 20 |  | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 15 | 0 | 16 |  | 55 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 28 | 21 | 28 | 28
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 25 | 42 | 34 | 42 |  | 8 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 24 | 40 | 40 |  | 10 | Engine problem
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 275 | 286 | 400 | 400 | 14
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 25 | 38 | 25 | 38 | 12 |  | Engine problem
136 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 8 | 44 |  | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 50 | 92 | 90 | 92 |  | 12 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 0 | 35 | 78 |  | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 0 | 35 | 78 |  | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 1 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1180 | 1407 | 1400 | 1400
| Rajshahi Area Total |  |  |  |  | 3653 | 3631 | 1589 | 2043 | 2074 | 2177 | 1267 | 85
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 6 | 34 | 6 | 35 | 78 |  | Fuel shortage
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 70 | 70 | 35 | 80 |  | Fuel shortage
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 13 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 62 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 256 | 274 | 414 | 240 | 283 | 189
| Total |  |  |  |  | 26504 | 25481 | 9918 | 10558 | 10376.6 | 11008 | 8616 | 3892
A. |  | 2024-01-22 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 10558 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 6937 | MW at | 4:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10616 | MW
3 | Day peak Generation : |  |  | 9918 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10075.85 | MW
4 | Evening peak Generation : |  |  | 10558 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 55 | MW
5 | Total Energy Generation : |  | 214.9725 | MKWHr | By Solar | 1.3845 | MKWHr
| By Gas : | 85.4879 | MKWHr |  | By Oil: | 24.3882 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 83.79 | MKWHr |  | By Hydro: | 1.8128 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.13872 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 8616 | MW | Dhaka | 3702.25 | 3702.25 |  | 0 |  | 18:00 |  | 75
|  |  | For Plants S/D or M/C prob = |  |  | 3892 | MW | Chittagong | 975.5 | 975.5 |  | 0 |  | 19:00 |  | 55
|  |  | Total = |  |  | 12508 | MW | Khulna | 1204.3 | 1204.3 |  | 0 |  | 19:30 |  | 34
7 | Total Gas Supplied : |  |  | 707.69 | MMCFD |  |  | Rajshahi | 1057.8 | 1057.8 |  | 0 |  | 20:00 |  | 29
8 | Fuel Cost : | i) Gas : | Taka | 256811961.966 | ii) Oil : | Taka | 438389216.61 | Comilla | 845 | 845 |  | 0 |  | 21:00 |  | 15
|  | iii) Coal : | Taka | 516382822.39 | Total | Taka | 1211584000.966 | Mymensingh | 883 | 828 |  | 55 |  | 22:00 |  | 50
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 366 | 366 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 780 | MW (W to E) at | 19:00 | hrs | Barisal | 297 | 297 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 680 | MW at | 8:00 | hrs | Rangpur | 745 | 745 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 17.4°C |  |  | Total | 10075.85 | 10020.85 |  | 55
B. |  | 2024-01-23 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 17.4°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 11008 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10000 | MW
4 | Reserve(Generation end) |  |  |  | 408 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 215.8277 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6763 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 15.5636 | MKWHr. | ii) HVDC Flow at Peak Time |  | 653 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.4067 | MKWHr. | iii) Maximum HVDC Flow : |  | 775 | MW at | 15:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 89.44 |  | (b) Today: | 89.32 |  | (c) Rule Curve: |  | 98.8
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-01-22 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 402 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 25 | 33 | 0 | 0 | 46 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 18 | 12 | 0 | 0 | 0 | 280 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 13 | 8 | 33 | 16 | 96 | 75 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 140 | 0 | 60 | 79 | 0 | 0 | 20 | 0 | 10 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 25 | 17 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 13 | 25 | 245 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 4 | 422 | 0 | 0 |  | 572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 299 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 550 | 180 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 548 | 0 | 200 | 1210 | 0 | 0 |  | 3843 | 3906 | 7749 | 1823 | 572 | 1440 | 0 | 158 | 3580 | 76 | 0 | 0 | 96 | 0 | 4 | 0 | 89.46
2:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 405 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 0 | 33 | 0 | 0 | 46 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 0 | 0 | 0 | 280 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 13 | 8 | 33 | 16 | 84 | 75 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 140 | 0 | 60 | 79 | 0 | 0 | 20 | 0 | 10 | 295 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 7 | 419 | 0 | 0 |  | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 568 | 0 | 178 | 1097 | 0 | 0 |  | 3694 | 3646 | 7340 | 1809 | 432 | 1470 | 0 | 0 | 3462 | 76 | 0 | 0 | 84 | 0 | 7 | 0 | 89.46
3:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 403 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 30 | 33 | 0 | 0 | 46 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 32 | 0 | 0 | 0 | 280 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 13 | 8 | 33 | 16 | 88 | 75 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 140 | 0 | 60 | 79 | 0 | 0 | 20 | 0 | 10 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 8 | 419 | 0 | 0 |  | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 522 | 0 | 150 | 997 | 0 | 0 |  | 3702 | 3453 | 7155 | 1834 | 432 | 1499 | 0 | 0 | 3218 | 76 | 0 | 0 | 88 | 0 | 8 | 0 | 89.45
4:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 401 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 30 | 33 | 0 | 0 | 46 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 40 | 0 | 0 | 0 | 290 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 13 | 8 | 33 | 13 | 82 | 75 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 120 | 0 | 40 | 50 | 0 | 0 | 20 | 0 | 10 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 9 | 420 | 0 | 85 |  | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 516 | 0 | 150 | 908 | 0 | 0 |  | 3676 | 3261 | 6937 | 1781 | 432 | 1503 | 0 | 0 | 3054 | 76 | 0 | 0 | 82 | 0 | 9 | 0 | 89.45
5:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 401 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 30 | 33 | 0 | 0 | 46 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 40 | 0 | 0 | 0 | 285 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 13 | 8 | 33 | 13 | 82 | 85 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 120 | 0 | 40 | 50 | 0 | 0 | 20 | 0 | 10 | 295 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 14 | 418 | 0 | 115 |  | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 528 | 0 | 150 | 911 | 0 | 0 |  | 3677 | 3265 | 6942 | 1754 | 432 | 1537 | 0 | 0 | 3047 | 76 | 0 | 0 | 82 | 0 | 14 | 0 | 89.44
6:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 402 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 30 | 33 | 0 | 0 | 46 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 35 | 0 | 0 | 0 | 365 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 13 | 8 | 33 | 13 | 90 | 85 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 163 | 0 | 60 | 79 | 0 | 0 | 20 | 0 | 10 | 300 | 16 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 19 | 419 | 0 | 150 |  | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530 | 0 | 150 | 915 | 0 | 0 |  | 3948 | 3363 | 7311 | 1849 | 432 | 1786 | 0 | 5 | 3054 | 76 | 0 | 0 | 90 | 0 | 19 | 0 | 89.44
7:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 402 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 30 | 33 | 2 | 0 | 46 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 4 | 14 | 30 | 0 | 0 | 0 | 335 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 13 | 8 | 33 | 13 | 90 | 74 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 163 | 0 | 61 | 79 | 0 | 0 | 20 | 0 | 10 | 300 | 16 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 1 | 25 | 0 | 5 | 0 | 9 | 2 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 25 | 200 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 14 | 417 | 0 | 230 |  | 620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 600 | 180 | 0 | 7 | 0 | 2 | 0 | 0 | 0 | 524 | 0 | 245 | 1128 | 0 | 0 |  | 4144 | 3948 | 8092 | 1772 | 620 | 1851 | 0 | 165 | 3484 | 76 | 0 | 17 | 90 | 3 | 14 | 0 | 89.43
8:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 403 | 0 |  | 0 | 450 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 8 | 24 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 33 | 33 | 8 | 0 | 46 | 30 | 0 | 0 | 6 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 25 | 0 | 6 | 14 | 10 | 0 | 0 | 0 | 350 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 1 | 13 | 8 | 33 | 13 | 94 | 68 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 163 | 0 | 60 | 79 | 0 | 0 | 20 | 0 | 10 | 330 | 16 | 0 | 0 | 3 | 0 | 0 | 56 | 0 | 17 | 5 | 25 | 16 | 6 | 0 | 9 | 17 | 15 | 1 | 16 | 0 | 17 | 0 | 9 | 25 | 200 | 17 | 3 | 0 | 17 | 0 | 0 | 1 | 0 | 0 | 0 | 17 | 0 | 400 | 12 | 420 | 0 | 217 |  | 664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 7 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 622 | 220 | 0 | 17 | 0 | 13 | 0 | 0 | 0 | 571 | 1 | 250 | 1302 | 8 | 0 |  | 4407 | 4341 | 8748 | 1757 | 664 | 1918 | 0 | 427 | 3735 | 76 | 0 | 33 | 94 | 32 | 12 | 0 | 89.43
9:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 402 | 0 |  | 0 | 450 | 0 | 10 | 62 | 0 | 0 | 0 | 0 | 65 | 50 | 16 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 33 | 33 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 56 | 2 | 25 | 0 | 6 | 14 | 2 | 0 | 0 | 0 | 280 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 13 | 8 | 30 | 13 | 92 | 68 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 163 | 0 | 60 | 79 | 0 | 0 | 20 | 0 | 10 | 310 | 16 | 0 | 0 | 57 | 0 | 0 | 56 | 0 | 61 | 10 | 25 | 17 | 5 | 0 | 9 | 17 | 17 | 2 | 16 | 4 | 17 | 0 | 9 | 25 | 230 | 52 | 3 | 0 | 17 | 0 | 9 | 8 | 0 | 0 | 0 | 17 | 0 | 415 | 5 | 419 | 0 | 217 |  | 662 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 22 | 0 | 0 | 0 | 6 | 0 | 1 | 0 | 622 | 220 | 0 | 17 | 0 | 24 | 0 | 0 | 0 | 588 | 2 | 250 | 1307 | 25 | 0 |  | 4734 | 4375 | 9109 | 1723 | 662 | 1856 | 0 | 758 | 3771 | 76 | 0 | 91 | 92 | 75 | 5 | 278 | 89.42
10:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 413 | 0 |  | 0 | 450 | 0 | 37 | 80 | 0 | 0 | 0 | 0 | 80 | 50 | 16 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 33 | 33 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 57 | 51 | 25 | 0 | 6 | 18 | 1 | 0 | 0 | 0 | 300 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 13 | 8 | 33 | 15 | 112 | 33 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 120 | 0 | 60 | 79 | 0 | 0 | 18 | 0 | 10 | 275 | 16 | 0 | 0 | 81 | 0 | 0 | 58 | 0 | 75 | 15 | 25 | 17 | 6 | 0 | 9 | 17 | 17 | 2 | 32 | 17 | 17 | 0 | 9 | 25 | 250 | 54 | 8 | 17 | 17 | 0 | 17 | 9 | 0 | 0 | 0 | 17 | 0 | 373 | 3 | 418 | 0 | 258 |  | 662 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 25 | 0 | 8 | 25 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 65 | 0 | 0 | 0 | 6 | 0 | 1 | 0 | 622 | 190 | 0 | 17 | 0 | 28 | 0 | 0 | 0 | 591 | 4 | 250 | 1237 | 35 | 0 |  | 4913 | 4347 | 9260 | 1747 | 662 | 1741 | 0 | 990 | 3661 | 76 | 0 | 166 | 112 | 102 | 3 | 181.45 | 89.42
11:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 428 | 0 |  | 0 | 450 | 0 | 70 | 80 | 0 | 0 | 0 | 0 | 84 | 50 | 16 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 33 | 33 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 48 | 51 | 25 | 0 | 6 | 18 | 1 | 0 | 0 | 0 | 280 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 13 | 8 | 33 | 18 | 104 | 33 | 0 | 0 | 1 | 43 | 30 | 0 | 0 | 120 | 0 | 60 | 79 | 0 | 0 | 18 | 0 | 10 | 300 | 0 | 0 | 0 | 81 | 0 | 0 | 67 | 0 | 82 | 17 | 25 | 17 | 6 | 0 | 9 | 17 | 17 | 4 | 49 | 17 | 17 | 0 | 9 | 25 | 320 | 54 | 11 | 17 | 17 | 0 | 17 | 9 | 0 | 0 | 0 | 17 | 0 | 338 | 4 | 419 | 0 | 413 |  | 663 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 9 | 0 | 0 | 67 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 28 | 34 | 0 | 0 | 25 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 283 | 93 | 0 | 0 | 0 | 6 | 0 | 5 | 0 | 622 | 220 | 0 | 17 | 0 | 42 | 0 | 0 | 0 | 542 | 7 | 250 | 1216 | 60 | 0 |  | 5142 | 4446 | 9588 | 1798 | 663 | 1955 | 0 | 1089 | 3557 | 46 | 0 | 216 | 104 | 156 | 4 | 154.71 | 89.41
12:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 418 | 0 |  | 0 | 450 | 0 | 76 | 80 | 15 | 0 | 0 | 0 | 84 | 50 | 16 | 13 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 18 | 15 | 33 | 33 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 48 | 51 | 35 | 0 | 6 | 20 | 1 | 0 | 0 | 0 | 360 | 0 | 157 | 0 | 0 | 9 | 0 | 0 | 51 | 0 | 18 | 8 | 13 | 8 | 33 | 18 | 120 | 33 | 0 | 0 | 1 | 43 | 30 | 0 | 0 | 163 | 0 | 59 | 79 | 0 | 0 | 18 | 0 | 10 | 290 | 8 | 0 | 0 | 80 | 0 | 0 | 67 | 0 | 82 | 20 | 25 | 17 | 10 | 0 | 9 | 17 | 17 | 4 | 49 | 17 | 17 | 0 | 9 | 25 | 390 | 54 | 13 | 35 | 17 | 0 | 17 | 18 | 0 | 0 | 0 | 17 | 0 | 290 | 4 | 419 | 0 | 415 |  | 687 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 12 | 0 | 0 | 67 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 28 | 25 | 0 | 0 | 25 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 93 | 0 | 0 | 0 | 6 | 0 | 5 | 0 | 622 | 220 | 0 | 17 | 1 | 39 | 0 | 0 | 0 | 588 | 13 | 250 | 1180 | 62 | 0 |  | 5446 | 4472 | 9918 | 1968 | 687 | 1982 | 0 | 1149 | 3519 | 76 | 0 | 237 | 120 | 176 | 4 | 78 | 89.41
13:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 421 | 0 |  | 0 | 450 | 0 | 69 | 80 | 15 | 0 | 0 | 0 | 84 | 66 | 16 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 33 | 33 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 48 | 51 | 25 | 0 | 6 | 21 | 2 | 0 | 0 | 0 | 290 | 0 | 157 | 0 | 0 | 30 | 0 | 0 | 51 | 0 | 25 | 8 | 15 | 8 | 33 | 18 | 120 | 32 | 0 | 0 | 1 | 43 | 30 | 0 | 0 | 163 | 0 | 60 | 79 | 0 | 0 | 18 | 0 | 10 | 295 | 8 | 0 | 0 | 81 | 0 | 0 | 58 | 0 | 82 | 19 | 25 | 17 | 6 | 0 | 9 | 17 | 17 | 3 | 51 | 17 | 17 | 0 | 9 | 25 | 400 | 62 | 24 | 0 | 17 | 0 | 17 | 16 | 0 | 0 | 0 | 17 | 0 | 313 | 2 | 418 | 0 | 404 |  | 766 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 11 | 0 | 0 | 70 | 17 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 28 | 25 | 0 | 0 | 25 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259 | 93 | 0 | 0 | 0 | 6 | 0 | 5 | 0 | 622 | 220 | 0 | 17 | 3 | 70 | 0 | 0 | 0 | 585 | 27 | 250 | 1259 | 103 | 0 |  | 5387 | 4706 | 10093 | 1938 | 766 | 1962 | 0 | 1094 | 3617 | 76 | 0 | 247 | 120 | 271 | 2 | 45 | 89.4
14:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 421 | 0 |  | 0 | 450 | 0 | 68 | 80 | 15 | 0 | 0 | 0 | 86 | 66 | 16 | 13 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 18 | 15 | 33 | 33 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 5 | 48 | 51 | 25 | 0 | 6 | 19 | 2 | 0 | 0 | 0 | 280 | 0 | 158 | 0 | 0 | 30 | 0 | 0 | 51 | 0 | 25 | 8 | 13 | 8 | 33 | 18 | 116 | 31 | 0 | 0 | 1 | 43 | 30 | 0 | 0 | 120 | 0 | 60 | 78 | 0 | 0 | 18 | 0 | 10 | 280 | 8 | 0 | 0 | 80 | 0 | 0 | 58 | 0 | 82 | 17 | 25 | 17 | 6 | 0 | 9 | 17 | 17 | 3 | 51 | 17 | 17 | 0 | 9 | 25 | 400 | 71 | 30 | 0 | 17 | 0 | 17 | 21 | 0 | 0 | 0 | 17 | 0 | 325 | 6 | 416 | 0 | 45 |  | 774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 28 | 34 | 0 | 0 | 25 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254 | 93 | 0 | 0 | 0 | 6 | 0 | 5 | 0 | 580 | 220 | 0 | 17 | 2 | 66 | 0 | 0 | 0 | 582 | 23 | 250 | 1272 | 74 | 0 |  | 5005 | 4626 | 9631 | 1924 | 774 | 1538 | 0 | 1118 | 3595 | 76 | 0 | 242 | 116 | 242 | 6 | 37 | 89.41
15:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 422 | 0 |  | 0 | 450 | 0 | 67 | 82 | 15 | 0 | 0 | 0 | 88 | 66 | 16 | 13 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 18 | 15 | 33 | 33 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 6 | 40 | 51 | 25 | 0 | 6 | 21 | 2 | 0 | 0 | 0 | 280 | 0 | 156 | 0 | 0 | 44 | 0 | 0 | 51 | 0 | 25 | 8 | 13 | 8 | 33 | 18 | 116 | 33 | 0 | 0 | 1 | 43 | 30 | 0 | 0 | 120 | 4 | 59 | 78 | 0 | 0 | 18 | 0 | 10 | 290 | 8 | 0 | 0 | 80 | 0 | 0 | 58 | 0 | 37 | 12 | 25 | 17 | 5 | 0 | 9 | 17 | 17 | 2 | 51 | 17 | 17 | 0 | 19 | 25 | 400 | 71 | 22 | 0 | 17 | 0 | 17 | 18 | 0 | 0 | 0 | 17 | 0 | 289 | 4 | 416 | 0 | 0 |  | 775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 70 | 13 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 28 | 34 | 0 | 0 | 25 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 93 | 0 | 0 | 0 | 6 | 0 | 4 | 8 | 500 | 220 | 0 | 17 | 2 | 47 | 0 | 0 | 0 | 546 | 15 | 200 | 1268 | 70 | 0 |  | 4912 | 4427 | 9339 | 1944 | 775 | 1494 | 0 | 1111 | 3389 | 76 | 0 | 237 | 116 | 193 | 4 | 30 | 89.39
16:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 414 | 0 |  | 0 | 450 | 0 | 19 | 82 | 15 | 9 | 0 | 0 | 81 | 50 | 32 | 13 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 18 | 15 | 33 | 33 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 6 | 40 | 51 | 25 | 7 | 6 | 21 | 4 | 0 | 0 | 0 | 280 | 0 | 157 | 8 | 0 | 41 | 3 | 0 | 51 | 0 | 25 | 8 | 13 | 8 | 33 | 18 | 104 | 36 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 163 | 0 | 40 | 78 | 0 | 0 | 18 | 0 | 10 | 290 | 8 | 0 | 0 | 80 | 0 | 0 | 58 | 0 | 36 | 7 | 25 | 17 | 6 | 0 | 9 | 17 | 17 | 1 | 51 | 0 | 17 | 0 | 37 | 25 | 400 | 71 | 10 | 0 | 17 | 0 | 17 | 10 | 0 | 0 | 0 | 17 | 0 | 278 | 4 | 418 | 0 | 60 |  | 765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 135 | 13 | 0 | 0 | 0 | 0 | 0 | 15 | 50 | 14 | 16 | 0 | 0 | 25 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241 | 70 | 0 | 0 | 0 | 6 | 0 | 2 | 35 | 460 | 180 | 0 | 17 | 1 | 25 | 17 | 0 | 0 | 484 | 9 | 150 | 1212 | 44 | 0 |  | 4912 | 4176 | 9088 | 1988 | 765 | 1563 | 0 | 1037 | 3172 | 76 | 0 | 270 | 104 | 109 | 4 | 0 | 89.39
17:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 354 | 0 |  | 0 | 370 | 0 | 6 | 82 | 15 | 10 | 0 | 0 | 60 | 50 | 42 | 15 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 18 | 15 | 33 | 33 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 6 | 40 | 51 | 25 | 12 | 9 | 21 | 13 | 0 | 0 | 0 | 280 | 0 | 155 | 8 | 0 | 42 | 17 | 0 | 51 | 0 | 17 | 8 | 15 | 8 | 33 | 18 | 100 | 36 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 163 | 0 | 40 | 78 | 0 | 0 | 18 | 0 | 10 | 310 | 8 | 0 | 0 | 80 | 0 | 0 | 58 | 0 | 36 | 1 | 25 | 26 | 8 | 0 | 9 | 17 | 17 | 0 | 102 | 0 | 17 | 0 | 37 | 25 | 400 | 55 | 2 | 0 | 17 | 0 | 17 | 2 | 0 | 14 | 0 | 17 | 0 | 279 | 4 | 418 | 0 | 67 |  | 766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 8 | 135 | 14 | 0 | 0 | 0 | 0 | 0 | 15 | 50 | 14 | 34 | 3 | 0 | 25 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257 | 93 | 0 | 1 | 0 | 28 | 0 | 0 | 35 | 460 | 180 | 0 | 17 | 0 | 7 | 17 | 0 | 0 | 492 | 2 | 183 | 1204 | 7 | 0 |  | 4807 | 4260 | 9067 | 1930 | 766 | 1550 | 0 | 1116 | 3206 | 76 | 0 | 298 | 100 | 21 | 4 | 0 | 89.38
18:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 352 | 0 |  | 0 | 450 | 0 | 46 | 82 | 15 | 10 | 0 | 0 | 65 | 91 | 98 | 25 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 18 | 0 | 33 | 33 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 6 | 50 | 51 | 25 | 13 | 19 | 15 | 8 | 0 | 0 | 0 | 300 | 0 | 154 | 8 | 0 | 45 | 20 | 0 | 51 | 0 | 21 | 8 | 16 | 8 | 33 | 18 | 110 | 36 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 120 | 0 | 59 | 78 | 0 | 0 | 20 | 0 | 10 | 290 | 16 | 0 | 0 | 130 | 0 | 0 | 68 | 0 | 36 | 0 | 25 | 17 | 12 | 0 | 9 | 105 | 17 | 0 | 103 | 0 | 17 | 0 | 68 | 25 | 330 | 53 | 0 | 17 | 17 | 0 | 17 | 0 | 13 | 17 | 0 | 17 | 0 | 281 | 4 | 420 | 0 | 74 |  | 766 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 46 | 0 | 8 | 135 | 18 | 16 | 0 | 0 | 0 | 0 | 15 | 92 | 28 | 42 | 16 | 8 | 38 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 93 | 0 | 30 | 0 | 33 | 0 | 0 | 35 | 480 | 220 | 0 | 54 | 0 | 0 | 70 | 0 | 0 | 501 | 0 | 250 | 1363 | 0 | 0 |  | 5192 | 4847 | 10039 | 1892 | 766 | 1639 | 0 | 1643 | 3465 | 76 | 0 | 444 | 110 | 0 | 4 | 75 | 89.38
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 408 | 0 |  | 0 | 450 | 0 | 79 | 82 | 30 | 23 | 0 | 0 | 92 | 91 | 98 | 25 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 18 | 0 | 33 | 33 | 17 | 0 | 46 | 30 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 6 | 64 | 51 | 25 | 13 | 19 | 15 | 12 | 0 | 0 | 0 | 360 | 0 | 159 | 8 | 0 | 45 | 30 | 0 | 51 | 0 | 25 | 8 | 16 | 8 | 33 | 18 | 106 | 36 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 163 | 0 | 61 | 78 | 0 | 0 | 20 | 0 | 10 | 300 | 16 | 0 | 0 | 130 | 0 | 0 | 68 | 0 | 36 | 0 | 25 | 17 | 13 | 0 | 9 | 105 | 17 | 0 | 104 | 0 | 17 | 0 | 79 | 25 | 320 | 54 | 0 | 17 | 17 | 0 | 17 | 0 | 18 | 17 | 0 | 17 | 0 | 352 | 1 | 419 | 0 | 34 |  | 653 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 34 | 0 | 8 | 135 | 19 | 16 | 0 | 0 | 0 | 32 | 15 | 92 | 21 | 42 | 24 | 8 | 38 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 286 | 93 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 610 | 220 | 0 | 54 | 0 | 0 | 70 | 0 | 0 | 579 | 0 | 250 | 1407 | 0 | 0 |  | 5538 | 5020 | 10558 | 2018 | 653 | 1673 | 0 | 1754 | 3787 | 76 | 0 | 490 | 106 | 0 | 1 | 55 | 89.36
19:30 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 403 | 0 |  | 0 | 450 | 0 | 51 | 82 | 15 | 49 | 0 | 0 | 92 | 91 | 98 | 25 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 18 | 20 | 33 | 33 | 17 | 0 | 46 | 30 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 6 | 64 | 51 | 25 | 12 | 19 | 15 | 12 | 0 | 0 | 0 | 310 | 0 | 158 | 8 | 0 | 45 | 38 | 0 | 51 | 0 | 25 | 8 | 16 | 8 | 33 | 18 | 108 | 43 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 120 | 0 | 61 | 78 | 0 | 0 | 20 | 0 | 10 | 295 | 16 | 0 | 0 | 130 | 0 | 0 | 68 | 0 | 36 | 0 | 25 | 17 | 13 | 0 | 9 | 70 | 17 | 0 | 105 | 0 | 17 | 0 | 79 | 25 | 300 | 54 | 0 | 17 | 17 | 0 | 17 | 0 | 36 | 17 | 0 | 17 | 0 | 390 | 1 | 418 | 0 | 63 |  | 653 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 28 | 0 | 8 | 135 | 20 | 16 | 0 | 0 | 0 | 34 | 15 | 92 | 0 | 42 | 32 | 8 | 38 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 287 | 93 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 622 | 220 | 0 | 54 | 0 | 0 | 70 | 0 | 0 | 601 | 0 | 250 | 1418 | 0 | 0 |  | 5483 | 5036 | 10519 | 1995 | 653 | 1664 | 0 | 1659 | 3869 | 76 | 0 | 494 | 108 | 0 | 1 | 34 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 405 | 0 |  | 0 | 450 | 0 | 60 | 82 | 15 | 52 | 0 | 0 | 89 | 91 | 98 | 25 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 18 | 22 | 33 | 33 | 17 | 0 | 46 | 30 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 6 | 64 | 51 | 25 | 13 | 19 | 15 | 14 | 0 | 0 | 0 | 310 | 0 | 157 | 8 | 0 | 45 | 37 | 0 | 51 | 0 | 25 | 8 | 16 | 8 | 33 | 18 | 108 | 59 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 120 | 0 | 60 | 78 | 0 | 0 | 20 | 0 | 10 | 280 | 16 | 0 | 0 | 130 | 0 | 0 | 68 | 0 | 36 | 0 | 25 | 17 | 15 | 0 | 9 | 70 | 17 | 0 | 104 | 0 | 17 | 0 | 79 | 25 | 300 | 54 | 0 | 17 | 17 | 0 | 17 | 0 | 31 | 17 | 0 | 17 | 0 | 374 | 0 | 418 | 0 | 66 |  | 653 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 23 | 3 | 8 | 135 | 20 | 16 | 0 | 0 | 0 | 34 | 15 | 92 | 0 | 42 | 32 | 8 | 38 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 288 | 93 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 622 | 220 | 0 | 54 | 0 | 0 | 70 | 0 | 0 | 621 | 0 | 250 | 1393 | 0 | 0 |  | 5479 | 5031 | 10510 | 2016 | 653 | 1654 | 0 | 1663 | 3848 | 76 | 0 | 492 | 108 | 0 | 0 | 29 | 89.37
21:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 402 | 0 |  | 0 | 450 | 0 | 8 | 82 | 15 | 105 | 0 | 0 | 14 | 91 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 33 | 33 | 17 | 0 | 46 | 30 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 6 | 64 | 51 | 25 | 13 | 19 | 15 | 16 | 0 | 0 | 0 | 310 | 0 | 158 | 8 | 0 | 45 | 40 | 0 | 51 | 0 | 25 | 8 | 16 | 8 | 33 | 18 | 106 | 76 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 163 | 0 | 60 | 78 | 0 | 0 | 20 | 0 | 10 | 310 | 16 | 0 | 0 | 130 | 0 | 0 | 68 | 0 | 23 | 0 | 25 | 17 | 15 | 0 | 9 | 70 | 17 | 0 | 106 | 0 | 17 | 0 | 79 | 25 | 300 | 54 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 290 | 0 | 418 | 0 | 65 |  | 653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 21 | 8 | 135 | 19 | 16 | 0 | 0 | 0 | 34 | 15 | 92 | 0 | 34 | 24 | 8 | 38 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 93 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 622 | 220 | 0 | 17 | 0 | 0 | 70 | 0 | 0 | 495 | 0 | 250 | 1374 | 0 | 0 |  | 5325 | 4861 | 10186 | 2084 | 653 | 1761 | 0 | 1396 | 3619 | 76 | 0 | 491 | 106 | 0 | 0 | 15 | 89.36
22:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 401 | 0 |  | 0 | 450 | 0 | 31 | 82 | 15 | 120 | 0 | 0 | 32 | 91 | 32 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 30 | 33 | 17 | 0 | 46 | 30 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 6 | 64 | 51 | 25 | 0 | 19 | 14 | 8 | 0 | 0 | 0 | 290 | 0 | 160 | 8 | 0 | 45 | 40 | 0 | 51 | 0 | 25 | 8 | 16 | 8 | 0 | 18 | 100 | 77 | 0 | 0 | 0 | 42 | 30 | 0 | 0 | 163 | 0 | 51 | 78 | 0 | 0 | 20 | 0 | 10 | 295 | 16 | 0 | 0 | 130 | 0 | 0 | 9 | 0 | 19 | 0 | 25 | 17 | 15 | 0 | 9 | 70 | 17 | 0 | 106 | 0 | 17 | 0 | 71 | 25 | 300 | 52 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 290 | 1 | 408 | 0 | 62 |  | 766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 24 | 8 | 135 | 21 | 16 | 0 | 0 | 0 | 34 | 15 | 92 | 0 | 34 | 24 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 93 | 0 | 35 | 0 | 27 | 0 | 0 | 35 | 600 | 220 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 250 | 1357 | 0 | 0 |  | 5133 | 4358 | 9491 | 2034 | 766 | 1748 | 0 | 1291 | 3075 | 76 | 0 | 400 | 100 | 0 | 1 | 50 | 89.36
23:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 365 | 0 |  | 0 | 450 | 0 | 55 | 38 | 15 | 150 | 0 | 0 | 80 | 16 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 30 | 33 | 17 | 0 | 46 | 30 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 6 | 64 | 51 | 25 | 0 | 19 | 10 | 15 | 0 | 0 | 0 | 290 | 0 | 123 | 8 | 0 | 45 | 40 | 0 | 51 | 0 | 25 | 8 | 16 | 8 | 0 | 18 | 98 | 75 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 120 | 0 | 63 | 78 | 0 | 0 | 20 | 0 | 10 | 290 | 16 | 0 | 0 | 80 | 0 | 0 | 9 | 0 | 17 | 0 | 24 | 17 | 20 | 0 | 9 | 35 | 17 | 0 | 52 | 0 | 17 | 0 | 49 | 25 | 275 | 37 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 280 | 6 | 420 | 0 | 65 |  | 766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 24 | 8 | 135 | 19 | 16 | 0 | 0 | 0 | 34 | 15 | 92 | 0 | 0 | 24 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 17 | 0 | 35 | 0 | 6 | 0 | 0 | 0 | 550 | 220 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 250 | 1417 | 0 | 0 |  | 4793 | 4221 | 9014 | 1970 | 766 | 1731 | 0 | 879 | 3087 | 76 | 0 | 401 | 98 | 0 | 6 | 0 | 89.35
24:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 353 | 0 |  | 0 | 450 | 0 | 0 | 6 | 15 | 332 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 30 | 33 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 6 | 10 | 15 | 0 | 0 | 0 | 295 | 0 | 159 | 8 | 0 | 45 | 40 | 0 | 51 | 0 | 0 | 8 | 16 | 8 | 0 | 15 | 94 | 75 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 120 | 0 | 62 | 78 | 0 | 0 | 20 | 0 | 10 | 300 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 17 | 20 | 0 | 9 | 17 | 17 | 0 | 5 | 0 | 17 | 0 | 48 | 25 | 270 | 36 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 280 | 7 | 420 | 0 | 66 |  | 748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 540 | 220 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 1370 | 0 | 0 |  | 4445 | 3787 | 8232 | 2172 | 748 | 1688 | 0 | 384 | 3030 | 76 | 0 | 33 | 94 | 0 | 7 | 0 | 89.35
KWH | 0 | 0 | 0 | 3478500 | 0 | 286454 | 0 | 9727200 | 0 |  | 0 | 9609800 | 0 | 701760 | 1093638 | 244320 | 626855 | 0 | 0 | 1075200 | 983808 | 688800 | 230975 | 0 | 0 | 0 | 64080 | 65989 | 65169 | 0 | 432000 | 352440 | 740600 | 815000 | 193920 | 0 | 1100760 | 712000 | 0 | 0 | 194761 | 0 | 0 | 0 | 0 |  | 72480 | 793649 | 729661 | 359760 | 75840 | 199680 | 369744 | 319680 | 0 | 0 | 0 | 7586000 | 0 | 3766000 | 66909 | 0 | 482472 | 267360 | 0 | 1252544 | 0 | 290000 | 139320 | 335304 | 206820 | 693700 | 388010 | 2406720 | 1329600 | 0 | 0 | 6350 | 1012000 | 685503 | 0 | 0 | 3641318 | 0 | 1343424 | 1794240 | 0 | 0 | 472000 | 0 | 244440 | 7275000 | 321888 | 0 | 0 | 1518000 | 0 | 0 | 960000 | 0 | 784944 | 120690 | 469440 | 331680 | 194036 | 0 | 186000 | 648000 | 306945 | 23277 | 1026218 | 125567 | 361310 | 0 | 646800 | 476160 | 6964300 | 849600 | 130220 | 118080 | 338727 | 0 | 302040 | 105221 | 83520 | 124200 | 0 | 306109 | 0 | 8498181 | 138720 | 10101818 | 0 | 3233243 |  | 15563636 | 0 | 0 | 0 | 161280 | 0 | 0 | 0 | 245760 | 66304 | 58875 | 2502000 | 391300 | 100608 | 0 | 0 | 0 | 175574 | 126373 | 935152 | 228880 | 471524 | 138214 | 88114 | 355008 | 0 | 0 | 147528 | 0 | 0 | 4152900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7289745 | 1250880 | 0 | 261312 | 0 | 265046 | 0 | 28085 | 263904 | 14529800 | 5037000 | 0 | 435600 | 14940 | 380160 | 339648 | 0 | 0 | 11832730 | 102067 | 5258200 | 29416364 | 473500 | 0 |  | 111884491 | 103088011 | 214972502 | 44778888 | 15563636 | 40709033 | 0 | 19537638 | 83789993 | 1812760 | 0 | 4850604 | 2406720 | 1384510 | 138720 | 0
Fuel Cost | 0 | 0 | 0 | 15479325 | 0 | 1094254.28 | 0 | 28014336 | 0 |  | 0 | 30559164 | 0 | 14112393.6 | 19510501.92 | 4219406.4 | 1911907.75 | 0 | 0 | 21149184 | 19813893.12 | 12687696 | 4171408.5 | 0 | 0 | 0 | 1157284.8 | 1111254.76 | 1040748.93 | 0 | 324000 | 0 | 0 | 0 | 3473107.2 | 0 | 0 | 0 | 0 | 0 | 3509593.22 | 0 | 0 | 0 | 0 |  | 1272748.8 | 13976158.89 | 13068228.51 | 6105127.2 | 1152009.6 | 3101030.4 | 1375447.68 | 0 | 0 | 0 | 0 | 21164940 | 0 | 12503120 | 224145.15 | 0 | 1625930.64 | 1171036.8 | 0 | 5022701.44 | 0 | 5193900 | 2506366.8 | 1247330.88 | 155115 | 2580564 | 291007.5 | 15788083.2 | 4135056 | 0 | 0 | 101219 | 3946800 | 2556926.19 | 0 | 0 | 12453307.56 | 0 | 7456003.2 | 9365932.8 | 0 | 0 | 3105760 | 0 | 977760 | 22479750 | 241416 | 0 | 0 | 31346700 | 0 | 0 | 14841600 | 0 | 14851140.48 | 1410866.1 | 7684732.8 | 5340048 | 2999796.56 | 0 | 2754660 | 11664000 | 5325495.75 | 362190.12 | 19026081.72 | 2476181.24 | 5354614.2 | 0 | 10238844 | 7847116.8 | 18525038 | 15607152 | 1881679 | 2132524.8 | 4972512.36 | 0 | 5282679.6 | 1257390.95 | 1382256 | 2107674 | 0 | 5491595.46 | 0 | 58892394.33 | 0 | 0 | 0 | 0 |  | 42799999 | 0 | 0 | 0 | 2748211.2 | 0 | 0 | 0 | 4622745.6 | 1247178.24 | 1047975 | 7906320 | 1854762 | 1910545.92 | 0 | 0 | 0 | 3144530.34 | 2318944.55 | 15719905.12 | 4547845.6 | 8916518.84 | 2475412.74 | 1557855.52 | 6358193.28 | 0 | 0 | 111678.696 | 0 | 0 | 35216592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21286055.4 | 24167001.6 | 0 | 5019803.52 | 0 | 4410365.44 | 0 | 310339.25 | 4423031.04 | 83982244 | 15665070 | 0 | 6943464 | 168971.4 | 4459276.8 | 5750240.64 | 0 | 0 | 75847799.3 | 0 | 39173590 | 223270202.76 | 0 | 0 |  | 620741346.99 | 659382668.796 | 1280124015.786 | 134658022.536 | 42799999 | 122153939.43 | 0 | 352084727.88 | 516382822.39 | 0 | 0 | 86304488.73 | 15788083.2 | 9951932.62 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 418 | 0 |  | 0 | 450 | 0 | 76 | 80 | 15 | 0 | 0 | 0 | 84 | 50 | 16 | 13 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 18 | 15 | 33 | 33 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 48 | 51 | 35 | 0 | 6 | 20 | 1 | 0 | 0 | 0 | 360 | 0 | 157 | 0 | 0 | 9 | 0 | 0 | 51 | 0 | 18 | 8 | 13 | 8 | 33 | 18 | 120 | 33 | 0 | 0 | 1 | 43 | 30 | 0 | 0 | 163 | 0 | 59 | 79 | 0 | 0 | 18 | 0 | 10 | 290 | 8 | 0 | 0 | 80 | 0 | 0 | 67 | 0 | 82 | 20 | 25 | 17 | 10 | 0 | 9 | 17 | 17 | 4 | 49 | 17 | 17 | 0 | 9 | 25 | 390 | 54 | 13 | 35 | 17 | 0 | 17 | 18 | 0 | 0 | 0 | 17 | 0 | 290 | 4 | 419 | 0 | 415 |  | 687 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 12 | 0 | 0 | 67 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 28 | 25 | 0 | 0 | 25 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 93 | 0 | 0 | 0 | 6 | 0 | 5 | 0 | 622 | 220 | 0 | 17 | 1 | 39 | 0 | 0 | 0 | 588 | 13 | 250 | 1180 | 62 | 0 |  | 9918 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 408 | 0 |  | 0 | 450 | 0 | 79 | 82 | 30 | 23 | 0 | 0 | 92 | 91 | 98 | 25 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 18 | 0 | 33 | 33 | 17 | 0 | 46 | 30 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 6 | 64 | 51 | 25 | 13 | 19 | 15 | 12 | 0 | 0 | 0 | 360 | 0 | 159 | 8 | 0 | 45 | 30 | 0 | 51 | 0 | 25 | 8 | 16 | 8 | 33 | 18 | 106 | 36 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 163 | 0 | 61 | 78 | 0 | 0 | 20 | 0 | 10 | 300 | 16 | 0 | 0 | 130 | 0 | 0 | 68 | 0 | 36 | 0 | 25 | 17 | 13 | 0 | 9 | 105 | 17 | 0 | 104 | 0 | 17 | 0 | 79 | 25 | 320 | 54 | 0 | 17 | 17 | 0 | 17 | 0 | 18 | 17 | 0 | 17 | 0 | 352 | 1 | 419 | 0 | 34 |  | 653 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 34 | 0 | 8 | 135 | 19 | 16 | 0 | 0 | 0 | 32 | 15 | 92 | 21 | 42 | 24 | 8 | 38 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 286 | 93 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 610 | 220 | 0 | 54 | 0 | 0 | 70 | 0 | 0 | 579 | 0 | 250 | 1407 | 0 | 0 |  | 10558 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 15 | 0 | 412 | 0 |  | 0 | 450 | 0 | 100 | 82 | 15 | 335 | 0 | 0 | 92 | 90 | 98 | 30 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 18 | 22 | 33 | 33 | 17 | 0 | 46 | 30 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 6 | 64 | 51 | 25 | 0 | 19 | 18 | 10 | 0 | 0 | 0 | 330 | 0 | 160 | 140 | 0 | 45 | 45 | 0 | 51 | 0 | 25 | 8 | 13 | 10 | 33 | 18 | 141 | 60 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 163 | 0 | 60 | 84 | 0 | 0 | 20 | 0 | 10 | 310 | 16 | 0 | 0 | 130 | 0 | 0 | 68 | 0 | 35 | 0 | 25 | 17 | 20 | 0 | 9 | 105 | 17 | 0 | 105 | 0 | 17 | 0 | 78 | 25 | 400 | 72 | 0 | 17 | 17 | 0 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 480 | 10 | 420 | 0 | 0 |  | 780 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 40 | 20 | 16 | 135 | 20 | 16 | 0 | 0 | 0 | 32 | 16 | 92 | 28 | 42 | 40 | 8 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 93 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 622 | 220 | 0 | 54 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 250 | 1400 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 412 | 0 | 0 | 0 | 450 | 0 | 100 | 82 | 15 | 335 | 0 | 0 | 92 | 70 | 48 | 30 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 18 | 22 | 30 | 33 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 |  | 0 | 0 | 0 | 2 | 60 | 51 | 25 | 0 | 6 | 18 | 5 | 0 | 0 | 0 | 320 | 0 | 160 | 140 | 0 | 50 | 45 | 0 | 51 | 0 | 25 | 8 | 13 | 10 | 33 | 11 | 128 | 35 | 0 | 0 | 1.6 | 43 | 30 | 0 | 0 | 110 | 0 | 60 | 84 | 0 | 0 | 20 | 0 | 10 | 310 | 16 | 0 | 0 | 80 | 0 | 0 | 56 | 0 | 50 | 20 | 25 | 17 | 6 | 0 | 9 | 17 | 17 | 5 | 50 | 0 | 17 | 0 | 9 | 25 | 250 | 35 | 50 | 17 | 17 | 0 | 17 | 35 | 0 | 0 | 0 | 17 | 0 | 400 | 10 | 415 | 0 | 0 |  | 780 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 15 | 20 | 0 | 135 | 20 | 16 | 0 | 0 | 0 | 32 | 0 | 90 | 28 | 34 | 40 | 8 | 25 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 93 | 0 | 0 | 0 | 6 | 0 | 8 | 0 | 622 | 220 |  | 17 | 6 | 100 | 70 | 0 |  | 0 | 30 | 250 | 1400 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 402 | 0 | 0 | 0 | 450 | 0 | 63 | 82 | 0 | 335 | 0 | 0 | 80 | 50 | 16 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 30 | 25 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 25 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 300 | 0 | 161 | 80 | 0 | 45 | 45 | 0 | 51 | 0 | 0 | 8 | 13 | 8 | 0 | 9 | 98 | 75 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 110 | 0 | 62 | 78 | 0 | 0 | 20 | 0 | 10 | 320 | 16 | 0 | 0 | 50 | 0 | 0 | 56 | 0 | 17 | 2 | 25 | 17 | 6 | 0 | 9 | 17 | 17 | 1 | 16 | 0 | 17 | 0 | 9 | 25 | 245 | 18 | 2 | 0 | 17 | 0 | 0 | 3 | 0 | 0 | 0 | 17 | 0 | 404 | 0 | 417 | 0 | 65 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 35 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 622 | 220 | 0 | 17 | 0 | 12 | 0 | 0 | 0 | 0 | 3 | 250 | 932 | 14 | 0 | 0 |  |  |  | 85487921 | 15563636 | 0 | 83789993 | 24388242 | 2406720 | 1384510 | 138720 | 1812760
[8 empty] | 299430 | [13 empty] | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [14 empty] | 299772 | [10 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 |  | 399747 |  |  |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 | [6 empty] | 399245 |  | 299282 | 399274 |  | 399223 |  | 399630 | 299864 | [11 empty] | 599468 |  |  |  | 230 | [27 empty] | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 | [8 empty] | 599726 | [9 empty] | 85.4879 | 15.5636 | 0 | 83.79 | 24.3882 | 2.4067 | 1.3845 | 0.13872 | 1.8128
| Minimum Generation |  | 6937 | 4:00
| Highest Generation |  | 10558 | 19:00 | [200 empty] | 214.9725
| Day Peak Generation |  | 9918 | 12:00
| Evening Peak Generation |  | 10558 | 19:00 | [200 empty] | 202699852
| HVDC Max Flow |  | 775 | 15:00 | [200 empty] | 202.6999
| HVDC EvPeak Flow |  | 653 | 19:00
| Load factor L.F |  | 84.84% | [166 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-01-23
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2024-01-22 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9918 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6763
Evening Peak Generation : |  |  | 10558 | MW Hour : | 19:00 | Available Max Generation : |  | 11008
E.P. Demand (at gen end) : |  |  | 10616 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 10600
Maximum Generation : |  |  | 10558 | MW Hour : | 19:00 | Reserve(Generation end) |  | 408
Total Gen. (MKWH) : |  |  | 214.9725 | System Load Factor : | 84.84% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 680 | MW at | 8:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-01-23
Actual : |  | 89.32 | Ft.(MSL) , | Rule curve : | 98.8 | Ft.( MSL )
Gas Consumed : |  | Total = | 707.69 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 256811961.966
: |  |  | Coal : | 516382822.39 | Oil : | 438389216.61 | Total : | 1211584000.966
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3499.7913 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 955.1576 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1336.0395 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1159.4645 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 954.9506 |  |  | 0 | 0%
Mymensingh Area |  | 55 | 1320:00 | 709.2906 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 398.5972 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 331.2534 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 647.895 |  |  | 0 | 0%
Total |  | 55 |  | 9992.4397 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Sikalbaha 225 MW
8) Ashuganj East
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:21 | 13:41 | Jashore 132/33kV S/S JH-1(L2) Project Work S/D Due to for project works.
08:22 | 13:42 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-1 Project Work S/D Due to Kaligonj line lilo works.
08:30 | 16:18 | Ashuganj-Cumilla(N) 230 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to Annual Maintenance. and
from Ashuganj 230/132/33kV end Due to annual Maintenance for comilla end.
08:30 |  | Sikalbaha 132kV bus-A was schedule S/D.
08:30 | 15:28 | Chowmuhani-Ramganj 132 kV Ckt-1 Scheduled S/D from Ramganj 132/33kV end Due to Annual Maintenance and from Chowmuhani
132/33kV end Due to Yearly maintenance.
08:36 |  | Gopalganj 400/132kV S/S 400kV Payra Ckt-1 Scheduled S/D Due to Payra ps end maintenance work.
08:37 | 12:00 | Fenchuganj-Sreemangal 132kV Ckt-1 Scheduled S/D from Fenchuganj 230/132/33kV end Due to Maintenance work.
08:38 | 17:15 | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D.
08:39 | 16:25 | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to TR-04 Transformer Bushing leakage Maintenance by Energypac.
08:41 | 16:44 | Aminbazar-Manikgonj PP 132kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to Anual Maintenace.
08:44 | 14:35 | Chhatak 132/33kV S/S T-3 HT Scheduled S/D Due to Annual maintanance.
08:50 | 17:22 | Gopalganj 132/33kV S/S Gopalganj 100 MW PS Scheduled S/D Due to Annual Maintenance.
08:56 | 15:42 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 LT Scheduled S/D Due to Annual maintenance.
08:57 | 15:42 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 HT Scheduled S/D Due to Annual maintenance.
08:58 | 16:08 | Bagerhat-Goalpara 132 kV Ckt-1 Scheduled S/D from Bagerhat 132/33kV end Due to Annual maintenance work.
09:01 | 21:48 | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Scheduled S/D from Fenchuganj 230/132/33kV end Due to Emergency 132KV
BUS -1 DS 110-89A Maintenance.
09:04 | 17:24 | Pabna 132/33kV S/S T-3 LT Scheduled S/D Due to Annual Maintenance.
09:05 | 17:04 | Barishal-Bhandaria 132 kV Ckt-1 Scheduled S/D from Barishal 132/33kV end Due to Annual Maintenance and from Bhandaria
132/33kV end Due to Annual maintenance
09:05 | 17:22 | Pabna 132/33kV S/S T-3 HT Scheduled S/D Due to Annual maintenance.
09:06 | 17:35 | Baroirhat-Hathazari 132 kV Ckt-1 Scheduled S/D from Baroirhat 132/33kV end. and from Hathazari 230/132/33kVend.
09:15 | 15:56 | Kulaura 132/33kV S/S 132 kV Bus-B Scheduled S/D Due to Annual maintenance.
09:22 | 10:15 | Joydebpur 132/33kV S/S GT-3 HT Scheduled S/D Due to Auxiliary Transformer(AT-2) Maintenance.
09:26 | 12:42 | Fenchuganj 230/132/33kV S/S TR-02 HT Scheduled S/D Due to Due to 132KV BUS-2 Shutdown .
09:28 | 11:42 | Fenchuganj 230/132/33kV S/S 132 KV Bus-2 Scheduled S/D Due to Emergency 132KV BUS -2 DS 107-89B Maintenance.
09:34 | 16:02 | Anowara-Sikalbaha 230 kV Ckt-1 Scheduled S/D from Shikalbaha 230/132kV end Due to Dead line checking .
09:37 | 14:27 | Agrabad-Rampur 132kV Ckt-1 Scheduled S/D from Agrabad 132/33kV end Due to Anneal Maintenance.
09:42 | 14:26 | Rampur 230/132/33 S/S Agrabad-1 Scheduled S/D Due to Agrabad Grid Annual Maintenance.
09:45 | 12:26 | Sonargaon 132/33kV S/S BUS B Scheduled S/D Due to Annual maintenance.
09:50 | 16:20 | Haripur-Meghnaghat 230kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to Annual Deadline Checking. and from
Meghnaghat 230/132kV end Due to As per request of NLDC .
09:58 |  | Maniknagar-Narinda 132kV Ckt-2 Scheduled S/D from Maniknagar 132/33kV end Due to Narinda Ckt-2 Maintenance
work at narinda S/S. (Oil centrifuge) .
10:00 | 15:37 | Fenchuganj 230/132/33kV S/S AT-02 LT Scheduled S/D Due to Emergency 132KV BUS -1 DS 101-89A Maintenance.
10:22 | 14:05 | Mirpur 132/33kV S/S T1 HT Scheduled S/D Due to Annual maintenance & Reserve Bus Work .
10:22 | 14:40 | Mirpur 132/33kV S/S T1 LT Scheduled S/D Due to Annual maintenance & Reserve Bus Work .
10:27 | 14:04 | Mirpur 132/33kV S/S Reserve Bus Scheduled S/D Due to Annual maintenance & Reserve Bus Work
10:55 | 12:48 | BIPTC S/S 20DF24 Forced S/D Due to Corrective maintenance.
11:01 | 12:23 | Bashundhara-Tongi 132 kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Relay testing.
11:43 | 15:53 | Mirsorai 230/33kV S/S TR-1, 718T HT Project Work S/D Due to EGCB Project Work.
12:28 | 13:19 | Bashundhara-Tongi 132 kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Relay Testing.
12:30 | 04:10 | Rampal 400/230kV S/S Bus Reactor Forced S/D Due to Due to Low Bus Voltage(392/391/390 kV) . | [5 empty] | 1.25 MW load interrup.
12:37 | 16:46 | Savar 132/33kV S/S Bus-A Scheduled S/D Due to 33 KV Bus-A shutdown due to DPBS-3 schedule work.
12:40 | 12:50 | Pabna 132/33kV S/S T-1 HT Scheduled S/D. | [5 empty] | 28 MW load interrup.
12:40 | 12:50 | Pabna 132/33kV S/S T-1 LT Scheduled S/D.
12:46 | 21:31 | Fenchuganj 230/132/33kV S/S TR-01 HT Scheduled S/D Due to Maintenance work.
12:50 | 13:10 | Savar 132/33kV S/S T-1 LT Tripped showing OC/EF relays Due to 33 KV Bus-B grounded by DPBS-3 during shutdown process | [5 empty] | 48 MW load interrup.
of L-39 Feeder.
12:50 | 13:10 | Savar 132/33kV S/S T-2 LT Tripped showing OC/EF relays Due to 33 KV Bus-B grounded by DPBS-3 during shutdown process
of L-39 Feeder.
12:50 | 13:10 | Savar 132/33kV S/S T-3 LT Tripped showing OC/EF relays Due to 33 KV Bus-B grounded by DPBS-3 during shutdown process
of L-39 Feeder.
12:58 | 21:23 | Fenchuganj 230/132/33kV S/S 132 KV Bus-1 Scheduled S/D Due to Emergency 132KV BUS -1 DS 101-89A Maintenance.
13:23 | 15:59 | Siddhirganj 132/33kV S/S 120MW EGCB GT2 Forced S/D Due to EEGCT GT-2 lube oil leakage checking.
14:40 |  | Meghnaghat CCPP(Summit)-2 Tripped
15:37 | 17:17 | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to 33kV busbar red-hot maintenance by PBS. | [5 empty] | 30 MW load interrup.
15:37 | 17:19 | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to 33kV busbar red hot maintenance by Barishal PBS-2.
| 15:48 | Siddhirganj 335 MW CCPP Syncronized with remarks:- GT.
| 15:55 | Meghnaghat CCPP(Summit)-2 Syncronized
| 16:13 | Bagerhat-Goalpara 132 kV Ckt-1 is restored.
| 18:41 | Siddhirganj 335 MW CCPP Syncronized with remarks:- ST
21:24 |  | Rampal 1320 MW (BIFPCL) Shutdown with remarks:- Unit-2.
06:55 |  | Bogura 230/132kV S/S 230KV Main 2 Scheduled S/D Due to Red Hot Maintenance 230kV Bogura Ckt-4.
07:05 |  | Barapukuria-Bogura 230 kV Ckt-2 Scheduled S/D from Bogura
230/132kV end Due to Red Maintenance
11:43 | 17:47 | Cumilla(N)-Daudkandi 132 kV Ckt-2 Forced S/D from Daudkandi
132/33kV end Due to ordered by NLDC
11:31 |  | Matarbari 2*600 MW (CPGCL) unit-2 tripped.
11:34 | 12:49 | Mirpur 132/33kV S/S T2 LT Scheduled S/D Due to SF6 Gas
filling
11:35 | 12:49 | Mirpur 132/33kV S/S T2 HT Scheduled S/D Due to 132KV
Circuit Breaker T-2 SF6 Gas filling.
12:00 |  | Day Peak Gen. 9019 MW
| 12:12 | BIPTC S/S 10CF15 is restored.
12:47 |  | Unique Meghnaghat Power Limited (UMPL) Shutdown with
remarks:- ST
12:52 |  | Meghnaghat 450 MW CCPP (MPL) Syncronized with remarks:- GT
1
12:55 |  | Unique Meghnaghat Power Limited (UMPL) Shutdown with
remarks:- GT
13:01 |  | Madaripur 132/33kV S/S T3-426T LT Forced S/D Due to Breaker
Gas leckage
13:03 |  | Madaripur 132/33kV S/S T3-426T HT Forced S/D Due to Breaker
Gas leckage

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-01-22 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 3478500 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 286454 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 408 | 9727200
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9609800
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 79 | 701760
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 82 | 1093638 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 30 | 244320 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 25 | 230975 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 92 | 1075200 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 23 | 626855 | Machine sync at 15:48.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 91 | 983808 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 64080 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 98 | 688800 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 65989 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 65169 | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 18 | 784440 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 740600
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 815000
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 17 | 193920 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 130 | 1518000 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 36 | 784944 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 648000
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 54 | 849600 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 118080 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 105221
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 124200 | Fuel shortage
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 34 | 3233243 | On test.
| Dhaka area Total |  |  |  | 5062 | 2081 | 38857796
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 194761 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 120690
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 199680 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 76 | 1812760 | Unit-3 under maint.
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 0 | 0 | Gas shortage
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 306945 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 64 | 793649 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 729661 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 25 | 359760 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 469440 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 15 | 369744 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 12 | 319680
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 13 | 75840 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 23277
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 104 | 1026218 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 125567 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 361310 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 476160 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 338727 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 17 | 306109 | Fuel shortage
| SS Power I |  | SS Power | 2*612 | 1224 | 352 | 8498181 | Coal shortage
| Cox's Bazar Wind |  | IPP | 66 | 0 | 1 | 138720 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 419 | 10101818 | On test.
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4344 | 1286 | 27148697
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 159 | 3766000 | ST under shutdown
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 360 | 7586000 | 0
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 45 | 482472
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 30 | 267360 | Gas shortage
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 66909 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1252544
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 13 | 194036 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 25 | 290000 | Fuel shortage
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 331680 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 335304 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 206820
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 106 | 2406720
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 693700
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 139320
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 18 | 388010 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 79 | 646800 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 302040 | Fuel shortage
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 18 | 83520 | Fuel shortage
| Cumilla Area Total |  |  |  | 2951 | 1011 | 19439235
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 36 | 1329600 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Contract Expired
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 6350
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 68 | 960000 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 186000 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 130220
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 72480 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 119 | 2684650
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1012000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 685503 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3641318
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1343424
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1794240
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Under maint.
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 20 | 472000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 321888 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7275000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Under maint.
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 244440
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 320 | 6964300
| Sylhet Area Total |  |  |  | 2427 | 1041 | 23754113
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 653 | 15563636
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 32 | 161280 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 34 | 245760 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 66304 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 58875 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 93 | 1250880 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 380160
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 579 | 11832730
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 1399 | 29559625
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 100608 | Fuel shortage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 19 | 391300 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 135 | 2502000 | ST Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 610 | 14529800 | Unit-2 under maint.
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5037000
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 435600 | Fuel shortage
| Barisal 307 MW |  | IPP | 307*1 | 307 | 250 | 5258200 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1304 | 28254508
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 175574 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 15 | 126373 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 21 | 228880 | Fuel shortage
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 471524 | Fuel shortage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 138214 | Fuel shortage
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 286 | 7289745 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 355008 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 147528 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 88114 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 935152 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 261312 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 263904 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 14940
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1407 | 29416364
| Rajshahi Area Total |  |  |  | 3631 | 2043 | 39912632
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4152900 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 265046 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 28085
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 70 | 339648 | Fuel shortage
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 102067
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 473500
| Rangpur Area Total |  |  |  | 950 | 274 | 5361246
| Total |  |  |  | 25481 | 10558 | 214972502
| Eastern Grid Total |  |  |  | 15398 | 5538 | 111884491
| Western Grid Total |  |  |  | 10083 | 5020 | 103088011
| National Grid Total |  |  |  | 25481 | 10558 | 214972502
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2024-01-22
| (a) ENTIRE EASTERN GRID : |  | 6716.75 | MW | (b) ENTIRE WESTERN GRID : |  | 3304.1 | MW
| i) Dhaka area |  | 3702.25 | MW | i) Khulna area |  | 1204.3 | MW
| ii) Chittagong area |  | 975.5 | MW | ii) Rajshahi area |  | 1057.8 | MW
| iii) Comilla area |  | 845 | MW | iii) Barisal area |  | 297 | MW
| iv) Mymensingh area |  | 828 | MW | iv) Rangpur area |  | 745 | MW
| v) Sylhet area |  | 366 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10020.85 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 18 | 18:00 | Kamrangirchar | 48.45 | 13:00 | Narinda | 46 | 13:00 | Sherpur | 114 | 21:00
2 | AKSML | 101 | 00:00 | Chowmuhani | 144 | 19:30 | Kaptai | N/A | N/A | Narshingdi | 149 | 19:00 | Shikalbaha | 27 | 20:00
3 | Aftabnagar | 22 | 14:00 | Chuadanga | 73 | 18:30 | Kazla | 93 | 13:00 | Natore | 100 | 18:00 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 55 | 13:00 | Coxsbazar | 90 | 18:00 | Keranigonj | 52 | 13:00 | Nawabganj | 28.4 | 20:00 | Shitalakhya | 77.7 | 12:00
5 | Agrabad | 48 | 18:30 | Cumilla(N) | 95 | 21:00 | Khagrachori | 24 | 18:00 | Netrakona | 123 | 21:00 | Sholosohor | 34 | 16:00
6 | Amnura | 54 | 11:00 | Cumilla(S) | 119 | 12:00 | Khulna | 70 | 13:00 | New | 16 | 17:00 | Shyampur | 118 | 00:00
7 | Ashuganj | 52 | 11:00 | Daudkandi | 105 | 19:00 | Khulshi | 141 | 20:00 | Niamatpur | 76 | 18:30 | Siddhirganj | 96 | 12:00
8 | BIPTC | N/A | N/A | Dhaka | 16 | 13:00 | Kishoreganj | 116 | 19:00 | Noapara | 37 | 19:00 | Sirajganj | 86 | 19:00
9 | BSRM | 65 | 05:00 | Dhamrai | 98 | 15:00 | Kodda | 250 | 10:00 | PHP | 4 | 18:00 | Sonargaon | 112 | 06:00
10 | Bagerhat | 70 | 19:30 | Dhanmondi | 90 | 13:00 | Kulaura | 24 | 18:00 | Pabna | 70 | 18:30 | Sreemongol | 47 | 18:00
11 | Bakulia | 59 | 13:00 | Dohazari | 67 | 18:30 | Kurigram | 60 | 18:00 | Palashbari | 79 | 18:30 | Sreepur | 61 | 18:30
12 | Banani | 20.8 | 13:00 | Faridpur | 114 | 20:00 | Kushtia | 102 | 18:30 | Panchagarh | 44 | 18:00 | Srinagar | 28.4 | 19:30
13 | Bangabhaban | 7 | 12:00 | Fatullah | 47 | 11:00 | Lalbag | 67 | 18:30 | Patuakhali | 66 | 20:00 | Sunamganj | 34 | 18:00
14 | Barapukuria | 52 | 18:00 | Fenchuganj | 23 | 18:00 | Lalmonirhat | 42 | 18:30 | Payra | 15 | 20:00 | Sylhet | 14 | 18:00
15 | Barguna | 14 | 20:00 | Feni | 69 | 18:00 | MI_Cement | 12.3 | 17:00 | Postogola | 39 | 13:00 | Sylhet-132 | 80 | 18:00
16 | Barishal | 79 | 13:00 | GPH | 97 | 08:00 | Madanganj | 31 | 09:00 | Purbachal | 13 | 13:00 | TK | 16 | 00:00
17 | Barishal-230 | 68 | 18:00 | Ghorashal | 54 | 11:00 | Madaripur | 63 | 18:30 | Purbasadipur | 107 | 18:30 | Tangail | 144 | 18:00
18 | Baroaulia | 59 | 10:00 | Goalpara | 28 | 18:30 | Madartek | 47.79 | 21:00 | Rahim | 38 | 03:00 | Thakurgaon | 75 | 18:30
19 | Baroirhat | 39 | 18:00 | Gollamari | 47 | 18:30 | Madunaghat | 34 | 13:00 | Rajbari | 50 | 19:00 | Tongi | 127 | 11:00
20 | Bashundhara | 123 | 13:00 | Gopalganj | 72.2 | 18:30 | Magura | 45 | 18:30 | Rajendrapur | 72 | 10:00 | Ullahpara | 16 | 09:00
21 | BashundharaCement | 7 | 12:00 | Gulshan | 62 | 13:00 | Mahasthangarh | 48 | 18:30 | Rajshahi | 112 | 18:30 | Ullon | 31 | 21:00
22 | Beanibazar | 40 | 18:00 | Halishahar | 72 | 15:00 | Manikganj | 94 | 20:00 | Rajshahi-230 | 25 | 20:00 | Uttara | 36 | 15:00
23 | Benapole | 48 | 07:00 | HaripurSBU | 146 | 12:00 | Maniknagar | 48 | 13:00 | Ramganj | 68 | 18:00 | UttaraNew | 28 | 13:00
24 | Bhaluka | 122 | 18:30 | Hasnabad | 67 | 10:00 | Matarbari | 31 | 19:30 | Rampur | 17 | 12:00 | Zigatola | 48 | 18:30
25 | Bhandaria | 34 | 20:00 | Hathazari | 49 | 13:00 | Matuail | 56 | 12:00 | Rangamati | 12 | 18:30
26 | Bhangura | 28 | 18:30 | Ishurdi | 50 | 18:30 | Millgate | 78 | 11:00 | Rangpur | 113 | 18:30
27 | Bheramara(GK) | 40 | 19:00 | Jaldhaka | 64 | 18:00 | Mirpur | 85 | 18:00 | Ruppur | 3.8 | 11:00
28 | Bhulta | 224 | 01:00 | Jamalpur | 124 | 08:00 | Mirsorai | 3.5 | 18:00 | SSM | 12 | 23:00
29 | Bog-Sherpur | 50 | 19:00 | Jashore | 107 | 13:00 | Mirzapur | 43 | 10:00 | Saidpur | 101 | 18:30
30 | Bogura | 109 | 18:00 | Jhenaidah | 93 | 18:00 | Mithapukur | 46 | 18:00 | Satkhira | 88 | 19:00
31 | Borhanuddin | 36 | 21:00 | Joydebpur | 135 | 12:00 | Modern | 0 | 00:00 | Satmasjid | 81 | 13:00
32 | Brahmanbaria | 110 | 19:30 | Joypurhat | 43 | 19:00 | Mogbazar | 62.1 | 12:00 | Savar | 130 | 12:00
33 | Cantonment | 91 | 13:00 | Juldah | 20 | 09:00 | Mongla | 24 | 23:00 | SevenRings | 8.2 | 19:00
34 | Chandpur | 43 | 19:30 | KSRM | 32 | 22:00 | Motijheel | 27 | 13:00 | ShahCement | 22 | 10:00
35 | Chandraghona | 25 | 09:00 | Kabirpur | 226 | 12:00 | Munshiganj | 62 | 13:00 | Shahjadpur | 56 | 18:30
36 | Chapai | 58 | 12:00 | Kachua | 46 | 19:30 | Mymensingh | 189 | 13:00 | Shahjibazar | 90 | 19:00
37 | Charsaidpur | 36 | 18:30 | Kallyanpur | 69 | 13:00 | Naogaon | 97 | 13:00 | Shahmirpur | 35 | 01:00
38 | Chauddagram | 38 | 13:00 | Kalurghat | 28 | 10:00 | Narail | 41 | 18:30 | Shariatpur | 50 | 20:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-01-22 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 409 | 05:00 | 389 | 12:00 | Gopalganj | 414 | 05:00 | 394 | 12:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 416 | 05:00 | 395 | 12:00
| Bhulta | 407 | 05:00 | 380 | 12:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 423 | 19:00 | 410 | 12:00 | Payra | 420 | 04:00 | 409 | 10:00
| BIPTC | 409 | 02:00 | 396 | 13:00 | Rahanpur | 416 | 05:00 | 395 | 08:00
| Bogura | N/A | N/A | N/A | N/A | Rampal | 411 | 04:00 | 396 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 238 | 04:00 | 224 | 12:00 | Hasnabad | 238 | 20:00 | 226 | 12:00
| AKSML | 241 | 17:00 | 229 | 12:00 | Hathazari | 241 | 19:30 | 229 | 12:00
| Aminbazar | 241 | 04:00 | 227 | 12:00 | Ishurdi | 242 | 05:00 | 225 | 08:00
| Ashuganj | 241 | 06:00 | 229 | 12:00 | Jhenaidah | 240 | 05:00 | 223 | 08:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 236 | 05:00 | 222 | 12:00
| Baghabari | 238 | 03:00 | 222 | 12:00 | Keranigonj | 238 | 05:00 | 224 | 12:00
| Barapukuria | 226 | 03:00 | 211 | 08:00 | Khulna(S) | 241 | 05:00 | 228 | 08:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 242 | 01:00 | 236 | 12:00 | Maniknagar | 241 | 22:00 | 226 | 12:00
| Bheramara | 241 | 05:00 | 224 | 08:00 | Meghnaghat | 242 | 00:00 | 233 | 12:00
| Bhulta | 243 | 05:00 | 226 | 12:00 | Mirsorai | 240 | 22:00 | 228 | 12:00
| Bibiana | 243 | 22:00 | 235 | 12:00 | Rajshahi | 242 | 05:00 | 225 | 08:00
| BIPTC | 241 | 04:00 | 223 | 08:00 | Rampal | 238 | 04:00 | 226 | 12:00
| Bogura | 232 | 06:00 | 218 | 13:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 245 | 04:00 | 242 | 13:00 | Rampura | 240 | 04:00 | 225 | 12:00
| BSRM | 241 | 19:00 | 227 | 12:00 | Shikalbaha | 239 | 19:30 | 229 | 13:00
| Cumilla(N) | 240 | 04:00 | 228 | 12:00 | Shyampur | 240 | 05:00 | 225 | 12:00
| Fenchuganj | 247 | 22:00 | 240 | 12:00 | Siddhirganj | 241 | 05:00 | 226 | 11:00
| Ghorashal | 240 | 00:00 | 240 | 00:00 | Sirajgonj | 242 | 05:00 | 229 | 12:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 238 | 05:00 | 224 | 12:00
| GPH | 240 | 21:00 | 226 | 12:00 | Tongi | 238 | 21:00 | 222 | 11:00
| Haripur | 241 | 22:00 | 225 | 12:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 137 | 04:00 | 127 | 12:00 | Lalbag | 137 | 05:00 | 128 | 12:00
| Agargaon | 141 | 05:00 | 131 | 12:00 | Lalmonirhat | 130 | 02:00 | 118 | 08:00
| Agrabad | 141 | 22:00 | 133 | 12:00 | Madanganj | 139 | 22:00 | 129 | 12:00
| AKS | 137 | 01:00 | 132 | 05:00 | Madaripur | 136 | 05:00 | 131 | 12:00
| Aminbazar | 136 | 02:00 | 128 | 12:00 | Madartek | 137 | 05:00 | 126 | 12:00
| Amnura | 141 | 19:00 | 126 | 09:00 | Madunaghat | 141 | 19:00 | 133 | 12:00
| Ashuganj | 141 | 04:00 | 135 | 12:00 | Magura | 139 | 02:00 | 130 | 12:00
| Bagerhat | 137 | 22:00 | 123 | 08:00 | Mahasthangarh | 137 | 05:00 | 124 | 08:00
| Bakulia | 141 | 19:00 | 131 | 12:00 | Manikganj | 135 | 09:00 | 121 | 12:00
| Banani | 137 | 04:00 | 126 | 12:00 | Maniknagar | 134 | 05:00 | 125 | 12:00
| Bangabhaban | 135 | 03:00 | 124 | 12:00 | Matarbari | 130 | 00:00 | 126 | 03:00
| Barapukuria | 159 | 12:00 | 124 | 08:00 | Matuail | 137.7 | 22:00 | 128.6 | 12:00
| Barguna | 137 | 04:00 | 133 | 12:00 | Millgate | 137 | 04:00 | 125 | 12:00
| Barishal | 139 | 22:00 | 136 | 12:00 | Mirpur | 135 | 22:00 | 128 | 12:00
| Barishal-230 | 138 | 01:00 | 135 | 12:00 | Mirzapur | 135 | 05:00 | 127 | 09:00
| Baroaulia | 141 | 19:00 | 133 | 12:00 | Mithapukur | 135 | 05:00 | 121 | 08:00
| Baroirhat | 138 | 00:00 | 127 | 12:00 | MI_Cement | 140 | 22:00 | 130.3 | 12:00
| Bashundhara | 137 | 03:00 | 125 | 12:00 | Modern | 140 | 19:00 | 133 | 12:00
| BashundharaCement | 139 | 22:00 | 129 | 12:00 | Mogbazar | 137 | 03:00 | 129 | 12:00
| Beanibazar | 136 | 03:00 | 116 | 13:00 | Mongla | 134 | 17:00 | 123 | 08:00
| Benapole | 137 | 03:00 | 124 | 07:00 | Motijheel | 135 | 03:00 | 124 | 12:00
| Bhaluka | 135 | 02:00 | 124 | 13:00 | Munshiganj | 139 | 22:00 | 130 | 12:00
| Bhandaria | 138 | 06:00 | 128 | 12:00 | Mymensingh | 137 | 09:00 | 119 | 13:00
| Bhangura | 142 | 05:00 | 132 | 08:00 | Naogaon | 135 | 04:00 | 121 | 08:00
| Bheramara | 140 | 05:00 | 130 | 08:00 | Narail | 139 | 04:00 | 130 | 08:00
| Bheramara(GK) | 138 | 06:00 | 131 | 08:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 127 | 22:00 | 120 | 12:00 | Narshingdi | 136 | 03:00 | 126 | 08:00
| Bog-Sherpur | 134 | 00:00 | 126 | 13:00 | Natore | 139 | 05:00 | 129 | 08:00
| Bogura | 138 | 04:00 | 128 | 08:00 | Nawabganj | 137 | 22:00 | 128 | 12:00
| Bogura-230 | 137 | 05:00 | 127 | 13:00 | Netrakona | 137 | 09:00 | 119 | 13:00
| Brahmanbaria | 138 | 22:00 | 128 | 12:00 | New | 138 | 22:00 | 125 | 12:00
| Cantonment | 141 | 04:00 | 131 | 12:00 | Niamatpur | 133 | 00:00 | 119 | 08:00
| Chandpur | 138 | 19:00 | 125 | 12:00 | Noapara | 137 | 03:00 | 127 | 12:00
| Chandraghona | 141 | 19:00 | 135 | 12:00 | Pabna | 142 | 05:00 | 130 | 12:00
| Chapai | 135 | 03:00 | 127 | 09:00 | Palashbari | 132 | 03:00 | 123 | 13:00
| Charsaidpur | 140 | 22:00 | 130 | 12:00 | Panchagarh | 136 | 04:00 | 118 | 08:00
| Chauddagram | 141 | 22:00 | 130 | 12:00 | Patuakhali | 137 | 18:00 | 133 | 12:00
| Chhatak | 135 | 00:00 | 116 | 14:00 | Payra | 136 | 00:00 | 133 | 12:00
| Chowmuhani | 138 | 19:30 | 125 | 12:00 | PHP | 138 | 18:30 | 128 | 12:00
| Chuadanga | 138 | 05:00 | 128 | 08:00 | Postogola | 139 | 05:00 | 132 | 12:00
| Coxsbazar | 129 | 10:00 | 124 | 07:00 | Purbachal | 138 | 03:00 | 126 | 12:00
| Cumilla(N) | 142 | 19:30 | 133 | 12:00 | Purbasadipur | 131 | 21:00 | 117 | 08:00
| Cumilla(S) | 141 | 20:00 | 128 | 10:00 | Rahanpur | 138 | 05:00 | 131 | 08:00
| Daudkandi | 137 | 22:00 | 126 | 07:00 | Rahim | 138 | 22:00 | 129 | 12:00
| Dhaka | 137 | 03:00 | 127 | 12:00 | Rajbari | 138 | 04:00 | 130 | 08:00
| Dhamrai | 136 | 04:00 | 126 | 12:00 | Rajendrapur | 135 | 18:30 | 126 | 13:00
| Dhanmondi | 138 | 22:00 | 129.5 | 12:00 | Rajshahi | 137 | 06:00 | 129 | 13:00
| Dohazari | 138 | 22:00 | 131 | 06:00 | Rajshahi-230 | 138 | 04:00 | 125 | 08:00
| Faridpur | 137 | 03:00 | 130 | 12:00 | Ramganj | 137 | 19:00 | 125 | 12:00
| Fatullah | 140 | 22:00 | 131 | 12:00 | Rampur | 140 | 18:30 | 133 | 11:00
| Fenchuganj | 140 | 05:00 | 126 | 13:00 | Rampura | 137 | 04:00 | 127 | 12:00
| Feni | 137 | 00:00 | 126 | 13:00 | Rangamati | 141 | 22:00 | 135 | 10:00
| Ghorashal | 142 | 00:00 | 135 | 13:00 | Rangpur | 133 | 03:00 | 122 | 03:00
| Goalpara | 138 | 22:00 | 128 | 08:00 | Ruppur | 140 | 04:00 | 133 | 12:00
| Gollamari | 136 | 05:00 | 128 | 12:00 | Saidpur | 132 | 06:00 | 121 | 08:00
| Gopalganj | 135 | 03:00 | 128 | 12:00 | Satkhira | 135 | 05:00 | 125 | 08:00
| Gopalganj-400 | 136 | 04:00 | 129 | 12:00 | Satmasjid | 141 | 05:00 | 131 | 12:00
| Gulshan | 137 | 03:00 | 127 | 12:00 | Savar | 134 | 22:00 | 126 | 12:00
| Halishahar | 140 | 19:00 | 133 | 12:00 | SevenRings | 144 | 04:00 | 134 | 12:00
| Haripur | 138 | 22:00 | 129 | 12:00 | ShahCement | 140 | 22:00 | 130 | 12:00
| HaripurSBU | 138 | 22:00 | 132 | 11:00 | Shahjadpur | 143 | 06:00 | 136 | 08:00
| Hasnabad | 138 | 18:00 | 132 | 12:00 | Shahjibazar | 138 | 22:00 | 127 | 12:00
| Hathazari | 141 | 19:00 | 135 | 07:00 | Shahmirpur | 140 | 18:30 | 134 | 11:00
| Ishurdi | 143 | 05:00 | 133 | 08:00 | Shariatpur | 136 | 04:00 | 130 | 12:00
| Jaldhaka | 131 | 04:00 | 116 | 08:00 | Sherpur | 133 | 09:00 | 112 | 08:00
| Jamalpur | 136 | 09:00 | 116 | 08:00 | Shikalbaha | 129 | 19:00 | 123 | 03:00
| Jashore | 135 | 02:00 | 125 | 10:00 | Shikalbaha-230 | 140 | 19:30 | 134 | 13:00
| Jhenaidah | 138 | 22:00 | 130 | 08:00 | Shitalakhya | 140 | 22:00 | 130 | 12:00
| Jhenaidah-230 | 142 | 05:00 | 130 | 08:00 | Sholosohor | 140 | 19:00 | 132 | 12:00
| Joydebpur | 145 | 04:00 | 135 | 12:00 | Shyampur | 138 | 19:30 | 132 | 12:00
| Joypurhat | 134 | 04:00 | 122 | 08:00 | Shyampur-230 | 139 | 22:00 | 130 | 12:00
| Juldah | 140 | 19:00 | 134 | 01:00 | Siddhirganj | 138 | 22:00 | 129 | 12:00
| Kabirpur | 136 | 09:00 | 120 | 12:00 | Sirajganj | 139 | 04:00 | 127 | 12:00
| Kachua | 139 | 19:00 | 128 | 12:00 | Sonargaon | 138 | 22:00 | 127 | 12:00
| Kaliakoir | 137 | 09:00 | 129 | 12:00 | Sreemongol | 137 | 22:00 | 126 | 12:00
| Kallyanpur | 136 | 01:00 | 129 | 12:00 | Sreepur | 136 | 05:00 | 127 | 12:00
| Kalurghat | 140 | 18:30 | 134 | 12:00 | Srinagar | 136 | 05:00 | 128 | 12:00
| Kamrangirchar | 137 | 22:00 | 128 | 12:00 | SSM | 147 | 15:00 | 138 | 12:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 135 | 02:00 | 116 | 13:00
| Kazla | 135 | 06:00 | 124 | 13:00 | Sylhet | 137 | 03:00 | 117 | 13:00
| Keranigonj | 137 | 05:00 | 128 | 12:00 | Sylhet-132 | 137 | 04:00 | 120 | 13:00
| Khagrachori | 140 | 22:00 | 132 | 12:00 | Tangail | 134 | 02:00 | 121 | 12:00
| Khulna | 136 | 22:00 | 128 | 08:00 | Thakurgaon | 136 | 21:00 | 116 | 08:00
| Khulna(S) | 137 | 22:00 | 128 | 08:00 | TK | 141 | 21:00 | 134 | 04:00
| Khulshi | 139 | 19:00 | 132 | 12:00 | Tongi | 136 | 21:00 | 127 | 11:00
| Kishoreganj | 137 | 04:00 | 128 | 12:00 | Ullahpara | 140 | 02:00 | 130 | 13:00
| Kodda | 141 | 19:00 | 126 | 12:00 | Ullon | 135 | 01:00 | 128 | 12:00
| KSRM | 141 | 22:00 | 134 | 11:00 | Uttara | 136 | 04:00 | 127 | 12:00
| Kulaura | 138 | 01:00 | 124 | 13:00 | UttaraNew | 137 | 04:00 | 125 | 12:00
| Kurigram | 131 | 21:00 | 113 | 08:00 | Zigatola | 137 | 22:00 | 129 | 12:00
| Kushtia | 139 | 03:00 | 130 | 08:00

## L-Curve
Date | 2024-01-22
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 882 | 4445 | 3787 | 8232 |  |  |  | QF-LDC-11
0:30 | 921 | 4144 | 3846.5 | 7990.5 | Date: | 2024-01-22
1:00 | 960 | 3843 | 3906 | 7749
1:30 | 940 | 3768.5 | 3776 | 7544.5
2:00 | 920 | 3694 | 3646 | 7340
2:30 | 885 | 3698 | 3549.5 | 7247.5 | [5 empty] | Gen. at Eve. Peak | 10558 | 10558 MW (19:00 )
3:00 | 850 | 3702 | 3453 | 7155 | [6 empty] | 19:00
3:30 | 805 | 3689 | 3357 | 7046 | [5 empty] | Gen. at Day Peak | 9918 | 9918 MW (12:00 )
4:00 | 760 | 3676 | 3261 | 6937 | [6 empty] | 12:00
4:30 | 750 | 3676.5 | 3263 | 6939.5 | [5 empty] | Highest Generation | 10558
5:00 | 740 | 3677 | 3265 | 6942 | [6 empty] | 19:00
5:30 | 740 | 3812.5 | 3314 | 7126.5
6:00 | 740 | 3948 | 3363 | 7311
6:30 | 750 | 4046 | 3655.5 | 7701.5
7:00 | 760 | 4144 | 3948 | 8092
7:30 | 720 | 4275.5 | 4144.5 | 8420
8:00 | 680 | 4407 | 4341 | 8748
8:30 | 735 | 4570.5 | 4358 | 8928.5
9:00 | 790 | 4734 | 4375 | 9109
9:30 | 800 | 4823.5 | 4361 | 9184.5
10:00 | 810 | 4913 | 4347 | 9260
10:30 | 850 | 5027.5 | 4396.5 | 9424
11:00 | 890 | 5142 | 4446 | 9588
11:30 | 900 | 5294 | 4459 | 9753
12:00 | 910 | 5446 | 4472 | 9918
12:30 | 922 | 5416.5 | 4589 | 10005.5
13:00 | 934 | 5387 | 4706 | 10093
13:30 | 920 | 5196 | 4666 | 9862
14:00 | 906 | 5005 | 4626 | 9631
14:30 | 1033 | 4958.5 | 4526.5 | 9485
15:00 | 1160 | 4912 | 4427 | 9339
15:30 | 1145 | 4912 | 4301.5 | 9213.5
16:00 | 1130 | 4912 | 4176 | 9088
16:30 | 1128 | 4859.5 | 4218 | 9077.5
17:00 | 1126 | 4807 | 4260 | 9067
17:30 | 1018 | 4999.5 | 4553.5 | 9553
18:00 | 910 | 5192 | 4847 | 10039
18:30 | 845 | 5365 | 4933.5 | 10298.5
19:00 | 780 | 5538 | 5020 | 10558
19:30 | 812 | 5483 | 5036 | 10519
20:00 | 826 | 5479 | 5031 | 10510 |  |  |  | Executive Engineer
20:30 | 854 | 5402 | 4946 | 10348 |  |  |  | Network Operation Division
21:00 | 882 | 5325 | 4861 | 10186
21:30 | 917 | 5229 | 4609.5 | 9838.5
22:00 | 952 | 5133 | 4358 | 9491 |  |  |  |  | Page 6 of 7
22:30 | 1036 | 4963 | 4289.5 | 9252.5
23:00 | 1120 | 4793 | 4221 | 9014
23:30 | 1001 | 4619 | 4004 | 8623
24:00 | 882 | 4445 | 3787 | 8232
10558 MW (19:00 )
9918 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-01-22 |  | Energy |  | 214972502
QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 2172 | 748 | 1688 | 0 | 384 | 3030 | 76 | 0 | 33 | 94 | 0 | 7 | 0
0:30 | 1997.5 | 660 | 1564 | 0 | 271 | 3305 | 76 | 0 | 16.5 | 95 | 0 | 5.5 | 0 |  | Date: | 43851
1:00 | 1823 | 572 | 1440 | 0 | 158 | 3580 | 76 | 0 | 0 | 96 | 0 | 4 | 0
1:30 | 1816 | 502 | 1455 | 0 | 79 | 3521 | 76 | 0 | 0 | 90 | 0 | 5.5 | 0 | [7 empty] | Total Energy | 214.9725 | 214.9725 | Total Energy Gen 214.973 MKWHr Energy Not Served 0.979 MKWHr Energy Requirement 215.952 MKWHr
2:00 | 1809 | 432 | 1470 | 0 | 0 | 3462 | 76 | 0 | 0 | 84 | 0 | 7 | 0 | [7 empty] | Energy not Served | 0.97935 | 0.97935
2:30 | 1821.5 | 432 | 1484.5 | 0 | 0 | 3340 | 76 | 0 | 0 | 86 | 0 | 7.5 | 0 | [7 empty] | Energy Requirement | 215.9519 | 215.9519
3:00 | 1834 | 432 | 1499 | 0 | 0 | 3218 | 76 | 0 | 0 | 88 | 0 | 8 | 0
3:30 | 1807.5 | 432 | 1501 | 0 | 0 | 3136 | 76 | 0 | 0 | 85 | 0 | 8.5 | 0
4:00 | 1781 | 432 | 1503 | 0 | 0 | 3054 | 76 | 0 | 0 | 82 | 0 | 9 | 0
4:30 | 1767.5 | 432 | 1520 | 0 | 0 | 3050.5 | 76 | 0 | 0 | 82 | 0 | 11.5 | 0
5:00 | 1754 | 432 | 1537 | 0 | 0 | 3047 | 76 | 0 | 0 | 82 | 0 | 14 | 0
5:30 | 1801.5 | 432 | 1661.5 | 0 | 2.5 | 3050.5 | 76 | 0 | 0 | 86 | 0 | 16.5 | 0
6:00 | 1849 | 432 | 1786 | 0 | 5 | 3054 | 76 | 0 | 0 | 90 | 0 | 19 | 0
6:30 | 1810.5 | 526 | 1818.5 | 0 | 85 | 3269 | 76 | 0 | 8.5 | 90 | 1.5 | 16.5 | 0 | [6 empty] | Coal
7:00 | 1772 | 620 | 1851 | 0 | 165 | 3484 | 76 | 0 | 17 | 90 | 3 | 14 | 0
7:30 | 1764.5 | 642 | 1884.5 | 0 | 296 | 3609.5 | 76 | 0 | 25 | 92 | 17.5 | 13 | 0 | [5 empty] | Oil
8:00 | 1757 | 664 | 1918 | 0 | 427 | 3735 | 76 | 0 | 33 | 94 | 32 | 12 | 0
8:30 | 1740 | 663 | 1887 | 0 | 592.5 | 3753 | 76 | 0 | 62 | 93 | 53.5 | 8.5 | 139
9:00 | 1723 | 662 | 1856 | 0 | 758 | 3771 | 76 | 0 | 91 | 92 | 75 | 5 | 278
9:30 | 1735 | 662 | 1798.5 | 0 | 874 | 3716 | 76 | 0 | 128.5 | 102 | 88.5 | 4 | 229.725
10:00 | 1747 | 662 | 1741 | 0 | 990 | 3661 | 76 | 0 | 166 | 112 | 102 | 3 | 181.45
10:30 | 1772.5 | 662.5 | 1848 | 0 | 1039.5 | 3609 | 61 | 0 | 191 | 108 | 129 | 3.5 | 168.08
11:00 | 1798 | 663 | 1955 | 0 | 1089 | 3557 | 46 | 0 | 216 | 104 | 156 | 4 | 154.71
11:30 | 1883 | 675 | 1968.5 | 0 | 1119 | 3538 | 61 | 0 | 226.5 | 112 | 166 | 4 | 116.355
12:00 | 1968 | 687 | 1982 | 0 | 1149 | 3519 | 76 | 0 | 237 | 120 | 176 | 4 | 78
12:30 | 1953 | 726.5 | 1972 | 0 | 1121.5 | 3568 | 76 | 0 | 242 | 120 | 223.5 | 3 | 57.5
13:00 | 1938 | 766 | 1962 | 0 | 1094 | 3617 | 76 | 0 | 247 | 120 | 271 | 2 | 37
13:30 | 1938 | 766 | 1962 | 0 | 1094 | 3617 | 76 | 0 | 247 | 120 | 271 | 2 | 37
14:00 | 1938 | 766 | 1962 | 0 | 1094 | 3617 | 76 | 0 | 247 | 120 | 271 | 2 | 37
14:30 | 1941 | 770.5 | 1728 | 0 | 1102.5 | 3503 | 76 | 0 | 242 | 118 | 232 | 3 | 33.5
15:00 | 1944 | 775 | 1494 | 0 | 1111 | 3389 | 76 | 0 | 237 | 116 | 193 | 4 | 30
15:30 | 1966 | 770 | 1528.5 | 0 | 1074 | 3280.5 | 76 | 0 | 253.5 | 110 | 151 | 4 | 15
16:00 | 1988 | 765 | 1563 | 0 | 1037 | 3172 | 76 | 0 | 270 | 104 | 109 | 4 | 0
16:30 | 1959 | 765.5 | 1556.5 | 0 | 1076.5 | 3189 | 76 | 0 | 284 | 102 | 65 | 4 | 0
17:00 | 1930 | 766 | 1550 | 0 | 1116 | 3206 | 76 | 0 | 298 | 100 | 21 | 4 | 0
17:30 | 1911 | 766 | 1594.5 | 0 | 1379.5 | 3335.5 | 76 | 0 | 371 | 105 | 10.5 | 4 | 37.5
18:00 | 1892 | 766 | 1639 | 0 | 1643 | 3465 | 76 | 0 | 444 | 110 | 0 | 4 | 75
18:30 | 1955 | 709.5 | 1656 | 0 | 1698.5 | 3626 | 76 | 0 | 467 | 108 | 0 | 2.5 | 65
19:00 | 2018 | 653 | 1673 | 0 | 1754 | 3787 | 76 | 0 | 490 | 106 | 0 | 1 | 55
19:30 | 1995 | 653 | 1664 | 0 | 1659 | 3869 | 76 | 0 | 494 | 108 | 0 | 1 | 42
20:00 | 2016 | 653 | 1654 | 0 | 1663 | 3848 | 76 | 0 | 492 | 108 | 0 | 0 | 29
20:30 | 2050 | 653 | 1707.5 | 0 | 1529.5 | 3733.5 | 76 | 0 | 491.5 | 107 | 0 | 0 | 22
21:00 | 2084 | 653 | 1761 | 0 | 1396 | 3619 | 76 | 0 | 491 | 106 | 0 | 0 | 15
21:30 | 2059 | 709.5 | 1754.5 | 0 | 1343.5 | 3347 | 76 | 0 | 445.5 | 103 | 0 | 0.5 | 32.5
22:00 | 2034 | 766 | 1748 | 0 | 1291 | 3075 | 76 | 0 | 400 | 100 | 0 | 1 | 50
22:30 | 2002 | 766 | 1739.5 | 0 | 1085 | 3081 | 76 | 0 | 400.5 | 99 | 0 | 3.5 | 25
23:00 | 1970 | 766 | 1731 | 0 | 879 | 3087 | 76 | 0 | 401 | 98 | 0 | 6 | 0
23:30 | 2071 | 757 | 1709.5 | 0 | 631.5 | 3058.5 | 76 | 0 | 217 | 96 | 0 | 6.5 | 0 |  | Max Temp. in Dhaka |  | 17.4°C
24:00 | 2172 | 748 | 1688 | 0 | 384 | 3030 | 76 | 0 | 33 | 94 | 0 | 7 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 214.973 MKWHr Energy Not Served 0.979 MKWHr Energy Requirement 215.952 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2024-01-22
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1100760
2 | Karnaphuli Hydro PP Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 712000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [6 empty] | 0 | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 17 | 17 | 17 | 17 | 17 | 17 | 8 | 194761
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 5 | 10 | 15 | 17 | 20 | 19 | 17 | 12 | 7 | 1 | [9 empty] | 120690
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [8 empty] | 2 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 0 | 729661
12 | Hathazari 100 MW peaking PP | [8 empty] | 56 | 57 | 48 | 48 | 48 | 48 | 40 | 40 | 40 | 50 |  | 64 | 64 | 64 | 64 | 64 | 64 |  | 793649
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [7 empty] | 15 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 306945
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [11 empty] | 18 | 25 | 25 | 25 | 25 | 17 | 21 |  | 25 | 25 | 25 | 25 | 25 | 25 |  | 290000
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | [15 empty] | 9 | 10 | 10 |  | 23 | 49 | 52 | 105 | 120 | 150 | 332 | 626855
18 | Kodda 300 MW PP Unit-2 (Summit) | [7 empty] | 3 | 57 | 81 | 81 | 80 | 81 | 80 | 80 | 80 | 80 | 130 |  | 130 | 130 | 130 | 130 | 130 | 80 |  | 1518000
19 | Ashuganj 195 MW PP (APSCL-United) | [15 empty] | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 66909
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 3478500
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 480 | 480 | 450 | 410 | 400 | 400 | 400 | 400 | 415 | 373 | 338 | 290 | 313 | 325 | 289 | 278 | 279 | 281 |  | 352 | 390 | 374 | 290 | 290 | 280 | 280 | 8498181
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | [11 empty] | 9 | 30 | 30 | 44 | 41 | 42 | 45 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 482472
33 | Ashuganj 225 MW CCPP | 140 | 148 | 160 | 160 | 161 | 158 | 158 | 150 | 160 | 161 | 160 | 157 | 157 | 158 | 156 | 157 | 155 | 154 |  | 159 | 158 | 157 | 158 | 160 | 123 | 159 | 3766000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 290 | 285 | 365 | 335 | 350 | 280 | 300 | 280 | 360 | 290 | 280 | 280 | 280 | 280 | 300 |  | 360 | 310 | 310 | 310 | 290 | 290 | 295 | 7586000
| Ashuganj 420 MW CCPP(East) | [26 empty] | 0
35 | Ashuganj 55 MW PP (Precision) | [15 empty] | 3 | 17 | 20 |  | 30 | 38 | 37 | 40 | 40 | 40 | 40 | 267360
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 402 | 405 | 403 | 401 | 401 | 402 | 402 | 403 | 402 | 413 | 428 | 418 | 421 | 421 | 422 | 414 | 354 | 352 |  | 408 | 403 | 405 | 402 | 401 | 365 | 353 | 9727200
Meghnaghat Unique power
| Summit Meghanghat-2 589 MW(Gas) |  |  |  | 85 | 115 | 150 | 230 | 217 | 217 | 258 | 413 | 415 | 404 | 45 | 0 | 60 | 67 | 74 |  | 34 | 63 | 66 | 65 | 62 | 65 | 66 | 3233243
40 | Meghnaghat 450 MW CCPP(MPL) | 350 | 350 | 350 | 350 | 350 | 400 | 400 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 370 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 9609800
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 75 | 75 | 75 | 75 | 85 | 85 | 74 | 68 | 68 | 33 | 33 | 33 | 32 | 31 | 33 | 36 | 36 | 36 |  | 36 | 43 | 59 | 76 | 77 | 75 | 75 | 1329600
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 0 | 3 | 3 | 8 | 11 | 13 | 24 | 30 | 22 | 10 | 2 | [9 empty] | 130220
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 42 | 43 | 43 | 1012000
45 | Fenchugonj CCPP Phase-2 | 40 | 40 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 685503
46 | Shajibazar 330 MW CCPP | [14 empty] | 4
47 | Shahjibazar GTPP Unit- 8 & 9 | 60 | 60 | 60 | 40 | 40 | 60 | 61 | 60 | 60 | 60 | 60 | 59 | 60 | 60 | 59 | 40 | 40 | 59 |  | 61 | 61 | 60 | 60 | 51 | 63 | 62 | 1343424
48 | Shahjibazar 86 MW PP (Shahjibazar) | 79 | 79 | 79 | 50 | 50 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 78 | 78 | 78 | 78 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1794240
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 472000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 244440
54 | Hobiganj 11 MW PP Cofidence-E
55 | Fenchugonj 51 MW PP (Barakatullah) | [26 empty] | 0
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 8 | 8 | 8 | 8 | 8 | 8 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 321888
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 295 | 290 | 290 | 295 | 300 | 300 | 330 | 310 | 275 | 300 | 290 | 295 | 280 | 290 | 290 | 310 | 290 |  | 300 | 295 | 280 | 310 | 295 | 290 | 300 | 7275000
| Bibiyana South 400 MW | 245 | 245 | 240 | 230 | 200 | 200 | 200 | 200 | 230 | 250 | 320 | 390 | 400 | 400 | 400 | 400 | 400 | 330 |  | 320 | 300 | 300 | 300 | 300 | 275 | 270 | 6964300
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 5 | 17 |  | 17 | 17 | 17 |  |  |  |  | 65169
59 | Tangail Palli Power Gen 22 MW | [13 empty] | 5 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 72480
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 17 | 14 | 11 | 14 | 14 | 14 | 18 | 18 | 20 | 21 | 19 | 21 | 21 | 21 | 15 |  | 15 | 15 | 15 | 15 | 14 | 10 | 10 | 369744
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 96 | 84 | 88 | 82 | 82 | 90 | 90 | 94 | 92 | 112 | 104 | 120 | 120 | 116 | 116 | 104 | 100 | 110 |  | 106 | 108 | 108 | 106 | 100 | 98 | 94 | 2406720
64 | Malancha, Ctg. EPZ (United) | 12 | 19 | 32 | 40 | 40 | 35 | 30 | 10 | 2 | 1 | 1 | 1 | 2 | 2 | 2 | 4 | 13 | 8 |  | 12 | 12 | 14 | 16 | 8 | 15 | 15 | 319680
65 | Feni 22 MW PP (Doreen) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 15 | 13 | 13 | 13 | 15 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 335304
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 206820
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 |  |  |  | 693700
68 | Cumilla 25 MW PP (Summit) | 16 | 16 | 16 | 13 | 13 | 13 | 13 | 13 | 13 | 15 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 15 | 388010
69 | Summit Ashulia | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 432000
70 | Summit Madhabdi | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 0 | 0 | 0 | 0 | 15 | 15 | 15 | 15 | 15 | 15 | 0 |  | 0 | 20 | 22 | 22 | 22 | 22 | 22 | 352440
71 | Maona 33 MW PP(Summit) | 25 |  | 30 | 30 | 30 | 30 | 30 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 30 | 30 | 30 | 740600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 815000
73 | Ghorashal 108 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 286454
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | 13 | [6 empty] | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 19 | 37 | 37 | 68 |  | 79 | 79 | 79 | 79 | 71 | 49 | 48 | 646800
| Manikgonj 162MW PP(MPGL) | [9 empty] | 17 | 17 | 35 | [5 empty] | 17 |  | 17 | 17 | 17 |  |  |  |  | 118080
77 | Siddhirganj 100 PP(Dutch Bangla) | [7 empty] | 8 | 65 | 80 | 84 | 84 | 84 | 86 | 88 | 81 | 60 | 65 |  | 92 | 92 | 89 | 14 | 32 | 80 |  | 1075200
78 | Gazipur 52 MW PP | [6 empty] | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 17 | 17 | 17 | 17 | 17 | 17 | 8 | 193920
79 | Kodda 150 MW PP | [7 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 42 | 98 |  | 98 | 98 | 98 | 88 | 32 | 32 | 16 | 688800
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [7 empty] | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 139320
| Gazipur 100 MW PP | [6 empty] | 2 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 105 |  | 105 | 70 | 70 | 70 | 70 | 35 | 17 | 648000
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 2 | 4 | 4 | 3 | 3 | 2 | 1 | 0 | [9 empty] | 23277
| Jodiac Power | [8 empty] | 4 | 17 | 17 | 17 | 17 | 17 | 17 | [11 empty] | 125567
| Karnaphuli Power Ltd. | 17 | [5 empty] | 9 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 361310
82 | Madanganj 102 PP(Summit) | [7 empty] | 4 | 62 | 80 | 80 | 80 | 80 | 80 | 82 | 82 | 82 | 82 |  | 82 | 82 | 82 | 82 | 82 | 38 | 6 | 1093638
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [7 empty] | 8 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 15 | 25 |  | 25 | 25 | 25 | 25 | 25 |  |  | 230975
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | [8 empty] | 10 | 37 | 70 | 76 | 69 | 68 | 67 | 19 | 6 | 46 |  | 79 | 51 | 60 | 8 | 31 | 55 |  | 701760
| Meghnaghat 104 MW PP (OPCL) | [7 empty] | 17 | 52 | 54 | 54 | 54 | 62 | 71 | 71 | 71 | 55 | 53 |  | 54 | 54 | 54 | 54 | 52 | 37 | 36 | 849600
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [7 empty] | 25 | 25 | 25 | 25 | 35 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 |  | 359760
92 | Fenchuganj 44 MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1252544
94 | Gagnagar 102 MW PP (Digital Power) | [7 empty] | 24 | 50 | 50 | 50 | 50 | 66 | 66 | 66 | 50 | 50 | 91 |  | 91 | 91 | 91 | 91 | 91 | 16 |  | 983808
95 | Patenga 50MW PP (Baraka) | 6 | [5 empty] | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 9 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 6 | 199680
96 | Chattogram 108 MW PP (ECPV) | [15 empty] | 7 | 12 | 13 |  | 13 | 12 | 13 | 13 |  |  |  | 75840
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [11 empty] | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 30 | 15 | 15 | 15 | 15 | 15 | 15 | 244320
100 | Manikganj 55 MW PP (Northern) | [11 empty] | 17 |  |  | 17 | 17 | [10 empty] | 65989
101 | Kushiara 163 MW CCPP (KP) | 140 | 140 | 140 | 120 | 120 | 163 | 163 | 163 | 163 | 120 | 120 | 163 | 163 | 120 | 120 | 163 | 163 | 120 |  | 163 | 120 | 120 | 163 | 163 | 120 | 120 | 3641318
102 | Sarishabari 3 MW Solar Plant | [7 empty] | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | [9 empty] | 6350
103 | Kamalaghat 54 MW PP(Banco Energy) | [13 empty] | 17 | 17 | 17 | [10 empty] | 64080
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 9 |  |  |  |  | 3 | 56 | 56 | 56 | 58 | 67 | 67 | 58 | 58 | 58 | 58 | 58 | 68 |  | 68 | 68 | 68 | 68 | 9 | 9 | 9 | 960000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 17 | 61 | 75 | 82 | 82 | 82 | 82 | 37 | 36 | 36 | 36 |  | 36 | 36 | 36 | 23 | 19 | 17 | 17 | 784944
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | [5 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 24 | 25 | 469440
116 | Chandpur 200 MW (Desh energy) | 17 | [6 empty] | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 26 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 331680
117 | Ashuganj 150 MW PP (Midland) | 6 | [5 empty] | 5 | 6 | 5 | 6 | 6 | 10 | 6 | 6 | 5 | 6 | 8 | 12 |  | 13 | 13 | 15 | 15 | 15 | 20 | 20 | 194036
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | [5 empty] | 2 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 186000
| Anwara 300 MW PP (United) | [7 empty] | 16 | 16 | 32 | 49 | 49 | 51 | 51 | 51 | 51 | 102 | 103 |  | 104 | 105 | 104 | 106 | 106 | 52 | 5 | 1026218
| Juldah unit-2 (Acorn) | 25 | [5 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 476160
| Anlima Energy Ltd. | 17 | [5 empty] | 15 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 338727
| Bhairob 54.5 MW | [8 empty] | 9 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 302040
| Spectra Solar Plant Ltd. | [6 empty] | 0 | 1 | 8 | 9 | 9 | 18 | 16 | 21 | 18 | 10 | 2 | [9 empty] | 105221
| Chandpur 115(Doreen) | [17 empty] | 13 |  | 18 | 36 | 31 |  |  |  |  | 83520
| Kanchan Purbachal Power Generation Ltd. | [16 empty] | 14 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 |  | 124200
| Mirsharai 150 MW (Oil) | [6 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 306109
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 4 | 7 | 8 | 9 | 14 | 19 | 14 | 12 | 5 | 3 | 4 | 4 | 2 | 6 | 4 | 4 | 4 | 4 |  | 1 | 1 | 0 | 0 | 1 | 6 | 7 | 138720
| Matarbari 2*600 MW (CPGCL) | 422 | 419 | 419 | 420 | 418 | 419 | 417 | 420 | 419 | 418 | 419 | 419 | 418 | 416 | 416 | 418 | 418 | 420 |  | 419 | 418 | 418 | 418 | 408 | 420 | 420 | 10101818
120 | Eastern Zone Total | 3843 | 3694 | 3702 | 3676 | 3677 | 3948 | 4144 | 4407 | 4734 | 4913 | 5142 | 5446 | 5387 | 5005 | 4912 | 4912 | 4807 | 5192 |  | 5538 | 5483 | 5479 | 5325 | 5133 | 4793 | 4445 | 111884491
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [8 empty] | 3 | 16 | 16 | 16 | 16 |  |  |  |  | 32 |  | 32 | 18 | 19 |  |  |  |  | 161280
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [10 empty] | 9 | 12 | 11 | 6 | 9 | 15 | 38 | 46 |  | 34 | 28 | 23 | 22 | 22 | 23 |  | 245760
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [7 empty] | 7 | 22 | 65 | 93 | 93 | 93 | 93 | 93 | 70 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 17 |  | 1250880
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 2 | 13 | 24 | 28 | 42 | 39 | 70 | 66 | 47 | 25 | 7 | [9 empty] | 380160
131 | Rampal 1320 MW (BIFPCL) | 548 | 568 | 522 | 516 | 528 | 530 | 524 | 571 | 588 | 591 | 542 | 588 | 585 | 582 | 546 | 484 | 492 | 501 |  | 579 | 601 | 621 | 495 |  |  |  | 11832730
132 | United Payra Power Ltd. | 17 | [5 empty] | 7 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 |  | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 435600
133 | Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 220 | 190 | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5037000
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 |  | 100608
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 200 | 178 | 150 | 150 | 150 | 150 | 245 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 200 | 150 | 183 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 5258200
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 132 | 132 | 132 | 105 | 105 | 105 | 65 | 67 | 67 | 67 | 67 | 67 | 70 | 70 | 70 | 135 | 135 | 135 |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 2502000
140 | Bhola 33 MW PP (Venture) | 17 | 16 | 16 | 15 | 14 | 17 | 16 | 16 | 16 | 15 | 16 | 16 | 17 | 16 | 13 | 13 | 14 | 18 |  | 19 | 20 | 20 | 19 | 21 | 19 | 18 | 391300
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [16 empty] | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 58875
143 | Gopalganj 100 MW Peaking PP | [21 empty] | 3 | 21 | 24 | 24 |  | 66304
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 572 | 432 | 432 | 432 | 432 | 432 | 620 | 664 | 662 | 662 | 663 | 687 | 766 | 774 | 775 | 765 | 766 | 766 |  | 653 | 653 | 653 | 653 | 766 | 766 | 748 | 15563636
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 550 | 550 | 510 | 480 | 470 | 470 | 600 | 622 | 622 | 622 | 622 | 622 | 622 | 580 | 500 | 460 | 460 | 480 |  | 610 | 622 | 622 | 622 | 600 | 550 | 540 | 14529800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4152900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 32 | 34 | 34 | 34 | 34 | 34 |  | 175574
| Sirajgonj 6.55 MW Solar | [7 empty] | 0 | 0 | 0 | 0 | 1 | 3 | 2 | 2 | 1 | 0 | [9 empty] | 14940
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 299 | 318 | 339 | 300 | 300 | 389 | 380 | 360 | 326 | 280 | 283 | 275 | 259 | 254 | 248 | 241 | 257 | 280 |  | 286 | 287 | 288 | 319 | 330 | 353 | 300 | 7289745
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [12 empty] | 4 | 4 | 4 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 126373
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 |  | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 147528
165 | Amnura 50 MW PP(Sinha) | [9 empty] | 28 | 28 | 28 | 28 | 28 | 28 | 14 | 14 | 28 |  | 21 | [6 empty] | 228880
166 | Katakhali 50 MW PP (Northern) | [7 empty] | 34 | 34 | 25 | 34 | 25 | 25 | 34 | 34 | 16 | 34 | 42 |  | 42 | 42 | 42 | 34 | 34 |  |  | 471524
167 | Katakhali 50 MW Peaking PP | [16 empty] | 3 | 16 |  | 24 | 32 | 32 | 24 | 24 | 24 |  | 138214
168 | Santahar 50 MW Peaking PP | [9 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 38 |  | 38 | 38 | 38 | 38 |  |  |  | 355008
169 | Natore 52 MW PP (Rajlanka) | [7 empty] | 8 | 8 | 8 | [7 empty] | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 88114
170 | Chapainawabganj 100 MW Peaking PP | [10 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 92 |  | 92 | 92 | 92 | 92 | 92 | 92 |  | 935152
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [16 empty] | 1 | 30 |  | 35 | 35 | 35 | 35 | 35 | 35 | 0 | 261312
172 | Confidence Power Bogura Unit-1 113 MW | [14 empty] | 8 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 |  |  | 263904
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 6 | [5 empty] | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 28 | 33 |  | 34 | 34 | 34 | 34 | 27 | 6 | 6 | 265046
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 1 | 1 | 5 | 5 | 5 | 5 | 4 | 2 | 0 | [9 empty] | 28085
178 | Energypac Power Venture Thakurgaon Ltd. | [15 empty] | 17 | 17 | 70 |  | 70 | 70 | 70 | 70 | 17 | 17 |  | 339648
| Intraco Solar 30 MW | [6 empty] | 0 | 1 | 2 | 4 | 7 | 13 | 27 | 23 | 15 | 9 | 2 | [9 empty] | 102067
| Adani Power Jharkhanda Ltd | 1210 | 1097 | 997 | 908 | 911 | 915 | 1128 | 1302 | 1307 | 1237 | 1216 | 1180 | 1259 | 1272 | 1268 | 1212 | 1204 | 1363 |  | 1407 | 1418 | 1393 | 1374 | 1357 | 1417 | 1370 | 29416364
178 | Teesta Solar Limited | [7 empty] | 8 | 25 | 35 | 60 | 62 | 103 | 74 | 70 | 44 | 7 | [9 empty] | 473500