## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2024-01-24 | Wednesday
|  | Date (day): | 2024-01-24 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10582.6 | MW |  |  | (b) At Evening Peak Hour : |  | 10818 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-01-23 | 2024-01-24 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 12 | 12 | 96 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 418 | 401 | 412 | 412
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 87 | 96 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 82 | 82 | 85 | 85 |  | 17 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 15 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 25 | 25 | 25 | 25 | 50 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 85 | 93 | 92 | 92 |  | 8 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 332 | 336 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 66 | 91 | 75 | 92 |  | 10 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 0 | 0 | 17 | 37 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 98 | 32 | 100 | 49 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 0 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 40 | 40 | 40 | 40 |  | 40 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 30 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 28 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 17 | 8 | 17 | 35 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 80 | 130 | 80 | 130 | 170 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 53 | 36 | 54 | 36 | 113 |  | Fuel shortage
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 88 | 17 | 105
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 39 | 53 | 53 | 72 | 32 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 17 | 35 | 17 | 145 |  | Fuel shortage
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 29 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 70 | 49 | 100 | 100 |  |  | on test
| Dhaka area Total |  |  |  |  | 5763 | 5062 | 2214 | 2439 | 2298 | 2567 | 1564 | 1015
38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
39 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 17 | 8 | 17 | 8 |  | Fuel shortage
40 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 19 | 6 | 19 | 31 |  | Fuel shortage
42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 76 | 76 | 76 | 76 | 154 |  | Low water lavel
43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 31 | 206 | 220 | 220 | 5 |  | Gas shortage
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 28 | 17 | 28 | 17 | 88 |  | Fuel shortage
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 48 | 66 | 60 | 72 | 26 |  | Fuel shortage
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 51 |  | Fuel shortage
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 17 | 18 | 18
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 1 | 20 | 5 | 10
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 5 | 0 | 0 | 108 |  | Fuel shortage
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 49 | 105 | 50 | 100 | 200 |  | Fuel shortage
54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 0 | 0 | 0 | 54 |  | Fuel shortage
55 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 17 | 17 | 93 |  | Fuel shortage
56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
57 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 17 | 99 |  | Fuel shortage
58 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 17 | 17 | 17 | 17 | 146 |  | Fuel shortage
59 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 447 | 400 | 400 | 400 | 824 |  | Coal Shortage.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 0 | 1 | 10 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 419 | 271 | 450 | 0 |  |  | On test.
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4404 | 4344 | 1295 | 1397 | 1533 | 1136 | 2292 | 330
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 157 | 160 | 160 |  | 61 | ST Under maint.
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 305 | 310 | 310 |  |  | FGMO
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Under maint
63 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 | 400 |  | Gas shortage
64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 44 | 44 | 50 | 45
65 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 52 | 44 | 45 | 45 | 10
66 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 117 | 8 | 0 | 0 | 195 |  | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
68 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 6 | 8 | 6 | 20 | 130 |  | Fuel shortage
69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 25 | 25 | 25 | 25 |  | 27 | Engine problem
70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
71 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 17 | 17 | 17 | 183 |  | Fuel shortage
72 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 13 | 13 | 13 | 13 |  | 9 | Engine problem
73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 110 | 108 | 128 | 141
74 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 17 | 11 | 18 |  | 7 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 0 | 114 |  | Fuel shortage
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 78 | 9 | 78 | 35 |  | Fuel shortage
79 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 17 | 17 | 17 |  | 37 | Engine problem
80 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 18 | 0 | 18 | 97 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2951 | 784 | 959 | 893 | 1009 | 1568 | 304
81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 33 | 34 | 35 | 40 | 162 |  | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 68 | 56 | 68 | 132 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 9 | 9 | 106 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 0 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 2 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 102 | 117 | 153.6 | 123 | 162 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 40 | 40 | 40 |  | 50 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 63 | 60 | 60
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 84 | 84 | 84
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 |  | 231 | Under maint.
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 20 | 20 | 20 | 20
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 9 |  | Gas shortage
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 300 | 310 | 310 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 360 | 360 | 250 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1046 | 1099 | 996 | 1146 | 110 | 1138
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 765 | 794 | 922 | 922
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 32 | 16 | 33 | 82 |  | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 12 | 32 | 15 | 40 |  | 14 | Engine problem
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 12 | 20 | 20 | 20 |  | 89 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 0 | 16 | 24 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 93 | 93 | 93 | 93 |  | 12 | Engine problem
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 77 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0 |  |  | Unit-2 test
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 975 | 979 | 1166 | 1124 | 1203 | 115
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 0 | 16
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 17 | 18 | 20 | 20 |  | 20 | Engine problem
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 135 | 135 | 135 | 135 |  | 59 | GT-2 & ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 622 | 622 | 622 | 622 |  | 622 | #01 Under maint.
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 54 | 17 | 54 | 96 |  | Fuel shortage
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 250 | 250 | 200 | 200 | 107 |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1261 | 1315 | 1214 | 1267 | 203 | 701
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 34 | 32 | 32 | 20 |  | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 4 | 15 | 0 | 16 |  | 55 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 28 | 21 | 28 | 28
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 25 | 34 | 25 | 42 |  | 8 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 15 | 32 | 0 | 34 |  | 16 | Engine problem
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 375 | 319 | 400 | 400 | 14 |  | Gas shortage
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 25 | 38 | 12 |  | Engine problem
136 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 8 | 44 |  | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 50 | 91 | 50 | 92 |  | 12 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 0 | 35 | 78 |  | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 0 | 35 | 78 |  | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 1 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1271 | 1470 | 1400 | 1400
| Rajshahi Area Total |  |  |  |  | 3653 | 3631 | 1774 | 2127 | 1985 | 2171 | 1267 | 91
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 6 | 41 | 6 | 35 | 78 |  | Fuel shortage
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 70 | 0 | 70 | 45 |  | Fuel shortage
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 28 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 137 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 346 | 281 | 344 | 275 | 248 | 189
| Total |  |  |  |  | 26504 | 25481 | 9797 | 10713 | 10582.6 | 10818 | 8617 | 3883
A. |  | 2024-01-23 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 10713 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 6763 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10713 | MW
3 | Day peak Generation : |  |  | 9797 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10172.29 | MW
4 | Evening peak Generation : |  |  | 10713 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 215.769 | MKWHr | By Solar | 1.7783 | MKWHr
| By Gas : | 97.2491 | MKWHr |  | By Oil: | 25.8664 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 70.3185 | MKWHr |  | By Hydro: | 1.8407 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.0504 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 8617 | MW | Dhaka | 3772.19 | 3772.19 |  | 0 |  | 18:00 |  | 50
|  |  | For Plants S/D or M/C prob = |  |  | 3883 | MW | Chittagong | 1012 | 1012 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 12500 | MW | Khulna | 1214.4 | 1214.4 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 772.04 | MMCFD |  |  | Rajshahi | 1068.8 | 1068.8 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 300725138.62 | ii) Oil : | Taka | 465560959.37 | Comilla | 847 | 847 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 439774732.6 | Total | Taka | 1206060830.59 | Mymensingh | 848 | 848 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 374 | 374 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 788 | MW (W to E) at | 19:00 | hrs | Barisal | 282.9 | 282.9 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 328 | MW at | 7:00 | hrs | Rangpur | 753 | 753 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 22.6°C |  |  | Total | 10172.29 | 10172.29 |  | 0
B. |  | 2024-01-24 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 22.6°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 10818 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10000 | MW
4 | Reserve(Generation end) |  |  |  | 18 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 217.5213 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6840 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 16.3011 | MKWHr. | ii) HVDC Flow at Peak Time |  | 794 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.3645 | MKWHr. | iii) Maximum HVDC Flow : |  | 899 | MW at | 15:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 89.32 |  | (b) Today: | 89.12 |  | (c) Rule Curve: |  | 98.6
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-01-23 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 353 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 30 | 33 | 0 | 0 | 46 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 10 | 15 | 0 | 0 | 0 | 285 | 0 | 160 | 8 | 0 | 45 | 40 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 0 | 15 | 84 | 76 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 163 | 0 | 63 | 78 | 0 | 0 | 20 | 0 | 10 | 295 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 25 | 17 | 10 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 14 | 25 | 265 | 15 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 11 | 419 | 0 | 71 |  | 571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 540 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 1358 | 0 | 0 |  | 4217 | 3569 | 7786 | 2163 | 571 | 1680 | 0 | 184 | 3017 | 76 | 0 | 0 | 84 | 0 | 11 | 0 | 89.34
2:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 353 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 30 | 33 | 0 | 0 | 46 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16 | 0 | 0 | 0 | 310 | 0 | 159 | 8 | 0 | 45 | 40 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 0 | 15 | 78 | 76 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 163 | 0 | 63 | 78 | 0 | 0 | 20 | 0 | 10 | 300 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 8 | 421 | 0 | 66 |  | 429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 1141 | 0 | 0 |  | 3994 | 3300 | 7294 | 2177 | 429 | 1744 | 0 | 0 | 2782 | 76 | 0 | 0 | 78 | 0 | 8 | 0 | 89.34
3:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 353 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 30 | 33 | 0 | 0 | 46 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 27 | 0 | 0 | 0 | 285 | 0 | 160 | 8 | 0 | 45 | 40 | 0 | 51 | 0 | 0 | 0 | 13 | 8 | 0 | 15 | 76 | 78 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 163 | 0 | 63 | 78 | 0 | 0 | 20 | 0 | 10 | 305 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 9 | 421 | 0 | 65 |  | 429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 910 | 0 | 0 |  | 3973 | 3028 | 7001 | 2142 | 429 | 1758 | 0 | 0 | 2511 | 76 | 0 | 0 | 76 | 0 | 9 | 0 | 89.33
4:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 353 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 30 | 17 | 0 | 0 | 46 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 31 | 0 | 0 | 0 | 290 | 0 | 160 | 8 | 0 | 45 | 40 | 0 | 51 | 0 | 0 | 0 | 13 | 8 | 0 | 15 | 82 | 88 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 140 | 0 | 63 | 78 | 0 | 0 | 20 | 0 | 10 | 300 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 8 | 420 | 0 | 65 |  | 429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 906 | 0 | 0 |  | 3952 | 2934 | 6886 | 2141 | 429 | 1734 | 0 | 0 | 2416 | 76 | 0 | 0 | 82 | 0 | 8 | 0 | 89.33
5:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 330 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 30 | 28 | 0 | 0 | 46 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40 | 0 | 0 | 0 | 290 | 0 | 160 | 8 | 0 | 45 | 38 | 0 | 51 | 0 | 0 | 0 | 13 | 8 | 0 | 15 | 80 | 86 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 140 | 0 | 63 | 78 | 0 | 0 | 20 | 0 | 10 | 295 | 16 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 5 | 421 | 0 | 65 |  | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 866 | 0 | 0 |  | 3878 | 2885 | 6763 | 2092 | 430 | 1706 | 0 | 7 | 2367 | 76 | 0 | 0 | 80 | 0 | 5 | 0 | 89.32
6:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 345 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 30 | 25 | 0 | 0 | 46 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 9 | 0 | 0 | 10 | 42 | 0 | 0 | 0 | 315 | 0 | 160 | 8 | 0 | 45 | 40 | 0 | 51 | 0 | 0 | 0 | 13 | 8 | 0 | 15 | 84 | 87 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 163 | 0 | 63 | 78 | 0 | 0 | 20 | 0 | 10 | 310 | 16 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 238 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 1 | 419 | 0 | 66 |  | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 867 | 0 | 0 |  | 4101 | 2966 | 7067 | 2123 | 430 | 1849 | 0 | 38 | 2466 | 76 | 0 | 0 | 84 | 0 | 1 | 0 | 89.32
7:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 402 | 0 |  | 0 | 380 | 0 | 30 | 20 | 0 | 300 | 0 | 0 | 38 | 40 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 30 | 25 | 4 | 0 | 46 | 30 | 0 | 0 | 6 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 25 | 0 | 6 | 10 | 6 | 0 | 0 | 0 | 340 | 0 | 160 | 8 | 0 | 45 | 40 | 0 | 51 | 0 | 0 | 1 | 13 | 8 | 0 | 15 | 84 | 75 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 163 | 0 | 63 | 78 | 0 | 0 | 20 | 0 | 10 | 305 | 16 | 0 | 0 | 20 | 0 | 0 | 55 | 0 | 8 | 0 | 25 | 16 | 5 | 0 | 9 | 5 | 17 | 0 | 16 | 0 | 5 | 0 | 2 | 25 | 236 | 7 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 395 | 0 | 420 | 0 | 67 |  | 559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 600 | 222 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 250 | 872 | 0 | 0 |  | 4596 | 3241 | 7837 | 2191 | 559 | 1728 | 0 | 458 | 2707 | 76 | 0 | 33 | 84 | 1 | 0 | 0 | 89.31
8:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 402 | 0 |  | 0 | 450 | 0 | 63 | 82 | 0 | 335 | 0 | 0 | 80 | 50 | 16 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 30 | 25 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 8 | 0 | 25 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 300 | 0 | 161 | 80 | 0 | 45 | 45 | 0 | 51 | 0 | 0 | 8 | 13 | 8 | 0 | 9 | 98 | 75 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 110 | 0 | 62 | 78 | 0 | 0 | 20 | 0 | 10 | 320 | 16 | 0 | 0 | 50 | 0 | 0 | 56 | 0 | 17 | 2 | 25 | 17 | 6 | 0 | 9 | 17 | 17 | 1 | 16 | 0 | 17 | 0 | 9 | 25 | 245 | 18 | 2 | 0 | 17 | 0 | 0 | 3 | 0 | 0 | 0 | 17 | 0 | 404 | 0 | 417 | 0 | 65 |  | 660 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 35 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 622 | 220 | 0 | 17 | 0 | 12 | 0 | 0 | 0 | 0 | 3 | 250 | 932 | 14 | 0 |  | 4987 | 3581 | 8568 | 2189 | 660 | 1873 | 0 | 799 | 2795 | 76 | 0 | 41 | 98 | 37 | 0 | 364.81 | 89.31
9:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 402 | 0 |  | 0 | 450 | 0 | 76 | 82 | 0 | 335 | 0 | 0 | 83 | 58 | 16 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 33 | 25 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 40 | 0 | 25 | 0 | 6 | 11 | 1 | 0 | 0 | 0 | 320 | 0 | 160 | 132 | 0 | 45 | 52 | 0 | 51 | 0 | 6 | 8 | 10 | 8 | 0 | 12 | 100 | 65 | 0 | 0 | 1 | 43 | 30 | 0 | 0 | 110 | 0 | 62 | 78 | 0 | 0 | 20 | 0 | 10 | 315 | 16 | 0 | 0 | 81 | 0 | 0 | 56 | 0 | 17 | 9 | 25 | 17 | 6 | 0 | 9 | 17 | 17 | 2 | 16 | 4 | 17 | 0 | 9 | 25 | 270 | 20 | 0 | 0 | 17 | 0 | 0 | 10 | 0 | 0 | 0 | 17 | 0 | 412 | 0 | 418 | 0 | 75 |  | 642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 35 | 0 | 0 | 0 | 6 | 0 | 2 | 0 | 622 | 220 | 0 | 17 | 1 | 32 | 0 | 0 | 0 | 0 | 7 | 250 | 949 | 37 | 0 |  | 5212 | 3630 | 8842 | 2227 | 642 | 1936 | 0 | 860 | 2821 | 76 | 0 | 79 | 100 | 101 | 0 | 437.39 | 89.3
10:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 404 | 0 |  | 0 | 450 | 0 | 85 | 82 | 0 | 335 | 0 | 0 | 76 | 58 | 16 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 33 | 25 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 54 | 0 | 25 | 0 | 6 | 13 | 1 | 0 | 0 | 0 | 295 | 0 | 160 | 142 | 0 | 45 | 50 | 0 | 51 | 0 | 25 | 8 | 10 | 8 | 0 | 12 | 100 | 33 | 0 | 0 | 1 | 43 | 30 | 0 | 0 | 80 | 0 | 59 | 81 | 0 | 0 | 20 | 0 | 10 | 285 | 16 | 0 | 0 | 81 | 0 | 0 | 58 | 0 | 35 | 17 | 25 | 17 | 6 | 0 | 9 | 17 | 28 | 3 | 49 | 17 | 17 | 0 | 9 | 25 | 340 | 33 | 0 | 0 | 17 | 0 | 0 | 19 | 0 | 0 | 0 | 17 | 0 | 440 | 0 | 419 | 0 | 70 |  | 642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 72 | 0 | 0 | 0 | 6 | 0 | 4 | 0 | 622 | 220 | 0 | 17 | 3 | 62 | 0 | 0 | 0 | 0 | 13 | 250 | 1072 | 79 | 0 |  | 5344 | 3866 | 9210 | 2241 | 642 | 1876 | 0 | 989 | 2973 | 76 | 0 | 112 | 100 | 201 | 0 | 133.7 | 89.29
11:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 416 | 0 |  | 0 | 450 | 0 | 85 | 82 | 7 | 332 | 0 | 0 | 83 | 58 | 16 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 33 | 25 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 20 | 0 | 0 | 0 |  | 0 | 46 | 0 | 25 | 0 | 6 | 16 | 1 | 0 | 0 | 0 | 300 | 0 | 108 | 117 | 0 | 38 | 52 | 0 | 51 | 0 | 25 | 8 | 13 | 8 | 0 | 12 | 110 | 33 | 0 | 0 | 2 | 43 | 30 | 0 | 0 | 80 | 0 | 59 | 81 | 0 | 0 | 20 | 0 | 10 | 300 | 16 | 0 | 0 | 81 | 0 | 0 | 58 | 0 | 45 | 20 | 25 | 17 | 5 | 0 | 9 | 17 | 28 | 4 | 49 | 17 | 17 | 0 | 9 | 25 | 400 | 35 | 0 | 17 | 17 | 0 | 0 | 27 | 0 | 0 | 0 | 17 | 0 | 447 | 0 | 419 | 0 | 70 |  | 669 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 3 | 10 | 0 | 135 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 25 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 392 | 93 | 0 | 0 | 0 | 6 | 0 | 5 | 0 | 622 | 220 | 0 | 17 | 4 | 76 | 0 | 0 | 0 | 0 | 26 | 250 | 1065 | 120 | 0 |  | 5434 | 3972 | 9406 | 2275 | 669 | 1851 | 0 | 1051 | 2973 | 76 | 0 | 117 | 110 | 284 | 0 | 113.645 | 89.28
12:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 418 | 0 |  | 0 | 450 | 0 | 87 | 82 | 15 | 332 | 0 | 0 | 85 | 66 | 16 | 25 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 18 | 22 | 33 | 25 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 31 | 0 | 0 | 0 |  | 0 | 48 | 0 | 25 | 0 | 6 | 15 | 1 | 0 | 0 | 0 | 310 | 0 | 0 | 117 | 0 | 44 | 52 | 0 | 51 | 0 | 25 | 8 | 13 | 8 | 0 | 14 | 110 | 33 | 0 | 0 | 2 | 43 | 30 | 0 | 0 | 112 | 0 | 59 | 81 | 0 | 0 | 20 | 0 | 10 | 315 | 16 | 0 | 0 | 80 | 0 | 0 | 58 | 0 | 53 | 20 | 25 | 17 | 6 | 0 | 9 | 17 | 28 | 4 | 49 | 17 | 17 | 0 | 9 | 25 | 360 | 39 | 0 | 35 | 17 | 0 | 0 | 29 | 0 | 0 | 0 | 17 | 0 | 447 | 0 | 419 | 0 | 70 |  | 765 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 12 | 12 | 0 | 135 | 17 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 28 | 25 | 15 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 93 | 0 | 0 | 0 | 6 | 0 | 5 | 0 | 622 | 220 | 0 | 17 | 1 | 77 | 0 | 0 | 0 | 0 | 28 | 250 | 1271 | 137 | 0 |  | 5441 | 4356 | 9797 | 2164 | 765 | 1883 | 0 | 1118 | 3179 | 76 | 0 | 199 | 110 | 303 | 0 | 170 | 89.27
13:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 420 | 0 |  | 0 | 450 | 0 | 93 | 82 | 15 | 332 | 0 | 0 | 86 | 66 | 16 | 25 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 18 | 10 | 33 | 30 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 30 | 0 | 0 | 0 |  | 0 | 58 | 51 | 25 | 0 | 6 | 15 | 2 | 0 | 0 | 0 | 315 | 0 | 0 | 160 | 0 | 45 | 53 | 0 | 51 | 0 | 25 | 8 | 13 | 8 | 0 | 16 | 118 | 30 | 0 | 0 | 2 | 43 | 30 | 0 | 0 | 117 | 0 | 59 | 82 | 0 | 0 | 20 | 0 | 10 | 315 | 16 | 0 | 0 | 72 | 0 | 0 | 67 | 0 | 53 | 19 | 25 | 17 | 6 | 0 | 9 | 17 | 28 | 4 | 52 | 17 | 17 | 0 | 9 | 25 | 360 | 52 | 0 | 0 | 52 | 0 | 13 | 29 | 0 | 0 | 0 | 17 | 0 | 447 | 0 | 419 | 0 | 70 |  | 765 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 11 | 10 | 0 | 135 | 18 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 28 | 34 | 26 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 93 | 0 | 0 | 0 | 6 | 0 | 5 | 0 | 622 | 220 | 0 | 17 | 4 | 73 | 0 | 0 | 0 | 0 | 26 | 250 | 1365 | 132 | 0 |  | 5596 | 4449 | 10045 | 2163 | 765 | 1924 | 0 | 1164 | 3273 | 76 | 0 | 268 | 118 | 294 | 0 | 148 | 89.26
14:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 402 | 0 |  | 0 | 450 | 0 | 93 | 82 | 15 | 330 | 0 | 0 | 92 | 66 | 16 | 25 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 18 | 22 | 33 | 30 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 31 | 0 | 0 | 0 |  | 2 | 60 | 51 | 25 | 0 | 6 | 11 | 2 | 0 | 0 | 0 | 280 | 0 | 128 | 103 | 0 | 45 | 54 | 0 | 51 | 0 | 25 | 8 | 13 | 8 | 14 | 15 | 110 | 27 | 0 | 0 | 1 | 43 | 30 | 0 | 0 | 40 | 0 | 58 | 82 | 0 | 0 | 20 | 0 | 10 | 295 | 16 | 0 | 0 | 55 | 0 | 0 | 58 | 0 | 53 | 17 | 25 | 17 | 6 | 0 | 9 | 17 | 28 | 3 | 52 | 17 | 31 | 0 | 9 | 25 | 400 | 53 | 0 | 0 | 111 | 0 | 17 | 26 | 0 | 0 | 0 | 17 | 0 | 447 | 0 | 418 | 0 | 70 |  | 765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 10 | 0 | 100 | 17 | 0 | 0 | 0 | 0 | 0 | 14 | 50 | 28 | 34 | 34 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 93 | 0 | 0 | 0 | 8 | 0 | 5 | 0 | 590 | 180 | 0 | 17 | 3 | 63 | 0 | 0 | 0 | 0 | 24 | 220 | 1365 | 111 | 0 |  | 5620 | 4266 | 9886 | 2259 | 765 | 1715 | 0 | 1210 | 3210 | 76 | 0 | 288 | 110 | 253 | 0 | 90 | 89.28
15:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 397 | 0 |  | 0 | 450 | 0 | 92 | 83 | 15 | 280 | 0 | 0 | 92 | 66 | 16 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 33 | 28 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 37 | 0 | 0 | 0 |  | 6 | 72 | 51 | 25 | 0 | 6 | 13 | 0 | 0 | 0 | 0 | 280 | 0 | 141 | 16 | 0 | 41 | 52 | 0 | 51 | 0 | 25 | 8 | 13 | 8 | 25 | 17 | 106 | 28 | 0 | 0 | 1 | 43 | 30 | 0 | 0 | 40 | 0 | 40 | 82 | 0 | 0 | 20 | 0 | 10 | 280 | 16 | 0 | 0 | 47 | 0 | 0 | 58 | 0 | 39 | 14 | 25 | 17 | 6 | 0 | 9 | 17 | 28 | 2 | 52 | 17 | 23 | 0 | 19 | 25 | 400 | 53 | 0 | 0 | 121 | 0 | 17 | 18 | 1 | 0 | 0 | 17 | 0 | 439 | 0 | 333 | 0 | 35 |  | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 10 | 0 | 135 | 13 | 0 | 0 | 0 | 0 | 0 | 15 | 50 | 28 | 34 | 34 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 93 | 0 | 0 | 0 | 11 | 0 | 4 | 0 | 520 | 220 | 0 | 17 | 2 | 49 | 0 | 0 | 0 | 0 | 16 | 220 | 1313 | 76 | 0 |  | 5316 | 4276 | 9592 | 2250 | 899 | 1592 | 0 | 1191 | 2995 | 76 | 0 | 301 | 106 | 182 | 0 | 74 | 89.24
16:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 370 | 0 |  | 0 | 400 | 0 | 60 | 54 | 15 | 280 | 0 | 0 | 57 | 66 | 16 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 33 | 28 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 51 | 0 | 0 | 0 |  | 6 | 65 | 51 | 36 | 0 | 6 | 13 | 4 | 0 | 0 | 0 | 275 | 0 | 158 | 16 | 0 | 43 | 50 | 0 | 43 | 0 | 25 | 8 | 13 | 8 | 29 | 17 | 110 | 32 | 0 | 0 | 0 | 43 | 22 | 0 | 0 | 70 | 0 | 40 | 82 | 0 | 0 | 20 | 0 | 10 | 280 | 16 | 0 | 0 | 47 | 0 | 0 | 58 | 0 | 36 | 8 | 25 | 17 | 6 | 0 | 9 | 17 | 28 | 1 | 52 | 0 | 22 | 0 | 47 | 25 | 400 | 53 | 0 | 0 | 116 | 0 | 17 | 10 | 18 | 0 | 0 | 17 | 0 | 370 | 0 | 216 | 0 | 70 |  | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 18 | 8 | 135 | 13 | 0 | 0 | 0 | 0 | 0 | 15 | 50 | 14 | 16 | 24 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 70 | 0 | 8 | 0 | 13 | 0 | 2 | 35 | 480 | 220 | 0 | 17 | 1 | 27 | 17 | 0 | 0 | 0 | 8 | 208 | 1269 | 35 | 0 |  | 5055 | 4109 | 9164 | 2251 | 897 | 1588 | 0 | 1140 | 2713 | 76 | 0 | 297 | 110 | 92 | 0 | 0 | 89.23
17:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 371 | 0 |  | 0 | 370 | 0 | 50 | 34 | 15 | 280 | 0 | 0 | 50 | 66 | 39 | 25 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 18 | 22 | 33 | 28 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 85 | 0 | 0 | 0 |  | 6 | 65 | 51 | 36 | 5 | 16 | 15 | 10 | 0 | 0 | 0 | 305 | 0 | 155 | 16 | 0 | 44 | 52 | 0 | 51 | 0 | 25 | 8 | 13 | 8 | 33 | 17 | 112 | 34 | 0 | 0 | 0 | 46 | 40 | 0 | 0 | 130 | 0 | 40 | 87 | 0 | 0 | 20 | 0 | 10 | 300 | 16 | 0 | 0 | 50 | 0 | 0 | 58 | 0 | 36 | 2 | 25 | 17 | 5 | 0 | 9 | 34 | 17 | 0 | 102 | 0 | 17 | 0 | 47 | 25 | 400 | 53 | 0 | 0 | 17 | 0 | 17 | 2 | 23 | 28 | 0 | 17 | 0 | 351 | 0 | 149 | 0 | 65 |  | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 22 | 8 | 135 | 13 | 0 | 0 | 0 | 0 | 32 | 15 | 50 | 14 | 16 | 24 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 70 | 0 | 35 | 0 | 33 | 0 | 1 | 35 | 490 | 220 | 0 | 25 | 0 | 7 | 17 | 0 | 0 | 0 | 2 | 200 | 1268 | 9 | 0 |  | 5107 | 4175 | 9282 | 2343 | 897 | 1655 | 0 | 1173 | 2628 | 76 | 0 | 375 | 112 | 23 | 0 | 0 | 89.22
18:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 401 | 0 |  | 0 | 450 | 0 | 61 | 45 | 15 | 330 | 0 | 0 | 70 | 76 | 98 | 25 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 18 | 12 | 33 | 28 | 17 | 0 | 46 | 30 | 0 | 0 | 15 | 164 | 0 | 0 | 0 |  | 6 | 66 | 51 | 25 | 5 | 19 | 16 | 13 | 0 | 0 | 0 | 350 | 0 | 155 | 16 | 0 | 44 | 52 | 0 | 51 | 0 | 25 | 8 | 13 | 8 | 33 | 17 | 112 | 35 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 163 | 0 | 59 | 84 | 0 | 0 | 20 | 0 | 10 | 305 | 16 | 0 | 0 | 112 | 0 | 0 | 68 | 0 | 36 | 0 | 25 | 17 | 10 | 0 | 9 | 88 | 17 | 0 | 105 | 0 | 17 | 0 | 73 | 25 | 380 | 53 | 0 | 0 | 17 | 0 | 17 | 0 | 18 | 25 | 0 | 17 | 0 | 353 | 1 | 150 | 0 | 71 |  | 830 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 46 | 28 | 8 | 135 | 18 | 16 | 0 | 0 | 0 | 34 | 15 | 89 | 14 | 34 | 25 | 8 | 20 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 84 | 0 | 35 | 0 | 40 | 0 | 0 | 35 | 530 | 222 | 0 | 54 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 250 | 1398 | 0 | 0 |  | 5724 | 4564 | 10288 | 2535 | 830 | 1786 | 0 | 1583 | 2851 | 76 | 0 | 514 | 112 | 0 | 1 | 50 | 89.21
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 401 | 0 |  | 0 | 450 | 0 | 96 | 82 | 15 | 336 | 0 | 0 | 93 | 91 | 98 | 25 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 18 | 22 | 33 | 28 | 17 | 0 | 46 | 30 | 0 | 0 | 17 | 206 | 0 | 0 | 0 |  | 6 | 66 | 51 | 25 | 5 | 19 | 17 | 20 | 0 | 0 | 0 | 305 | 0 | 157 | 8 | 0 | 44 | 44 | 0 | 51 | 0 | 25 | 8 | 13 | 8 | 33 | 17 | 108 | 34 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 163 | 0 | 63 | 84 | 0 | 0 | 20 | 0 | 10 | 300 | 16 | 0 | 0 | 130 | 0 | 0 | 68 | 0 | 36 | 0 | 25 | 17 | 8 | 0 | 9 | 88 | 17 | 0 | 105 | 0 | 17 | 0 | 78 | 25 | 360 | 53 | 0 | 17 | 17 | 0 | 17 | 0 | 18 | 17 | 0 | 17 | 0 | 400 | 1 | 271 | 0 | 49 |  | 794 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 32 | 20 | 8 | 135 | 18 | 16 | 0 | 0 | 0 | 34 | 15 | 91 | 21 | 34 | 32 | 8 | 25 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 93 | 0 | 35 | 0 | 41 | 0 | 0 | 35 | 622 | 220 | 0 | 54 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 250 | 1470 | 0 | 0 |  | 6011 | 4702 | 10713 | 2537 | 794 | 1748 | 0 | 1760 | 3183 | 76 | 0 | 506 | 108 | 0 | 1 | 0 | 89.18
19:30 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 400 | 0 |  | 0 | 450 | 0 | 100 | 82 | 15 | 335 | 0 | 0 | 93 | 91 | 98 | 25 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 18 | 22 | 33 | 28 | 17 | 0 | 46 | 30 | 0 | 0 | 17 | 213 | 0 | 0 | 0 |  | 6 | 66 | 51 | 25 | 5 | 19 | 17 | 16 | 0 | 0 | 0 | 305 | 0 | 157 | 8 | 0 | 44 | 40 | 0 | 51 | 0 | 25 | 8 | 13 | 8 | 33 | 17 | 108 | 34 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 163 | 0 | 63 | 84 | 0 | 0 | 20 | 0 | 10 | 301 | 16 | 0 | 0 | 130 | 0 | 0 | 68 | 0 | 36 | 0 | 25 | 17 | 15 | 0 | 9 | 88 | 17 | 0 | 107 | 0 | 17 | 0 | 78 | 25 | 330 | 53 | 0 | 17 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 350 | 0 | 270 | 0 | 30 |  | 793 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 28 | 20 | 0 | 135 | 19 | 16 | 0 | 0 | 0 | 34 | 15 | 91 | 21 | 34 | 32 | 8 | 30 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 93 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 622 | 220 | 0 | 54 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 250 | 1466 | 0 | 0 |  | 5903 | 4686 | 10589 | 2512 | 793 | 1724 | 0 | 1741 | 3128 | 76 | 0 | 507 | 108 | 0 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 401 | 0 |  | 0 | 450 | 0 | 100 | 82 | 15 | 335 | 0 | 0 | 92 | 91 | 98 | 25 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 18 | 22 | 33 | 28 | 17 | 0 | 46 | 30 | 0 | 0 | 17 | 219 | 0 | 0 | 0 |  | 6 | 66 | 51 | 25 | 6 | 19 | 16 | 16 | 0 | 0 | 0 | 305 | 0 | 158 | 8 | 0 | 44 | 40 | 0 | 51 | 0 | 25 | 8 | 13 | 8 | 33 | 17 | 108 | 44 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 163 | 0 | 60 | 84 | 0 | 0 | 20 | 0 | 10 | 280 | 16 | 0 | 0 | 130 | 0 | 0 | 68 | 0 | 36 | 0 | 25 | 17 | 18 | 0 | 9 | 88 | 17 | 0 | 107 | 0 | 17 | 0 | 78 | 25 | 310 | 54 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 363 | 0 | 270 | 0 | 40 |  | 793 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 28 | 20 | 0 | 135 | 19 | 16 | 0 | 0 | 0 | 34 | 16 | 91 | 21 | 34 | 34 | 8 | 25 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 93 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 622 | 220 | 0 | 54 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 250 | 1463 | 0 | 0 |  | 5886 | 4679 | 10565 | 2506 | 793 | 1712 | 0 | 1727 | 3138 | 76 | 0 | 505 | 108 | 0 | 0 | 0 | 89.19
21:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 373 | 0 |  | 0 | 450 | 0 | 96 | 82 | 15 | 300 | 0 | 0 | 53 | 91 | 32 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 33 | 28 | 17 | 0 | 46 | 30 | 0 | 0 | 17 | 216 | 0 | 0 | 0 |  | 6 | 66 | 51 | 25 | 6 | 19 | 16 | 13 | 0 | 0 | 0 | 280 | 0 | 157 | 8 | 0 | 44 | 40 | 0 | 51 | 0 | 25 | 8 | 13 | 8 | 33 | 17 | 104 | 78 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 130 | 0 | 60 | 84 | 0 | 0 | 20 | 0 | 10 | 305 | 16 | 0 | 0 | 130 | 0 | 0 | 68 | 0 | 36 | 0 | 25 | 17 | 18 | 0 | 9 | 88 | 17 | 0 | 107 | 0 | 17 | 0 | 78 | 25 | 310 | 54 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 324 | 1 | 271 | 0 | 68 |  | 793 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 23 | 20 | 0 | 135 | 20 | 16 | 0 | 0 | 0 | 34 | 16 | 91 | 21 | 25 | 32 | 8 | 25 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 93 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 622 | 220 | 0 | 17 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 250 | 1472 | 0 | 0 |  | 5643 | 4632 | 10275 | 2448 | 793 | 1742 | 0 | 1570 | 3109 | 76 | 0 | 432 | 104 | 0 | 1 | 0 | 89.18
22:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 366 | 0 |  | 0 | 450 | 0 | 70 | 82 | 15 | 300 | 0 | 0 | 25 | 91 | 16 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 33 | 28 | 17 | 0 | 46 | 30 | 0 | 0 | 17 | 213 | 0 | 0 | 0 |  | 6 | 66 | 51 | 25 | 0 | 19 | 16 | 16 | 0 | 0 | 0 | 280 | 0 | 159 | 8 | 0 | 44 | 40 | 0 | 51 | 0 | 25 | 8 | 13 | 8 | 33 | 17 | 100 | 74 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 130 | 0 | 40 | 84 | 0 | 0 | 20 | 0 | 10 | 290 | 16 | 0 | 0 | 130 | 0 | 0 | 9 | 0 | 19 | 0 | 25 | 17 | 20 | 0 | 9 | 70 | 17 | 0 | 107 | 0 | 17 | 0 | 69 | 25 | 280 | 54 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 320 | 0 | 272 | 0 | 63 |  | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 20 | 0 | 135 | 20 | 16 | 0 | 0 | 0 | 34 | 15 | 91 | 21 | 0 | 32 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 93 | 0 | 35 | 0 | 6 | 0 | 0 | 35 | 570 | 220 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 250 | 1436 | 0 | 0 |  | 5371 | 4502 | 9873 | 2383 | 899 | 1728 | 0 | 1279 | 3018 | 76 | 0 | 390 | 100 | 0 | 0 | 0 | 89.17
23:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 366 | 0 |  | 0 | 400 | 0 | 13 | 35 | 15 | 300 | 0 | 0 | 18 | 66 | 16 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 33 | 28 | 17 | 0 | 46 | 30 | 0 | 0 | 17 | 214 | 0 | 0 | 0 |  | 6 | 66 | 51 | 25 | 0 | 19 | 13 | 17 | 0 | 0 | 0 | 280 | 0 | 159 | 0 | 0 | 44 | 40 | 0 | 51 | 0 | 16 | 8 | 13 | 8 | 33 | 17 | 94 | 71 | 0 | 0 | 0 | 43 | 41 | 0 | 0 | 130 | 0 | 40 | 84 | 0 | 0 | 20 | 0 | 10 | 280 | 16 | 0 | 0 | 45 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 17 | 20 | 0 | 9 | 70 | 17 | 0 | 16 | 0 | 17 | 0 | 50 | 25 | 275 | 54 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 285 | 0 | 271 | 0 | 63 |  | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 20 | 0 | 80 | 19 | 16 | 0 | 0 | 0 | 34 | 15 | 91 | 0 | 0 | 32 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 93 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 550 | 220 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 250 | 1291 | 0 | 0 |  | 4907 | 4185 | 9092 | 2319 | 899 | 1661 | 0 | 851 | 2817 | 76 | 0 | 375 | 94 | 0 | 0 | 0 | 89.16
24:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 366 | 0 |  | 0 | 400 | 0 | 9 | 32 | 15 | 300 | 0 | 0 | 17 | 66 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 26 | 28 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 214 | 0 | 0 | 0 |  | 6 | 64 | 51 | 25 | 0 | 6 | 13 | 20 | 0 | 0 | 0 | 280 | 0 | 159 | 0 | 0 | 44 | 40 | 0 | 51 | 0 | 16 | 8 | 13 | 8 | 33 | 17 | 96 | 73 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 130 | 0 | 40 | 84 | 0 | 0 | 20 | 0 | 10 | 280 | 16 | 0 | 0 | 45 | 0 | 0 | 9 | 0 | 17 | 0 | 24 | 17 | 20 | 0 | 9 | 17 | 17 | 0 | 16 | 0 | 17 | 0 | 47 | 25 | 275 | 54 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 285 | 1 | 270 | 0 | 46 |  | 728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 20 | 0 | 80 | 18 | 16 | 0 | 0 | 0 | 34 | 15 | 44 | 0 | 0 | 24 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 93 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 550 | 220 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 1181 | 0 | 0 |  | 4761 | 3836 | 8597 | 2313 | 728 | 1657 | 0 | 708 | 2706 | 76 | 0 | 312 | 96 | 0 | 1 | 0 | 89.15
KWH | 0 | 0 | 0 | 4441500 | 0 | 289590 | 0 | 9259200 | 0 |  | 0 | 9604500 | 0 | 1249920 | 1108942 | 220680 | 7715667 | 0 | 0 | 1167360 | 1196064 | 609120 | 374483 | 0 | 0 | 0 | 50040 | 66833 | 65452 | 0 | 432000 | 488160 | 785520 | 615400 | 205440 | 0 | 1104720 | 736000 | 0 | 0 | 205619 | 1517352 | 0 | 0 | 0 |  | 71040 | 917472 | 592568 | 424920 | 30720 | 204480 | 295008 | 337920 | 0 | 0 | 0 | 7710300 | 0 | 3436000 | 1037090 | 0 | 1049256 | 1082400 | 0 | 1247293 | 0 | 358032 | 151757 | 309996 | 180540 | 314700 | 350350 | 2364480 | 1304640 | 0 | 0 | 9200 | 1017000 | 764760 | 0 | 0 | 3123818 | 0 | 1361280 | 1944000 | 0 | 0 | 488000 | 0 | 250020 | 7326000 | 397392 | 0 | 0 | 1427673 | 0 | 0 | 964800 | 0 | 616896 | 129060 | 474240 | 341760 | 197381 | 0 | 183600 | 726720 | 402290 | 23039 | 1021200 | 123811 | 359630 | 0 | 677880 | 481920 | 7417300 | 825600 | 2030 | 96480 | 691255 | 0 | 236880 | 171363 | 82560 | 146160 | 0 | 322836 | 0 | 8645453 | 50400 | 8523636 | 0 | 1494091 |  | 16301090 | 0 | 0 | 0 | 145920 | 0 | 0 | 0 | 251520 | 218240 | 30375 | 3147000 | 388500 | 108960 | 0 | 0 | 0 | 266592 | 159594 | 867344 | 334800 | 422253 | 308898 | 97286 | 73774 | 0 | 0 | 144000 | 0 | 0 | 4131000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8852909 | 1352160 | 0 | 259584 | 0 | 271929 | 0 | 32420 | 254592 | 14597300 | 5328682 | 0 | 427200 | 24960 | 484560 | 342912 | 0 | 0 | 0 | 158263 | 5698200 | 28722909 | 743380 | 0 |  | 120819938 | 94949106 | 215769044 | 54942321 | 16301090 | 42306813 | 0 | 20920457 | 70318498 | 1840720 | 0 | 4945990 | 2364480 | 1778275 | 50400 | 0
Fuel Cost | 0 | 0 | 0 | 19764675 | 0 | 1106233.8 | 0 | 26666496 | 0 |  | 0 | 30542310 | 0 | 25135891.2 | 19783525.28 | 3811143.6 | 23532784.35 | 0 | 0 | 22961971.2 | 24088728.96 | 11219990.4 | 6763162.98 | 0 | 0 | 0 | 903722.4 | 1125467.72 | 1045268.44 | 0 | 324000 | 0 | 0 | 0 | 3679430.4 | 0 | 0 | 0 | 0 | 0 | 3705254.38 | 4840352.88 | 0 | 0 | 0 |  | 1247462.4 | 16156681.92 | 10612892.88 | 7210892.4 | 466636.8 | 3175574.4 | 1097429.76 | 0 | 0 | 0 | 0 | 21511737 | 0 | 11407520 | 3474251.5 | 0 | 3535992.72 | 4740912 | 0 | 5001644.93 | 0 | 6412353.12 | 2730108.43 | 1153185.12 | 135405 | 1170684 | 262762.5 | 15510988.8 | 4057430.4 | 0 | 0 | 146648 | 3966300 | 2852554.8 | 0 | 0 | 10683457.56 | 0 | 7555104 | 10147680 | 0 | 0 | 3211040 | 0 | 1000080 | 22637340 | 298044 | 0 | 0 | 29481447.45 | 0 | 0 | 14915808 | 0 | 11671672.32 | 1508711.4 | 7763308.8 | 5502336 | 3051510.26 | 0 | 2719116 | 13080960 | 6979731.5 | 358486.84 | 18933048 | 2441552.92 | 5329716.6 | 0 | 10730840.4 | 7942041.6 | 19730018 | 15166272 | 29333.5 | 1742428.8 | 10147623.4 | 0 | 4143031.2 | 2047787.85 | 1366368 | 2480335.2 | 0 | 5791677.84 | 0 | 59912989.29 | 0 | 0 | 0 | 0 |  | 44827997.5 | 0 | 0 | 0 | 2486476.8 | 0 | 0 | 0 | 4731091.2 | 4105094.4 | 540675 | 9944520 | 1841490 | 2069150.4 | 0 | 0 | 0 | 4774662.72 | 2928549.9 | 14580052.64 | 6652476 | 7984804.23 | 5532363.18 | 1720016.48 | 1321292.34 | 0 | 0 | 109008 | 0 | 0 | 35030880 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25850494.28 | 26123731.2 | 0 | 4986608.64 | 0 | 4524898.56 | 0 | 358241 | 4266961.92 | 84372394 | 16572201.02 | 0 | 6809568 | 282297.6 | 5683888.8 | 5805500.16 | 0 | 0 | 0 | 0 | 42451590 | 218006879.31 | 0 | 0 |  | 679539356.6 | 597275855.28 | 1276815211.88 | 167127043.53 | 44827997.5 | 133598095.09 | 0 | 377394256.83 | 439774732.6 | 0 | 0 | 88166702.54 | 15510988.8 | 10415394.99 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 418 | 0 |  | 0 | 450 | 0 | 87 | 82 | 15 | 332 | 0 | 0 | 85 | 66 | 16 | 25 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 18 | 22 | 33 | 25 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 31 | 0 | 0 | 0 |  | 0 | 48 | 0 | 25 | 0 | 6 | 15 | 1 | 0 | 0 | 0 | 310 | 0 | 0 | 117 | 0 | 44 | 52 | 0 | 51 | 0 | 25 | 8 | 13 | 8 | 0 | 14 | 110 | 33 | 0 | 0 | 2 | 43 | 30 | 0 | 0 | 112 | 0 | 59 | 81 | 0 | 0 | 20 | 0 | 10 | 315 | 16 | 0 | 0 | 80 | 0 | 0 | 58 | 0 | 53 | 20 | 25 | 17 | 6 | 0 | 9 | 17 | 28 | 4 | 49 | 17 | 17 | 0 | 9 | 25 | 360 | 39 | 0 | 35 | 17 | 0 | 0 | 29 | 0 | 0 | 0 | 17 | 0 | 447 | 0 | 419 | 0 | 70 |  | 765 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 12 | 12 | 0 | 135 | 17 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 28 | 25 | 15 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 93 | 0 | 0 | 0 | 6 | 0 | 5 | 0 | 622 | 220 | 0 | 17 | 1 | 77 | 0 | 0 | 0 | 0 | 28 | 250 | 1271 | 137 | 0 |  | 9797 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 401 | 0 |  | 0 | 450 | 0 | 96 | 82 | 15 | 336 | 0 | 0 | 93 | 91 | 98 | 25 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 18 | 22 | 33 | 28 | 17 | 0 | 46 | 30 | 0 | 0 | 17 | 206 | 0 | 0 | 0 | 0 | 6 | 66 | 51 | 25 | 5 | 19 | 17 | 20 | 0 | 0 | 0 | 305 | 0 | 157 | 8 | 0 | 44 | 44 | 0 | 51 | 0 | 25 | 8 | 13 | 8 | 33 | 17 | 108 | 34 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 163 | 0 | 63 | 84 | 0 | 0 | 20 | 0 | 10 | 300 | 16 | 0 | 0 | 130 | 0 | 0 | 68 | 0 | 36 | 0 | 25 | 17 | 8 | 0 | 9 | 88 | 17 | 0 | 105 | 0 | 17 | 0 | 78 | 25 | 360 | 53 | 0 | 17 | 17 | 0 | 17 | 0 | 18 | 17 | 0 | 17 | 0 | 400 | 1 | 271 | 0 | 49 |  | 794 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 32 | 20 | 8 | 135 | 18 | 16 | 0 | 0 | 0 | 34 | 15 | 91 | 21 | 34 | 32 | 8 | 25 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 93 | 0 | 35 | 0 | 41 | 0 | 0 | 35 | 622 | 220 | 0 | 54 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 250 | 1470 | 0 | 0 |  | 10713 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 412 | 0 |  | 0 | 450 | 0 | 100 | 85 | 15 | 335 | 0 | 0 | 92 | 92 | 100 | 25 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 18 | 22 | 33 | 33 | 17 | 0 | 46 | 30 | 0 | 0 | 17 | 220 | 0 | 0 | 0 |  | 6 | 72 | 51 | 25 | 0 | 19 | 18 | 10 | 0 | 0 | 0 | 310 | 0 | 160 | 0 | 0 | 45 | 45 | 0 | 51 | 0 | 25 | 8 | 13 | 10 | 33 | 18 | 141 | 40 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 163 | 0 | 60 | 84 | 0 | 0 | 20 | 0 | 10 | 310 | 16 | 0 | 0 | 130 | 0 | 0 | 68 | 0 | 36 | 0 | 25 | 17 | 20 | 0 | 9 | 105 | 17 | 0 | 100 | 0 | 17 | 0 | 78 | 25 | 400 | 72 | 0 | 17 | 17 | 0 | 17 | 0 | 18 | 17 | 0 | 17 | 0 | 400 | 10 | 0 | 0 | 100 |  | 922 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 40 | 20 | 16 | 135 | 20 | 16 | 0 | 0 | 0 | 32 | 16 | 92 | 28 | 42 | 34 | 8 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 93 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 622 | 220 | 0 | 54 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 200 | 1400 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 412 | 0 | 0 | 0 | 450 | 0 | 100 | 85 | 15 | 335 | 0 | 0 | 92 | 75 | 32 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 30 | 33 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 220 |  | 0 | 0 | 0 | 2 | 60 | 51 | 25 | 0 | 6 | 18 | 5 | 0 | 0 | 0 | 310 | 0 | 160 | 0 | 0 | 50 | 45 | 0 | 51 | 0 | 25 | 8 | 13 | 10 | 33 | 11 | 128 | 35 | 0 | 0 | 1.6 | 43 | 40 | 0 | 0 | 163 | 0 | 60 | 84 | 0 | 0 | 20 | 0 | 10 | 310 | 16 | 0 | 0 | 80 | 0 | 0 | 56 | 0 | 54 | 20 | 25 | 17 | 6 | 0 | 9 | 17 | 28 | 5 | 50 | 0 | 17 | 0 | 9 | 25 | 250 | 53 | 50 | 35 | 17 | 0 | 17 | 35 | 0 | 0 | 0 | 17 | 0 | 400 | 10 | 450 | 0 | 100 |  | 922 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 15 | 20 | 0 | 135 | 20 | 0 | 0 | 0 | 0 | 32 | 0 | 50 | 28 | 25 | 0 | 8 | 25 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 93 | 0 | 0 | 0 | 6 | 0 | 8 | 0 | 622 | 220 |  | 17 | 6 | 100 | 0 | 0 |  | 0 | 30 | 200 | 1400 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 388 | 0 | 0 | 0 | 450 | 0 | 31 | 70 | 0 | 281 | 0 | 0 | 47 | 50 | 16 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 26 | 17 | 8 | 0 | 46 | 30 | 0 | 0 | 8 | 216 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 25 | 0 | 6 | 13 | 5 | 0 | 0 | 0 | 305 | 0 | 161 | 0 | 0 | 44 | 20 | 0 | 51 | 0 | 0 | 8 | 13 | 8 | 33 | 17 | 100 | 72 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 163 | 0 | 58 | 79 | 0 | 0 | 20 | 0 | 10 | 325 | 16 | 0 | 0 | 47 | 0 | 0 | 56 | 0 | 18 | 2 | 25 | 17 | 6 | 0 | 9 | 17 | 17 | 0 | 16 | 0 | 17 | 0 | 9 | 25 | 240 | 45 | 2 | 0 | 17 | 0 | 0 | 2 | 0 | 0 | 0 | 17 | 0 | 284 | 1 | 271 | 0 | 60 | 0 | 807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 25 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 90 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 622 | 220 | 0 | 17 | 0 | 4 | 0 | 0 | 0 | 0 | 3 | 250 | 1216 | 17 | 0 | 0 |  |  |  | 97249134 | 16301090 | 0 | 70318498 | 25866447 | 2364480 | 1778275 | 50400 | 1840720
[8 empty] | 299430 | [13 empty] | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [14 empty] | 299772 | [10 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 |  | 399747 |  |  |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 | [6 empty] | 399245 |  | 299282 | 399274 |  | 399223 |  | 399630 | 299864 | [11 empty] | 599468 |  |  |  | 230 | [27 empty] | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 | [8 empty] | 599726 | [9 empty] | 97.2491 | 16.3011 | 0 | 70.3185 | 25.8664 | 2.3645 | 1.7783 | 0.0504 | 1.8407
| Minimum Generation |  | 6763 | 5:00
| Highest Generation |  | 10713 | 19:00 | [200 empty] | 215.769
| Day Peak Generation |  | 9797 | 12:00
| Evening Peak Generation |  | 10713 | 19:00 | [200 empty] | 202699852
| HVDC Max Flow |  | 899 | 15:00 | [200 empty] | 202.6999
| HVDC EvPeak Flow |  | 794 | 19:00
| Load factor L.F |  | 83.92% | [166 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-01-24
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2024-01-23 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9797 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6840
Evening Peak Generation : |  |  | 10713 | MW Hour : | 19:00 | Available Max Generation : |  | 10818
E.P. Demand (at gen end) : |  |  | 10713 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 10800
Maximum Generation : |  |  | 10713 | MW Hour : | 19:00 | Reserve(Generation end) |  | 18
Total Gen. (MKWH) : |  |  | 215.769 | System Load Factor : | 83.92% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 328 | MW at | 7:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-01-24
Actual : |  | 89.12 | Ft.(MSL) , | Rule curve : | 98.6 | Ft.( MSL )
Gas Consumed : |  | Total = | 772.04 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 300725138.62
: |  |  | Coal : | 439774732.6 | Oil : | 465560959.37 | Total : | 1206060830.59
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3661.4317 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1000.5536 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1399.9249 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1215.2638 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1000.7249 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 743.4794 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 417.6068 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 347.2366 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 679.152 |  |  | 0 | 0%
Total |  | 0 |  | 10465.3737 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Ashuganj East
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
8:14 | 12:13 | Jashore 132/33kV S/S JH-2(L1) Project Work S/D Due to Tower Piling Project work.
8:14 | 8:39 | Kushtia 132/33kV S/S T2 LT Forced S/D Due to ৩৩ কেভি পাওয়ার কেবল স্থানান্তর, T-3 এর পাওয়ার কেবল ট্রেস্ন নির্মানের জন্য |  |  |  |  | 20.0MW load interrup.
8:15 | - | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) LT Scheduled S/D Due to Redhot maintenance at 33kV feeder. |  |  |  |  | 12.0MW load interrup.
8:15 | 16:15 | Benapole-Jashore 132 kV Ckt-1 Scheduled S/D from Benapole 132/33kV end Due to Annual Maintenance. and from
Jashore 132/33kV end Due to Annual Maintenance. Benapole end.
8:16 | - | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) HT Scheduled S/D Due to Redhot maintenance at 33kV feeder. |  |  |  |  | 12.0MW load interrup.
8:23 | 17:02 | Fenchuganj-Sreemangal 132kV Ckt-1 Scheduled S/D from Sreemongol 132/33kV end Due to None and from
Fenchuganj 230/132/33kV end Due to Due to dead line checking of Fen-Srm -1.
8:27 | - | Haripur-Meghnaghat 230kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to Annual Deadline Checking. and from
Meghnaghat 230/132kV end Due to Annual Maintenance.
8:34 | 16:38 | Aminbazar-Manikgonj PP 132kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to Dead line cheeking.
8:37 | - | Ashuganj-Cumilla(N) 230 kV Ckt-2 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to Disc Cleaning and from
Ashuganj 230/132/33kV end Due to Annual Maintenance work..
- | 8:38 | Kushtia 132/33kV S/S T2 HT is restored.
8:41 | 13:48 | Bheramara(GK) 132/33kV S/S TR-1 LT Scheduled S/D Due to Annual Maintenance work.
8:42 | 13:43 | Bheramara(GK) 132/33kV S/S TR-1 HT Scheduled S/D Due to Annual Maintenance work.
8:47 | 17:17 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Scheduled S/D from Shahjibazar 132/33kV end Due to A/M.
8:48 | - | Chowmuhani-Ramganj 132 kV Ckt-1 Scheduled S/D from Chowmuhani 132/33kV end Due to Due to yearly maintenance and
from Ramganj 132/33kV end Due to Annual Maintenance.
8:53 | 15:26 | Baroirhat-Hathazari 132 kV Ckt-2 Scheduled S/D from Baroirhat 132/33kV end Due to Annual deadline checking.
8:53 | 15:26 | Baroirhat-Hathazari 132 kV Ckt-2 Scheduled S/D from Baroirhat 132/33kV end Due to Annual deadline checking.
8:54 | 15:40 | Goalpara 132/33kV S/S Goalpara-NWPGCL Scheduled S/D Due to Annual Maintenance. works.
8:55 | 14:32 | Sreemongol 132/33kV S/S 132/33kv T-1AB LT Scheduled S/D Due to Tr-1A Transformer remove & capacity improve.
8:56 | 17:16 | Ashuganj-Brahmanbaria 132kV Ckt-2 Scheduled S/D from Brahmanbaria 132/33kV end Due to Annual Maintenance.
8:56 | 14:30 | Sreemongol 132/33kV S/S 132/33kv T-1AB HT Scheduled S/D Due to Tr-1A Transformer remove & capacity improve.
8:57 | 12:07 | Agrabad-Rampur 132kV Ckt-2 Scheduled S/D from Agrabad 132/33kV end Due to Annual Maintenance.
8:57 | 13:16 | Hasnabad-Keraniganj 230kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to Dead line check from Hasnabd
End. and from Hasnabad 230/132kV end Due to Dead line checking .
9:08 | 12:06 | Rampur 230/132/33 S/S Agrabad-2 Scheduled S/D Due to Annual Maintenance. of Agrabad.
- | 9:09 | Barapukuria-Bogura 230 kV Ckt-2 is restored.
- | 9:12 | Bogura 230/132kV S/S 230KV Main 2 is restored.
9:14 | 16:16 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 LT Scheduled S/D Due to Maintenance work.
9:14 | 16:31 | Gopalganj(N)-Madaripur 132kV Ckt-2 Scheduled S/D from Gopalganj 400/132kV end. and from Madaripur 132/33kV end
Due to Annual Maintenance.
9:14 | 16:07 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 HT Scheduled S/D Due to Maintenance work.
9:15 | - | Kushtia 132/33kV S/S T2 HT Forced S/D Due to ৩৩ কেভি পাওয়ার কেবল স্থানান্তর, T-3 এর পাওয়ার কেবল ট্রেস্ন নির্মানের জন্য |  |  |  |  | 20.0MW load interrup.
9:18 | 16:30 | Mogbazar 132/33kV S/S GT-1 LT Scheduled S/D Due to 33 KV Bus -1 Maintenance.
9:20 | 16:32 | Mogbazar 132/33kV S/S GT-3 LT Scheduled S/D Due to 33 KV Bus -1 Shutdown.
9:22 | 14:58 | Pabna 132/33kV S/S T-3 LT Scheduled S/D Due to None.
9:23 | 14:56 | Pabna 132/33kV S/S T-3 HT Scheduled S/D.
9:29 | 16:37 | Barishal-Bhandaria 132 kV Ckt-1 Scheduled S/D from Bhandaria 132/33kV end Due to Annual Maintenance. and from |  |  |  |  | and 23.0MW load interrup.
|  | Barishal 132/33kV end Due to Annual Maintenance. |  |  |  |  | Barishal 132/33kV end
9:38 | 16:54 | Aminbazar-Kallyanpur 132kV Ckt-2 Scheduled S/D from Kallyanpur 132/33kV end Due to Annual Maintenance.
9:45 | 20:38 | Mymensingh 132/33kV S/S 50 MW Solar Plant Scheduled S/D Due to Annual Maintenance work.s of A-Bus
9:55 | - | Faridpur-Gopalganj(N) 132 kV Ckt-2 Scheduled S/D from Gopalganj 400/132kV end Due to Annual Maintenance. and from
Faridpur 132/33kV end Due to Annual Maintenance.
10:02 | 17:44 | Bhulta-Ghorasal 230 kV Ckt-1 Scheduled S/D from Bhulta 400/230kV end Due to Dead line checking by Rampura Grid SS.
10:02 | - | BSRM 230/33kV S/S 230/33 kV Transformer-2 (125/140 MVA) LT Scheduled S/D Due to Yearly Maintenance.
10:03 | - | BSRM 230/33kV S/S 230/33 kV Transformer-2 (125/140 MVA) HT Scheduled S/D Due to Yearly Maintenance.
10:05 | 18:30 | Savar 132/33kV S/S T-2 LT Scheduled S/D Due to Ten delta test & Annual Maintenance.
10:05 | 18:30 | Savar 132/33kV S/S T-2 HT Scheduled S/D Due to Ten delta test & Annual Maintenance.
10:07 | 16:26 | Anowara-Sikalbaha 230 kV Ckt-2 Scheduled S/D from Shikalbaha 230/132kV end.
10:15 | 15:23 | Bhaluka-Mymensingh 132 kV Ckt-1 Scheduled S/D from Mymensingh 132/33kV end Due to Annual Maintenance work.s of A-Bus DS (301S)
10:15 | 15:23 | Bhaluka-Mymensingh 132 kV Ckt-2 Scheduled S/D from Mymensingh 132/33kV end Due to Annual Maintenance work.s of A-Bus DS (311S)
10:16 | 14:35 | Mymensingh 132/33kV S/S Bus A Scheduled S/D Due to Annual Maintenance works.
10:27 | 11:22 | Kishoreganj 132/33kV S/S Bus-A Scheduled S/D Due to Project work.
10:32 | - | Gopalganj 400/132kV S/S ATR-01 LT Project Work S/D Due to Testing & relay change.
10:38 | - | Gopalganj 400/132kV S/S ATR-01 HT Project Work S/D Due to 10:38.
10:43 | 18:45 | BIPTC S/S Baharampur-2 Scheduled S/D Due to Annual Maintenance.
10:44 | 15:52 | Aminbazar-Meghnaghat 230kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to Bay maintenance.
10:48 | 13:15 | Jaldhaka 132/33kV S/S 406T LT Scheduled S/D Due to Due to change Energy Meter.
10:50 | 13:14 | Jaldhaka 132/33kV S/S 406T HT Scheduled S/D Due to Due to change Energy Meter.
10:51 | 16:46 | Kaliakoir 400/230/132kV S/S 400/230kV TR1 LT Scheduled S/D Due to Annual Maintenance.
10:52 | 16:46 | Kaliakoir 400/230/132kV S/S 400/230kV TR1 HT Scheduled S/D Due to Annual Maintenance.
11:00 | - | Sikalbaha 225MW CCPP Syncronized.
11:01 | - | Sikalbaha Gas 225MW GT was sync.
11:01 | - | Sikalbaha 225MW CCPP Syncronized.
11:04 | - | Ashuganj CCPP 225MW GT tripped due to high temperature in turbine outlet.
11:04 | - | Ashuganj CCPP 225 MW Shutdown.
11:28 | 12:27 | Kishoreganj 132/33kV S/S BUS-B Project Work S/D.
11:36 | 23:35 | Rampal 400/230kV S/S Bus Reactor Forced S/D Due to Due to 400 kv low bus voltage-R/Y/B(392/393/390
11:57 | 12:32 | Jaldhaka-Saidpur 132kV Ckt-2 Scheduled S/D from Jaldhaka 132/33kV end Due to Due to Energy Meter Change By Metering Division.
12:00 | - | Day Peak Generation: 9798 MW
12:03 | 18:44 | Savar 132/33kV S/S Bus-B Scheduled S/D Due to Schedule work of DBPS-3.
12:06 | 12:18 | Kishoreganj 132/33kV S/S Tr-3 (424T) HT Project Work S/D |  |  |  |  | 30.0MW load interrup.
12:28 | 13:51 | Maniknagar 132/33kV S/S Transformer GT-2 HT Tripped showing 95/86A, 95/86B, 195, 295, 95/96 relays Due to As the oil level in the OLTC drops.
12:54 | 16:08 | BIPTC S/S 20DF24 Forced S/D Due to Corrective maintenance.
13:08 | 14:24 | Mirpur 132/33kV S/S T3 HT Scheduled S/D Due to Annual Maintenance. Relay Test By SPMD -2.
13:08 | 14:24 | Mirpur 132/33kV S/S T3 LT Scheduled S/D Due to AM Work - Relay test by SPMD, Dhaka - 2,PGCB.
13:16 | - | Ashuganj CCPP 225MW GT was sync.
13:16 | - | Ashuganj CCPP 225 MW Syncronized with remarks:- GT
13:21 | 14:14 | Jaldhaka 132/33kV S/S 416T LT Scheduled S/D Due to Due to Energy Meter Change
13:22 | 14:13 | Jaldhaka 132/33kV S/S 416T HT Scheduled S/D Due to Due to Energy Meter Change
13:23 | 16:19 | Hasnabad-Keraniganj 230kV Ckt-2 Scheduled S/D from Keranigonj 230/132/33kV end Due to dead line check from Hasnabad
end. and from Hasnabad 230/132kV end Due to Dead line checking.
13:36 | - | Bogura (West) 230 Kv Bus B1 & B2 S/D.
13:47 | 15:48 | Aminbazar-Mirpur 132kV Ckt-2 Scheduled S/D from Mirpur 132/33kV end Due to AM Work- Relay testing work by SPMD - 2, Dhaka,PGCB.
15:02 | 15:42 | Mirpur-Uttara 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to AM work (Relay testing by SPMD-2, Dhaka, PGCB).
- | 15:05 | Maniknagar-Narinda 132kV Ckt-2 is restored.
15:29 | 17:49 | Bhangura 132/33kV S/S Tr-1(403T) HT Forced S/D Due to Red hot maintenance
15:50 | 16:22 | Mirpur-Uttara 3PH 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to AM work (Relay testing by SPMD-2, Dhaka, PGCB).
16:23 | - | Shikalbaha 225 MW CCPP STG synch.
16:23 | - | Sikalbaha 225MW CCPP Syncronized with remarks:- ST.
19:00 | - | Peak generation 10713 MW
- | 19:42 | Gopalganj 400/132kV S/S 400kV Payra Ckt-1 is restored.
4:19 | 7:23 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Tripped showing LBB initiation relays Due to Trip
4:19 | - | Matuail-Siddhirganj 132kV Ckt-1 Tripped from Siddhirganj 132/33kV end showing 1.General trip 2.Distance trip zone 1 & 2, |  |  |  |  | and 39.0MW load interrup. Matuail 132/33kV end
Phase Y & B, Distance 0.1 km, Lock out relay. relays Due to Pot head B-phase conductor break down in ss end. and from
Matuail 132/33kV end showing Distance Relay relays Due to None.
5:00 | - | Minimum Generation: 6840 MW.
6:16 | 6:38 | Aminbazar-Meghnaghat 230kV Ckt-2 Tripped from Aminbazar 400/230/132kV end showing 7SA87 relays Due to Trip as Meghnaghat End.
7:10 | - | BSRM-Cumilla(N) 230 kV Ckt-2 Project Work S/D from Cumilla(N) 230/132/33kV end.
7:52 | - | Bogura 132/33kV S/S Transformer-2 LT Scheduled S/D Due to red hot work t-2 33kv isolator.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-01-23 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4441500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 289590 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 401 | 9259200
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9604500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 96 | 1249920
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 82 | 1108942 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 220680 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 25 | 374483 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 93 | 1167360 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 336 | 7715667
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 91 | 1196064 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 50040 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 98 | 609120 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 66833 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 65452 | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 40 | 920160 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 785520
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 615400
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 17 | 205440 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 130 | 1427673 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 36 | 616896 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 726720 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 53 | 825600 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 96480 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 171363
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 146160 | Fuel shortage
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 49 | 1494091 | On test.
| Dhaka area Total |  |  |  | 5062 | 2439 | 45450854
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 205619 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 129060
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 204480 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 76 | 1840720 | Unit-3 under maint.
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 206 | 1517352 | Gas shortage
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 402290 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 66 | 917472 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 592568 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 25 | 424920 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 474240 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 295008 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 20 | 337920
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 5 | 30720 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 23039
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 105 | 1021200 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 123811 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 359630 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 481920 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 691255 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 17 | 322836 | Fuel shortage
| SS Power I |  | SS Power | 2*612 | 1224 | 400 | 8645453 | Coal shortage
| Cox's Bazar Wind |  | IPP | 66 | 0 | 1 | 50400 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 271 | 8523636 | On test.
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4344 | 1397 | 27615549
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 157 | 3436000 | ST under shutdown
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 305 | 7710300 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 44 | 1049256
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 44 | 1082400 | Gas shortage
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 1037090 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1247293
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 8 | 197381 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 25 | 358032 | Fuel shortage
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 341760 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 13 | 309996 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 180540 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 108 | 2364480
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 314700
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 151757 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 17 | 350350 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 78 | 677880 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 236880 | Fuel shortage
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 18 | 82560 | Fuel shortage
| Cumilla Area Total |  |  |  | 2951 | 959 | 21128655
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 34 | 1304640 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Contract Expired
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9200
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 68 | 964800 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 183600 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 2030
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 71040 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 117 | 2535310
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1017000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 764760 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3123818
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1361280
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1944000
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Under maint.
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 20 | 488000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 397392 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7326000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Under maint.
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 250020
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 360 | 7417300
| Sylhet Area Total |  |  |  | 2427 | 1099 | 24089570
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 794 | 16301090
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 32 | 145920 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 32 | 251520 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 20 | 218240 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 30375 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 93 | 1352160 | Engine problem
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 484560
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 979 | 18783865
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 108960 | Fuel shortage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 18 | 388500 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 135 | 3147000 | ST Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 622 | 14597300 | Unit-2 under maint.
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5328682
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 427200 | Fuel shortage
| Barisal 307 MW |  | IPP | 307*1 | 307 | 250 | 5698200 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1315 | 29695842
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 266592 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 15 | 159594 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 21 | 334800 | Fuel shortage
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 422253 | Fuel shortage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 308898 | Fuel shortage
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 319 | 8852909 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 73774 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 144000 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 97286 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 91 | 867344 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 259584 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 254592 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 24960
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1470 | 28722909
| Rajshahi Area Total |  |  |  | 3631 | 2127 | 40789495
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4131000 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 41 | 271929 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 32420
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 70 | 342912 | Fuel shortage
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 158263
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 743380
| Rangpur Area Total |  |  |  | 950 | 281 | 5679904
| Total |  |  |  | 25481 | 10713 | 215769044
| Eastern Grid Total |  |  |  | 15398 | 6011 | 120819938
| Western Grid Total |  |  |  | 10083 | 4702 | 94949106
| National Grid Total |  |  |  | 25481 | 10713 | 215769044
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2024-01-23
| (a) ENTIRE EASTERN GRID : |  | 6853.19 | MW | (b) ENTIRE WESTERN GRID : |  | 3319.1 | MW
| i) Dhaka area |  | 3772.19 | MW | i) Khulna area |  | 1214.4 | MW
| ii) Chittagong area |  | 1012 | MW | ii) Rajshahi area |  | 1068.8 | MW
| iii) Comilla area |  | 847 | MW | iii) Barisal area |  | 282.9 | MW
| iv) Mymensingh area |  | 848 | MW | iv) Rangpur area |  | 753 | MW
| v) Sylhet area |  | 374 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10172.29 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 14 | 09:00 | Kamrangirchar | 46.9 | 15:00 | Narinda | 48 | 13:00 | Sherpur | 108 | 19:30
2 | AKSML | 104 | 11:00 | Chowmuhani | 142 | 19:00 | Kaptai | N/A | N/A | Narshingdi | 150 | 19:00 | Shikalbaha | 21 | 10:00
3 | Aftabnagar | 22 | 12:00 | Chuadanga | 73 | 18:30 | Kazla | 90 | 13:00 | Natore | 106 | 18:30 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 59 | 13:00 | Coxsbazar | 90 | 18:00 | Keranigonj | 54 | 13:00 | Nawabganj | 28 | 13:00 | Shitalakhya | 77.1 | 12:00
5 | Agrabad | 46 | 18:00 | Cumilla(N) | 94 | 14:00 | Khagrachori | 24 | 18:00 | Netrakona | 117 | 07:00 | Sholosohor | 32 | 12:00
6 | Amnura | 53 | 12:00 | Cumilla(S) | 118 | 13:00 | Khulna | 84 | 13:00 | New | 18 | 11:00 | Shyampur | 144 | 14:00
7 | Ashuganj | 45 | 14:00 | Daudkandi | 108 | 19:30 | Khulshi | 138 | 19:00 | Niamatpur | 76 | 19:30 | Siddhirganj | 92 | 12:00
8 | BIPTC | N/A | N/A | Dhaka | 16 | 13:00 | Kishoreganj | 114 | 19:00 | Noapara | 37 | 18:30 | Sirajganj | 88 | 19:00
9 | BSRM | 89 | 23:00 | Dhamrai | 116 | 18:00 | Kodda | 238 | 18:00 | PHP | 3 | 12:00 | Sonargaon | 102 | 23:00
10 | Bagerhat | 73 | 18:30 | Dhanmondi | 81 | 13:00 | Kulaura | 26 | 18:00 | Pabna | 81 | 18:00 | Sreemongol | 46 | 18:00
11 | Bakulia | 60 | 13:00 | Dohazari | 66 | 18:00 | Kurigram | 63 | 18:00 | Palashbari | 88 | 18:30 | Sreepur | 56 | 18:30
12 | Banani | 22 | 13:00 | Faridpur | 121 | 18:30 | Kushtia | 102 | 18:30 | Panchagarh | 45 | 18:30 | Srinagar | 29.6 | 13:00
13 | Bangabhaban | 7 | 12:00 | Fatullah | 49 | 12:00 | Lalbag | 68 | 18:30 | Patuakhali | 65.8 | 21:00 | Sunamganj | 36 | 18:30
14 | Barapukuria | 53 | 19:00 | Fenchuganj | 25 | 18:00 | Lalmonirhat | 40 | 18:30 | Payra | 14 | 18:30 | Sylhet | 14 | 18:00
15 | Barguna | 14 | 18:30 | Feni | 72 | 18:00 | MI_Cement | 12.6 | 19:30 | Postogola | 39 | 13:00 | Sylhet-132 | 90 | 18:30
16 | Barishal | 79 | 13:00 | GPH | 98 | 19:30 | Madanganj | 31 | 17:00 | Purbachal | 13 | 12:00 | TK | 19.5 | 19:00
17 | Barishal-230 | 64 | 19:30 | Ghorashal | 55 | 18:30 | Madaripur | 67 | 20:00 | Purbasadipur | 106 | 18:30 | Tangail | 144 | 18:00
18 | Baroaulia | 62 | 10:00 | Goalpara | 24 | 18:30 | Madartek | 53.64 | 13:00 | Rahim | 44 | 12:00 | Thakurgaon | 75 | 18:30
19 | Baroirhat | 38 | 19:00 | Gollamari | 44 | 10:00 | Madunaghat | 33 | 18:00 | Rajbari | 52 | 18:30 | Tongi | 118 | 11:00
20 | Bashundhara | 128 | 13:00 | Gopalganj | 79.4 | 18:30 | Magura | 42 | 19:30 | Rajendrapur | 80 | 21:00 | Ullahpara | 15 | 10:00
21 | BashundharaCement | 6 | 01:00 | Gulshan | 62 | 13:00 | Mahasthangarh | 50 | 18:30 | Rajshahi | 108 | 21:00 | Ullon | 37 | 13:00
22 | Beanibazar | 41 | 18:00 | Halishahar | 66 | 11:00 | Manikganj | 87 | 19:00 | Rajshahi-230 | 28 | 13:00 | Uttara | 38 | 13:00
23 | Benapole | 46 | 11:00 | HaripurSBU | 141 | 12:00 | Maniknagar | 53 | 13:00 | Ramganj | 76 | 18:00 | UttaraNew | 29 | 13:00
24 | Bhaluka | 144 | 14:00 | Hasnabad | 71 | 12:00 | Matarbari | 31 | 18:00 | Rampur | 17 | 13:00 | Zigatola | 42 | 13:00
25 | Bhandaria | 34 | 19:30 | Hathazari | 50 | 18:00 | Matuail | 58 | 12:00 | Rangamati | 12 | 18:00
26 | Bhangura | 22 | 08:00 | Ishurdi | 49 | 18:30 | Millgate | 81 | 12:00 | Rangpur | 106 | 19:00
27 | Bheramara(GK) | 40 | 18:30 | Jaldhaka | 63 | 18:30 | Mirpur | 88 | 18:30 | Ruppur | 3.8 | 09:00
28 | Bhulta | 251 | 23:00 | Jamalpur | 120 | 19:00 | Mirsorai | 3.5 | 11:00 | SSM | 14 | 22:00
29 | Bog-Sherpur | 50 | 18:00 | Jashore | 106 | 12:00 | Mirzapur | 44 | 18:00 | Saidpur | 99 | 18:30
30 | Bogura | 118 | 19:00 | Jhenaidah | 91 | 18:30 | Mithapukur | 44 | 18:00 | Satkhira | 94 | 18:30
31 | Borhanuddin | 37 | 21:00 | Joydebpur | 134 | 18:00 | Modern | 0 | 00:00 | Satmasjid | 89 | 13:00
32 | Brahmanbaria | 107 | 14:00 | Joypurhat | 44 | 19:30 | Mogbazar | 48.3 | 09:00 | Savar | 118 | 12:00
33 | Cantonment | 92 | 13:00 | Juldah | 17 | 19:30 | Mongla | 29 | 13:00 | SevenRings | 12.57 | 17:00
34 | Chandpur | 41 | 18:00 | KSRM | 31 | 09:00 | Motijheel | 27 | 13:00 | ShahCement | 21 | 12:00
35 | Chandraghona | 23 | 18:30 | Kabirpur | 195 | 10:00 | Munshiganj | 67 | 13:00 | Shahjadpur | 49 | 19:00
36 | Chapai | 49 | 12:00 | Kachua | 46 | 20:00 | Mymensingh | 174 | 08:00 | Shahjibazar | 90 | 19:00
37 | Charsaidpur | 39 | 16:00 | Kallyanpur | 72 | 13:00 | Naogaon | 98 | 20:00 | Shahmirpur | 38 | 16:00
38 | Chauddagram | 40 | 18:00 | Kalurghat | 28 | 10:00 | Narail | 40 | 18:30 | Shariatpur | 52 | 20:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-01-23 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 411 | 04:00 | 393 | 12:00 | Gopalganj | 414 | 20:00 | 396 | 12:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 417 | 04:00 | 400 | 12:00
| Bhulta | 409 | 04:00 | 390 | 12:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 421 | 06:00 | 410 | 12:00 | Payra | 419 | 05:00 | 409 | 11:00
| BIPTC | 410 | 03:00 | 389 | 16:00 | Rahanpur | 414 | 03:00 | 394 | 13:00
| Bogura | N/A | N/A | N/A | N/A | Rampal | 417 | 04:00 | 392 | 11:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 238 | 04:00 | 226 | 12:00 | Hasnabad | 239 | 23:00 | 231 | 13:00
| AKSML | 237 | 23:00 | 227 | 11:00 | Hathazari | 239 | 15:00 | 231 | 11:00
| Aminbazar | 240 | 19:30 | 223 | 05:00 | Ishurdi | 238 | 04:00 | 223 | 12:00
| Ashuganj | 242 | 08:00 | 232 | 12:00 | Jhenaidah | 237 | 04:00 | 221 | 12:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 236 | 04:00 | 225 | 14:00
| Baghabari | 236 | 04:00 | 223 | 12:00 | Keranigonj | 238 | 04:00 | 227 | 12:00
| Barapukuria | 225 | 03:00 | 213 | 18:30 | Khulna(S) | 242 | 04:00 | 228 | 11:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 243 | 19:00 | 238 | 12:00 | Maniknagar | 242 | 08:00 | 232 | 12:00
| Bheramara | 237 | 04:00 | 223 | 12:00 | Meghnaghat | 246 | 05:00 | 238 | 11:00
| Bhulta | 243 | 04:00 | 232 | 12:00 | Mirsorai | 240 | 08:00 | 229 | 12:00
| Bibiana | 241 | 22:00 | 233 | 12:00 | Rajshahi | 239 | 05:00 | 226 | 11:00
| BIPTC | 237 | 04:00 | 222 | 12:00 | Rampal | 240 | 04:00 | 227 | 11:00
| Bogura | 232 | 05:00 | 216 | 12:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 245 | 03:00 | 242 | 12:00 | Rampura | 241 | 05:00 | 230 | 12:00
| BSRM | 239 | 08:00 | 230 | 12:00 | Shikalbaha | 236 | 16:00 | 229 | 02:00
| Cumilla(N) | 241 | 20:00 | 230 | 12:00 | Shyampur | 239 | 04:00 | 230 | 12:00
| Fenchuganj | 246 | 04:00 | 237 | 12:00 | Siddhirganj | 243 | 03:00 | 234 | 11:00
| Ghorashal | 240 | 00:00 | 240 | 00:00 | Sirajgonj | 241 | 05:00 | 230 | 12:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 238 | 05:00 | 226 | 12:00
| GPH | 238 | 22:00 | 229 | 02:00 | Tongi | 236 | 21:00 | 223 | 11:00
| Haripur | 240 | 22:00 | 231 | 12:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 138 | 05:00 | 130 | 11:00 | Lalbag | 137 | 04:00 | 129 | 12:00
| Agargaon | 141 | 04:00 | 133 | 12:00 | Lalmonirhat | 132 | 04:00 | 122 | 13:00
| Agrabad | 138 | 15:00 | 132 | 12:00 | Madanganj | 138 | 20:00 | 131 | 12:00
| AKS | 137 | 03:00 | 132 | 11:00 | Madaripur | 135 | 20:00 | 130 | 11:00
| Aminbazar | 138 | 03:00 | 129 | 11:00 | Madartek | 137 | 04:00 | 129 | 12:00
| Amnura | 141 | 19:30 | 124 | 13:00 | Madunaghat | 140 | 23:00 | 135 | 11:00
| Ashuganj | 142 | 08:00 | 135 | 12:00 | Magura | 139 | 03:00 | 130 | 12:00
| Bagerhat | 136 | 23:00 | 128 | 12:00 | Mahasthangarh | 136 | 04:00 | 125 | 13:00
| Bakulia | 140 | 22:00 | 133 | 10:00 | Manikganj | 134 | 00:00 | 127 | 10:00
| Banani | 136 | 03:00 | 126 | 12:00 | Maniknagar | 135 | 05:00 | 128 | 12:00
| Bangabhaban | 135 | 08:00 | 128 | 12:00 | Matarbari | 131 | 15:00 | 125 | 12:00
| Barapukuria | 135 | 03:00 | 127 | 12:00 | Matuail | 137.8 | 20:00 | 132 | 12:00
| Barguna | 138 | 20:00 | 133 | 11:00 | Millgate | 137 | 04:00 | 125 | 12:00
| Barishal | 139 | 05:00 | 136 | 11:00 | Mirpur | 135 | 04:00 | 128 | 11:00
| Barishal-230 | 139 | 03:00 | 135 | 12:00 | Mirzapur | 134 | 04:00 | 127 | 12:00
| Baroaulia | 140 | 19:00 | 134 | 12:00 | Mithapukur | 135 | 04:00 | 123 | 12:00
| Baroirhat | 138 | 22:00 | 128 | 12:00 | MI_Cement | 139 | 20:00 | 133 | 12:00
| Bashundhara | 138 | 03:00 | 125 | 12:00 | Modern | 140 | 22:00 | 133 | 12:00
| BashundharaCement | 138 | 20:00 | 131 | 12:00 | Mogbazar | 139 | 05:00 | 130 | 12:00
| Beanibazar | 138 | 05:00 | 131 | 12:00 | Mongla | 135 | 19:00 | 127 | 03:00
| Benapole | 135 | 03:00 | 122 | 12:00 | Motijheel | 135 | 08:00 | 128 | 12:00
| Bhaluka | 134 | 03:00 | 127 | 12:00 | Munshiganj | 138 | 07:00 | 132 | 12:00
| Bhandaria | 138 | 19:30 | 126 | 12:00 | Mymensingh | 135 | 08:00 | 121 | 22:00
| Bhangura | 141 | 04:00 | 130 | 12:00 | Naogaon | 134 | 04:00 | 121 | 12:00
| Bheramara | 138 | 04:00 | 129 | 12:00 | Narail | 139 | 04:00 | 130 | 12:00
| Bheramara(GK) | 138 | 00:00 | 128 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 128 | 20:00 | 120 | 12:00 | Narshingdi | 137 | 01:00 | 124 | 12:00
| Bog-Sherpur | 138 | 05:00 | 126 | 12:00 | Natore | 136 | 03:00 | 129 | 12:00
| Bogura | 138 | 04:00 | 127 | 13:00 | Nawabganj | 137 | 20:00 | 129 | 12:00
| Bogura-230 | 137 | 05:00 | 127 | 12:00 | Netrakona | 135 | 09:00 | 122 | 19:30
| Brahmanbaria | 139 | 06:00 | 131 | 12:00 | New | 136 | 04:00 | 126 | 14:00
| Cantonment | 140 | 04:00 | 132 | 13:00 | Niamatpur | 130 | 04:00 | 120 | 11:00
| Chandpur | 138 | 19:00 | 128 | 12:00 | Noapara | 136 | 23:00 | 127 | 11:00
| Chandraghona | 141 | 22:00 | 135 | 09:00 | Pabna | 140 | 04:00 | 131 | 11:00
| Chapai | 134 | 01:00 | 125 | 12:00 | Palashbari | 132 | 03:00 | 122 | 13:00
| Charsaidpur | 139 | 20:00 | 133 | 11:00 | Panchagarh | 137 | 04:00 | 120 | 13:00
| Chauddagram | 140 | 22:00 | 130 | 12:00 | Patuakhali | 136 | 21:00 | 133 | 08:00
| Chhatak | 138 | 03:00 | 130 | 12:00 | Payra | 137 | 04:00 | 134 | 10:00
| Chowmuhani | 137 | 20:00 | 127 | 12:00 | PHP | 138 | 00:00 | 128 | 12:00
| Chuadanga | 139 | 04:00 | 126 | 12:00 | Postogola | 141 | 20:00 | 133 | 12:00
| Coxsbazar | 130 | 15:00 | 123 | 18:00 | Purbachal | 138 | 03:00 | 125 | 12:00
| Cumilla(N) | 142 | 23:00 | 134 | 12:00 | Purbasadipur | 131 | 03:00 | 118 | 13:00
| Cumilla(S) | 141 | 20:00 | 128 | 12:00 | Rahanpur | 136 | 02:00 | 130 | 13:00
| Daudkandi | 135 | 18:30 | 130 | 12:00 | Rahim | 137 | 05:00 | 132 | 12:00
| Dhaka | 137 | 04:00 | 130 | 12:00 | Rajbari | 137 | 03:00 | 128 | 12:00
| Dhamrai | 136 | 04:00 | 126 | 12:00 | Rajendrapur | 136 | 18:30 | 126 | 13:00
| Dhanmondi | 138.5 | 20:00 | 132 | 12:00 | Rajshahi | 136 | 19:30 | 130 | 11:00
| Dohazari | 136 | 09:00 | 132 | 11:00 | Rajshahi-230 | 137 | 05:00 | 124 | 12:00
| Faridpur | 136 | 04:00 | 130 | 11:00 | Ramganj | 137 | 16:00 | 127 | 12:00
| Fatullah | 139 | 20:00 | 133 | 12:00 | Rampur | 138 | 21:00 | 132 | 12:00
| Fenchuganj | 141 | 04:00 | 135 | 12:00 | Rampura | 138 | 04:00 | 129 | 12:00
| Feni | 136 | 18:00 | 127 | 12:00 | Rangamati | 140 | 22:00 | 134 | 12:00
| Ghorashal | 144 | 06:00 | 138 | 11:00 | Rangpur | 131 | 01:00 | 122 | 18:00
| Goalpara | 138 | 04:00 | 129 | 12:00 | Ruppur | 138 | 03:00 | 132 | 11:00
| Gollamari | 136 | 03:00 | 128 | 11:00 | Saidpur | 133 | 05:00 | 121 | 09:00
| Gopalganj | 135 | 03:00 | 128 | 11:00 | Satkhira | 135 | 04:00 | 126 | 11:00
| Gopalganj-400 | 136 | 20:00 | 129 | 11:00 | Satmasjid | 140 | 04:00 | 132 | 13:00
| Gulshan | 136 | 02:00 | 130 | 12:00 | Savar | 135 | 20:00 | 125 | 12:00
| Halishahar | 139 | 20:00 | 133 | 01:00 | SevenRings | 145 | 05:00 | 138 | 11:00
| Haripur | 137 | 05:00 | 132 | 12:00 | ShahCement | 139 | 20:00 | 133 | 11:00
| HaripurSBU | 137 | 05:00 | 132 | 12:00 | Shahjadpur | 140 | 00:00 | 136 | 12:00
| Hasnabad | 139 | 07:00 | 133 | 12:00 | Shahjibazar | 139 | 06:00 | 133 | 12:00
| Hathazari | 140 | 08:00 | 136 | 10:00 | Shahmirpur | 139 | 18:30 | 133 | 12:00
| Ishurdi | 141 | 04:00 | 132 | 12:00 | Shariatpur | 136 | 23:00 | 130 | 11:00
| Jaldhaka | 131 | 03:00 | 118 | 12:00 | Sherpur | 130 | 09:00 | 114 | 22:00
| Jamalpur | 133 | 08:00 | 117 | 22:00 | Shikalbaha | 128 | 08:00 | 122 | 01:00
| Jashore | 135 | 01:00 | 123 | 12:00 | Shikalbaha-230 | 139 | 16:00 | 134 | 12:00
| Jhenaidah | 138 | 23:00 | 131 | 11:00 | Shitalakhya | 139 | 20:00 | 133 | 12:00
| Jhenaidah-230 | 141 | 04:00 | 129 | 12:00 | Sholosohor | 139 | 22:00 | 133 | 02:00
| Joydebpur | 143 | 20:00 | 133 | 11:00 | Shyampur | 138 | 03:00 | 135 | 10:00
| Joypurhat | 133 | 04:00 | 121 | 13:00 | Shyampur-230 | 139 | 20:00 | 132 | 12:00
| Juldah | 139 | 22:00 | 133 | 09:00 | Siddhirganj | 138 | 19:30 | 132 | 12:00
| Kabirpur | 137 | 18:00 | 123 | 12:00 | Sirajganj | 136 | 01:00 | 126 | 12:00
| Kachua | 139 | 08:00 | 130 | 12:00 | Sonargaon | 138 | 19:30 | 132 | 11:00
| Kaliakoir | 138 | 18:00 | 131 | 12:00 | Sreemongol | 139 | 03:00 | 132 | 11:00
| Kallyanpur | 136 | 07:00 | 130 | 12:00 | Sreepur | 136 | 04:00 | 128 | 12:00
| Kalurghat | 140 | 19:00 | 133 | 12:00 | Srinagar | 136 | 04:00 | 130 | 11:00
| Kamrangirchar | 137 | 19:30 | 129 | 13:00 | SSM | 141 | 07:00 | 138 | 12:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 138 | 05:00 | 129 | 13:00
| Kazla | 135 | 04:00 | 127 | 13:00 | Sylhet | 138 | 02:00 | 132 | 12:00
| Keranigonj | 137 | 04:00 | 130 | 12:00 | Sylhet-132 | 138 | 01:00 | 133 | 11:00
| Khagrachori | 139 | 20:00 | 133 | 11:00 | Tangail | 133 | 08:00 | 125 | 22:00
| Khulna | 136 | 04:00 | 127 | 12:00 | Thakurgaon | 135 | 04:00 | 118 | 13:00
| Khulna(S) | 136 | 04:00 | 128 | 12:00 | TK | 139 | 00:00 | 136 | 04:00
| Khulshi | 139 | 22:00 | 132 | 12:00 | Tongi | 137 | 06:00 | 127 | 11:00
| Kishoreganj | 137 | 00:00 | 127 | 11:00 | Ullahpara | 140 | 03:00 | 129 | 12:00
| Kodda | 142 | 23:00 | 126 | 12:00 | Ullon | 137 | 05:00 | 130 | 12:00
| KSRM | 140 | 19:00 | 134 | 02:00 | Uttara | 138 | 04:00 | 126 | 12:00
| Kulaura | 139 | 01:00 | 134 | 14:00 | UttaraNew | 135 | 03:00 | 124 | 12:00
| Kurigram | 133 | 06:00 | 122 | 08:00 | Zigatola | 137 | 04:00 | 37 | 07:00
| Kushtia | 138 | 05:00 | 128 | 12:00

## L-Curve
Date | 2024-01-23
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 770 | 4761 | 3836 | 8597 |  |  |  | QF-LDC-11
0:30 | 815 | 4489 | 3702.5 | 8191.5 | Date: | 2024-01-23
1:00 | 860 | 4217 | 3569 | 7786
1:30 | 790 | 4105.5 | 3434.5 | 7540
2:00 | 720 | 3994 | 3300 | 7294
2:30 | 675 | 3983.5 | 3164 | 7147.5 | [5 empty] | Gen. at Eve. Peak | 10713 | 10713 MW (19:00 )
3:00 | 630 | 3973 | 3028 | 7001 | [6 empty] | 19:00
3:30 | 615 | 3962.5 | 2981 | 6943.5 | [5 empty] | Gen. at Day Peak | 9797 | 9797 MW (12:00 )
4:00 | 600 | 3952 | 2934 | 6886 | [6 empty] | 12:00
4:30 | 576 | 3915 | 2909.5 | 6824.5 | [5 empty] | Highest Generation | 10713
5:00 | 552 | 3878 | 2885 | 6763 | [6 empty] | 19:00
5:30 | 503 | 3989.5 | 2925.5 | 6915
6:00 | 454 | 4101 | 2966 | 7067
6:30 | 391 | 4348.5 | 3103.5 | 7452
7:00 | 328 | 4596 | 3241 | 7837
7:30 | 364 | 4791.5 | 3411 | 8202.5
8:00 | 400 | 4987 | 3581 | 8568
8:30 | 385 | 5099.5 | 3605.5 | 8705
9:00 | 370 | 5212 | 3630 | 8842
9:30 | 478 | 5278 | 3748 | 9026
10:00 | 586 | 5344 | 3866 | 9210
10:30 | 649 | 5389 | 3919 | 9308
11:00 | 712 | 5434 | 3972 | 9406
11:30 | 847 | 5437.5 | 4164 | 9601.5
12:00 | 982 | 5441 | 4356 | 9797
12:30 | 951 | 5518.5 | 4402.5 | 9921
13:00 | 920 | 5596 | 4449 | 10045
13:30 | 950 | 5608 | 4357.5 | 9965.5
14:00 | 980 | 5620 | 4266 | 9886
14:30 | 1050 | 5468 | 4271 | 9739
15:00 | 1120 | 5316 | 4276 | 9592
15:30 | 1150 | 5185.5 | 4192.5 | 9378
16:00 | 1180 | 5055 | 4109 | 9164
16:30 | 1190 | 5081 | 4142 | 9223
17:00 | 1200 | 5107 | 4175 | 9282
17:30 | 1020 | 5415.5 | 4369.5 | 9785
18:00 | 840 | 5724 | 4564 | 10288
18:30 | 814 | 5867.5 | 4633 | 10500.5
19:00 | 788 | 6011 | 4702 | 10713
19:30 | 820 | 5903 | 4686 | 10589
20:00 | 836 | 5886 | 4679 | 10565 |  |  |  | Executive Engineer
20:30 | 863 | 5764.5 | 4655.5 | 10420 |  |  |  | Network Operation Division
21:00 | 890 | 5643 | 4632 | 10275
21:30 | 960 | 5507 | 4567 | 10074
22:00 | 1030 | 5371 | 4502 | 9873 |  |  |  |  | Page 6 of 7
22:30 | 1015 | 5139 | 4343.5 | 9482.5
23:00 | 1000 | 4907 | 4185 | 9092
23:30 | 885 | 4834 | 4010.5 | 8844.5
24:00 | 770 | 4761 | 3836 | 8597
10713 MW (19:00 )
9797 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-01-23 |  | Energy |  | 215769044
[14 empty] | Date: | 2024-01-23 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 2313 | 728 | 1657 | 0 | 708 | 2706 | 76 | 0 | 312 | 96 | 0 | 1 | 0
0:30 | 2238 | 649.5 | 1668.5 | 0 | 446 | 2861.5 | 76 | 0 | 156 | 90 | 0 | 6 | 0 |  |  | Date: | 43852
1:00 | 2163 | 571 | 1680 | 0 | 184 | 3017 | 76 | 0 | 0 | 84 | 0 | 11 | 0
1:30 | 2170 | 500 | 1712 | 0 | 92 | 2899.5 | 76 | 0 | 0 | 81 | 0 | 9.5 | 0 | [8 empty] | Total Energy | 215.769 | 215.769 | Total Energy Gen 215.769 MKWHr Energy Not Served 1.463 MKWHr Energy Requirement 217.232 MKWHr
2:00 | 2177 | 429 | 1744 | 0 | 0 | 2782 | 76 | 0 | 0 | 78 | 0 | 8 | 0 | [8 empty] | Energy not Served | 1.4626 | 1.4626
2:30 | 2159.5 | 429 | 1751 | 0 | 0 | 2646.5 | 76 | 0 | 0 | 77 | 0 | 8.5 | 0 | [8 empty] | Energy Requirement | 217.2316 | 217.2316
3:00 | 2142 | 429 | 1758 | 0 | 0 | 2511 | 76 | 0 | 0 | 76 | 0 | 9 | 0
3:30 | 2141.5 | 429 | 1746 | 0 | 0 | 2463.5 | 76 | 0 | 0 | 79 | 0 | 8.5 | 0
4:00 | 2141 | 429 | 1734 | 0 | 0 | 2416 | 76 | 0 | 0 | 82 | 0 | 8 | 0
4:30 | 2116.5 | 429.5 | 1720 | 0 | 3.5 | 2391.5 | 76 | 0 | 0 | 81 | 0 | 6.5 | 0
5:00 | 2092 | 430 | 1706 | 0 | 7 | 2367 | 76 | 0 | 0 | 80 | 0 | 5 | 0
5:30 | 2107.5 | 430 | 1777.5 | 0 | 22.5 | 2416.5 | 76 | 0 | 0 | 82 | 0 | 3 | 0
6:00 | 2123 | 430 | 1849 | 0 | 38 | 2466 | 76 | 0 | 0 | 84 | 0 | 1 | 0
6:30 | 2157 | 494.5 | 1788.5 | 0 | 248 | 2586.5 | 76 | 0 | 16.5 | 84 | 0.5 | 0.5 | 0 | [7 empty] | Coal
7:00 | 2191 | 559 | 1728 | 0 | 458 | 2707 | 76 | 0 | 33 | 84 | 1 | 0 | 0
7:30 | 2190 | 609.5 | 1800.5 | 0 | 628.5 | 2751 | 76 | 0 | 37 | 91 | 19 | 0 | 182.405 | [6 empty] | Oil
8:00 | 2189 | 660 | 1873 | 0 | 799 | 2795 | 76 | 0 | 41 | 98 | 37 | 0 | 364.81
8:30 | 2208 | 651 | 1904.5 | 0 | 829.5 | 2808 | 76 | 0 | 60 | 99 | 69 | 0 | 401.1
9:00 | 2227 | 642 | 1936 | 0 | 860 | 2821 | 76 | 0 | 79 | 100 | 101 | 0 | 437.39
9:30 | 2234 | 642 | 1906 | 0 | 924.5 | 2897 | 76 | 0 | 95.5 | 100 | 151 | 0 | 285.545
10:00 | 2241 | 642 | 1876 | 0 | 989 | 2973 | 76 | 0 | 112 | 100 | 201 | 0 | 133.7
10:30 | 2258 | 655.5 | 1863.5 | 0 | 1020 | 2973 | 76 | 0 | 114.5 | 105 | 242.5 | 0 | 123.6725
11:00 | 2275 | 669 | 1851 | 0 | 1051 | 2973 | 76 | 0 | 117 | 110 | 284 | 0 | 113.645
11:30 | 2219.5 | 717 | 1867 | 0 | 1084.5 | 3076 | 76 | 0 | 158 | 110 | 293.5 | 0 | 141.8225
12:00 | 2164 | 765 | 1883 | 0 | 1118 | 3179 | 76 | 0 | 199 | 110 | 303 | 0 | 170
12:30 | 2163.5 | 765 | 1903.5 | 0 | 1141 | 3226 | 76 | 0 | 233.5 | 114 | 298.5 | 0 | 130
13:00 | 2163 | 765 | 1924 | 0 | 1164 | 3273 | 76 | 0 | 268 | 118 | 294 | 0 | 90
13:30 | 2163 | 765 | 1924 | 0 | 1164 | 3273 | 76 | 0 | 268 | 118 | 294 | 0 | 90
14:00 | 2163 | 765 | 1924 | 0 | 1164 | 3273 | 76 | 0 | 268 | 118 | 294 | 0 | 90
14:30 | 2206.5 | 832 | 1758 | 0 | 1177.5 | 3134 | 76 | 0 | 284.5 | 112 | 238 | 0 | 82
15:00 | 2250 | 899 | 1592 | 0 | 1191 | 2995 | 76 | 0 | 301 | 106 | 182 | 0 | 74
15:30 | 2250.5 | 898 | 1590 | 0 | 1165.5 | 2854 | 76 | 0 | 299 | 108 | 137 | 0 | 37
16:00 | 2251 | 897 | 1588 | 0 | 1140 | 2713 | 76 | 0 | 297 | 110 | 92 | 0 | 0
16:30 | 2297 | 897 | 1621.5 | 0 | 1156.5 | 2670.5 | 76 | 0 | 336 | 111 | 57.5 | 0 | 0
17:00 | 2343 | 897 | 1655 | 0 | 1173 | 2628 | 76 | 0 | 375 | 112 | 23 | 0 | 0
17:30 | 2439 | 863.5 | 1720.5 | 0 | 1378 | 2739.5 | 76 | 0 | 444.5 | 112 | 11.5 | 0.5 | 25
18:00 | 2535 | 830 | 1786 | 0 | 1583 | 2851 | 76 | 0 | 514 | 112 | 0 | 1 | 50
18:30 | 2536 | 812 | 1767 | 0 | 1671.5 | 3017 | 76 | 0 | 510 | 110 | 0 | 1 | 25
19:00 | 2537 | 794 | 1748 | 0 | 1760 | 3183 | 76 | 0 | 506 | 108 | 0 | 1 | 0
19:30 | 2512 | 793 | 1724 | 0 | 1741 | 3128 | 76 | 0 | 507 | 108 | 0 | 0 | 0
20:00 | 2506 | 793 | 1712 | 0 | 1727 | 3138 | 76 | 0 | 505 | 108 | 0 | 0 | 0
20:30 | 2477 | 793 | 1727 | 0 | 1648.5 | 3123.5 | 76 | 0 | 468.5 | 106 | 0 | 0.5 | 0
21:00 | 2448 | 793 | 1742 | 0 | 1570 | 3109 | 76 | 0 | 432 | 104 | 0 | 1 | 0
21:30 | 2415.5 | 846 | 1735 | 0 | 1424.5 | 3063.5 | 76 | 0 | 411 | 102 | 0 | 0.5 | 0
22:00 | 2383 | 899 | 1728 | 0 | 1279 | 3018 | 76 | 0 | 390 | 100 | 0 | 0 | 0
22:30 | 2351 | 899 | 1694.5 | 0 | 1065 | 2917.5 | 76 | 0 | 382.5 | 97 | 0 | 0 | 0
23:00 | 2319 | 899 | 1661 | 0 | 851 | 2817 | 76 | 0 | 375 | 94 | 0 | 0 | 0
23:30 | 2316 | 813.5 | 1659 | 0 | 779.5 | 2761.5 | 76 | 0 | 343.5 | 95 | 0 | 0.5 | 0 |  |  | Max Temp. in Dhaka |  | 22.6°C
24:00 | 2313 | 728 | 1657 | 0 | 708 | 2706 | 76 | 0 | 312 | 96 | 0 | 1 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 215.769 MKWHr Energy Not Served 1.463 MKWHr Energy Requirement 217.232 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2024-01-23
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1104720
2 | Karnaphuli Hydro PP Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 736000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [6 empty] | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 15 |  | 17 | 17 | 17 | 17 | 17 | 17 | 8 | 205619
| Teknaf 20MW PP (Solartech) | [6 empty] | 0 | 2 | 9 | 17 | 20 | 20 | 19 | 17 | 14 | 8 | 2 | [9 empty] | 129060
6 | Sikalbaha 225MW CCPP (Gas) | [10 empty] | 20 | 31 | 30 | 31 | 37 | 51 | 85 | 164 |  | 206 | 213 | 219 | 216 | 213 | 214 | 214 | 1517352
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [12 empty] | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 592568
12 | Hathazari 100 MW peaking PP | [7 empty] | 8 | 40 | 54 | 46 | 48 | 58 | 60 | 72 | 65 | 65 | 66 |  | 66 | 66 | 66 | 66 | 66 | 66 | 64 | 917472
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [6 empty] | 17 | 17 | 17 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 402290
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [8 empty] | 6 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 16 | 16 | 358032
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 335 | 335 | 335 | 335 | 300 | 300 | 300 | 335 | 335 | 335 | 332 | 332 | 332 | 330 | 280 | 280 | 280 | 330 |  | 336 | 335 | 335 | 300 | 300 | 300 | 300 | 7715667
18 | Kodda 300 MW PP Unit-2 (Summit) | [6 empty] | 20 | 50 | 81 | 81 | 81 | 80 | 72 | 55 | 47 | 47 | 50 | 112 |  | 130 | 130 | 130 | 130 | 130 | 45 | 45 | 1427673
19 | Ashuganj 195 MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 80 | 132 | 142 | 117 | 117 | 160 | 103 | 16 | 16 | 16 | 16 |  | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 1037090
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4441500
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 280 | 280 | 280 | 280 | 280 | 300 | 395 | 404 | 412 | 440 | 447 | 447 | 447 | 447 | 439 | 370 | 351 | 353 |  | 400 | 350 | 363 | 324 | 320 | 285 | 285 | 8645453
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 38 | 44 | 45 | 45 | 41 | 43 | 44 | 44 |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 1049256
33 | Ashuganj 225 MW CCPP | 160 | 159 | 160 | 160 | 160 | 160 | 160 | 161 | 160 | 160 | 108 |  |  | 128 | 141 | 158 | 155 | 155 |  | 157 | 157 | 158 | 157 | 159 | 159 | 159 | 3436000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 285 | 310 | 285 | 290 | 290 | 315 | 340 | 300 | 320 | 295 | 300 | 310 | 315 | 280 | 280 | 275 | 305 | 350 |  | 305 | 305 | 305 | 280 | 280 | 280 | 280 | 7710300
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | 40 | 40 | 40 | 40 | 38 | 40 | 40 | 45 | 52 | 50 | 52 | 52 | 53 | 54 | 52 | 50 | 52 | 52 |  | 44 | 40 | 40 | 40 | 40 | 40 | 40 | 1082400
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 353 | 353 | 353 | 353 | 330 | 345 | 402 | 402 | 402 | 404 | 416 | 418 | 420 | 402 | 397 | 370 | 371 | 401 |  | 401 | 400 | 401 | 373 | 366 | 366 | 366 | 9259200
Meghnaghat Unique power
| Summit Meghanghat-2 589 MW(Gas) | 71 | 66 | 65 | 65 | 65 | 66 | 67 | 65 | 75 | 70 | 70 | 70 | 70 | 70 | 35 | 70 | 65 | 71 |  | 49 | 30 | 40 | 68 | 63 | 63 | 46 | 1494091
40 | Meghnaghat 450 MW CCPP(MPL) | 400 | 350 | 350 | 350 | 320 | 420 | 380 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 400 | 370 | 450 |  | 450 | 450 | 450 | 450 | 450 | 400 | 400 | 9604500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 76 | 76 | 78 | 88 | 86 | 87 | 75 | 75 | 65 | 33 | 33 | 33 | 30 | 27 | 28 | 32 | 34 | 35 |  | 34 | 34 | 44 | 78 | 74 | 71 | 73 | 1304640
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 0 | 2 | [18 empty] | 2030
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 46 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1017000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 22 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 41 | 40 | 764760
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 62 | 62 | 59 | 59 | 59 | 59 | 58 | 40 | 40 | 40 | 59 |  | 63 | 63 | 60 | 60 | 40 | 40 | 40 | 1361280
48 | Shahjibazar 86 MW PP (Shahjibazar) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 81 | 81 | 81 | 82 | 82 | 82 | 82 | 87 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1944000
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 488000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 250020
54 | Hobiganj 11 MW PP Cofidence-E
55 | Fenchugonj 51 MW PP (Barakatullah)
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 397392
57 | Bibiana-II 341 MW CCPP (Summit) | 295 | 300 | 305 | 300 | 295 | 310 | 305 | 320 | 315 | 285 | 300 | 315 | 315 | 295 | 280 | 280 | 300 | 305 |  | 300 | 301 | 280 | 305 | 290 | 280 | 280 | 7326000
| Bibiyana South 400 MW | 265 | 255 | 245 | 245 | 245 | 238 | 236 | 245 | 270 | 340 | 400 | 360 | 360 | 400 | 400 | 400 | 400 | 380 |  | 360 | 330 | 310 | 310 | 280 | 275 | 275 | 7417300
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 5 | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 65452
59 | Tangail Palli Power Gen 22 MW | [13 empty] | 2 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 71040
60 | Barabkunda 22 MW PP (Regent) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 13 | 16 | 15 | 15 | 11 | 13 | 13 | 15 | 16 |  | 17 | 17 | 16 | 16 | 16 | 13 | 13 | 295008
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 84 | 78 | 76 | 82 | 80 | 84 | 84 | 98 | 100 | 100 | 110 | 110 | 118 | 110 | 106 | 110 | 112 | 112 |  | 108 | 108 | 108 | 104 | 100 | 94 | 96 | 2364480
64 | Malancha, Ctg. EPZ (United) | 15 | 16 | 27 | 31 | 40 | 42 | 6 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 0 | 4 | 10 | 13 |  | 20 | 16 | 16 | 13 | 16 | 17 | 20 | 337920
65 | Feni 22 MW PP (Doreen) | 16 | 16 | 13 | 13 | 13 | 13 | 13 | 13 | 10 | 10 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 309996
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 180540
67 | Jangalia 33 MW PP (Summit) | [13 empty] | 14 | 25 | 29 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 314700
68 | Cumilla 25 MW PP (Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 9 | 12 | 12 | 12 | 14 | 16 | 15 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 350350
69 | Summit Ashulia | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 432000
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 15 | 22 | 10 | 22 | 22 | 22 | 22 | 12 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 488160
71 | Maona 33 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 26 | 785520
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 17 | 28 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 30 | 30 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 615400
73 | Ghorashal 108 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 289590
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | 14 | [5 empty] | 2 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 19 | 47 | 47 | 73 |  | 78 | 78 | 78 | 78 | 69 | 50 | 47 | 677880
| Manikgonj 162MW PP(MPGL) | [10 empty] | 17 | 35 | [7 empty] | 17 | 17 |  |  |  |  | 0 | 96480
77 | Siddhirganj 100 PP(Dutch Bangla) | [6 empty] | 38 | 80 | 83 | 76 | 83 | 85 | 86 | 92 | 92 | 57 | 50 | 70 |  | 93 | 93 | 92 | 53 | 25 | 18 | 17 | 1167360
78 | Gazipur 52 MW PP | [6 empty] | 4 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 8 | 205440
79 | Kodda 150 MW PP | [6 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 39 | 98 |  | 98 | 98 | 98 | 32 | 16 | 16 | 16 | 609120
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [6 empty] | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 151757
| Gazipur 100 MW PP | [6 empty] | 5 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 88 |  | 88 | 88 | 88 | 88 | 70 | 70 | 17 | 726720
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 23039
| Jodiac Power | [8 empty] | 4 | 17 | 17 | 17 | 17 | 17 | 17 | [10 empty] | 0 | 123811
| Karnaphuli Power Ltd. | 17 | [5 empty] | 5 | 17 | 17 | 17 | 17 | 17 | 17 | 31 | 23 | 22 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 359630
82 | Madanganj 102 PP(Summit) | [6 empty] | 20 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 83 | 54 | 34 | 45 |  | 82 | 82 | 82 | 82 | 82 | 35 | 32 | 1108942
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [6 empty] | 15 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 17 | 13 | 0 | 374483
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | [6 empty] | 30 | 63 | 76 | 85 | 85 | 87 | 93 | 93 | 92 | 60 | 50 | 61 |  | 96 | 100 | 100 | 96 | 70 | 13 | 9 | 1249920
| Meghnaghat 104 MW PP (OPCL) | 15 | [5 empty] | 7 | 18 | 20 | 33 | 35 | 39 | 52 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 54 | 54 | 54 | 54 | 54 | 825600
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [5 empty] | 9 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 36 | 36 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 424920
92 | Fenchuganj 44 MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1247293
94 | Gagnagar 102 MW PP (Digital Power) | [6 empty] | 40 | 50 | 58 | 58 | 58 | 66 | 66 | 66 | 66 | 66 | 66 | 76 |  | 91 | 91 | 91 | 91 | 91 | 66 | 66 | 1196064
95 | Patenga 50MW PP (Baraka) | 6 | [5 empty] | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 16 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 6 | 204480
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 | [5 empty] | 5 | 5 |  | 5 | 5 | 6 | 6 |  |  | 0 | 30720
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [10 empty] | 7 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 220680
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 17 |  | 35 | 35 | 35 |  |  |  | 0 | 66833
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 140 | 140 | 163 | 163 | 110 | 110 | 80 | 80 | 112 | 117 | 40 | 40 | 70 | 130 | 163 |  | 163 | 163 | 163 | 130 | 130 | 130 | 130 | 3123818
102 | Sarishabari 3 MW Solar Plant | [7 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 0 | 0 | [9 empty] | 9200
103 | Kamalaghat 54 MW PP(Banco Energy) | [11 empty] | 17 | 17 | 17 | [11 empty] | 0 | 50040
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 9 |  |  |  | 7 | 12 | 55 | 56 | 56 | 58 | 58 | 58 | 67 | 58 | 58 | 58 | 58 | 68 |  | 68 | 68 | 68 | 68 | 9 | 9 | 9 | 964800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [6 empty] | 8 | 17 | 17 | 35 | 45 | 53 | 53 | 53 | 39 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 19 | 17 | 17 | 616896
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 |  |  |  |  | 2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 474240
116 | Chandpur 200 MW (Desh energy) | 17 |  |  |  |  | 1 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 341760
117 | Ashuganj 150 MW PP (Midland) | 10 | [5 empty] | 5 | 6 | 6 | 6 | 5 | 6 | 6 | 6 | 6 | 6 | 5 | 10 |  | 8 | 15 | 18 | 18 | 20 | 20 | 20 | 197381
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 9 |  |  |  |  | 2 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 183600
| Anwara 300 MW PP (United) | [6 empty] | 16 | 16 | 16 | 49 | 49 | 49 | 52 | 52 | 52 | 52 | 102 | 105 |  | 105 | 107 | 107 | 107 | 107 | 16 | 16 | 1021200
| Juldah unit-2 (Acorn) | 25 |  |  |  |  | 11 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 481920
| Anlima Energy Ltd. | 17 |  |  |  |  | 1 | 17 | 17 | 17 | 17 | 17 | 17 | 52 | 111 | 121 | 116 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 691255
| Bhairob 54.5 MW | 17 | [11 empty] | 13 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 236880
| Spectra Solar Plant Ltd. | [6 empty] | 0 | 3 | 10 | 19 | 27 | 29 | 29 | 26 | 18 | 10 | 2 | [9 empty] | 171363
| Chandpur 115(Doreen) | [14 empty] | 1 | 18 | 23 | 18 |  | 18 | [5 empty] | 0 | 82560
| Kanchan Purbachal Power Generation Ltd. | [16 empty] | 28 | 25 |  | 17 | 17 | 17 | 17 | 17 | 17 |  | 146160
| Mirsharai 150 MW (Oil) | [6 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 322836
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 11 | 8 | 9 | 8 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 50400
| Matarbari 2*600 MW (CPGCL) | 419 | 421 | 421 | 420 | 421 | 419 | 420 | 417 | 418 | 419 | 419 | 419 | 419 | 418 | 333 | 216 | 149 | 150 |  | 271 | 270 | 270 | 271 | 272 | 271 | 270 | 8523636
120 | Eastern Zone Total | 4217 | 3994 | 3973 | 3952 | 3878 | 4101 | 4596 | 4987 | 5212 | 5344 | 5434 | 5441 | 5596 | 5620 | 5316 | 5055 | 5107 | 5724 |  | 6011 | 5903 | 5886 | 5643 | 5371 | 4907 | 4761 | 120819938
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [10 empty] | 16 | 16 | 16 |  |  |  |  | 32 |  | 32 | 32 | 32 | 16 |  |  | 0 | 145920
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [10 empty] | 3 | 12 | 11 | 11 | 11 | 16 | 35 | 46 |  | 32 | 28 | 28 | 23 | 23 | 17 | 11 | 251520
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [7 empty] | 35 | 35 | 72 | 93 | 93 | 93 | 93 | 93 | 70 | 70 | 84 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 1352160
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 1 | 12 | 32 | 62 | 76 | 77 | 73 | 63 | 49 | 27 | 7 | [9 empty] | 484560
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [6 empty] | 2 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 54 |  | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 427200
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 220 | 222 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 220 | 220 | 220 | 222 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5328682
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 108960
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 250 | 250 | 250 | 200 | 200 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 220 | 220 | 208 | 200 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 5698200
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 100 | 135 | 135 | 135 | 135 |  | 135 | 135 | 135 | 135 | 135 | 80 | 80 | 3147000
140 | Bhola 33 MW PP (Venture) | 17 | 16 | 15 | 15 | 15 | 15 | 16 | 16 | 16 | 15 | 15 | 17 | 18 | 17 | 13 | 13 | 13 | 18 |  | 18 | 19 | 19 | 20 | 20 | 19 | 18 | 388500
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [15 empty] | 8 | 8 | 8 |  | 8 | [5 empty] | 0 | 30375
143 | Gopalganj 100 MW Peaking PP | [10 empty] | 10 | 12 | 10 | 10 | 10 | 18 | 22 | 28 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 218240
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 571 | 429 | 429 | 429 | 430 | 430 | 559 | 660 | 642 | 642 | 669 | 765 | 765 | 765 | 899 | 897 | 897 | 830 |  | 794 | 793 | 793 | 793 | 899 | 899 | 728 | 16301090
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 540 | 520 | 480 | 440 | 430 | 460 | 600 | 622 | 622 | 622 | 622 | 622 | 622 | 590 | 520 | 480 | 490 | 530 |  | 622 | 622 | 622 | 622 | 570 | 550 | 550 | 14597300
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4131000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [16 empty] | 32 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 266592
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 1 | 3 | 4 | 1 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 24960
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 300 | 414 | 414 | 414 | 414 | 414 | 370 | 414 | 414 | 409 | 392 | 375 | 364 | 349 | 331 | 318 | 319 | 319 |  | 319 | 320 | 319 | 331 | 334 | 335 | 346 | 8852909
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [11 empty] | 4 | 4 | 14 | 15 | 15 | 15 | 15 |  | 15 | 15 | 16 | 16 | 15 | 15 | 15 | 159594
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 144000
165 | Amnura 50 MW PP(Sinha) | [7 empty] | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 14 | 14 | 14 |  | 21 | 21 | 21 | 21 | 21 |  | 0 | 334800
166 | Katakhali 50 MW PP (Northern) | [6 empty] | 25 | 34 | 34 | 34 | 25 | 25 | 34 | 34 | 34 | 16 | 16 | 34 |  | 34 | 34 | 34 | 25 |  |  |  | 422253
167 | Katakhali 50 MW Peaking PP | [11 empty] | 15 | 26 | 34 | 34 | 24 | 24 | 25 |  | 32 | 32 | 34 | 32 | 32 | 32 | 24 | 308898
168 | Santahar 50 MW Peaking PP | [17 empty] | 20 |  | 25 | 30 | 25 | 25 |  |  |  | 73774
169 | Natore 52 MW PP (Rajlanka) | [6 empty] | 8 | 8 | 8 | 8 | [6 empty] | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 97286
170 | Chapainawabganj 100 MW Peaking PP | [11 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 89 |  | 91 | 91 | 91 | 91 | 91 | 91 | 44 | 867344
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [15 empty] | 8 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 |  | 0 | 259584
172 | Confidence Power Bogura Unit-1 113 MW | [15 empty] | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 |  | 0 | 254592
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 3 | [5 empty] | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 8 | 11 | 13 | 33 | 40 |  | 41 | 35 | 34 | 34 | 6 | 6 | 6 | 271929
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 2 | 4 | 5 | 5 | 5 | 5 | 4 | 2 | 1 | [9 empty] | 32420
178 | Energypac Power Venture Thakurgaon Ltd. | [15 empty] | 17 | 17 | 70 |  | 70 | 70 | 70 | 70 | 17 | 17 | 0 | 342912
| Intraco Solar 30 MW | [6 empty] | 0 | 3 | 7 | 13 | 26 | 28 | 26 | 24 | 16 | 8 | 2 | [9 empty] | 158263
| Adani Power Jharkhanda Ltd | 1358 | 1141 | 910 | 906 | 866 | 867 | 872 | 932 | 949 | 1072 | 1065 | 1271 | 1365 | 1365 | 1313 | 1269 | 1268 | 1398 |  | 1470 | 1466 | 1463 | 1472 | 1436 | 1291 | 1181 | 28722909
178 | Teesta Solar Limited | [7 empty] | 14 | 37 | 79 | 120 | 137 | 132 | 111 | 76 | 35 | 9 | [9 empty] | 743380